[7 empty] | 7179 | 20427 | 1632843 | 2019-01-21 03:00 | 2019-01-21 18:30 | 930 | 11kV | 2790 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191156 A Phase DOLF : 5 Amp Excluded OMS 1632444 | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-01-21 | N | 930 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2038.8497
[7 empty] | 5500 | 1975 | 1632538 | 2019-01-21 21:43 | 2019-01-21 23:06 | 83 | 11kV | 83 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191159 B Phase DOLF : 10 Amp Excluded OMS 1632538 | January | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-01-21 | N | 83 | N | 20 | Y | Y | 1.1101 | 39.4971 | 60.654
[7 empty] | 7056 | 19167 | 1632543 | 2019-01-21 23:11 | 2019-01-22 00:45 | 94 | 11kV | 43456 | 1159 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | At S4545 Meadowbank - 11kv Panel 41 "Lovell Russell" tripped on: Relays: EF, OC(led 2), fault check, EFI Signals: 11kv trip Remarks: Possum found at base of PT.85 with two 50A drop out fuses operated. The HDO fuse may not have graded with feeder protection or possum has bridged across fuses and across to the other phases | January | 2019 | 2019Q3 | 2019 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2019-01-21 | N | 37.4944 | N | 20 | Y | Y | 1.1101 | 39.4971 | 31756.3631
[7 empty] | 6190 | 9941 | 1632553 | 2019-01-22 03:17 | 2019-01-22 04:45 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191160 3 Phase DOLF : 31 Amp Excluded OMS 1632553 | January | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2019-01-22 | N | 88 | N | 2 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 6899 | 17581 | 1632511 | 2019-01-21 18:58 | 2019-01-22 10:15 | 917 | 11kV | 4742 | 13 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 191158 1 fault operation Earth fault Faulty lightning arrestors on 47516 Excluded OMS 1632511 & 1632550 | January | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-01-21 | N | 364.7692 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3465.3137
[7 empty] | 6192 | 9957 | 1632377 | 2019-01-21 13:35 | 2019-01-22 17:00 | 1645 | 11kV | 17891 | 95 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV CB PA13 From UGOH to LB61388 to IR64691 tee PT18615 HV bond off Cause: bond off pole no PR508 See 1633113,6 ex 1632377,93,600 | January | 2019 | 2019Q3 | 2019 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2019-01-21 | N | 188.3263 | N | 20 | Y | Y | 1.1101 | 39.4971 | 13074.2151
[7 empty] | 6483 | 13113 | 1632766 | 2019-01-22 19:40 | 2019-01-22 21:25 | 105 | 11kV | 26694 | 276 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @Sub35370 Galston ZN EX Panel #2 labelled Galston High School section of feeder interrupted from LB 196 Abnormal: LB62157 closed, LB1548 and LB408 open due to DMA Remarks: interrupted for safety reasons. Tree on section of 11kv CCT between B 196 and LB 914 tee PT 651 Carters Galson | January | 2019 | 2019Q3 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2019-01-22 | N | 96.7174 | N | 2 | N | N | 1.1101 | 39.4971 | 19507.1879
[7 empty] | 6694 | 15159 | 1632822 | 2019-01-23 03:14 | 2019-01-23 04:28 | 74 | 11kV | 86876 | 1174 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN9550 Gwaley Bay Panel No.4 "Feeder tripped and reclosed and tripped on Signals: 11kv trip Relays: B & C phase O/C EFI: nil Abnormal: LB47897 closed with LB47770 open Remarks: cause not ascertained. Dop patrolled feeder and found no fault. Possible transient phase to phase fault on OH | January | 2019 | 2019Q3 | 2019 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Veg | 2019-01-23 | N | 74 | N | 8 | N | N | 1.1101 | 39.4971 | 63486.4184
[7 empty] | 6570 | 14043 | 1632925 | 2019-01-23 12:04 | 2019-01-23 13:14 | 70 | 11kV | 130060 | 1858 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN35400 NORTH SYDNEY 11kV CB PA110 "Alfred Bray" tripped on A & B phase O/C and Earth Fault EFI 11kv trip EFI's Nil Cause: UG Fault. Frontline 11kV feeder fault from Zn35400 Nth Sydney Panel 110 to S48019SwA to S6211SwB | January | 2019 | 2019Q3 | 2019 | ZN35400:PA110 | ZN35400:PA110 | ZN35400/000110 | NORTH SYDNEY | UG | Not Veg | 2019-01-23 | N | 70 | N | 8 | N | N | 1.1101 | 39.4971 | 95044.0119
[7 empty] | 6226 | 10217 | 1632960 | 2019-01-23 13:32 | 2019-01-23 14:33 | 61 | 11kV | 3843 | 63 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 191201 B Phase DOLF faulty dolf (B phase) needs to be replaced at sub 8117, LV supply back on at 1433hrs Fauly DOLF - Restored by LV // Excluded OMS 1632960 | January | 2019 | 2019Q3 | 2019 | 257:81999 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2019-01-23 | N | 61 | N | 8 | N | N | 1.1101 | 39.4971 | 2808.3511
[7 empty] | 5789 | 5459 | 1633016 | 2019-01-23 14:35 | 2019-01-23 16:54 | 139 | 11kV | 172310 | 1260 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @Zn1290 Leightonfield 11kv VCB panel 9 "S-7472" feeder tripped re-closed tripped and locked out on Relays: B phase earth fault O/C, SEF, lockout, EFI, trip indicator Field EFI's: Signals: 11kv trip Remarks: tree trimming in area. Tree trimmers in gurney rd dropped limb on 11kv O/H. Fault current burnt off bonds at UGOH between S-47019 and S-35957 L/men on site will repair. | January | 2019 | 2019Q3 | 2019 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Veg | 2019-01-23 | N | 136.754 | N | 8 | N | N | 1.1101 | 39.4971 | 125919.0657
[7 empty] | 6221 | 10189 | 1633200 | 2019-01-23 19:22 | 2019-01-23 22:00 | 158 | 11kV | 948 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191208 3 phase DOLF : 10 Amp Also blown A phase 10A DOLF at sub 51151 Excluded OMS 1633200 | January | 2019 | 2019Q3 | 2019 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2019-01-23 | N | 158 | N | 8 | N | N | 1.1101 | 39.4971 | 692.7704
[7 empty] | 5681 | 4428 | 1633204 | 2019-01-23 19:45 | 2019-01-23 23:05 | 200 | 11kV | 400 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191209 B Phase DOLF : 10 Amp Excluded OMS 1633204 | January | 2019 | 2019Q3 | 2019 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2019-01-23 | N | 200 | N | 8 | N | N | 1.1101 | 39.4971 | 292.3082
[7 empty] | 5369 | 416 | 1633212 | 2019-01-23 20:44 | 2019-01-23 23:50 | 186 | 11kV | 372 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191210 C Phase DOLF : 10 Amp Excluded OMS 1633212 | January | 2019 | 2019Q3 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2019-01-23 | N | 186 | N | 8 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 6983 | 18344 | 1633234 | 2019-01-24 07:19 | 2019-01-24 08:20 | 61 | 11kV | 61 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191211 A Phase DOLF : 31 Amp Myna Bird Excluded OMS 1633234 | January | 2019 | 2019Q3 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2019-01-24 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 5922 | 6647 | 1633459 | 2019-01-24 22:39 | 2019-01-24 23:37 | 58 | 11kV | 38932 | 970 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.6 tripped & reclosed on: B phase O/C B phase bond open circuit adj PT13554 See 1633626 1633627 | January | 2019 | 2019Q3 | 2019 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2019-01-24 | N | 40.1361 | N | 2 | N | N | 1.1101 | 39.4971 | 28450.3573
[7 empty] | 7010 | 18604 | 1633468 | 2019-01-25 00:48 | 2019-01-25 13:30 | 762 | 11kV | 60041 | 886 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | Ex ZN14892 CHARMHAVEN section of 11kV CB PA8 'Charmhaven' tripped, reclosed, tripped locked out on: Relays: O/C and Earth Fault (50T ABC), timing, L/O, EFI Signals: 11kv trip, #1 Tx GE Cause: fire S63308 Forrow Bannister destroyed by fire. NSWFR incident 16413 reports Kiosk 18389 on fire near carpark See 1634967,8,9,70,1 ex 1633467,8,9,78 | January | 2019 | 2019Q3 | 2019 | ZN14892:PA8 | ZN14892:PA8 | ZN14892/000008 | CENTRAL COAST | UG | Not Veg | 2019-01-25 | N | 67.7664 | N | 7 | N | N | 1.1101 | 39.4971 | 43876.1919
[7 empty] | 5599 | 3558 | 1635027 | 2019-01-23 19:24 | 2019-01-25 13:32 | 2528 | 11kV | 2528 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191204 1 fault operation Overcurrent Bayswater control room notified. Will call when OK to re-energise. | January | 2019 | 2019Q3 | 2019 |  |  |  | SINGLETON | OH | Veg | 2019-01-23 | N | 2528 | N | 8 | N | N | 1.1101 | 39.4971 | 1847.3878
[7 empty] | 5629 | 3790 | 1633605 | 2019-01-25 14:22 | 2019-01-25 15:50 | 88 | 11kV | 264 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191232 Single phase DOLF : 10 Amp Tx Volts 238V Excluded OMS 1633605 & 1633614 | January | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-01-25 | N | 88 | N | 7 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 6778 | 15988 | 1633620 | 2019-01-25 12:49 | 2019-01-25 16:30 | 221 | 11kV | 442 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 191231 Single phase DOLF assembly DOLF assembly broken. Excluded OMS 1633620, 1633574 | January | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-01-25 | N | 221 | N | 7 | N | N | 1.1101 | 39.4971 | 323.0006
[7 empty] | 7121 | 19711 | 1633670 | 2019-01-25 16:52 | 2019-01-25 17:51 | 59 | 11kV | 118989 | 2045 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | ZN12640 UMINA 11kV CB PA13 'Umina Aux No.1' fdr tripped and locked out on: Relays: A & b Phase IOC EFI's Nil Cause: Birds caused flashover @ PT18022. no apparent damage, supply restored See 1635079,80 wx 1633670,2,3 | January | 2019 | 2019Q3 | 2019 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2019-01-25 | N | 58.1853 | N | 7 | N | N | 1.1101 | 39.4971 | 86953.6516
[7 empty] | 6573 | 14094 | 1633681 | 2019-01-25 17:57 | 2019-01-25 19:05 | 68 | 11kV | 7140 | 105 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191233 A Phase DOLF : 31 Amp Supply off 1808hrs back on 1905hrs A phase 31.5a DOLF sub 1198 no cause found Excluded OMS 1633681, 1633693 | January | 2019 | 2019Q3 | 2019 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Veg | 2019-01-25 | N | 68 | N | 7 | N | N | 1.1101 | 39.4971 | 5217.7014
[7 empty] | 5700 | 4660 | 1633698 | 2019-01-25 18:59 | 2019-01-25 19:50 | 50.9 | 11kV | 5191.8 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191234 C Phase DOLF : 20 Amp Excluded OMS 1633716 | January | 2019 | 2019Q3 | 2019 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Veg | 2019-01-25 | N | 50.9 | N | 7 | N | N | 1.1101 | 39.4971 | 3794.0143
[7 empty] | 5365 | 314 | 1634407 | 2019-01-25 21:30 | 2019-01-25 22:15 | 45 | 11kV | 135 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 191235 Main off pin insulator pole AL-10147 | January | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-01-25 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 7058 | 19202 | 1633762 | 2019-01-26 09:23 | 2019-01-26 10:57 | 93.65 | 11kV | 7585.65 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV CB PA5 'Wyong' fdr RE45017 Whiteman tripped reclosed tripped and locked out on O/C Cause: Tree branch removed by DOp beyond CP43160 | January | 2019 | 2019Q3 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-01-26 | N | 93.65 | N | 3 | N | N | 1.1101 | 39.4971 | 5543.3693
[7 empty] | 5777 | 5387 | 1633775 | 2019-01-26 10:37 | 2019-01-26 12:06 | 89 | 11kV | 140589 | 1701 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn9245 Engadine - Pnl.21L tripped on: IOC (A, B & C phase) Field EFIs: S48146 S91999 S64942 Abnormal: LB35051 Open with S9230 Sw/B closed UGOH cable near SE exploded between LB48596 to LB35524 to S9288 Sw/A See 1635037 1635038 | January | 2019 | 2019Q3 | 2019 | ZN9245:PA21 | ZN9245:PA21 | ZN09245/000021 | SUTHERLAND | Unknown | Unknown | 2019-01-26 | N | 82.6508 | N | 3 | N | N | 1.1101 | 39.4971 | 102738.2945
[7 empty] | 5958 | 7007 | 1633831 | 2019-01-26 14:42 | 2019-01-26 17:00 | 138.4333 | 11kV | 138.4333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191239 A & B Phase DOLF : 10 Amp CUSTOMER JUST NOTICED IT. STORM WAS WED | January | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-01-26 | N | 138.4333 | N | 3 | N | N | 1.1101 | 39.4971 | 101.163
[7 empty] | 5881 | 6186 | 1633962 | 2019-01-27 14:12 | 2019-01-27 15:42 | 90 | 11kV | 125910 | 1399 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | At S965 Pennant Hills Panel 33 tripped on A and B phase Overcurrent lockout reclose tim delay Cause: Tree branch on OH mains Tree branch near PT1693 See 1635040 LV// 1636501 ex 1633952,5,8,9,62 | January | 2019 | 2019Q3 | 2019 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2019-01-27 | N | 90 | N | 12 | N | N | 1.1101 | 39.4971 | 92011.3143
[7 empty] | 7087 | 19483 | 1633982 | 2019-01-27 15:20 | 2019-01-27 15:55 | 35 | 11kV | 350 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN12690 BERKELEY VALE 11kV CB PA11 'S14772' fdr has tripped Signals: 11kv trip, Tx3 GE Relays: EF, EFI EFI's: Nil Cause: UG Fault frontline feeder between Zn12690 Berkeley Vale panel 11 and S14772SwA | January | 2019 | 2019Q3 | 2019 | ZN12690:PA11 | ZN12690:PA11 | ZN12690/000011 | CENTRAL COAST | UG | Not Veg | 2019-01-27 | N | 35 | N | 12 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 7090 | 19509 | 1634030 | 2019-01-27 18:23 | 2019-01-27 20:10 | 107 | 11kV | 317643 | 3020 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3922 Drummoyne, 11kv Panel 11 "S35633 Thornley Victoria" has tripped on Relays: earth fault, fault check, EFI Signals: Tx1 group earth, zone earth, 11kv trip Field EFI's: S35633, S7738 Abnormal: closed at Sw/A ar S35090 Cameron Church, Open at Sw/B at S5672 Caroline Lane Remarks: 11kv underground fault from S7738 Renwick Roseby Sw/B to S3874 P.M.G Balmain Sw/A to S2872 Darling Birch Sw/A | January | 2019 | 2019Q3 | 2019 | ZN3922:PA11 | ZN3922:PA11 | ZN03922/000011 | INNER WEST | UG | Not Veg | 2019-01-27 | N | 105.1798 | N | 12 | N | N | 1.1101 | 39.4971 | 232124.1355
[7 empty] | 5833 | 5752 | 1634040 | 2019-01-27 18:46 | 2019-01-27 21:15 | 149.3667 | 11kV | 1493.6667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191254 Single phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | January | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-01-27 | N | 149.3667 | N | 12 | N | N | 1.1101 | 39.4971 | 1091.5275
[7 empty] | 6327 | 11187 | 1633963 | 2019-01-27 14:46 | 2019-01-27 21:55 | 429 | 11kV | 63001 | 589 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex ZN35370 GALSTON section of 11kV CB PA4 RE428 Bayfield Road tripped, reclosed and locked out on: Relays: OC trip, Lockout EFI's: Nil Fault indicators: LB62159 Abnormal: LB3252 Open LB62159 closed Cause: OH down. adjacent PT2149 See 1635373,80,1 Ex 1633963,4,85,4022 | January | 2019 | 2019Q3 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2019-01-27 | N | 106.9626 | N | 12 | N | N | 1.1101 | 39.4971 | 46039.2726
[7 empty] | 6413 | 12203 | 1634065 | 2019-01-27 20:05 | 2019-01-27 22:55 | 170 | 11kV | 288123 | 2112 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN12620 NORAVILLE 11kV CB PA7 'Fravent St' fdr has tripped Singals: 11kv trip, Tx1, 2 and 3 no volts Relays: EF, EFI EFI's S14590 S14589 S48014 S14588 S14587 S14695 did not operate until section below was tried back. S14397 was found operated Cause: UG Fault between S14695SwB and S14397SwA T/Con - EFI issues - EFI S14695 did not operate until faulted section after it was tried back, S14397 was found operated on initial diagnosis. T/PE - Spring charge fuse on panel 7 at Norvaille blew at some time requiring DOp to attend the zone so the feeder could be tried back See 1634870,1,2,3 ex 1634065 | January | 2019 | 2019Q3 | 2019 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | UG | Not Veg | 2019-01-27 | N | 136.4219 | N | 12 | N | N | 1.1101 | 39.4971 | 210551.7902
[7 empty] | 5613 | 3667 | 1634061 | 2019-01-27 19:48 | 2019-01-27 23:15 | 207.2833 | 11kV | 207.2833 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191248 Single phase DOLF : 10 Amp Tx Volts : 242V Excluded OMS 1634104 | January | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-01-27 | N | 207.2833 | N | 12 | N | N | 1.1101 | 39.4971 | 151.4765
[7 empty] | 6310 | 11016 | 1634032 | 2019-01-27 18:27 | 2019-01-27 23:45 | 318 | 11kV | 96709 | 1380 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | ZN36200 EMPIRE BAY 11kV CB PA8 'S49860 fdr has tripped Signals: 11kv trip Relays: EF Trip, EFI, Rec Timer, LO EFI's: S49860 11kv wire down outside 73 maitland bay dr. located electrically between LB48657 and LB48654 Cause: storm See 1635095,7,8,9 Ex 1634032,8,41 | January | 2019 | 2019Q3 | 2019 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2019-01-27 | N | 70.079 | N | 12 | N | N | 1.1101 | 39.4971 | 70672.0848
[7 empty] | 6741 | 15494 | 1634106 | 2019-01-27 21:44 | 2019-01-27 23:45 | 121 | 11kV | 15843 | 183 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191262 1 fault operation Single phase DOLF : 10 Amp Sensitive Earth Fault ; Substation DOLF Both 10A DOLF at sub 51650 found blown. Excluded OMS No. 1634106 + 1634110 | January | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-01-27 | N | 86.5738 | N | 12 | N | N | 1.1101 | 39.4971 | 11577.5971
[7 empty] | 5649 | 4107 | 1634076 | 2019-01-27 20:58 | 2019-01-28 00:02 | 184 | 11kV | 268314 | 1556 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S3472 Sefton, 11kv Panel 28 "S35463 Baird Buist", S7805 Rangers Ferrier" has tripped on Relays: trip, OC A & C phase, fault check, reclose & lockout, EFI, SEF Signals: 11kv trip Remarks: Bond. S3472 Sefton, ex panel No28 11kv bond off on pole NoRP12551 (UGOH pole) between S46754 Sw/B to S4349 Sw/A. Sw tag @ S46754. | January | 2019 | 2019Q3 | 2019 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-01-27 | N | 172.4383 | N | 12 | N | N | 1.1101 | 39.4971 | 196075.9573
[7 empty] | 7063 | 19307 | 1634143 | 2019-01-28 00:25 | 2019-01-28 04:45 | 260 | 11kV | 1040 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191271 A & C Phase DOLF : 10 Amp Excluded OMS 1634143 | January | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-01-28 | N | 260 | N | 11 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 7005 | 18575 | 1634116 | 2019-01-27 22:04 | 2019-01-28 10:55 | 771 | 11kV | 1270588 | 1851 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | At S9252 Jannali 11kv Panel 25 "Woronora" feeder tripped on Relays: A & C phase overcurrent, EFI, recloser, lockout Signals: 11kv trip Abnormal: Sw/A closed @ S9980 LB 35051 open, Sw/B @ S9230, Sw/A open @ S9288 Remarks: UG fault. S9252 Jannali, ex panel No25, LB35248 etc feeder HV UGOH is defective between AB35340 to AB35478 to S48498 Sw/A | January | 2019 | 2019Q3 | 2019 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | UG | Not Veg | 2019-01-27 | N | 686.4333 | N | 12 | N | N | 1.1101 | 39.4971 | 928508.2344
[7 empty] | 6261 | 10489 | 1634186 | 2019-01-28 09:13 | 2019-01-28 14:15 | 302 | 11kV | 1101 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 191274 A Phase OHM found only a meter off the ground also sub 51649 was faulty Excluded oms 1634186 | January | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-01-28 | N | 183.5 | N | 11 | N | N | 1.1101 | 39.4971 | 804.5783
[7 empty] | 5885 | 6232 | 1634129 | 2019-01-27 22:24 | 2019-01-28 18:00 | 1176 | 11kV | 93635 | 96 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | Ex ZN15013 TERREY HILLS section of 11kV CB PA10 'terrey hills' 11kV Recloser 20852 McCarrs Creek Rd, tripped, reclosed and locked out on: Relays: OC trip, EF Trip, Lockout EFI's S16910 CP49122: oC C phase fault detection, sectionaliser trip, E/Fault Cause: Lightning/ Surge Arrestor Suspected lightning strike Note: Dee Why OH O/C stood down till 0800 Interrupted for safety @ 1120 to try back section of 11kv feeder from RE20852 mcCarrs Ck Rd Defective UGOH from USL24299 to SwA@S46269 Cottage Point Cowan Surge Arrestors found blown at UGOH below 11kv LK 24299 See 1634899,900,2,3 ex 1634129,233,901 | January | 2019 | 2019Q3 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-01-27 | N | 975.3646 | N | 12 | N | N | 1.1101 | 39.4971 | 68425.6962
[7 empty] | 6536 | 13695 | 1634260 | 2019-01-28 14:25 | 2019-01-28 20:00 | 335 | 11kV | 9480 | 116 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex ZN12600 LISAROW section of 11kV CB PA2 'Holgate' RE41020 Wattle Tree Road North has tripped Relays: OC trip and LO Cause: Tree outside 23 Patterson Cl has pulled down three bays of LV and knocked 11kv wires off all pin insulators on two cross arms See 1635105,6,7 Ex 1634260,4,9,78,330 | January | 2019 | 2019Q3 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2019-01-28 | N | 81.7241 | N | 11 | N | N | 1.1101 | 39.4971 | 6927.7044
[7 empty] | 5820 | 5681 | 1634293 | 2019-01-28 18:01 | 2019-01-28 20:22 | 141 | 11kV | 34997 | 463 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191278 2 fault operation B & C Phase Overcurrent Excluded OMS 1634293 | January | 2019 | 2019Q3 | 2019 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2019-01-28 | N | 75.5875 | N | 11 | N | N | 1.1101 | 39.4971 | 25574.7754
[7 empty] | 5368 | 415 | 1634291 | 2019-01-28 17:52 | 2019-01-28 21:38 | 226 | 11kV | 41820 | 651 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 191277 2 fault operation B & C Phase Overcurrent 3 X Lightning arrestors replaced at ugoh pole AJ-30415 Excluded OMS 1634291 | January | 2019 | 2019Q3 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2019-01-28 | N | 64.2396 | N | 11 | N | N | 1.1101 | 39.4971 | 30560.8225
[7 empty] | 6067 | 8319 | 1634287 | 2019-01-28 17:11 | 2019-01-28 22:35 | 324 | 11kV | 6672 | 40 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 191276 2 fault operation mains down adjacent 11kv links 15719 section isolated for repair. Excluded OMS 1634287 | January | 2019 | 2019Q3 | 2019 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2019-01-28 | N | 166.8 | N | 11 | N | N | 1.1101 | 39.4971 | 4875.7008
[7 empty] | 6997 | 18506 | 1634351 | 2019-01-28 23:01 | 2019-01-28 23:13 | 12 | 11kV | 636 | 53 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 191287 sw 74441 tripped while trying back dolf at sub 71298, sub isolated to replace arrestors, power restored from sw 74441, See #191288/OMS 1635053 | January | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2019-01-28 | N | 12 | N | 11 | N | N | 1.1101 | 39.4971 | 464.77
[7 empty] | 5622 | 3716 | 1634349 | 2019-01-28 22:22 | 2019-01-28 23:35 | 73 | 11kV | 146 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV CB PA26 PT12388 SCENIC PICKETTS 1.2 Right hand side HV fuse 16Amp was blown due to fuse fatigue See 1635109 ex 1634349 | January | 2019 | 2019Q3 | 2019 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2019-01-28 | N | 73 | N | 11 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 6102 | 8829 | 1634338 | 2019-01-28 20:58 | 2019-01-28 23:45 | 167 | 11kV | 167 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 191288 Single phase DOLF : 10 Amp sub isolated to replace arrestors Excluded oms 1634338 | January | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2019-01-28 | N | 167 | N | 11 | N | N | 1.1101 | 39.4971 | 122.0387
[7 empty] | 6430 | 12495 | 1634313 | 2019-01-28 19:14 | 2019-01-29 00:22 | 308 | 11kV | 924 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191289 C Phase DOLF : 10 Amp Excluded OMS 1634313 Note: customers were also affected by wider area outage at same time refer to OMS 1635054 | January | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2019-01-28 | N | 308 | N | 11 | N | N | 1.1101 | 39.4971 | 675.2319
[7 empty] | 6349 | 11420 | 1634306 | 2019-01-28 18:51 | 2019-01-29 02:00 | 429 | 11kV | 83152 | 935 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 191285 2 fault operation A & C Phase Sensitive Earth Fault; Overcurrent 11kV down from ABS 19329 towards pole JU-20949. Repaired burnt off tapping at pole JU-21182. Targets: Aprot - OC A/Cph Bprot - OC A/Cph, SEF Excluded OMS No. 1634306, 1634308, 1634309, 1634312, 1634311, 1634307 | January | 2019 | 2019Q3 | 2019 | 257:81999 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2019-01-28 | N | 88.9326 | N | 11 | N | N | 1.1101 | 39.4971 | 60765.029
[7 empty] | 5585 | 3408 | 1634370 | 2019-01-29 07:16 | 2019-01-29 12:28 | 312 | 11kV | 460 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 191299 A & B Phase Fuse : 80 Amp Main off Insulator | January | 2019 | 2019Q3 | 2019 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2019-01-29 | N | 230 | N | 6 | N | N | 1.1101 | 39.4971 | 336.1544
[7 empty] | 5425 | 1163 | 1634399 | 2019-01-29 09:01 | 2019-01-29 14:05 | 304 | 11kV | 608 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191300 A Phase DOLF : 10 Amp Excluded OMS 1634399 | January | 2019 | 2019Q3 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2019-01-29 | N | 304 | N | 6 | N | N | 1.1101 | 39.4971 | 444.3085
[7 empty] | 6346 | 11406 | 1634647 | 2019-01-29 19:33 | 2019-01-29 22:00 | 147 | 11kV | 294 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191308 Single phase DOLF : 10 Amp Excluded OMS 1634647 | January | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-01-29 | N | 147 | N | 6 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 6469 | 12964 | 1634584 | 2019-01-29 16:19 | 2019-01-29 22:30 | 371 | 11kV | 268951 | 1545 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | ZN35370 GALSTON 11kV CB PA10 'Galston Aux No.2' tripped, reclosed and tripped and locked out Relays: A & C Phase IOC and SEL lock out Signals: 11kv trip, station Aux no.415 Volt Abnormal: LB1548 open, LB408 open, LB62157 closed S6680 SwB Closed & S6048 SwA Open AB2270 flashed over and is now defective and bonded through See 1635471,2,3,4,5,9,80 Ex 1634584,5,94,644,5 | January | 2019 | 2019Q3 | 2019 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | OH | Not Veg | 2019-01-29 | N | 174.0783 | N | 6 | N | N | 1.1101 | 39.4971 | 196541.4581
[7 empty] | 6652 | 14831 | 1634408 | 2019-01-29 22:00 | 2019-01-29 23:35 | 95 | 11kV | 95 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | LID 191309 Leaking transformer replaced Excluded OMS 1634408 | January | 2019 | 2019Q3 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | UG | Not Veg | 2019-01-29 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 6336 | 11256 | 1634654 | 2019-01-29 19:47 | 2019-01-30 01:00 | 313 | 11kV | 240794 | 3890 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | LID 191307 2 fault operations Sensitive Earth Fault; Earth Fault Cable box fdr 2121 caught fire causing outage of fdr 2121, then 2120 and then Tarro zone sub off loaded to allow fire to be extinguished and 11 kv bus bar to be isolated for repairs. sw 2121 SEF, sw 2120 EF, SW 2122 Inst ef & aux RI Excluded OMS 1634654, 1634664, 1634700, 1634705 | January | 2019 | 2019Q3 | 2019 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | UG | Not Veg | 2019-01-29 | N | 61.9008 | N | 6 | N | N | 1.1101 | 39.4971 | 175965.153
[7 empty] | 7178 | 20416 | 1634743 | 2019-01-30 07:51 | 2019-01-30 08:59 | 68 | 11kV | 167370 | 2639 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1285 Greenacre Park Panel 31 "S5729 Anzac Dominon" feeder has tripped Signals: 11kv trip, Zone Earth, Tx4 Group Earth Relays: Panel 31L EFI, B phase timed, lock out relay Remarks: Zn1285 Greenacre Park Panel 31 "S5729 Anzac Dominon" feeder 11kv UG fault between S7100 Anzac Brunker Sw/B to S4864 Hill Crest Nth Sw/A | January | 2019 | 2019Q3 | 2019 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-01-30 | N | 63.4218 | N | 3 | N | N | 1.1101 | 39.4971 | 122309.0594
[7 empty] | 5844 | 5842 | 1635326 | 2019-01-30 15:40 | 2019-01-30 17:15 | 95 | 11kV | 190 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 191326 A Phase 11kV on broken crossarm | January | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-01-30 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 6232 | 10310 | 1635003 | 2019-01-30 22:18 | 2019-01-31 03:30 | 312 | 11kV | 8932 | 1157 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN13000 LAKE MUNMORAH section of 11kV CB PA5 's14743' fdr RE45140 Pinnaroo Colledina tripped and reclosed on EF, OC, IOC PT14292 GAREMA EUCLA 11kV 31.5K Footpath side dropout fuse operated due to fuse fatigue See 1635117,289 ex 1635003 | January | 2019 | 2019Q3 | 2019 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2019-01-30 | N | 7.72 | N | 3 | N | N | 1.1101 | 39.4971 | 6527.2422
[7 empty] | 6923 | 17798 | 1635008 | 2019-01-31 02:59 | 2019-01-31 05:51 | 172 | 11kV | 253011 | 1803 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | @Zn9245 Engadine 11kv Panel No.13 "S9668 Cooper St" feeder tripped, reclosed and locked out Relays: B + C phase IOC, timing & lockout relays Remarks: cause not ascertained. Feeder patrolled by Dop | January | 2019 | 2019Q3 | 2019 | ZN9245:PA13 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Veg | 2019-01-31 | N | 140.3278 | N | 11 | N | N | 1.1101 | 39.4971 | 184892.9762
[7 empty] | 7028 | 18790 | 1635026 | 2019-01-31 09:30 | 2019-01-31 10:14 | 44 | 11kV | 4688 | 107 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | Y | LID 191341 Wire off pin at pole 4I-70113 Small grass fir 2 metre square Excluded OMS 1635026 | January | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-01-31 | N | 43.8131 | N | 11 | N | N | 1.1101 | 39.4971 | 3425.8521
[7 empty] | 5927 | 6707 | 1635009 | 2019-01-31 05:26 | 2019-01-31 12:38 | 432 | 11kV | 33078 | 77 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 191352 2 fault operatioon B Phase Earth Fault Dead possum found at sub 52998. Bph Fault Current: 75A Excluded OMS No. 1635009 | January | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-01-31 | N | 429.5844 | N | 11 | N | N | 1.1101 | 39.4971 | 24172.4268
[7 empty] | 6992 | 18444 | 1635436 | 2019-01-31 15:41 | 2019-01-31 15:45 | 4 | 11kV | 14188 | 3547 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Hot >35C | Y | At Zn10999 Kogarah panel 10 tripped on A phase OC At Zn10993 Hurstville North Panel 22L tripped on OC Cause: Above two feeder tripped wihile switching NAR 34645 (abnormal switching S/A closed at S10224) See OMS 1637536 1637534 | January | 2019 | 2019Q3 | 2019 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | Unknown | Unknown | 2019-01-31 | Y | 4 | N | 11 | N | Y | 1.1101 | 39.4971 | 10368.1719
[7 empty] | 6970 | 18195 | 1635365 | 2019-01-31 14:14 | 2019-01-31 16:20 | 126 | 11kV | 1134 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | Y | LID 191357 A Phase DOLF : 10 Amp Branch caused LV mains to clash. Excluded OMS 1635365. | January | 2019 | 2019Q3 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-01-31 | Y | 126 | N | 11 | N | Y | 1.1101 | 39.4971 | 828.6938
[7 empty] | 7034 | 18872 | 1635441 | 2019-01-31 15:44 | 2019-01-31 17:08 | 84 | 11kV | 96775 | 1316 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | Y | ZN36300 BALGOWLAH NORTH 11kV CB PA5 'S17148 Hope Sydney' fdr tripped on: Relays: Earth Fault (51N), EFI, fault check Signals: Tx1 Group Earth, 11kv trip EFI: S17148 S16758 S16759 S16505 S16506 S16517 S66042 S16508 Cause: UGOH cable on fire located between S16508 to S16509 tee to S16701 See 1636454,5,6 Ex 1635441,67,81 | January | 2019 | 2019Q3 | 2019 | ZN36300:PA5 | ZN36300:PA5 | ZN36300/000005 | NORTHERN BEACHES | Unknown | Unknown | 2019-01-31 | N | 73.5372 | N | 11 | N | N | 1.1101 | 39.4971 | 70720.3156
[7 empty] | 5349 | 32 | 1635507 | 2019-01-31 16:42 | 2019-01-31 17:20 | 38 | 11kV | 76 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | Y | LID 191358 Wire off pin at pole HY-60029 Excluded OMS 1635507 | January | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2019-01-31 | N | 38 | N | 11 | N | N | 1.1101 | 39.4971 | 55.5386
[7 empty] | 5396 | 750 | 1635409 | 2019-01-31 15:09 | 2019-01-31 17:44 | 155 | 11kV | 21810.2 | 141 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | Y | At PT2468 Lyle Ronald ex S4545 Meadowbank Panel 36 50A ASEA HDO blew Cause: Fuse fatigue See OMS 1635413 1635409 | January | 2019 | 2019Q3 | 2019 | ZN4545:PA36 | ZN4545:PA36 | ZN04545/000036 | RYDE | OH | Not Veg | 2019-01-31 | N | 154.6823 | N | 11 | N | N | 1.1101 | 39.4971 | 15938.2509
[7 empty] | 6647 | 14801 | 1635524 | 2019-01-31 17:35 | 2019-01-31 17:51 | 16.4667 | 11kV | 9830.6 | 597 | HV | Overload | Utility Process Issue | Zone STS Transformer | Unplanned | Hot >35C | Y | At S690 Campsie Panel 5 was opened by AOP for load relief TX2 was exceeding rating | January | 2019 | 2019Q3 | 2019 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | Exclude | Not Veg | 2019-01-31 | N | 16.4667 | N | 11 | N | N | 1.1101 | 39.4971 | 7183.9125
[7 empty] | 6389 | 11904 | 1635506 | 2019-01-31 16:51 | 2019-01-31 18:00 | 69 | 11kV | 23547 | 375 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | ZN1610 HOMEBUSH BAY 11kV CB 17 'S8920 Perkins Spitz' has tripped on Relays: C Phase OC, Earth Fault, Trip Signals: 11kv trip EFI: S8920 Cause: 11kv fdr fault from S8920SwB to S1191SwA See 1637483,5 Ex 1635506 | January | 2019 | 2019Q3 | 2019 | ZN1610:PA17 | ZN1610:PA17 | ZN01610/000017 | PARRAMATTA | UG | Not Veg | 2019-01-31 | N | 62.792 | N | 11 | N | N | 1.1101 | 39.4971 | 17207.4531
[7 empty] | 6643 | 14759 | 1635495 | 2019-01-31 16:35 | 2019-01-31 19:30 | 175 | 11kV | 141425 | 1057 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | At Zn129 Hunters Hill Panel 52 tripped on A protn - Trip, A phase, Neutral, IOC and EF B protn - Trip, EFI and IOC Cause: UG cable Fault See OMS 1637578 1637580 1635495 | January | 2019 | 2019Q3 | 2019 | ZN129:PA52 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2019-01-31 | N | 133.7985 | N | 11 | N | N | 1.1101 | 39.4971 | 103349.2187
[7 empty] | 6343 | 11366 | 1635538 | 2019-01-31 17:45 | 2019-01-31 20:28 | 163 | 11kV | 728 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | ZN35900 POTTS HILL 11kV CB 7 'Potts Hill Aux No.1' has tripped on: Relays: 51N Earth Fault, 50TN Earth Fault Check Signals: 11kv trip EFI: S47648 S8529 S76809 . S437 did not operate Cause: 11kV Underground Fault Between S76809SwB to S3770SwA to S3746SwD See 1637497,8,9 Ex 1635538 | January | 2019 | 2019Q3 | 2019 | ZN35900:PA7 | ZN35900:PA7 | ZN35900/000007 | CUMBERLAND | UG | Not Veg | 2019-01-31 | Y | 91 | N | 11 | N | Y | 1.1101 | 39.4971 | 532.0009
[7 empty] | 6185 | 9913 | 1635353 | 2019-01-31 14:04 | 2019-01-31 21:00 | 416 | 11kV | 41551 | 338 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Hot >35C | Y | ZN35900 POTTS HILL 11kV CB PA6 'S3860 Lewis St' has tripped on Relays: OC A&B Phase, Earth Fault, Reclose, Lockout Signals: 11kv trip EFI: S3860 S62911 Cause: Car has hit pole at UGOH SwA side of S49270 Main College See 1637380,2 ex 1635353,94 | January | 2019 | 2019Q3 | 2019 | ZN35900:PA6 | ZN35900:PA6 | ZN35900/000006 | CUMBERLAND | OH | Not Veg | 2019-01-31 | Y | 122.932 | N | 11 | N | Y | 1.1101 | 39.4971 | 30364.2453
[7 empty] | 6393 | 11942 | 1635644 | 2019-01-31 18:48 | 2019-01-31 21:08 | 140.1667 | 11kV | 441805.3333 | 3152 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | At S10999 Kogarah Panel 12 tripped and reclosed and locked out on the 50TBC OC relay Cause not ascertained for outage | January | 2019 | 2019Q3 | 2019 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Veg | 2019-01-31 | Y | 140.1667 | N | 11 | N | Y | 1.1101 | 39.4971 | 322858.3065
[7 empty] | 6166 | 9576 | 1635948 | 2019-01-31 21:19 | 2019-01-31 22:48 | 89 | 11kV | 56693 | 637 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | Y | LID 191359 1 fault operation Faulty ABS 42358 Excluded OMS 1635948 | January | 2019 | 2019Q3 | 2019 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2019-01-31 | Y | 89 | N | 11 | N | Y | 1.1101 | 39.4971 | 41429.5722
[7 empty] | 6998 | 18512 | 1635521 | 2019-01-31 17:25 | 2019-01-31 23:23 | 358 | 11kV | 365478 | 1084 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | At S9245 Engadine Panel 1 feeder tripped on B/C OC and EFI Cause: Tree branch brought down OH. See 1637543,4,5,46724 Ex 1635521,5 | January | 2019 | 2019Q3 | 2019 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Veg | 2019-01-31 | N | 337.1568 | N | 11 | N | N | 1.1101 | 39.4971 | 267080.5426
[7 empty] | 6323 | 11146 | 1635571 | 2019-01-31 18:05 | 2019-02-01 00:30 | 385 | 11kV | 108089 | 1684 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | At Zn10994 Mortdale Panel 7 tripped and reclosed on Relays: A phase IOC and EFI Signals; 11kV trip and No1 group earth Cause: OH down @ 84 Queens Rd See OMS 1637518 1637520 1637521 1635996 1635571 | January | 2019 | 2019Q3 | 2019 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2019-01-31 | N | 64.1859 | N | 11 | N | N | 1.1101 | 39.4971 | 78988.2531
[7 empty] | 5537 | 2585 | 1636031 | 2019-02-01 02:31 | 2019-02-01 07:00 | 269 | 11kV | 95176 | 1079 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 191368 Sw 7487 OPENED by S.O. broken xarm at pole KU-10217 Excluded oms 1636044 | February | 2019 | 2019Q3 | 2019 | 228:7487 | 228:85410 | ZN00228/085410 | NEWCASTLE | OH | Not Veg | 2019-02-01 | N | 88.2076 | N | 9 | N | N | 1.1101 | 39.4971 | 69551.8136
[7 empty] | 5502 | 2007 | 1636005 | 2019-01-31 23:04 | 2019-02-01 07:15 | 491 | 11kV | 311853 | 930 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | Y | LID 191363 2 fault operations A Phase Overcurrent; Earth Fault Broken crossarm 33 & 11 kV on pole SW-30006 Excluded OMS 1636005 | January | 2019 | 2019Q3 | 2019 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2019-01-31 | Y | 335.3258 | N | 11 | N | Y | 1.1101 | 39.4971 | 227892.9743
[7 empty] | 6407 | 12140 | 1636076 | 2019-02-01 05:19 | 2019-02-01 08:16 | 177 | 11kV | 231101 | 1523 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | ZN12570 AVOCA 11kV CB PA37 'Avoca Beach' tripped and locked out on: Relays: B Phase OC, EF, EFI left, reclose timing, lockout EFI's down to S18135 Cause: UGOH fault short circuit. arrestor blown at UGOH to S14563 See 1636415,6,8,9,20,1 Ex 1636076 | February | 2019 | 2019Q3 | 2019 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | Unknown | Unknown | 2019-02-01 | N | 151.7406 | N | 9 | N | N | 1.1101 | 39.4971 | 168881.7945
[7 empty] | 6146 | 9392 | 1636103 | 2019-02-01 06:17 | 2019-02-01 11:29 | 312 | 11kV | 2513 | 28 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 191380 Burnt off tapping load side of links 74635 Excluded OMS 1636103 | February | 2019 | 2019Q3 | 2019 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2019-02-01 | N | 89.75 | N | 9 | N | N | 1.1101 | 39.4971 | 1836.4263
[7 empty] | 5597 | 3555 | 1636034 | 2019-02-01 00:55 | 2019-02-01 12:36 | 701 | 33kV Distribution | 4206 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 191367 2 fault operations A & B Phase Earth Fault Sw 80491 targets A Prot = A & B E/F B Prot = 50TB & 50TN Excluded oms 1636034 | February | 2019 | 2019Q3 | 2019 | 417:80491 | 417:80491 | ZN00417/080491 | NEWCASTLE | OH | Not Veg | 2019-02-01 | N | 701 | N | 9 | N | N | 1.1101 | 39.4971 | 3073.6207
[7 empty] | 5579 | 3299 | 1636524 | 2019-02-01 16:49 | 2019-02-01 18:27 | 98 | 11kV | 36244 | 372 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex ZN12650 WEST GOSFORD section of 11kV CB 2 RE50247 Blackett Faunce opened and locked out on OC & lockout EFI's operated @ S1493 Cause: UG Fault between S14933 & S18611 See 1637737,8 Ex 1636524 | February | 2019 | 2019Q3 | 2019 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | UG | Not Veg | 2019-02-01 | N | 97.4301 | N | 9 | N | N | 1.1101 | 39.4971 | 26486.0462
[7 empty] | 5960 | 7030 | 1636627 | 2019-02-01 20:09 | 2019-02-01 20:47 | 38 | 11kV | 10298 | 271 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN12600 LISAROW section of 11kV CB 2 Re41845 North Erina opend, reclosed, opened & locked out on OC Cause: tree/branch on oh mains. Branch removed from 11kv OH adjacent to AB42920 See 1636627 ex 1636629,31 | February | 2019 | 2019Q3 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2019-02-01 | N | 38 | N | 9 | N | N | 1.1101 | 39.4971 | 7525.4747
[7 empty] | 6825 | 16654 | 1636685 | 2019-02-01 21:50 | 2019-02-01 22:52 | 62 | 11kV | 24388 | 397 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191389 2 fault operations B & C Phase Overcurrent branch fell on OHM at pole JQ-77104 Excluded oms 1636685 | February | 2019 | 2019Q3 | 2019 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2019-02-01 | N | 61.4307 | N | 9 | N | N | 1.1101 | 39.4971 | 17822.0311
[7 empty] | 5703 | 4682 | 1636671 | 2019-02-01 21:35 | 2019-02-02 00:15 | 160 | 11kV | 83246 | 678 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex ZN35370 GALSTON section of 11kV Panel 10 IR50015 Quarry old Northern tripped Relays: OC trip Abnormal: S6680 SwB closed, S5928SwA Open Cause: lightning/surge arrestor blown at PT2175. Isolated high and low. PT is shown as non parralleling but Dop has installed USL 10679. Live line connectors opened. Sw/Tag left at PT See 1637831,2,3 Ex 1636671,3,83,708 | February | 2019 | 2019Q3 | 2019 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | OH | Not Veg | 2019-02-01 | N | 122.7817 | N | 9 | N | N | 1.1101 | 39.4971 | 60833.7215
[7 empty] | 6177 | 9790 | 1636713 | 2019-02-01 23:47 | 2019-02-02 01:45 | 118 | 11kV | 96576 | 937 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | ZN12600 LISAROW 11kV CB 11 'Wyoming' fdr tripped Relays: EF, EFI Signals: 11kv trip EFI S65961 S18280 S77642 Cause: lightning/surge arrestor blown on cct tee PT12464 11kv fdr isolated from S77642 to LB43426 to PT12464 LV// usl 36171, network pillar 21203 Switch tag at PT12464 See 1637746,8,9 Ex 1636713,21,3 | February | 2019 | 2019Q3 | 2019 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Not Veg | 2019-02-01 | N | 103.0694 | N | 9 | N | N | 1.1101 | 39.4971 | 70574.8923
[7 empty] | 5353 | 183 | 1636736 | 2019-02-02 03:43 | 2019-02-02 06:56 | 193 | 11kV | 27213 | 141 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 191393 Tree branch at pole TC 50039 | February | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-02-02 | N | 193 | N | 9 | N | N | 1.1101 | 39.4971 | 19886.4578
[7 empty] | 6158 | 9471 | 1636768 | 2019-02-02 05:39 | 2019-02-02 08:30 | 171 | 11kV | 113245 | 857 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | ZN12600 LISAROW 11kV CB 13 'Brush Rd' tripped, reclosed and locked out on: Relays: B & C phase OC, Reclose, Timing and lockout Signals: 11kv trip EFI: Nil Cause: not ascertained See 1637756,7,8,60,1 ex 1636768 | February | 2019 | 2019Q3 | 2019 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2019-02-02 | N | 132.1412 | N | 9 | N | N | 1.1101 | 39.4971 | 82756.1058
[7 empty] | 6684 | 15104 | 1636832 | 2019-02-02 08:42 | 2019-02-02 10:22 | 100 | 11kV | 204932 | 2072 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN2635 EPPING 11kV CB Panel 31 'Essex Pembroke' fdr opened Cable cut between S7061 & S6227 Cause: UG cable damaged by contractor See 1637845,6 Ex 1636832,6 | February | 2019 | 2019Q3 | 2019 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2019-02-02 | N | 98.9054 | N | 9 | N | N | 1.1101 | 39.4971 | 149758.2611
[7 empty] | 6961 | 18125 | 1636881 | 2019-02-02 10:22 | 2019-02-02 14:06 | 224 | 11kV | 83476 | 463 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191395 2 fault operations B & C phase Overcurrent Patrolled to ABS 74964 Prot. 51BC 3200Amps. Similar event on # 191278 Excluded OMS 1636881 | February | 2019 | 2019Q3 | 2019 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2019-02-02 | N | 180.2937 | N | 9 | N | N | 1.1101 | 39.4971 | 61001.7987
[7 empty] | 5938 | 6821 | 1637019 | 2019-02-02 15:02 | 2019-02-02 16:10 | 68 | 11kV | 4692 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191396 B Phase DOLF : 31 Amp B Phase DOLF replaced. Original report via phone from Ausgrid employee Aaron Mohony 1502hrs, heard explosion. | February | 2019 | 2019Q3 | 2019 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Veg | 2019-02-02 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 3428.7752
[7 empty] | 5421 | 1111 | 1636997 | 2019-02-02 14:30 | 2019-02-02 16:41 | 131 | 11kV | 172789 | 1319 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN847 HORNSBY 11kV CB Panel 7 'Government Pound' fdr tripped on Relays: EF, A Phase, EF check Signals: Trip, Alarm EFI: Nil Cause: UG fault between S847:pa7 and S8054SwA | February | 2019 | 2019Q3 | 2019 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | UG | Not Veg | 2019-02-02 | N | 131 | N | 9 | N | N | 1.1101 | 39.4971 | 126269.1048
[7 empty] | 5371 | 438 | 1637066 | 2019-02-02 19:25 | 2019-02-02 20:24 | 59 | 11kV | 15458 | 262 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN129 HUNTERS HILL section of 11kV Panel 41 'Pittwwater Gannet' AB2317 Bond Burned off See 1637850 ex 1637066,73 | February | 2019 | 2019Q3 | 2019 | ZN129:PA41 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Not Veg | 2019-02-02 | N | 59 | N | 9 | N | N | 1.1101 | 39.4971 | 11296.2505
[7 empty] | 5598 | 3556 | 1637082 | 2019-02-02 20:55 | 2019-02-02 21:40 | 45.1667 | 11kV | 3116.5 | 69 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 191399 B Phase Lightning Arrestor & Dolf Excluded OMS 1637083 CC1: 22-"Refer to SOp" | February | 2019 | 2019Q3 | 2019 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2019-02-02 | N | 45.1667 | N | 9 | N | N | 1.1101 | 39.4971 | 2277.4463
[7 empty] | 6046 | 8106 | 1637047 | 2019-02-02 17:45 | 2019-02-03 00:50 | 425 | 11kV | 21658 | 59 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 191398 A Phase Burnt off tapping pole 9L-40295. Earlier trip/reclose, see #191397 Also tapping of at pole 9L-40063 and pole 9L-40811 Excluded OMS 1637047 | February | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2019-02-02 | N | 367.0847 | N | 9 | N | N | 1.1101 | 39.4971 | 15827.0276
[7 empty] | 7099 | 19564 | 1637080 | 2019-02-03 01:28 | 2019-02-03 07:31 | 363 | 11kV | 182254 | 1910 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN2602 CLOVELLY 11kV CB Panel 30 'Darley Carr' tripped on Relays: B & C phase timed O/C, F/C and EFI Signals: 11kv trip and Tx2 Group Earth EFI: S76847 S8981 S2132 Cause: UG fault between S2132:B to S8570:B Note: Access issues @ S8570 Original note: no access to S8570 to check EFI. Dop left swithing tag at S2132 See 1637934,5,6 Ex 1637080,107 | February | 2019 | 2019Q3 | 2019 | ZN2602:PA30 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2019-02-03 | N | 95.4209 | N | 3 | N | N | 1.1101 | 39.4971 | 133185.8476
[7 empty] | 5899 | 6394 | 1637105 | 2019-02-03 02:30 | 2019-02-03 09:15 | 405 | 11kV | 98688 | 1013 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191400 bat on OHM @ sub 50375 then broken 11kV tapping @ pole HS-43343 prot = 51 B-C Excluded oms 1637105 | February | 2019 | 2019Q3 | 2019 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2019-02-03 | N | 97.4215 | N | 3 | N | N | 1.1101 | 39.4971 | 72118.2796
[7 empty] | 5411 | 982 | 1637124 | 2019-02-03 09:17 | 2019-02-03 11:10 | 113 | 11kV | 3051 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191401 C Phase DOLF : 20 Amp Excluded OMS 1637124 | February | 2019 | 2019Q3 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2019-02-03 | N | 113 | N | 3 | N | N | 1.1101 | 39.4971 | 2229.5808
[7 empty] | 5790 | 5486 | 1637265 | 2019-02-04 00:53 | 2019-02-04 02:50 | 117 | 11kV | 164611 | 1537 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12650 WEST GOSFORD 11kV CB Panel 20 'Central Moor' fdr tripped on C phase, IOC, B&C phase timed overcurrent, EFI, SEL EFI: Cause: not ascertained. NB recloser is manual See 1637781,2,3,4 Ex 1637265 | February | 2019 | 2019Q3 | 2019 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Veg | 2019-02-04 | N | 107.0989 | N | 6 | N | N | 1.1101 | 39.4971 | 120292.8636
[7 empty] | 6903 | 17605 | 1637339 | 2019-02-04 09:57 | 2019-02-04 12:02 | 125 | 11kV | 211199 | 1711 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN35800 BANKSTOWN 11kV CB Panel 22 'Bonds Martin' fdr tripped on A&B phase OC Cause: Underground cable fault from S6352 to S8097 to S8320 See 1637922,4,5 Ex 1637339 | February | 2019 | 2019Q3 | 2019 | ZN35800:PA22 | ZN35800:PA22 | ZN35800/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-02-04 | N | 123.436 | N | 6 | N | N | 1.1101 | 39.4971 | 154337.9999
[7 empty] | 6077 | 8362 | 1637416 | 2019-02-04 12:14 | 2019-02-04 14:10 | 116 | 11kV | 46440 | 891 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S720 Hannans Rd "Earls Karne" feeder operated on A phase OC & Earth fault Remarks: UG fault. UG Cable fault between S720 Hannas Rd to Sub 35933 Karne St to S3295 karne Ventura | February | 2019 | 2019Q3 | 2019 | ZN35800:PA22 | ZN35800:PA22 | ZN35800/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-02-04 | N | 52.1212 | N | 6 | N | N | 1.1101 | 39.4971 | 33936.9823
[7 empty] | 5536 | 2528 | 1637554 | 2019-02-04 15:03 | 2019-02-04 19:15 | 252 | 11kV | 120838 | 1555 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191419 Tree fallen on to Overhead Main | February | 2019 | 2019Q3 | 2019 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Veg | 2019-02-04 | N | 77.7093 | N | 6 | N | N | 1.1101 | 39.4971 | 88304.8463
[7 empty] | 6436 | 12552 | 1637661 | 2019-02-04 19:49 | 2019-02-04 20:50 | 61 | 11kV | 61 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191420 C Phase DOLF : 10 Amp dead bird at base of pole. incorrect sub in OMS Excluded OMS 1637661 | February | 2019 | 2019Q3 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2019-02-04 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 6880 | 17346 | 1637666 | 2019-02-04 20:09 | 2019-02-04 21:40 | 91 | 11kV | 910 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN15013 TERREY HILLS section of 11kV Panel 10 PT15672 TUMBLEDOWN DICK 11kv 20A HDO footpath side blown Cause: Animals/Birds See 1637799 ex 1637666 | February | 2019 | 2019Q3 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-02-04 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 6332 | 11241 | 1637691 | 2019-02-05 01:40 | 2019-02-05 06:00 | 259.55 | 11kV | 5191 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191421 Feeder patrolled. No Fault found. Fuse Saver was found open. Reclosed Fuse saver. | February | 2019 | 2019Q3 | 2019 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2019-02-05 | N | 259.55 | N | 3 | N | N | 1.1101 | 39.4971 | 3793.4297
[7 empty] | 6462 | 12853 | 1637969 | 2019-02-05 20:34 | 2019-02-05 22:30 | 116 | 11kV | 580 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191437 C Phase DOLF : 10 Amp excluded OMS 1637969 | February | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-02-05 | N | 116 | N | 3 | N | N | 1.1101 | 39.4971 | 423.8469
[7 empty] | 5545 | 2699 | 1637931 | 2019-02-05 17:09 | 2019-02-05 23:18 | 369 | 11kV | 7809 | 46 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191435 2 fault operations Tree on mains pole 9L-70414 Excluded OMS 1637931 | February | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2019-02-05 | N | 169.7609 | N | 3 | N | N | 1.1101 | 39.4971 | 5706.5869
[7 empty] | 5427 | 1170 | 1638017 | 2019-02-06 08:04 | 2019-02-06 10:52 | 168 | 11kV | 1848 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191445 C Phase DOLF : 16 Amp Excluded OMS 1638017 | February | 2019 | 2019Q3 | 2019 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2019-02-06 | N | 168 | N | 3 | N | N | 1.1101 | 39.4971 | 1350.4639
[7 empty] | 6171 | 9620 | 1637995 | 2019-02-06 02:42 | 2019-02-06 11:15 | 513 | 11kV | 145935 | 705 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.26 tripped on: OC (51N) Tree branch brought down OH mains (HV into LV) in Yanderra Near Ellis See 1639411 1639413 1639414 | February | 2019 | 2019Q3 | 2019 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Veg | 2019-02-06 | N | 207 | N | 3 | N | N | 1.1101 | 39.4971 | 106644.9936
[7 empty] | 6716 | 15280 | 1638126 | 2019-02-06 13:16 | 2019-02-06 16:35 | 199 | 11kV | 17114 | 86 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN2635 EPPING section of 11kV Panel 52 PT2443 GLOUCESTER DORSET 11kV HDO 50 Amp footpath phase fuse blown Cause not ascertained. 11kv surge arrestor at the UGOH leading to PT2443 is defective and hanging. Refion to access an drepair as required | February | 2019 | 2019Q3 | 2019 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | PARRAMATTA | OH | Not Veg | 2019-02-06 | N | 199 | N | 3 | N | N | 1.1101 | 39.4971 | 12506.4064
[7 empty] | 5690 | 4552 | 1638296 | 2019-02-07 08:34 | 2019-02-07 12:02 | 208 | 11kV | 297127 | 2215 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.14 tripped on A Phase timed O/C Contractor hit cable in premises of 424-426 Canterbury Rd Campsie. See 1639301 1638294 | February | 2019 | 2019Q3 | 2019 | ZN690:PA14 | ZN690:PA14 | ZN00690/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-02-07 | N | 134.1431 | N | 4 | N | N | 1.1101 | 39.4971 | 217131.6478
[7 empty] | 5822 | 5687 | 1638515 | 2019-02-07 17:48 | 2019-02-07 18:28 | 40 | 11kV | 9840 | 246 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | iR49996 Churchill Fairban tripped & locked out on: O/C Tree branch on OH mains outside 20 Barrie St, East Killara | February | 2019 | 2019Q3 | 2019 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2019-02-07 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 7190.7818
[7 empty] | 6054 | 8178 | 1638520 | 2019-02-07 17:58 | 2019-02-07 21:10 | 192 | 11kV | 5303 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC45117 Glenning Valley tripped on: IOC and EF Tree branch into mains near PT18760. HV into LV See 1639361 1639362 1639363 1639364 | February | 2019 | 2019Q3 | 2019 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2019-02-07 | N | 67.9872 | N | 4 | N | N | 1.1101 | 39.4971 | 3875.276
[7 empty] | 6180 | 9818 | 1638975 | 2019-02-07 20:07 | 2019-02-08 02:00 | 353 | 11kV | 192972 | 1394 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 191487 2 fault operations A Phase Overcurrent; Earth Fault 11kV tapping broken at pole FS-82963. Targets: A prot Aph O/C B prot Aph O/C , E/F Excluded OMS No. 1638975 + 1639024 | February | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2019-02-07 | N | 138.4304 | N | 4 | N | N | 1.1101 | 39.4971 | 141018.2459
[7 empty] | 5723 | 4987 | 1638705 | 2019-02-08 15:38 | 2019-02-08 18:50 | 192 | 11kV | 384 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191479 Single phase DOLF : 3 Amp Bird contacted HV blowing fuse. OMS job was never sent to the Control Room, so above OMS job was the only one we could locate. Excluded OMS # 1638705 | February | 2019 | 2019Q3 | 2019 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2019-02-08 | N | 192 | N | 24 | Y | Y | 1.1101 | 39.4971 | 280.6159
[7 empty] | 5732 | 5083 | 1638793 | 2019-02-08 18:52 | 2019-02-08 20:15 | 83 | 11kV | 581 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191483 A Phase DOLF : 10 Amp Excluded OMS 1638793 | February | 2019 | 2019Q3 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2019-02-08 | N | 83 | N | 24 | Y | Y | 1.1101 | 39.4971 | 424.5777
[7 empty] | 5465 | 1549 | 1638754 | 2019-02-08 18:14 | 2019-02-08 20:44 | 150 | 11kV | 248700 | 1658 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | N | Zn1287 Revesby - Pnl.21 tripped and locked out on: A & Cphase IOC mains down between PE23067 to PE23068 | February | 2019 | 2019Q3 | 2019 | ZN1287:PA21 | ZN1287:PA21 | ZN01287/000021 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-02-08 | N | 150 | N | 24 | Y | Y | 1.1101 | 39.4971 | 181742.6246
[7 empty] | 7035 | 18883 | 1638821 | 2019-02-08 18:58 | 2019-02-08 20:44 | 106 | 11kV | 82786 | 781 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | Zn3922 Drummoyne - Pnl.3 tripped on A & B phase IOC UG cable fault. Front line section | February | 2019 | 2019Q3 | 2019 | ZN3922:PA3 | ZN3922:PA3 | ZN03922/000003 | CANADA BAY | UG | Not Veg | 2019-02-08 | N | 106 | N | 24 | Y | Y | 1.1101 | 39.4971 | 60497.567
[7 empty] | 6639 | 14736 | 1638916 | 2019-02-08 19:32 | 2019-02-08 21:17 | 105 | 11kV | 107625 | 1025 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | REC20397 Pittwater Cabbage tree tripped Cause not ascertained. CC1: 22-"Refer to SOp" | February | 2019 | 2019Q3 | 2019 | ZN15014:PA7 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2019-02-08 | N | 105 | N | 24 | Y | Y | 1.1101 | 39.4971 | 78649.1756
[7 empty] | 6468 | 12949 | 1638812 | 2019-02-08 18:56 | 2019-02-08 21:53 | 177 | 11kV | 94221 | 562 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | REC46120 Lovell Russell tripped & reclosed on: O/C Lightning arrestor blown @ PT2008.. See 1639336 1639337 | February | 2019 | 2019Q3 | 2019 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2019-02-08 | N | 167.653 | N | 24 | Y | Y | 1.1101 | 39.4971 | 68853.9278
[7 empty] | 7142 | 19905 | 1639023 | 2019-02-08 19:31 | 2019-02-08 22:15 | 164 | 11kV | 148822 | 1066 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | Zn12610 long jetty - Pnl.17 tripped, reclosed & locked out on: C phase IOC Lightning arrestor blown on UGOH below AB41946 See 1639379 1639380 1639381 | February | 2019 | 2019Q3 | 2019 | ZN12610:PA17 | ZN12610:PA17 | ZN12610/000017 | CENTRAL COAST | OH | Not Veg | 2019-02-08 | N | 139.6079 | N | 24 | Y | Y | 1.1101 | 39.4971 | 108754.7281
[7 empty] | 5524 | 2411 | 1639019 | 2019-02-08 20:37 | 2019-02-08 23:10 | 153 | 11kV | 1143 | 79 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | REC45016 Dickson tripped & reclosed on: O/C Suspected lighting strike See 1639394 1639395 | February | 2019 | 2019Q3 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-02-08 | N | 14.4684 | N | 24 | Y | Y | 1.1101 | 39.4971 | 835.2707
[7 empty] | 5819 | 5680 | 1638741 | 2019-02-08 17:17 | 2019-02-09 00:20 | 423 | 11kV | 88657 | 462 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Electrical Storm | N | LID 191499 3 fault operations Earth Fault Two phases had damaged 11kV insulators on steel x arm at pole AJ-30267, assuming lightning/storm damaged insulators. Excluded OMS 1638741 | February | 2019 | 2019Q3 | 2019 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2019-02-08 | N | 191.8983 | N | 24 | Y | Y | 1.1101 | 39.4971 | 64787.9207
[7 empty] | 5943 | 6875 | 1638891 | 2019-02-08 18:28 | 2019-02-09 00:30 | 362 | 11kV | 2534 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191497 B Phase DOLF : 10 Amp Excluded OMS 1638891 | February | 2019 | 2019Q3 | 2019 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2019-02-08 | N | 362 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1851.7725
[7 empty] | 5478 | 1666 | 1638830 | 2019-02-08 18:59 | 2019-02-09 01:10 | 371 | 11kV | 463980 | 1312 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | Zn129 Hunters Hill - Pnl.35 tripped on: A, B & C IOC Lightning arrestor blown on UGOH to S5227 See 1639347 1639348 1639349 | February | 2019 | 2019Q3 | 2019 | ZN129:PA35 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Not Veg | 2019-02-08 | N | 353.6433 | N | 24 | Y | Y | 1.1101 | 39.4971 | 339062.8989
[7 empty] | 5503 | 2012 | 1638894 | 2019-02-08 19:28 | 2019-02-09 01:50 | 382 | 11kV | 104439 | 1729 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12600 Lisarwo - Pnl.3 tripped on: A & C phase O/C Field EFIs: S12399 S18173 S14623 S14247 S18521 Mains down due to lightning strike on Wyoming Rd. See 1639353 1639355 1639357 | February | 2019 | 2019Q3 | 2019 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2019-02-08 | N | 60.4043 | N | 24 | Y | Y | 1.1101 | 39.4971 | 76320.9408
[7 empty] | 5657 | 4248 | 1638776 | 2019-02-08 18:37 | 2019-02-09 02:00 | 443 | 11kV | 139375 | 923 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Lightning | N | Zn965 Pennant Hills - Pnl.26 tripped on: C phase O/C Field EFis: All down to S7942 OH mains down - HV in LV See 1639340 1639341 1639343 1639344 | February | 2019 | 2019Q3 | 2019 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Not Veg | 2019-02-08 | N | 151.0022 | N | 24 | Y | Y | 1.1101 | 39.4971 | 101851.1391
[7 empty] | 5544 | 2697 | 1638737 | 2019-02-08 17:13 | 2019-02-09 02:05 | 532 | 11kV | 532 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 191538 Single phase DOLF : 10 Amp Transformer failed in service Excluded OMS 1638737 | February | 2019 | 2019Q3 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2019-02-08 | N | 532 | N | 24 | Y | Y | 1.1101 | 39.4971 | 388.7699
[7 empty] | 5471 | 1635 | 1639160 | 2019-02-09 07:17 | 2019-02-09 09:40 | 143 | 11kV | 286 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | PT15160 Oxford Falls North - Footpath phase HDO blown Previous storm. | February | 2019 | 2019Q3 | 2019 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2019-02-09 | N | 143 | N | 6 | N | N | 1.1101 | 39.4971 | 209.0004
[7 empty] | 6651 | 14815 | 1638752 | 2019-02-08 18:09 | 2019-02-09 10:24 | 975 | 11kV | 324687 | 1264 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn1290 leightonfield - Pnl.9 tripped and locked out on: A & B phase O/C Lightning strike S35957 Wolumba Bent - Dist #2 - A, B & C phases interrupted at 23:18 HV into LV due to lightningt strike Pnl.9 See 1639406 1639407 1639408 | February | 2019 | 2019Q3 | 2019 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-02-08 | N | 256.8726 | N | 24 | Y | Y | 1.1101 | 39.4971 | 237271.683
[7 empty] | 6155 | 9449 | 1639109 | 2019-02-08 23:13 | 2019-02-09 11:25 | 732 | 11kV | 732 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191502 A Phase DOLF : 10 Amp Excluded OMS 1639109 | February | 2019 | 2019Q3 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2019-02-08 | N | 732 | N | 24 | Y | Y | 1.1101 | 39.4971 | 534.924
[7 empty] | 5746 | 5134 | 1639114 | 2019-02-08 23:27 | 2019-02-09 12:00 | 753 | 11kV | 1506 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191503 Single phase DOLF : 10 Amp Excluded OMS 1639114 | February | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-02-08 | N | 753 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1100.5404
[7 empty] | 6772 | 15847 | 1639134 | 2019-02-09 03:30 | 2019-02-09 12:15 | 525 | 11kV | 352876 | 1836 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.40 tripped on: Earth Fault UG cable fault betwen S64687 Sw/B and LB1965 tee S5086 See 1639453 1639454 1639455 | February | 2019 | 2019Q3 | 2019 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | UG | Not Veg | 2019-02-09 | N | 192.1983 | N | 6 | N | N | 1.1101 | 39.4971 | 257871.3727
[7 empty] | 5527 | 2438 | 1638802 | 2019-02-08 18:56 | 2019-02-09 12:40 | 1064 | 11kV | 2128 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Previous Storm | N | LID 191505 A Phase DOLF : 10 Amp DOLF Carrier replaced due to being burnt up. Excluded OMS 1638802. | February | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-02-08 | N | 1064 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1555.0796
[7 empty] | 6934 | 17901 | 1638759 | 2019-02-08 17:56 | 2019-02-09 13:25 | 1169 | 11kV | 15240 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 191508 3 phase DOLF's HV Wires down. BQ-90149 to PT 51893. Excluded OMS 1639234. | February | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-02-08 | N | 635 | N | 24 | Y | Y | 1.1101 | 39.4971 | 11136.9425
[7 empty] | 5797 | 5546 | 1639326 | 2019-02-09 12:50 | 2019-02-09 14:00 | 70 | 11kV | 2450 | 35 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Lightning | N | Section of 11kV feeder form LB9 to LB66058 interrupted for safety while repairing LB32 See 1639326 1639327 | February | 2019 | 2019Q3 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2019-02-09 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 1790.3877
[7 empty] | 6043 | 8070 | 1638818 | 2019-02-08 18:56 | 2019-02-09 14:15 | 1159 | 11kV | 460503 | 939 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn2400 berowra - Pnl.26 tripped on: A & C phase IOC Tree branch brought down mains between S50340 Sw/B to S7194 Sw/A to AB3157 tee S7232. Also brought down LV from S7232 See 1639460 1639458 1639459 | February | 2019 | 2019Q3 | 2019 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2019-02-08 | N | 490.4185 | N | 24 | Y | Y | 1.1101 | 39.4971 | 336522.0099
[7 empty] | 5385 | 598 | 1638761 | 2019-02-08 18:23 | 2019-02-09 15:20 | 1257 | 11kV | 2514 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 191509 Single phase DOLF : 3 Amp Replace L/A's Excluded OMS 1638761 | February | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-02-08 | N | 1257 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1837.157
[7 empty] | 6041 | 8062 | 1638859 | 2019-02-08 18:48 | 2019-02-09 16:10 | 1282 | 11kV | 620569 | 1038 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN35370 GALSTON 11kV CB Panel 4 'Galston Aux No.1' tripped on B and C Phase Abnormal: LB62159 closed and AB3252 opened Cause: not ascertained. See trip on Galston Panel 8 @ PT1616 (dayshift emso to check HV into LV) See 1640188,90,1,2,3,4,5,6 Ex 1638798,806,59,928,9322,59,99 | February | 2019 | 2019Q3 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2019-02-08 | N | 597.8507 | N | 24 | Y | Y | 1.1101 | 39.4971 | 453493.5215
[7 empty] | 6507 | 13369 | 1639268 | 2019-02-09 11:08 | 2019-02-09 16:30 | 322 | 11kV | 644 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191513 A Phase DOLF : 10 Amp Excluded OMS 1639268 | February | 2019 | 2019Q3 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2019-02-09 | N | 322 | N | 6 | N | N | 1.1101 | 39.4971 | 470.6162
[7 empty] | 5506 | 2045 | 1639265 | 2019-02-09 11:00 | 2019-02-09 17:10 | 370 | 11kV | 1850 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191514 Single phase DOLF : 10 Amp Excluded OMS 1639265 | February | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-02-09 | N | 370 | N | 6 | N | N | 1.1101 | 39.4971 | 1351.9254
[7 empty] | 6735 | 15415 | 1638817 | 2019-02-08 18:56 | 2019-02-09 18:45 | 1429 | 11kV | 375387 | 438 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN2400 BEROWRA 11kV CB Panel 13 'S77032 Beaumont Yatala' has tripped on Relays: A Phase OC, EFI Signals: 11kv trip EFI: S35309 S8344 S4779 S35942 S6731 Abnormal: AB1262 closed, AB80 is open and defective Cause: tree/branch brought down oh. Adjacent to AB80 See 1640213,4,5 Ex 1638815,7,9351 | February | 2019 | 2019Q3 | 2019 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Veg | 2019-02-08 | N | 857.0479 | N | 24 | Y | Y | 1.1101 | 39.4971 | 274321.7476
[7 empty] | 6362 | 11612 | 1638822 | 2019-02-08 18:54 | 2019-02-09 18:45 | 1431 | 11kV | 98662 | 196 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Ex ZN847 HORNSBY section of 11kV Panel 45 'AB3100 etc' RE420 Reynolds Crosslands tripped & locked out Relays: SEF trip, lockout Signals: EFI: Nil Cause: tree/branch brought down 11kv OH adj Pole Noe AR27676. 11kv has been cutaway and made safe. PT2024 is still interrupted See 1640206,8,9 Ex 1638822,9173 | February | 2019 | 2019Q3 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-02-08 | N | 503.3776 | N | 24 | Y | Y | 1.1101 | 39.4971 | 72099.2796
[7 empty] | 6780 | 16082 | 1639543 | 2019-02-09 21:36 | 2019-02-09 21:55 | 19 | 11kV | 38 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191523 A Phase DOLF : 10 Amp Excluded OMS 1639543 | February | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-02-09 | N | 19 | N | 6 | N | N | 1.1101 | 39.4971 | 27.7693
[7 empty] | 6831 | 16749 | 1639567 | 2019-02-10 05:30 | 2019-02-10 06:32 | 62 | 11kV | 70680 | 1140 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1287 Revesby Panel 5 "Davies Banks" feeder tripped on B & C phase overcurrent Remarks: tree/branch on OH mains. At ugoh to S8912 removed by dop | February | 2019 | 2019Q3 | 2019 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2019-02-10 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 51650.8593
[7 empty] | 5687 | 4522 | 1639602 | 2019-02-10 10:01 | 2019-02-10 12:48 | 167 | 11kV | 501 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191532 C Phase DOLF : 20 Amp Carrier also replaced Excluded OMS 1639602 | February | 2019 | 2019Q3 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2019-02-10 | N | 167 | N | 8 | N | N | 1.1101 | 39.4971 | 366.116
[7 empty] | 5861 | 6012 | 1639615 | 2019-02-10 11:20 | 2019-02-10 12:50 | 90 | 11kV | 630 | 7 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191533 C Phase DOLF : 10 Amp Possum Excluded OMS 1639615 | February | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-02-10 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 5707 | 4736 | 1639630 | 2019-02-10 12:37 | 2019-02-10 14:05 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191534 Single phase DOLF : 10 Amp Excluded OMS 1639630 | February | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-02-10 | N | 88 | N | 8 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 6368 | 11694 | 1639603 | 2019-02-10 10:00 | 2019-02-10 17:26 | 445.7167 | 11kV | 24894.4167 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex ZN847 HORNSBY section of 11kV Panel 45 From CP129 to CP702 interrupted for safety & repair @1000 Abnormal: CP1767 closed CP702 Open Tree branch on 11kv mains below LB129 AP issued to lineowrker @1140 (cc tree trimmer) See 1639604 ex 1639603 | February | 2019 | 2019Q3 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-02-10 | N | 444.5432 | N | 8 | N | N | 1.1101 | 39.4971 | 18192.1054
[7 empty] | 6595 | 14338 | 1639586 | 2019-02-10 08:40 | 2019-02-10 19:10 | 630 | 11kV | 1260 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 191535 DOLF : 10 Amp Tx failed, job delayed with mains on private equipment blowing sub lv fuse until this section of private mains disconnected and customer advised to have contractor fix fault. Excluded OMS 1639586 | February | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-02-10 | N | 630 | N | 8 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 6815 | 16542 | 1639690 | 2019-02-10 19:13 | 2019-02-10 20:24 | 70.95 | 11kV | 5746.95 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 5 RE45107 Whiteman Opened & locked out on overcurrent & lockout Cause: tree/branch on oh mains. Load side of autolink 49334. OH mains to inspect in daylight for possible burn marks | February | 2019 | 2019Q3 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-02-10 | N | 70.95 | N | 8 | N | N | 1.1101 | 39.4971 | 4199.7016
[7 empty] | 6655 | 14886 | 1639702 | 2019-02-10 23:23 | 2019-02-10 23:52 | 29 | 11kV | 31030 | 1070 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn9245 Panel 1 "S48147 Engadine Aux No2" feeder has tripped Signals: 11kv trip CB 1, Auto recloser lockout Relays: B C O/C, EFI Remarks: Animals/birds. Bat found on ground Cnr Lantana and Gort lane, Engadine | February | 2019 | 2019Q3 | 2019 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2019-02-10 | N | 29 | N | 8 | N | N | 1.1101 | 39.4971 | 22675.8088
[7 empty] | 6783 | 16106 | 1639721 | 2019-02-11 03:36 | 2019-02-11 04:44 | 68 | 11kV | 16048 | 236 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN3425 CASTLE COVE section of 11kV Panel 33 IR64824 Deepwater Holly has tripped Relays: OC trip and LO Cause: dead possum found at LB62056 Surge Arrestors damaged, requires repairs See 1639721 ex 1639723 | February | 2019 | 2019Q3 | 2019 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2019-02-11 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 11727.4051
[7 empty] | 5538 | 2594 | 1639719 | 2019-02-11 02:47 | 2019-02-11 07:35 | 288 | 11kV | 1728 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191537 C Phase DOLF : 20 Amp Excluded OMS 1639719 | February | 2019 | 2019Q3 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2019-02-11 | N | 288 | N | 6 | N | N | 1.1101 | 39.4971 | 1262.7714
[7 empty] | 5879 | 6180 | 1639783 | 2019-02-11 13:50 | 2019-02-11 14:40 | 50 | 11kV | 300 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 191543 A Phase Burnt off tapping pole ES-33411 Excluded OMS 1639783 | February | 2019 | 2019Q3 | 2019 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2019-02-11 | N | 50 | N | 6 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 6342 | 11342 | 1639839 | 2019-02-11 11:28 | 2019-02-11 16:10 | 282.1833 | 11kV | 1410.9167 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191546 B Phase DOLF : 20 Amp Copper Conductor broken Mid Span near P. AH-52447 | February | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-02-11 | N | 282.1833 | N | 6 | N | N | 1.1101 | 39.4971 | 1031.0563
[7 empty] | 6399 | 12023 | 1640027 | 2019-02-11 19:57 | 2019-02-11 20:36 | 39 | 11kV | 25662 | 658 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV Panel 33 'Scarybrook Wladron' IR40507 The Scenic Bounty opened on overcurrent Casue: Tree/branch on 11kV OH mains near PT11717 & removed by Dop. Extensive tree trimming required in area See 1640027 ex 1640028 | February | 2019 | 2019Q3 | 2019 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2019-02-11 | N | 39 | N | 6 | N | N | 1.1101 | 39.4971 | 18753.0327
[7 empty] | 7066 | 19317 | 1640047 | 2019-02-11 23:35 | 2019-02-12 02:10 | 155.1 | 11kV | 1706.1 | 11 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191552 B & C Phase DOLF : 20 Amp Bat contacted 11kv mains blowing 2 line dolf's. | February | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2019-02-11 | N | 155.1 | N | 6 | N | N | 1.1101 | 39.4971 | 1246.7676
[7 empty] | 6120 | 9100 | 1640052 | 2019-02-12 03:37 | 2019-02-12 05:23 | 106 | 11kV | 108226 | 1021 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn10994 Mortdale Panel 19L 'S50482' feeder has tripped Signals: 11kv trip Relays: IOC B and C, EFI, EF, Reclose LO Remarks: Animals/Birds. Possum at UGOH near Sub 10731 | February | 2019 | 2019Q3 | 2019 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2019-02-12 | N | 106 | N | 7 | N | N | 1.1101 | 39.4971 | 79088.3687
[7 empty] | 6330 | 11233 | 1640055 | 2019-02-12 05:58 | 2019-02-12 10:20 | 262 | 11kV | 24934 | 97 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kv Bond burned off and resting on other phase on tee off to PT64515 Linden Valentia and S10731 Renway Valentia Ex S.10994 Mortdale Panel 19L "S50482, etc" Remarks: bond 11kv bond burned off and resting on other phase on tee off to PT64515 Linden Valentia and S10731 Renway Valentia | February | 2019 | 2019Q3 | 2019 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2019-02-12 | N | 257.0515 | N | 7 | N | N | 1.1101 | 39.4971 | 18221.0318
[7 empty] | 6858 | 16994 | 1640216 | 2019-02-12 11:55 | 2019-02-12 12:30 | 35 | 11kV | 35 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 191560 A Phase DOLF Excluded OMS 1640216 | February | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2019-02-12 | N | 35 | N | 7 | N | N | 1.1101 | 39.4971 | 25.577
[7 empty] | 6683 | 15101 | 1640251 | 2019-02-12 13:23 | 2019-02-12 15:03 | 100 | 11kV | 17004 | 182 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 191569 2 fault operations B phase Overcurrent targets = 51B feeder patrolled no fault found Excluded OMS 1640251 | February | 2019 | 2019Q3 | 2019 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Veg | 2019-02-12 | N | 93.4286 | N | 7 | N | N | 1.1101 | 39.4971 | 12426.0217
[7 empty] | 5749 | 5148 | 1640267 | 2019-02-12 13:53 | 2019-02-12 17:40 | 227 | 11kV | 13762 | 71 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 3 IR49206 Mangrove Mountain West opened & locked out on OC & Lockout Cause: Tree/Branch on OH mains adjacent to AB43698. Removed by lineworker See 1640585 ex 1640590 | February | 2019 | 2019Q3 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2019-02-12 | N | 193.831 | N | 7 | N | N | 1.1101 | 39.4971 | 10056.8637
[7 empty] | 6207 | 10056 | 1640365 | 2019-02-12 16:39 | 2019-02-12 18:17 | 98 | 11kV | 77566 | 824 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | ZN12580 ERINA 11kV CB Panel 8 'Entrance Salvation' fdr tripped on Relays: A Phase IOC time Signals: 11kv trip EFI: S14427 S18654 S14889 Cause: Tree branch near PT14420 removed by DOp See 1640592,3 ex 1640365 | February | 2019 | 2019Q3 | 2019 | ZN12580:PA8 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Veg | 2019-02-12 | N | 94.1335 | N | 7 | N | N | 1.1101 | 39.4971 | 56682.945
[7 empty] | 5739 | 5099 | 1640398 | 2019-02-12 17:50 | 2019-02-12 19:02 | 72 | 11kV | 15984 | 222 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 191573 A Phase DOLF : 40 Amp Excluded OMS 1640398 CC1: 22-"Refer to SOp" | February | 2019 | 2019Q3 | 2019 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Veg | 2019-02-12 | N | 72 | N | 7 | N | N | 1.1101 | 39.4971 | 11680.6358
[7 empty] | 6888 | 17419 | 1640486 | 2019-02-13 06:08 | 2019-02-13 06:40 | 32 | 11kV | 256 | 8 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | Y | LID 191577 B and C Fuse, 40 Amp Substation DOLF Reported that dead possum found at base of PT 19573, 2 dolf's down, 1 fuse still up. | February | 2019 | 2019Q3 | 2019 | 239:82128 | 239:82128 | ZN00239/082128 | LAKE MACQUARIE | OH | Not Veg | 2019-02-13 | Y | 32 | N |  | N | Y | 1.1101 | 39.4971 | 187.0772
[7 empty] | 5752 | 5173 | 1640714 | 2019-02-13 19:07 | 2019-02-13 20:22 | 75 | 11kV | 7292 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 191589 Wire off pin at Pole 4J-10002 | February | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-02-13 | Y | 68.1495 | N |  | N | Y | 1.1101 | 39.4971 | 5328.7785
[7 empty] | 7110 | 19643 | 1640790 | 2019-02-14 01:59 | 2019-02-14 05:25 | 206.4833 | 11kV | 2271.3167 | 11 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191592 B and C phases, 20 Amp fuses, Line DOLF Flying fox found at base of LF 40444 | February | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2019-02-14 | N | 206.4833 | N | 6 | N | N | 1.1101 | 39.4971 | 1659.8112
[7 empty] | 6481 | 13087 | 1644445 | 2019-02-14 07:22 | 2019-02-14 08:45 | 83 | 11kV | 94703 | 1141 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 21 tripped on Relays: C phase OC, EFI, Fault Check Signale: No signals due to SCADA fail Abnormal Switching: SW/B at S8577 Open, S65613 Closed. Cause: Surge arrestor failed on pole MC5630 O/S 67 Armor St NOTE: Hornsby Zone in SCAN fail at the time of trip - due to TX2 Fault/Fire - Trip reported by DOp on site | February | 2019 | 2019Q3 | 2019 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2019-02-14 | N | 83 | N | 6 | N | N | 1.1101 | 39.4971 | 69206.1591
[7 empty] | 6730 | 15370 | 1640833 | 2019-02-14 11:12 | 2019-02-14 12:09 | 57 | 11kV | 2708 | 48 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 191602 Burnt off 11kV tapping at pole 9L-40811 Note: customers were reporting low volts and part supply from 14/02/19 08:43 | February | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2019-02-14 | N | 56.4167 | N | 6 | N | N | 1.1101 | 39.4971 | 1978.9265
[7 empty] | 6425 | 12380 | 1640880 | 2019-02-14 11:01 | 2019-02-14 12:42 | 101 | 11kV | 202 | 2 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191606 40 Amp Fuse, possum contacted the 11kV Reported that - BLOWN DOLF AT TX HP54165, DEAD POSSUM AT BASE OF POLE. POSSUM NEST AND PAPER WASP NEST ON TX, REMOVED WITH HEIGHT STICK (WHILE REMOVING NEXT ANOTHER POSSUM ESCAPED TO ADJACENT TREE). S.O 2 NOTIFIED - PETER. REPLACED 40 AMP (K TYPE) FUSE, SUPPLY RESTORED AT 12:42. A-N=235 VOLTS, B-N=233 VOLTS, C-N=235 VOLTS | February | 2019 | 2019Q3 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2019-02-14 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 5829 | 5731 | 1641050 | 2019-02-14 19:23 | 2019-02-14 20:40 | 76.85 | 11kV | 1844.4 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN35370 GALSTON section of 11kV Panel 10 beyond LB2928 interrupted 11kv tee off to PT stranded required repairs Lineworkers unable to repair LB2928 will not open | February | 2019 | 2019Q3 | 2019 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2019-02-14 | N | 76.85 | N | 6 | N | N | 1.1101 | 39.4971 | 1347.8331
[7 empty] | 5971 | 7107 | 1641065 | 2019-02-14 23:46 | 2019-02-15 01:10 | 84 | 11kV | 84000 | 1000 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv Panel No.4 "46609 Tower Condon" at ZN1287 Revesby tripped under fault. Relays Signals at Zone sub: 51N trip (E/fault), EFI, fault check, recloser lockout Signals@Zone sub - 11kv trip, zone earth, Tx1 group earth Remarks: animals/birds. Bat found on cable sealing ends at PT137 Rodgers Tower. Bat removed and fdr restored | February | 2019 | 2019Q3 | 2019 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-02-14 | N | 84 | N | 6 | N | N | 1.1101 | 39.4971 | 61384.7224
[7 empty] | 7091 | 19514 | 1641073 | 2019-02-15 02:27 | 2019-02-15 03:48 | 81 | 11kV | 58563 | 723 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN9252 JANNALI section of 11kV Panel 31 RE63272 Georges Wattle trippped under fault Protection Flags at Recloser: OC trip, Reclose Lockout Abnormal: 11kv open bonds at PT9401 (DMA) Enitre overhead section of feeder patrolled and UGOH inspected, nil defects evident. suspect wildlife See 1641073 ex 1641074 | February | 2019 | 2019Q3 | 2019 | ZN9252:PA31 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Veg | 2019-02-15 | N | 81 | N | 5 | N | N | 1.1101 | 39.4971 | 42796.1131
[7 empty] | 6080 | 8413 | 1640817 | 2019-02-15 07:46 | 2019-02-15 11:22 | 216 | 11kV | 76032 | 352 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN847 HORNSBY section of 11kV Panel 22 11kV Intellirupter 2935 Somerville Pike tripped, reclosed and locked out on Relays: OC trip, lokcout EFI: Zn847 Pa22 S6373 S5996 S8248 S5159 S36034 Singals: Zone Eart, Group Earth Abnormal: PT632 Somerrbille Camirir OOS and in LV// Cause: Defective Sruge Arrestor at PT638. Arrestor cut away See 1641081 ex 1640817 | February | 2019 | 2019Q3 | 2019 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2019-02-15 | N | 216 | N | 5 | N | N | 1.1101 | 39.4971 | 55561.943
[7 empty] | 6382 | 11805 | 1641425 | 2019-02-15 17:30 | 2019-02-15 19:35 | 125 | 11kV | 3000 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN35370 GALSTON section of 11kV Panel 10 section of 11kV fdr from LB2928 to LB62156 tee PT2062, PT1752, PT1121, PT2175 interrupted for safety. Damaged 11kV mains in danger of falling Pole DU42063 | February | 2019 | 2019Q3 | 2019 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2019-02-15 | N | 125 | N | 5 | N | N | 1.1101 | 39.4971 | 2192.3115
[7 empty] | 5738 | 5098 | 1641344 | 2019-02-15 16:36 | 2019-02-15 22:00 | 324 | 11kV | 39496 | 1623 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | ZN13000 LAKE MUNMORAH 11kV CB Panel 11 was opened for safety as there was 11kV mains down on the truck Cause: vehicle hit pole. A truck has hit pole BU407 and broken HV crossarm and 11kV mains had fallen to the ground See 1641783,5,7 Ex 1641316,44,79 | February | 2019 | 2019Q3 | 2019 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2019-02-15 | N | 24.3352 | N | 5 | N | N | 1.1101 | 39.4971 | 28862.5119
[7 empty] | 5558 | 2988 | 1641432 | 2019-02-15 18:25 | 2019-02-16 00:25 | 360 | 11kV | 45000 | 125 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S9174 Wilbung Moreton Ex S9900 Menai Panel 8 "Hall Trumper" suspected Tx fault Remarks: transformer failure fault | February | 2019 | 2019Q3 | 2019 | ZN9900:PA8 | ZN9900:PA8 | ZN09900/000008 | SUTHERLAND | UG | Not Veg | 2019-02-15 | N | 360 | N | 5 | N | N | 1.1101 | 39.4971 | 32884.6727
[7 empty] | 6646 | 14789 | 1641502 | 2019-02-16 13:06 | 2019-02-16 14:30 | 84 | 11kV | 756 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN35500 TOP RYDE section of 11kV Panel 32 Fuse 1435 Caravan Plassey (11kV Centre Phase HDO 63K) Cause: not ascertained. DOp patrolled feeder but could not find cause See 1641502 ex 1641511,818 | February | 2019 | 2019Q3 | 2019 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2019-02-16 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 552.4625
[7 empty] | 6501 | 13298 | 1641543 | 2019-02-16 18:57 | 2019-02-16 23:50 | 293 | 11kV | 203134 | 2269 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN9700 Kirrawee Panel #17 'S9048 Hotham Badto' feeder has tripped & reclosed on: Signals: 11kv trip Relays: A phase timed OC, timer, lockout Field EFI's: nil Remarks: OH down. Feeder tripped & reclosed with 1 span down & live over tree/car/ground nr #116 Coonong Rd, Gymea Bay. Interrupted for safety @ 19:15 at request of Dop due to HV wires down in Coonong Rd, nr Arcadia Ave, Gymea Bay. 11kv feeder isolated from AB35839 to LB 35674 to LB35042 to AB358555 tee PT 48154 Kalkada Coonong, Tee PT9067 Marina Molong. Dop reports wires damaged car (Rego CZN81L) | February | 2019 | 2019Q3 | 2019 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2019-02-16 | N | 89.5258 | N | 3 | N | N | 1.1101 | 39.4971 | 148444.3358
[7 empty] | 6442 | 12606 | 1641572 | 2019-02-16 21:58 | 2019-02-17 01:01 | 183 | 11kV | 27347 | 167 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191630 2 Fault operations, ABC Phases, Overcurrent Targets No 1 prot: B & C O/C. No 2 prot: A,B & C O/C. Bats on mains around poles FR-75206, FR-75209, FR-75252. Note: refer to following event LID 191634 - OMS 1642122, same pole separate flying fox incident, pole in question to be investigated is FR-75206 | February | 2019 | 2019Q3 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2019-02-16 | N | 163.7545 | N | 3 | N | N | 1.1101 | 39.4971 | 19984.381
[7 empty] | 6072 | 8337 | 1641682 | 2019-02-17 22:42 | 2019-02-18 00:30 | 108 | 11kV | 16764 | 167 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191634 2 Fault operations, B and C Phase, Overcurrent. Flying fox at pole FR-75206, all supply on 00.30hrs Please check construction of pole as this is the second time in 2 days a flying fox has cuased feeder outage at this pole | February | 2019 | 2019Q3 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2019-02-17 | N | 100.3832 | N | 2 | N | N | 1.1101 | 39.4971 | 12250.6367
[7 empty] | 6971 | 18217 | 1641681 | 2019-02-17 22:13 | 2019-02-18 03:07 | 294 | 11kV | 16506 | 162 | HV | Animal Flying Fox | Animal | O/H Link | Unplanned | No Weather Impact | N | LID 191633 3 Fault operations, A and C Phases, Overcurrent, Earth Fault Flying fox removed between phase at links 40559 | February | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2019-02-17 | N | 101.8889 | N | 2 | N | N | 1.1101 | 39.4971 | 12062.098
[7 empty] | 6873 | 17184 | 1641687 | 2019-02-18 04:47 | 2019-02-18 06:18 | 91 | 11kV | 145885 | 1855 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN15008 HARBORD 11kV CB Panel 10 'oliver north' tripped and locked out on Relays: B & C phase O/C, timed OC, reclosed and lockout EFI: Nil Cause: Bat found on OH mains Outside 104 Wyadra Ave. Bat removed fdr returned to service See 1641794,6 Ex 1641687,8 | February | 2019 | 2019Q3 | 2019 | ZN15008:PA10 | ZN15008:PA10 | ZN15008/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-02-18 | N | 78.6442 | N | 5 | N | N | 1.1101 | 39.4971 | 106608.4551
[7 empty] | 7157 | 20044 | 1641748 | 2019-02-18 09:53 | 2019-02-18 11:05 | 72 | 11kV | 72 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191644 10 Amp C Phase Fuse, substation DOLF | February | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2019-02-18 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 5775 | 5378 | 1641728 | 2019-02-18 09:35 | 2019-02-18 11:18 | 103 | 11kV | 160824 | 1640 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn36100 Rose Bay 11kv Panel 5 "Fernleigh Spencer, etc" feeder tripped on: Relays: earth fault with fault check Signals: 11kv trip wit hefi Field efi's: nil Abnormal: sw/B closed at S8377 and sw/A opened at S50349 Remarks: suspect cable damaged at 520 Old south head road by civil foundation group | February | 2019 | 2019Q3 | 2019 | ZN36100:PA5 | ZN36100:PA5 | ZN36100/000005 | WOOLLAHRA | UG | Not Veg | 2019-02-18 | N | 98.0634 | N | 5 | N | N | 1.1101 | 39.4971 | 117525.4357
[7 empty] | 7024 | 18729 | 1641699 | 2019-02-18 08:50 | 2019-02-18 11:30 | 160 | 11kV | 160120 | 1847 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN2400 BEROWRA 11kV CB Panel 22 'Crawford Glenview, etc" fdr tripped, reclosed, tripped and locked out on: Relays: Timed OC B phase, Timed OC B-C phase, EFI, FC, Lock out Signals: 11kv trip EFI: S4777 S47461 S8984 S4485 Abnormal: S4485SwB, LB2901 open, AB80 open Cause: UGOH fault short circuit between AB1337 and S4485 North Hollside failed exlosively See 1644478,9,80 ex 1641699,705,6,13,4,22,3 | February | 2019 | 2019Q3 | 2019 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | Unknown | Unknown | 2019-02-18 | N | 86.6919 | N | 5 | N | N | 1.1101 | 39.4971 | 117010.9733
[7 empty] | 5919 | 6607 | 1641990 | 2019-02-18 17:58 | 2019-02-18 19:00 | 62.1333 | 11kV | 10530.6667 | 204 | HV | Overload LV Parallel | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S9174 Wilbung Moreton Dist No.1,2,3 Abnormal: Tx at S9174 Wilbung Moreton has failed. Centre is in LV// Remarks: LV parallel failure. Tx at S9174 Wilbung Moreton has failed. Centre is in LV//. C phase fuses feeding LV// have blown at S9930 and S9915. Fuses replaced at 1900, 1802/19, volts checked satisfacotry at S9174 | February | 2019 | 2019Q3 | 2019 | ZN9900:PA8 | ZN9900:PA8 | ZN09900/000008 | SUTHERLAND | OH | Not Veg | 2019-02-18 | N | 51.6209 | N | 5 | N | N | 1.1101 | 39.4971 | 7695.5006
[7 empty] | 7009 | 18603 | 1642027 | 2019-02-19 00:47 | 2019-02-19 02:43 | 116 | 11kV | 4031 | 46 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191653 3 Fault operations, pole mounted RAGCB bats (flying foxes, removed from OHM at sub pole 25411 | February | 2019 | 2019Q3 | 2019 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2019-02-19 | N | 87.6304 | N | 10 | N | N | 1.1101 | 39.4971 | 2945.7359
[7 empty] | 5975 | 7211 | 1642073 | 2019-02-19 09:40 | 2019-02-19 10:51 | 71 | 11kV | 60138 | 876 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | @Zn10999 Kogarah 11kv Panel 39L labelled "S10379 & S10805" tripped, reclosed & locked out: Relays: E/F, EF check, rec lockout ,efi Remarks: UG cable damaged by contractor. 11kv underground feeder fault damaged by escavator from Sw/A @ S10344 Rocky Darrell to Sw/B @ S64682 Rocky Weeney No.2 | February | 2019 | 2019Q3 | 2019 | ZN10999:PA39 | ZN10999:PA39 | ZN10999/000039 | BAYSIDE | UG | Not Veg | 2019-02-19 | N | 68.6507 | N | 10 | N | N | 1.1101 | 39.4971 | 43947.0766
[7 empty] | 6050 | 8159 | 1642239 | 2019-02-19 16:28 | 2019-02-19 17:28 | 60 | 11kV | 197100 | 3285 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7900 Campbell St, 11kv Panel No2 "S6401 providence Arnold" feeder tripped on Relays: Overcurrent & E/F, EFI, E/F check relay Signals Tx No1 group E, 11kv trip Abnormal: Sw/B closed @ S8322 Hutchinson Fitzroy, Sw/D open @ S8528 Bourke Hill, Sw/A closed @ S4430 Richards Coll, Sw/E open @ S63 Little Riley St Remarks: UG fault. At S7900 Campbell St 11kv feeder fault from S7900 panel No2 to S6401 Providence Arnold Sw/A | February | 2019 | 2019Q3 | 2019 | ZN7900:PA2 | ZN7900:PA2 | ZN07900/000002 | SYDNEY | UG | Not Veg | 2019-02-19 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 144034.8665
[7 empty] | 6406 | 12133 | 1642182 | 2019-02-19 14:32 | 2019-02-19 18:23 | 230.8333 | 11kV | 73174.1667 | 317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 191667 1 Fault operations, A,B,C Phases Overcurrent, Earth Fault, Instantaneous Earth Fault Likely Cable Fault, no location provided at time of entry, as event still ongoing, network currently abnormal, all customers had supply returned due to backfeeding | February | 2019 | 2019Q3 | 2019 | 224:80331 | 224:80331 | ZN00224/080331 | LAKE MACQUARIE | UG | Not Veg | 2019-02-19 | N | 230.8333 | N | 10 | N | N | 1.1101 | 39.4971 | 53473.5227
[7 empty] | 5448 | 1367 | 1642276 | 2019-02-19 18:00 | 2019-02-19 19:45 | 104.9833 | 11kV | 9973.4167 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191683 A Phase DOLF | February | 2019 | 2019Q3 | 2019 | 257:81987 | 257:81987 | ZN00257/081987 | NEWCASTLE | OH | Veg | 2019-02-19 | N | 104.9833 | N | 10 | N | N | 1.1101 | 39.4971 | 7288.2787
[7 empty] | 6260 | 10488 | 1642325 | 2019-02-19 20:47 | 2019-02-19 22:05 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191684 A Phase 10 Amp fuse substation dolf | February | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-02-19 | N | 78 | N | 10 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 6987 | 18399 | 1642371 | 2019-02-19 22:36 | 2019-02-19 23:37 | 61 | 11kV | 127368 | 2088 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At ZN10993 Hurstville Nth 11kv fdr Pa22 "Barnards Ave" tripped and reclosed on: Signals: 11kv trip Relays: earth fault, EFI Remarks: cause not found. Dop attended report 1642371 and talked to caller. Nothing faound. To be patrolled daylight hours. EFI S10627 (no access school) to be reset daylight hours | February | 2019 | 2019Q3 | 2019 | ZN10993:PA22 | ZN10993:PA22 | ZN10993/000022 | BAYSIDE | OH | Veg | 2019-02-19 | N | 61 | N | 10 | N | N | 1.1101 | 39.4971 | 93076.7777
[7 empty] | 5851 | 5911 | 1642381 | 2019-02-19 23:50 | 2019-02-20 00:25 | 35 | 11kV | 25795 | 737 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN10993 Hurstville Nth 11kv fdr Pa.23 "Croot Stoney" tripped and locked out on: Signals: 11kv trip Relays: overcurrent A & B, EFI, reclose lockout Remarks: Animals/Birds, bat | February | 2019 | 2019Q3 | 2019 | ZN10993:PA23 | ZN10993:PA23 | ZN10993/000023 | GEORGES RIVER | OH | Not Veg | 2019-02-19 | N | 35 | N | 10 | N | N | 1.1101 | 39.4971 | 18850.2252
[7 empty] | 5511 | 2110 | 1642622 | 2019-02-19 22:22 | 2019-02-20 00:27 | 125 | 11kV | 18695 | 153 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 3 RE45071 Central Mangrove Relays: EF Trip Cause: lifting ring on top of IR49206 was loose and resting against surge arrestor (centre phase) See 1642622 ex 1642623 | February | 2019 | 2019Q3 | 2019 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2019-02-19 | N | 122.1895 | N | 10 | N | N | 1.1101 | 39.4971 | 13661.7546
[7 empty] | 6776 | 15894 | 1642382 | 2019-02-19 23:48 | 2019-02-20 04:08 | 260 | 11kV | 87560 | 373 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN35370 GALSTON 11kV CB Panel 2 'Galston High School' tripped, reclosed and locked out on B&C phase IOC Lockout and 11kv trip Cause: Tree/branch on oh mains See 1644506,8 ex 1642382 | February | 2019 | 2019Q3 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2019-02-19 | N | 234.7453 | N | 10 | N | N | 1.1101 | 39.4971 | 63986.2654
[7 empty] | 5428 | 1172 | 1642506 | 2019-02-20 10:15 | 2019-02-20 11:20 | 65 | 11kV | 195 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 191689 Single phase DOLF : 10 Amp Carrier replaced. excluded OMS 1642506 | February | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-02-20 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 7069 | 19328 | 1642626 | 2019-02-20 16:35 | 2019-02-20 18:25 | 110 | 11kV | 440 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 191717 Sub 23180 31,5A A phase DOLF carrier burnt up supply off 1625hrs back on 1825hrs | February | 2019 | 2019Q3 | 2019 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2019-02-20 | N | 110 | N | 5 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 5866 | 6057 | 1642574 | 2019-02-20 14:15 | 2019-02-20 18:55 | 280 | 11kV | 280 | 1 | HV | 3rd Party Action | 3rd Party Impact | Circuit Breaker | Unplanned | No Weather Impact | N | At Sub 79492 Biloela Street #5 11kv RMCB tripped on A phase overcurrent 1500kva transformer Remarks: cause not ascertained. II and TPE assisted and okay. Suspect customer fault | February | 2019 | 2019Q3 | 2019 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2019-02-20 | N | 280 | N | 5 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 5727 | 5002 | 1642801 | 2019-02-20 18:22 | 2019-02-20 20:51 | 149 | 11kV | 149 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191716 1 Fault Operations, Earth Fault Liddel called they will patrol their network | February | 2019 | 2019Q3 | 2019 |  |  |  | SINGLETON | OH | Veg | 2019-02-20 | N | 149 | N | 5 | N | N | 1.1101 | 39.4971 | 108.8848
[7 empty] | 6101 | 8819 | 1642690 | 2019-02-20 21:23 | 2019-02-20 23:45 | 142 | 11kV | 1562 | 11 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191718 B and C Phase 40 Amp fuse, Line DOLF Bat on Fdr near sub 54528 B & C LF 6871 blown supply off 2123hrs back on 2345hrs | February | 2019 | 2019Q3 | 2019 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2019-02-20 | N | 142 | N | 5 | N | N | 1.1101 | 39.4971 | 1141.4635
[7 empty] | 6893 | 17501 | 1642710 | 2019-02-21 03:42 | 2019-02-21 05:25 | 103 | 11kV | 76542 | 1041 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191719 2 fault operations Car hit pole 163 NewEnglandHWY Fdr 29877 tripped 0342hrs section isolated to repair mains | February | 2019 | 2019Q3 | 2019 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2019-02-21 | N | 73.5274 | N | 5 | N | N | 1.1101 | 39.4971 | 55934.636
[7 empty] | 5959 | 7024 | 1642731 | 2019-02-21 07:14 | 2019-02-21 09:35 | 141 | 11kV | 130002 | 922 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN1193 LINDFIELD section of 11kV Panel 12 'Wolseley Pacific' 11kV bond burnt off on B phase at AB576 Repairs required see DMA See 1644509 ex 1642731 | February | 2019 | 2019Q3 | 2019 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2019-02-21 | N | 141 | N | 5 | N | N | 1.1101 | 39.4971 | 95001.6272
[7 empty] | 6687 | 15119 | 1642853 | 2019-02-21 13:10 | 2019-02-21 13:55 | 45 | 11kV | 450 | 10 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 191727 Broken crossarm. Pole number not supplied Excluded OMS 1642853 | February | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-02-21 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 6214 | 10133 | 1642874 | 2019-02-21 14:28 | 2019-02-21 17:35 | 187 | 11kV | 187 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 191733 A Phase Sub isolated to repair Live Line Clamp | February | 2019 | 2019Q3 | 2019 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2019-02-21 | N | 187 | N | 5 | N | N | 1.1101 | 39.4971 | 136.6541
[7 empty] | 6033 | 7935 | 1642954 | 2019-02-21 20:50 | 2019-02-22 02:50 | 360 | 11kV | 82815 | 1063 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 191737 2 fault operations 3 Phase Overcurrent; Earth fault 2050hrs Fdr 33413 Open 3 phase O/C & EF trip Cause faulty UGOH OS-20183 all supply back on 0250hrs Excluded OMS 1642954 | February | 2019 | 2019Q3 | 2019 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | Unknown | Unknown | 2019-02-21 | N | 77.9069 | N | 5 | N | N | 1.1101 | 39.4971 | 60518.7594
[7 empty] | 5533 | 2492 | 1643171 | 2019-02-22 18:40 | 2019-02-22 20:00 | 80 | 11kV | 1200 | 15 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 191755 Wire off pin pole EV-71791 Excluded OMS 1643171 | February | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-02-22 | N | 80 | N | 1 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 7100 | 19575 | 1643286 | 2019-02-23 16:30 | 2019-02-23 18:00 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191761 A Phase DOLF : 10 Amp Excluded OMS 1643286 | February | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-02-23 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 6707 | 15230 | 1643245 | 2019-02-23 12:56 | 2019-02-23 23:00 | 604 | 11kV | 21196 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN36200 EMPIRE BAY section of 11kV Panel 4 RE63686 Bundeleer Empire Bay tripped on overcurrent Cause: tree/branch brought down OH 6 Nyeena Avenue Bensville See 1643508,10,1 Ex 1643245,6,94 | February | 2019 | 2019Q3 | 2019 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2019-02-23 | N | 307.1884 | N | 2 | N | N | 1.1101 | 39.4971 | 15489.4116
[7 empty] | 6152 | 9440 | 1643331 | 2019-02-24 01:07 | 2019-02-24 02:37 | 90 | 11kV | 11118 | 194 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191762 2 fault operations 3 phase Overcurrent detailed patrol in daylight req. dq Excluded oms 1643331 | February | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-02-24 | N | 57.3093 | N | 2 | N | N | 1.1101 | 39.4971 | 8124.7065
[7 empty] | 6107 | 8918 | 1643333 | 2019-02-24 03:47 | 2019-02-24 04:45 | 57.6667 | 11kV | 18914.6667 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN15014 MONA VALE section of 11kV Panel 14 RE 22381 Lane Cove Walter tripped on Relays: IOC and OC trip Signals: N/A EFI: N/A Tree branch has fallen onto 11kv mains adjacent PT15577 | February | 2019 | 2019Q3 | 2019 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2019-02-24 | N | 57.6667 | N | 2 | N | N | 1.1101 | 39.4971 | 13822.2805
[7 empty] | 6627 | 14601 | 1643746 | 2019-02-25 08:50 | 2019-02-25 11:10 | 140 | 11kV | 560 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 191776 See planned switching NAR 35177 Depot staff found severely damaged insulators both sides of ABS 6A021 and advised it needed immediate repairs. This required an axtra area to be interrupted, but this area was only interrupted whilst the ABS was repaired. No protection operated. | February | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-02-25 | N | 140 | N | 3 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 7075 | 19374 | 1643540 | 2019-02-25 10:58 | 2019-02-25 12:50 | 112 | 11kV | 13234 | 244 | HV | 3rd Party Action | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S35555 Croydon 11kv Panel No14 "S7491 Frederick Parramatta" feeder tripped on Relays: EFI, 50 TABC Signals: 11kv trip Remarks: contractor error caused failure. West connex Electrician applied line side earth switch instead of applying load side earth switch | February | 2019 | 2019Q3 | 2019 | ZN35555:PA14 | ZN35555:PA14 | ZN35555/000014 | INNER WEST | Unknown | Not Veg | 2019-02-25 | N | 54.2377 | N | 3 | N | N | 1.1101 | 39.4971 | 9671.0169
[7 empty] | 6208 | 10065 | 1643718 | 2019-02-25 20:02 | 2019-02-26 00:37 | 275 | 11kV | 36025 | 131 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191778 3 fault operations 3 phase Overcurrent faulty 11kv main at sub 1505. Excluded OMS 1643718 & 1643724 | February | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2019-02-25 | N | 275 | N | 3 | N | N | 1.1101 | 39.4971 | 26326.0074
[7 empty] | 5578 | 3294 | 1643767 | 2019-02-26 08:46 | 2019-02-26 10:15 | 89 | 11kV | 178 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 191786 A Phase DOLF : 31 Amp Excluded OMS 1643767 | February | 2019 | 2019Q3 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2019-02-26 | N | 89 | N | 2 | N | N | 1.1101 | 39.4971 | 130.0771
[7 empty] | 6395 | 11951 | 1643903 | 2019-02-26 13:35 | 2019-02-26 14:23 | 48 | 11kV | 96 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191795 2 fault operations A & B phase, Overcurrent, Earth Fault JESMOND SUB Sw 80794 - 51AB, 51N Newcastle Uni sub 1 - Dir E/F Note: SUPPLY RESTORED TO ALL CUSTOMERS AT 1423hrs, Testing of 11kV cables organised. | February | 2019 | 2019Q3 | 2019 | 258:80794 | 258:80794 | ZN00258/080794 | NEWCASTLE | OH | Veg | 2019-02-26 | N | 48 | N | 2 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 6498 | 13273 | 1644027 | 2019-02-27 03:51 | 2019-02-27 04:46 | 55 | 11kV | 62865 | 1143 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1287 REVESBY 11kV CB Panel 5 'S6360 Davis Banks #3' tripped on Earth Fault, Lockout, EFI, 11kv trip Cause: UG Fault from Panel 5 to S6360 Sub Davies Banks #3 See 1644027 ex 1644029 | February | 2019 | 2019Q3 | 2019 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-02-27 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 45939.8878
[7 empty] | 6108 | 8936 | 1644077 | 2019-02-27 09:20 | 2019-02-27 12:00 | 160 | 11kV | 345273 | 2980 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kv Panel 15 CB at ZN2835 Burwood tripped and locked out on: Signals: 11kv trip, Tx2 group earth, Zone earth Relays: EFI, fault check, B phase EF, SC Remarks: UG fault. There is an 11kv UG fault between S49124 Short St East to S20232 Underwood POM tee to S5752 Wentworth Coleman | February | 2019 | 2019Q3 | 2019 | ZN2835:PA15 | ZN2835:PA15 | ZN02835/000015 | STRATHFIELD | UG | Not Veg | 2019-02-27 | N | 115.8634 | N | 3 | N | N | 1.1101 | 39.4971 | 252315.3246
[7 empty] | 6318 | 11108 | 1644043 | 2019-02-27 07:11 | 2019-02-27 15:50 | 519 | 11kV | 50689 | 1030 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191806 1 fault operation C Phase Overcurrent 11kV Mains on the ground had fallen on TAFE Fence near pole HS-43366, feeder opened by Control Room for Safety. Conductor failed at crimp joint. No 1 Protection Panel 51C The Control Room initially had no field operators available so could only do initial load transfers to other feeders via SCADA. The interruption area could have been minimised had remote operation been available from Sw 66337 at Moorebank Columbard sub. The lack of remote operation for this switch was reported in October 2017. Excluded OMS 1444062 & 1644043. | February | 2019 | 2019Q3 | 2019 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2019-02-27 | N | 49.2126 | N | 3 | N | N | 1.1101 | 39.4971 | 37042.0261
[7 empty] | 6219 | 10166 | 1644493 | 2019-02-28 14:50 | 2019-02-28 16:29 | 99 | 11kV | 9974 | 106 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2196 Milperra Panel 11 'S6481 etc' feeder has tripped Signals: 11kv trip Relays: EF, EFI, FC Field EFI's @ Subs: All down to and including S4243 Remarks: UG fault. Possible UG fault between Sw/B @ S4243 Milperra Edgar No.1, Sw/A @ S8243 Edgar Milperra and Sw/A @ S2607 IIma St | February | 2019 | 2019Q3 | 2019 | ZN2196:PA11 | ZN2196:PA11 | ZN02196/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-02-28 | N | 94.0943 | N | 3 | N | N | 1.1101 | 39.4971 | 7288.705
[7 empty] | 5842 | 5833 | 1644491 | 2019-02-28 14:50 | 2019-02-28 17:42 | 172 | 11kV | 10368 | 65 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2196 Milperra Panel 6 "S6224' Feeder has tripped Signals: 11kv trip Relays: A and B phase OC, EF, EFI, FC Remarks: UG Fault. See associated outage on panel 20 during restoration At 1713. UG fault located between Sw/D @ S6182 Violet St No5 and Sw/A @ S4175 Violet St No.1 | February | 2019 | 2019Q3 | 2019 | ZN2196:PA6 | ZN2196:PA6 | ZN02196/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-02-28 | N | 159.5077 | N | 3 | N | N | 1.1101 | 39.4971 | 7576.6286
[7 empty] | 6863 | 17056 | 1644549 | 2019-02-28 20:28 | 2019-02-28 20:55 | 27 | 11kV | 52650 | 1950 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 191836 2 fault operation B & C Phase Overcurrent possum at pole IV-32099 no damage caused | February | 2019 | 2019Q3 | 2019 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2019-02-28 | N | 27 | N | 3 | N | N | 1.1101 | 39.4971 | 38475.0671
[7 empty] | 5868 | 6067 | 1644697 | 2019-03-01 17:22 | 2019-03-01 20:53 | 211 | 11kV | 3228 | 58 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191869 1 fault operation Single phase Sensitive Earth Fault Tree on mais pole FK-23080 Small fire started, put out by crew. RFS to attend for inspection/mop up. Excluded OMS 1644697 & 1644698 | March | 2019 | 2019Q3 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2019-03-01 | N | 55.6552 | N | 3 | N | N | 1.1101 | 39.4971 | 2358.9272
[7 empty] | 6139 | 9302 | 1644733 | 2019-03-01 21:39 | 2019-03-01 23:50 | 131.0833 | 11kV | 2228.4167 | 17 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 191870 A & B phase DOLF : 31 Amp bats removed from OHM | March | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2019-03-01 | N | 131.0833 | N | 3 | N | N | 1.1101 | 39.4971 | 1628.4612
[7 empty] | 6926 | 17822 | 1644715 | 2019-03-01 20:26 | 2019-03-02 11:40 | 914 | 11kV | 80180 | 675 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Panel 10 Galston CP50015 Quarry Old Northern tripped Abnormal Switching: SW/B closed @ S6680, SW/A open @ S5928 Cause: 23 Hermers Rd Galston - HV Clashed with LV Mains at PT814 - Customer Switchboard inspections required. See OMS 1645354 1635356 1635358 1545359 1644716 1644715 1644727 1644730 1644752 | March | 2019 | 2019Q3 | 2019 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | OH | Veg | 2019-03-01 | N | 118.7852 | N | 3 | N | N | 1.1101 | 39.4971 | 58593.1791
[7 empty] | 6293 | 10802 | 1644805 | 2019-03-02 14:20 | 2019-03-02 15:45 | 85 | 11kV | 20723 | 285 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN14144 WAMBERAL 11kV CB Panel 5 'LK41596' tripped and reclosed on: Relays: A & b phase OC Signals: 11k trip EFI: Nil Cause: Tree branch contact - other Feeder originallu reclosed. Tree brought down 11kV mains outside 3 Mittara Rd. Fdr interrupted for safety after hazard recieved See 1645326,7 ex 1644806 | March | 2019 | 2019Q3 | 2019 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2019-03-02 | N | 72.7123 | N | 1 | N | N | 1.1101 | 39.4971 | 15143.7572
[7 empty] | 5359 | 224 | 1644843 | 2019-03-03 02:32 | 2019-03-03 04:13 | 101 | 11kV | 148289 | 1689 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ Sub 690 Campsie Zn Panel #28 labelled Allen Onslow tripped on A phase Timed OC EFI, E/L, 11kv trip, Field EFIs operated correctly Remarks: UG fault. | March | 2019 | 2019Q3 | 2019 | ZN690:PA28 | ZN690:PA28 | ZN00690/000028 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-03-03 | N | 87.7969 | N | 3 | N | N | 1.1101 | 39.4971 | 108365.2274
[7 empty] | 5647 | 4092 | 1644914 | 2019-03-03 17:18 | 2019-03-03 20:09 | 171 | 11kV | 188811 | 1177 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN15005 BELROSE 11kV CB Panel 10 'Forest Way Dawes' fdr tripped Realys: OC & EF SignalsL ZE, Trip EFI: All EFI's down to and including S16399 2nd attempt: ZN15005 BELROSE 11kV CB Panel 10 'Forest Way Dawes' fdr tripped Relays: OC & EF Singals: ZE, trip EFI: S16807 S16752 S17065 S49367 S16782 Abnormal: LB22982 closed, sw/B open at S16736, SwA closed at S17155, AB25115 open Cause: UG Fault 11kv fdr fault from S16782 to S16781 See 1645350,61 Ex 1644914,5,21 | March | 2019 | 2019Q3 | 2019 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | UG | Not Veg | 2019-03-03 | N | 160.4172 | N | 3 | N | N | 1.1101 | 39.4971 | 137977.5098
[7 empty] | 6787 | 16141 | 1644937 | 2019-03-03 19:55 | 2019-03-03 21:19 | 84 | 11kV | 138486 | 2091 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S9035 Caringbah Panel 4 "S9797 Cawarra Dian etc" fdr tripped on Relays: LHS C Phase IOC, EF, Lockout, Timing, EFI Signals: 11kv trip, ZE, Tx2 GE Remarks: UG fault. 11kv UG cable fault from S9524 Boulevarde Taren Point To S9552 Captain Taren to S9728 Taren Boulevarde | March | 2019 | 2019Q3 | 2019 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | UG | Not Veg | 2019-03-03 | N | 66.2296 | N | 3 | N | N | 1.1101 | 39.4971 | 101201.4842
[7 empty] | 5780 | 5404 | 1644958 | 2019-03-04 03:46 | 2019-03-04 05:35 | 109 | 11kV | 68195 | 736 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn10993 Hurstville North Panel 23 'Lyle St' feeder has tripped Signals: 11kv trip Relays: 51BC EFI trip LO Field EFI's @ Subs: nil Remarks: animals/birds. Bat has flown into main, location cnr Stoney Creek Rd & Monaro Ave, Kingsgrove, reports of arcing wires | March | 2019 | 2019Q3 | 2019 | ZN10993:PA23 | ZN10993:PA23 | ZN10993/000023 | GEORGES RIVER | OH | Not Veg | 2019-03-04 | N | 92.6562 | N | 1 | N | N | 1.1101 | 39.4971 | 49834.8946
[7 empty] | 6986 | 18396 | 1645308 | 2019-03-05 13:15 | 2019-03-05 14:05 | 50 | 11kV | 2500 | 50 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Hot >35C | N | LID 191921 Conductor off pin pole 8F-90149 Excluded OMS 1645232, | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-03-05 | N | 50 | N | 1 | N | N | 1.1101 | 39.4971 | 1826.9263
[7 empty] | 6017 | 7810 | 1645453 | 2019-03-06 02:00 | 2019-03-06 03:58 | 118 | 11kV | 82537 | 704 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN14892 CHARMHAVEN 11kV CB Panel 9 'S14513 Advance Crowe" fdr tripped on: Relays: 50T BC phase, lockout, reclose, fault check Signals: 11kv trip, Tx1 Group Earth EFI: S14513 S14237 Cause: not ascertained See 1646782,5 Ex 1645453 | March | 2019 | 2019Q3 | 2019 | ZN14892:PA9 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Veg | 2019-03-06 | N | 117.2401 | N | 16 | N | N | 1.1101 | 39.4971 | 60315.6052
[7 empty] | 5370 | 436 | 1645493 | 2019-03-06 09:30 | 2019-03-06 09:45 | 15 | 11kV | 2760 | 184 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 191939 3 Phase section isolated for removal of tree from mains pole mn 53932 | March | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-03-06 | N | 15 | N | 16 | N | N | 1.1101 | 39.4971 | 2016.9266
[7 empty] | 7166 | 20244 | 1645490 | 2019-03-06 09:05 | 2019-03-06 11:15 | 130 | 11kV | 165886 | 1725 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN10995 Riverwood Panel #6 'Pearce Av' feeder has tripped/recosed triped and locked out on: Signals: 11kv trip, Tx1 Group Earth. Relays: A phase O/C, A phase IOC, lockout, timing Remarks: UG cable damaged by contractor. Ex Zn10995 Riverwood Panel #6 - 11kv section of feeder from S65982 to S65704 to S10839 to S10178 tee PT10959 Pritchard Forest (q type). $4 prtichard pl, peakhurst "Furgo Smith - contractor wires damaged during excavation. No one injured. Work has stopped on site". | March | 2019 | 2019Q3 | 2019 | ZN10995:PA6 | ZN10995:PA6 | ZN10995/000006 | GEORGES RIVER | UG | Not Veg | 2019-03-06 | N | 96.1658 | N | 16 | N | N | 1.1101 | 39.4971 | 121224.596
[7 empty] | 6071 | 8336 | 1645583 | 2019-03-06 13:28 | 2019-03-06 15:19 | 111 | 11kV | 40293 | 363 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | 11kv Rec49253 Rex McLean tripped on SEL. Section on Pnl 32 "Cantrell St, etc" feeder at Zn 1850 Bass Hill Abnormal: Sw/B closed at S47485 Bambi Rex, Sw/A open at S5081 Bellevue Birdwood R.49253 Rex Mclean By-passed Remarks: protection malfunction. Rec49253 was by passed at the time with the Auto reclose and SEL left auto | March | 2019 | 2019Q3 | 2019 | ZN1850:PA32 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-03-06 | N | 111 | N | 16 | N | N | 1.1101 | 39.4971 | 29444.936
[7 empty] | 5721 | 4974 | 1645645 | 2019-03-06 15:04 | 2019-03-06 16:15 | 71 | 11kV | 142 | 2 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Replaced Blown Dolf | March | 2019 | 2019Q3 | 2019 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2019-03-06 | N | 71 | N | 16 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 6380 | 11781 | 1645683 | 2019-03-06 15:54 | 2019-03-06 18:17 | 143 | 11kV | 39761 | 281 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191956 2 fault operations A & C phases Overcurrent Excluded OMS 1645683 | March | 2019 | 2019Q3 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2019-03-06 | N | 141.4982 | N | 16 | N | N | 1.1101 | 39.4971 | 29056.166
[7 empty] | 5459 | 1471 | 1645708 | 2019-03-06 16:59 | 2019-03-06 18:40 | 101.4333 | 11kV | 2130.1 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 191960 A Phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | March | 2019 | 2019Q3 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-03-06 | N | 101.4333 | N | 16 | N | N | 1.1101 | 39.4971 | 1556.6143
[7 empty] | 5787 | 5456 | 1645722 | 2019-03-06 17:32 | 2019-03-06 21:05 | 213.0333 | 11kV | 21090.3 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191965 B Phase DOLF : 40 Amp Excluded OMS 1645732 | March | 2019 | 2019Q3 | 2019 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Veg | 2019-03-06 | N | 213.0333 | N | 16 | N | N | 1.1101 | 39.4971 | 15412.1692
[7 empty] | 6359 | 11575 | 1645779 | 2019-03-06 20:16 | 2019-03-06 21:50 | 94 | 11kV | 188 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191980 C Phase DOLF : 10 Amp Excluded OMS 1645779 | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-03-06 | N | 94 | N | 16 | N | N | 1.1101 | 39.4971 | 137.3849
[7 empty] | 6143 | 9344 | 1645671 | 2019-03-06 15:34 | 2019-03-06 22:15 | 401 | 11kV | 70214 | 386 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex ZN14891 WYONG section of 11kV Panel 12 Cedar Northcott CP50630 Yarramalong Chandlers 0.1 has tripped Relays: OC trip and LO Abnormal: @RE48813 Yarramalong Boyds 3.7 LB48813Z is closed due to REG CP48814 Yarramlong Boyds 3.8 defective Cause: Tree/branch brought down OH outside 573 Ravendale Rd Ravendale. Lineworkers have made repairs See 1646797,8,9,800,1,2 Ex 1645671,716,804 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2019-03-06 | N | 181.9016 | N | 16 | N | N | 1.1101 | 39.4971 | 51310.3202
[7 empty] | 5462 | 1524 | 1645758 | 2019-03-06 18:44 | 2019-03-06 22:15 | 210.9167 | 11kV | 2109.1667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 191982 DOLF : 20 Amp | March | 2019 | 2019Q3 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-03-06 | N | 210.9167 | N | 16 | N | N | 1.1101 | 39.4971 | 1541.3168
[7 empty] | 6542 | 13758 | 1645776 | 2019-03-06 20:07 | 2019-03-06 22:20 | 133 | 11kV | 133 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 191981 DOLF : 10 Amp | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-03-06 | N | 133 | N | 16 | N | N | 1.1101 | 39.4971 | 97.1925
[7 empty] | 6270 | 10592 | 1645743 | 2019-03-06 17:55 | 2019-03-07 00:10 | 375 | 11kV | 31576 | 175 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 191976 1 fault operation Pole down AI-80183, wire off pin AI-50092 Targets required Excluded OMS 1645749, 1645753 ## | March | 2019 | 2019Q3 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2019-03-06 | N | 180.4343 | N | 16 | N | N | 1.1101 | 39.4971 | 23074.8095
[7 empty] | 6328 | 11226 | 1645752 | 2019-03-06 18:28 | 2019-03-07 01:10 | 402 | 11kV | 8040 | 20 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 191989 A Phase DOLF : 40 Amp Faulty L/A's Excluded OMS 1645752 | March | 2019 | 2019Q3 | 2019 | 257:82003 | 257:82003 | ZN00257/082003 | NEWCASTLE | OH | Not Veg | 2019-03-06 | N | 402 | N | 16 | N | N | 1.1101 | 39.4971 | 5875.3949
[7 empty] | 7033 | 18855 | 1645723 | 2019-03-06 17:34 | 2019-03-07 04:15 | 641 | 11kV | 4487 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 191990 A & B Phase DOLF : 20 Amp LAs replaced at sub 71253. Excluded oms 1645723 | March | 2019 | 2019Q3 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-03-06 | N | 641 | N | 16 | N | N | 1.1101 | 39.4971 | 3278.9673
[7 empty] | 5387 | 611 | 1645750 | 2019-03-06 18:19 | 2019-03-07 13:15 | 1136 | 11kV | 10501 | 17 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 191974 Broken crossarm & mains down pole EI-20016 Excluded OMS 1645350, 1645770 | March | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-03-06 | N | 617.7059 | N | 16 | N | N | 1.1101 | 39.4971 | 7673.8211
[7 empty] | 6582 | 14263 | 1646248 | 2019-03-08 18:00 | 2019-03-08 18:40 | 40 | 11kV | 80 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 12 Feeder between CP62447 & CP40899 interrutped for safety reasons. Truck ran into pole outside 230 BUmble Hill Kulnura. 11kv fdr interrupted to remove truck from pole. See 1646814 ex 1646216,47,8,9 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-03-08 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 6635 | 14684 | 1646280 | 2019-03-08 19:25 | 2019-03-08 20:20 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Planned LID 192013 Single phase DOLF : 3 Amp Excluded OMS 1646280 | March | 2019 | 2019Q3 | 2019 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2019-03-08 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 6172 | 9722 | 1646277 | 2019-03-08 18:59 | 2019-03-08 22:55 | 236 | 11kV | 236 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 192012 Single phase DOLF : 20 Amp sub isolated for repairs, FAULTY ARRESTOR ON A- PHASE Excluded oms 1646277 | March | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-03-08 | N | 236 | N | 3 | N | N | 1.1101 | 39.4971 | 172.4618
[7 empty] | 6495 | 13239 | 1646306 | 2019-03-09 04:14 | 2019-03-09 05:04 | 50 | 11kV | 97500 | 1950 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192016 2 fault operations B & C Phase Overcurrent possum found at pole IV-32099. Excluded oms report 1646308 | March | 2019 | 2019Q3 | 2019 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2019-03-09 | N | 50 | N | 25 | Y | Y | 1.1101 | 39.4971 | 71250.1242
[7 empty] | 5978 | 7258 | 1646338 | 2019-03-09 11:05 | 2019-03-09 11:15 | 10 | 11kV | 1080 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 10 Wyongah' fdr between LB45153 to PT18776 PT78119 PT18777 PT14424 isolated. Branch on 11kv mains, possible flash over from HV to LV See 1646354 ex 1646338 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2019-03-09 | N | 10 | N | 25 | Y | Y | 1.1101 | 39.4971 | 789.2321
[7 empty] | 6013 | 7773 | 1646335 | 2019-03-09 09:30 | 2019-03-09 11:50 | 140 | 11kV | 140 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192018 Single phase DOLF : 10 Amp Excluded OMS 1646335 | March | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-03-09 | N | 140 | N | 25 | Y | Y | 1.1101 | 39.4971 | 102.3079
[7 empty] | 5745 | 5130 | 1646392 | 2019-03-09 14:34 | 2019-03-09 15:30 | 56 | 11kV | 112 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192021 A Phase DOLF : 10 Amp Excluded OMS 1646392 | March | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-03-09 | N | 56 | N | 25 | Y | Y | 1.1101 | 39.4971 | 81.8463
[7 empty] | 5883 | 6201 | 1646381 | 2019-03-09 13:43 | 2019-03-09 17:00 | 197 | 11kV | 25105 | 165 | HV | Lightning Strike | Adverse Weather/Environment | OTHER - REFER COMMENTS | Unplanned | Electrical Storm | N | LID 192022 1 fault operation C Phase Overcurrent intellirupter 77136. 2ph closed 1ph opened after lighting strike. Excluded OMS 1646381 | March | 2019 | 2019Q3 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | Unknown | Not Veg | 2019-03-09 | N | 152.1515 | N | 25 | Y | Y | 1.1101 | 39.4971 | 18345.9935
[7 empty] | 5366 | 354 | 1646386 | 2019-03-09 14:07 | 2019-03-09 17:20 | 193 | 11kV | 61250 | 898 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192020 1 fault operation Earth Fault Tree on OHM Excluded OMS 1636386 | March | 2019 | 2019Q3 | 2019 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2019-03-09 | N | 68.2071 | N | 25 | Y | Y | 1.1101 | 39.4971 | 44759.6934
[7 empty] | 5454 | 1452 | 1646446 | 2019-03-09 17:04 | 2019-03-09 18:44 | 100 | 11kV | 3700 | 37 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192026 B & C Phase DOLF : 31 Amp Sub 54735 Faulty Cph LA cut away, 10A DOLF replaced also. Excluded oms 1646446 | March | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2019-03-09 | N | 100 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2703.8509
[7 empty] | 5364 | 310 | 1646472 | 2019-03-09 17:53 | 2019-03-09 18:45 | 52 | 11kV | 52 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192024 Single phase DOLF : 10 Amp Excluded OMS 1646472 | March | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-03-09 | N | 52 | N | 25 | Y | Y | 1.1101 | 39.4971 | 38.0001
[7 empty] | 5550 | 2840 | 1646408 | 2019-03-09 15:37 | 2019-03-09 19:10 | 213 | 11kV | 3408 | 16 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 192023 Single phase DOLF : 10 Amp Broken xarm & blown DOLF sub 50748 | March | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2019-03-09 | N | 213 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2490.4659
[7 empty] | 5582 | 3347 | 1646427 | 2019-03-09 16:22 | 2019-03-09 19:30 | 188 | 11kV | 3572 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192027 B Phase DOLF : 63 Amp Excluded OMS 1646427 | March | 2019 | 2019Q3 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2019-03-09 | N | 188 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2610.3122
[7 empty] | 5436 | 1252 | 1646429 | 2019-03-09 16:21 | 2019-03-09 20:18 | 237 | 11kV | 202730 | 856 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192030 1 fault operation Earth Fault Excluded OMS 1646429 | March | 2019 | 2019Q3 | 2019 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2019-03-09 | N | 236.8341 | N | 25 | Y | Y | 1.1101 | 39.4971 | 148149.1045
[7 empty] | 5711 | 4797 | 1646500 | 2019-03-09 20:12 | 2019-03-09 20:55 | 42.8667 | 11kV | 42.8667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192033 Single phase DOLF : 10 Amp Excluded OMS 1646501 | March | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2019-03-09 | N | 42.8667 | N | 25 | Y | Y | 1.1101 | 39.4971 | 31.3257
[7 empty] | 5785 | 5451 | 1646422 | 2019-03-09 16:12 | 2019-03-09 21:55 | 343 | 11kV | 686 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192036 A Phase DOLF : 10 Amp Excluded OMS 1646422 | March | 2019 | 2019Q3 | 2019 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2019-03-09 | N | 343 | N | 25 | Y | Y | 1.1101 | 39.4971 | 501.3086
[7 empty] | 6461 | 12845 | 1646437 | 2019-03-09 16:43 | 2019-03-09 22:10 | 327 | 11kV | 654 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192037 A Phase DOLF : 10 Amp Excluded OMS 1646437 | March | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-03-09 | N | 327 | N | 25 | Y | Y | 1.1101 | 39.4971 | 477.9239
[7 empty] | 5658 | 4254 | 1646449 | 2019-03-09 17:09 | 2019-03-09 22:35 | 326 | 11kV | 326 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192038 Single phase DOLF : 10 Amp 10A LF 42250 & sub DOLF 71044 replaced. Excluded OMS No. 1646449 | March | 2019 | 2019Q3 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2019-03-09 | N | 326 | N | 25 | Y | Y | 1.1101 | 39.4971 | 238.2312
[7 empty] | 6097 | 8725 | 1646430 | 2019-03-09 17:00 | 2019-03-09 23:00 | 360 | 11kV | 11160 | 31 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 192028 11kV OHM down at pole AK-32419. Excluded OMS No. 1646475 | March | 2019 | 2019Q3 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-03-09 | N | 360 | N | 25 | Y | Y | 1.1101 | 39.4971 | 8155.3988
[7 empty] | 7012 | 18634 | 1646466 | 2019-03-09 17:34 | 2019-03-09 23:37 | 363 | 11kV | 1089 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192039 Single phase DOLF : 10 Amp Replace sub L/A's Excluded OMS 1646466 | March | 2019 | 2019Q3 | 2019 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2019-03-09 | N | 363 | N | 25 | Y | Y | 1.1101 | 39.4971 | 795.8091
[7 empty] | 5485 | 1768 | 1646457 | 2019-03-09 17:21 | 2019-03-10 00:05 | 404 | 11kV | 404 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192041 Single phase DOLF : 10 Amp Excluded OMS 1646457 | March | 2019 | 2019Q3 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-03-09 | N | 404 | N | 25 | Y | Y | 1.1101 | 39.4971 | 295.2313
[7 empty] | 6738 | 15452 | 1646468 | 2019-03-09 17:34 | 2019-03-10 00:20 | 406 | 11kV | 406 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192044 Single phase DOLF : 10 Amp Excluded OMS 1646468 | March | 2019 | 2019Q3 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-03-09 | N | 406 | N | 25 | Y | Y | 1.1101 | 39.4971 | 296.6928
[7 empty] | 5792 | 5492 | 1646411 | 2019-03-09 15:39 | 2019-03-10 01:02 | 563 | 11kV | 36812 | 463 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192043 2 fault operation Earth Fault Replace L/A's at Sw 61201 Excluded OMS 1646411 | March | 2019 | 2019Q3 | 2019 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2019-03-09 | N | 79.5076 | N | 25 | Y | Y | 1.1101 | 39.4971 | 26901.1238
[7 empty] | 6167 | 9585 | 1646418 | 2019-03-09 15:29 | 2019-03-10 02:40 | 671 | 11kV | 54623 | 108 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192042 3 fault operations Single phase Sensitive Earth Fault 11kV OHM down between poles CI-60149 & CI-60150. Blown LAs & Broken sub DOLF 70212 E Kennedy sub.and sub DOLF 70232 (LID 192047) Excluded OMS 1646407, 1646454 | March | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-03-09 | N | 505.7685 | N | 25 | Y | Y | 1.1101 | 39.4971 | 39916.8773
[7 empty] | 6218 | 10156 | 1646520 | 2019-03-10 01:53 | 2019-03-10 03:13 | 80 | 11kV | 109040 | 1363 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S4545 Meadowbaank Panel 42 tripped and locked out on OC/EF relay, 50TAC, Fault Check, TX3 Fault Check, Reclose IO Cause: Fruit Bat in Darwin St | March | 2019 | 2019Q3 | 2019 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Veg | 2019-03-10 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 79683.2159
[7 empty] | 6723 | 15331 | 1646529 | 2019-03-10 03:50 | 2019-03-10 04:55 | 65 | 11kV | 62855 | 967 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12690 BERKELEY VALE 11kV CB Panel 6 'the krone enterprize' fdr tripped, reclosed and locked out on B/C phase OC Cause: not ascertained | March | 2019 | 2019Q3 | 2019 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2019-03-10 | N | 65 | N | 7 | N | N | 1.1101 | 39.4971 | 45932.5801
[7 empty] | 7101 | 19577 | 1646537 | 2019-03-10 07:15 | 2019-03-10 09:20 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192060 C Phase DOLF : 10 Amp Excluded OMS 1646537 | March | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2019-03-10 | N | 125 | N | 7 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 5569 | 3158 | 1646492 | 2019-03-09 19:03 | 2019-03-10 14:15 | 1152 | 11kV | 1152 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192073 Substation DOLF Replaced arrestors Excluded OMS 1646492 | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-03-09 | N | 1152 | N | 25 | Y | Y | 1.1101 | 39.4971 | 841.8476
[7 empty] | 6279 | 10698 | 1646481 | 2019-03-09 18:29 | 2019-03-10 14:15 | 1186 | 11kV | 1186 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192077 Single phase DOLF : 10 Amp Excluded OMS 1646481 | March | 2019 | 2019Q3 | 2019 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2019-03-09 | N | 1186 | N | 25 | Y | Y | 1.1101 | 39.4971 | 866.6938
[7 empty] | 6549 | 13803 | 1646504 | 2019-03-09 21:02 | 2019-03-10 15:18 | 1095.8833 | 11kV | 20821.7833 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192051 SW 74495 OPENED 11KV MAIN DOWN BETWEEN POLES AH-82524 & AH-82525.(LIVE ON BACKFEED) STAFF TO RETURN IN MORNING. Excluded OMS REPORT 1646528 | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-03-09 | N | 1095.8833 | N | 25 | Y | Y | 1.1101 | 39.4971 | 15215.9451
[7 empty] | 6792 | 16239 | 1646609 | 2019-03-10 15:17 | 2019-03-10 16:20 | 63 | 11kV | 1071 | 17 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12600 LISAROW section of 11kV Panel 2 PT46693 THE RIDGEWAY TIMBER 11kv roadside 16A HDO fuse operated Fuse Fatigue | March | 2019 | 2019Q3 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2019-03-10 | N | 63 | N | 7 | N | N | 1.1101 | 39.4971 | 782.6552
[7 empty] | 6786 | 16123 | 1646571 | 2019-03-10 10:32 | 2019-03-10 17:25 | 413 | 11kV | 4036 | 323 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 192074 found from J.Frazer going to another job. Replace TX and Xarms. Tripped Sw 76909 on try back and would not close Sw by-passed | March | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2019-03-10 | N | 12.4954 | N | 7 | N | N | 1.1101 | 39.4971 | 2949.3898
[7 empty] | 6444 | 12616 | 1646432 | 2019-03-09 16:29 | 2019-03-10 18:45 | 1576 | 11kV | 15001 | 33 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 192068 Earth Fault Sensitive Earth Fault sub 51783 isolated RAGCB was able to be closed. Excluded oms 1646432, 1646518. | March | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-03-09 | N | 454.5758 | N | 25 | Y | Y | 1.1101 | 39.4971 | 10962.2883
[7 empty] | 6253 | 10454 | 1646628 | 2019-03-10 19:22 | 2019-03-10 20:01 | 39 | 11kV | 3861 | 99 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 192082 B Phase Defectyive lightning arrestor faulty arrestor at sub 8463 Bourke st. Fdr 80791 tripped on SEF when sub interconnected. Excluded OMS 1646630, 1646631, 1646628 | March | 2019 | 2019Q3 | 2019 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Not Veg | 2019-03-10 | N | 39 | N | 7 | N | N | 1.1101 | 39.4971 | 2821.5049
[7 empty] | 6300 | 10917 | 1647103 | 2019-03-10 19:52 | 2019-03-10 20:01 | 9 | 11kV | 6606 | 734 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 192083 1 fault operation B Phase Sensitive Earth Fault oms report 1646628. faulty arrestor at sub 8463. also see UPOR 192082/OMS 1647101 reclose turned off for switching. | March | 2019 | 2019Q3 | 2019 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Not Veg | 2019-03-10 | N | 9 | N | 7 | N | N | 1.1101 | 39.4971 | 4827.47
[7 empty] | 6585 | 14287 | 1646668 | 2019-03-11 07:50 | 2019-03-11 09:15 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192109 A Phase DOLF : 10 Amp Excluded OMS 1646668 | March | 2019 | 2019Q3 | 2019 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2019-03-11 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 5486 | 1770 | 1646672 | 2019-03-11 08:13 | 2019-03-11 10:10 | 117 | 11kV | 117 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 192110 DOLF : 10 Amp Excluded OMS 1646672 | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-03-11 | N | 117 | N | 7 | N | N | 1.1101 | 39.4971 | 85.5001
[7 empty] | 7030 | 18805 | 1646684 | 2019-03-11 09:11 | 2019-03-11 11:30 | 139 | 11kV | 417 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192114 A Phase DOLF : 10 Amp Excluded OMS 1646684 | March | 2019 | 2019Q3 | 2019 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2019-03-11 | N | 139 | N | 7 | N | N | 1.1101 | 39.4971 | 304.7313
[7 empty] | 6431 | 12503 | 1646760 | 2019-03-11 11:48 | 2019-03-11 14:50 | 182 | 11kV | 182 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192116 A Phase DOLF : 10 Amp Excluded OMS 1646760 | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-03-11 | N | 182 | N | 7 | N | N | 1.1101 | 39.4971 | 133.0002
[7 empty] | 6606 | 14397 | 1646861 | 2019-03-11 15:26 | 2019-03-11 16:36 | 70 | 11kV | 87076.25 | 1285 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 38 tripped on B phase IOC, Earth Fault and EFI Signals: 11kV Trip. Cause: 11kV feeder from S5026 to S8520 is defective See OMS 1647000 1647001 1646866 1646861 | March | 2019 | 2019Q3 | 2019 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | UG | Not Veg | 2019-03-11 | N | 67.7636 | N | 7 | N | N | 1.1101 | 39.4971 | 63632.7552
[7 empty] | 6704 | 15212 | 1646666 | 2019-03-11 10:00 | 2019-03-11 16:40 | 400 | 11kV | 2400 | 6 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Previous Storm | N | LID 192118 pole and transformer on fire, feeder did not trip Excluded oms 1646666 | March | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-03-11 | N | 400 | N | 7 | N | N | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 5403 | 865 | 1646906 | 2019-03-11 20:19 | 2019-03-11 22:46 | 147 | 11kV | 2793 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192121 Low 11kV OHM between poles AH-82524 & AH-82521. Excluded OMS No. 1646906 | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-03-11 | N | 147 | N | 7 | N | N | 1.1101 | 39.4971 | 2041.042
[7 empty] | 7154 | 20026 | 1647159 | 2019-03-12 16:50 | 2019-03-12 17:50 | 60 | 11kV | 60 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 192140 B Phase DOLF : 10 Amp | March | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2019-03-12 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 5945 | 6909 | 1647184 | 2019-03-12 19:05 | 2019-03-12 21:04 | 119 | 11kV | 187736 | 1888 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1610 Homebush Panel 19 Evans Asia "Tripped on: earth leakage" Field EFI's down to S4790 NB S3019 did not operate Remarks: UG fault. Underground cable fault in section of cable from S4790 Sw/B to S4790 Sw/B | March | 2019 | 2019Q3 | 2019 | ZN1610:PA19 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2019-03-12 | N | 99.4364 | N | 2 | N | N | 1.1101 | 39.4971 | 137191.9315
[7 empty] | 6007 | 7721 | 1647216 | 2019-03-13 05:36 | 2019-03-13 06:55 | 79 | 11kV | 98514 | 1382 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North Panel 19 tripped reclosed tripped and locked out on Signals: 11kV Trip, No1 TX group earth Relays Fault Check, EFI, UF, Trip, Reclose, Timed and Lockout Cause: Lightning arrestors and UGOH damaged to S15938 Wakehurst Golf Club See OMS 1647216 1647226 1647217 | March | 2019 | 2019Q3 | 2019 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Veg | 2019-03-13 | N | 71.2836 | N | 7 | N | N | 1.1101 | 39.4971 | 71991.1255
[7 empty] | 6148 | 9402 | 1647371 | 2019-03-13 13:45 | 2019-03-13 14:49 | 64 | 11kV | 22528 | 352 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.63 tripped on: O/C Field EFIs: S3224 S074 S48275 S5758 UG cable fault between S5758 Sw/B and S3811 Sw/A See 1647479 1647515 | March | 2019 | 2019Q3 | 2019 | ZN384:PA63 | ZN384:PA63 | ZN00384/000063 | INNER WEST | UG | Not Veg | 2019-03-13 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 16462.7979
[7 empty] | 6291 | 10789 | 1647385 | 2019-03-13 14:30 | 2019-03-13 15:09 | 39 | 11kV | 4290 | 110 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9035 CARINBAH 11kv Pnl 8 "Kirimbia Kareena" tripped on Relays: overcurrent Signals: 11kv trip with efi Field efi's: nil Remarks: UG fault. Cable fault from Pnl 8 at ZN9035 Caringbah to Sub 9017 Kirimbla Kreena | March | 2019 | 2019Q3 | 2019 | ZN9035:PA8 | ZN9035:PA8 | ZN09035/000008 | SUTHERLAND | UG | Not Veg | 2019-03-13 | N | 39 | N | 7 | N | N | 1.1101 | 39.4971 | 3135.0055
[7 empty] | 6164 | 9551 | 1647237 | 2019-03-13 07:51 | 2019-03-13 16:20 | 509 | 11kV | 3054 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN14891 WYONG section of 11kV Panel 8 PT13659 PRESTONS VALLEY HDO operated. Large tree brought LV wires down and damaged pole at 58 Prestons Rd. Tx then found to be defective due to fault current Note: PT remained with out supply until 13/03/2019 19:25 refer 1647549 as upstream USL42275 interrutped for safety | March | 2019 | 2019Q3 | 2019 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2019-03-13 | N | 509 | N | 7 | N | N | 1.1101 | 39.4971 | 2231.7731
[7 empty] | 7093 | 19530 | 1647443 | 2019-03-13 17:05 | 2019-03-13 18:17 | 71.6833 | 11kV | 1290.3 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex ZN12650 WEST GOSFORD section of 11kV Panel 1 CP45010 Palm Grove interrupted for safety. To reattach 11kV CCT onto X-arm in Palm Grove | March | 2019 | 2019Q3 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2019-03-13 | N | 71.6833 | N | 7 | N | N | 1.1101 | 39.4971 | 942.9132
[7 empty] | 6333 | 11244 | 1647432 | 2019-03-13 16:20 | 2019-03-13 19:10 | 170 | 11kV | 2890 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 8 USL42275 interrutped for safety To replace faulty tx on PT13659. See separate interruption report on PT13659 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2019-03-13 | N | 170 | N | 7 | N | N | 1.1101 | 39.4971 | 2111.9268
[7 empty] | 6993 | 18475 | 1647465 | 2019-03-13 18:37 | 2019-03-13 21:05 | 148 | 11kV | 296 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12650 WEST GOSFORD section of 11kV Panel 1 PT14852 TELSTRA HUT HORTICULTUR 11kv HDO operated Fuse Fatigue See 1647552 ex 1647465 | March | 2019 | 2019Q3 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2019-03-13 | N | 148 | N | 7 | N | N | 1.1101 | 39.4971 | 216.3081
[7 empty] | 7072 | 19355 | 1647682 | 2019-03-14 15:19 | 2019-03-14 16:33 | 74 | 11kV | 148 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 192192 Single phase DOLF : 10 Amp Excluded OMS 1647682 & 92 | March | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-03-14 | N | 74 | N | 7 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 5804 | 5576 | 1647754 | 2019-03-14 19:38 | 2019-03-14 21:00 | 82 | 11kV | 50676 | 618 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | At Zn965 Pennant Hills Panel 13 tripped on A and C phase OC EFI Signals: Tree branch on OH mains - Removed by DOp | March | 2019 | 2019Q3 | 2019 | ZN965:PA13 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Veg | 2019-03-14 | N | 82 | N | 7 | N | N | 1.1101 | 39.4971 | 37032.5261
[7 empty] | 5957 | 6998 | 1647782 | 2019-03-14 20:48 | 2019-03-15 01:26 | 278 | 11kV | 147008 | 1306 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | Y | At S80 Chatswood Panel 31 Tripped and reclosed on: IOC reclose time delay Lockout. Cause: Lightning strike caused CP253 to open See OMS 1648830 1648831 1647782 | March | 2019 | 2019Q3 | 2019 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Not Veg | 2019-03-14 | N | 112.5636 | N | 7 | N | N | 1.1101 | 39.4971 | 107429.1104
[7 empty] | 6891 | 17448 | 1647940 | 2019-03-15 00:20 | 2019-03-15 02:47 | 147 | 11kV | 38073 | 259 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Previous Storm | N | At S10925 Forest Water Board: 11kV CB Sw/A and Sw/B tripped Relays: A and B phase O/C At PT10382 Docos Croydon centre phase HDO 31.5amp type K operated Remarks: animals/birds. Possum removed by Dop at PT10382 | March | 2019 | 2019Q3 | 2019 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | GEORGES RIVER | OH | Not Veg | 2019-03-15 | N | 147 | N | 8 | N | N | 1.1101 | 39.4971 | 27822.6254
[7 empty] | 6081 | 8432 | 1647760 | 2019-03-14 19:55 | 2019-03-15 03:00 | 425 | 11kV | 183678 | 1346 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN847 Hornsby Panel 15 Tripped on A and B phase OC Cause: HV into Low voltage distributor #3 @ S7920 Grosvenor Fisher 11kV Feeder between S4465 and S7920 tee PT2046 See OMS 1648996 1648998 1647760 1647919 | March | 2019 | 2019Q3 | 2019 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Not Veg | 2019-03-14 | N | 136.4621 | N | 7 | N | N | 1.1101 | 39.4971 | 134226.4648
[7 empty] | 5880 | 6185 | 1647773 | 2019-03-14 20:29 | 2019-03-15 03:41 | 432 | 11kV | 451908 | 1060 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | ZN15002 NARRABEEN 11kV CB Panel 8 ' Relays: C phase timed OC, frame leakage fault check, EFI Signals: 11kv trip, Zone Earth, UV Prot, CB8 Open EFI: CP24276 S15366 S16347 S16913 EFI @ S47436 did not operate Cause: tree branch contact other @ tee off to PT15224 See 1648130,1,3 Ex 1647773 | March | 2019 | 2019Q3 | 2019 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Veg | 2019-03-14 | N | 426.3283 | N | 7 | N | N | 1.1101 | 39.4971 | 330241.0374
[7 empty] | 6769 | 15776 | 1647953 | 2019-03-15 01:57 | 2019-03-15 07:45 | 348 | 11kV | 117852 | 1429 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN14891 WYONG 11kV CB Panel 5 'Wyong' fdr has tripped Signals: 11kv trip Relays: ABC timed OC, fault check lock out recloser timming relay Cause: UGOH fault short circuit. Feeder isolated at Zn12410 Wyong Tech to LB42251 to LB43241 tee to S11996 Wyong High. Line worker required. Check loads at Recloser 50560 180Amp pick up See 1649095,7,8 Ex 1647953,7 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | Unknown | Unknown | 2019-03-15 | N | 82.4717 | N | 8 | N | N | 1.1101 | 39.4971 | 86122.7656
[7 empty] | 6541 | 13756 | 1647929 | 2019-03-14 23:42 | 2019-03-15 08:30 | 528 | 11kV | 176264 | 907 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | ZN12610 LONG JETTY 11kV CB Panel 20 'Matcham St' fdr tripped Singals: 11kv trip Relays: Earth Fault, EFI, Fault CHeck EFI's S18759, EFI did not operate at S18758 Tumbi Umbi LB50250 (FD) Relay OC Detection B Cause: weather related RE45000 Tumbi Umbi failed to operate and to pick up fault 11kv fault between S18758 SwB to S18759 SwA to PT18347 See 1648974,5,6,8 Ex 1647929,73 | March | 2019 | 2019Q3 | 2019 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | UG | Not Veg | 2019-03-14 | N | 194.3374 | N | 7 | N | N | 1.1101 | 39.4971 | 128808.5323
[7 empty] | 6176 | 9764 | 1647934 | 2019-03-14 23:55 | 2019-03-15 09:50 | 595 | 11kV | 3570 | 6 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Rain Wind Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 1 PT11805 ELMO FOOTES 0.7 Footpath side HDO fuse operated. 10Amp Fuse replaced 15/3, 9:50 Cause: weather related. Lightning reported in area at time of fault See 1649038 ex 1647934 | March | 2019 | 2019Q3 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2019-03-14 | N | 595 | N | 7 | N | N | 1.1101 | 39.4971 | 2608.8507
[7 empty] | 6354 | 11495 | 1647984 | 2019-03-15 05:27 | 2019-03-15 11:00 | 333 | 11kV | 74259 | 223 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn15002 narrabeen Pnl.8 - Footpath phase bond burnt off AB20259 | March | 2019 | 2019Q3 | 2019 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2019-03-15 | N | 333 | N | 8 | N | N | 1.1101 | 39.4971 | 54266.2869
[7 empty] | 6307 | 10976 | 1647838 | 2019-03-14 21:31 | 2019-03-15 11:45 | 854 | 11kV | 76784 | 96 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | REC.20852 McCarrs Creek Rd - tripped on: O/C trip Dop found blown surge arrestor at teh UGOH above S46269 Cottage Point Cowan See 1647838 1648070 | March | 2019 | 2019Q3 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-03-14 | Y | 799.8333 | N | 7 | N | Y | 1.1101 | 39.4971 | 56111.4825
[7 empty] | 6090 | 8615 | 1648226 | 2019-03-15 16:35 | 2019-03-15 17:30 | 55 | 11kV | 19580 | 356 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP24701 Scotland Island - Sw6000 interrupted for safety to remove tree branch from OH mains. | March | 2019 | 2019Q3 | 2019 | ZN15014:PA10 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2019-03-15 | N | 55 | N | 8 | N | N | 1.1101 | 39.4971 | 14308.4865
[7 empty] | 6921 | 17778 | 1648222 | 2019-03-15 16:27 | 2019-03-15 19:00 | 153 | 11kV | 4896 | 32 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 192216 no protection operation, blown 11kV tapping pole JU-54786 & also damaged UGOH at same pole, isolated faulty UGOH at pole JU- 54786. Crews organised to repair UGOH. | March | 2019 | 2019Q3 | 2019 | 261:81886 | 261:81886 | ZN00261/081886 | NEWCASTLE | Unknown | Unknown | 2019-03-15 | N | 153 | N | 8 | N | N | 1.1101 | 39.4971 | 3577.8524
[7 empty] | 7108 | 19628 | 1648270 | 2019-03-15 19:13 | 2019-03-15 21:11 | 118 | 11kV | 7914 | 107 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Giore HIll Panel 17 tripped Signals: 11kV Trip, Relays: EF, EFI, Fault Check Abnormal Switching: S7771 SW/A to S3795 OOS and defective - SW/A closed @ 2627 Cause: UG cable fault between S7770 and S8483 See OMS 1649033 1649035 1648270 | March | 2019 | 2019Q3 | 2019 | ZN5868:PA17 | ZN5868:PA17 | ZN05868/000017 | WILLOUGHBY | UG | Not Veg | 2019-03-15 | N | 73.9626 | N | 8 | N | N | 1.1101 | 39.4971 | 5783.3178
[7 empty] | 6822 | 16619 | 1648225 | 2019-03-15 16:25 | 2019-03-15 21:40 | 315 | 11kV | 1060 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN15012 KILLARNEY section of 11kV Panel 6L "Killarney West" RE26228 KILLARNEY Valley Road tripped, reclosed, tripped and locked out Tree branch brought down 11kv OH See 1649284,5 ex 1648225 | March | 2019 | 2019Q3 | 2019 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2019-03-15 | N | 265 | N | 8 | N | N | 1.1101 | 39.4971 | 774.6167
[7 empty] | 6113 | 9023 | 1648215 | 2019-03-15 15:56 | 2019-03-15 22:10 | 374 | 11kV | 2244 | 6 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 192217 Repaired burning up LLC Excluded OMS 1648215, 1648218 | March | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2019-03-15 | N | 374 | N | 8 | N | N | 1.1101 | 39.4971 | 1639.849
[7 empty] | 6813 | 16535 | 1648266 | 2019-03-16 00:21 | 2019-03-16 01:07 | 46 | 11kV | 34086 | 741 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN195 Pymble Panel 30 Recloser CP46113 Fiddens Wharf Coronga has tripped on Relays: OC trip and LOckout Branch near AB2303 | March | 2019 | 2019Q3 | 2019 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2019-03-16 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 24909.0434
[7 empty] | 6950 | 18014 | 1648304 | 2019-03-16 00:17 | 2019-03-16 01:20 | 63 | 11kV | 5292 | 84 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN14144 WAMBERAL section of 11kV Panel 7 PT11286 BLUEBELL DILL road and centre phase HDO's were blown (31.5A) Branch across the HV at PT. Tree/Branch on OH mains See 1649121 ex 1648304 | March | 2019 | 2019Q3 | 2019 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2019-03-16 | N | 63 | N | 6 | N | N | 1.1101 | 39.4971 | 3867.2375
[7 empty] | 6915 | 17708 | 1648323 | 2019-03-16 06:53 | 2019-03-16 11:43 | 290 | 11kV | 2610 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 13 USL42028 interrupted for safety. Emergency Repairs See 1648349 ex 1648323 | March | 2019 | 2019Q3 | 2019 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2019-03-16 | N | 290 | N | 6 | N | N | 1.1101 | 39.4971 | 1907.311
[7 empty] | 5799 | 5550 | 1648320 | 2019-03-16 05:58 | 2019-03-16 14:05 | 487 | 11kV | 1294 | 7 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN2466 Flemington 11kv Panel '21' labelled S4444 Hill Carter No.1 tripped on: relays: EF, EFI, Fault check Signals: 11kv trip, Tx4 Group earth, Zone earth At S3620 Tooheys Lidcombe Sw/B tripped on: Relays: B phase OC, Directional earth fault Remarks: UG fault Section of 11kv feeder defective from S4444 Hill Carter No.1 Sw/B to S3620 Tooheys Lidcombe Sw/B to S48233 Parramatta John No.2 Sw/B tee S3298 Nyrang Par No.1 is defective | March | 2019 | 2019Q3 | 2019 | ZN2466:PA21 | ZN2466:PA21 | ZN02466/000021 | PARRAMATTA | UG | Not Veg | 2019-03-16 | N | 184.8571 | N | 6 | N | N | 1.1101 | 39.4971 | 945.617
[7 empty] | 6496 | 13261 | 1648426 | 2019-03-16 14:14 | 2019-03-16 17:45 | 211 | 11kV | 47405 | 703 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At Zn9037 Miranda P7 "Bates Drive" tripped on e/f, efi Remarks: vehicle hit pole. Princess hwy near bates kareela | March | 2019 | 2019Q3 | 2019 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2019-03-16 | N | 67.4324 | N | 6 | N | N | 1.1101 | 39.4971 | 34642.1758
[7 empty] | 6979 | 18307 | 1648476 | 2019-03-16 20:10 | 2019-03-16 22:58 | 168 | 11kV | 8568 | 51 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 192228 No protection operation Section of 11kV OHM isolated to repair 33kV OHM at pole HR-50495. See report 192227/OMS 1648919 | March | 2019 | 2019Q3 | 2019 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2019-03-16 | N | 168 | N | 6 | N | N | 1.1101 | 39.4971 | 6261.2417
[7 empty] | 6303 | 10931 | 1648501 | 2019-03-17 02:51 | 2019-03-17 04:20 | 89 | 11kV | 10858 | 122 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15013 Terrey Hills recloser 21350 Booralie Kulgoa has tripped tree branch on OH mains See OMS 1649148 1648501 | March | 2019 | 2019Q3 | 2019 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2019-03-17 | N | 89 | N | 6 | N | N | 1.1101 | 39.4971 | 7934.7061
[7 empty] | 7119 | 19694 | 1648570 | 2019-03-17 10:05 | 2019-03-17 15:04 | 299 | 11kV | 32715 | 158 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 192231 Supply off 1005hrs Sw 43402 E/F trip cause tree on OHM between MG-97057 & MG-97056 supply back on 1504hrs Excluded OMS 1648570 1648579 | March | 2019 | 2019Q3 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2019-03-17 | N | 207.057 | N | 6 | N | N | 1.1101 | 39.4971 | 23907.1571
[7 empty] | 7068 | 19325 | 1648548 | 2019-03-17 09:18 | 2019-03-17 15:49 | 391 | 11kV | 32029 | 1038 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 192232 B Phase Supply off 0918hrs Sub 9436 blown B phase DOLF replaced at 1525hrs and found transformer faulty Fdr 33600 Opened to isolate transformer supply back on 1549hrs Excluded OMS 1648548 | March | 2019 | 2019Q3 | 2019 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Veg | 2019-03-17 | N | 30.8565 | N | 6 | N | N | 1.1101 | 39.4971 | 23405.8485
[7 empty] | 6702 | 15201 | 1648576 | 2019-03-17 12:38 | 2019-03-17 17:56 | 317.7 | 11kV | 23509.8 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN36200 EMPIRE BAY section of 11kV Panel 11 PT12229 EMPIRE BAY HILLCREST interrupted by DOp Tree/branch brought down OH. outside 41 Del Rio Drive | March | 2019 | 2019Q3 | 2019 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Veg | 2019-03-17 | N | 317.7 | N | 6 | N | N | 1.1101 | 39.4971 | 17180.2684
[7 empty] | 6513 | 13485 | 1648539 | 2019-03-17 07:34 | 2019-03-17 19:15 | 701 | 11kV | 96940 | 711 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn14891 Wyong Panel 12 "Yarramalong" tripped & locked out on: A&C phase overcurrent EFI no Field EFI's Cause: Tree/branch brought down OH A/P issued to lineworkers @ 11:06 to make repairs RE45015 Brush Creek tripped & locked out on: IOC Broken Crossarm 103 Brush Creek Rd See 1649138,9,40,3,4 Ex 1648525,39,86,626,7 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2019-03-17 | N | 136.3432 | N | 6 | N | N | 1.1101 | 39.4971 | 70840.8928
[7 empty] | 6559 | 13882 | 1648862 | 2019-03-18 08:52 | 2019-03-18 10:20 | 88 | 11kV | 101490 | 1573 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | At ZN9252 Jannali 11kv Panel '22' labelled 'S63052 Jannali Aux No.1", tripped, reclosed and locked out on: Relays: IOC, A phase OC, EF, EFI. Timing and lockout Signals: 11kv trip Remarks: lightning/surge arrestor. Defective surge arrestor at PT9041 National Lilac. 11kv feeder from AB35501 to AB35502 tee PT9041 National Lilac is isolated and defective | March | 2019 | 2019Q3 | 2019 | ZN9252:PA22 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Not Veg | 2019-03-18 | N | 64.52 | N | 1 | N | N | 1.1101 | 39.4971 | 74165.8986
[7 empty] | 6313 | 11023 | 1648628 | 2019-03-17 11:57 | 2019-03-18 11:14 | 1397 | 11kV | 232388 | 362 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Flood | N | @ 1157 - Zn4990 City Central - 51/52A tripped on Bz @ 1219 - Zn4990 City Central 51/52 C tripped on Bz Abnormal: Tx 52B out of service S776 defective Flooding at S776 caused 51/52A & C to trip. S4395 S7173 S2998 interrupted to allow water to be pumped out of S776 and returned to service. See 1648618 1648628 1649250 1648637 1649249 1649283 1649282 1649281 | March | 2019 | 2019Q3 | 2019 | ZN4990:PA51 52ABC | ZN4990:PA51 52ABC | ZN04990/51 52ABC | SYDNEY | UG | Not Veg | 2019-03-17 | N | 641.9558 | N | 6 | N | N | 1.1101 | 39.4971 | 169822.2961
[7 empty] | 6592 | 14311 | 1649191 | 2019-03-19 02:12 | 2019-03-19 03:12 | 60 | 11kV | 78840 | 1314 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At ZN129 Hunters Hill 11kv feeder Panel No.35 "Flagstaff dowell etc" feeder tripped and oon: Relays: A protection: trip B and C phase O/C, IOC, BCT B protection: trip, IOC, B and C phase O/C Remarks: animals/birds. Bat removed by Dop cnr Prince Edward and Isler St | March | 2019 | 2019Q3 | 2019 | ZN129:PA35 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Not Veg | 2019-03-19 | Y | 60 | N |  | N | Y | 1.1101 | 39.4971 | 57613.9466
[7 empty] | 5542 | 2665 | 1649226 | 2019-03-19 09:12 | 2019-03-19 11:53 | 161 | 33kV Distribution | 966 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | Y | LID 192252 33kV Fdr 80491 opened by SO, to replace broken crossarm at JT-61934 OHM low <3m White rot in crossarm caused it to break | March | 2019 | 2019Q3 | 2019 | 417:80491 | 417:80491 | ZN00417/080491 | NEWCASTLE | OH | Not Veg | 2019-03-19 | Y | 161 | N |  | N | Y | 1.1101 | 39.4971 | 705.9243
[7 empty] | 5602 | 3573 | 1649361 | 2019-03-19 13:46 | 2019-03-19 14:35 | 49 | 11kV | 3528 | 72 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | Y | LID 192261 A Phase 40 Amp fuse, substation DOLF Fuse fatigue | March | 2019 | 2019Q3 | 2019 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2019-03-19 | Y | 49 | N |  | N | Y | 1.1101 | 39.4971 | 2578.1583
[7 empty] | 6615 | 14498 | 1649455 | 2019-03-19 17:06 | 2019-03-19 18:57 | 111 | 11kV | 46139 | 417 | HV | Arcing | Equipment Failure | Cross arm | Unplanned | No Weather Impact | Y | REC54189 Cooks Peats Ridge 0.5 tripped on: SEF Evidence of a flash over on HV cross arm (Pole LM26) between LV44820 and PT14913. See 1649845 1649846 | March | 2019 | 2019Q3 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-03-19 | Y | 110.6451 | N |  | N | Y | 1.1101 | 39.4971 | 33717.0203
[7 empty] | 7016 | 18675 | 1649506 | 2019-03-19 23:05 | 2019-03-19 23:46 | 41 | 11kV | 54202 | 1322 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 192269 2 Fault operations, A and B phases overcurrent Dead baby possum found at pole JV-20489 | March | 2019 | 2019Q3 | 2019 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2019-03-19 | Y | 41 | N |  | N | Y | 1.1101 | 39.4971 | 39609.2229
[7 empty] | 5571 | 3197 | 1649518 | 2019-03-20 03:57 | 2019-03-20 07:32 | 215 | 11kV | 104447 | 979 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.7 tripped on: Earth Fault Abnormal: AB61759 Closed with LB40372 and LB45440 Open Cause not ascertained See 1649849 1649850 1649851 | March | 2019 | 2019Q3 | 2019 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2019-03-20 | N | 106.6874 | N | 3 | N | N | 1.1101 | 39.4971 | 76326.7869
[7 empty] | 5405 | 884 | 1649526 | 2019-03-20 06:19 | 2019-03-20 07:36 | 77 | 11kV | 149586 | 1952 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192270 2 Fault operations, B and C phase Overcurrent Possum between B and C phases at pole IV-32099 | March | 2019 | 2019Q3 | 2019 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2019-03-20 | N | 76.6322 | N | 3 | N | N | 1.1101 | 39.4971 | 109313.0368
[7 empty] | 6036 | 8002 | 1649693 | 2019-03-20 13:44 | 2019-03-20 14:14 | 30 | 11kV | 15390 | 513 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12570 Avoca 11kv panel No.34 "Terrigal" feeder tripped on Relays: B and C phase O/C, timing relay Abnormal: Sw/b closed at S18705 Barhill Grosvenor, LB41002 copen Remarks: tree branch contact | March | 2019 | 2019Q3 | 2019 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2019-03-20 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 11246.5581
[7 empty] | 6967 | 18192 | 1649898 | 2019-03-21 11:11 | 2019-03-21 12:50 | 99.0667 | 11kV | 8123.4667 | 82 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192291 B Phase DOLF : 40 Amp | March | 2019 | 2019Q3 | 2019 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2019-03-21 | N | 99.0667 | N | 3 | N | N | 1.1101 | 39.4971 | 5936.3898
[7 empty] | 6968 | 18193 | 1649941 | 2019-03-21 15:06 | 2019-03-21 17:50 | 163.8833 | 11kV | 2622.1333 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192294 C Phase DOLF : 16 Amp Tree branch on LV mains pole GW-50191 repaired under CTW. C ph DOLF 16A; B ph LVF 200A. | March | 2019 | 2019Q3 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-03-21 | N | 163.8833 | N | 3 | N | N | 1.1101 | 39.4971 | 1916.1777
[7 empty] | 6756 | 15643 | 1649964 | 2019-03-21 16:23 | 2019-03-21 22:35 | 372 | 11kV | 9779 | 138 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 192295 A & B Phase Overcurrent Truck hit pole AL-30053 causing 11kV outage. Excluded OMS 1649964, 1649968, 1649988 | March | 2019 | 2019Q3 | 2019 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2019-03-21 | N | 70.8623 | N | 3 | N | N | 1.1101 | 39.4971 | 7146.2048
[7 empty] | 5389 | 674 | 1650030 | 2019-03-22 01:21 | 2019-03-22 03:27 | 126 | 11kV | 25830 | 205 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnls.15, 17, 20 & 23 tripped on: Translay + B & C phase O/C @ S1074 Unitec - Sw/C tripped on Translay with an EFI on Sw/E UG cable fault on section of feeder from Pnl.15 to S1074 Sw/C to S7846 Sw/B See 1650087 1650089 1650090 | March | 2019 | 2019Q3 | 2019 | ZN35600:PA20 | ZN35600:PA20 | ZN35600/000020 | RANDWICK | UG | Not Veg | 2019-03-22 | N | 126 | N | 19 | N | N | 1.1101 | 39.4971 | 18875.8021
[7 empty] | 6228 | 10230 | 1650200 | 2019-03-22 18:14 | 2019-03-22 20:33 | 139 | 11kV | 19738 | 142 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | REC555 Arcadia - tripped & reclosed on: O/C PT746 strcuk by lightning | March | 2019 | 2019Q3 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2019-03-22 | N | 139 | N | 19 | N | N | 1.1101 | 39.4971 | 14423.9482
[7 empty] | 7041 | 18988 | 1650225 | 2019-03-22 19:23 | 2019-03-22 21:50 | 147 | 11kV | 1176 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192354 C Phase DOLF : 10 Amp Excluded OMS 1650225 | March | 2019 | 2019Q3 | 2019 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2019-03-22 | N | 147 | N | 19 | N | N | 1.1101 | 39.4971 | 859.3861
[7 empty] | 5378 | 482 | 1650230 | 2019-03-22 20:00 | 2019-03-22 22:20 | 140 | 11kV | 140 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192355 Single phase DOLF : 10 Amp Excluded OMS 1650230 | March | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-03-22 | N | 140 | N | 19 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 5441 | 1317 | 1650216 | 2019-03-22 18:29 | 2019-03-22 22:34 | 245 | 11kV | 19429 | 202 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192332 B Phase Earth Fault Excluded OMS 1650216 | March | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2019-03-22 | N | 96.1832 | N | 19 | N | N | 1.1101 | 39.4971 | 14198.1401
[7 empty] | 5460 | 1477 | 1650223 | 2019-03-22 19:13 | 2019-03-22 22:42 | 209 | 11kV | 11913 | 97 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192319 A phase Instantaneous Overcurrent also refer to LID 1923314 | March | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2019-03-22 | N | 122.8144 | N | 19 | N | N | 1.1101 | 39.4971 | 8705.669
[7 empty] | 5350 | 80 | 1650218 | 2019-03-22 18:52 | 2019-03-22 22:50 | 238 | 11kV | 238 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192356 DOLF : 10 Amp Excluded OMS 1650218 | March | 2019 | 2019Q3 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2019-03-22 | N | 238 | N | 19 | N | N | 1.1101 | 39.4971 | 173.9234
[7 empty] | 6490 | 13188 | 1650130 | 2019-03-22 12:09 | 2019-03-22 22:56 | 647 | 11kV | 91591 | 254 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192314 A & B phase Earth Fault Old steel 11kV conductor burnt down and fell to the ground adjacent to pole FR-61901. See LID 192319 Excluded OMS 1650116, 1650130, 1650131' 1650117 | March | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2019-03-22 | N | 360.5945 | N | 19 | N | N | 1.1101 | 39.4971 | 66932.0013
[7 empty] | 7081 | 19434 | 1650195 | 2019-03-22 18:03 | 2019-03-22 23:57 | 354 | 11kV | 16284 | 46 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192327 2 fault operations MAINS DOWN POLE 9L-40303 SECTION ISOLATED FOR REPAIR. | March | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2019-03-22 | N | 354 | N | 19 | N | N | 1.1101 | 39.4971 | 11899.8669
[7 empty] | 6458 | 12787 | 1650226 | 2019-03-22 19:32 | 2019-03-23 00:30 | 298 | 11kV | 1788 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192357 DOLF : 10 Amp Excluded OMS 1650226 | March | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-03-22 | N | 298 | N | 19 | N | N | 1.1101 | 39.4971 | 1306.6177
[7 empty] | 6953 | 18062 | 1650212 | 2019-03-22 18:31 | 2019-03-23 02:00 | 449 | 11kV | 12792 | 135 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 192317 2 fault operations crossarm failed pole MD-90739 | March | 2019 | 2019Q3 | 2019 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2019-03-22 | N | 94.7556 | N | 19 | N | N | 1.1101 | 39.4971 | 9348.0163
[7 empty] | 5541 | 2644 | 1650236 | 2019-03-22 22:49 | 2019-03-23 02:25 | 216 | 11kV | 5053 | 51 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192353 2 fault operation Mains down at pole AN-60522 Excluded OMS 1650236 | March | 2019 | 2019Q3 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2019-03-22 | N | 99.0784 | N | 19 | N | N | 1.1101 | 39.4971 | 3692.5834
[7 empty] | 5692 | 4582 | 1650211 | 2019-03-22 18:31 | 2019-03-23 03:50 | 559 | 11kV | 38094 | 71 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192318 2 fault operations | March | 2019 | 2019Q3 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2019-03-22 | N | 536.5352 | N | 19 | N | N | 1.1101 | 39.4971 | 27837.9716
[7 empty] | 6321 | 11124 | 1650263 | 2019-03-23 03:17 | 2019-03-23 04:15 | 58 | 11kV | 4466 | 77 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192360 DOLF : 31 Amp Possum 31.5 A phase DOLF sub supply off 0317hrs back on 0415hrs excluded OMS 1650263 | March | 2019 | 2019Q3 | 2019 | 270:83590 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Not Veg | 2019-03-23 | N | 58 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3263.6211
[7 empty] | 5627 | 3778 | 1650242 | 2019-03-22 21:34 | 2019-03-23 10:50 | 796 | 11kV | 3184 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 192361 DOLF line fuse Excluded OMS 1650242 | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-03-22 | N | 796 | N | 19 | N | N | 1.1101 | 39.4971 | 2326.7733
[7 empty] | 5669 | 4324 | 1650262 | 2019-03-23 03:05 | 2019-03-23 11:59 | 534 | 11kV | 32459 | 202 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 192364 2 fault operation Broken insulators pole AL-10166 Wire off pin AL-10029 Excluded OMS 1650262 ## | March | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-03-23 | N | 160.6881 | N | 25 | Y | Y | 1.1101 | 39.4971 | 23720.0798
[7 empty] | 6473 | 13020 | 1650304 | 2019-03-22 20:33 | 2019-03-23 12:15 | 942 | 11kV | 942 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192363 DOLF : 10 Amp Excluded OMS 1650304 | March | 2019 | 2019Q3 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2019-03-22 | N | 942 | N | 19 | N | N | 1.1101 | 39.4971 | 688.3858
[7 empty] | 5400 | 820 | 1650259 | 2019-03-22 22:43 | 2019-03-23 14:30 | 947.4833 | 11kV | 1894.9667 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192368 A Phase DOLF : 16 Amp OHM down pole FE-70080 customer was also a part of wider area outage - refer to OMS 1651698 | March | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2019-03-22 | N | 947.4833 | N | 19 | N | N | 1.1101 | 39.4971 | 1384.7857
[7 empty] | 5423 | 1122 | 1651737 | 2019-03-23 07:00 | 2019-03-23 14:45 | 465 | 11kV | 3255 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 192369 3 phase Line DOLF Dolf also replaced at sub 70526 | March | 2019 | 2019Q3 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2019-03-23 | N | 465 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2378.658
[7 empty] | 5912 | 6495 | 1650189 | 2019-03-22 17:47 | 2019-03-23 15:45 | 1318 | 11kV | 51758 | 56 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192370 3 fault operation Tree on mains adj sub 71162 *report shows no customers, bypass ABS was closed in LID. I changed it to N/O but it didn't change customer number??? Excluded OMS 1650189,1650257, 1650277 | March | 2019 | 2019Q3 | 2019 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2019-03-22 | N | 924.25 | N | 19 | N | N | 1.1101 | 39.4971 | 37823.2198
[7 empty] | 5656 | 4218 | 1650266 | 2019-03-22 19:07 | 2019-03-23 17:20 | 1333 | 11kV | 10742 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192372 2 fault operation Excluded OMS 1650266 | March | 2019 | 2019Q3 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-03-22 | N | 447.5833 | N | 19 | N | N | 1.1101 | 39.4971 | 7849.9368
[7 empty] | 6710 | 15247 | 1650228 | 2019-03-22 19:37 | 2019-03-23 17:40 | 1323 | 11kV | 105866 | 226 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192347 1 fault operation Sensitive Earth Fault Excluded OMS 1650234 | March | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2019-03-22 | N | 468.4336 | N | 19 | N | N | 1.1101 | 39.4971 | 77363.7503
[7 empty] | 5997 | 7545 | 1650289 | 2019-03-23 08:45 | 2019-03-23 18:00 | 555 | 11kV | 11255 | 89 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 192373 1 fault operation Sensitive Earth Fault lightning arrestor failed sub 42396 Excluded OMS 1650290 & 1650297 | March | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Not Veg | 2019-03-23 | N | 126.4607 | N | 25 | Y | Y | 1.1101 | 39.4971 | 8224.822
[7 empty] | 6857 | 16993 | 1650273 | 2019-03-23 07:38 | 2019-03-23 18:37 | 659 | 11kV | 659 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192376 A Phase DOLF : 5 Amp | March | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-03-23 | N | 659 | N | 25 | Y | Y | 1.1101 | 39.4971 | 481.5778
[7 empty] | 6758 | 15664 | 1650365 | 2019-03-23 21:01 | 2019-03-23 22:35 | 93.65 | 11kV | 1685.7 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192379 A & B Phase DOLF : 20 Amp and also includes LID 192380 A Phase DOLF : 10 Amp on device 70141:11kV | March | 2019 | 2019Q3 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2019-03-23 | N | 93.65 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1231.8598
[7 empty] | 6454 | 12719 | 1650362 | 2019-03-23 20:46 | 2019-03-23 22:53 | 127 | 11kV | 5919 | 60 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192381 1 fault operation Patrolled but no cause found. Excluded oms 1650362. | March | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-03-23 | N | 98.65 | N | 25 | Y | Y | 1.1101 | 39.4971 | 4325.4306
[7 empty] | 6210 | 10080 | 1650358 | 2019-03-23 19:57 | 2019-03-23 23:15 | 198 | 11kV | 396 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192382 A Phase DOLF : 10 Amp Excluded OMS 1650358 | March | 2019 | 2019Q3 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2019-03-23 | N | 198 | N | 25 | Y | Y | 1.1101 | 39.4971 | 289.3851
[7 empty] | 6889 | 17437 | 1650360 | 2019-03-23 21:14 | 2019-03-24 00:45 | 211 | 11kV | 13383 | 196 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192383 1 fault operation Earth Fault Excluded OMS 1650360 | March | 2019 | 2019Q3 | 2019 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2019-03-23 | N | 68.2806 | N | 25 | Y | Y | 1.1101 | 39.4971 | 9779.9017
[7 empty] | 5838 | 5806 | 1650416 | 2019-03-23 23:50 | 2019-03-24 01:12 | 81.9167 | 11kV | 58570.4167 | 715 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN12640 UMINA section of 11kV Panel 4 RE45090 "Pearl Beach" opened to carry out repairs at LB42533 Crossarm brace adrift within clearance of LB contacts Repairs Complete | March | 2019 | 2019Q3 | 2019 | ZN12640:PA4 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2019-03-23 | N | 81.9167 | N | 25 | Y | Y | 1.1101 | 39.4971 | 42801.533
[7 empty] | 6165 | 9572 | 1650371 | 2019-03-23 22:04 | 2019-03-24 01:24 | 200.1833 | 11kV | 4804.4 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192384 C Phase DOLF : 40 Amp Robert Mancini replaced c phase 40amp LF 400443 and c phase 10 amp dolf at sub 54739 | March | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2019-03-23 | N | 200.1833 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3510.9138
[7 empty] | 6076 | 8358 | 1650423 | 2019-03-24 01:19 | 2019-03-24 03:10 | 111 | 11kV | 1332 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192391 A & B Phase DOLF : 10 Amp replaced A& B phase dolfs at LF 3507, replaced b phase dolf sub 63419, Excluded oms 1650423 | March | 2019 | 2019Q3 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2019-03-24 | N | 111 | N | 21 | Y | Y | 1.1101 | 39.4971 | 973.3863
[7 empty] | 6593 | 14330 | 1650387 | 2019-03-23 22:22 | 2019-03-24 03:20 | 298 | 11kV | 12218 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192390 section isolated for repair of mains at tee off to sub71140 Excluded oms 1650387 | March | 2019 | 2019Q3 | 2019 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2019-03-23 | N | 298 | N | 25 | Y | Y | 1.1101 | 39.4971 | 8928.554
[7 empty] | 7176 | 20388 | 1650370 | 2019-03-23 21:45 | 2019-03-24 04:41 | 416 | 11kV | 39520 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192472 Trip & Reclose 1 fault operation LID 192396 A & B phase SUB 1569 ISOLATED FOR REPAIR. | March | 2019 | 2019Q3 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-03-23 | N | 416 | N | 25 | Y | Y | 1.1101 | 39.4971 | 28880.0504
[7 empty] | 6083 | 8452 | 1651079 | 2019-03-23 21:45 | 2019-03-24 05:30 | 465 | 11kV | 2325 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192398 A & B Phase DOLF : 16 Amp See report 192396/OMS 1651077 | March | 2019 | 2019Q3 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-03-23 | N | 465 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1699.0414
[7 empty] | 7111 | 19646 | 1650449 | 2019-03-24 05:32 | 2019-03-24 06:52 | 80 | 11kV | 127224 | 1601 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.4 tripped on SEF Bond burnt off load side of AB31006 See 1650998 1650999 | March | 2019 | 2019Q3 | 2019 | ZN10999:PA4 | ZN10999:PA4 | ZN10999/000004 | GEORGES RIVER | OH | Not Veg | 2019-03-24 | N | 79.4653 | N | 21 | Y | Y | 1.1101 | 39.4971 | 92971.5467
[7 empty] | 5863 | 6019 | 1650394 | 2019-03-23 22:38 | 2019-03-24 08:15 | 577 | 11kV | 2308 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192402 A Phase DOLF : 10 Amp | March | 2019 | 2019Q3 | 2019 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2019-03-23 | N | 577 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1686.6183
[7 empty] | 7137 | 19847 | 1650454 | 2019-03-24 06:32 | 2019-03-24 09:00 | 148 | 11kV | 2072 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 192403 C Phase DOLF : 10 Amp Excluded OMS 1650454 | March | 2019 | 2019Q3 | 2019 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2019-03-24 | N | 148 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1514.1565
[7 empty] | 6058 | 8218 | 1650392 | 2019-03-23 22:35 | 2019-03-24 09:03 | 628 | 11kV | 1884 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192404 DOLF : 10 Amp Excluded OMS 1650392 | March | 2019 | 2019Q3 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2019-03-23 | N | 628 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1376.7716
[7 empty] | 5559 | 2991 | 1650415 | 2019-03-23 23:41 | 2019-03-24 10:10 | 629 | 11kV | 4403 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192407 B & C Phase DOLF : 20 Amp Excluded OMS 1650415 | March | 2019 | 2019Q3 | 2019 | 239:82127 | 239:82127 | ZN00239/082127 | LAKE MACQUARIE | OH | Veg | 2019-03-23 | N | 629 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3217.5825
[7 empty] | 5730 | 5071 | 1650389 | 2019-03-23 22:28 | 2019-03-24 10:45 | 737 | 11kV | 92599 | 608 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex ZN14143 SOMERSBY section of 11kV Panel 17 IR50001 Pacific Morgans 0.46 tripped on Fault Flags: OC Trip, Lockout OH cables twisted together adjacent Pole BR112. mains seperated, however cables damaged/stranded- repairs required See 1650721,2,6,7,8,30,2 Ex 1650389,447 | March | 2019 | 2019Q3 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2019-03-23 | N | 152.301 | N | 25 | Y | Y | 1.1101 | 39.4971 | 67668.618
[7 empty] | 5593 | 3518 | 1650472 | 2019-03-24 07:51 | 2019-03-24 10:50 | 179 | 11kV | 358 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192408 A Phase DOLF : 10 Amp Excluded OMS 1650472 | March | 2019 | 2019Q3 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2019-03-24 | N | 179 | N | 21 | Y | Y | 1.1101 | 39.4971 | 261.6158
[7 empty] | 5655 | 4172 | 1650383 | 2019-03-23 22:19 | 2019-03-24 11:00 | 761 | 11kV | 32590 | 50 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192409 Line DOLF cut away suss L/A at sub 78756 and replace 31A Dolf Excluded oms 1650383 | March | 2019 | 2019Q3 | 2019 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2019-03-23 | N | 651.8 | N | 25 | Y | Y | 1.1101 | 39.4971 | 23815.8108
[7 empty] | 5895 | 6361 | 1650375 | 2019-03-23 22:03 | 2019-03-24 11:30 | 807 | 11kV | 191605 | 764 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192385 2 fault operations 11kV OHM down at IU-27073 HV into LV despatch advised | March | 2019 | 2019Q3 | 2019 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2019-03-23 | N | 250.7919 | N | 25 | Y | Y | 1.1101 | 39.4971 | 140019.2826
[7 empty] | 5779 | 5402 | 1650382 | 2019-03-23 22:15 | 2019-03-24 11:50 | 815 | 11kV | 94014 | 147 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 192410 Earth fault Broken insulator HS-80007 Excluded OMS 1650382 | March | 2019 | 2019Q3 | 2019 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2019-03-23 | N | 639.551 | N | 25 | Y | Y | 1.1101 | 39.4971 | 68702.6583
[7 empty] | 5706 | 4726 | 1650487 | 2019-03-24 08:59 | 2019-03-24 12:15 | 196 | 11kV | 392 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192414 3 Phase DOLF's : 10 Amp Excluded OMS 1650487 | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-03-24 | N | 196 | N | 21 | Y | Y | 1.1101 | 39.4971 | 286.462
[7 empty] | 6789 | 16188 | 1650402 | 2019-03-23 22:54 | 2019-03-24 12:25 | 811.35 | 11kV | 6490.8 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192412 A Phase DOLF : 40 Amp | March | 2019 | 2019Q3 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2019-03-23 | N | 811.35 | N | 25 | Y | Y | 1.1101 | 39.4971 | 4743.2852
[7 empty] | 6836 | 16785 | 1650520 | 2019-03-24 11:04 | 2019-03-24 12:30 | 86 | 11kV | 1118 | 13 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | Ex ZN14144 WAMBERAL section of 11kV Panel 5 PT14281 HASTINGS SERPENTINE 16Amp middle phase HDO fuse blew Customer private pole fell down | March | 2019 | 2019Q3 | 2019 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | Unknown | Not Veg | 2019-03-24 | N | 86 | N | 21 | Y | Y | 1.1101 | 39.4971 | 817.0014
[7 empty] | 7116 | 19683 | 1650436 | 2019-03-24 02:48 | 2019-03-24 12:48 | 600 | 11kV | 1200 | 2 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | No Control Room report raised, refer to related record | March | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2019-03-24 | N | 600 | N | 21 | Y | Y | 1.1101 | 39.4971 | 876.9246
[7 empty] | 6079 | 8364 | 1650479 | 2019-03-24 08:23 | 2019-03-24 13:00 | 277 | 11kV | 277 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192424 DOLF : 10 Amp Excluded OMS 1650479 | March | 2019 | 2019Q3 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2019-03-24 | N | 277 | N | 21 | Y | Y | 1.1101 | 39.4971 | 202.4234
[7 empty] | 5572 | 3236 | 1650414 | 2019-03-23 23:38 | 2019-03-24 13:20 | 822 | 11kV | 3288 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 192417 A Phase DOLF : 20 Amp Note: start time amended to reflect first no supply call made - refer to related record | March | 2019 | 2019Q3 | 2019 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2019-03-23 | N | 822 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2402.7734
[7 empty] | 5445 | 1344 | 1650499 | 2019-03-24 09:36 | 2019-03-24 13:20 | 224 | 11kV | 448 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192416 DOLF : 10 Amp Excluded OMS 1650499 | March | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-03-24 | N | 224 | N | 21 | Y | Y | 1.1101 | 39.4971 | 327.3852
[7 empty] | 6140 | 9312 | 1650401 | 2019-03-23 22:50 | 2019-03-24 14:00 | 910 | 11kV | 910 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192423 DOLF : 10 Amp Excluded OMS 1650512 | March | 2019 | 2019Q3 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2019-03-23 | N | 910 | N | 25 | Y | Y | 1.1101 | 39.4971 | 665.0012
[7 empty] | 5916 | 6535 | 1650496 | 2019-03-24 09:31 | 2019-03-24 15:43 | 372 | 11kV | 372 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192425 DOLF : 10 Amp Excluded OMS 1650496 | March | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-03-24 | N | 372 | N | 21 | Y | Y | 1.1101 | 39.4971 | 271.8466
[7 empty] | 6223 | 10202 | 1650369 | 2019-03-23 21:10 | 2019-03-24 15:45 | 1115 | 11kV | 56740 | 140 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 192393 3 phase tree on mains pole AS-30078 section isolated for repairs in daylight power restored 0345. also includes LID 192458 Trip & Reclose 1 fault operation @ 23/03/19 21:10 on device HC 2389 and LID 192505 Trip & Reclose 1 fault operation @ 23/03/19 22:27 on device HC 2389 and | March | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-03-23 | N | 405.2857 | N | 25 | Y | Y | 1.1101 | 39.4971 | 41463.9185
[7 empty] | 6554 | 13848 | 1650480 | 2019-03-24 08:31 | 2019-03-24 16:05 | 454 | 11kV | 908 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192426 DOLF : 10 Amp Excluded OMS 1650480 | March | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Veg | 2019-03-24 | N | 454 | N | 21 | Y | Y | 1.1101 | 39.4971 | 663.5396
[7 empty] | 6587 | 14293 | 1650576 | 2019-03-24 16:42 | 2019-03-24 17:26 | 44 | 11kV | 6072 | 138 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 192430 repair stranded mains pole TC 50038 | March | 2019 | 2019Q3 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-03-24 | N | 44 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4437.2385
[7 empty] | 6764 | 15749 | 1650478 | 2019-03-24 08:20 | 2019-03-24 17:45 | 565 | 11kV | 1695 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 192431 DOLF : 20 Amp Excluded OMS 1650478, 1650542 | March | 2019 | 2019Q3 | 2019 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Veg | 2019-03-24 | N | 565 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1238.656
[7 empty] | 6074 | 8341 | 1650398 | 2019-03-24 15:00 | 2019-03-24 19:07 | 247 | 11kV | 247 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 192459 Single phase Tx Replaced Excluded OMS 1650398 | March | 2019 | 2019Q3 | 2019 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2019-03-24 | N | 247 | N | 21 | Y | Y | 1.1101 | 39.4971 | 180.5003
[7 empty] | 5487 | 1813 | 1650610 | 2019-03-24 07:57 | 2019-03-24 19:25 | 688.4 | 11kV | 14456.4 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192449 Single phase DOLF : 10 Amp | March | 2019 | 2019Q3 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-03-24 | N | 688.4 | N | 21 | Y | Y | 1.1101 | 39.4971 | 10564.3107
[7 empty] | 5811 | 5624 | 1650587 | 2019-03-24 18:02 | 2019-03-24 19:33 | 91 | 11kV | 1638 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192432 DOLF : 20 Amp | March | 2019 | 2019Q3 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2019-03-24 | N | 91 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1197.0021
[7 empty] | 6645 | 14788 | 1650598 | 2019-03-24 19:02 | 2019-03-24 22:02 | 180 | 11kV | 58977 | 379 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192455 2 fault operations Earth fault replaced DOLF ar sub 50035 also note there was a T&R at HC47754 at 24/03/19 19:08 whilst customers were still off see LID192519 Trip & reclose 1 fault operation Earth Fault Overcurrent | March | 2019 | 2019Q3 | 2019 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2019-03-24 | N | 155.6121 | N | 21 | Y | Y | 1.1101 | 39.4971 | 43098.6521
[7 empty] | 6026 | 7882 | 1650622 | 2019-03-24 20:34 | 2019-03-24 22:45 | 131 | 11kV | 131 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192448 Single phase DOLF : 10 Amp Excluded OMS 1650622 | March | 2019 | 2019Q3 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2019-03-24 | N | 131 | N | 21 | Y | Y | 1.1101 | 39.4971 | 95.7309
[7 empty] | 6601 | 14368 | 1650615 | 2019-03-24 19:53 | 2019-03-25 00:14 | 261 | 11kV | 225051 | 1890 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192436 2 fault operations excluded OMS 1650615 | March | 2019 | 2019Q3 | 2019 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2019-03-24 | N | 119.0746 | N | 21 | Y | Y | 1.1101 | 39.4971 | 164460.6329
[7 empty] | 5995 | 7529 | 1651160 | 2019-03-25 00:05 | 2019-03-25 00:45 | 40 | 11kV | 480 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192438 C Phase DOLF : 16 Amp | March | 2019 | 2019Q3 | 2019 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2019-03-25 | N | 40 | N | 12 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 5565 | 3127 | 1650639 | 2019-03-25 03:50 | 2019-03-25 05:15 | 85 | 11kV | 80260 | 1000 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.41 tripped on: A & B phase O/C Abnormal: LB62449 Closed with LB1562 open UG cable fault between S35110 Sw/B to S8530 Sw/A to S8790 Sw/B See 1651043 1651044 | March | 2019 | 2019Q3 | 2019 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | UG | Not Veg | 2019-03-25 | N | 80.26 | N | 12 | N | N | 1.1101 | 39.4971 | 58651.6407
[7 empty] | 5740 | 5115 | 1650608 | 2019-03-24 19:31 | 2019-03-25 06:00 | 629 | 11kV | 11322 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 192443 3 phase DOLF : 10 Amp Excluded OMS 1650635 Note: start time amended to reflect first no supply call received refer to related records | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-03-24 | N | 629 | N | 21 | Y | Y | 1.1101 | 39.4971 | 8273.7837
[7 empty] | 5659 | 4264 | 1650687 | 2019-03-25 08:54 | 2019-03-25 11:20 | 146 | 11kV | 146 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192523 Single phase DOLF : 10 Amp Excluded OMS 1650687 | March | 2019 | 2019Q3 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2019-03-25 | N | 146 | N | 12 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 6010 | 7737 | 1650683 | 2019-03-25 08:45 | 2019-03-25 12:45 | 240 | 11kV | 240 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 192524 3 phase DOLF : 10 Amp L/A's blown Excluded OMS 1650683 | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-03-25 | N | 240 | N | 12 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 6538 | 13721 | 1650678 | 2019-03-25 09:35 | 2019-03-25 13:45 | 250 | 11kV | 1795 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 8 Tree on CCT near AB43855 isolated by DOp for safety Cause: tree branch contact - other See 1651066 edx 1650678,719,34 | March | 2019 | 2019Q3 | 2019 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2019-03-25 | N | 179.5 | N | 12 | N | N | 1.1101 | 39.4971 | 1311.7331
[7 empty] | 6245 | 10388 | 1650766 | 2019-03-25 12:02 | 2019-03-25 14:35 | 153 | 11kV | 306 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192529 A Phase DOLF : 16 Amp Tx volts: Aph -237V, Bph - 245V, Cph - 246V Excluded OMS No. 1650766 | March | 2019 | 2019Q3 | 2019 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2019-03-25 | N | 153 | N | 12 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 6906 | 17648 | 1650794 | 2019-03-25 13:32 | 2019-03-25 15:40 | 128 | 11kV | 128 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192533 Single phase DOLF : 10 Amp Excluded OMS 1650794 | March | 2019 | 2019Q3 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2019-03-25 | N | 128 | N | 12 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 6693 | 15156 | 1650737 | 2019-03-25 10:47 | 2019-03-25 16:30 | 343 | 11kV | 686 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192534 Single phase DOLF : 10 Amp Excluded OMS 1650737 | March | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-03-25 | N | 343 | N | 12 | N | N | 1.1101 | 39.4971 | 501.3086
[7 empty] | 6025 | 7873 | 1650928 | 2019-03-25 17:11 | 2019-03-25 17:15 | 4 | 11kV | 1352 | 338 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 192538 2 fault operations Replace Faulty 11kV link. Small grass fire adjacent to pole at 11kV link 4913. Excluded OMS 1650946 | March | 2019 | 2019Q3 | 2019 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2019-03-25 | N | 4 | N | 12 | N | N | 1.1101 | 39.4971 | 988.0017
[7 empty] | 6840 | 16804 | 1650973 | 2019-03-25 23:18 | 2019-03-26 00:45 | 87 | 11kV | 26268 | 326 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.15 tripped on: B phase O/C & E/F Note: Due to no EFI @ S338 Opened Pnl.15 @ 0023 to allow closing S5862 to prove fault location remotely. UG cable fault from S338 Sw/B to S64149 Sw/B See 1651019 1651021 1651023 | March | 2019 | 2019Q3 | 2019 | ZN188:PA15 | ZN188:PA15 | ZN00188/000015 | SYDNEY | UG | Not Veg | 2019-03-25 | N | 80.5767 | N | 12 | N | N | 1.1101 | 39.4971 | 19195.8796
[7 empty] | 5909 | 6455 | 1650905 | 2019-03-25 16:38 | 2019-03-26 02:10 | 572 | 11kV | 572 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 192541 Blown Tx. Mansini operator. Tx replaced. Excluded OMS 1650905 | March | 2019 | 2019Q3 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Not Veg | 2019-03-25 | N | 572 | N | 12 | N | N | 1.1101 | 39.4971 | 418.0007
[7 empty] | 7115 | 19680 | 1650934 | 2019-03-25 17:44 | 2019-03-26 02:20 | 516 | 11kV | 1548 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 192542 Single phase DOLF : 10 Amp CUT AWAY ARRESTORS ON TX 64939 excluded OMS 1650934 | March | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-03-25 | N | 516 | N | 12 | N | N | 1.1101 | 39.4971 | 1131.2327
[7 empty] | 6902 | 17598 | 1650979 | 2019-03-26 02:15 | 2019-03-26 04:42 | 147 | 11kV | 10735 | 103 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192543 3 fault operations A & B phase Overcurrent Excluded OMS 1650979 | March | 2019 | 2019Q3 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2019-03-26 | N | 104.2233 | N | 14 | N | N | 1.1101 | 39.4971 | 7844.8214
[7 empty] | 6398 | 12002 | 1651000 | 2019-03-26 08:05 | 2019-03-26 09:09 | 64 | 11kV | 64 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 192544 A & B Phase DOLF : 10 Amp Excluded OMS 1651000 | March | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-03-26 | N | 64 | N | 14 | N | N | 1.1101 | 39.4971 | 46.7693
[7 empty] | 6775 | 15871 | 1651048 | 2019-03-26 09:19 | 2019-03-26 11:00 | 101 | 11kV | 606 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192554 A Phase DOLF : 16 Amp Excluded OMS 1651048 | March | 2019 | 2019Q3 | 2019 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2019-03-26 | N | 101 | N | 14 | N | N | 1.1101 | 39.4971 | 442.8469
[7 empty] | 7083 | 19450 | 1651062 | 2019-03-26 09:42 | 2019-03-26 11:46 | 124 | 11kV | 51741 | 418 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN8000 Macquarie Park Panel 10 Relays: 10L E/F, fault check and EFI Signals: 11kv trip Remarks: UG fault. 11kv feeder fault from ZN8000 Macquarie Park panel 10 and 29 to S4874 to S63031 to S8157 to S64449 to S64706 | March | 2019 | 2019Q3 | 2019 | ZN8000:PA10 | ZN8000:PA10 | ZN08000/000010 | RYDE | UG | Not Veg | 2019-03-26 | N | 123.7823 | N | 14 | N | N | 1.1101 | 39.4971 | 37810.7967
[7 empty] | 6175 | 9763 | 1651080 | 2019-03-26 10:06 | 2019-03-26 11:48 | 102 | 11kV | 102 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192553 A Phase DOLF : 10 Amp Excluded OMS 1651080 | March | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2019-03-26 | N | 102 | N | 14 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 5481 | 1679 | 1650987 | 2019-03-26 07:21 | 2019-03-26 13:45 | 384 | 11kV | 384 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192558 C Phase DOLF : 10 Amp Excluded OMS 1650987 | March | 2019 | 2019Q3 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2019-03-26 | N | 384 | N | 14 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 5449 | 1373 | 1651045 | 2019-03-26 09:28 | 2019-03-26 15:00 | 332 | 11kV | 664 | 2 | HV | Animal Other | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | S16127 Ingleside 30 - 11kV 50A - A Phase SIBA fuse blown Rat found on ground near exposed 11kV at sub | March | 2019 | 2019Q3 | 2019 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-03-26 | N | 332 | N | 14 | N | N | 1.1101 | 39.4971 | 485.2316
[7 empty] | 5704 | 4708 | 1651218 | 2019-03-26 14:17 | 2019-03-26 15:20 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192560 Single phase DOLF : 10 Amp Excluded OMS 1651218 | March | 2019 | 2019Q3 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2019-03-26 | N | 63 | N | 14 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 6944 | 17956 | 1651229 | 2019-03-26 14:36 | 2019-03-26 16:15 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192561 Single phase DOLF : 10 Amp Excluded OMS 1651283 | March | 2019 | 2019Q3 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2019-03-26 | N | 99 | N | 14 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 6329 | 11228 | 1652113 | 2019-03-26 18:04 | 2019-03-26 18:09 | 5 | 11kV | 160 | 32 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192568 1 fault operation Sensitive Earth Fault on a try back of sub 51299 Sw 42033 tripped on SEF covered by this report. | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-03-26 | N | 5 | N | 14 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 6028 | 7904 | 1651319 | 2019-03-26 17:13 | 2019-03-26 18:10 | 57 | 11kV | 133905 | 2419 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN262 Marrickville 11kv Panel 15 labelled "S3058 Hrrison Enfield & S7592 Marrickville" tripped: Relays: B phase OC, EFI, Fault check Signals: CB15 open, Zone earth, 11kv trip, Tx3 Group earth, Tx4 group earth Abnormal: 415lv board @ S1457 Davis st is isolated & in LV// Remarks: UG fault. 11kv section of feeder from Sw/B @ S2712 Darley Marrick to Sw/A @ S8163 St Marouns School | March | 2019 | 2019Q3 | 2019 | ZN262:PA15 | ZN262:PA15 | ZN00262/000015 | INNER WEST | UG | Not Veg | 2019-03-26 | N | 55.3555 | N | 14 | N | N | 1.1101 | 39.4971 | 97853.8245
[7 empty] | 5936 | 6817 | 1650991 | 2019-03-26 07:43 | 2019-03-26 21:00 | 797 | 11kV | 28412 | 76 | HV | Staff Other | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | AT S5868 Gore Hill 11kv Panel 17 "Reserve Campbell" tripped on Relays: EF, fault check, trip & EFI Signals: 11kv, Zone and Tx3 Group earths Abnormal: Sw/A closed @ S2627, DMA 11kv feeder Sw/A open @ S8483 to Sw/B open @ S7770. See separate DMA Remark: Section of feeder already OOS and defective from S7770 to S8483. Jointers at the time ID'ed feeder but cut the in service feeder from S3266 to S7770 | March | 2019 | 2019Q3 | 2019 | ZN5868:PA17 | ZN5868:PA17 | ZN05868/000017 | WILLOUGHBY | Unknown | Not Veg | 2019-03-26 | N | 373.8421 | N | 14 | N | N | 1.1101 | 39.4971 | 20762.6516
[7 empty] | 7144 | 19924 | 1651283 | 2019-03-26 16:15 | 2019-03-26 22:40 | 385 | 11kV | 770 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 192565 B Phase DOLF : 10 Amp Tx and arrestors replacced, SAO required. Excluded OMS 1651283 | March | 2019 | 2019Q3 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-03-26 | N | 385 | N | 14 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 6021 | 7844 | 1651354 | 2019-03-27 03:39 | 2019-03-27 04:38 | 58.8667 | 11kV | 101839.3333 | 1730 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN12600 LISAROW 11kV CB Panel 3 'S18221' fdr tripped and reclosed on and locked out Relays: A phase inst and timed, E?F, EFI EFI: S12399 S14623 S14247 Singals: 11kv trip Cause: animals/birds Possum at Base of UGOH pole adj to S14247 pole GO9796 S18173 EFI faulty with no indication | March | 2019 | 2019Q3 | 2019 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2019-03-27 | N | 58.8667 | N | 6 | N | N | 1.1101 | 39.4971 | 74421.181
[7 empty] | 6711 | 15250 | 1651350 | 2019-03-26 23:54 | 2019-03-27 06:45 | 411 | 11kV | 33631 | 831 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex ZN12620 NORAVILLE section of 11kV Panel 11 RE45054 Noraville REC tripped and reclosed on IOC, EF PT13738 Ocean Kerry Louise footpath HDO operated 31.5amp type LAS Cause: animals/birds Possum caused flashover at PT13738, suspected defective 11kv/415v transformer, failed attempts to restore HDO, PT restored via LV// (event ID: 1555) See 1651705,6 ex 1651350,7 | March | 2019 | 2019Q3 | 2019 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2019-03-26 | N | 40.4705 | N | 14 | N | N | 1.1101 | 39.4971 | 24576.5429
[7 empty] | 6560 | 13889 | 1651403 | 2019-03-27 09:41 | 2019-03-27 11:15 | 94 | 11kV | 94 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192576 Single phase DOLF : 10 Amp Excluded OMS 1651403 | March | 2019 | 2019Q3 | 2019 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2019-03-27 | N | 94 | N | 6 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 5440 | 1291 | 1651455 | 2019-03-27 11:47 | 2019-03-27 14:40 | 173 | 11kV | 346 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 192583 DOLF : 10 Amp Excluded OMS 1651455 | March | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-03-27 | N | 173 | N | 6 | N | N | 1.1101 | 39.4971 | 252.8466
[7 empty] | 5529 | 2463 | 1651518 | 2019-03-27 15:30 | 2019-03-27 16:55 | 85 | 11kV | 340 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC26228 Valley Rd tripped, relcosed and locked out on: OC Tree branch on mains in section after LK22297 | March | 2019 | 2019Q3 | 2019 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2019-03-27 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 6126 | 9184 | 1651548 | 2019-03-27 16:28 | 2019-03-27 17:42 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192590 C Phase DOLF : 10 Amp Excluded OMS 1651548 | March | 2019 | 2019Q3 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2019-03-27 | N | 74 | N | 6 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 5480 | 1674 | 1651611 | 2019-03-27 22:27 | 2019-03-27 23:36 | 69 | 11kV | 104742 | 1518 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn1193 Lindfield - Pnl.26 tripped on: B & C phase IOC tree branch on OH mains outside 52 Finlay St. | March | 2019 | 2019Q3 | 2019 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2019-03-27 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 76542.3642
[7 empty] | 6703 | 15205 | 1651626 | 2019-03-28 04:40 | 2019-03-28 08:00 | 200 | 11kV | 12887 | 76 | HV | 3rd Party Action | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn35370 Galston - Pnl.8 - AB275 opened by unknown person (lock cut) Police and security notified See 1651967 1651968 1651969 | March | 2019 | 2019Q3 | 2019 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2019-03-28 | N | 169.5658 | N | 4 | N | N | 1.1101 | 39.4971 | 9417.4395
[7 empty] | 6419 | 12293 | 1651846 | 2019-03-28 07:30 | 2019-03-28 18:35 | 665 | 11kV | 3325 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192614 DOLF : 10 Amp Excluded OMS 1651846 | March | 2019 | 2019Q3 | 2019 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2019-03-28 | N | 665 | N | 4 | N | N | 1.1101 | 39.4971 | 2429.8119
[7 empty] | 5994 | 7479 | 1651853 | 2019-03-28 15:42 | 2019-03-28 19:15 | 213 | 11kV | 426 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192615 A Phase DOLF : 10 Amp Excluded OMS 1651853 | March | 2019 | 2019Q3 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-03-28 | N | 213 | N | 4 | N | N | 1.1101 | 39.4971 | 311.3082
[7 empty] | 6819 | 16584 | 1651916 | 2019-03-28 21:56 | 2019-03-28 22:20 | 24 | 11kV | 48 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192617 A Phase DOLF : 6 Amp Excluded OMS 1651916 | March | 2019 | 2019Q3 | 2019 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-03-28 | N | 24 | N | 4 | N | N | 1.1101 | 39.4971 | 35.077
[7 empty] | 5490 | 1845 | 1651964 | 2019-03-29 07:56 | 2019-03-29 09:00 | 64 | 11kV | 384 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192618 C Phase DOLF : 10 Amp | March | 2019 | 2019Q3 | 2019 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2019-03-29 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 7046 | 19058 | 1651923 | 2019-03-29 00:12 | 2019-03-29 12:44 | 752 | 11kV | 6441 | 18 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S1535 Moore Baker - B & C phase HV fuses blown Customer supplied from Dist #1 switchboard failed. Grading problem with LV & HV fuses See 1652919 1652920 | March | 2019 | 2019Q3 | 2019 | ZN3672:PA42 | ZN3672:PA42 | ZN03672/000042 | BAYSIDE | Unknown | Not Veg | 2019-03-29 | N | 357.8333 | N | 3 | N | N | 1.1101 | 39.4971 | 4706.8928
[7 empty] | 5463 | 1535 | 1652100 | 2019-03-29 15:10 | 2019-03-29 15:57 | 47.3667 | 11kV | 4263 | 90 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | LID 192627 A Phase DOLF : 31 Amp CC1: 22-"Refer to SOp" | March | 2019 | 2019Q3 | 2019 | 256:80644 | 256:80644 | ZN00256/080644 | NEWCASTLE | OH | Not Veg | 2019-03-29 | N | 47.3667 | N | 3 | N | N | 1.1101 | 39.4971 | 3115.2747
[7 empty] | 5758 | 5232 | 1652208 | 2019-03-30 03:17 | 2019-03-30 04:35 | 78 | 11kV | 59380 | 771 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At ZN9550 Gwawley Bay 11kv feeder Panel No.36 "LB47770 etc" feeder tripped and locked out on Relays: ABC O/C (150 TABAC), E/F (150TN) Signals: No.3 grp earth, znone earth Field efis: nil Remarks: storm, feeder patrolled no cause found, supply restored | March | 2019 | 2019Q3 | 2019 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Veg | 2019-03-30 | N | 77.0169 | N | 17 | N | N | 1.1101 | 39.4971 | 43393.1526
[7 empty] | 5645 | 4067 | 1652211 | 2019-03-30 03:58 | 2019-03-30 08:20 | 262 | 11kV | 362566 | 2273 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Rain Heavy | N | At ZN9700 Kirrawee 11kv feeder Panel No17 "Hotham Badto" feeder tripped and locked out on: Relays: B phase O/C, timing, lockout, EFI, fault check Signals: 11kv trip, Zn earth, No3 grp earth Remarks: storm, 11kv UGOH between LB35658 and S9173 Cormorant Swallow Sw/A is damaged after lightning strike | March | 2019 | 2019Q3 | 2019 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2019-03-30 | N | 159.5099 | N | 17 | N | N | 1.1101 | 39.4971 | 264952.5389
[7 empty] | 5735 | 5088 | 1652222 | 2019-03-30 07:32 | 2019-03-30 09:12 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 192635 A & B phase DOLF : 16 Amp Excluded OMS 1652227 | March | 2019 | 2019Q3 | 2019 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2019-03-30 | N | 100 | N | 17 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 5517 | 2265 | 1652223 | 2019-03-30 12:15 | 2019-03-30 16:35 | 260 | 11kV | 15600 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | PT2046 Curtin Page - isolated from S4465 to S7920 11kV isolated for safe removal of tree branch. LV cross arm rebuild required. | March | 2019 | 2019Q3 | 2019 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2019-03-30 | N | 260 | N | 17 | N | N | 1.1101 | 39.4971 | 11400.0199
[7 empty] | 7026 | 18781 | 1652448 | 2019-03-30 17:16 | 2019-03-30 18:25 | 69 | 11kV | 138 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 192640 B & C Phase DOLF : 10 Amp Excluded OMS 1652448 | March | 2019 | 2019Q3 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2019-03-30 | N | 69 | N | 17 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 6531 | 13670 | 1652362 | 2019-03-30 16:11 | 2019-03-30 18:50 | 159 | 11kV | 138214 | 874 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn15013 Terry Hills Pnl.4 tripped & reclosed on: C phase OC Tree branch found on 11kV outside 101 Booralie St. See 1652965 1652967 | March | 2019 | 2019Q3 | 2019 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2019-03-30 | N | 158.1396 | N | 17 | N | N | 1.1101 | 39.4971 | 101002.7146
[7 empty] | 6705 | 15214 | 1650426 | 2019-03-24 01:27 | 2019-03-30 19:30 | 9723 | 11kV | 218708 | 281 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 192535 Faulty Tx 303 Thompson No3. sub. Excluded OMS 1650426 & 1650453 | March | 2019 | 2019Q3 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-03-24 | N | 778.3203 | N | 21 | Y | Y | 1.1101 | 39.4971 | 159825.3556
[7 empty] | 6423 | 12307 | 1652348 | 2019-03-30 15:57 | 2019-03-30 19:30 | 213 | 11kV | 27894 | 142 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC555 Arcadia Park tripped on: IOC & OC trip Tree leaning against 11kV mains outside 32 Bay Rd. See 1652947 1652948 1652949 | March | 2019 | 2019Q3 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2019-03-30 | N | 196.4366 | N | 17 | N | N | 1.1101 | 39.4971 | 20384.1125
[7 empty] | 6799 | 16374 | 1652237 | 2019-03-30 16:20 | 2019-03-30 19:35 | 195 | 11kV | 4485 | 23 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 192637 B Phase No protection operated, open circuit fault. in Bundled ABC cable near pole JR-72407. HV supplyinnfg adjacent subs had to be interrupted to allow LV mains to be tensioned. Excluded OMS 1652237 | March | 2019 | 2019Q3 | 2019 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2019-03-30 | N | 195 | N | 17 | N | N | 1.1101 | 39.4971 | 3277.5057
[7 empty] | 6254 | 10467 | 1652506 | 2019-03-30 18:19 | 2019-03-30 20:10 | 111 | 11kV | 666 | 6 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 192643 C Phase DOLF : 10 Amp Tree branch on OHM. Excluded OMS 1652506 | March | 2019 | 2019Q3 | 2019 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2019-03-30 | N | 111 | N | 17 | N | N | 1.1101 | 39.4971 | 486.6932
[7 empty] | 5852 | 5923 | 1652488 | 2019-03-30 19:00 | 2019-03-30 22:25 | 205 | 11kV | 5330 | 26 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 192639 Fdr isolated to repair broken crossarm at pole SF-60613. Excluded OMS No. 1652488, 1652574 | March | 2019 | 2019Q3 | 2019 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-03-30 | N | 205 | N | 17 | N | N | 1.1101 | 39.4971 | 3895.0068
[7 empty] | 5367 | 414 | 1652509 | 2019-03-30 18:41 | 2019-03-31 01:35 | 414 | 11kV | 13605 | 95 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Wind Strong | N | LID 192645 1 fault operation 2 span CCT on ground to sub 43701. Excluded OMS No. 1652527, 1652509, 1652533 | March | 2019 | 2019Q3 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2019-03-30 | N | 143.2105 | N | 17 | N | N | 1.1101 | 39.4971 | 9942.1327
[7 empty] | 7079 | 19431 | 1652451 | 2019-03-30 13:30 | 2019-03-31 01:36 | 726 | 11kV | 12450 | 19 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 192644 3 fault operations A & B Phase Overcurrent Wire off pin burnt pole 3H-50049. Excluded OMS No. 1652421 | March | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-03-30 | N | 655.2632 | N | 17 | N | N | 1.1101 | 39.4971 | 9098.0928
[7 empty] | 6509 | 13405 | 1652590 | 2019-03-30 20:45 | 2019-03-31 10:02 | 797 | 11kV | 3985 | 5 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 192650 Single phase DOLF : 10 Amp Excluded OMS 1652656 Nlote: start time amended to reflect first NO Supply call received refer to related records | March | 2019 | 2019Q3 | 2019 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2019-03-30 | N | 797 | N | 17 | N | N | 1.1101 | 39.4971 | 2912.1205
[7 empty] | 5672 | 4337 | 1652543 | 2019-03-30 19:04 | 2019-03-31 10:45 | 941 | 11kV | 269355 | 1021 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN965 Pennant Hills the 11kv Panel 43 CB tripped and locked out on: Signals: 11kv trip Relays: overcurrent A & C phase Remarks: tree/branch brought down OH. See seperate DMA on section of panel 33. Sw/tag at LB2671. PT1649 restored via LV// usl's 6268, 6112, 6374 | March | 2019 | 2019Q3 | 2019 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Veg | 2019-03-30 | N | 263.8149 | N | 17 | N | N | 1.1101 | 39.4971 | 196836.6894
[7 empty] | 5660 | 4268 | 1652453 | 2019-03-30 17:19 | 2019-03-31 12:20 | 1141 | 11kV | 164316 | 1714 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12650 West Gosford - Pnl.1 tripped on: B & C phase O/C Abnormal: REC44936 bypassed. REC44937 Bypassed Weather related - 2 faults. 11kV down adj REC44937 + Tree branch on OH mains adj AB44378 See 1652993 1652994 1652995 1652996 | March | 2019 | 2019Q3 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2019-03-30 | N | 95.867 | N | 17 | N | N | 1.1101 | 39.4971 | 120077.2863
[7 empty] | 6850 | 16885 | 1652586 | 2019-03-30 20:39 | 2019-03-31 12:50 | 971 | 11kV | 20441 | 1299 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN965 Pennant Hills the 11kv Panel 33 tripped and locked out on: Signals: 11kv trip Relays: A & C phase OC, lockout, timing and EFI Remarks: OH cables twisted together. Dop Drewett went to open LB378 but inadvertently closed it. This closed onto a fault on Panel 43. This caused the 11kv mains to twist together. When the feeder was tried back. This caused a bond to burn off and 11kv to come down nr PT356 MWS&DB West Thornleigh | March | 2019 | 2019Q3 | 2019 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2019-03-30 | N | 15.736 | N | 17 | N | N | 1.1101 | 39.4971 | 14937.6799
[7 empty] | 5379 | 512 | 1652725 | 2019-03-31 13:12 | 2019-03-31 14:35 | 83 | 11kV | 83 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192652 DOLF : 10 Amp Excluded OMS 1652725 | March | 2019 | 2019Q3 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-03-31 | N | 83 | N | 2 | N | N | 1.1101 | 39.4971 | 60.654
[7 empty] | 7151 | 20004 | 1652539 | 2019-03-30 19:01 | 2019-03-31 16:00 | 1259 | 11kV | 191395 | 1479 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12600 Lisarwo - Pnl.9 tripped on A & C phase IOC Tree branch brought down HV into LV mains at PT13860. PT13860 & PT12400 isolated for repairs. See 1652997 1652998 | March | 2019 | 2019Q3 | 2019 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2019-03-30 | N | 129.4084 | N | 17 | N | N | 1.1101 | 39.4971 | 139865.8208
[7 empty] | 6110 | 8961 | 1652787 | 2019-03-31 21:17 | 2019-03-31 22:15 | 58 | 11kV | 4640 | 80 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex 11kv Panel 23 'S9819 Talara Kingsway' at ZN 9700 Kirrawee At PT9628 Sylvanis Matong. 11kv road side 31A HDO fuse has operated Protection Relay operations at Zone sub: Tx3A fault check, 11kv Panel 23 EFI Signal Operations at Zone sub: Zone earth, Tx3 group earth Remarks: dead possum found at base of PT-9628 pole. | March | 2019 | 2019Q3 | 2019 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2019-03-31 | N | 58 | N | 2 | N | N | 1.1101 | 39.4971 | 3390.7751
[7 empty] | 6839 | 16802 | 1652797 | 2019-04-01 01:08 | 2019-04-01 02:24 | 76 | 11kV | 4970 | 66 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC21799 Oxford Brooker tripped on: OC trip Cause not ascertained See 1652974 1652975 | April | 2019 | 2019Q4 | 2019 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Veg | 2019-04-01 | N | 75.303 | N | 4 | N | N | 1.1101 | 39.4971 | 3631.9294
[7 empty] | 5352 | 157 | 1652798 | 2019-04-01 02:25 | 2019-04-01 03:35 | 70 | 11kV | 7350 | 105 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT18597 Sylvania Mt Ettalong - 11kV Footpath phase HDO operated. Possum made contact with PT | April | 2019 | 2019Q4 | 2019 | ZN12640:PA4 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2019-04-01 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 5371.1632
[7 empty] | 6275 | 10644 | 1652802 | 2019-04-01 04:31 | 2019-04-01 06:42 | 131 | 11kV | 94352 | 1115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12620 NORAVILLE 11kV CB Panel 10 'Buff Point' fdr tripped on: Relays: E/F, EFI Signals: 11kv trip EFI: S18584 S18098 S49389 Cause: not ascertained See 1653203,4,5,6,7 Ex 1652802,3 | April | 2019 | 2019Q4 | 2019 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2019-04-01 | N | 84.6206 | N | 4 | N | N | 1.1101 | 39.4971 | 68949.6587
[7 empty] | 5979 | 7264 | 1652912 | 2019-04-01 11:25 | 2019-04-01 12:45 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 192656 A Phase DOLF : 16 Amp Excluded OMS 1652912 | April | 2019 | 2019Q4 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2019-04-01 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 6505 | 13350 | 1653109 | 2019-04-02 06:36 | 2019-04-02 07:50 | 74 | 11kV | 86318 | 1327 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN14143 SOMERSBY 11kV CB Panel 12 'Cp 44663 Phillips Gindurra' tripped on Relays: A and B phase IOC Signals: 11kv trip EFI: Nil PT11707 Acacia Debenham 11kv HDO's 31.5 Amp, Road and centre phase Note: SCADA defect on Auto reclose relay at Somersby, panel did not auto reclose Cause: Tree/Branch on mains at PT11707, 2x blown 11kv HDO's replaced 31.5 Amp road centre phase See 1653769,70 ex 1653109 | April | 2019 | 2019Q4 | 2019 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Veg | 2019-04-02 | N | 65.0475 | N | 8 | N | N | 1.1101 | 39.4971 | 63078.6485
[7 empty] | 5564 | 3106 | 1653137 | 2019-04-02 08:24 | 2019-04-02 09:04 | 40 | 11kV | 34240 | 856 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN12600 LISAROW 11kV CB Panel 13 'Bursh Rd' tripped, reclosed and locked outon: relays: B & C phase overcurrent, reclose and lockout Signals: 11kv tripEFI: N/A Cause: tree/rbanch on oh mains adjacent to AB44454 | April | 2019 | 2019Q4 | 2019 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2019-04-02 | N | 40 | N | 8 | N | N | 1.1101 | 39.4971 | 25021.5821
[7 empty] | 5576 | 3287 | 1653141 | 2019-04-02 08:32 | 2019-04-02 12:02 | 210 | 11kV | 25566 | 167 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 192658 fdr interupted by sop after reports of HV x arm snapped and inservice HV main resting on LV x arm. dq Excluded OMS 1653141. dq | April | 2019 | 2019Q4 | 2019 | 256:80652 | 256:80652 | ZN00256/080652 | NEWCASTLE | OH | Not Veg | 2019-04-02 | N | 153.0898 | N | 8 | N | N | 1.1101 | 39.4971 | 18682.8787
[7 empty] | 7140 | 19895 | 1653295 | 2019-04-02 15:12 | 2019-04-02 16:40 | 88 | 11kV | 176 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192660 C Phase DOLF : 10 Amp Excluded OMS 1653295 | April | 2019 | 2019Q4 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2019-04-02 | N | 88 | N | 8 | N | N | 1.1101 | 39.4971 | 128.6156
[7 empty] | 5453 | 1450 | 1653310 | 2019-04-02 16:24 | 2019-04-02 17:52 | 88 | 11kV | 8287 | 96 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 192663 A Phase 11kV on crossarm Excluded OMS 1653317, 1653323 | April | 2019 | 2019Q4 | 2019 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2019-04-02 | N | 86.3229 | N | 8 | N | N | 1.1101 | 39.4971 | 6055.8952
[7 empty] | 5662 | 4286 | 1653247 | 2019-04-02 12:35 | 2019-04-02 18:15 | 340 | 11kV | 101180 | 879 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | LID 192664 C Phase Overcurrent, Earth Fault Excluded OMS 1653247 | April | 2019 | 2019Q4 | 2019 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2019-04-02 | N | 115.1081 | N | 8 | N | N | 1.1101 | 39.4971 | 73939.3597
[7 empty] | 6699 | 15192 | 1653356 | 2019-04-02 20:57 | 2019-04-02 22:22 | 85 | 11kV | 340 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN15012 KILLARNEY section of 11kV Panel 6 Re26228 Valley Rd triupped Relays: OC trip, IOC trip, L/O Lots of trees require trimming. Tree on oh mains | April | 2019 | 2019Q4 | 2019 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2019-04-02 | N | 85 | N | 8 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 5918 | 6576 | 1653212 | 2019-04-02 10:58 | 2019-04-03 01:32 | 874 | 11kV | 107078 | 1354 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN9900 Menai 11kv feeder Panel No: 1 "Raine Marsden etc" feeder TRIPPED and on Relays: E/F, EFI, timing, lockout Abnormal: DMA @ S9174 in LV// Remarks: Excavator hit UG cable on cnr Recreation Drive and New Illawarra Rd section of 11kv feeder from S9428 Ella imbrey to S9020 Old Illawarra Dris 1 tee PT9424 New Illawarra Rd tee S9480 Sports Field I11 No2 to S9407 Sport Field New Illawarra Rd (3DC's interrupted) | April | 2019 | 2019Q4 | 2019 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2019-04-02 | N | 79.0827 | N | 8 | N | N | 1.1101 | 39.4971 | 78249.4441
[7 empty] | 6503 | 13332 | 1653358 | 2019-04-03 01:35 | 2019-04-03 08:42 | 426.5167 | 11kV | 6824.2667 | 16 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN14144 WAMBERAL section of 11kV Panel 2 PT12138 OAK MCGARRITY 0.4 11kV HDO's Footpath and Middle Phases 31.5A Fuses Blown Cause: A Possum has made contact with the surge arrestors at PT12138 See 1653358 ex 1653366 | April | 2019 | 2019Q4 | 2019 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Not Veg | 2019-04-03 | N | 426.5167 | N | 1 | N | N | 1.1101 | 39.4971 | 4986.9728
[7 empty] | 6124 | 9135 | 1653600 | 2019-04-04 09:49 | 2019-04-04 12:00 | 131 | 11kV | 262 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192677 Single phase DOLF : 10 Amp Excluded OMS 1653600 | April | 2019 | 2019Q4 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2019-04-04 | N | 131 | N | 4 | N | N | 1.1101 | 39.4971 | 191.4619
[7 empty] | 6824 | 16629 | 1653589 | 2019-04-04 09:12 | 2019-04-04 12:42 | 210 | 11kV | 60288 | 533 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 192675 broken xarm pole SW-40304 section isolated for repairs see report # 192671 192676 Excluded oms 1653562 1653589 1653634 | April | 2019 | 2019Q4 | 2019 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2019-04-04 | N | 113.1107 | N | 4 | N | N | 1.1101 | 39.4971 | 44056.6922
[7 empty] | 5915 | 6501 | 1653562 | 2019-04-04 10:02 | 2019-04-04 12:42 | 160 | 11kV | 18880 | 118 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192676 LH LVF 12941 isolated for 11kV repairs at pole SW-40304 see report # 192675/OMS 1654051 Excluded oms # 1653606 | April | 2019 | 2019Q4 | 2019 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2019-04-04 | N | 160 | N | 4 | N | N | 1.1101 | 39.4971 | 13796.9471
[7 empty] | 6004 | 7648 | 1653618 | 2019-04-04 10:43 | 2019-04-04 13:45 | 182 | 11kV | 2730 | 15 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At S3325 Horsley Amour, 11kv 75A OHFMA fuses operated Ex ZN2196 Milperra 11kv Panel 17 "Armour Ladbroke" feeder Remarks: Transformer failure. HV 75A 'B' & 'C' fuses blew on the 03/04/19 Tx defective. Dist #2 restored at 1200. Dist #1 (direct dist) restored at 1345. Customer suhinder Singhcalsi has agreed to restricted 200A supply. LV bars is solid at S3325. LV//: N/O dist #1 at S49766 Horsley Ladbroke | April | 2019 | 2019Q4 | 2019 | ZN2196:PA17 | ZN2196:PA17 | ZN02196/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-04-04 | N | 182 | N | 4 | N | N | 1.1101 | 39.4971 | 1995.0035
[7 empty] | 6404 | 12071 | 1654094 | 2019-04-05 09:17 | 2019-04-05 10:58 | 101 | 11kV | 124734 | 1290 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zb342 Paddington Zn - Pnl.28 tripped ON: C phase O/C & E/F Building site at 65 Craigend St, Darlinghurst: Metal fence post driven into UG cable. Section of feeder between S4567 and S77330 See 1654837 1654838 | April | 2019 | 2019Q4 | 2019 | ZN342:PA28 | ZN342:PA28 | ZN00342/000028 | SYDNEY | UG | Not Veg | 2019-04-05 | N | 96.693 | N | 3 | N | N | 1.1101 | 39.4971 | 91151.9282
[7 empty] | 6721 | 15306 | 1654124 | 2019-04-05 10:13 | 2019-04-05 14:00 | 227 | 11kV | 34809 | 207 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192687 Sub 64089 HV dropper faulty Excluded OMS 1654124 | April | 2019 | 2019Q4 | 2019 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Not Veg | 2019-04-05 | N | 168.1594 | N | 3 | N | N | 1.1101 | 39.4971 | 25437.3905
[7 empty] | 5843 | 5835 | 1654847 | 2019-04-05 17:55 | 2019-04-05 21:00 | 185 | 11kV | 370 | 2 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Section of 11kV feeder (Pnl.28 Paddington) interrupted for safety after steel picket was driven into 11kV earlier in the day. (see 1654837) Section from S77330 to S1681 See 1654847 1654848 | April | 2019 | 2019Q4 | 2019 | ZN342:PA28 | ZN342:PA28 | ZN00342/000028 | SYDNEY | UG | Not Veg | 2019-04-05 | N | 185 | N | 3 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 5543 | 2691 | 1654311 | 2019-04-06 07:47 | 2019-04-06 11:15 | 208 | 11kV | 1248 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192688 B Phase DOLF : 10 Amp Excluded OMS 1654311 | April | 2019 | 2019Q4 | 2019 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2019-04-06 | N | 208 | N | 2 | N | N | 1.1101 | 39.4971 | 912.0016
[7 empty] | 6795 | 16258 | 1654394 | 2019-04-06 22:50 | 2019-04-06 23:58 | 68 | 11kV | 131360 | 2035 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN3472 Sefton 11kv feeder Panel No.30 "Royal Gas etc" feeder tripped and locked out on Relays: SEF Field EFIs: nil Remarks: 11kv bond burnt off on pole RP11146 (O/S 48 Smith Rd) section of 11kv feeder from S8169 Ward Smith (Sw/B) to S8756 Saltash Valentine (Sw/A) | April | 2019 | 2019Q4 | 2019 | ZN3472:PA30 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-04-06 | N | 64.5504 | N | 2 | N | N | 1.1101 | 39.4971 | 95994.0135
[7 empty] | 7004 | 18574 | 1654420 | 2019-04-07 00:18 | 2019-04-07 03:00 | 162 | 11kV | 4770 | 40 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 192693 11kV main on xarm pole 9M-90026, repairs complete. Excluded OMS 1654420 | April | 2019 | 2019Q4 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-04-07 | N | 119.25 | N | 3 | N | N | 1.1101 | 39.4971 | 3485.7753
[7 empty] | 6626 | 14598 | 1654470 | 2019-04-07 16:31 | 2019-04-07 18:40 | 129 | 11kV | 1870 | 180 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192698 mains down between pole 4H-60025 & 4H-90087. Sw 75074 Opened and Section isolated for repairs. Excluded OMS 1654470 | April | 2019 | 2019Q4 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-04-07 | N | 10.3889 | N | 3 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 5513 | 2159 | 1654487 | 2019-04-07 20:50 | 2019-04-07 23:52 | 182 | 11kV | 364 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192701 DOLF : 10 Amp Excluded OMS 1654487 | April | 2019 | 2019Q4 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2019-04-07 | N | 182 | N | 3 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 6920 | 17775 | 1654517 | 2019-04-08 00:49 | 2019-04-08 02:45 | 116 | 11kV | 9280 | 80 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192702 C Phase DOLF : 40 Amp Excluded OMS 1654517 | April | 2019 | 2019Q4 | 2019 | 224:80326 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Veg | 2019-04-08 | N | 116 | N | 3 | N | N | 1.1101 | 39.4971 | 6781.5503
[7 empty] | 6034 | 7947 | 1654523 | 2019-04-08 05:55 | 2019-04-08 12:50 | 415 | 11kV | 50109 | 876 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192706 B and C Phase Trees on mains at NR-90079 and Pin broken at NR-90204. Also interr Sub 22766. to extend the area. #OMS 1654523, 1654524, 1654525, 1654594 | April | 2019 | 2019Q4 | 2019 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2019-04-08 | N | 57.2021 | N | 3 | N | N | 1.1101 | 39.4971 | 36618.1792
[7 empty] | 5620 | 3711 | 1654773 | 2019-04-09 03:52 | 2019-04-09 05:17 | 85 | 11kV | 197230 | 2400 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.32 tripped on: Earth Fault UG cable fault between S6169 Sw/B and S1690 Sw/A See 1654849 1654850 | April | 2019 | 2019Q4 | 2019 | ZN2568:PA32 | ZN2568:PA32 | ZN02568/000032 | SYDNEY | UG | Not Veg | 2019-04-09 | N | 82.1792 | N | 8 | N | N | 1.1101 | 39.4971 | 144129.8667
[7 empty] | 5477 | 1657 | 1654802 | 2019-04-09 09:28 | 2019-04-09 10:19 | 51 | 11kV | 39321 | 771 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9550 Gwawley bay - Pnl.36 tripped on: Earth Fault Bird came into contact with 11kV UGOH above S9875 Belgrave Lachlan. | April | 2019 | 2019Q4 | 2019 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2019-04-09 | N | 51 | N | 8 | N | N | 1.1101 | 39.4971 | 28734.627
[7 empty] | 6602 | 14372 | 1654866 | 2019-04-09 12:05 | 2019-04-09 13:25 | 80 | 11kV | 8800 | 110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192714 Wire off pin at Pole 4I-30014. Emergency SI T0052 | April | 2019 | 2019Q4 | 2019 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2019-04-09 | N | 80 | N | 8 | N | N | 1.1101 | 39.4971 | 6430.7804
[7 empty] | 6676 | 15056 | 1654839 | 2019-04-09 12:20 | 2019-04-09 13:40 | 80 | 11kV | 800 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192712 Hazardous tree branch overhanging 11kV OHM adj pole DV-74430 | April | 2019 | 2019Q4 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-04-09 | N | 80 | N | 8 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 5434 | 1215 | 1654886 | 2019-04-09 13:45 | 2019-04-09 14:15 | 30 | 11kV | 150 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 192720 Broken pin insulator at Pole 4I-30014 | April | 2019 | 2019Q4 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-04-09 | N | 30 | N | 8 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 6304 | 10941 | 1654893 | 2019-04-08 15:36 | 2019-04-09 15:21 | 1425 | 11kV | 46488 | 252 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15013 Terrey Hills Panel 6 tripped under fault Cause: Protection relay flags/ Signals at Zone Sub A and C phase Timed IOC C phase timed oc recloser time delay Recloser Lockout 11kV Trip Cause: Tree branch found and removed from OH 11kV Mains between USL24937 and PT15377 See OMS 1655256 1655259 1648493 1654467 | April | 2019 | 2019Q4 | 2019 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2019-04-08 | N | 184.4762 | N | 3 | N | N | 1.1101 | 39.4971 | 33972.0592
[7 empty] | 6052 | 8168 | 1654972 | 2019-04-09 19:14 | 2019-04-09 20:37 | 83.1167 | 11kV | 27262.2667 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15014 Mona Vale Panel 11kV Recloser CP22381 Lane Cove Tripped under faulxst Cause: Tree branch found and removed from 11kV OH mains adjacent ttio PT15577 Sanitary Depot | April | 2019 | 2019Q4 | 2019 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2019-04-09 | N | 83.1167 | N | 8 | N | N | 1.1101 | 39.4971 | 19922.4604
[7 empty] | 5788 | 5458 | 1654984 | 2019-04-09 20:02 | 2019-04-09 21:43 | 101 | 11kV | 107466 | 1266 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1290 Leightonfield P9 Christina Birmingham etc fdr tripped reclosed and locked out on b phase oc, lockout relay and efi Remarks; UG fault. S5923 Shaddock boral to S3119 Marple shaddock | April | 2019 | 2019Q4 | 2019 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-04-09 | N | 84.8863 | N | 8 | N | N | 1.1101 | 39.4971 | 78532.9831
[7 empty] | 6364 | 11622 | 1654867 | 2019-04-09 17:43 | 2019-04-10 00:20 | 397 | 11kV | 331178 | 2166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12580 Erina Panel 4 tripped on Relays: IOC and Timed A phase Signals: 11kV Trip. Field EFI's NIL Cause: Tree on 11kV adjacent PT12320 - Removed by linesman IR49612 Protection did not grade T/PE to investigate. Cause: Tree branch on OH mains. See OMS 1655778 1655779 1655780 1654959 1655007 1654999 1654971 | April | 2019 | 2019Q4 | 2019 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2019-04-09 | N | 152.8984 | N | 8 | N | N | 1.1101 | 39.4971 | 242015.1143
[7 empty] | 6533 | 13682 | 1654353 | 2019-04-10 13:18 | 2019-04-10 13:45 | 27 | 11kV | 135 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 192726 repairs to loose crossarm coach screw at pole DP-50399. Excluded OMS 1654353 | April | 2019 | 2019Q4 | 2019 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2019-04-10 | N | 27 | N | 2 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 6286 | 10760 | 1655204 | 2019-04-10 20:47 | 2019-04-10 22:30 | 103 | 11kV | 2060 | 20 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 192733 Broken stay at sub 53305 unable to isolate at LLCs, section isolated due to live work directive. | April | 2019 | 2019Q4 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2019-04-10 | N | 103 | N | 2 | N | N | 1.1101 | 39.4971 | 1505.3872
[7 empty] | 5546 | 2707 | 1655368 | 2019-04-11 16:40 | 2019-04-11 17:45 | 65 | 11kV | 585 | 9 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 192742 Found by field crew. M.Brown. X-arm was badly split. | April | 2019 | 2019Q4 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-04-11 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 427.5007
[7 empty] | 6229 | 10249 | 1655366 | 2019-04-11 16:40 | 2019-04-11 18:27 | 107 | 11kV | 5136 | 48 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 192744 Section isolated to repair 11kV tapping. see LID report 192745 & SI T0054 Excluded OMS1655366 | April | 2019 | 2019Q4 | 2019 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2019-04-11 | N | 107 | N | 2 | N | N | 1.1101 | 39.4971 | 3753.2373
[7 empty] | 6567 | 14018 | 1655397 | 2019-04-12 02:09 | 2019-04-12 04:10 | 121 | 11kV | 8107 | 67 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN15001 BROOKVALE section of 11kV Panel 18 PT15265 ALFRED RD 1 31.5amp roadside phase HDO blown Cause: not ascertained See 1655442 ex 1655397 | April | 2019 | 2019Q4 | 2019 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Veg | 2019-04-12 | N | 121 | N | 5 | N | N | 1.1101 | 39.4971 | 5924.3565
[7 empty] | 5468 | 1578 | 1655458 | 2019-04-12 11:18 | 2019-04-12 12:40 | 82 | 11kV | 110171 | 1563 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN15011 Beacon Hill Panel 10 Tripped Relays: Panel 10R SEL Signals 11kV trip Filed EFi's nil Cause: 11kV bond burnt off middle phase on pole FF44468 See OMS 1656077 165078 1655458 | April | 2019 | 2019Q4 | 2019 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-04-12 | N | 70.4869 | N | 5 | N | N | 1.1101 | 39.4971 | 80509.7173
[7 empty] | 6277 | 10653 | 1655548 | 2019-04-12 16:35 | 2019-04-12 20:30 | 235 | 11kV | 11280 | 48 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 192758 No protection operations. Fdr isolated replace faulty insulators at poles KS-40220 & KS-40219 under AP. Excluded OMS 1655548. | April | 2019 | 2019Q4 | 2019 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2019-04-12 | N | 235 | N | 5 | N | N | 1.1101 | 39.4971 | 8243.0913
[7 empty] | 6095 | 8695 | 1655527 | 2019-04-12 17:15 | 2019-04-12 22:40 | 325 | 11kV | 26325 | 81 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Section of panel 10R beyond LB 41141 to CP40724 interrupted to effect emergency repairs AB40724 Closed Ab40725 Open and Defective CauseL Vehicle striuck pole See OMS 1656808 1655527 1655528 1655538 1655555 | April | 2019 | 2019Q4 | 2019 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2019-04-12 | N | 325 | N | 5 | N | N | 1.1101 | 39.4971 | 19237.5335
[7 empty] | 5623 | 3723 | 1655578 | 2019-04-12 22:55 | 2019-04-12 23:52 | 57 | 11kV | 58995 | 1035 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.4 tripped on: Translay UG cable fault from S8742 Sw/B to S3039 Sw/B | April | 2019 | 2019Q4 | 2019 | ZN35600:PA4 | ZN35600:PA4 | ZN35600/000004 | RANDWICK | UG | Not Veg | 2019-04-12 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 43111.8059
[7 empty] | 6540 | 13729 | 1655677 | 2019-04-14 09:22 | 2019-04-14 10:27 | 65 | 11kV | 780 | 12 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | LID 192762 3 phase section of 11kV interupted by dop to repair broken xarm brace after car hit pole. dq Excluded OMS## 1655677. dq | April | 2019 | 2019Q4 | 2019 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2019-04-14 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 570.001
[7 empty] | 6594 | 14334 | 1655698 | 2019-04-14 12:13 | 2019-04-14 15:20 | 187 | 11kV | 177583 | 1289 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.41 tripped on: Earth Fault Field EFIs; S5730 S4230 S2978 S488 Ug cable fault between S2978 Sw/B & S488 Sw/A See 1655856 1655857 1655858 1655859 | April | 2019 | 2019Q4 | 2019 | ZN2602:PA41 | ZN2602:PA41 | ZN02602/000041 | RANDWICK | UG | Not Veg | 2019-04-14 | N | 137.768 | N | 5 | N | N | 1.1101 | 39.4971 | 129772.4186
[7 empty] | 6130 | 9221 | 1655726 | 2019-04-14 17:10 | 2019-04-14 18:15 | 65 | 11kV | 350 | 7 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 192765 Outage to allow repairs to replace broken dead end insulator. Excluded OMS 1655726 | April | 2019 | 2019Q4 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2019-04-14 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 6429 | 12463 | 1655737 | 2019-04-14 18:42 | 2019-04-14 20:15 | 93 | 11kV | 1581 | 17 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT46693 The Ridgeway Timber 11kV Footpath HDO operated Ex Zn12600 Lisarow Panel 2 Holgate Cause: Fuse Fatigue | April | 2019 | 2019Q4 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2019-04-14 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 1155.3482
[7 empty] | 6545 | 13776 | 1655745 | 2019-04-14 21:26 | 2019-04-14 22:15 | 49 | 11kV | 34202 | 698 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Ex Zn12690 Berkeley Vale Panel 10 Chittaway USL 40030 centre phase link has fallen apart See OMS 1656093 1655745 | April | 2019 | 2019Q4 | 2019 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2019-04-14 | N | 49 | N | 5 | N | N | 1.1101 | 39.4971 | 24993.8128
[7 empty] | 6907 | 17651 | 1655810 | 2019-04-15 09:26 | 2019-04-15 13:05 | 219 | 11kV | 219 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 192769 B phase DOLF : 10 Amp Replace L/A's | April | 2019 | 2019Q4 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2019-04-15 | N | 219 | N | 3 | N | N | 1.1101 | 39.4971 | 160.0387
[7 empty] | 6150 | 9429 | 1655933 | 2019-04-15 18:50 | 2019-04-15 21:40 | 170 | 11kV | 35190 | 207 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At PT64886 Bennett Adelaide 400A fuse blown on A B and C phase of distributor 1. Cause: Broken LV cross arm on the CNR of Adelaide and Bennett St - Distributor 1 and NO2 Interrupted @ PT64886 to allow Emergency repairs See OMS 1655933 1655955 | April | 2019 | 2019Q4 | 2019 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Not Veg | 2019-04-15 | N | 170 | N | 3 | N | N | 1.1101 | 39.4971 | 25715.8141
[7 empty] | 6872 | 17183 | 1656058 | 2019-04-15 22:13 | 2019-04-15 23:08 | 55 | 11kV | 47080 | 856 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn12600 Lisarow Panel 13 has tripped on Signnals: 11kV Trip Relays: 51 TS, 51A, 51N, Recloser timer and Lockout Field EFI's NIL Cause: Possum located at the base of first UGOH Animals/Birds | April | 2019 | 2019Q4 | 2019 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2019-04-15 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 34404.6754
[7 empty] | 6367 | 11687 | 1656071 | 2019-04-16 02:31 | 2019-04-16 10:40 | 489 | 11kV | 195123 | 1293 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn12610 Long Jetty Panel 24 tripped on Signals: 11kV trip, Group 3 Earth Fault Relays: C phase OC, EF, EFI Reclose and Lockout Field EFI's NIL Clamp where UGOH Connects to OH (Copper to Aluminium) has gone HR and Melted causing OG to fall down on side to AB42246 AB 42246 will not fully open, AB 44580 has also had high resistance and burnt a contact. See OMS 1657969 1657971 1657973 1657972 1657970 1656070 1656074 1656096 1656071 1656072 1656304 | April | 2019 | 2019Q4 | 2019 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Not Veg | 2019-04-16 | N | 150.9072 | N | 3 | N | N | 1.1101 | 39.4971 | 142590.1332
[7 empty] | 7089 | 19499 | 1656082 | 2019-04-16 09:00 | 2019-04-16 11:10 | 130 | 11kV | 650 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 192777 11 kV main off pin insulator pole 8M-60144 Excluded OMS 1656082 | April | 2019 | 2019Q4 | 2019 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2019-04-16 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 5592 | 3507 | 1656280 | 2019-04-16 18:35 | 2019-04-16 20:40 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192785 B Phase DOLF : 10 Amp excluded OMS 1656280 | April | 2019 | 2019Q4 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-04-16 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 5534 | 2499 | 1656230 | 2019-04-17 07:00 | 2019-04-17 14:15 | 435 | 11kV | 1740 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 192797 A Phase DOLF : 10 Amp Excluded OMS 1656230 | April | 2019 | 2019Q4 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2019-04-17 | N | 435 | N | 3 | N | N | 1.1101 | 39.4971 | 1271.5407
[7 empty] | 5685 | 4500 | 1656381 | 2019-04-17 12:26 | 2019-04-17 14:15 | 109 | 11kV | 218 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192798 A Phase DOLF : 10 Amp Excluded OMS 1656381 | April | 2019 | 2019Q4 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2019-04-17 | N | 109 | N | 3 | N | N | 1.1101 | 39.4971 | 159.308
[7 empty] | 5937 | 6819 | 1656510 | 2019-04-17 16:45 | 2019-04-17 18:35 | 110 | 11kV | 11660 | 106 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | HV Crossarm defective at PT13522 Three Points Endeavour 11kV feeder from AB41333 to LB41682 to LB49195 tee PT13522 - TeePT11638 Endeavour Carnedie HV Crossarm defective at PT13522 | April | 2019 | 2019Q4 | 2019 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2019-04-17 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 8520.7841
[7 empty] | 6801 | 16391 | 1656630 | 2019-04-18 16:00 | 2019-04-19 00:01 | 481 | 11kV | 962 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex Xn9900 Menai Pnl.11 - FDR from S9949 to S9248 interrupted. Snapped cross arm on pole SU08667. See 1656630 1656631 | April | 2019 | 2019Q4 | 2019 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | OH | Not Veg | 2019-04-18 | N | 481 | N | 1 | N | N | 1.1101 | 39.4971 | 703.0012
[7 empty] | 6914 | 17692 | 1656764 | 2019-04-19 17:59 | 2019-04-19 20:20 | 141 | 11kV | 2256 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192815 C Phase 10 Amp fuse, substation DOLF No cause found not storm conditions | April | 2019 | 2019Q4 | 2019 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2019-04-19 | N | 141 | N | 2 | N | N | 1.1101 | 39.4971 | 1648.6183
[7 empty] | 6238 | 10327 | 1656755 | 2019-04-19 16:32 | 2019-04-20 15:50 | 1398 | 11kV | 44225 | 118 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Recloser CP61097 Wise Ferry Lavendar 10.2 Open and Locked out on OC Section of Panel 1 Peats Ridge Cause: Vehicle Hit LB43531 and Brought Down 11kV OH. Feeder from 40601 to USL43530 isolated and earthed overnight. - Interruptions to PT13629, PT63074 PT13631 1657258 1657263 1656755 1656840 1655174 1656772 1656773 1656834 | April | 2019 | 2019Q4 | 2019 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-04-19 | N | 374.7881 | N | 2 | N | N | 1.1101 | 39.4971 | 32318.3256
[7 empty] | 6561 | 13896 | 1656811 | 2019-04-20 09:17 | 2019-04-20 15:55 | 398 | 11kV | 1592 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 192816 C Phase, 10 Amp Substation DOLF - replaced faulty lightning arrestors Found C phase HV arrestor blown as well as C phase DOLF on Pole top substation - 10472. S.O. notified. LVFs 10472 opened off, DOLFs 10472 opened and removed. A warning tag has been attached to pole. | April | 2019 | 2019Q4 | 2019 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2019-04-20 | N | 398 | N | 2 | N | N | 1.1101 | 39.4971 | 1163.3866
[7 empty] | 7011 | 18631 | 1656839 | 2019-04-20 17:02 | 2019-04-20 19:35 | 153 | 11kV | 153 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192817 ABC Phase, dropper lead burnt off top of DOLF sub, isolated for repair | April | 2019 | 2019Q4 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2019-04-20 | N | 153 | N | 2 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 5768 | 5332 | 1656889 | 2019-04-21 10:48 | 2019-04-21 11:47 | 59 | 11kV | 120714 | 2046 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Zn10993 Hurstville North - Pnl.35 tripped & reclosed on: B & C phase OC Abnormal: S10213 Sw/A with S49279 Sw/B Closed. AB31012 closed with S10589 Sw/A Open Tree branch hit mains and burnt off bond "B" phase on pole PE17675 | April | 2019 | 2019Q4 | 2019 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Veg | 2019-04-21 | N | 59 | N | 1 | N | N | 1.1101 | 39.4971 | 88214.2307
[7 empty] | 5612 | 3652 | 1656962 | 2019-04-22 07:40 | 2019-04-22 08:51 | 71 | 11kV | 22933 | 323 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192819 2 Fault Operations, C Phase, Overcurrent Magpie between phases pole IS62835 Sw 2728 C phase O/C Sw 90525 C phase O/C. CC1: 22-"Refer to SOp" | April | 2019 | 2019Q4 | 2019 | 235:2728 | 235:2728 | ZN00235/002728 | NEWCASTLE | OH | Not Veg | 2019-04-22 | N | 71 | N | 1 | N | N | 1.1101 | 39.4971 | 16758.76
[7 empty] | 6478 | 13069 | 1657099 | 2019-04-23 10:11 | 2019-04-23 13:20 | 189 | 11kV | 378 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192822 B Phase 10 Amp fuse, substation DOLF Tx Volts A/B/Cph: 243V | April | 2019 | 2019Q4 | 2019 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2019-04-23 | N | 189 | N | 4 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 5548 | 2723 | 1657144 | 2019-04-23 14:19 | 2019-04-23 17:00 | 161 | 11kV | 322 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192828 C[h HV lead broken off DPLF 50088 | April | 2019 | 2019Q4 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2019-04-23 | N | 161 | N | 4 | N | N | 1.1101 | 39.4971 | 235.3081
[7 empty] | 6904 | 17629 | 1657220 | 2019-04-23 19:30 | 2019-04-23 20:30 | 60 | 11kV | 990 | 341 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12690 Berkeley Vale Panel 16 tripped and reclosed on Relays: A and B phase IOC and EFI. Signals: 11kV Trip and TX3 Group earth Cause: Stick across HV fuses at PT13181 See OMS 1657343 1657344 1657221 1657220 1657225 | April | 2019 | 2019Q4 | 2019 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2019-04-23 | N | 2.9032 | N | 4 | N | N | 1.1101 | 39.4971 | 723.4628
[7 empty] | 7120 | 19697 | 1657238 | 2019-04-23 22:07 | 2019-04-24 05:05 | 418 | 11kV | 16892 | 142 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192830 3 Fault operations, A,B,C Phases, Overcurrent, Earth Fault Swan into Mains at Pole JP-96066 Mains down between Pole JP-96066 and JP-95067 | April | 2019 | 2019Q4 | 2019 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2019-04-23 | N | 118.9577 | N | 4 | N | N | 1.1101 | 39.4971 | 12344.1754
[7 empty] | 7084 | 19460 | 1657288 | 2019-04-24 09:59 | 2019-04-24 11:11 | 72 | 11kV | 14400 | 200 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S14891 Wyong Panel 1 - HV bond off adjacent to AB43337 Footpath Side. See OMS 1657289 1657313 1657317 1657288 | April | 2019 | 2019Q4 | 2019 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | OH | Not Veg | 2019-04-24 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 10523.0953
[7 empty] | 6949 | 18007 | 1657835 | 2019-04-24 09:40 | 2019-04-24 13:05 | 205 | 33kV Distribution | 205 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192837 Emergency repairs on customer equipment | April | 2019 | 2019Q4 | 2019 |  |  |  | NEWCASTLE | OH | Not Veg | 2019-04-24 | N | 205 | N | 3 | N | N | 1.1101 | 39.4971 | 149.808
[7 empty] | 7073 | 19362 | 1657351 | 2019-04-24 14:26 | 2019-04-24 15:18 | 52 | 11kV | 4420 | 85 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 192839 Interrupted for broken x arm replacement a pole MG-97050 Excluded OMS 1657351 | April | 2019 | 2019Q4 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2019-04-24 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 3230.0056
[7 empty] | 6612 | 14453 | 1657411 | 2019-04-25 03:30 | 2019-04-25 04:55 | 85 | 11kV | 1069 | 13 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At ZN167 Auburn 11kv feeder Panel 8 "Silverwater Fariola etc" feeder tripped on: Relays: C phase O/C Signals: 11kv trip Remarks: TPE required to investigate relay operation @ ZN167 Auburn for feeder panel No8 "Silverwater Fariola etc", the associated feeder was all U/G, no E/F or EFI at zone or in field and Panel all went back, possible relay faulty | April | 2019 | 2019Q4 | 2019 | ZN167:PA8 | ZN167:PA8 | ZN00167/000008 | PARRAMATTA | Unknown | Not Veg | 2019-04-25 | N | 82.2308 | N | 2 | N | N | 1.1101 | 39.4971 | 781.1937
[7 empty] | 5552 | 2874 | 1657448 | 2019-04-25 15:04 | 2019-04-25 16:03 | 59 | 11kV | 19352 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | Recloser CP22381 Tripped on overcurrent and IOC Cause: Tree branch contact vicinity PT15577 | April | 2019 | 2019Q4 | 2019 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2019-04-25 | N | 59 | N | 2 | N | N | 1.1101 | 39.4971 | 14141.8708
[7 empty] | 6418 | 12275 | 1657629 | 2019-04-27 02:32 | 2019-04-27 03:53 | 81 | 11kV | 19849 | 267 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Epping Panel 51 Tripped on Relays: C phase IOC 950TC), Earth Fault IOC (150TN) EFI Signals: 11kV Trip EFi's Cause: After DOp Tried back LV fuse at S1796 Herring Talaverya Distributor 2 Panel 51 Epping Tripped. See OMS 1657805 1657806 1657629 | April | 2019 | 2019Q4 | 2019 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | UG | Not Veg | 2019-04-27 | N | 74.3408 | N | 2 | N | N | 1.1101 | 39.4971 | 14505.0638
[7 empty] | 6767 | 15759 | 1657682 | 2019-04-27 12:30 | 2019-04-27 13:35 | 65 | 11kV | 130 | 2 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192847 Single phase DOLF : 10 Amp Excluded OMS 1657682 10A sub DOLF 72904 & 10A Line DOLF 43790 replaced. Dead Indian Myna found at sub 72904. | April | 2019 | 2019Q4 | 2019 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2019-04-27 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 5664 | 4308 | 1657714 | 2019-04-28 10:00 | 2019-04-28 11:00 | 60 | 11kV | 8700 | 145 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | @S4855 Gipps Flav of Panel 27 @ S2835 Burwood. Tx interrupted for safety Remarks: Interrupted to allow 3 dist to be made dead to allow work dead for oms job 1657714 car hit pole | April | 2019 | 2019Q4 | 2019 | ZN2835:PA27 | ZN2835:PA27 | ZN02835/000027 | CANADA BAY | OH | Not Veg | 2019-04-28 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 6357.7034
[7 empty] | 5770 | 5346 | 1657727 | 2019-04-28 09:49 | 2019-04-28 11:13 | 84 | 11kV | 336 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192853 A Phase broken dolf dropper Excluded OMS 1657727 | April | 2019 | 2019Q4 | 2019 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2019-04-28 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 6544 | 13772 | 1657734 | 2019-04-28 10:24 | 2019-04-28 11:20 | 56 | 11kV | 1456 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192851 A Phase DOLF : 20 Amp Excluded OMS 1657734 | April | 2019 | 2019Q4 | 2019 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2019-04-28 | N | 56 | N | 3 | N | N | 1.1101 | 39.4971 | 1064.0019
[7 empty] | 5890 | 6322 | 1657796 | 2019-04-29 04:40 | 2019-04-29 06:02 | 82 | 11kV | 119733 | 1659 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.12 tripped on: A & C phase O/C UG cable fault between Pnl.12 and S1868 Sw/A and S3240 Sw/B See 1658059 GIS1657800 | April | 2019 | 2019Q4 | 2019 | ZN3472:PA12 | ZN3472:PA12 | ZN03472/000012 | CUMBERLAND | UG | Not Veg | 2019-04-29 | N | 72.1718 | N | 2 | N | N | 1.1101 | 39.4971 | 87497.3449
[7 empty] | 5519 | 2288 | 1657860 | 2019-04-29 10:09 | 2019-04-29 11:42 | 93 | 11kV | 7998 | 86 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Centre Phase 63A HDO @ PT466192 Dwyer Jarett HV fuse blown. Cause: Fuse Fatigue See OMS 1658537 1657871 1657860 | April | 2019 | 2019Q4 | 2019 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2019-04-29 | N | 93 | N | 2 | N | N | 1.1101 | 39.4971 | 5844.7025
[7 empty] | 6408 | 12145 | 1653077 | 2019-04-30 10:18 | 2019-04-30 11:56 | 98 | 11kV | 119760 | 1308 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15008 Harbord Zone Panel 5 tripped under fault Protection Relay operations at Harbord Zone Panel 5L: A phase IOC Trip, Recloser Timing, Recloser Lockout Cause: Balloon Found and Removed from 11kVOH mains Near 45 Evans St Freshwater See OMS 1658471 1658472 1658101 1653077 | April | 2019 | 2019Q4 | 2019 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Veg | 2019-04-30 | N | 91.5596 | N | 5 | N | N | 1.1101 | 39.4971 | 87517.0757
[7 empty] | 7022 | 18717 | 1658164 | 2019-04-30 14:39 | 2019-04-30 16:15 | 96 | 11kV | 81362 | 2108 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay - Pnl.23 tripped on: F/C Field EFIs: S3361 S2423 S49321 S48873 Note: S8669 EFI did not operate UG cable fault between S8669 and S2521 See 1658280 1658281 1658282 GIS1658168 | April | 2019 | 2019Q4 | 2019 | ZN36100:PA23 | ZN36100:PA23 | ZN36100/000023 | WAVERLEY | UG | Not Veg | 2019-04-30 | N | 38.5968 | N | 5 | N | N | 1.1101 | 39.4971 | 59456.9498
[7 empty] | 7156 | 20043 | 1658170 | 2019-04-30 14:55 | 2019-04-30 16:49 | 114 | 11kV | 68521 | 667 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 11kV Recloser CP48437 Peats Ridge Cooks 1.35 tripped and reclosed and locked out on OC Trip. DOPS have patrolled feeder but no cause was found See OMS 1658622 1658621 1658620 1658619 1658170 1658177 1658204 | April | 2019 | 2019Q4 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2019-04-30 | N | 102.7301 | N | 5 | N | N | 1.1101 | 39.4971 | 50073.1258
[7 empty] | 6037 | 8007 | 1658227 | 2019-04-30 16:31 | 2019-04-30 20:25 | 234 | 11kV | 164403 | 1347 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 192878 2 fault operations C Phase Earth Fault Excluded OMS 1658277 | April | 2019 | 2019Q4 | 2019 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | UG | Not Veg | 2019-04-30 | N | 122.0512 | N | 5 | N | N | 1.1101 | 39.4971 | 120140.8633
[7 empty] | 6045 | 8101 | 1658264 | 2019-04-30 22:19 | 2019-04-30 23:19 | 60 | 11kV | 14340 | 239 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP527 Catherine Paul (ex Panel 23 St Ives) tripped and reclosed tripped and locke3d out Relays: IOC and OC Signals: 11 kV trip Tree branch on OH mains outside 21 Cassandra | April | 2019 | 2019Q4 | 2019 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2019-04-30 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 10479.249
[7 empty] | 6603 | 14375 | 1658313 | 2019-05-01 09:46 | 2019-05-01 10:52 | 66 | 11kV | 18480 | 280 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | At S14891 Wyong Zone Panel 16 report of no supply @ Subs downs stream of 11kV USL 40139 Cause: Ab43655 Closed, CP43337 Open | May | 2019 | 2019Q4 | 2019 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2019-05-01 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 13504.6389
[7 empty] | 5800 | 5552 | 1658451 | 2019-05-01 19:50 | 2019-05-02 10:00 | 850 | 11kV | 18610 | 22 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Pnl.2 Galston - outside 5 Cotswold Rd - tree branch brought down 11kV mains. PT2353 & PT49970 interrupted to make repairs See 1659364 1659365 | May | 2019 | 2019Q4 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2019-05-01 | N | 845.9091 | N | 2 | N | N | 1.1101 | 39.4971 | 13599.6391
[7 empty] | 7061 | 19268 | 1658670 | 2019-05-03 05:25 | 2019-05-03 06:30 | 65 | 11kV | 56420 | 868 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192914 2 fault operations | May | 2019 | 2019Q4 | 2019 | 205:12206 | 205:12206 | ZN00205/012206 | NEWCASTLE | OH | Veg | 2019-05-03 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 41230.0719
[7 empty] | 6098 | 8727 | 1658909 | 2019-05-03 20:55 | 2019-05-03 23:13 | 138 | 11kV | 15173 | 136 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 192919 3 fault operation 3 phase Overcurrent tree branch removed from OHM pole HW-50017. B phase 11kV skirt is damaged from previous lightning strike at pole HW-50148 and requires replacement. Voltage on pole test OK 12V wet pole. A phase LV stranded between pole HW-50232 and HW-50233. Please investigate and repair. dq excluded OMS 1658909## | May | 2019 | 2019Q4 | 2019 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2019-05-03 | N | 111.5662 | N | 2 | N | N | 1.1101 | 39.4971 | 11087.9809
[7 empty] | 6104 | 8832 | 1658908 | 2019-05-04 13:55 | 2019-05-04 14:25 | 30 | 11kV | 2670 | 89 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv/415v Pt2209 Burns Picnic interrupted for safety Remarks: interrupted for safety reasons. To replace LV service during live work ban | May | 2019 | 2019Q4 | 2019 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-05-04 | N | 30 | N | 1 | N | N | 1.1101 | 39.4971 | 1951.1572
[7 empty] | 6123 | 9134 | 1659103 | 2019-05-05 18:50 | 2019-05-05 21:50 | 180 | 11kV | 6660 | 37 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14143 SOMERSBY section of 11kV Panel 17 'Somersby Falls' 11kv overhead isolated from AB44019 to AB44200 tee PT13396, PT12914, PT63392, pT63391, PT64386. Cause: tree/branch brought down OH. at 185 Morgans Rd. See 1660241 ex 1659103,4,5,6,7 | May | 2019 | 2019Q4 | 2019 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2019-05-05 | N | 180 | N | 3 | N | N | 1.1101 | 39.4971 | 4866.9316
[7 empty] | 6424 | 12312 | 1659127 | 2019-05-05 23:25 | 2019-05-06 00:52 | 87 | 11kV | 116493 | 1339 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV Panel 22 Roadside burnt off bond @ AB40388 Feeder isolated from AB40388 to RE46529 to S65223 See 1660258 ex 1659127,30 | May | 2019 | 2019Q4 | 2019 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2019-05-05 | N | 87 | N | 3 | N | N | 1.1101 | 39.4971 | 85129.6484
[7 empty] | 6369 | 11697 | 1659206 | 2019-05-06 10:10 | 2019-05-06 10:30 | 20 | 11kV | 100 | 5 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 192930 A phase Cracked insulator pole, AK-50012. Section isolated for repair | May | 2019 | 2019Q4 | 2019 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-05-06 | N | 20 | N | 1 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 5798 | 5548 | 1659098 | 2019-05-05 18:03 | 2019-05-06 15:15 | 1272 | 11kV | 206064 | 162 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Defective 11kv/415v TX @ S5660 Denison Eltham Remarks: Transformer failure. Subs to investigate | May | 2019 | 2019Q4 | 2019 | ZN398:PA3 | ZN398:PA3 | ZN00398/000003 | INNER WEST | UG | Not Veg | 2019-05-05 | N | 1272 | N | 3 | N | N | 1.1101 | 39.4971 | 150585.4933
[7 empty] | 5956 | 6985 | 1659496 | 2019-05-07 18:24 | 2019-05-07 21:40 | 196 | 11kV | 196 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 192951 Single phase Burnt up LL Clamp on OHM at sub 51301. Excluded OMS 1659496, 1659497, 1659500 | May | 2019 | 2019Q4 | 2019 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2019-05-07 | N | 196 | N | 1 | N | N | 1.1101 | 39.4971 | 143.231
[7 empty] | 6611 | 14450 | 1659817 | 2019-05-08 10:59 | 2019-05-08 12:07 | 68 | 11kV | 91392 | 1344 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.15 tripped on: A & C phase IOC Tree branch on OH mains outside 172 Grosvenor | May | 2019 | 2019Q4 | 2019 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2019-05-08 | N | 68 | N | 3 | N | N | 1.1101 | 39.4971 | 66786.578
[7 empty] | 6543 | 13771 | 1659804 | 2019-05-08 10:00 | 2019-05-08 14:30 | 270 | 11kV | 2340 | 38 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192957 LEAD TO DOLF 52951 BURNT OFF SECTION ISOLATED FOR REPAIR Excluded OMS 1659804 | May | 2019 | 2019Q4 | 2019 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2019-05-08 | N | 61.5789 | N | 3 | N | N | 1.1101 | 39.4971 | 1710.003
[7 empty] | 6057 | 8208 | 1659935 | 2019-05-08 19:15 | 2019-05-08 21:15 | 120 | 11kV | 6720 | 56 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 192959 section isolated to replace faulty xarm pole JT-50234 excluded oms 1659935 | May | 2019 | 2019Q4 | 2019 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | OH | Not Veg | 2019-05-08 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 4910.7778
[7 empty] | 6743 | 15500 | 1659958 | 2019-05-09 05:20 | 2019-05-09 06:35 | 75 | 11kV | 113574 | 2070 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 24 tripped on Relays: 24R IOC A and C phase Field EFI's - NIl Cause: Possum on mains in Potts Street beyond AB375 See OMS 1660677 1660678 1659958 | May | 2019 | 2019Q4 | 2019 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2019-05-09 | N | 54.8667 | N | 4 | N | N | 1.1101 | 39.4971 | 82996.5293
[7 empty] | 6266 | 10563 | 1660077 | 2019-05-09 14:15 | 2019-05-09 15:35 | 80 | 11kV | 13120 | 164 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192970 broken 11kv cable pole 8M-30087, SECTION ISOLATED FOR REPAIR Excluded OMS 1660077 | May | 2019 | 2019Q4 | 2019 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2019-05-09 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 9587.709
[7 empty] | 5390 | 683 | 1660139 | 2019-05-09 20:48 | 2019-05-09 21:30 | 42.2167 | 11kV | 2659.65 | 63 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 192974 A Phase DOLF : 31 Amp possum on trans | May | 2019 | 2019Q4 | 2019 | 270:83591 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Not Veg | 2019-05-09 | N | 42.2167 | N | 4 | N | N | 1.1101 | 39.4971 | 1943.5938
[7 empty] | 5858 | 5992 | 1660816 | 2019-05-09 23:36 | 2019-05-10 00:50 | 74 | 11kV | 10806 | 147 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 59 tripped on Relays: A B and C phase IOC and EFI Cause: 11kV feeder fault in section fromn S77334 to S5328. See OMS 1660816 1660817 | May | 2019 | 2019Q4 | 2019 | ZN2635:PA59 | ZN2635:PA59 | ZN02635/000059 | RYDE | UG | Not Veg | 2019-05-09 | N | 73.5102 | N | 4 | N | N | 1.1101 | 39.4971 | 7896.7061
[7 empty] | 6205 | 10047 | 1660147 | 2019-05-10 00:45 | 2019-05-10 01:29 | 44 | 11kV | 28820 | 655 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 21 tripped on Relays: B phase OC EFI. Cause: At PT1887 Chapman Cardinal possum caused flashover - No apparent damage - Supply restored. See OMS 1660147 1660149 | May | 2019 | 2019Q4 | 2019 | ZN965:PA21 | ZN965:PA21 | ZN00965/000021 | HORNSBY | OH | Not Veg | 2019-05-10 | N | 44 | N | 5 | N | N | 1.1101 | 39.4971 | 21060.806
[7 empty] | 6695 | 15161 | 1660157 | 2019-05-10 08:53 | 2019-05-10 11:30 | 157 | 11kV | 21783 | 227 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 62 Tripped on Signals: 11kV Trip Relays: 50TC, 150TN, IOC C phase trip, EFI, Protction Trip Latched. Cause: UG cable fault between S6353 to S6097 to S5736 Abnormal Switching: SW/D closed @ S7392, SW/A Open at S5328 See OMS 1660643 1660644 1660179 1660180 1660204 | May | 2019 | 2019Q4 | 2019 | ZN2635:PA59 | ZN2635:PA59 | ZN02635/000059 | RYDE | UG | Not Veg | 2019-05-10 | N | 95.9604 | N | 5 | N | N | 1.1101 | 39.4971 | 15918.3739
[7 empty] | 7006 | 18579 | 1660156 | 2019-05-10 06:30 | 2019-05-10 12:20 | 350 | 11kV | 350 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 192977 Single phase Broken Live Line Clamp Excluded OMS 1660156 | May | 2019 | 2019Q4 | 2019 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2019-05-10 | N | 350 | N | 5 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 5845 | 5849 | 1660288 | 2019-05-10 18:10 | 2019-05-10 18:45 | 35 | 11kV | 385 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 192983 11kV off pin at CI-30166 Excluded OMS 1660288 | May | 2019 | 2019Q4 | 2019 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-05-10 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 281.3466
[7 empty] | 6631 | 14633 | 1660349 | 2019-05-11 04:45 | 2019-05-11 05:45 | 60 | 11kV | 1620 | 27 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192985 Burnt off 11kV dropper lead between OHM & DOLF. Excluded OMS 1660348, 1663449 | May | 2019 | 2019Q4 | 2019 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2019-05-11 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 5554 | 2901 | 1660366 | 2019-05-11 08:31 | 2019-05-11 12:40 | 249 | 11kV | 226629 | 1828 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192988 1 fault operation Earth Fault, Sensitive Earth Fault OHM down between IU-60210 & IU-6331 OHM down at ABS 6933 Blown tapping at ABS 23146 Sw 8667 faulty would not close Excluded OMS 1660371 1660357 1660366 1660354 | May | 2019 | 2019Q4 | 2019 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | OH | Not Veg | 2019-05-11 | N | 123.9765 | N | 3 | N | N | 1.1101 | 39.4971 | 165613.7888
[7 empty] | 7015 | 18673 | 1660354 | 2019-05-11 06:47 | 2019-05-11 14:02 | 435 | 11kV | 88451 | 922 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 192987 Earth Fault, Sensitive Earth Fault OHM down between IU-60210 & IU-6331 OHM down at ABS 6933 Blown tapping at ABS 23146 Sw 8667 faulty would not close Excluded OMS 1660371 1660357 1660366 1660354 | May | 2019 | 2019Q4 | 2019 | 214:8667 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Not Veg | 2019-05-11 | N | 95.9338 | N | 3 | N | N | 1.1101 | 39.4971 | 64637.3819
[7 empty] | 6885 | 17402 | 1660150 | 2019-05-10 02:00 | 2019-05-11 17:00 | 2340 | 11kV | 127230 | 1280 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.31 tripped on: B Phase O/C Abnormal: DMA 11kV Feeder S3746, S3770 S76809 UG cable fault from S4130 Sw/B to S3746 Sw/A tee S850 tee S879 See 1662517 1662520 1662521 1662522 1662523 1660150 1660151 | May | 2019 | 2019Q4 | 2019 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2019-05-10 | N | 99.3984 | N | 5 | N | N | 1.1101 | 39.4971 | 92975.9314
[7 empty] | 5714 | 4838 | 1660778 | 2019-05-13 17:10 | 2019-05-13 18:00 | 50 | 11kV | 750 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193003 Isolated to repair stranded mains on pole WC-74313 | May | 2019 | 2019Q4 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-05-13 | N | 50 | N | 1 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 6470 | 12981 | 1660856 | 2019-05-14 09:06 | 2019-05-14 10:40 | 94 | 11kV | 18493 | 242 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn1648 Enfield - Pnl.2 tripped on: O/C UG cable fault in front line section of feeder from Pnl.2 to S7769 Sw/A to S2513 Sw/A to S3564 Sw/A Building site on cnr Rickhard & liverpool Rd, workers digging have struck cable. Worker received shock. See 1661083 | May | 2019 | 2019Q4 | 2019 | ZN1648:PA2 | ZN4853:PA27 | ZN04853/000027 | STRATHFIELD | UG | Not Veg | 2019-05-14 | N | 76.4174 | N | 4 | N | N | 1.1101 | 39.4971 | 13514.1389
[7 empty] | 5929 | 6718 | 1660852 | 2019-05-14 09:10 | 2019-05-14 11:00 | 110 | 11kV | 1650 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193011 broken strands on conductor | May | 2019 | 2019Q4 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-05-14 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 5496 | 1933 | 1660956 | 2019-05-14 15:16 | 2019-05-14 17:35 | 139 | 11kV | 94262 | 1257 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 193016 2 fault operation Earth Fault Excluded OMS 1660956 | May | 2019 | 2019Q4 | 2019 | 238:34151 | 238:34136 | ZN00238/034136 | MAITLAND | UG | Not Veg | 2019-05-14 | N | 74.9897 | N | 4 | N | N | 1.1101 | 39.4971 | 68883.8893
[7 empty] | 6989 | 18413 | 1660996 | 2019-05-14 17:35 | 2019-05-14 19:15 | 100 | 11kV | 2500 | 25 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12650 West Gosford Panel 1 Isolated to remove tree from 11kV OH Feeder. Cause: Section of Feeder isolated for lineworker to remove tree from OH mains | May | 2019 | 2019Q4 | 2019 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2019-05-14 | N | 100 | N | 4 | N | N | 1.1101 | 39.4971 | 1826.9263
[7 empty] | 7043 | 19004 | 1661097 | 2019-05-15 12:55 | 2019-05-15 17:15 | 260 | 11kV | 29270 | 371 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser 50247 Blackett Faunce tripped on Signals: 11kV Trip. Relays:OC - SEF trip Cause: Antenna Fallen onto OH mains near the Cnr Tathra and Yandina Rd . Antenna found removed. See OMS 1661609 1661610 1661611 1661612 1661097 | May | 2019 | 2019Q4 | 2019 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Veg | 2019-05-15 | N | 78.8949 | N | 2 | N | N | 1.1101 | 39.4971 | 21389.6527
[7 empty] | 5903 | 6407 | 1661206 | 2019-05-15 21:30 | 2019-05-15 22:26 | 56 | 11kV | 74088 | 1323 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | At Zn847 Hornsby 11kV Panel 7 tripped. Relays: A and C phase IOC, EFI, T1 Fault Check3 Signals: Tx1 Group Earth, Zone Earth, 11kV Trip. possum on PT1470 See OMS 1661206 1661207/210/211/214/208/213 | May | 2019 | 2019Q4 | 2019 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | OH | Not Veg | 2019-05-15 | N | 56 | N | 2 | N | N | 1.1101 | 39.4971 | 54141.3252
[7 empty] | 5967 | 7073 | 1661229 | 2019-05-16 00:01 | 2019-05-16 09:00 | 539 | 11kV | 1078 | 2 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193035 A Phase DOLF : 10 Amp Excluded OMS 1661229 | May | 2019 | 2019Q4 | 2019 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2019-05-16 | N | 539 | N | 3 | N | N | 1.1101 | 39.4971 | 787.7706
[7 empty] | 5479 | 1670 | 1661252 | 2019-05-16 09:32 | 2019-05-16 11:00 | 88 | 11kV | 3168 | 36 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193037 11kV conductor on X arm | May | 2019 | 2019Q4 | 2019 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-05-16 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 2315.081
[7 empty] | 5720 | 4968 | 1661281 | 2019-05-16 11:53 | 2019-05-16 14:20 | 147 | 11kV | 4410 | 30 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193048 11kV main off pin, on xarm pole GU-33123 Excluded oms 1661281 | May | 2019 | 2019Q4 | 2019 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2019-05-16 | N | 147 | N | 3 | N | N | 1.1101 | 39.4971 | 3222.6979
[7 empty] | 6897 | 17568 | 1661645 | 2019-05-17 17:25 | 2019-05-18 03:00 | 575 | 11kV | 46000 | 80 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | S883 Warbrick Park - Pnl.18 isolated by DOp for safety. (Live work pause) Car hit pole PA 05922, pole snapped. | May | 2019 | 2019Q4 | 2019 | ZN874:PA18 | ZN874:PA18 | ZN00874/000018 | CANADA BAY | OH | Not Veg | 2019-05-17 | N | 575 | N | 1 | N | N | 1.1101 | 39.4971 | 33615.4432
[7 empty] | 5643 | 4055 | 1661799 | 2019-05-19 14:06 | 2019-05-19 14:53 | 47 | 11kV | 138621 | 3000 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.9 tripped on: Earth Fault Field EFI @ S8560 UG cable fault between S8560, S5472 and S3006 | May | 2019 | 2019Q4 | 2019 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2019-05-19 | N | 46.207 | N | 1 | N | N | 1.1101 | 39.4971 | 101300.1382
[7 empty] | 6191 | 9944 | 1661852 | 2019-05-20 00:39 | 2019-05-20 02:14 | 95 | 11kV | 133161 | 1415 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Zn9252 Jannali - Pnl.31 tripped on: Earth Fault @ PT9435 Duller St - Roadside HDO operated No cause found - HDO replaced and supply restored. Low volts experienced at PT9401 (DMA PT which has been removed from service and network in permanent LV // until replacement of PT occurs) S9237 Waterview Oyster - A, B & C fuses found blown See 1661917 1661918 1661919 | May | 2019 | 2019Q4 | 2019 | ZN9252:PA31 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2019-05-20 | N | 94.1067 | N | 3 | N | N | 1.1101 | 39.4971 | 97310.1312
[7 empty] | 7052 | 19113 | 1661871 | 2019-05-20 03:04 | 2019-05-20 05:19 | 135 | 11kV | 124605 | 923 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 26 Tripped, Reclosed Tripped and locked out on Relays: A and C phase OC, A phase TImed OC, Timing and Lockout Cause: Tree branch on the Cnr Of Larool Cres and Wareemba Ave See OMS 1661871 1661872 1661874 | May | 2019 | 2019Q4 | 2019 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2019-05-20 | N | 135 | N | 3 | N | N | 1.1101 | 39.4971 | 91057.6588
[7 empty] | 5424 | 1146 | 1661939 | 2019-05-20 09:43 | 2019-05-20 13:20 | 217 | 11kV | 217 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193075 Single phase sub isolated for repair to hv bushings Excluded oms 1661939 | May | 2019 | 2019Q4 | 2019 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2019-05-20 | N | 217 | N | 3 | N | N | 1.1101 | 39.4971 | 158.5772
[7 empty] | 6438 | 12573 | 1662233 | 2019-05-22 02:52 | 2019-05-22 04:25 | 93 | 11kV | 22385 | 261 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S814 Platform St - "Ann John" feeder tripped on: E/L @ Zn2466 Flemington - EFI and Fault check relays UG cable fault between S4022 Sw/B & S7845 Sw/A See 1662940 1662941 | May | 2019 | 2019Q4 | 2019 | ZN2466:PA16 | ZN2466:PA16 | ZN02466/000016 | CUMBERLAND | UG | Not Veg | 2019-05-22 | N | 85.7663 | N | 2 | N | N | 1.1101 | 39.4971 | 16358.2978
[7 empty] | 7042 | 18998 | 1662370 | 2019-05-22 17:15 | 2019-05-22 19:04 | 108.7167 | 11kV | 4131.2333 | 38 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193109 section deenergised for emergency repair of crossarm at pole IR-62418 | May | 2019 | 2019Q4 | 2019 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2019-05-22 | N | 108.7167 | N | 2 | N | N | 1.1101 | 39.4971 | 3018.9835
[7 empty] | 5729 | 5051 | 1662402 | 2019-05-23 08:28 | 2019-05-23 15:46 | 438 | 11kV | 107680 | 982 | HV | 3rd Party Vehicle | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 193117 2 fault operation A & B Phase Instantaneous Overcurrent; Earth Fault cable damaged Dangar St Wickham 79155B/78512A Excluded oms 1662402; 1662434 | May | 2019 | 2019Q4 | 2019 | 204:82699 | 204:82699 | ZN00204/082699 | NEWCASTLE | UG | Not Veg | 2019-05-23 | N | 109.6538 | N | 4 | N | N | 1.1101 | 39.4971 | 78689.368
[7 empty] | 5763 | 5294 | 1662458 | 2019-05-23 11:06 | 2019-05-23 18:10 | 424 | 11kV | 1184 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 193132 Substation DOLF faulty transformer 11kV isolated for replacment Excluded oms 1662458 | May | 2019 | 2019Q4 | 2019 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2019-05-23 | N | 131.5556 | N | 4 | N | N | 1.1101 | 39.4971 | 865.2323
[7 empty] | 6565 | 13997 | 1662496 | 2019-05-23 13:42 | 2019-05-23 19:34 | 352 | 11kV | 8988 | 39 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 193135 Tapping burnt off at pole 8V-60018 Excluded OMS 1662496 | May | 2019 | 2019Q4 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-05-23 | N | 230.4615 | N | 4 | N | N | 1.1101 | 39.4971 | 6568.1653
[7 empty] | 5854 | 5932 | 1662548 | 2019-05-23 17:43 | 2019-05-23 20:05 | 142 | 11kV | 386597 | 3011 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2310 Punchbowl Panel 4 "S4906 Pentland Payten" feeder has tripped Signals: 11kv trip Relays: IOC B & C, Earth fault, EFI Remarks: 11kv UG fault between S35230 Wangee Punchbowl No2 Sw/B to S4012 Hampden Rd Nth Sw/A | May | 2019 | 2019Q4 | 2019 | ZN2310:PA4 | ZN2310:PA4 | ZN02310/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-05-23 | N | 128.3949 | N | 4 | N | N | 1.1101 | 39.4971 | 282513.6849
[7 empty] | 5751 | 5163 | 1662621 | 2019-05-24 18:30 | 2019-05-24 21:15 | 165 | 11kV | 5280 | 32 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At Zn35370 Galston Ex Panel 2 CP2831 feeder from USL751 has been ingterrupted for repairs. Cause: Broken crossarm with CCT twisted together after breaking away from crossarm outside 46 Carters Rd. | May | 2019 | 2019Q4 | 2019 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2019-05-24 | N | 165 | N | 1 | N | N | 1.1101 | 39.4971 | 3858.4683
[7 empty] | 6358 | 11546 | 1662747 | 2019-05-25 12:07 | 2019-05-25 13:18 | 71 | 11kV | 81234 | 1158 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills - Panel 4 labelled LB2929 trippe reclosed tripped an dlocked out on Relays: Earth faul, EFI, Timing and lockout SIgnals: Zone Earth, Group Earth, 11kV Trip Cause: section of 11kV From LB1209 to S6452 (UGOH fault Short circuit). See OMS 1662880 1662881 1662747 1662756 1662748 | May | 2019 | 2019Q4 | 2019 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | Unknown | Unknown | 2019-05-25 | N | 70.1503 | N | 1 | N | N | 1.1101 | 39.4971 | 59363.4112
[7 empty] | 5438 | 1276 | 1662801 | 2019-05-26 03:01 | 2019-05-26 08:15 | 314 | 11kV | 21666 | 69 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | LID 193165 HV lead between switch gear & Tx failed. Excluded oms 1662801 | May | 2019 | 2019Q4 | 2019 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | UG | Not Veg | 2019-05-26 | N | 314 | N | 4 | N | N | 1.1101 | 39.4971 | 15832.8738
[7 empty] | 6294 | 10808 | 1662818 | 2019-05-26 09:46 | 2019-05-26 11:01 | 75 | 11kV | 49543 | 707 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 63 tripped on Relays: A phase feeder protection Relay B phase, EF. Trip B feeder EF, Trip and EFI Signals: 11kV Trip Cause: UG cable fault from S5233 Mars Woodcock SW/D to S2773 Ross Burns SW/A to S46610 Currawond Eloora SW/A See OMS 1662887 16628888 1662818 | May | 2019 | 2019Q4 | 2019 | ZN129:PA63 | ZN129:PA63 | ZN00129/000063 | LANE COVE | UG | Not Veg | 2019-05-26 | N | 70.075 | N | 4 | N | N | 1.1101 | 39.4971 | 36204.5631
[7 empty] | 6790 | 16207 | 1662829 | 2019-05-26 11:41 | 2019-05-26 16:19 | 278 | 11kV | 13914 | 55 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 193167 A Phase SECTION ISOLATED AND ABS 17825 REPAIRED Excluded OMS 1662829 | May | 2019 | 2019Q4 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-05-26 | N | 252.9818 | N | 4 | N | N | 1.1101 | 39.4971 | 10167.9408
[7 empty] | 5443 | 1341 | 1662861 | 2019-05-26 22:44 | 2019-05-26 23:31 | 47 | 11kV | 44509 | 947 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.15 tripped on: A & B phase OC Possum on UGOH adj AB35872 | May | 2019 | 2019Q4 | 2019 | ZN9245:PA15 | ZN9245:PA15 | ZN09245/000015 | SUTHERLAND | OH | Not Veg | 2019-05-26 | N | 47 | N | 4 | N | N | 1.1101 | 39.4971 | 32525.8644
[7 empty] | 5650 | 4113 | 1662867 | 2019-05-27 02:46 | 2019-05-27 04:21 | 95 | 11kV | 171803 | 1852 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT Zn15008 Harbord 11kV Panel 10 tripped on Relays: B and C phase IOC, EFI, Timing and Lockout Signals: 11kV Trip, Zone Earth Cause: Section of 11kV Feeder from S17028 to S17153 is defective See OMS 1663602 1663604 1662867 1662869 | May | 2019 | 2019Q4 | 2019 | ZN15008:PA10 | ZN15008:PA10 | ZN15008/000010 | NORTHERN BEACHES | UG | Not Veg | 2019-05-27 | N | 92.7662 | N | 20 | Y | Y | 1.1101 | 39.4971 | 125548.5651
[7 empty] | 5892 | 6340 | 1664299 | 2019-05-27 13:39 | 2019-05-27 13:49 | 10 | 11kV | 780 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex ZN12690 BERKELEY VALE section of 11kV Panel 24 RE45117 Glenn Valley tripped and reclosed Relays: IOC trip, OC trip Cause: not ascertaiend. Linewoker to patrol | May | 2019 | 2019Q4 | 2019 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2019-05-27 | N | 10 | N | 20 | Y | Y | 1.1101 | 39.4971 | 570.001
[7 empty] | 7172 | 20374 | 1663082 | 2019-05-27 13:37 | 2019-05-27 15:10 | 93 | 11kV | 5013 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex ZN36200 EMPIRE BAY section of 11kV Panel 4 "Bensville" IR63686 Bundaleer Empire Bay 0.2 tripped & locked out Relays: O?C Trip, Lockout Signals: CB47607 open EFI: Cause: not ascertained. DOp has patrolled feeder no cause found See 1664296,7 ex 1663082 | May | 2019 | 2019Q4 | 2019 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2019-05-27 | N | 72.6522 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3663.3525
[7 empty] | 6798 | 16372 | 1663118 | 2019-05-27 14:31 | 2019-05-27 17:30 | 179 | 11kV | 3966 | 24 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12600 LISAROW section of 11kV Panel 9 'Wyoming South' section of 11kV feeder isolated between AB41709 and LB43155 Abnormal: RE47607 Toomeys Rd Open. See separate interruption Cause: tree/branch on OH mains Large tree caused CCT to com edown thru LV mains 11kv fdr isolated between AB41709 and lB43155 to make safe and make repairs PT11670 interrupted at 1640 to make repairs to CCT See 1664311,2 ex 1663118,26,41,57,63,224,67,9 | May | 2019 | 2019Q4 | 2019 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2019-05-27 | N | 165.25 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2898.2358
[7 empty] | 6835 | 16780 | 1663235 | 2019-05-27 14:58 | 2019-05-27 18:14 | 196 | 11kV | 163049 | 875 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193193 A & B Phase Overcurrent BRANCH REMOVED FROM MAINS ADJ ABS 40193 Excluded OMS1663235 | May | 2019 | 2019Q4 | 2019 | 238:34147 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2019-05-27 | N | 186.3417 | N | 20 | Y | Y | 1.1101 | 39.4971 | 119151.4001
[7 empty] | 5733 | 5084 | 1663175 | 2019-05-27 14:55 | 2019-05-27 19:21 | 266 | 11kV | 52390 | 321 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 193192 Section isolated to remove tree & restring mains and services under AP Excluded OMS 1663175. | May | 2019 | 2019Q4 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-05-27 | N | 163.2087 | N | 20 | Y | Y | 1.1101 | 39.4971 | 38285.0668
[7 empty] | 5813 | 5634 | 1662996 | 2019-05-27 13:48 | 2019-05-27 19:39 | 351 | 11kV | 352689 | 3127 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 28 tripped on Signals: 11kV Trip Relays: A and B phase OC, EFI Field EFI's Abnormal Switching: LB280 Open, SW/B Closed @ S4932 See OMS 1664154 1665211 1662996 1663108 1663125 1663329 | May | 2019 | 2019Q4 | 2019 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Veg | 2019-05-27 | N | 112.7883 | N | 20 | Y | Y | 1.1101 | 39.4971 | 257734.7186
[7 empty] | 6578 | 14195 | 1662995 | 2019-05-27 11:42 | 2019-05-27 19:45 | 483 | 11kV | 239259 | 700 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Section of Panel 11 Brookvale CP3282 Alberta Avenue tripped on Overcurrent and SEF Cause: Mains down between LK2337 and Recloser CP17723 Seymour Creek See OMS 1663789 1663687 | May | 2019 | 2019Q4 | 2019 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2019-05-27 | N | 341.7986 | N | 20 | Y | Y | 1.1101 | 39.4971 | 174843.4203
[7 empty] | 6020 | 7839 | 1663130 | 2019-05-27 14:12 | 2019-05-27 20:05 | 353 | 11kV | 64291 | 216 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN14891 WYONG section of 11kV Panel 5 IR62705 Jilliby Durren has tripped IR has SCADA tag never recieved trip or relays RE45016 Dickson did not operate has SCADA Defect Tag RE45017 Whitman has SCADA Defect Tag Cause: Tree/Branch on OH mains Tree/Branch on 11kv OH mains at PT13785 Fuses isolated at PT to customers MSB for Lineworker to repair service wire damaged by tree branch See 1664328,9,30,1 ex 1663130,448 | May | 2019 | 2019Q4 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-05-27 | N | 297.6435 | N | 20 | Y | Y | 1.1101 | 39.4971 | 46981.9665
[7 empty] | 6628 | 14617 | 1663080 | 2019-05-27 12:28 | 2019-05-27 20:15 | 467 | 11kV | 86787 | 1043 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn1290 Leightonfield Panel 12 tripped and reclosed. Relays: A phase timing relay, lock out and EFI Signals: 11kv trip Remarks: weather related. 11kv feeder defective from LB21 to S35969 Bildela Marple Sw/A to N/O LB 189 tee S8370 Goondah Lowana. Pin insulator cracked on 11kv cross arm. | May | 2019 | 2019Q4 | 2019 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-05-27 | N | 83.209 | N | 20 | Y | Y | 1.1101 | 39.4971 | 63421.3798
[7 empty] | 7037 | 18903 | 1663287 | 2019-05-27 15:09 | 2019-05-27 20:20 | 310.7167 | 11kV | 4971.4667 | 16 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193199 A & B Phase DOLF : 20 Amp Shed blown into OHM Risin conductor damaged just beyond LF 2105. CC1: 11-"Despatch to re-issue" | May | 2019 | 2019Q4 | 2019 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2019-05-27 | N | 310.7167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3633.0012
[7 empty] | 6871 | 17174 | 1663072 | 2019-05-27 13:30 | 2019-05-27 20:45 | 435 | 11kV | 62865 | 229 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn15013 Terrey Hills Panel 6 Tripped on Relays: A and B phase IOC and TIme OC. EFI, Fault Checkl, Lockout, reclose Field EFI's Nil Cause: HV OH came down O/S216 Cooyong Rd Terrey Hills @ the time of heavy winds See OMS 1663615 1663616 1663072 1663386 1663387 | May | 2019 | 2019Q4 | 2019 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2019-05-27 | N | 274.5197 | N | 20 | Y | Y | 1.1101 | 39.4971 | 45939.8878
[7 empty] | 6665 | 14952 | 1663187 | 2019-05-27 14:41 | 2019-05-27 21:45 | 424 | 11kV | 848 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 193198 interrupt to repair connection to top of DOLF at sub 14307 Excluded oms 1663187 | May | 2019 | 2019Q4 | 2019 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2019-05-27 | N | 424 | N | 20 | Y | Y | 1.1101 | 39.4971 | 619.6934
[7 empty] | 5910 | 6467 | 1663088 | 2019-05-27 13:45 | 2019-05-27 22:30 | 525 | 11kV | 166450 | 1098 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN12600 LISAROW section of 11kV Panel 9 'Wyoming South' RE47607 Toomeys Rd has tripped Relays: OC trip and LO Abnormal: LB43155 open, AB41711 closed. See separate interrutpion on section of panel 9 fdr Cause: tree/branch brought down oh Outside 98 Blackbutt tree has brought down 11kv mains AP issued to LW to make repairs See 1664303,4 ex 1663088,393 | May | 2019 | 2019Q4 | 2019 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2019-05-27 | N | 151.5938 | N | 20 | Y | Y | 1.1101 | 39.4971 | 121636.7506
[7 empty] | 5474 | 1650 | 1663435 | 2019-05-27 21:55 | 2019-05-27 22:40 | 45 | 11kV | 630 | 14 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193203 Tree on OHM pole KS-40053 | May | 2019 | 2019Q4 | 2019 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2019-05-27 | N | 45 | N | 20 | Y | Y | 1.1101 | 39.4971 | 460.3854
[7 empty] | 6556 | 13868 | 1663415 | 2019-05-27 18:58 | 2019-05-27 23:10 | 252 | 11kV | 504 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 193206 interrupt to repair loose neutral connection at sub Excluded oms 1663415 | May | 2019 | 2019Q4 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-05-27 | N | 252 | N | 20 | Y | Y | 1.1101 | 39.4971 | 368.3083
[7 empty] | 5795 | 5507 | 1663260 | 2019-05-27 15:05 | 2019-05-27 23:35 | 510 | 11kV | 17998 | 123 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 193188 Broken mains near sub 7840 SECTION ISOLATED FOR REPAIR.11KV LINKS 13419 OPENED. FDR RESTORED TO LINKS | May | 2019 | 2019Q4 | 2019 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2019-05-27 | N | 146.3252 | N | 20 | Y | Y | 1.1101 | 39.4971 | 13152.4075
[7 empty] | 6125 | 9156 | 1663431 | 2019-05-27 18:24 | 2019-05-28 00:05 | 341 | 11kV | 160396 | 1542 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex ZN12570 AVOCA section of 11kV Panel 24 RE77908 Copacabanna Koorabel tripped and locked out Relays: O/C trip On trying back from LB42041 IR77909 Del Mar Pueblo tripped and locked out (Set on 1 shot trying back feeder) Relays: O/C trip @ 21:09 Cause: bond Fault 1: Bond burnt off near LB42022 Fault 2: Possum removed off O/H near LB43148, no apparent damage See 1664346,7 ex 1663367,78,401,6,8,31 | May | 2019 | 2019Q4 | 2019 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2019-05-27 | N | 104.0182 | N | 20 | Y | Y | 1.1101 | 39.4971 | 117212.6659
[7 empty] | 5815 | 5647 | 1663129 | 2019-05-27 17:55 | 2019-05-28 00:32 | 397 | 11kV | 123817 | 385 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN14891 WYONG section of 11kV Panel 12 IR50630 Yarramalong Chandlers 0.1 open at 1755 to make site safe IR48813 Yarramalong Boyds 3.7 is defective with bypass closed IR44753 Bunning Creek has SCADA Defect & in RTU fail no operation or relays to record Cause: weather related PT11505 11kv fdr found on ground by lineworker IR50630 open to de-energise fdr due to 11kv fdr on ground with no protection operation at IR44753 has SCADA defect See 1664340,1 ex 1663129,443 | May | 2019 | 2019Q4 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-05-27 | N | 321.6026 | N | 20 | Y | Y | 1.1101 | 39.4971 | 90481.8116
[7 empty] | 6161 | 9499 | 1663451 | 2019-05-28 02:27 | 2019-05-28 03:30 | 63 | 11kV | 5670 | 90 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 193207 Interrupted to remove tree | May | 2019 | 2019Q4 | 2019 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2019-05-28 | N | 63 | N | 7 | N | N | 1.1101 | 39.4971 | 4143.4688
[7 empty] | 7104 | 19601 | 1663427 | 2019-05-27 21:11 | 2019-05-28 05:20 | 488.6167 | 11kV | 10260.95 | 21 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193208 A & C Phase DOLF : 10 Amp tree debris removed on line patrol - no damage | May | 2019 | 2019Q4 | 2019 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-05-27 | N | 488.6167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 7498.3996
[7 empty] | 6771 | 15836 | 1663555 | 2019-05-28 10:27 | 2019-05-28 11:15 | 48 | 11kV | 768 | 16 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 193216 B Phase LLC broken out of DOLF Excluded OMS 1663555 | May | 2019 | 2019Q4 | 2019 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2019-05-28 | N | 48 | N | 7 | N | N | 1.1101 | 39.4971 | 561.2317
[7 empty] | 5417 | 1067 | 1663508 | 2019-05-28 10:27 | 2019-05-28 11:19 | 52 | 11kV | 45500 | 875 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193212 Trip & Reclose 1 fault operation Earth fault Stick on Mains Excluded OMS 1663508 | May | 2019 | 2019Q4 | 2019 | 238:34147 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2019-05-28 | N | 52 | N | 7 | N | N | 1.1101 | 39.4971 | 33250.058
[7 empty] | 7171 | 20335 | 1663565 | 2019-05-28 09:42 | 2019-05-28 15:15 | 333 | 11kV | 2997 | 9 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Wind Strong | N | Ex ZN14891 WYONG section of 11kV Panel 12 'Yarramalong' Auto link 44780 Stinsons Lane - opened for safety Cause: Interrupted for safety reasons 'Live' work ban | May | 2019 | 2019Q4 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | Unknown | Unknown | 2019-05-28 | N | 333 | N | 7 | N | N | 1.1101 | 39.4971 | 2190.1192
[7 empty] | 6814 | 16540 | 1663452 | 2019-05-28 12:55 | 2019-05-28 16:00 | 185 | 11kV | 2405 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | Ex ZN14891 WYONG section of 11kV Panel 5 RE45016 Dickson opened for safety Abnornal: Closed @ LB44532, Open @ USL43590 Cause: OH resting on cross arm Interrupt for safety/repair @ 1255 AP & CTW issued @ 1310 First centre 1530 last 1600 See 1664337 ex 1663452,84 | May | 2019 | 2019Q4 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-05-28 | N | 185 | N | 7 | N | N | 1.1101 | 39.4971 | 1757.5031
[7 empty] | 6668 | 14974 | 1663749 | 2019-05-28 18:17 | 2019-05-28 18:43 | 26 | 11kV | 22438 | 863 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.19 tripped, reclosed and locked out on: B & C phase IOC Abnormal: Open Bonds adjacent LB35051 - S9980 Sw/A closed Possum found at base of UGOH corner Kingswood Rd and Geneva place. | May | 2019 | 2019Q4 | 2019 | ZN9245:PA19 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2019-05-28 | N | 26 | N | 7 | N | N | 1.1101 | 39.4971 | 16397.0286
[7 empty] | 5814 | 5645 | 1663745 | 2019-05-28 18:04 | 2019-05-28 22:00 | 236 | 11kV | 43984 | 1452 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193232 B & C Phase Overcurrent tree fallen on mains pole HR-62218 Section isolated for repair. Excluded oms 1663745 | May | 2019 | 2019Q4 | 2019 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2019-05-28 | N | 30.292 | N | 7 | N | N | 1.1101 | 39.4971 | 32142.2099
[7 empty] | 6580 | 14224 | 1663927 | 2019-05-29 12:17 | 2019-05-29 13:16 | 59 | 11kV | 35931 | 609 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex ZN12580 ERINA section of 11kV Panel 16 RE46673 Terrigal Penrose tripped & locked out on O/C Abnormal: AB42530 open & defective, LB61009 closed Remarks: Lots of branches on the ground. weather related | May | 2019 | 2019Q4 | 2019 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2019-05-29 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 26257.315
[7 empty] | 6933 | 17878 | 1663912 | 2019-05-29 11:53 | 2019-05-29 13:53 | 120 | 11kV | 16967 | 146 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 193264 2 fault operations Overcurrent; Sensitive Earth fault First trip on OC 2nd on SEF. WIre off pin. | May | 2019 | 2019Q4 | 2019 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2019-05-29 | N | 116.2123 | N | 6 | N | N | 1.1101 | 39.4971 | 12398.9832
[7 empty] | 7169 | 20303 | 1663855 | 2019-05-29 10:24 | 2019-05-29 14:02 | 218 | 11kV | 116264 | 1514 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193255 2 fault operations single phase Earth Fault Tree branch onto Mains between poles GS-51704 & GS-51703. HV into LV, Despatch organised IIs. Excluded OMS 1663855 | May | 2019 | 2019Q4 | 2019 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2019-05-29 | N | 76.7926 | N | 6 | N | N | 1.1101 | 39.4971 | 84962.302
[7 empty] | 6700 | 15193 | 1664034 | 2019-05-29 15:51 | 2019-05-29 17:44 | 113 | 11kV | 12543 | 111 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex ZN14891 WYONG section of 11kV Panel 12 'Cedar Northcott' RE44753 Bunning Creek tripped & locked out (note re44753 SCADA defect previously reported) Cause: not ascertained. Debris from trees all over area See 1664040 ex 1664034 CC1: 22-"Refer to SOp" | May | 2019 | 2019Q4 | 2019 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2019-05-29 | N | 113 | N | 6 | N | N | 1.1101 | 39.4971 | 9166.0544
[7 empty] | 6581 | 14257 | 1664082 | 2019-05-29 17:08 | 2019-05-29 19:00 | 112 | 11kV | 336 | 3 | HV | Wind Blown Debris | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 193273 B & C Phase DOLF : 10 Amps see related jobs Excluded OMS 1664082 | May | 2019 | 2019Q4 | 2019 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2019-05-29 | N | 112 | N | 6 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 6689 | 15125 | 1664131 | 2019-05-30 06:43 | 2019-05-30 10:00 | 197 | 11kV | 1182 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193276 B & C Phase Line DOLF Excluded OMS 1664131 | May | 2019 | 2019Q4 | 2019 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2019-05-30 | N | 197 | N | 4 | N | N | 1.1101 | 39.4971 | 863.7707
[7 empty] | 7047 | 19072 | 1664177 | 2019-05-30 09:31 | 2019-05-30 10:41 | 70 | 11kV | 91073 | 1321 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn690 Campsie 11kv Panel '33', labelled 'S.77782 Canterbury Elizabeth', tripped on: Relays: A phase OC, Earth fault, EFI Signals: Zone earth, Tx4 Group Earth, 11kv trip Remarks: UG fault. Section of 11kv feeder defective from S6454 Elizabeth Cant Sw/B to S3428 Kent York Sw/A | May | 2019 | 2019Q4 | 2019 | ZN690:PA33 | ZN690:PA33 | ZN00690/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-05-30 | N | 68.9425 | N | 4 | N | N | 1.1101 | 39.4971 | 66553.4622
[7 empty] | 5475 | 1652 | 1664166 | 2019-05-30 09:07 | 2019-05-30 12:55 | 228 | 11kV | 228 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193281 A Phase Live Line dropper lead broken Excluded OMS 1664166 | May | 2019 | 2019Q4 | 2019 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2019-05-30 | N | 228 | N | 4 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 6725 | 15338 | 1664907 | 2019-05-29 12:18 | 2019-05-30 14:50 | 1592 | 11kV | 19400 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 11 'Somersby' Relays Panel 11 EFI, Protection B fault Flag RE44938 Somersby tripped & locked out on EF & IOC Cause: OH down 1 bay of 11kv down beyond PT11461 See 1664907,8 | May | 2019 | 2019Q4 | 2019 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2019-05-29 | N | 1212.5 | N | 6 | N | N | 1.1101 | 39.4971 | 14176.9478
[7 empty] | 5824 | 5698 | 1664094 | 2019-05-30 13:44 | 2019-05-30 15:50 | 126 | 11kV | 6930 | 55 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | LID 193295 Oil leak from transformer C phase HV bushing Replace transformer Excluded OMS 1664094 | May | 2019 | 2019Q4 | 2019 | 228:7490 | 228:85413 | ZN00228/085413 | NEWCASTLE | OH | Not Veg | 2019-05-30 | N | 126 | N | 4 | N | N | 1.1101 | 39.4971 | 5064.2396
[7 empty] | 5556 | 2965 | 1664374 | 2019-05-31 01:01 | 2019-05-31 02:22 | 81 | 11kV | 190386 | 2618 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN15006 Dee Why West 11kV Feeder Panel 9 tripped on Relays: B phase OC. EFI and Fault Check. Cause: UG csable fault from S16989 to S17015 See OMS 1665097 1665098 1664374 | May | 2019 | 2019Q4 | 2019 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2019-05-31 | N | 72.7219 | N | 4 | N | N | 1.1101 | 39.4971 | 139128.4734
[7 empty] | 5805 | 5578 | 1664433 | 2019-05-31 09:55 | 2019-05-31 11:09 | 74 | 11kV | 153106 | 2069 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 24 tripped under fault Protection relay flags at Top Ryde: Panel 24 R Earth Fault Trip, Fault Check, EFI Signals: TX3 Group Earth Protection Trip. Cause: Sydney Water Contractors HIt 11kV cable outside 19 Morrisson Rd Gladesville See OMS 1664433 1664451 1664468 | May | 2019 | 2019Q4 | 2019 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | UG | Not Veg | 2019-05-31 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 111885.3489
[7 empty] | 6800 | 16375 | 1664434 | 2019-05-31 09:59 | 2019-05-31 14:30 | 271 | 11kV | 4878 | 18 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S6879 Miller Metroplaza No1 were found to have operated due to low gas pressure. Cause: Low SF Gas on the NO2 RMCB at S6879 | May | 2019 | 2019Q4 | 2019 | ZN35400:PA56 | ZN35400:PA56 | ZN35400/000056 | NORTH SYDNEY | Unknown | Unknown | 2019-05-31 | N | 271 | N | 4 | N | N | 1.1101 | 39.4971 | 3564.6985
[7 empty] | 6352 | 11449 | 1664430 | 2019-05-31 09:47 | 2019-06-01 | 853 | 11kV | 286398 | 2012 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12650 WEST GOSFORD 11kV CB Panel 12 's11973 fielder Hely etc' fdr tripped, reclosed, tripped & locked out on Relays: O/C, EF, Time delay, EF Check, 51N, 150TN Signals: 11kv trip Abnormal: AB40725 Open & Defective AB40724 closed Cause: UG cable damaged by contractor. Cut through conduits outside 90 Faunce st Adj S18658 See 1664929,30,1,2,3,4 Ex 1664430,64,5,84,5 | May | 2019 | 2019Q4 | 2019 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | UG | Not Veg | 2019-05-31 | N | 142.3449 | N | 4 | N | N | 1.1101 | 39.4971 | 209291.2111
[7 empty] | 5887 | 6279 | 1664581 | 2019-06-01 03:29 | 2019-06-01 04:06 | 37 | 11kV | 91686 | 2478 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT ZN36300 Balgowlah North 11kV Panel 3 Labelled S17119 Jackson White Tripped on Relays: A B and C phase IOC and EFI Signals: Tx12 Group Earth Abnormal Switching: SW/A at S16453, LB47128. Cause: Possum at LB61276 - Inspection Required Duing Daylight hours for possible damage See OMS 1665114 1664581 1664582 | June | 2019 | 2019Q4 | 2019 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2019-06-01 | N | 37 | N | 4 | N | N | 1.1101 | 39.4971 | 67001.4245
[7 empty] | 6297 | 10841 | 1664652 | 2019-06-01 12:26 | 2019-06-01 13:37 | 71 | 11kV | 103911 | 1524 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12570 AVOCA 11kV CB Panel 37 'Avoca Beach' tripped on: Relays: 50TBC instant OC B & C phase, 150TN instant earth fault, EFI Signals: 11kv trip EFI: Nil Cause: not ascertained. Feeder patrolled by DOps See 1664963,4 ex 1664652 | June | 2019 | 2019Q4 | 2019 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2019-06-01 | N | 68.1831 | N | 4 | N | N | 1.1101 | 39.4971 | 75935.0939
[7 empty] | 6727 | 15349 | 1664656 | 2019-06-01 12:54 | 2019-06-01 15:41 | 167 | 11kV | 214898 | 1347 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | U/G Cable | Unplanned | No Weather Impact | N | At Zn847 Hornsby Panel 15 tripped on Relays: 11kV Trip, Zone earth, TX1 Group Earth, TX1 Fault Check. Signals: Earth Fault, EFI, Fauylt Check, OC Relay Trip Cause: The 11kVC UG cable was damaged by and excavator outside 26 Derby Rd Hornsby - Electrically between ZN847 PA15 amd S4722 See OMS 1665101 1664656 | June | 2019 | 2019Q4 | 2019 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | UG | Not Veg | 2019-06-01 | N | 159.5382 | N | 4 | N | N | 1.1101 | 39.4971 | 157041.12
[7 empty] | 5410 | 959 | 1664696 | 2019-06-01 17:49 | 2019-06-01 19:20 | 90.9333 | 11kV | 1091.2 | 12 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 193320 A & B phase DOLF : 20 Amp removed tree branch from OHM. | June | 2019 | 2019Q4 | 2019 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2019-06-01 | N | 90.9333 | N | 4 | N | N | 1.1101 | 39.4971 | 797.4168
[7 empty] | 5766 | 5322 | 1664815 | 2019-06-03 05:06 | 2019-06-03 07:57 | 171 | 11kV | 7695 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193327 C Phase DOLF : 20 Amp Excluded OMS 1664815 | June | 2019 | 2019Q4 | 2019 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Veg | 2019-06-03 | N | 171 | N | 4 | N | N | 1.1101 | 39.4971 | 5623.279
[7 empty] | 6965 | 18180 | 1664870 | 2019-06-03 10:01 | 2019-06-03 11:15 | 74 | 11kV | 59676 | 969 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.39 tripped on: Earth Leakage Contractor struck cable outside 655 King St. Feeder between Zn2568 Pnl.39, S8141 Sw/A & S3171 Sw/A See 1665077 | June | 2019 | 2019Q4 | 2019 | ZN2568:PA39 | ZN2568:PA39 | ZN02568/000039 | INNER WEST | UG | Not Veg | 2019-06-03 | N | 61.5851 | N | 4 | N | N | 1.1101 | 39.4971 | 43609.4607
[7 empty] | 6883 | 17392 | 1664816 | 2019-06-03 09:50 | 2019-06-03 12:00 | 130 | 11kV | 130 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193331 line inspection found 11kV off pin pole Excluded oms 1664816 | June | 2019 | 2019Q4 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-06-03 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 5461 | 1478 | 1664939 | 2019-06-03 12:14 | 2019-06-03 13:32 | 78 | 11kV | 88206 | 1297 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 24 Tripped on Relays: B and C phase OC and Lockout tree branch on 11kV OH mains on tee off to PT2271 and PTY2178 | June | 2019 | 2019Q4 | 2019 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2019-06-03 | N | 68.0077 | N | 4 | N | N | 1.1101 | 39.4971 | 64458.3432
[7 empty] | 7088 | 19486 | 1665093 | 2019-06-04 07:31 | 2019-06-04 08:27 | 56 | 11kV | 59884 | 1250 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 193334 C Phase Earth Fault cockatoos flashed across ohm at pole IU-32667. Sw 80341 did not reclose tried to close from control room, would not close (faulty) Excluded oms 1665093,1665094,1665096,1665099 | June | 2019 | 2019Q4 | 2019 | 224:80341 | 224:80341 | ZN00224/080341 | LAKE MACQUARIE | OH | Not Veg | 2019-06-04 | N | 47.9072 | N | 12 | N | N | 1.1101 | 39.4971 | 43761.4609
[7 empty] | 6457 | 12735 | 1665072 | 2019-06-04 06:21 | 2019-06-04 08:40 | 139 | 11kV | 7096 | 196 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn847 Hornsby - REC420 Reynolds Crosslands tripped & reclosed on: IOC REC705 Knights Chadd tripped and locked out on Earth Fault Cause not ascertained. See 1665625 1665626 | June | 2019 | 2019Q4 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-06-04 | N | 36.2041 | N | 12 | N | N | 1.1101 | 39.4971 | 5185.5475
[7 empty] | 6500 | 13288 | 1665121 | 2019-06-04 08:38 | 2019-06-04 10:57 | 139 | 11kV | 195542 | 1600 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN12570 AVOCA 11kV CB Panel 22 'Davies Wilima' fdr tripped on Relays: B & C phase IOC, Lockout Signals: 11kv trip EFI: Nil Cause: not ascertained See 1665765,6,7,8 Ex 1665121 | June | 2019 | 2019Q4 | 2019 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2019-06-04 | N | 122.2138 | N | 12 | N | N | 1.1101 | 39.4971 | 142896.3261
[7 empty] | 5604 | 3582 | 1665186 | 2019-06-04 10:37 | 2019-06-04 12:05 | 88 | 11kV | 71368 | 811 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | REC35756 Bundeena tripped on: O/C Weather related. Bond burnt off load side of LB35911 | June | 2019 | 2019Q4 | 2019 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2019-06-04 | N | 88 | N | 12 | N | N | 1.1101 | 39.4971 | 52153.6294
[7 empty] | 6827 | 16656 | 1665104 | 2019-06-04 08:03 | 2019-06-04 12:55 | 292 | 11kV | 111151 | 1381 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN36200 EMPIRE BAY 11kV CB Panel 8 'Poole Belrose' fdr tripped on Relays: B & C Phase O/C, SEF, Recloser, Lockout Signals: 11kv trip EFI: Nil Cause: tree/branch brought down OH 11kv between LB48645 and LB48657 See 1665749,50 Ex 1665104 | June | 2019 | 2019Q4 | 2019 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2019-06-04 | N | 80.4859 | N | 12 | N | N | 1.1101 | 39.4971 | 81225.8724
[7 empty] | 6607 | 14403 | 1665202 | 2019-06-04 11:03 | 2019-06-04 15:03 | 240 | 11kV | 9333 | 113 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193343 11kV mains down on ground Excluded OMS 1665202 | June | 2019 | 2019Q4 | 2019 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2019-06-04 | N | 82.5929 | N | 12 | N | N | 1.1101 | 39.4971 | 6820.2811
[7 empty] | 6855 | 16968 | 1665339 | 2019-06-04 14:09 | 2019-06-04 17:25 | 196 | 11kV | 4704 | 24 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex ZN12640 UMINA section of 11kV Panel 13 'Umina Aux No.1' the roadside 16Amp HDO blew PT12574 PATONGA BAY 0.6 Tree branch contact other. Tree near TX See 1655799 ex 1655339 | June | 2019 | 2019Q4 | 2019 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2019-06-04 | N | 196 | N | 12 | N | N | 1.1101 | 39.4971 | 3437.5445
[7 empty] | 7023 | 18724 | 1665455 | 2019-06-04 17:24 | 2019-06-04 18:17 | 53 | 11kV | 74836 | 1412 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex ZN12570 AVOCA section of 11kV Panel 22 AB44517 footpath side bond burnt off See 1665816 ex 1665455 | June | 2019 | 2019Q4 | 2019 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2019-06-04 | N | 53 | N | 12 | N | N | 1.1101 | 39.4971 | 54687.9415
[7 empty] | 6892 | 17452 | 1665223 | 2019-06-04 11:32 | 2019-06-04 18:26 | 414 | 11kV | 95824 | 700 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 193344 Broken cross arm pole LQ-30124 interrupt to repair x-arm pole LQ-30124 Excluded OMS 1665223 | June | 2019 | 2019Q4 | 2019 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2019-06-04 | N | 136.8914 | N | 12 | N | N | 1.1101 | 39.4971 | 70025.3529
[7 empty] | 6015 | 7795 | 1665423 | 2019-06-04 16:17 | 2019-06-04 19:10 | 173 | 11kV | 136567 | 831 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Wind Storm | N | Ex ZN12620 NORAVILLE section of 11kV Panel 11 'Norah Head' RE45054 Noraville tripped, reclosed, tripped and locked out Cause: Load Side links at RE45054 Noraville flashed over See 1665805,6,7 ex 1665423,6,7,30,44 | June | 2019 | 2019Q4 | 2019 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2019-06-04 | N | 164.3406 | N | 12 | N | N | 1.1101 | 39.4971 | 99799.1356
[7 empty] | 6405 | 12125 | 1665523 | 2019-06-04 19:44 | 2019-06-04 20:21 | 37 | 11kV | 22940 | 620 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12610 LONG JETTY section of 11kV Panel 2 'Bateu Bay' IR62165 Point Larkin tripped Cause: tree/branch on oh mains on USL41757 See 1665523 ex 1665524,6 | June | 2019 | 2019Q4 | 2019 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Veg | 2019-06-04 | N | 37 | N | 12 | N | N | 1.1101 | 39.4971 | 16763.8754
[7 empty] | 6203 | 10041 | 1665501 | 2019-06-04 22:30 | 2019-06-05 00:45 | 135 | 11kV | 1485 | 11 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 193345 interrupt to remove tree from OHM at sub 54050 Exccluded oms 1665501 | June | 2019 | 2019Q4 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-06-04 | N | 135 | N | 12 | N | N | 1.1101 | 39.4971 | 1085.1942
[7 empty] | 6243 | 10382 | 1665542 | 2019-06-05 00:30 | 2019-06-05 08:33 | 483 | 11kV | 9114 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 193346 33kV pin explosion at pole OS-10024 damaged LV ABC. Section of 11kV isolated to do repairs on LV from sub 63562. Excluded OMS 1665580 & 1665542 | June | 2019 | 2019Q4 | 2019 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2019-06-05 | N | 414.2727 | N | 4 | N | N | 1.1101 | 39.4971 | 6660.2424
[7 empty] | 6657 | 14896 | 1665571 | 2019-06-05 02:10 | 2019-06-05 10:05 | 475 | 11kV | 153620 | 1882 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 193348 3 fault operations B Phase Blown L/A at pole NB-77019. Excluded OMS 1665571, 1665577 | June | 2019 | 2019Q4 | 2019 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2019-06-05 | N | 81.6259 | N | 4 | N | N | 1.1101 | 39.4971 | 112260.965
[7 empty] | 5570 | 3170 | 1665666 | 2019-06-05 09:58 | 2019-06-05 11:46 | 108 | 11kV | 177870 | 1703 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill - Pnl.2 tripped, reclosed and locked out on: C phase IOC Field EFIs: S16011 Tree branch on mains at PT15164. | June | 2019 | 2019Q4 | 2019 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Veg | 2019-06-05 | N | 104.4451 | N | 4 | N | N | 1.1101 | 39.4971 | 129982.1497
[7 empty] | 6204 | 10044 | 1665707 | 2019-06-05 11:32 | 2019-06-05 15:04 | 212 | 11kV | 158856 | 753 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 193358 1 fault operation Sensitive Earth Fault Tree resting against mains at pole MN-55435. Cleared with operating stick Excluded OMS 1665707 & 745 & 769 etc | June | 2019 | 2019Q4 | 2019 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-06-05 | N | 210.9641 | N | 4 | N | N | 1.1101 | 39.4971 | 116087.2793
[7 empty] | 5429 | 1173 | 1670856 | 2019-06-06 11:00 | 2019-06-06 13:19 | 139 | 33kV Distribution | 139 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | No Weather Impact | N | LID 193365 LOW SF6 Filled under AP | June | 2019 | 2019Q4 | 2019 |  |  |  | NEWCASTLE | Unknown | Unknown | 2019-06-06 | N | 139 | N | 2 | N | N | 1.1101 | 39.4971 | 101.5771
[7 empty] | 6911 | 17680 | 1666098 | 2019-06-06 14:49 | 2019-06-06 17:18 | 149 | 11kV | 179295 | 1256 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.6 tripped on: Earth Fault UG cabel fault between S36221 to S3332 to S5806 See 1667127 1667128 | June | 2019 | 2019Q4 | 2019 | ZN35600:PA6 | ZN35600:PA6 | ZN35600/000006 | RANDWICK | UG | Not Veg | 2019-06-06 | N | 142.7508 | N | 2 | N | N | 1.1101 | 39.4971 | 131023.4977
[7 empty] | 6455 | 12722 | 1666295 | 2019-06-07 13:01 | 2019-06-07 14:10 | 69.45 | 11kV | 3264.15 | 47 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 193397 Broken King Bolt on Pole 4H-70052 | June | 2019 | 2019Q4 | 2019 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-06-07 | N | 69.45 | N | 6 | N | N | 1.1101 | 39.4971 | 2385.3445
[7 empty] | 6472 | 13006 | 1666338 | 2019-06-07 15:26 | 2019-06-07 16:10 | 44 | 11kV | 308 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193400 Tree blown onto mains REEDY CREEK 3000 WYBONG RD DEAN STARKEY (HELICOPTER PATROLS) TREE ON MAINS - 11KV ON GROUND IDENTIFIED FROM AERIAL PATROLS | June | 2019 | 2019Q4 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2019-06-07 | N | 44 | N | 6 | N | N | 1.1101 | 39.4971 | 225.0773
[7 empty] | 6242 | 10359 | 1666311 | 2019-06-07 14:35 | 2019-06-07 16:50 | 135 | 11kV | 4995 | 37 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 193403 DAVID BOND - David reports he came across UG cable from cabinet severed and exposed. Reports wire is live. Blew one* of the buckets on excavator and also seen sparking. Also refer to previous Event OM S 1666403 | June | 2019 | 2019Q4 | 2019 | 202:34240 | 202:34240 | ZN00202/034240 | NEWCASTLE | UG | Not Veg | 2019-06-07 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 3650.1987
[7 empty] | 5522 | 2337 | 1666335 | 2019-06-07 13:51 | 2019-06-07 17:23 | 212 | 11kV | 364 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 193402 Broken LL lead sub 27633 | June | 2019 | 2019Q4 | 2019 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-06-07 | N | 72.8 | N | 6 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 6292 | 10792 | 1666425 | 2019-06-07 19:59 | 2019-06-07 20:42 | 43 | 11kV | 103802 | 2414 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zb10999 Jogarah - Pnl.36 tripped on: B & Cphase IOC Car hit pole outside 2 Norman St, Allwah | June | 2019 | 2019Q4 | 2019 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | OH | Not Veg | 2019-06-07 | N | 43 | N | 6 | N | N | 1.1101 | 39.4971 | 75855.44
[7 empty] | 5772 | 5355 | 1666270 | 2019-06-07 08:55 | 2019-06-08 09:55 | 1500 | 11kV | 190500 | 127 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S5085 Clinton Dianne - Vehicle HIt kiosk. S5085 Decommissioned PT77705 Taking custimers S5085 + MG Note: amended start time to reflect first customer NS call | June | 2019 | 2019Q4 | 2019 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Not Veg | 2019-06-07 | N | 1500 | N | 6 | N | N | 1.1101 | 39.4971 | 139211.7812
[7 empty] | 5431 | 1179 | 1666573 | 2019-06-08 21:07 | 2019-06-09 12:30 | 923 | 11kV | 117221 | 127 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S5085 Clinton Dianne MG tripped off due to unbalanced load (Previously vehicle hit kiosk S5085 - Decommissioned | June | 2019 | 2019Q4 | 2019 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | Unknown | Not Veg | 2019-06-08 | N | 923 | N | 1 | N | N | 1.1101 | 39.4971 | 85661.6494
[7 empty] | 5784 | 5448 | 1666606 | 2019-06-09 14:50 | 2019-06-09 16:00 | 70 | 11kV | 70 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193410 Tree on service, sub isolated to make repairs Found single phase SW low across property. Tree branch has brought wire down. Removed branch. Sw is off TX pole 22810. LV Tx fuse has come away from pole also. SF has come away from private pole also. Cust has supply. Unable to retension SW and maintain safe clearances at TX. Please isolate TX and replace SW ASAP | June | 2019 | 2019Q4 | 2019 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-06-09 | N | 70 | N | 1 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 6355 | 11516 | 1666670 | 2019-06-10 06:52 | 2019-06-11 00:10 | 1038 | 11kV | 127037 | 1279 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood Zn - Pnl.31 tripped on: 3 Phase O/C, Earth Fault , EFI Field EFIS: all down to S4130 @ S3746 Wereroona Cemetary No.2 - Sw/A Open and Sw/D auto closed. UG cabel fault between S4130 Sw/B and S3746 Sw/A tee S850 & S879 (N//) See 1667051 1667052 | June | 2019 | 2019Q4 | 2019 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2019-06-10 | N | 99.3253 | N | 1 | N | N | 1.1101 | 39.4971 | 92834.8926
[7 empty] | 7173 | 20376 | 1666800 | 2019-06-11 13:10 | 2019-06-11 13:23 | 13 | 11kV | 11492 | 884 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn10995 Riverwood - Pnl.7 - loss of supply beyond S10179 Broad Arrow Bryant to AB31012 On restoration of planned worked, load relief switching was not pinned on DNMS, causing a loss of supply when attempting to restore abnormal switching. | June | 2019 | 2019Q4 | 2019 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | Unknown | Unknown | 2019-06-11 | N | 13 | N | 2 | N | N | 1.1101 | 39.4971 | 8398.0146
[7 empty] | 5608 | 3615 | 1666879 | 2019-06-11 12:52 | 2019-06-11 13:37 | 45 | 11kV | 1212 | 28 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193431 LIDAR Defect. Faulty Insulator P.5G30002 | June | 2019 | 2019Q4 | 2019 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2019-06-11 | N | 43.2857 | N | 2 | N | N | 1.1101 | 39.4971 | 885.6939
[7 empty] | 6225 | 10215 | 1666987 | 2019-06-12 02:37 | 2019-06-12 05:27 | 169.95 | 11kV | 11556.6 | 68 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 193438 Section isolated for repairs, also refer previous event LID 193436 - OMS 1667084, T&R UNABLE TO CONFIRM IF HV INTO LV. LINESMAN WILL INSPECT UNDER ACCESS FROM AN EWP. IF HV INTO LV CUSTOMER INSPECTIONS ARE REQUIRED, DAY WORK EMSO WILL ATTEND. STOLEN TIPPER TRUCK HIT AG POLE HR-61162. BROKEN 11KV CROSS ARM AND SL HEAD. DR1 FORM COMPLETED BY EMSO. DOPS AND ON CALL STAFF NOW ON SITE. Reported by NSWPOL CADD 615171 | June | 2019 | 2019Q4 | 2019 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2019-06-12 | N | 169.95 | N | 3 | N | N | 1.1101 | 39.4971 | 8445.2224
[7 empty] | 5983 | 7286 | 1667001 | 2019-06-12 08:07 | 2019-06-12 09:44 | 97 | 11kV | 20858 | 234 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.26 tripped. Field EFIs: S78731 S78631 S48512 UG cable by excavator at 5 Uhrig Rd, Flemington See 1667237 1667238 | June | 2019 | 2019Q4 | 2019 | ZN2466:PA26 | ZN2466:PA18 | ZN02466/000018 | PARRAMATTA | UG | Not Veg | 2019-06-12 | N | 89.1368 | N | 3 | N | N | 1.1101 | 39.4971 | 15242.4112
[7 empty] | 5826 | 5711 | 1666994 | 2019-06-12 06:48 | 2019-06-12 14:25 | 457 | 11kV | 457 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 193453 C phase, Tapping burnt of LVF Assembly Burnt off tapping to LVF assembly repaired. Supply restored at 1425hrs. | June | 2019 | 2019Q4 | 2019 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2019-06-12 | N | 457 | N | 3 | N | N | 1.1101 | 39.4971 | 333.9621
[7 empty] | 6654 | 14884 | 1667195 | 2019-06-13 04:35 | 2019-06-13 05:46 | 71 | 11kV | 62767 | 947 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.15L tripped ON: A & B phase IOC UG cable fault between S9509 Sw/B and S9849 to LB35872 See 1667252 1667253 | June | 2019 | 2019Q4 | 2019 | ZN9245:PA15 | ZN9245:PA15 | ZN09245/000015 | SUTHERLAND | UG | Not Veg | 2019-06-13 | N | 66.2798 | N | 3 | N | N | 1.1101 | 39.4971 | 45868.2723
[7 empty] | 6287 | 10761 | 1667299 | 2019-06-13 16:10 | 2019-06-13 17:30 | 80 | 11kV | 800 | 10 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193472 A Phase Fdr didnt trip. Reported from customer. X-arm broken at 9J-30040 Excluded oms 1667299 | June | 2019 | 2019Q4 | 2019 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2019-06-13 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 6688 | 15124 | 1667316 | 2019-06-13 20:10 | 2019-06-13 21:10 | 60 | 11kV | 13620 | 227 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193473 Bolt fallen out of Crossarm straps Pole HR-21117 Excluded OMS 1667343 & 1667316 | June | 2019 | 2019Q4 | 2019 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2019-06-13 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 9953.0943
[7 empty] | 6877 | 17262 | 1667414 | 2019-06-14 11:51 | 2019-06-14 12:48 | 57 | 11kV | 121809 | 2137 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.44 tripped on: C phase O/C UG cable fault between S35572, S3091 and S342 See 1667414 | June | 2019 | 2019Q4 | 2019 | ZN3155:PA44 | ZN3155:PA44 | ZN03155/000044 | WOOLLAHRA | UG | Not Veg | 2019-06-14 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 89014.4244
[7 empty] | 7029 | 18792 | 1667492 | 2019-06-14 16:38 | 2019-06-14 17:26 | 48 | 11kV | 720 | 15 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193488 Broken insulator at pole 8K-20286, mains burning cross arm, spotted by aerial patrol. Excluded OMS 1667492 | June | 2019 | 2019Q4 | 2019 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-06-14 | N | 48 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 5897 | 6371 | 1667516 | 2019-06-14 22:57 | 2019-06-15 00:30 | 93 | 11kV | 48523 | 539 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S35500 Top Ryde 11kV Panel 32 Feeder tripped on Relays: Earth Fault. B and C phase IOC, Fault Check andf Lockiut Cause: 11kV Cable damaged between S5250 and CP78456 1667785 1667786 1667516 | June | 2019 | 2019Q4 | 2019 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2019-06-14 | N | 90.0241 | N | 3 | N | N | 1.1101 | 39.4971 | 35459.1772
[7 empty] | 7133 | 19793 | 1667618 | 2019-06-15 21:45 | 2019-06-15 22:58 | 73 | 11kV | 49381 | 925 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Snow / Hail Storm | N | @S1850 Bass Hill Panel 40 'S5041 Bellevue Birdwood' fdr tripped on: Relays: Inst O/C Inst E/F and EFI Signals: 11kv trip Remarks: Section of 11kv UG feeder from S7396 Ashecroft Rex Sw B to S4899 Ashcroft St Sw/A | June | 2019 | 2019Q4 | 2019 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-06-15 | N | 53.3849 | N | 3 | N | N | 1.1101 | 39.4971 | 36086.1783
[7 empty] | 6061 | 8247 | 1667630 | 2019-06-15 22:07 | 2019-06-15 23:45 | 98 | 11kV | 165292 | 1697 | HV | Animal Bird | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN36200 EMPIRE BAY section of 11kV Panel 1 IR63103 Pine Ave tripped on Relays: OC trip, Lockout Abnormal: S14409 Sw B Closed, RE46529 Open, LB61929 Open Cause: Animals/Birds. Flying Fox found near LB45073 See 1667950,1 ex 1667630,1,5,42 | June | 2019 | 2019Q4 | 2019 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2019-06-15 | N | 97.4025 | N | 3 | N | N | 1.1101 | 39.4971 | 120790.5183
[7 empty] | 7051 | 19109 | 1667620 | 2019-06-15 21:53 | 2019-06-16 00:50 | 177 | 11kV | 210398 | 1837 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 38 Tripped on Signals: 11kV Trip, Zone Earth, No2 TX group Earth. Relays: 51N, Earth Fault, OC and EFI Field EFI's S613 and S5929 Abnormal Switching: SW/B CLosed at S5789 SW/A open at S5568 Cause: Cable fault between S5929 and S6109 See OMS 1667585 1667859 1667860 1667620 1667621 | June | 2019 | 2019Q4 | 2019 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | UG | Not Veg | 2019-06-15 | N | 114.5335 | N | 3 | N | N | 1.1101 | 39.4971 | 153752.6527
[7 empty] | 5825 | 5700 | 1667644 | 2019-06-16 00:28 | 2019-06-16 03:34 | 186 | 11kV | 3348 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193495 C Phase DOLF : 20 Amp Excluded OMS 1667644 | June | 2019 | 2019Q4 | 2019 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | OH | Veg | 2019-06-16 | N | 186 | N | 4 | N | N | 1.1101 | 39.4971 | 2446.6197
[7 empty] | 5594 | 3519 | 1667652 | 2019-06-16 08:26 | 2019-06-16 12:00 | 214 | 11kV | 155918 | 1219 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 193496 Car Hit Pole JU45242 Excluded OMS 1667652 | June | 2019 | 2019Q4 | 2019 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Not Veg | 2019-06-16 | N | 127.9065 | N | 4 | N | N | 1.1101 | 39.4971 | 113940.2756
[7 empty] | 6599 | 14356 | 1667662 | 2019-06-16 11:18 | 2019-06-16 12:07 | 49 | 11kV | 2058 | 42 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193497 LV section isolated to earth up 11kV fdr see report No 193496 Excluded oms # 1667687 | June | 2019 | 2019Q4 | 2019 | 261:81870 | 261:81870 | ZN00261/081870 | NEWCASTLE | OH | Not Veg | 2019-06-16 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 1503.9257
[7 empty] | 5932 | 6771 | 1667767 | 2019-06-16 19:26 | 2019-06-16 21:57 | 151 | 11kV | 116369 | 1241 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN12650 WEST GOSFORD 11kV CB Panel 6 'SCC Racecourse' fdr tripped and reclosed on earth fault RE50531 Showground Maliwa 0.35 tripped and locked out on overcurrent Cause: UG Fault S18235 efi operated incorrectly Cable Fault between LB44599 and S18235 to S18228 See 1667968,70,1,2,3 ex 1667767 | June | 2019 | 2019Q4 | 2019 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | UG | Not Veg | 2019-06-16 | N | 93.7703 | N | 4 | N | N | 1.1101 | 39.4971 | 85039.0329
[7 empty] | 5563 | 3101 | 1667841 | 2019-06-17 09:42 | 2019-06-17 11:41 | 119 | 11kV | 31912 | 328 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.17L tripped on: B phase OC UG cable fault between S7642 to S35777 to S35095 See 1668554 1668555 | June | 2019 | 2019Q4 | 2019 | ZN7481:PA17 | ZN7481:PA17 | ZN07481/000017 | SYDNEY | UG | Not Veg | 2019-06-17 | N | 97.2927 | N | 3 | N | N | 1.1101 | 39.4971 | 23320.3484
[7 empty] | 7048 | 19073 | 1667949 | 2019-06-17 16:43 | 2019-06-17 17:07 | 24 | 11kV | 864 | 36 | HV | Vandalism | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 193512 Isolated sub to replace stolen earth cables. Excluded OMS 1667949 | June | 2019 | 2019Q4 | 2019 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | Unknown | Not Veg | 2019-06-17 | N | 24 | N | 3 | N | N | 1.1101 | 39.4971 | 631.3857
[7 empty] | 5774 | 5373 | 1667897 | 2019-06-17 13:06 | 2019-06-17 19:40 | 394 | 11kV | 54745 | 277 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Panel 8 Galston Reserve beyond CP559 Cobah Rd tripped and locked out on EF Cause: 11kV OH down between CP2902 and LB2422. HV into LV Abnormal Switching: CP2063 Closed, AB340 Open LB62158 Closed, Recloser CP3281 Open CP473 Closed, AB2295 Open See OMS 1668666 1668667 1668668 1667897 1667899 1667963 | June | 2019 | 2019Q4 | 2019 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2019-06-17 | N | 197.6354 | N | 3 | N | N | 1.1101 | 39.4971 | 40006.0313
[7 empty] | 5654 | 4144 | 1668112 | 2019-06-18 11:15 | 2019-06-18 14:15 | 180 | 11kV | 180 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193531 C Phase DOLF : 10 Amp Excluded OMS 1668112 | June | 2019 | 2019Q4 | 2019 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-06-18 | N | 180 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 6740 | 15488 | 1668094 | 2019-06-18 16:20 | 2019-06-18 17:10 | 50 | 11kV | 800 | 16 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 10 Section of feeder from LB40985 tee PT12736 tee PT13236 tee PT11880 tee PT11925 interrupted for emergency tree trimming Tree extremely close to multiple phases of 11kv mains. Pole PR280. See 1668211 ex 1668094 | June | 2019 | 2019Q4 | 2019 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2019-06-18 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 5575 | 3285 | 1668159 | 2019-06-18 13:47 | 2019-06-18 18:10 | 263 | 11kV | 261486 | 1914 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn2835 Burwood - Pnl.23L tripped on: O/C B phase UG cable fault from S136 Sw/B to S46336. S3052 restored after feeder due to LV down on Dist #2 caused by LV //. See1670294 1670295 1670296 | June | 2019 | 2019Q4 | 2019 | ZN2835:PA23 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2019-06-18 | N | 136.6176 | N | 3 | N | N | 1.1101 | 39.4971 | 191086.2563
[7 empty] | 6168 | 9607 | 1668272 | 2019-06-19 04:27 | 2019-06-19 09:40 | 313 | 11kV | 439566 | 1653 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | @Zn2196 Milperra - 11kv Panel No.5 "Sub 8696 Milperra Amour No.4" feeder tripped, reclosed and locked out Relays: EFI, Lockout, Fault check, A & B phase OC Signals: 11kv trip, No.3 Group Earth, Zone earth Remarks: UGOH fault short circuit. There was an explosion at the 11kv UGOH above LB 133 on pole EH-340. Dop also found 11kv wire touching crossarm on Pole EH-1598. Dop also found cracked insulator on UGOH Pole EH-1206 | June | 2019 | 2019Q4 | 2019 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2019-06-19 | N | 265.9201 | N | 3 | N | N | 1.1101 | 39.4971 | 321221.8678
[7 empty] | 6363 | 11613 | 1668286 | 2019-06-19 08:03 | 2019-06-19 10:55 | 172 | 11kV | 20619 | 239 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | LID 193536 3 fault operations 3 phase Instantaneous Overcurrent UGM fault between Sw 28743 & Sw 59388. Faulty 11kV cable enbox at Diamantina Place sub 29768. Excluded OMS No. 1668286 | June | 2019 | 2019Q4 | 2019 | 508:82576 | 508:82576 | ZN00508/082576 | PORT STEPHENS | UG | Not Veg | 2019-06-19 | N | 86.272 | N | 3 | N | N | 1.1101 | 39.4971 | 15067.757
[7 empty] | 6151 | 9430 | 1668271 | 2019-06-19 04:16 | 2019-06-19 21:21 | 1025 | 11kV | 126027 | 707 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | @ZN2196 Milperra - 11kv Panel No.26 "Sub 63412 Nancy Milperra McDonalds" feeder tripped Relays: 51N Earth Fault, EFI, Fault Check Signals: 11kv trip, Zone Earth, No.3 Group Earth Remarks: vehicle hit pole. Car hit pole on Edgar St, Near IIma St Bankstown. Pole PE-18658 | June | 2019 | 2019Q4 | 2019 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-06-19 | N | 178.256 | N | 3 | N | N | 1.1101 | 39.4971 | 92096.8144
[7 empty] | 5633 | 3828 | 1668587 | 2019-06-20 13:46 | 2019-06-20 15:36 | 110 | 11kV | 90617 | 850 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.2 tripped & reclosed on: Earth Fault UG cable fault in front line section of feeder from Pnl.2 to S1883 Sw/A to S8878 Sw/A | June | 2019 | 2019Q4 | 2019 | ZN384:PA2 | ZN384:PA2 | ZN00384/000002 | SYDNEY | UG | Not Veg | 2019-06-20 | N | 106.6082 | N | 4 | N | N | 1.1101 | 39.4971 | 66220.2309
[7 empty] | 5589 | 3445 | 1668634 | 2019-06-20 15:20 | 2019-06-20 16:10 | 50 | 11kV | 2550 | 51 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193554 Repair wire on crossarm at pole 6N-10005. | June | 2019 | 2019Q4 | 2019 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2019-06-20 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 1863.4648
[7 empty] | 5874 | 6121 | 1668644 | 2019-06-20 18:20 | 2019-06-20 19:10 | 50 | 11kV | 350 | 7 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193557 Wire off pin at pole WT-40007. Excluded OMS No. 1668644 | June | 2019 | 2019Q4 | 2019 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2019-06-20 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 5691 | 4557 | 1668664 | 2019-06-20 16:39 | 2019-06-20 20:45 | 246 | 11kV | 24630 | 270 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12600 LISAROW section of 11kV Panel 2 RE41845 North Erina tripped and locked out E/F and SEF Cause: tree/branch brought down oh in Wingrove Rd See 1670833,4,5 ex 1668664,70,5,6,83 | June | 2019 | 2019Q4 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2019-06-20 | N | 91.2222 | N | 4 | N | N | 1.1101 | 39.4971 | 17998.8775
[7 empty] | 6991 | 18427 | 1668737 | 2019-06-21 03:43 | 2019-06-21 06:06 | 143 | 11kV | 163229 | 1360 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9252 Janalli Panel 25 "Waronora" tripped on : EF and overcurrent ith reclose time delay efi Remarks: Cable fault between S48498 The Crescent Thorpe to Sub 9987 Warrangerree Wylah to Sub 9980 Bundanoon Shearwater | June | 2019 | 2019Q4 | 2019 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | UG | Not Veg | 2019-06-21 | N | 120.0213 | N | 3 | N | N | 1.1101 | 39.4971 | 119282.9388
[7 empty] | 5973 | 7143 | 1668795 | 2019-06-21 10:45 | 2019-06-21 12:00 | 75 | 11kV | 750 | 10 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193569 Broken crossarm pole 8L-40047 excluded OMS 1668795 | June | 2019 | 2019Q4 | 2019 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2019-06-21 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 5467 | 1570 | 1668854 | 2019-06-21 15:40 | 2019-06-21 17:25 | 105 | 11kV | 840 | 8 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193570 Broken crossarm | June | 2019 | 2019Q4 | 2019 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2019-06-21 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 6117 | 9065 | 1669025 | 2019-06-22 19:25 | 2019-06-22 20:31 | 66 | 11kV | 16170 | 245 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP421 Crosslands Rd tripped on Relays: Overcurrent. Cause: Tree branch on OH mains near PT1732 Fishburns Rd CC1: 22-"Refer to SOp" | June | 2019 | 2019Q4 | 2019 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-06-22 | N | 66 | N | 1 | N | N | 1.1101 | 39.4971 | 11816.5591
[7 empty] | 5617 | 3687 | 1669191 | 2019-06-23 21:39 | 2019-06-23 23:00 | 81 | 11kV | 2916 | 36 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Rain Heavy | N | Ex ZN12570 AVOCA section of 11kV Panel 40 PT13412 HUMPHREYS CARRELA 11kv footpath side HDO operated Cause: Lightning 20A ABB fuse replaced with correct 31A fuse See 1670841 ex 1669191,3 | June | 2019 | 2019Q4 | 2019 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Not Veg | 2019-06-23 | N | 81 | N | 2 | N | N | 1.1101 | 39.4971 | 2130.9268
[7 empty] | 6384 | 11834 | 1669163 | 2019-06-23 18:39 | 2019-06-24 01:40 | 421 | 11kV | 531514 | 2177 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kv Panel 12 CB at Zn10997 Sans Souci Arncliffe tripped, reclosed and locked out on: Signals: 11kv trip Abnormal: Panel 11 at Sans Souci is O/O/S Sw/B closed at S10154 Wellington Plimsoll Remarks: flashover/arcing. There was an explosion on the 11kv links 30382. See separate interruption on Dist 2 at S10545 McMillan Clareville | June | 2019 | 2019Q4 | 2019 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2019-06-23 | N | 244.1497 | N | 2 | N | N | 1.1101 | 39.4971 | 388414.7542
[7 empty] | 6314 | 11032 | 1669210 | 2019-06-24 00:55 | 2019-06-24 03:25 | 150 | 11kV | 3000 | 20 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex ZN12570 AVOCA section of 11kV Panel 40 PT14579 BROULA HUMPHREYS 11kv footpath HDO operated Footpath phase arrestor blown after lightning strike See 1670844 ex 1669210 | June | 2019 | 2019Q4 | 2019 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Not Veg | 2019-06-24 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 2192.3115
[7 empty] | 6464 | 12879 | 1669429 | 2019-06-24 15:15 | 2019-06-24 15:55 | 40 | 11kV | 2160 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 193589 B Phase DOLF : 40 Amp Fuse element broken , not blown. Excluded OMS 1669429 | June | 2019 | 2019Q4 | 2019 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | OH | Not Veg | 2019-06-24 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 1578.4643
[7 empty] | 6400 | 12047 | 1669267 | 2019-06-24 05:33 | 2019-06-24 16:05 | 632 | 11kV | 138108 | 605 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN14891 WYONG 11kV CB Panel 21 'Virginia Road' fdr interrupted for safety. AOp tripped for safety Cause: Report of 11kv down corner Warnervale and Virginia See 1670850,1,2 ex 1669267 | June | 2019 | 2019Q4 | 2019 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2019-06-24 | N | 228.2777 | N | 5 | N | N | 1.1101 | 39.4971 | 100925.2529
[7 empty] | 7141 | 19896 | 1669466 | 2019-06-24 16:28 | 2019-06-24 19:40 | 192.1 | 11kV | 4994.6 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex ZN14891 WYONG section of 11kV Panel 5 CP44781 auto link centre phase 40Amp operated Cause nto ascertained. Patrolled by DOp CC1: 22-"Refer to SOp" FRC1: 329-"High Voltage Fuse - Requires replacement" | June | 2019 | 2019Q4 | 2019 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-06-24 | N | 192.1 | N | 5 | N | N | 1.1101 | 39.4971 | 3649.9064
[7 empty] | 6690 | 15132 | 1669472 | 2019-06-24 16:35 | 2019-06-24 23:37 | 422 | 11kV | 8018 | 19 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex ZN12600 LISAROW section of 11kV Panel 2 Section of Feeder from LB42172 to LK41935 to LB41264 tee PT11472 & PT79222 Broken Cross arm at LK41457 See 1670906 ex 1669472,503 | June | 2019 | 2019Q4 | 2019 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2019-06-24 | N | 422 | N | 5 | N | N | 1.1101 | 39.4971 | 5859.3179
[7 empty] | 6945 | 17957 | 1669645 | 2019-06-25 12:06 | 2019-06-25 13:10 | 64 | 11kV | 832 | 13 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193595 Need to retension mains from sub 70149. No Protection. Emergency Switching Only | June | 2019 | 2019Q4 | 2019 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2019-06-25 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 608.0011
[7 empty] | 7094 | 19544 | 1669602 | 2019-06-25 09:15 | 2019-06-25 14:04 | 289 | 11kV | 289 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 193599 C Phase DOLF : 16 Amp Contractor piering new kiosk cut through 11kV underground cable. Could not repair cable today, customers supplied via generator connected to load side of LVL 52465. | June | 2019 | 2019Q4 | 2019 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | UG | Not Veg | 2019-06-25 | N | 289 | N | 3 | N | N | 1.1101 | 39.4971 | 211.1927
[7 empty] | 5483 | 1708 | 1669767 | 2019-06-25 20:09 | 2019-06-25 22:24 | 135 | 11kV | 363945 | 2787 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.17 tripped on: SEF Open bond Roadside/ loadside of AB31309 See 1670185 1670186 | June | 2019 | 2019Q4 | 2019 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2019-06-25 | N | 130.5867 | N | 3 | N | N | 1.1101 | 39.4971 | 265960.2714
[7 empty] | 6475 | 13042 | 1669800 | 2019-06-26 01:39 | 2019-06-26 04:55 | 196 | 11kV | 170302 | 1617 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood Panel 22 tripped under fault. Protection relay flags: Panel 22 Earth Fault, EFI, Fault Check. Tx11 Fault Check. At S46610 Currawong Eloora SWB closed and SWB open Cause: UG cable fault between S35000, S3911, S46610, S3027 and S 3026 See OMS 1670309 1670310 1669801 1670311 | June | 2019 | 2019Q4 | 2019 | ZN80:PA22 | ZN80:PA22 | ZN00080/000022 | LANE COVE | UG | Not Veg | 2019-06-26 | N | 105.3197 | N | 5 | N | N | 1.1101 | 39.4971 | 124451.6785
[7 empty] | 6006 | 7697 | 1669913 | 2019-06-26 11:44 | 2019-06-26 13:08 | 84 | 11kV | 140784 | 1676 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.26 tripped on: Earth Fault UG cable fault in front line section of feeder between Pnl.26, S9790 Sw/A and S9027 Sw/B | June | 2019 | 2019Q4 | 2019 | ZN9118:PA26 | ZN9118:PA26 | ZN09118/000026 | SUTHERLAND | UG | Not Veg | 2019-06-26 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 102880.7948
[7 empty] | 5750 | 5162 | 1669942 | 2019-06-26 13:50 | 2019-06-26 14:58 | 68 | 11kV | 1564 | 23 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 193613 No protection operations. Outage to repair broken cross arm at pole 7L-40084. | June | 2019 | 2019Q4 | 2019 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2019-06-26 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 1142.9251
[7 empty] | 6471 | 12985 | 1670041 | 2019-06-26 21:20 | 2019-06-26 22:50 | 90.2667 | 11kV | 11644.4 | 129 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex ZN12640 UMINA section of 11kV Panel 7 PT13858 KOURUNG THE ESPLANADE centre and road side 11kv hdo fuses blown (31.5Amp) Cause: Possum found as cause at PT13858 transformer tank. Fuses replaced and network restored See 1670041 ex 1670044,7 | June | 2019 | 2019Q4 | 2019 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Not Veg | 2019-06-26 | N | 90.2667 | N | 5 | N | N | 1.1101 | 39.4971 | 8509.3841
[7 empty] | 5501 | 1993 | 1670043 | 2019-06-26 21:15 | 2019-06-26 22:52 | 97 | 11kV | 58394 | 602 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12570 AVOCA 11kV CB Panel 29 'Bensville' fdr tripped and locked out under fault Protection flags at zone sub: A phase IOC, Earth Fault, EFI EFI: Nil Cause: UG Fault between Zn12570 Avoca Pa29 & S12692 Sw/A | June | 2019 | 2019Q4 | 2019 | ZN12570:PA29 | ZN12570:PA29 | ZN12570/000029 | CENTRAL COAST | UG | Not Veg | 2019-06-26 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 42672.6129
[7 empty] | 5530 | 2480 | 1670098 | 2019-06-27 09:54 | 2019-06-27 12:05 | 131.0333 | 11kV | 131.0333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 193623 Single phase DOLF : 10 Amp | June | 2019 | 2019Q4 | 2019 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2019-06-27 | N | 131.0333 | N | 1 | N | N | 1.1101 | 39.4971 | 95.7553
[7 empty] | 6212 | 10100 | 1670365 | 2019-06-28 10:58 | 2019-06-28 12:41 | 103 | 11kV | 10757 | 203 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.15, 17 & 20 tripped on: Pnl.15 : Translay Pnl.17: Earth Fault Pnl.20 Earth Fault Pnl.22L : EFI (no trip) @S1074 Untiec - SwC : Translay trip Abnormal: Sw/B @ S1074 was open due to defective shutters. Kingsford DNMS was in test due to T/Tele working there. UG cable fault between Pnl.15, S7846 and S1074. | June | 2019 | 2019Q4 | 2019 | ZN35600:PA20 | ZN35600:PA20 | ZN35600/000020 | RANDWICK | UG | Not Veg | 2019-06-28 | N | 52.9901 | N | 2 | N | N | 1.1101 | 39.4971 | 7860.8983
[7 empty] | 5398 | 810 | 1670485 | 2019-06-28 19:34 | 2019-06-28 20:49 | 75 | 11kV | 29428 | 1814 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 193632 2 fault operations B Phase Earth Fault 11KV U/G CABLE FAULT. Repairs required Excluded OMS 1670485, 1670487,1670489. | June | 2019 | 2019Q4 | 2019 | 256:80647 | 256:80647 | ZN00256/080647 | NEWCASTLE | UG | Not Veg | 2019-06-28 | N | 16.2227 | N | 2 | N | N | 1.1101 | 39.4971 | 21505.1144
[7 empty] | 5823 | 5695 | 1670513 | 2019-06-29 08:06 | 2019-06-29 13:00 | 294 | 11kV | 14236 | 69 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 193634 3 fault operations 11kV OHM on ground from pole IT-21711. Swan hit OHM. Repairs completed Excluded OMS 1670513 | June | 2019 | 2019Q4 | 2019 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2019-06-29 | N | 206.3188 | N | 7 | N | N | 1.1101 | 39.4971 | 10403.2489
[7 empty] | 5510 | 2086 | 1670545 | 2019-06-29 12:43 | 2019-06-29 13:47 | 64 | 11kV | 1582 | 34 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Zn1285 Greenacre Park 11kv Pnl 30 "Hume Como" feeder tripped on Relays: earth fault and overcurrent with fault check Remarks: contractor error caused failure. Cable damaged, Pnl 36 at Greenacre Park to Sub 3894 Hume Como to sub 3413 Hume Shellcote #2 by ausgrid contractor at 222 hume highway | June | 2019 | 2019Q4 | 2019 | ZN1285:PA30 | ZN37100:PA15 | ZN37100/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-06-29 | N | 46.5294 | N | 7 | N | N | 1.1101 | 39.4971 | 1156.0789
[7 empty] | 6446 | 12621 | 1670557 | 2019-06-29 13:01 | 2019-06-29 14:43 | 102 | 11kV | 161367 | 1590 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.32 tripped on: A & C phase IOC Cause not ascertained See 1670736 1670737 | June | 2019 | 2019Q4 | 2019 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | OH | Veg | 2019-06-29 | N | 101.4887 | N | 7 | N | N | 1.1101 | 39.4971 | 117922.2441
[7 empty] | 5644 | 4058 | 1670512 | 2019-06-29 08:05 | 2019-06-29 16:10 | 485 | 11kV | 173707 | 1943 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn15005 Belrose Panel 2 tripped and reclosed tripped and locked out on Relays: 50 T time, OC A phase, Lockout Fault Check and EFI. Signals: 11kV Trip Cause: UG cable fault from S16969 to CP23625 to AB20513. See OMS 1670717 16970718 1670719 1670721 1670724 1670726 1670538 1670537 | June | 2019 | 2019Q4 | 2019 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | UG | Not Veg | 2019-06-29 | N | 89.4014 | N | 7 | N | N | 1.1101 | 39.4971 | 126939.9521
[7 empty] | 6379 | 11769 | 1670581 | 2019-06-29 17:50 | 2019-06-29 18:50 | 60 | 11kV | 29206 | 503 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | S35700 Port Botany - Pnl.10 tripped on: 51ABC End box fault @ S6371 Sw/B See 1670729 1670732 | June | 2019 | 2019Q4 | 2019 | ZN35700:PA10 | ZN35700:PA10 | ZN35700/000010 | RANDWICK | UG | Not Veg | 2019-06-29 | N | 58.0636 | N | 7 | N | N | 1.1101 | 39.4971 | 21342.8834
[7 empty] | 6019 | 7815 | 1670585 | 2019-06-29 18:05 | 2019-06-29 19:42 | 97 | 11kV | 151759 | 1619 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S180 Mosman Panel 7 tripped on C phase overcurrent and earth leakage with EFI Cause: UG cable fault insection of 11kV feeder from S4245 to S1332 See OMS 1670714 1670715 1670585 | June | 2019 | 2019Q4 | 2019 | ZN180:PA7 | ZN180:PA7 | ZN00180/000007 | MOSMAN | UG | Not Veg | 2019-06-29 | N | 93.7363 | N | 7 | N | N | 1.1101 | 39.4971 | 110901.0011
[7 empty] | 6023 | 7852 | 1670611 | 2019-06-29 20:26 | 2019-06-29 23:10 | 164 | 11kV | 32115 | 296 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2466 Flemington 11kv Panel '27' labelled 'S.2566 Carter King' tripped on: Relays: B phase OC, earth fault, EFI, Fault check Signals: 11kv trip, Tx3 GE Remarks: UG fault. Section of 11kv feeder from Sw/B S.8775 Hill M4 to Sw/B S.7616 Parramatta Day No.1 tee S.791 Grace John is defective. UG Cable fault. | June | 2019 | 2019Q4 | 2019 | ZN2466:PA27 | ZN2466:PA1 | ZN02466/000001 | PARRAMATTA | UG | Not Veg | 2019-06-29 | N | 108.4966 | N | 7 | N | N | 1.1101 | 39.4971 | 23468.6948
[7 empty] | 6403 | 12069 | 1670634 | 2019-06-30 07:14 | 2019-06-30 13:10 | 356 | 11kV | 23840 | 115 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | LID 193639 B Phase HV Cartridge fuse : 31 Amp Replaced B phase 31.5A with 3 new 40A fuses. Fault in LV SP OS-20014 on Cct 23806 caused Hazemeyer HV fuse to blow, no LVF operation. See report 193640 for LVF operation at sub 24029 cct 24034 when trying to interconnect LV. See report 193641 for outage to replace HV fuses due to operating restrictions. Excluded OMS 1670634 | June | 2019 | 2019Q4 | 2019 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2019-06-30 | N | 207.3043 | N | 3 | N | N | 1.1101 | 39.4971 | 17421.5688
[7 empty] | 6435 | 12550 | 1670680 | 2019-06-30 18:04 | 2019-06-30 20:40 | 156 | 11kV | 624 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193646 A Phase DOLF : 10 Amp Excluded OMS 1670680 | June | 2019 | 2019Q4 | 2019 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-06-30 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 5963 | 7039 | 1670673 | 2019-06-30 15:42 | 2019-06-30 22:10 | 388 | 11kV | 37636 | 97 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | No Weather Impact | N | LID 193643 A Phase DOLF : 20 Amp Tree branch fell and broke LV xarm pole VP-30126 which has N/O link 26075 attached Isolated RH LVF 4763 & LH LVF 26703 to make repairs. Sub 4763 blown A phase DOLF 20A & RH LVF 4763 250A. | June | 2019 | 2019Q4 | 2019 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2019-06-30 | N | 388 | N | 3 | N | N | 1.1101 | 39.4971 | 27503.2787
[7 empty] | 4895 | 15920 | 1670960 | 2019-07-01 19:59 | 2019-07-02 01:00 | 301 | 11kV | 210535 | 1321 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AtS 847 Hornsby Panel 7 Tripped Cause: Tree branch brought down OH in Clarke Rd - Two pole snapped and 11kV and LV mains on the ground. See Other interruptions due to LV parallel and live work pause. See OMS 1671003 1671004 1671005 1670970 1670972 1670974 1670962 1670963 1670964 | July | 2019 | 2020Q1 | 2020 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | OH | Veg | 2019-07-01 | N | 159.3755 | N | 1 | N | N | 1.1101 | 39.4971 | 153852.7683
[7 empty] | 3389 | 872 | 1671094 | 2019-07-02 13:45 | 2019-07-02 15:22 | 97 | 11kV | 112088 | 1233 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn9900 Menai - Pnl.1 tripped on: Earth Fault UG cable hit by exacator outside 23 Moreton Rd. See 1671206 1671207 | July | 2019 | 2020Q1 | 2020 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2019-07-02 | N | 90.9067 | N | 2 | N | N | 1.1101 | 39.4971 | 81910.6044
[7 empty] | 4272 | 9986 | 1671197 | 2019-07-03 05:45 | 2019-07-03 08:50 | 185 | 11kV | 1295 | 7 | HV | Animal Possum | Animal | Fuse | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 21 'Virinia Rd' PT13598 DAKARA BRUCE 10K HDO blown Cause: Animals/birds. Possum on PT See 1671511 ex 1671197 1671211 | July | 2019 | 2020Q1 | 2020 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2019-07-03 | N | 185 | N | 1 | N | N | 1.1101 | 39.4971 | 946.3478
[7 empty] | 4706 | 14164 | 1671109 | 2019-07-02 14:37 | 2019-07-03 17:20 | 1603 | 11kV | 129475 | 657 | HV | Overload LV Parallel | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT Zn187 Crows Nest Panel 14 Burlington west tripped on Relays: Earth fault, EFI and E/F check Signals: 11kV trip TX12 E/F Cause: Due to LV parallel link closed mains burnt to the ground Water was inside S4316 and caused RMI to flash over See OMS 1674031 1674032 1671163 1671109 | July | 2019 | 2020Q1 | 2020 | ZN187:PA14 | ZN187:PA14 | ZN00187/000014 | NORTH SYDNEY | OH | Not Veg | 2019-07-02 | N | 197.07 | N | 2 | N | N | 1.1101 | 39.4971 | 94616.5111
[7 empty] | 4702 | 14128 | 1671625 | 2019-07-04 19:52 | 2019-07-04 21:50 | 118 | 11kV | 158922 | 1899 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @S9118 Cronulla Panel 11 (S9755 Ewos Waratah ETC) tripped on Signals: 11kv trip Relays: A & B phase IOC Remarks: animals/birds. Bat on 11kv near PT64584 | July | 2019 | 2020Q1 | 2020 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2019-07-04 | N | 83.6872 | N | 1 | N | N | 1.1101 | 39.4971 | 116135.5102
[7 empty] | 4765 | 14673 | 1671643 | 2019-07-05 01:19 | 2019-07-05 10:25 | 546 | 11kV | 59515 | 380 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP47749 Palmtree Nerra tripped, reclosed and tripped on OC and earth fault with lockout Cause not ascertained for outage to be patrolled Friday Daylight hours SAe eOMS 1675251/252/253/254/255/256 1671643 1671644 | July | 2019 | 2020Q1 | 2020 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2019-07-05 | N | 156.6184 | N | 3 | N | N | 1.1101 | 39.4971 | 43491.8066
[7 empty] | 3821 | 5323 | 1671852 | 2019-07-05 14:33 | 2019-07-05 17:21 | 168 | 11kV | 18648 | 111 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 193749 B phase DOLF : 31 Amp faulty arrestor. fault detector at sw 64651 operated 1433. B Ph O/C Excluded oms report no 1671861. | July | 2019 | 2020Q1 | 2020 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2019-07-05 | N | 168 | N | 3 | N | N | 1.1101 | 39.4971 | 13627.4084
[7 empty] | 4434 | 11347 | 1671772 | 2019-07-05 12:32 | 2019-07-05 19:30 | 418 | 11kV | 146201 | 1364 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 193748 2 fault operations 3 phase Overcurrent Truck hit pole HS-72527. HV into LV & SL Pole HS-72527 & all crossarms broken, need replacing. It was advised several spans of redundant SL cable was removed. Excluded OMS 1671772 | July | 2019 | 2020Q1 | 2020 | 507:80917 | 507:80917 | ZN00507/080917 | CESSNOCK | OH | Not Veg | 2019-07-05 | N | 107.1855 | N | 3 | N | N | 1.1101 | 39.4971 | 106839.3786
[7 empty] | 4716 | 14250 | 1672078 | 2019-07-06 02:51 | 2019-07-06 05:26 | 155 | 11kV | 13640 | 88 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | 11kV HOD middle and footpath side fuse opersated at S15302 Mass St Section of Panel 8 Narraweenma feeder Cause: Animals /Birds possum | July | 2019 | 2020Q1 | 2020 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2019-07-06 | N | 155 | N | 4 | N | N | 1.1101 | 39.4971 | 9967.7097
[7 empty] | 4871 | 15728 | 1672188 | 2019-07-06 11:20 | 2019-07-06 13:45 | 145 | 11kV | 128528 | 1078 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.13 tripped & locked out on: IOC C phase Field EFIs: S10785 S10676 UG cable fault from S10676 Sw/B to AB31321 tee S10533 See 1673339 1673340 | July | 2019 | 2020Q1 | 2020 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | UG | Not Veg | 2019-07-06 | N | 119.2282 | N | 4 | N | N | 1.1101 | 39.4971 | 93924.4715
[7 empty] | 3447 | 1460 | 1672089 | 2019-07-06 07:39 | 2019-07-06 17:05 | 566 | 11kV | 70344 | 320 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 193754 Tree on Fdr at JW-500169 Excluded OMS 1672089 | July | 2019 | 2020Q1 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-07-06 | N | 219.825 | N | 4 | N | N | 1.1101 | 39.4971 | 51405.3204
[7 empty] | 4782 | 14835 | 1672241 | 2019-07-06 13:08 | 2019-07-06 18:55 | 347 | 11kV | 41578 | 878 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.2 tripped & reclosed on: B & C phase IOC Pnl.2 interrupted by AOp @ 1308 on advise from DOp Patterson. 11kV Cross arm and pole fire outside 90 General Holmes Dr. LV// link 988 found closed. See 1673345 1673346 1673347 1673348 | July | 2019 | 2020Q1 | 2020 | ZN10998:PA2 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2019-07-06 | N | 47.3554 | N | 4 | N | N | 1.1101 | 39.4971 | 30383.9761
[7 empty] | 3824 | 5341 | 1672599 | 2019-07-07 08:24 | 2019-07-07 11:49 | 205.15 | 11kV | 76639.4 | 705 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn185 Zetland - Pnl.9 tripped onL Earth Fault UG cabel fault between S5987 Sw/B and S5505 Sw/A | July | 2019 | 2020Q1 | 2020 | ZN188:PA9 | ZN188:PA9 | ZN00188/000009 | SYDNEY | UG | Not Veg | 2019-07-07 | N | 108.7084 | N | 3 | N | N | 1.1101 | 39.4971 | 56005.813
[7 empty] | 4460 | 11570 | 1672737 | 2019-07-07 11:26 | 2019-07-07 14:18 | 172 | 11kV | 145622 | 1307 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | At S2400 Berowra Panel 15 tripped reclosed tripped and locked out on Relays: A and Cphase OC, A and C phase Time OC, Loickout Signals: OC trip Filed EFI's Cause: HV insulator broken in railway corridor near pole MC20390 between S49939 SW to LB1442 to S49943 See OMS 1674813 1674815 1674816 1672737 | July | 2019 | 2020Q1 | 2020 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Not Veg | 2019-07-07 | N | 111.417 | N | 3 | N | N | 1.1101 | 39.4971 | 106416.2625
[7 empty] | 4196 | 9299 | 1672597 | 2019-07-07 11:15 | 2019-07-07 17:31 | 376 | 11kV | 42112 | 112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600Lisarow Panel 9 Section of feeder from AB41990 to LB4109 to Recloser CP41708 tee PT11670 interrupted for safety Abnormal Switching : Recloser CP41708 Closed Recloser CPO41066 Open and Defective Cause: Tree on HV 12 atkinson Rd - HV and LV interrupted for safety See oMS 1672720 1672722 1672597 | July | 2019 | 2020Q1 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2019-07-07 | N | 376 | N | 3 | N | N | 1.1101 | 39.4971 | 30774.2075
[7 empty] | 4891 | 15846 | 1673231 | 2019-07-08 13:35 | 2019-07-08 16:15 | 160 | 11kV | 480 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 193764 Urgent replacement of broken links 26923. Excluded OMS No. 1673275 + 1673231 | July | 2019 | 2020Q1 | 2020 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2019-07-08 | N | 160 | N | 2 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 5245 | 19424 | 1673307 | 2019-07-08 18:00 | 2019-07-08 19:25 | 85 | 11kV | 1785 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 193766 A Phase DOLF : 10 Amp Excluded OMS 1673307 | July | 2019 | 2020Q1 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-07-08 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 1304.4254
[7 empty] | 5033 | 17576 | 1673336 | 2019-07-09 07:29 | 2019-07-09 07:36 | 7 | 11kV | 6958 | 994 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S195 Pymble Panel 28 Bridge Pacific Tripped on Signals: TX4 Group Earth, Zone Earth 11kV Trip. Relays: A and C phase OC, Earth Fault, Fault Check and EFI. Cause: NAR41486 Section of feeder to be isolated between S36004 to S35136 SWA Suring Switching DOP Closed SW/B At S4459 and Opened SW/B at S35136 then isolated SWA at S36004 and Earthed SW A then returned to S35136 and applied arth to SWB See oMS 1673955 1673336 | July | 2019 | 2020Q1 | 2020 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | Unknown | Not Veg | 2019-07-09 | N | 7 | N | 4 | N | N | 1.1101 | 39.4971 | 5084.7012
[7 empty] | 3701 | 3971 | 1673453 | 2019-07-09 14:15 | 2019-07-09 15:50 | 95 | 11kV | 1710 | 18 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | LID 193778 Broken crossarm pole 3J-90173 | July | 2019 | 2020Q1 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | Unknown | Not Veg | 2019-07-09 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 1249.6176
[7 empty] | 4202 | 9332 | 1673456 | 2019-07-09 15:00 | 2019-07-09 17:05 | 125 | 11kV | 250 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 193782 Outage to fix satety defects identified in oms job 1673456 by pole inspector. Excluded OMS 1674356 | July | 2019 | 2020Q1 | 2020 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2019-07-09 | N | 125 | N | 4 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 5150 | 18594 | 1673507 | 2019-07-09 18:30 | 2019-07-09 20:20 | 110 | 11kV | 1870 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12600 LISAROW section of 11kV Panel 2 "Holgate" 11kv fdr was de-energised to allow emergency repairs from USL41935 to AB41934 tee PT12365 and PT47611 Cause: tree/branch on oh mains See 1679724 ex 1673518 | July | 2019 | 2020Q1 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2019-07-09 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 4688 | 13996 | 1673663 | 2019-07-10 16:50 | 2019-07-10 19:10 | 140 | 11kV | 6020 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12690 Berkeley Vale feeder de energised between LB42211 to PT13334 Glenning Beckingham to PT 12516 Cause: Tree on OH - Large tree fallen onto 11kv mains. Emso on site at present. Road closed for safety. Please arrange line crew and DOP asap See OMS 1673683 1673663 | July | 2019 | 2020Q1 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2019-07-10 | N | 140 | N | 1 | N | N | 1.1101 | 39.4971 | 4399.2384
[7 empty] | 3542 | 2410 | 1673712 | 2019-07-11 02:58 | 2019-07-11 04:35 | 97 | 11kV | 13217 | 165 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP44946 Kunarra RD Tripped reclosed and locked out on OC Cause: Large tree resting on mains 2 Bays past resloser CP44946 (Beyond Locked fire trail gate) See OMS 1673808 1673811 1673712 1673198 | July | 2019 | 2020Q1 | 2020 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2019-07-11 | N | 80.103 | N | 3 | N | N | 1.1101 | 39.4971 | 9658.5938
[7 empty] | 3365 | 659 | 1673717 | 2019-07-11 07:20 | 2019-07-11 10:05 | 165 | 11kV | 1320 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193811 C Phase DOLF : 16 Amp Excluded OMS 1673717 | July | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-07-11 | N | 165 | N | 3 | N | N | 1.1101 | 39.4971 | 964.6171
[7 empty] | 3984 | 6763 | 1673711 | 2019-07-11 02:01 | 2019-07-11 11:35 | 574 | 11kV | 208373 | 1305 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | 33kV Feeder "350" from TS7140 Bunnerong to Zn340 Botany Tx 2 tripped on: Translay ITR at the same time Pnl.3 @ Botany Zn tripped on: B phase E/F and EFI UG cable fault between S7520 Sw/B and S3807 Sw/B tee S2122 Sw/A Possible protection malgrade. PE to investigate. See 1673933 1673934 1693936 1693938 | July | 2019 | 2020Q1 | 2020 | ZN340:PA3 | ZN340:PA3 | ZN00340/000003 | BAYSIDE | UG | Not Veg | 2019-07-11 | N | 159.6728 | N | 3 | N | N | 1.1101 | 39.4971 | 152272.8424
[7 empty] | 4353 | 10667 | 1674073 | 2019-07-12 17:00 | 2019-07-12 18:30 | 89.8 | 11kV | 1706.2 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193846 1 fault operation Overcurrent Fuse Saver found open, suspect fuse saver opend ona fault and did not reclose. UPDATE. May have not been reset to AR properly. | July | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-07-12 | N | 89.8 | N | 3 | N | N | 1.1101 | 39.4971 | 1246.8406
[7 empty] | 4555 | 12596 | 1674092 | 2019-07-12 18:50 | 2019-07-12 21:05 | 135 | 11kV | 3105 | 23 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 193845 Tree has fallen across CCT at pole FR-44815 & FR-44816 . Excluded OMS 1674092 | July | 2019 | 2020Q1 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2019-07-12 | N | 135 | N | 3 | N | N | 1.1101 | 39.4971 | 2269.0424
[7 empty] | 3336 | 448 | 1674037 | 2019-07-12 14:30 | 2019-07-12 21:20 | 410 | 11kV | 2460 | 6 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind Strong | N | LID 193844 Emergency pole replacement. KS-90302 Excluded OMS 1674037 | July | 2019 | 2020Q1 | 2020 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2019-07-12 | N | 410 | N | 3 | N | N | 1.1101 | 39.4971 | 1797.6954
[7 empty] | 4680 | 13927 | 1674121 | 2019-07-13 07:46 | 2019-07-13 09:15 | 89 | 11kV | 89 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 193847 A Phase Distribution fuse : 160 Amp Re-attached HV LLC Replaced LV Aph fuse Excluded OMS 1674121 | July | 2019 | 2020Q1 | 2020 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2019-07-13 | N | 89 | N | 4 | N | N | 1.1101 | 39.4971 | 65.0386
[7 empty] | 4650 | 13623 | 1674113 | 2019-07-13 04:08 | 2019-07-13 12:15 | 487 | 11kV | 5844 | 12 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 193848 tapping at pole JR-42440 Excluded OMS 1674113 | July | 2019 | 2020Q1 | 2020 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2019-07-13 | N | 487 | N | 4 | N | N | 1.1101 | 39.4971 | 4270.6228
[7 empty] | 3707 | 4030 | 1674122 | 2019-07-13 07:48 | 2019-07-13 18:15 | 627 | 11kV | 241451 | 1731 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12600 LISAROW 11kV CB Panel 3 'S12399 Lisarow High taylor' tripped relays: Earth Fault, EFI Signals: 11kv trip, CB3 Open EFI: S12399 S14623 S14247 S18521 Note: S18173 appears to be faulty Cause: Tree/Branch brought down OH. Corner of Wyoming Rd & Crawford Cres, Wyoming CTW issued to lineworker @ 1215 Main AP Folder @ PT13577 See 1674857,8,60 ex 1674122,51 | July | 2019 | 2020Q1 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2019-07-13 | N | 139.4864 | N | 4 | N | N | 1.1101 | 39.4971 | 176445.2692
[7 empty] | 4707 | 14170 | 1674123 | 2019-07-13 10:10 | 2019-07-13 18:35 | 505 | 11kV | 46995 | 94 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12650 WEST GOSFORD section of 11kV Panel 6 from S49470 Crawford Tamarisk 0.1 to LB44024 interrupted by DOp for safety. Repair Damage to Panel 3 @ Zn12600 Lisarow See 1674148, 1674147 ex 1674124,7 | July | 2019 | 2020Q1 | 2020 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2019-07-13 | N | 499.9468 | N | 4 | N | N | 1.1101 | 39.4971 | 34342.5599
[7 empty] | 5335 | 20247 | 1674321 | 2019-07-14 07:36 | 2019-07-14 10:05 | 149 | 11kV | 447 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 193852 A Phase LLC cable broken. Replaced under AP. Wrong sub in OMS. Excluded OMS 1674321. | July | 2019 | 2020Q1 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2019-07-14 | N | 149 | N | 1 | N | N | 1.1101 | 39.4971 | 326.6544
[7 empty] | 4437 | 11408 | 1674514 | 2019-07-15 11:25 | 2019-07-15 13:05 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 193860 A & B Phase DOLF : 10 Amp Fuses may have blown ina previous storm. Excluded OMS 1674514 | July | 2019 | 2020Q1 | 2020 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2019-07-15 | N | 100 | N | 3 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 4153 | 8794 | 1674433 | 2019-07-15 11:45 | 2019-07-15 17:30 | 345 | 11kV | 9921 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT S12650 EX panel 1 Dog Trap Road Recloser CP44853 Ourimbah Bumble tripped on Signals: N/A Relays Scan Fail See OMS 1676342 1676343 1674433 1674436 1674517 1674525 1674526 164551 | July | 2019 | 2020Q1 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2019-07-15 | N | 230.7209 | N | 3 | N | N | 1.1101 | 39.4971 | 7249.9742
[7 empty] | 4819 | 15224 | 1674366 | 2019-07-15 17:28 | 2019-07-15 19:55 | 146.9333 | 11kV | 2204 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | At S14891 Wyong Panel 5 Section of 11kV feeder from USL41028 to LB 44532 tee associated PTs were interrupted to aloow emergency repairs Cause: Tree on 11kV CCT adjacent PT14855 Dickson Durren 1.1 | July | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-07-15 | N | 146.9333 | N | 3 | N | N | 1.1101 | 39.4971 | 1610.6182
[7 empty] | 4097 | 8160 | 1674830 | 2019-07-16 15:38 | 2019-07-16 16:36 | 58 | 11kV | 61435 | 1215 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S12690 Berkeley Vale Panel 19R tripped on A and B phase IOC Cause: OH feeder patrolled by DOps and nothing found. See OMS 1676336 1676337 1674830 1674833 1674835 1674842 | July | 2019 | 2020Q1 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2019-07-16 | N | 50.5638 | N | 1 | N | N | 1.1101 | 39.4971 | 44894.886
[7 empty] | 4956 | 16670 | 1674922 | 2019-07-17 05:20 | 2019-07-17 06:23 | 63 | 11kV | 156177 | 2479 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.3 tripped on: ABC IOC Abnormal: S16453 Sw/A Closed with LB47128 Open Defective Possum found at base of LB61276. On energising, footpath phase bond on Pnl.3 side of LB61276 was glowing and needs replacing. Opened and left warning tag. | July | 2019 | 2020Q1 | 2020 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2019-07-17 | N | 63 | N | 2 | N | N | 1.1101 | 39.4971 | 114129.5452
[7 empty] | 4423 | 11261 | 1675169 | 2019-07-17 12:58 | 2019-07-17 13:07 | 9 | 11kV | 9 | 1 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 193888 1 fault operation Overcurrent | July | 2019 | 2020Q1 | 2020 |  |  |  | SINGLETON | OH | Not Veg | 2019-07-17 | N | 9 | N | 2 | N | N | 1.1101 | 39.4971 | 6.5769
[7 empty] | 3464 | 1640 | 1675334 | 2019-07-18 17:45 | 2019-07-18 18:46 | 60.6333 | 11kV | 82097.5333 | 1354 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At 12640 Umina - ex panel 4 11kV Bond blown off at AB40651 | July | 2019 | 2020Q1 | 2020 | ZN12640:PA4 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2019-07-18 | N | 60.6333 | N | 4 | N | N | 1.1101 | 39.4971 | 59994.4559
[7 empty] | 4023 | 7213 | 1675371 | 2019-07-18 20:17 | 2019-07-18 21:20 | 63 | 11kV | 158749 | 2580 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN10998 Rockdale Panel 3 "S10234' feeder has tripped Signals: 11kv trip Relays: C phase OC and EF, EFI Abnormal: AB31309 is open and defective Panel 3 closed @ Rockdale Remarks: UGOH fault open circuit. 11kv UGOH on the corner of Earle Rd and Wollongong Rd has burnt up. Located eletrically between LB30099, Sw/A @ S10879 tee AB 30098 | July | 2019 | 2020Q1 | 2020 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | Unknown | Unknown | 2019-07-18 | N | 61.5306 | N | 4 | N | N | 1.1101 | 39.4971 | 116009.0869
[7 empty] | 4426 | 11286 | 1675367 | 2019-07-18 19:45 | 2019-07-18 22:00 | 135 | 11kV | 5535 | 41 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | At S12492 North Skye Sub interrupted for safety Cause: Copper link had falled on LV TX bushingwhen emso attempted to open LV board screening .On arrival found burn marks between a and b phase bushings on Tx and bushings. Also found burn and arc marks on a phase LV surge arrestor. Replaced damaged a phase LV surge arrestor and cleaned up burn marks and discolouration with methylated spirits. | July | 2019 | 2020Q1 | 2020 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | UG | Not Veg | 2019-07-18 | N | 135 | N | 4 | N | N | 1.1101 | 39.4971 | 4044.8147
[7 empty] | 4561 | 12701 | 1675287 | 2019-07-18 14:23 | 2019-07-19 00:40 | 617 | 11kV | 617 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | @ S2835 Burwood Zn Ex Panel 8 section of 11kv feeder tripped from S6310 George park #2 tee #2 Tx (BZ send to sub 6155 George Park #1 tee Tx#3 IT receive) Remarks: Buchholz trip. BZ trip @ S6310 # 2Tx | July | 2019 | 2020Q1 | 2020 | ZN2835:PA8 | ZN2835:PA8 | ZN02835/000008 | BURWOOD | UG | Not Veg | 2019-07-18 | N | 617 | N | 4 | N | N | 1.1101 | 39.4971 | 450.8854
[7 empty] | 5079 | 18119 | 1675621 | 2019-07-20 08:28 | 2019-07-20 10:02 | 94 | 11kV | 137413 | 2238 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S10994 Mortdale Panel 4L tripped, reclosed tripped and locked out on Signals: No1 TX Group earth Relays: AB and Cphase OC, B phase IOC, EF check, Lockout and EFI Cause: 11kV UGOH defective ex S63599 See OMS 1676765 1676766 1675621 | July | 2019 | 2020Q1 | 2020 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | Unknown | Unknown | 2019-07-20 | N | 61.3999 | N | 2 | N | N | 1.1101 | 39.4971 | 100417.3674
[7 empty] | 3762 | 4698 | 1675612 | 2019-07-20 07:09 | 2019-07-20 11:40 | 271 | 11kV | 13569 | 197 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Cold <10C | N | LID 193944 2 fault operations Sensitive Earth Fault 11kV OHM down between poles 6J-10087 & 6J-10089. Excluded OMS No. 1675612 | July | 2019 | 2020Q1 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2019-07-20 | N | 68.8782 | N | 2 | N | N | 1.1101 | 39.4971 | 9915.825
[7 empty] | 5238 | 19383 | 1675711 | 2019-07-21 03:09 | 2019-07-21 04:24 | 75 | 11kV | 3375 | 45 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 193948 A Phase DOLF : 40 Amp Possum Excluded OMS 1675711 | July | 2019 | 2020Q1 | 2020 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2019-07-21 | N | 75 | N | 5 | N | N | 1.1101 | 39.4971 | 2466.3505
[7 empty] | 5313 | 19978 | 1675777 | 2019-07-21 17:25 | 2019-07-21 18:05 | 40 | 11kV | 2640 | 66 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At CP1409 HV Bond Blown Off. See OMS 1675777 1678999 | July | 2019 | 2020Q1 | 2020 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2019-07-21 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 1929.2341
[7 empty] | 4682 | 13945 | 1675770 | 2019-07-21 15:15 | 2019-07-21 18:16 | 181 | 11kV | 86330 | 788 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S9550 Gwawley Bay Panel 31 tripped on 50TB and C phase Cause: UGOH fault short circuit - Suspect possum See OMS 1676391 1676393 1676394 1676395 1675774 1675772 1675770 1675769 | July | 2019 | 2020Q1 | 2020 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2019-07-21 | N | 109.5558 | N | 5 | N | N | 1.1101 | 39.4971 | 63087.4177
[7 empty] | 3720 | 4117 | 1675776 | 2019-07-21 16:20 | 2019-07-21 18:33 | 133 | 11kV | 18753 | 141 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 193952 Replace broken insulators at poles BQ-90017/8/9. | July | 2019 | 2020Q1 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-07-21 | N | 133 | N | 5 | N | N | 1.1101 | 39.4971 | 13704.1393
[7 empty] | 3797 | 5003 | 1675791 | 2019-07-21 17:51 | 2019-07-21 19:55 | 124 | 11kV | 5952 | 48 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 193953 Only B phase leg opened on possible feeder fault due to car clipping pole JQ-60322. A & C ph remained closed. (Faulty operation) Software error received. Was able to clear error. Closed B phase to restore supply. Intellirupter is faulty. Incorrect operation. | July | 2019 | 2020Q1 | 2020 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2019-07-21 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 4349.546
[7 empty] | 4557 | 12631 | 1675866 | 2019-07-22 06:17 | 2019-07-22 08:02 | 105 | 11kV | 111261 | 1233 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9900 Menai Panel 1 feeder tripped on Relays: Earth Faulyt, EFI, Timing relay and lockout relay Cause: Ay S9900 Menai 11kV panel 1 UG cable fault from Menaio to S9900 to S9930 tio S9044 See OMS 1677383 1677384 1677385 1675866 | July | 2019 | 2020Q1 | 2020 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2019-07-22 | N | 90.236 | N | 1 | N | N | 1.1101 | 39.4971 | 81306.2572
[7 empty] | 3672 | 3649 | 1676065 | 2019-07-23 03:31 | 2019-07-23 05:23 | 112 | 11kV | 102074 | 1062 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT S965 Pennant Hills Panel 7 reclosed and tripped on Signals 11kV trip, Zone Earth and No1 Group Earth Cause: UG cable fault betwen S5480 to S47571 See OMS 166780 16764781 1676065 | July | 2019 | 2020Q1 | 2020 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | UG | Not Veg | 2019-07-23 | N | 96.1149 | N | 1 | N | N | 1.1101 | 39.4971 | 74592.6685
[7 empty] | 5156 | 18630 | 1676257 | 2019-07-24 02:37 | 2019-07-24 04:03 | 86 | 11kV | 140696 | 1636 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN9700 Kirrawee Panel 15 tripped on Relays: Earth fault timing and lockout, fault check and efi Abnormal Switching: SW/B at S9172 Closed, SW/A 9173 open for DMA Cause: Possum on UGOH pole to SU12708 Lineworkers to check condition of UGOH See OMS 1677388 1676257 | July | 2019 | 2020Q1 | 2020 | ZN9700:PA15 | ZN9700:PA15 | ZN09700/000015 | SUTHERLAND | OH | Veg | 2019-07-24 | N | 86 | N | 2 | N | N | 1.1101 | 39.4971 | 102816.487
[7 empty] | 3671 | 3643 | 1676345 | 2019-07-24 12:20 | 2019-07-24 13:25 | 65 | 11kV | 10595 | 163 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 194005 section isolated to make repairs at pole IV-30439 excluded oms # 1676345 | July | 2019 | 2020Q1 | 2020 | 217:33605 | 217:33605 | ZN00217/033605 | LAKE MACQUARIE | OH | Not Veg | 2019-07-24 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 7742.5135
[7 empty] | 5000 | 17199 | 1677000 | 2019-07-28 02:06 | 2019-07-28 08:00 | 354 | 11kV | 3186 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT12076 Cutrock Coonara 0.5 16A roadside HDO blown Cause: Fuse Fatigue OMS 16777783 1677004 1677000 | July | 2019 | 2020Q1 | 2020 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2019-07-28 | N | 354 | N | 1 | N | N | 1.1101 | 39.4971 | 2328.2348
[7 empty] | 4514 | 12196 | 1677407 | 2019-07-29 16:10 | 2019-07-29 17:38 | 88 | 11kV | 9304 | 106 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.11 tripped on: Earth Fault UG cable fault between S4243 Sw/B and S8243 Sw/A | July | 2019 | 2020Q1 | 2020 | ZN2196:PA11 | ZN2196:PA11 | ZN02196/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-07-29 | N | 87.7736 | N | 1 | N | N | 1.1101 | 39.4971 | 6799.0888
[7 empty] | 4845 | 15512 | 1677560 | 2019-07-30 12:13 | 2019-07-30 13:01 | 48 | 11kV | 25008 | 521 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP44824 - Locked out on OC trip and IOC trip Cause: Tree branch on OH mains near pt14102 | July | 2019 | 2020Q1 | 2020 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Veg | 2019-07-30 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 18275.1088
[7 empty] | 4425 | 11268 | 1677705 | 2019-07-30 08:15 | 2019-07-30 14:10 | 355 | 11kV | 15975 | 45 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Planned LID 194090 SINO 194090 | July | 2019 | 2020Q1 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-07-30 | N | 355 | N | 4 | N | N | 1.1101 | 39.4971 | 11674.0588
[7 empty] | 4835 | 15396 | 1677641 | 2019-07-30 21:47 | 2019-07-30 22:20 | 33 | 11kV | 726 | 22 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 194127 A Phase Suspect Transformer bushing Restored vial LV parallel | July | 2019 | 2020Q1 | 2020 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2019-07-30 | N | 33 | N | 4 | N | N | 1.1101 | 39.4971 | 530.5394
[7 empty] | 3996 | 6944 | 1677648 | 2019-07-30 23:58 | 2019-07-31 01:20 | 82 | 11kV | 76505 | 1400 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Panel 55 Feeder tripped on Signals: 11kV Trip Relays: IOC a phase EFI, earth leakage Cause: 11kV Cable fault from SW/B at S4626 Kent Cliff to SW/A at S64667 to SW/B S65872 tpo S77015 tee PT64863 See OMS 1678735 1678738 1678739 | July | 2019 | 2020Q1 | 2020 | ZN2635:PA55 | ZN2635:PA55 | ZN02635/000055 | PARRAMATTA | UG | Not Veg | 2019-07-30 | N | 54.6464 | N | 4 | N | N | 1.1101 | 39.4971 | 55907.5975
[7 empty] | 5153 | 18617 | 1677650 | 2019-07-31 00:24 | 2019-07-31 03:10 | 166 | 11kV | 354708 | 2298 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn12570 Avoca Panel 21 "LB49826" fdr hsa tripped Signals: 11kv trip AR Lock out Relays: IOC ABC phase EFI First attempt: S64802 S77326 S14356 S14357 S14355 S8012 EFI not down at S14890 Second Attempt: S64802 S77326 S14356 S4357 S14355 EFi not down at S14890 Cause: not ascertained. DOp or line worker to patrol in daylight 11kv fdr isolated at S14355/SwB to S114610/SwA & S18012/SwA Switching tag left at S1410. EFI did not operate at S14890 See 1677773,5 ex 1677650 | July | 2019 | 2020Q1 | 2020 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Veg | 2019-07-31 | N | 154.3551 | N | 3 | N | N | 1.1101 | 39.4971 | 259210.1443
[7 empty] | 3328 | 361 | 1677655 | 2019-07-31 03:29 | 2019-07-31 04:55 | 86 | 11kV | 87996 | 1157 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN965 Pennant Hills Panel 4 tripped Signals: 11kV Trip, Zone Earth, TX1 Group Earth Relays: Earth Fault, B phase timed OC and C phase IOC timed, Timing relay, Lockout and EFI Cause: UG cable fault between S7512 and S7373 See OMS 1677757 1677758 1677655 | July | 2019 | 2020Q1 | 2020 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2019-07-31 | N | 76.0553 | N | 3 | N | N | 1.1101 | 39.4971 | 64304.8814
[7 empty] | 3467 | 1662 | 1677779 | 2019-07-31 15:36 | 2019-07-31 16:42 | 66 | 11kV | 97236 | 1512 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At Sub 874 Concord Panel No.22 "Norman Rogers" feeder opned on A phase IOC, EFI 11kv Trip, Zone Earth Remarks: UG Fault. Front Line Feeder from Sub 874 Concord Panel No.22 to Sub 4153 Norman Majors | July | 2019 | 2020Q1 | 2020 | ZN874:PA22 | ZN874:PA22 | ZN00874/000022 | CANADA BAY | UG | Not Veg | 2019-07-31 | N | 64.3095 | N | 3 | N | N | 1.1101 | 39.4971 | 71057.2008
[7 empty] | 3728 | 4212 | 1677902 | 2019-08-01 07:25 | 2019-08-01 14:30 | 425 | 11kV | 239409 | 1299 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North panerl 13 tripped reclosed tripped and locke dout on Signals: 11kV Trip Relays: IOC - B and C phase, Fault Check, Lockout There is a bond blown off on the 11kV OH outside 1B Paton Place Manly Vale - The HV also came into contact with the LV See OMS 1679474 1679475 1677857 1677858 1677902 1677933 | August | 2019 | 2020Q1 | 2020 | ZN36300:PA13 | ZN36300:PA13 | ZN36300/000013 | NORTHERN BEACHES | OH | Not Veg | 2019-08-01 | N | 184.3025 | N | 2 | N | N | 1.1101 | 39.4971 | 174953.0358
[7 empty] | 5270 | 19598 | 1678052 | 2019-08-01 22:56 | 2019-08-02 01:01 | 125 | 11kV | 109158 | 874 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9035 Carringbah 11kv feeer Panel No.2 "Kitchner St" feeder tripped on: Relays: A phase IOC, EFI, timing, lockout Field EFI's: S9796 Remarks: UG fault. Note: At time of feeder failure LV // was found in due DMA dated 27/5 ratting AA. More notes available upon request of bluey | August | 2019 | 2020Q1 | 2020 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | UG | Not Veg | 2019-08-01 | N | 124.8947 | N | 2 | N | N | 1.1101 | 39.4971 | 79769.4468
[7 empty] | 4927 | 16377 | 1678074 | 2019-08-02 08:41 | 2019-08-02 09:50 | 69 | 11kV | 7038 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 194147 A Phase DOLF : 40 Amp Possible hot joint on A Ph fuse. S Geddes reported to Field Services. Excluded OMS 1678074 | August | 2019 | 2020Q1 | 2020 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Veg | 2019-08-02 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 5143.1628
[7 empty] | 3303 | 174 | 1678188 | 2019-08-02 16:30 | 2019-08-02 19:10 | 160 | 11kV | 4480 | 28 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | 11kV feeder from LB40831 to S77037 interrupted for emergency repairs to replace broken cross arm. See OMS 1678800 1678190 1678178 1678180 1678182 1678184 1678185 | August | 2019 | 2020Q1 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2019-08-02 | N | 160 | N | 3 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 4634 | 13524 | 1678211 | 2019-08-02 21:39 | 2019-08-02 22:43 | 64 | 33kV Distribution | 1229 | 22 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | LID 194164 1 fault operation C Phase Earth Fault targets: 80500 A prot C-E & M/T; B prot 51N & M/T. 90700 Dir E/F. End box Sw 57839 found blackened. Section isolated. Excluded OMS 1678211. | August | 2019 | 2020Q1 | 2020 | 417:80500 | 417:80500 | ZN00417/080500 | NEWCASTLE | UG | Not Veg | 2019-08-02 | N | 55.8636 | N | 3 | N | N | 1.1101 | 39.4971 | 898.117
[7 empty] | 3775 | 4810 | 1678444 | 2019-08-03 09:35 | 2019-08-03 12:17 | 162 | 33kV Distribution | 480 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | LID 194165 3 phase interupted to make emergency repairs/isolate defective switch 57841 Orica No 1 sub see interuption report for fdr trip LID 194164 | August | 2019 | 2020Q1 | 2020 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | UG | Not Veg | 2019-08-03 | N | 160 | N | 1 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 4131 | 8498 | 1678353 | 2019-08-04 12:02 | 2019-08-04 14:45 | 163 | 11kV | 57687 | 1183 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12580 Erina Panel 1 Tripped, reclosed tripped and locked out on IOC and Timed OC, Reclose Timing and Lockout Relays with EFI 11kV UG fault from LB62719 to S65223 tee PT11929 CP62719 cannpot be locked off and cannot be used as an isolation point. HDO replaced at PT18632 Note: Feeder tripped a second time during restoration See OMS 1679676 1679680/681/682/683/685/686/696/698/699/701 1678353 1678358 | August | 2019 | 2020Q1 | 2020 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | UG | Not Veg | 2019-08-04 | N | 48.7633 | N | 1 | N | N | 1.1101 | 39.4971 | 42155.9581
[7 empty] | 3654 | 3401 | 1678402 | 2019-08-05 00:53 | 2019-08-05 06:56 | 363 | 11kV | 48045 | 362 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn12690 Berkeley Vale 11kV Panel 22 tripped on Relays: EF and EFI Cause: UG cable fault between S14923 and S18329 See OMS 1678751 1678753 1678402 1678404 | August | 2019 | 2020Q1 | 2020 | ZN12690:PA22 | ZN12690:PA22 | ZN12690/000022 | CENTRAL COAST | UG | Not Veg | 2019-08-05 | N | 132.721 | N | 4 | N | N | 1.1101 | 39.4971 | 35109.8689
[7 empty] | 5093 | 18178 | 1678481 | 2019-08-05 10:17 | 2019-08-05 12:09 | 112 | 11kV | 258586 | 2398 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | At Zn262 Marrickville 11kv pnl 16 "Victoria Sydenham" feeder tripped on: Relays: earth fault with fault check Signals: 11kv trip, ei, Tx3 group and zone earth Remarks: Ausgrid pole crew damaged cable fromsub 5296 Middle bright to S1447 Brighton Place at 45 Railway St The pole crew were excavating for install a new pole for a upgrade to the network. The outage was caused when the Pole excavation machine made unexpected contact with on of our 11 kv cables. This contact caused the feeder to trip and resulted in an outage | August | 2019 | 2020Q1 | 2020 | ZN262:PA16 | ZN262:PA16 | ZN00262/000016 | INNER WEST | UG | Not Veg | 2019-08-05 | N | 107.834 | N | 4 | N | N | 1.1101 | 39.4971 | 188967.0218
[7 empty] | 5273 | 19615 | 1678410 | 2019-08-05 08:05 | 2019-08-05 18:00 | 595 | 11kV | 92820 | 156 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 194182 Truck hit pole dislodged A phase from 52046L and B phase from 52046R. LV, 11kV & 33kV isolated to safely replace pole. Excluded OMS 1678425 | August | 2019 | 2020Q1 | 2020 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2019-08-05 | N | 595 | N | 4 | N | N | 1.1101 | 39.4971 | 67830.1183
[7 empty] | 4275 | 9992 | 1678548 | 2019-08-05 12:45 | 2019-08-05 19:55 | 430 | 11kV | 10788 | 67 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ex S12630 Peats Ridge Panel 8 Recloser 44994 Mangrove Creek Tripped on Relays IOC trip, Lockout Cause: OH down - wires down boomerang creek track off Kyola Rd Kulnura See OMS 1678791 1678742 1678793 1678631 1678548 | August | 2019 | 2020Q1 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2019-08-05 | N | 161.0149 | N | 4 | N | N | 1.1101 | 39.4971 | 7883.5522
[7 empty] | 5211 | 19100 | 1678707 | 2019-08-06 08:41 | 2019-08-06 10:00 | 79 | 11kV | 158 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 194201 A Phase DOLF : 31 Amp Excluded OMS 1678707 | August | 2019 | 2020Q1 | 2020 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2019-08-06 | N | 79 | N | 5 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 5024 | 17487 | 1678750 | 2019-08-06 09:50 | 2019-08-06 10:27 | 37 | 11kV | 5583 | 155 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN12650 WEST GOSFORD 11kV CB Panel 16 'S50231 Faunce Batlay etc' fdr tripped on: Relays: B Phase timed O/C EFI Signals: 11kv trip, Tx13 415V no volts EFI: S50231 S14601 Cause: contractor error caused fialure Contractor digging a tree out with excavator outside 19 Sinclair St Gosforf tripped tha cables out of the ground See 1679257,8 ex 1678750,8,61,3 | August | 2019 | 2020Q1 | 2020 | ZN12650:PA16 | ZN12650:PA16 | ZN12650/000016 | CENTRAL COAST | UG | Not Veg | 2019-08-06 | N | 36.0194 | N | 5 | N | N | 1.1101 | 39.4971 | 4079.8917
[7 empty] | 3586 | 2708 | 1678736 | 2019-08-06 09:22 | 2019-08-06 10:40 | 78 | 11kV | 46124 | 647 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN187 CROWS NEST 11kV CB Panel 23 'opened on B * C phase IOC with EFI Protection Trip, Protection Latch, No.11 Tx Group Earth EFI operated @ S6876 S3173 S6527 Cause: UG Fault from S6527 to S6743 See 1679250,1 ex 1678736 | August | 2019 | 2020Q1 | 2020 | ZN187:PA23 | ZN187:PA23 | ZN00187/000023 | LANE COVE | UG | Not Veg | 2019-08-06 | N | 71.289 | N | 5 | N | N | 1.1101 | 39.4971 | 33706.0588
[7 empty] | 4958 | 16694 | 1678673 | 2019-08-06 07:33 | 2019-08-06 12:32 | 299 | 11kV | 11063 | 37 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 194185 A Phase Broken Live Line Clamp Excluded OMS 1678673 | August | 2019 | 2020Q1 | 2020 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2019-08-06 | N | 299 | N | 5 | N | N | 1.1101 | 39.4971 | 8084.5141
[7 empty] | 4506 | 12123 | 1678914 | 2019-08-07 02:16 | 2019-08-07 03:50 | 94 | 11kV | 185932 | 2138 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3155 Double Bay 11kv panel 44 "S6008 New Mclean New South Head etc" feeder tripped on Relays: 3 phase OC, fault check, EFI Signals: 11kv trip, Zone earth, Tx2 group earth Abnormal: Sw/B open @ S35572 Goodhope Glenmore (feeder DMA beyond S35572) Remarks: UG cable fault between S4522 new Beach Loftus Sw/B to S2803 New Beach Yarra Sw/A | August | 2019 | 2020Q1 | 2020 | ZN3155:PA44 | ZN3155:PA44 | ZN03155/000044 | WOOLLAHRA | UG | Not Veg | 2019-08-07 | N | 86.9654 | N | 2 | N | N | 1.1101 | 39.4971 | 135873.6215
[7 empty] | 3349 | 559 | 1679032 | 2019-08-07 13:18 | 2019-08-07 14:39 | 81 | 11kV | 76171 | 1064 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn965 Pennant Hill - Pnl.6 tripped on SEF Open bond centre phase load side of AB 453. See 1682401 1682402 | August | 2019 | 2020Q1 | 2020 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | OH | Not Veg | 2019-08-07 | N | 71.5893 | N | 2 | N | N | 1.1101 | 39.4971 | 55663.5201
[7 empty] | 4115 | 8330 | 1678854 | 2019-08-06 14:58 | 2019-08-07 14:55 | 1437 | 11kV | 33561 | 118 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | IR61097 Wise Ferry Lavender 10.3 has trip[ped Relays: OC trip and Lockout Cause: Truck hit pole O/S6129 Wisemans Ferry Rd. Pole reqiores replacement See OMS 1679660 1679661 1679662 1678886 1678864 168854 | August | 2019 | 2020Q1 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2019-08-06 | N | 284.4153 | N | 5 | N | N | 1.1101 | 39.4971 | 24525.3889
[7 empty] | 4844 | 15498 | 1679229 | 2019-08-08 11:25 | 2019-08-08 13:45 | 140 | 11kV | 15260 | 109 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn3154 St Ives Pnl.17 - 11kV Bond burnt off roadside phase, zone side of AB1388. | August | 2019 | 2020Q1 | 2020 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Not Veg | 2019-08-08 | N | 140 | N | 2 | N | N | 1.1101 | 39.4971 | 11151.5579
[7 empty] | 3387 | 859 | 1679341 | 2019-08-08 18:28 | 2019-08-08 19:29 | 61 | 11kV | 52094 | 854 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.27 tripped on: B & C Phase O/C & E/F Possum made contact with 11kV mains near PT1952 Conrad Coxes | August | 2019 | 2020Q1 | 2020 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Not Veg | 2019-08-08 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 38068.7587
[7 empty] | 4595 | 13121 | 1679369 | 2019-08-09 02:50 | 2019-08-09 04:18 | 88 | 11kV | 17424 | 198 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn931 Darlinghurst - Dist #26 tripped ON: Earth Fault Field EFIs: 7948. S8491 did not operate UG cable fault between Pnl.26 and S8491 Sw/B. | August | 2019 | 2020Q1 | 2020 | ZN931:PA26 | ZN931:PA26 | ZN00931/000026 | SYDNEY | UG | Not Veg | 2019-08-09 | N | 88 | N | 15 | N | N | 1.1101 | 39.4971 | 12732.9453
[7 empty] | 4737 | 14386 | 1679514 | 2019-08-09 11:39 | 2019-08-09 13:08 | 89 | 11kV | 90380 | 1603 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194237 2 fault operations Tree on mains adjacent ELBS 1552 Excluded OMS 1679512 | August | 2019 | 2020Q1 | 2020 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2019-08-09 | N | 56.3818 | N | 15 | N | N | 1.1101 | 39.4971 | 66047.0382
[7 empty] | 5249 | 19459 | 1679517 | 2019-08-09 13:25 | 2019-08-09 14:30 | 65 | 11kV | 260 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194245 No protection operations. Section isolated to repair broken brace strap pole JT 40006 Excluded OMS 1679517. | August | 2019 | 2020Q1 | 2020 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2019-08-09 | N | 65 | N | 15 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 4993 | 17103 | 1679704 | 2019-08-09 15:20 | 2019-08-09 16:45 | 85 | 11kV | 8075 | 95 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194251 11kV taken OOS to repair 33kV X arm OR8-0260. Refer to 1680237 | August | 2019 | 2020Q1 | 2020 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2019-08-09 | N | 85 | N | 15 | N | N | 1.1101 | 39.4971 | 5900.9718
[7 empty] | 4521 | 12233 | 1679533 | 2019-08-09 11:59 | 2019-08-09 18:00 | 361 | 11kV | 3249 | 9 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 194253 A Phase Live Line Clamp broken Excluded OMS 1679533 | August | 2019 | 2020Q1 | 2020 | 264:81232 | 264:81232 | ZN00264/081232 | MAITLAND | OH | Not Veg | 2019-08-09 | N | 361 | N | 15 | N | N | 1.1101 | 39.4971 | 2374.2734
[7 empty] | 5298 | 19826 | 1679723 | 2019-08-09 15:42 | 2019-08-09 19:00 | 198.1667 | 11kV | 198.1667 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194254 Single phase Excluded OMS 1679723 & 1679747 | August | 2019 | 2020Q1 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2019-08-09 | N | 198.1667 | N | 15 | N | N | 1.1101 | 39.4971 | 144.8144
[7 empty] | 5246 | 19435 | 1679575 | 2019-08-09 10:40 | 2019-08-09 19:41 | 541 | 11kV | 3246 | 6 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 194255 A Phase broken A phase llc, no blown fuses KERB SIDE HV LEAD BURNT OFF AT TOP OF HV DOF ASSEMBLY AT SUB 9480. Excluded oms1679468 | August | 2019 | 2020Q1 | 2020 | 238:34148 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2019-08-09 | N | 541 | N | 15 | N | N | 1.1101 | 39.4971 | 2372.0811
[7 empty] | 3592 | 2766 | 1679791 | 2019-08-09 19:22 | 2019-08-09 20:05 | 42.6833 | 11kV | 3457.35 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 194256 A Phase DOLF : 31 Amp Excluded OMS 1679791 CC1: 22-"Refer to SOp" | August | 2019 | 2020Q1 | 2020 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Veg | 2019-08-09 | N | 42.6833 | N | 15 | N | N | 1.1101 | 39.4971 | 2526.5294
[7 empty] | 5203 | 18986 | 1681004 | 2019-08-09 18:30 | 2019-08-09 20:20 | 110 | 11kV | 1870 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S11600 Lisariw Ex Panel 2 feeder de energised to allow emergency repairs from USL 41935 to AB41934 tee pt12365 AND PT46711 Cause: Tree branch on OH minas See OMS 1681005 1681004 | August | 2019 | 2020Q1 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2019-08-09 | N | 110 | N | 15 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 3739 | 4367 | 1679548 | 2019-08-09 12:08 | 2019-08-09 21:10 | 542 | 11kV | 353384 | 652 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV Recloser 49684 Brisbane Water Lara Tripped and Locked out DMA1: AB40725 Open with AB40724 Closed DMA2 AB48311 Open with LB41110 Closed OH down - HV into LV OS12 Brisbane Water Dr Koolewong See OMS 1681015 1679568 1679549 | August | 2019 | 2020Q1 | 2020 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Not Veg | 2019-08-09 | N | 542 | N | 15 | N | N | 1.1101 | 39.4971 | 258242.6041
[7 empty] | 4471 | 11703 | 1679587 | 2019-08-09 12:54 | 2019-08-09 21:50 | 536 | 11kV | 105842 | 387 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP50630 Yarramalong Chandlers tripped and reclosed oin IOC and OC Trip Cause: Large Tree brought down HV mains on section of 11kV Feeder from LK42546 to LK40948 tee PT12197 tee PT12890 See OMS 1680962 1680965 1679732 1679744 1679587 | August | 2019 | 2020Q1 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2019-08-09 | N | 273.4935 | N | 15 | N | N | 1.1101 | 39.4971 | 77346.2118
[7 empty] | 5057 | 17873 | 1679614 | 2019-08-09 13:30 | 2019-08-10 00:52 | 682 | 11kV | 36146 | 53 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | CP44806 Interrupted by DOp for emergency repairs HV CCT mains Opened LB44806 11kV CCT down adjacent to PT11023 Pomona Wards Hiill mains onsite to Carry out repairs. | August | 2019 | 2020Q1 | 2020 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2019-08-09 | N | 682 | N | 15 | N | N | 1.1101 | 39.4971 | 26414.4307
[7 empty] | 5306 | 19931 | 1679803 | 2019-08-09 14:30 | 2019-08-10 02:50 | 740 | 11kV | 130980 | 177 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT9214 Box Princess - HV interrupted for safety PT62983 Edward Rocklea - HV interrupted for safety OH 33 kV Earth Wires down near 11kV mains corner Box Rd and Princes Hwy. 11kV isolated between AB35906 to LB35013 tee PT9214. See 1679825 1679826 | August | 2019 | 2020Q1 | 2020 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | OH | Not Veg | 2019-08-09 | N | 740 | N | 15 | N | N | 1.1101 | 39.4971 | 95716.3207
[7 empty] | 5263 | 19551 | 1679823 | 2019-08-09 23:10 | 2019-08-10 03:36 | 266 | 11kV | 43358 | 163 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Section of 11kV OH isolated from LB43567 to LB62907 to AB43024 tee PT12591, PT11479 and PT62992 cause: tree across HV cct on Pole AV3586 See OMS 1679829 1679823 1679824 | August | 2019 | 2020Q1 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2019-08-09 | N | 266 | N | 15 | N | N | 1.1101 | 39.4971 | 31684.7476
[7 empty] | 4898 | 15958 | 1679789 | 2019-08-09 18:51 | 2019-08-10 07:35 | 764 | 11kV | 3056 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194258 A & B Phase DOLF : 20 Amp Excluded OMS 1679789 | August | 2019 | 2020Q1 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-08-09 | N | 764 | N | 15 | N | N | 1.1101 | 39.4971 | 2233.2347
[7 empty] | 4318 | 10355 | 1679914 | 2019-08-10 12:00 | 2019-08-10 13:37 | 97 | 11kV | 31583 | 332 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Panel 23 exiting Zn2400 Berowra Tripped, Reclosed tripped and locked out Cause: There was a large tree branch on the 11kV OH on the corner of the pacific highway and Collingridge Way Berowra See OMS 1680980 1680981 1679914 1679924 | August | 2019 | 2020Q1 | 2020 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | OH | Veg | 2019-08-10 | N | 95.1295 | N | 3 | N | N | 1.1101 | 39.4971 | 23079.9249
[7 empty] | 5038 | 17657 | 1679981 | 2019-08-10 17:12 | 2019-08-10 19:01 | 108.5833 | 11kV | 27145.8333 | 250 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 194267 A & B Phase DOLF : 40 Amp bird in mains pole HW-70822. No further action req. dq excluded oms1679987 | August | 2019 | 2020Q1 | 2020 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2019-08-10 | N | 108.5833 | N | 3 | N | N | 1.1101 | 39.4971 | 19837.3743
[7 empty] | 4148 | 8665 | 1679969 | 2019-08-10 17:15 | 2019-08-10 21:00 | 225 | 11kV | 8550 | 38 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194268 3 phase interupted for safety due to tree branch on ohm pole MW90010. dq LID 194266 large tree branch on 11kv mains section isolated for repairs | August | 2019 | 2020Q1 | 2020 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2019-08-10 | N | 225 | N | 3 | N | N | 1.1101 | 39.4971 | 6248.0878
[7 empty] | 3872 | 5692 | 1680025 | 2019-08-11 06:45 | 2019-08-11 09:30 | 165 | 11kV | 49830 | 302 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 194270 & 194271 intrupted to repair car hit pole JT-71556 section isolated to make repairs at pole JT-71556 Excluded oms # 1680025 1680029 1680030 1680031 | August | 2019 | 2020Q1 | 2020 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2019-08-11 | N | 165 | N | 3 | N | N | 1.1101 | 39.4971 | 36414.2943
[7 empty] | 5102 | 18242 | 1680109 | 2019-08-11 13:36 | 2019-08-11 14:13 | 37 | 11kV | 4240 | 118 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.8 tripped on: Earth Fault UG cable fault in front line section of feeder between Pnl.8 and S9017 Sw/A | August | 2019 | 2020Q1 | 2020 | ZN9035:PA8 | ZN9035:PA8 | ZN09035/000008 | SUTHERLAND | UG | Not Veg | 2019-08-11 | N | 35.9322 | N | 3 | N | N | 1.1101 | 39.4971 | 3098.4669
[7 empty] | 4375 | 10813 | 1680140 | 2019-08-11 17:18 | 2019-08-11 18:50 | 92 | 11kV | 276 | 3 | HV | Wind Blown Debris | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 194277 excluded OMS 1680140 | August | 2019 | 2020Q1 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-08-11 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 201.6927
[7 empty] | 4231 | 9569 | 1680413 | 2019-08-12 19:22 | 2019-08-12 21:15 | 113 | 11kV | 73118 | 1534 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | AT S12610 Long Jetty Panel 11 Tripped on B phase OC - Reclose time delay, Lockout EF check, SEL Cause: 11kV Bond off UGOH to S14377 SW/A Boorana Wyong See OMS 1680934/935/936/937 1680413/415/416/417 | August | 2019 | 2020Q1 | 2020 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2019-08-12 | N | 47.6649 | N | 1 | N | N | 1.1101 | 39.4971 | 53432.4778
[7 empty] | 4549 | 12546 | 1680561 | 2019-08-13 11:50 | 2019-08-13 13:10 | 80 | 11kV | 2296 | 32 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194305 wire off pin Pole SF-40262 | August | 2019 | 2020Q1 | 2020 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2019-08-13 | N | 71.75 | N | 2 | N | N | 1.1101 | 39.4971 | 1677.8491
[7 empty] | 3962 | 6555 | 1680661 | 2019-08-13 18:20 | 2019-08-13 21:55 | 215 | 11kV | 1495 | 7 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | AT S2196 Milperra Ex panel No.5 "S8696 Marigold Amour No4 feeder" PT61716 Maxlaw and PT2003 Webster St were interrupted after a truck hit pole, HV cable had come off the insulator on pole #EH00596 Note: DMA on panel 5 from AB1565 to LB133 to AB2362 so feeder couldn't be switched. Abnormal: Lb133 open, sw/A at S8011 Truscott Batchelor closed Remarks: vehicle hit pole. Dop and lineworker repaired and restored | August | 2019 | 2020Q1 | 2020 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-08-13 | N | 213.5714 | N | 2 | N | N | 1.1101 | 39.4971 | 1092.5019
[7 empty] | 3777 | 4820 | 1680793 | 2019-08-14 12:30 | 2019-08-14 13:35 | 65 | 11kV | 650 | 10 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194319 Section isolated at ABS 17175 to remove tree from Fdr at GW-40236 Supply off 1230hrs back on 1335hrs | August | 2019 | 2020Q1 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-08-14 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 4332 | 10457 | 1680830 | 2019-08-14 15:34 | 2019-08-14 17:43 | 129 | 11kV | 3870 | 30 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194322 B Phase Cracked insulator at cap bank. Excluded oms 1680830. | August | 2019 | 2020Q1 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2019-08-14 | N | 129 | N | 2 | N | N | 1.1101 | 39.4971 | 2828.0819
[7 empty] | 4735 | 14382 | 1681155 | 2019-08-16 11:55 | 2019-08-16 12:45 | 50 | 11kV | 6250 | 125 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S847 Hornsby ex panel 21 from S4617 to S49774 Rosamond Watson tee PT64487 and PT2425 Manor Arriogna interrupted for safety toi allow removal of tree branch os 17 Watson Ave Hornsby | August | 2019 | 2020Q1 | 2020 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2019-08-16 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 4567.3157
[7 empty] | 4800 | 15057 | 1681156 | 2019-08-16 16:55 | 2019-08-16 18:50 | 115 | 11kV | 5865 | 51 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 194356 11kV mains stranding at pole JT-70831. Isolated section 11kV to repair. 33kV Fdr 3305 isolated for safety refer to LID194357 CASS B PHASE 11 KV CONDUCTOR BETWEEN POLES KT40829 AND KT70831 HAS ONLY A FEW STRANDS HOLDING IT TOGETHER, ISSUE REGARDING ACCESS/DUNES, ACCESS VIA A GATE 15M FROM KT40829, NOTIFIED SECURITY THAT CREWS WILL BE ATTENDING. | August | 2019 | 2020Q1 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2019-08-16 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 4285.969
[7 empty] | 5288 | 19754 | 1681289 | 2019-08-16 21:26 | 2019-08-16 22:17 | 51 | 11kV | 100968 | 2068 | HV | Animal Possum | Animal | Bond | Unplanned | No Weather Impact | N | At CP40219 Bond Burnt off Abnormal Switching SW/A Open , SW/A Closed at S14377 See OMS 182397 1681289 1681296 1681308 1681309 1681310 1681312 1681313 | August | 2019 | 2020Q1 | 2020 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2019-08-16 | N | 48.824 | N | 3 | N | N | 1.1101 | 39.4971 | 73784.4363
[7 empty] | 5175 | 18770 | 1681337 | 2019-08-17 08:29 | 2019-08-17 10:45 | 136.15 | 11kV | 408.45 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 194359 20 Amp fuse, Line DOLF | August | 2019 | 2020Q1 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-08-17 | N | 136.15 | N | 2 | N | N | 1.1101 | 39.4971 | 298.4832
[7 empty] | 3407 | 1065 | 1681419 | 2019-08-17 18:55 | 2019-08-17 20:12 | 77 | 11kV | 91630 | 1190 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN965 Pennant Hills Panel 8 Tripped on Relays: B phase Overcurrent Signals Zone and TX1 Group earth Cause: Cable Fault from S5581 to S5689 | August | 2019 | 2020Q1 | 2020 | ZN965:PA8 | ZN965:PA8 | ZN00965/000008 | HORNSBY | UG | Not Veg | 2019-08-17 | N | 77 | N | 2 | N | N | 1.1101 | 39.4971 | 66960.5014
[7 empty] | 3296 | 92 | 1681477 | 2019-08-18 11:15 | 2019-08-18 12:34 | 79 | 11kV | 5375 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S14144 Wamberal Panel 4 tripped on 50T IOC A and B phase @PT12362 Footpath and Centre phase HDO blown Cause: Tree branch contact PT12362 See OMS 1682357 1682358 1681477 1681481 1681482 1681479 | August | 2019 | 2020Q1 | 2020 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2019-08-18 | N | 6.3161 | N | 2 | N | N | 1.1101 | 39.4971 | 3927.8915
[7 empty] | 5300 | 19832 | 1681436 | 2019-08-18 00:57 | 2019-08-18 12:50 | 713 | 11kV | 230322 | 2007 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At Zn14892 Charmhaven Panel 16 Charmhaven San Remo has tripped Signals: 11kV Trip Relays: OCEF relay - 51N, Faulct Chekc, Recloser Timer , Lockout, Prohibition Relay Cause: 65 Panorama St - Police Suspect white hilux hit pole whilst performing burnout. 11kV into low and on the ground. Customers switchboard at 11 Tingira St failed expolosively as a result 1682346 1682347 1682349 161437 1681438 1681444 1682350 1681436 | August | 2019 | 2020Q1 | 2020 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2019-08-18 | N | 114.7593 | N | 2 | N | N | 1.1101 | 39.4971 | 168312.5243
[7 empty] | 3848 | 5483 | 1681801 | 2019-08-20 01:26 | 2019-08-20 02:41 | 75 | 11kV | 40200 | 536 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 24 Tripped on Relays: Earth Fault, EFI, Fault Check, TX2 Fault Check Signals: Tx2 Group Earth, Zone Earth, 11kV Trip Cause: Section of 11kV defective Zn4545 Meadowbank Pa24 to S1835. | August | 2019 | 2020Q1 | 2020 | ZN4545:PA24 | ZN4545:PA24 | ZN04545/000024 | RYDE | UG | Not Veg | 2019-08-20 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 29376.9743
[7 empty] | 5285 | 19722 | 1681809 | 2019-08-20 07:38 | 2019-08-20 09:07 | 89 | 11kV | 36890 | 418 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At ZN8000 Macquarie Park Panel 10 feeder has tripped on Signals: 11kV Trip Relays: Pa10 Earth Fault, EFI and Fault Check Cause: Cable strike adjacent tio S77944 Spine Epping. See OMS 1682386 1681809 1682387 | August | 2019 | 2020Q1 | 2020 | ZN8000:PA10 | ZN8000:PA10 | ZN08000/000010 | RYDE | UG | Not Veg | 2019-08-20 | N | 88.2536 | N | 2 | N | N | 1.1101 | 39.4971 | 26958.1239
[7 empty] | 4998 | 17180 | 1682027 | 2019-08-21 10:33 | 2019-08-21 11:28 | 55 | 11kV | 11180 | 207 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.2 tripped on: Earth Fault UG cable fault S35168 Sw/B to S7635 Sw/A See 1682262 1682263 | August | 2019 | 2020Q1 | 2020 | ZN8100:PA2 | ZN8100:PA2 | ZN08100/000002 | SYDNEY | UG | Not Veg | 2019-08-21 | N | 54.0097 | N | 2 | N | N | 1.1101 | 39.4971 | 8170.0142
[7 empty] | 3417 | 1148 | 1682139 | 2019-08-21 19:49 | 2019-08-21 20:55 | 66 | 11kV | 80560 | 1789 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn12610 Long Jetty Panel 6 bond burn off adjacent to AB40821 See OMS 1682391 1682392 1682139 | August | 2019 | 2020Q1 | 2020 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2019-08-21 | N | 45.0307 | N | 2 | N | N | 1.1101 | 39.4971 | 58870.8719
[7 empty] | 4060 | 7686 | 1682224 | 2019-08-22 09:52 | 2019-08-22 11:04 | 72 | 11kV | 23242 | 326 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S188 Zetland Panel 15 tripped on earth Leakage EFI and Fault Check. Cause; Contractor Struck Cable @ 511 Botney Rd Zetland See OMS 1683609 1683611 1682228 1682224 | August | 2019 | 2020Q1 | 2020 | ZN188:PA15 | ZN188:PA15 | ZN00188/000015 | SYDNEY | UG | Not Veg | 2019-08-22 | N | 71.2945 | N | 3 | N | N | 1.1101 | 39.4971 | 16984.5681
[7 empty] | 4994 | 17123 | 1682290 | 2019-08-22 13:04 | 2019-08-22 19:40 | 396 | 11kV | 373724 | 1712 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12650 West Gosford Panel 1 fdr tripped, reclosed & locked out on: Relays: A & C phase OC, EFI, Reclose & Lock out Signals: 11kv trip Abnormal: RE44936 bypass closed Cause: Tree brought down 11kv mains outside 47 alan st Niagara Park. Section of 11kv fdr from LB45434 to AB444473 tee PT11779 , PT14550. Section of 11kv from Zn12650 Panel 1 to LB62727 to CP47848 to CP44936 isolated for safety. 415V Dist 1 PT12211 isolated for safety See 1682879,80 81 ex 1682369,290 | August | 2019 | 2020Q1 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2019-08-22 | N | 218.2967 | N | 3 | N | N | 1.1101 | 39.4971 | 273106.4762
[7 empty] | 3961 | 6537 | 1682385 | 2019-08-22 20:08 | 2019-08-22 20:55 | 47 | 11kV | 6392 | 136 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 194436 section isolated for repairs at pole JV-20675 Excluded oms # 1682385 1682417 | August | 2019 | 2020Q1 | 2020 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2019-08-22 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 4671.0851
[7 empty] | 3315 | 220 | 1682466 | 2019-08-23 08:56 | 2019-08-23 10:23 | 87 | 11kV | 82522 | 1053 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S398 Dulwich Hill Panel 29 Tripped on Signals: 11kV Trip, Zone Earth, Tx4 Group Eartth Relays: Earth Fault, EFI See OMS 1683594 1683597 1682466 1682468 | August | 2019 | 2020Q1 | 2020 | ZN398:PA29 | ZN398:PA29 | ZN00398/000029 | INNER WEST | UG | Not Veg | 2019-08-23 | N | 78.3685 | N | 2 | N | N | 1.1101 | 39.4971 | 60304.6436
[7 empty] | 3376 | 765 | 1682528 | 2019-08-23 13:38 | 2019-08-23 15:40 | 122 | 11kV | 244 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 194454 Single phase DOLF : 10 Amp sub isolated to replace blown arrestor Excluded oms 1682528 | August | 2019 | 2020Q1 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-08-23 | N | 122 | N | 2 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 3744 | 4417 | 1682597 | 2019-08-24 02:52 | 2019-08-24 04:50 | 118 | 11kV | 32154 | 327 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn15014 Mona Vale Panel 15 has tripped on Relays: IOC trip, OC trip and Lockout Cause: Tre eon OH mains at pole TH3587 - Caused mains to come of pin insulator PT15577 Sanitary Depot in LV parallel - link 43223 see event ID3641 See OMS 1683426 168379 1683378 1682597 | August | 2019 | 2020Q1 | 2020 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2019-08-24 | N | 98.3303 | N | 3 | N | N | 1.1101 | 39.4971 | 23497.1948
[7 empty] | 3335 | 447 | 1682642 | 2019-08-24 11:53 | 2019-08-24 14:00 | 127 | 11kV | 127 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194461 Live Line lead broke away at sub. No protection Excluded OMS 1682646 and 1682642 | August | 2019 | 2020Q1 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2019-08-24 | N | 127 | N | 3 | N | N | 1.1101 | 39.4971 | 92.8079
[7 empty] | 4053 | 7614 | 1682653 | 2019-08-24 12:59 | 2019-08-24 14:00 | 61 | 11kV | 305 | 5 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194462 C Phase DOLF : 10 Amp Blown Dolf suspect caused by high winds today. Excluded OMS 1682653 | August | 2019 | 2020Q1 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-08-24 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 222.885
[7 empty] | 4299 | 10213 | 1682690 | 2019-08-25 07:27 | 2019-08-25 07:36 | 9 | 11kV | 19215 | 2135 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 194465 1 fault operation Sensitive Earth fault Sub 15129 had blown DOLF started to interconnect LV and trippd Fdr on SEF. Restored Fdr,Isolated sub & closed LV parallels to restore supply to sub 15129. Excluded OMS 1682694, 1682690, 1682695 | August | 2019 | 2020Q1 | 2020 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2019-08-25 | N | 9 | N | 4 | N | N | 1.1101 | 39.4971 | 14041.7553
[7 empty] | 4134 | 8520 | 1682695 | 2019-08-25 06:08 | 2019-08-25 08:05 | 117 | 11kV | 11934 | 102 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 194470 Single phase DOLF : 40 Amp Blown LA A phase, restored LV by interrconnecting Links. See reports 194465 & 194471 Excluded OMS 1682694 | August | 2019 | 2020Q1 | 2020 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2019-08-25 | N | 117 | N | 4 | N | N | 1.1101 | 39.4971 | 8721.0152
[7 empty] | 3559 | 2575 | 1682721 | 2019-08-25 15:10 | 2019-08-25 17:00 | 110 | 11kV | 330 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194472 11kV wire off insulator at pole 9K-40077 & tree branch on service wire from sub 72840. Excluded OMS No. 1682721 | August | 2019 | 2020Q1 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-08-25 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 5046 | 17776 | 1682716 | 2019-08-25 16:10 | 2019-08-25 19:05 | 175 | 11kV | 40075 | 229 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | At S36200 Empire Bay HV cvable has come off insulator adjacent to USL 42217 LB42218 Opened for safety and for DOp to make Isolations of lineworker. Ap to be issuesd to make repairs Cause: Insulator has rusted through and broken away from pole 11kV Wire haniging low See OMS 1682747 1682716 | August | 2019 | 2020Q1 | 2020 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2019-08-25 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 29285.628
[7 empty] | 3524 | 2253 | 1682793 | 2019-08-26 08:12 | 2019-08-26 13:19 | 307 | 11kV | 48506 | 158 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 194475 Fire brought down tree onto Fdr near sub 1924 section isolated for repairs supply off 0812hrs back on 1319hrs | August | 2019 | 2020Q1 | 2020 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2019-08-26 | N | 307 | N | 6 | N | N | 1.1101 | 39.4971 | 35446.7541
[7 empty] | 4715 | 14248 | 1682806 | 2019-08-26 08:11 | 2019-08-26 13:40 | 329 | 11kV | 33735 | 404 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex S10997 Sans Souci - Section of 11kV OH from LB31160 to AB30772 to LB31202 Cause: Boken Cross Arm near LB 31160 11kV Down and into LV service to 580 Rocky Point Rd. EMSO organised to Check HV/LV Intermix See OMS 1683226 1683227 1683229 1682858 1682859 1682806 1682794 | August | 2019 | 2020Q1 | 2020 | ZN10997:PA11 | ZN10997:PA11 | ZN10997/000011 | GEORGES RIVER | OH | Not Veg | 2019-08-26 | N | 83.5025 | N | 6 | N | N | 1.1101 | 39.4971 | 24652.543
[7 empty] | 4084 | 8003 | 1682942 | 2019-08-26 13:58 | 2019-08-26 15:17 | 79 | 11kV | 2212 | 28 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12570 Avoca Panel 37L Tripped and reclosed Relays: B and C phase IOC and efi Signals 11kV Trtip Field EFI's Nil Abnormal Switching: AB40431 Open, SW/A Open at S14561 LB40436 Closed Cause: Branch hit HV mains o/s360 Avoca Dr Avoca Beach | August | 2019 | 2020Q1 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2019-08-26 | N | 79 | N | 6 | N | N | 1.1101 | 39.4971 | 1616.4644
[7 empty] | 3619 | 2998 | 1682961 | 2019-08-26 14:29 | 2019-08-26 15:38 | 69 | 11kV | 41400 | 600 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP45180 Avoca Beach Tripped Relays: Dead tree branch on mains opp 1004 Ridgeway Rd Avoca Beach | August | 2019 | 2020Q1 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2019-08-26 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 30253.8989
[7 empty] | 4072 | 7806 | 1682982 | 2019-08-26 16:58 | 2019-08-26 17:45 | 47 | 11kV | 61570 | 1310 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV panel 31 tripped, reclosed tripped and locked out on Signals: 11kV Trip Relays: B and C phase IOC, EFI, Lockout and Timing Cause: A stick was found on the 11kV OS 7 Shartland Ave Chatswood | August | 2019 | 2020Q1 | 2020 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2019-08-26 | N | 47 | N | 6 | N | N | 1.1101 | 39.4971 | 44993.54
[7 empty] | 4816 | 15185 | 1683087 | 2019-08-27 09:08 | 2019-08-27 10:02 | 54 | 11kV | 250388 | 4810 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.70 tripped on: Earth Fault, A Phase IOC UG cable fault between S267 Sw/A and S63605 Sw/B and S5624 See 1683359 1683360 | August | 2019 | 2020Q1 | 2020 | ZN384:PA70 | ZN384:PA70 | ZN00384/000070 | SYDNEY | UG | Not Veg | 2019-08-27 | N | 52.0557 | N | 4 | N | N | 1.1101 | 39.4971 | 182976.1652
[7 empty] | 4406 | 11096 | 1682778 | 2019-08-26 06:10 | 2019-08-27 14:30 | 1940 | 11kV | 1940 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Transformer | Unplanned | No Weather Impact | N | S35374 Christina Miller No.2 - HV fuses operated on RMI Car hit kiosk LV board and kiosk badly damaged - requires full replacement. S6480 Christina Miller - Dist #2 - Interrupted to allow UGOH to S35374 Dist #1 to be reconnected. See 1682821 1682846 | August | 2019 | 2020Q1 | 2020 | ZN1290:PA8 | ZN1290:PA8 | ZN01290/000008 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-08-26 | N | 1940 | N | 6 | N | N | 1.1101 | 39.4971 | 1417.6948
[7 empty] | 3390 | 873 | 1683216 | 2019-08-27 13:35 | 2019-08-27 15:10 | 95 | 11kV | 55466 | 584 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.15 tripped on Earth Fault UG cable fault between S1150 Sw/B and S6145 Sw/A See 1683384 1683385 | August | 2019 | 2020Q1 | 2020 | ZN2466:PA15 | ZN2466:PA15 | ZN02466/000015 | CUMBERLAND | UG | Not Veg | 2019-08-27 | N | 94.976 | N | 4 | N | N | 1.1101 | 39.4971 | 40532.9168
[7 empty] | 3680 | 3722 | 1683240 | 2019-08-27 14:22 | 2019-08-27 15:35 | 73 | 11kV | 61258 | 866 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9990 Menai - Pnl.3 tripped on: earth fault UG cable fault between Pnl.3 and S9141 Sw/A and S9327 Sw/A | August | 2019 | 2020Q1 | 2020 | ZN9900:PA3 | ZN9900:PA3 | ZN09900/000003 | SUTHERLAND | UG | Not Veg | 2019-08-27 | N | 70.7367 | N | 4 | N | N | 1.1101 | 39.4971 | 44765.5396
[7 empty] | 3951 | 6458 | 1683289 | 2019-08-27 22:25 | 2019-08-27 23:42 | 77 | 11kV | 81044 | 1199 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 194497 C phase Overcurrent; Earth Fault Excluded OMS 1683289 | August | 2019 | 2020Q1 | 2020 | 801:74119 | 801:74119 | ZN00801/074119 | MUSWELLBROOK | OH | Veg | 2019-08-27 | N | 67.593 | N | 4 | N | N | 1.1101 | 39.4971 | 59224.5648
[7 empty] | 5337 | 20286 | 1683490 | 2019-08-29 05:55 | 2019-08-29 07:06 | 71 | 11kV | 50623 | 713 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.26 tripped on: A & B phase O/C Abnormal: S8243 Edgar Millperra Sw/B Closed with Sw/A open for DMA Dead bird found bellow 11kV OH cnr Edgar & Eldridge Sts. | August | 2019 | 2020Q1 | 2020 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-08-29 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 36993.7953
[7 empty] | 4018 | 7182 | 1683524 | 2019-08-29 08:48 | 2019-08-29 15:56 | 428 | 11kV | 232605 | 2037 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | At Zn12610 Long Jetty 11kV Feeder tripped and locked out on SEF Cause: 11kV Bond Failure Phase down to CP61730 See OMS 1684955 1683524 | August | 2019 | 2020Q1 | 2020 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2019-08-29 | N | 114.19 | N | 4 | N | N | 1.1101 | 39.4971 | 169980.8733
[7 empty] | 3291 | 13 | 1683658 | 2019-08-29 16:49 | 2019-08-29 18:42 | 113 | 11kV | 66400 | 638 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 194531 2 fault operations 3 phase Earth Fault Excluded OMS 1683658 | August | 2019 | 2020Q1 | 2020 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Veg | 2019-08-29 | N | 104.0752 | N | 4 | N | N | 1.1101 | 39.4971 | 48523.1615
[7 empty] | 3888 | 5832 | 1683700 | 2019-08-29 20:52 | 2019-08-29 22:53 | 121 | 11kV | 263081 | 2481 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn3922 Drummoyne Panel 5 "S.36165 Brynes Mannings' feeder has tripped Signals: 11kv trip, No.1 tx group earth, zone earth Relay: C phase timed O/C, efi, fault check Remarks: UG fualt. 11kv UG fault between S.8394 Wulumay Waragal No.2 Sw/B to S.2595 Wisebeach St Sw/A | August | 2019 | 2020Q1 | 2020 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2019-08-29 | N | 106.0383 | N | 4 | N | N | 1.1101 | 39.4971 | 192251.8352
[7 empty] | 3374 | 728 | 1683725 | 2019-08-30 00:01 | 2019-08-30 01:26 | 85 | 11kV | 11135 | 131 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN15013 Terrey Hills Panel 4 CP 213510 Booralie Kulgoa tripped on Relays: O/C Signals: Zone Earth, CP 21350 Cause - DOp cleared bark off UGOH | August | 2019 | 2020Q1 | 2020 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | Unknown | Unknown | 2019-08-30 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 8137.1296
[7 empty] | 3584 | 2695 | 1683740 | 2019-08-30 05:41 | 2019-08-30 08:12 | 151 | 11kV | 238249 | 1629 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn13000 Lake Munmorah Panel 11 Tripped and reclosed on IOC A and B phase 11kV Roadside Bond blown at Link 43196 See OMS 1684949 1684938 1684939 | August | 2019 | 2020Q1 | 2020 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2019-08-30 | N | 146.2548 | N | 11 | N | N | 1.1101 | 39.4971 | 174105.342
[7 empty] | 3621 | 3002 | 1683736 | 2019-08-30 04:03 | 2019-08-30 08:19 | 256 | 11kV | 11423 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser CP705 Knights Chad Tripped and Lockedout on Earth Fault. Cause: DOp patrolled and could not find any issues See OMS1684409 1684415 1684416 1683736 1683737 | August | 2019 | 2020Q1 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-08-30 | N | 228.46 | N | 11 | N | N | 1.1101 | 39.4971 | 8347.5915
[7 empty] | 4446 | 11455 | 1683728 | 2019-08-30 02:06 | 2019-08-30 13:50 | 704 | 11kV | 60748 | 420 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn14891 Wyong Panel 5 Recloser CP40082 Jilliby Tripped and Locked out on O/C Cause: DOp found bond off at LB41176 (Line side) See OMS 1684974 1684973 1684970 1683735 1683734 1683733 1683731 1683730 1683728 | August | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-08-30 | N | 144.6381 | N | 11 | N | N | 1.1101 | 39.4971 | 44392.8466
[7 empty] | 3901 | 5970 | 1683837 | 2019-08-30 11:10 | 2019-08-30 16:01 | 291 | 11kV | 2910 | 10 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 194549 3 phase interupted to carry out tree removal to maintain statutory compliance. OMS 1683837. dq See NAR 45120. Unplanned interuption between LF 49510 and LF 8556 only | August | 2019 | 2020Q1 | 2020 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2019-08-30 | N | 291 | N | 11 | N | N | 1.1101 | 39.4971 | 2126.5422
[7 empty] | 4976 | 16869 | 1683891 | 2019-08-30 15:03 | 2019-08-30 16:30 | 87 | 11kV | 435 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 194550 A Phase DOLF Branch on L/A's Excluded OMS 1683891 | August | 2019 | 2020Q1 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-08-30 | N | 87 | N | 11 | N | N | 1.1101 | 39.4971 | 317.8852
[7 empty] | 4445 | 11443 | 1683910 | 2019-08-30 15:57 | 2019-08-30 17:01 | 64 | 11kV | 30805 | 500 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.21 tripped on: Earth Fault Field EFIs: S1696 S63099 UG cable fault between S63099 Sw/B and S7755 Sw/A. Joint failed in pit cnr New South Head Rd and Wolseley Rd (outside Cranbrook School) See 1684489 1684490 | August | 2019 | 2020Q1 | 2020 | ZN3155:PA21 | ZN3155:PA21 | ZN03155/000021 | WOOLLAHRA | UG | Not Veg | 2019-08-30 | N | 61.61 | N | 11 | N | N | 1.1101 | 39.4971 | 22511.3854
[7 empty] | 4923 | 16317 | 1683950 | 2019-08-30 17:45 | 2019-08-30 19:10 | 85 | 11kV | 10025 | 127 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kV OH Feeder from USL 43322 to LB 40068 tee PT11261 and PT13471 DCs interrupted to repair HV bond @ LB41176 See OMS 1683950 1683951 | August | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-08-30 | N | 78.937 | N | 11 | N | N | 1.1101 | 39.4971 | 7325.9743
[7 empty] | 4309 | 10306 | 1683881 | 2019-08-30 14:16 | 2019-08-30 19:15 | 299 | 11kV | 6997 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S14143 Somersby Panel 10 tripped and locked out on Relays: A and B phase IOC Signals: 11kV Trip Cause: Tree branch on OH mains 0 Large tree branch on 11kV OH near PT18563 See OMS 1684964 1684965 1684966 1683887 1683881 | August | 2019 | 2020Q1 | 2020 | ZN14143:PA10 | ZN14143:PA10 | ZN14143/000010 | CENTRAL COAST | OH | Veg | 2019-08-30 | N | 124.9464 | N | 11 | N | N | 1.1101 | 39.4971 | 5113.2012
[7 empty] | 4236 | 9604 | 1683961 | 2019-08-30 18:09 | 2019-08-30 22:40 | 271 | 11kV | 1084 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 194551 Single phase Repaired LV cable between bushing & LVF. Excluded OMS 1683980, 1683961 | August | 2019 | 2020Q1 | 2020 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2019-08-30 | N | 271 | N | 11 | N | N | 1.1101 | 39.4971 | 792.1552
[7 empty] | 4387 | 10888 | 1683995 | 2019-08-31 10:00 | 2019-08-31 10:55 | 55 | 11kV | 55 | 1 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 194553 B Phase DOLF : 10 Amp Magpie nest on LA | August | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-08-31 | N | 55 | N | 6 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 3495 | 1989 | 1684066 | 2019-08-31 09:42 | 2019-08-31 12:40 | 178 | 11kV | 178 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 194555 Evidence of bird activity and LA covers Missing/ Dislodged. Excluded oms 1684066 | August | 2019 | 2020Q1 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-08-31 | N | 178 | N | 6 | N | N | 1.1101 | 39.4971 | 130.0771
[7 empty] | 3820 | 5315 | 1683942 | 2019-08-30 17:13 | 2019-08-31 15:10 | 1317 | 11kV | 63753 | 949 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12600 Lisarow Panel 11 tripped, reclosed tripped and locked out on Relays: A phase OC Cause: Large tree on OH near AB44963 See OMS 1684942 1684943 1684946 1683942 1683972 | August | 2019 | 2020Q1 | 2020 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Veg | 2019-08-30 | N | 67.1791 | N | 11 | N | N | 1.1101 | 39.4971 | 46588.812
[7 empty] | 5021 | 17435 | 1684114 | 2019-08-31 13:08 | 2019-08-31 19:15 | 367 | 11kV | 367 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 194558 LV between trans and LVF faulty sub isolated for repairs Excluded OMS 1684114 | August | 2019 | 2020Q1 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2019-08-31 | N | 367 | N | 6 | N | N | 1.1101 | 39.4971 | 268.1928
[7 empty] | 5076 | 18095 | 1684187 | 2019-08-31 18:17 | 2019-08-31 20:50 | 153 | 11kV | 459 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 194560 A Phase DOLF : 20 Amp Second time in a week. May need arrestors changing. Excluded OMS 1684187 | August | 2019 | 2020Q1 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-08-31 | N | 153 | N | 6 | N | N | 1.1101 | 39.4971 | 335.4237
[7 empty] | 4287 | 10060 | 1684141 | 2019-08-31 14:42 | 2019-08-31 21:25 | 403 | 11kV | 60105 | 946 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At S12260 Woy Woy Panel 16 tripped Cause: OH resting on Crossarm O/S 18 Inkerman Avenue Broken HV crossarm - High into Low See OMS 1684976 1684977 1684978 1684979 1684980 1684179 1684154 1684148 1684142 1684141 | August | 2019 | 2020Q1 | 2020 | ZN12660:PA16 | ZN12660:PA16 | ZN12660/000016 | CENTRAL COAST | OH | Not Veg | 2019-08-31 | N | 63.5359 | N | 6 | N | N | 1.1101 | 39.4971 | 43922.9612
[7 empty] | 5122 | 18385 | 1683997 | 2019-08-31 01:30 | 2019-08-31 23:59 | 1349 | 11kV | 12114 | 9 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Section of Panel No 11 Somersby feeder ex 12630 Peats Ridge from LB 79577 to LB46841 te PT77997 and PT13779 Cause: at PT13779 Wise Ferry Konda 2.8 pole damaged - requires replacement - interrupted to make safet - pole could fail Vehicle hit pole See OMS 1684006 1684005 1683997 | August | 2019 | 2020Q1 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2019-08-31 | N | 1346 | N | 6 | N | N | 1.1101 | 39.4971 | 8852.5539
[7 empty] | 3591 | 2765 | 1684232 | 2019-09-01 10:05 | 2019-09-01 13:35 | 210 | 11kV | 70980 | 338 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 194569 Broke crossarm JT 70152 section isolated for repair Excluded OMS 1684232 | September | 2019 | 2020Q1 | 2020 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Not Veg | 2019-09-01 | N | 210 | N | 3 | N | N | 1.1101 | 39.4971 | 51870.0904
[7 empty] | 5244 | 19418 | 1684216 | 2019-09-01 06:48 | 2019-09-01 15:26 | 518 | 11kV | 106928 | 1236 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 194572 2 fault operations Earth Fault Tree on Fdr at IV-80463 Excluded OMS 1684227 | September | 2019 | 2020Q1 | 2020 | 270:83587 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2019-09-01 | N | 86.5113 | N | 3 | N | N | 1.1101 | 39.4971 | 78139.8286
[7 empty] | 4449 | 11484 | 1684269 | 2019-09-01 14:39 | 2019-09-01 15:42 | 63 | 11kV | 56043 | 925 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn874 Concord - Pnl.17 tripped on: Earth Fault Field EFIs: S2828 S7573 UG cable fault between S7573 Sw/B and S5401 Sw/A See 1684404 1684405 | September | 2019 | 2020Q1 | 2020 | ZN874:PA17 | ZN874:PA17 | ZN00874/000017 | CANADA BAY | UG | Not Veg | 2019-09-01 | N | 60.587 | N | 3 | N | N | 1.1101 | 39.4971 | 40954.5714
[7 empty] | 4151 | 8737 | 1684320 | 2019-09-02 07:23 | 2019-09-02 12:35 | 312 | 11kV | 522 | 4 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 194582 1 fault operation 3 phase Earth Fault underground cable fault in private mains and apparutus owned by Stockton mental hospital. Excluded oms 1684320 | September | 2019 | 2020Q1 | 2020 | 228:7486 | 228:85407 | ZN00228/085407 | NEWCASTLE | Unknown | Not Veg | 2019-09-02 | N | 130.5 | N | 3 | N | N | 1.1101 | 39.4971 | 381.4622
[7 empty] | 3695 | 3880 | 1684532 | 2019-09-02 17:43 | 2019-09-02 21:45 | 242 | 11kV | 61782 | 1428 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 194586 2 fault operations 3 phase Overcurrent mains down beyond ABS 40294, section isolated for repairs. Excluded oms 1684532 | September | 2019 | 2020Q1 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2019-09-02 | N | 43.2647 | N | 3 | N | N | 1.1101 | 39.4971 | 45148.4633
[7 empty] | 3832 | 5371 | 1684561 | 2019-09-02 22:57 | 2019-09-02 23:30 | 33 | 11kV | 1881 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 194588 C Phase DOLF : 31 Amp Excluded OMS 1684561 | September | 2019 | 2020Q1 | 2020 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2019-09-02 | N | 33 | N | 3 | N | N | 1.1101 | 39.4971 | 1374.5793
[7 empty] | 3998 | 6960 | 1684598 | 2019-09-03 08:56 | 2019-09-03 11:06 | 130 | 11kV | 16135 | 126 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.14 tripped on: 14Left IOC, Earth Fault (same relays on second attempt) UG cable damaged by Metal factory workers between S2688 Sw/A and S7231 Sw/B (N/O) All Field EFIs found down and no hazards reported at the time of first put back attempt. Hazard call to notifiy of damage came in after first attempt. | September | 2019 | 2020Q1 | 2020 | ZN2196:PA14 | ZN2196:PA14 | ZN02196/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-09-03 | N | 128.0556 | N | 5 | N | N | 1.1101 | 39.4971 | 11790.9821
[7 empty] | 5109 | 18283 | 1684652 | 2019-09-03 11:00 | 2019-09-03 11:40 | 40 | 11kV | 4400 | 110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 194595 mains faulty pole NB-50110 section isolated for repair. Excluded oms 1684652 | September | 2019 | 2020Q1 | 2020 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2019-09-03 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 3215.3902
[7 empty] | 4564 | 12734 | 1684704 | 2019-09-03 15:10 | 2019-09-03 17:50 | 160 | 11kV | 160 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194599 broken insulator bracket on pole NB-40916, Section isolated for repairs Excluded oms 1684704 | September | 2019 | 2020Q1 | 2020 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2019-09-03 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 4619 | 13396 | 1684761 | 2019-09-03 19:55 | 2019-09-03 20:08 | 13 | 11kV | 3003 | 231 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV mains between S7001 to LK62008 to S48549 interrupted to remove rope that may of clashed against HV and LV mains. Had to wait for ROL as job was on mains road. See 1684761 1684762 | September | 2019 | 2020Q1 | 2020 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Veg | 2019-09-03 | N | 13 | N | 5 | N | N | 1.1101 | 39.4971 | 2194.5038
[7 empty] | 5025 | 17497 | 1684769 | 2019-09-03 21:48 | 2019-09-04 02:50 | 302 | 11kV | 149832 | 1328 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194602 2 fault operation Earth Fault Broken polymeric insulator at pole JV-20102 Bombala st. 11kv mains into LV mains. Excluded OMS 1684770 & 1684769. | September | 2019 | 2020Q1 | 2020 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2019-09-03 | N | 112.8253 | N | 5 | N | N | 1.1101 | 39.4971 | 109492.8063
[7 empty] | 4205 | 9338 | 1684909 | 2019-09-04 14:29 | 2019-09-04 15:04 | 35 | 11kV | 45345 | 1324 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S10995 Riverwood Panel 12 tripped on Relays: A and C phase OC and Timed OC, Reclose Timing relay and lockout with EFI Signals: 11kV Trip. TX2 Group Earth Cause: UGOH fault short circuited - located below S10832 Belmorwe Shenstone Feeder Isolated from S10832 to S10897 to AB31087 See OMS 1685210 1685211 1684909 1684913 1684914 1684917 | September | 2019 | 2020Q1 | 2020 | ZN10995:PA12 | ZN10995:PA12 | ZN10995/000012 | GEORGES RIVER | Unknown | Unknown | 2019-09-04 | N | 34.2485 | N | 4 | N | N | 1.1101 | 39.4971 | 33136.7885
[7 empty] | 5315 | 19997 | 1684895 | 2019-09-04 13:40 | 2019-09-04 15:13 | 93 | 11kV | 930 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 194619 See planeed SI44922 and LID 194618 11kV link 74954 fell apart | September | 2019 | 2020Q1 | 2020 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2019-09-04 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 679.6166
[7 empty] | 4606 | 13251 | 1684923 | 2019-09-04 14:43 | 2019-09-04 16:40 | 117 | 11kV | 119363 | 1622 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 194622 1 Fault operations, Instantaneous Earth Fault Full Patrol done, No cause found Note: 11KV network Abnormal due to defects: SW 66781 - Closed SW 56821 - Closed SW74639 - Open SW69238 - Open | September | 2019 | 2020Q1 | 2020 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2019-09-04 | N | 73.59 | N | 4 | N | N | 1.1101 | 39.4971 | 87226.9598
[7 empty] | 4138 | 8549 | 1684958 | 2019-09-04 16:05 | 2019-09-04 18:00 | 114.75 | 11kV | 2983.5 | 26 | HV | Staff Operation | Utility Process Issue | Fuse | Unplanned | Wind Strong | N | LID 194623 Single Phase Following SI41457 operator believes he may have inadvertently operated and closed the trip mechanism on fusesaver device | September | 2019 | 2020Q1 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Not Veg | 2019-09-04 | N | 114.75 | N | 4 | N | N | 1.1101 | 39.4971 | 2180.2538
[7 empty] | 4728 | 14345 | 1685144 | 2019-09-05 16:37 | 2019-09-05 17:25 | 48 | 11kV | 720 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 194639 A Phase 11kv link was loose, J Frazer pushed fully in about an inch. no further action required. Excluded SEE OMS 1685144 AND 1685147. | September | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-09-05 | N | 48 | N | 2 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 4429 | 11306 | 1685163 | 2019-09-05 18:23 | 2019-09-05 19:15 | 52 | 11kV | 16664 | 416 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.10 tripped on: Earth Fault Field EFIs: S36218 S8922 S62805 UG cable fault between S62805, S568 and S8632 See 1685258 1685261 | September | 2019 | 2020Q1 | 2020 | ZN901:PA10 | ZN901:PA10 | ZN00901/000010 | SYDNEY | UG | Not Veg | 2019-09-05 | N | 40.0577 | N | 2 | N | N | 1.1101 | 39.4971 | 12177.5597
[7 empty] | 4525 | 12251 | 1685187 | 2019-09-06 00:08 | 2019-09-06 01:56 | 108 | 11kV | 246261 | 2300 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Atr Zn12570 Avoca - Panel 21 feeder tripped Relays: SEL Signals: Trip Cause: A phase bond burnt off at AB41357 See OMS 1685319 1685320 1685321 1685187 | September | 2019 | 2020Q1 | 2020 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2019-09-06 | N | 107.07 | N | 15 | N | N | 1.1101 | 39.4971 | 179960.2753
[7 empty] | 4214 | 9409 | 1685304 | 2019-09-06 15:28 | 2019-09-06 17:02 | 94.2167 | 11kV | 29112.95 | 309 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 194658 Broken cross arm at pole DR-40008 Excluded oms 1685304 | September | 2019 | 2020Q1 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2019-09-06 | N | 94.2167 | N | 15 | N | N | 1.1101 | 39.4971 | 21274.8852
[7 empty] | 3902 | 5979 | 1685745 | 2019-09-06 19:49 | 2019-09-06 21:50 | 121 | 11kV | 98494 | 814 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | N | Ex Zn12620 Noraville Pnl.3 - Centre phase bond burnt off UGOH below S11808 Sw/B | September | 2019 | 2020Q1 | 2020 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | Unknown | Unknown | 2019-09-06 | N | 121 | N | 15 | N | N | 1.1101 | 39.4971 | 71976.5101
[7 empty] | 3712 | 4065 | 1685532 | 2019-09-06 18:50 | 2019-09-06 22:50 | 240 | 11kV | 49188 | 1160 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 194659 3 fault operations Earth Fault; Instantaneous Overcurrent wire off pin pole AK-60356 Fdr abnomal - 66781 closed,74639 open,56821 closed, 69234 open. Tried to dress OMS to reflect network state T/R twice before lockout | September | 2019 | 2020Q1 | 2020 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2019-09-06 | N | 42.4034 | N | 15 | N | N | 1.1101 | 39.4971 | 35945.1396
[7 empty] | 5177 | 18787 | 1685425 | 2019-09-06 17:43 | 2019-09-06 23:35 | 352 | 11kV | 297312 | 881 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn847 Hornsby - Pnl.18 tripped, reclosed and locked out on: A & C phase IOC Field EFIs; S4526 Tree brought down OH on cnr Galston and Sydney Rd. See 1686513 1686514 | September | 2019 | 2020Q1 | 2020 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2019-09-06 | N | 337.4711 | N | 15 | N | N | 1.1101 | 39.4971 | 217266.8404
[7 empty] | 3668 | 3594 | 1685830 | 2019-09-07 00:10 | 2019-09-07 00:55 | 45 | 11kV | 675 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194664 Tree on Feeder isolated from 66736 | September | 2019 | 2020Q1 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-09-07 | N | 45 | N | 18 | N | N | 1.1101 | 39.4971 | 493.2701
[7 empty] | 4421 | 11252 | 1685539 | 2019-09-06 18:23 | 2019-09-07 02:40 | 497 | 11kV | 216632 | 1118 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn10998 Rockdale - Pnl.28 tripped on: B & C phase IOC Tree brnach brought down 11kV. S10193 Victoria Willington - Dist #5 - Interrupted to repair 11kV mains. See 1686518 1686519 1686520 | September | 2019 | 2020Q1 | 2020 | ZN10998:PA28 | ZN10998:PA28 | ZN10998/000028 | BAYSIDE | OH | Veg | 2019-09-06 | N | 193.7674 | N | 15 | N | N | 1.1101 | 39.4971 | 158308.276
[7 empty] | 4284 | 10043 | 1685702 | 2019-09-06 19:30 | 2019-09-07 03:50 | 500.1333 | 11kV | 39010.4 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194665 Tree damaged fdr. near 43917 | September | 2019 | 2020Q1 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-09-06 | N | 500.1333 | N | 15 | N | N | 1.1101 | 39.4971 | 28507.6497
[7 empty] | 3525 | 2254 | 1685762 | 2019-09-06 20:11 | 2019-09-07 04:00 | 469 | 11kV | 22408 | 184 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194661 3 phase Overcurrent Tree om mains adj sub 50541 Excluded OMS 1685806 | September | 2019 | 2020Q1 | 2020 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2019-09-06 | N | 121.7826 | N | 15 | N | N | 1.1101 | 39.4971 | 16375.1055
[7 empty] | 4158 | 8906 | 1685887 | 2019-09-07 04:44 | 2019-09-07 05:30 | 46 | 11kV | 2898 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 194666 A Phase DOLF : 30 Amp Excluded OMS 1685887 | September | 2019 | 2020Q1 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Veg | 2019-09-07 | N | 46 | N | 18 | N | N | 1.1101 | 39.4971 | 2117.7729
[7 empty] | 4480 | 11830 | 1685870 | 2019-09-07 00:59 | 2019-09-07 08:19 | 440 | 11kV | 66644 | 218 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Section of 11kV Panel 5 Wyong CP62705 Jilliby Durren found opened Cause: Windstorm See OMS 1686844 1686845 1686846 1685866 1685869 1685870 1685884 1685885 | September | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-09-07 | N | 305.7064 | N | 18 | N | N | 1.1101 | 39.4971 | 48701.4695
[7 empty] | 4217 | 9445 | 1685667 | 2019-09-06 19:13 | 2019-09-07 09:58 | 885 | 11kV | 93788 | 222 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12650 West Gosford Pnl.1 - REC47849 Reservior Beckford 0.5 tripped on: Earth Fault OH mains down between AB43611 and AB47975 tee PT13783 See 1686417 1686418 1686419 1686420 1686423 1686424 1686425 1686426 | September | 2019 | 2020Q1 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2019-09-06 | N | 422.4685 | N | 15 | N | N | 1.1101 | 39.4971 | 68537.5041
[7 empty] | 3410 | 1086 | 1685805 | 2019-09-06 20:47 | 2019-09-07 10:50 | 843 | 11kV | 23587 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 194674 Earth Fault | September | 2019 | 2020Q1 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2019-09-06 | N | 291.1975 | N | 15 | N | N | 1.1101 | 39.4971 | 17236.6839
[7 empty] | 3458 | 1593 | 1686014 | 2019-09-07 09:27 | 2019-09-07 12:00 | 153 | 11kV | 153 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 194675 Broken LL Lead | September | 2019 | 2020Q1 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2019-09-07 | N | 153 | N | 18 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 4893 | 15895 | 1686161 | 2019-09-07 13:01 | 2019-09-07 13:41 | 40 | 11kV | 22280 | 557 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S35370 Panel 8 Galston Reserve Feeder tripped on A and C phase O/C, Reclose Lockout Cause: Tree branch on OH mains @ 67 Arcadia Rd Abnormal Switching: CP572 Open | September | 2019 | 2020Q1 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-09-07 | N | 40 | N | 18 | N | N | 1.1101 | 39.4971 | 16281.5669
[7 empty] | 4355 | 10672 | 1685665 | 2019-09-07 12:31 | 2019-09-07 13:59 | 88 | 11kV | 120296 | 1367 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S15008 Harbord Panel 6 tripped on A phase oc, A/C phase IOC, Reclose lockout, earth fault, TX1 a phase earth fault Cause: Tree on OH mains See OMS 1686150 1686151 1686163 | September | 2019 | 2020Q1 | 2020 | ZN15008:PA6 | ZN15008:PA6 | ZN15008/000006 | NORTHERN BEACHES | OH | Not Veg | 2019-09-07 | N | 88 | N | 18 | N | N | 1.1101 | 39.4971 | 87908.7687
[7 empty] | 5034 | 17621 | 1685408 | 2019-09-06 17:39 | 2019-09-07 14:00 | 1221 | 11kV | 290799 | 401 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | ZN35370 Galston Panel 8 Recloser CP554 Arcadia Rosscommon tripped, reclosed tripped and locked out on A phase OC, Reclose lockout Cause: Tree branch brought down OH om Cobah and Sunnyridge Abnormal Switching:CP340 Open, CP2063 Closed 11kV I/E with Access permits from LB572 to LB42 tee PT2328 Cobah Sunnyridge South Recloser CP3281 Tripped @ 0640 07/09/2019. Due to Vandalism: Ausgrid Poles Cut Down. See OMS 1687215 1687216 1687218 1687220 16787223 CC1: 22-"Refer to SOp" | September | 2019 | 2020Q1 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-09-06 | N | 725.1845 | N | 15 | N | N | 1.1101 | 39.4971 | 212507.3321
[7 empty] | 4319 | 10364 | 1686158 | 2019-09-07 12:49 | 2019-09-07 14:13 | 84 | 11kV | 47964 | 571 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194680 2 fault operations A & B phase Overcurrent prot = 50TAB Excluded OMS 1686158 | September | 2019 | 2020Q1 | 2020 | 264:81238 | 264:81238 | ZN00264/081238 | PORT STEPHENS | OH | Veg | 2019-09-07 | N | 84 | N | 18 | N | N | 1.1101 | 39.4971 | 35050.6765
[7 empty] | 3312 | 213 | 1686051 | 2019-09-07 12:25 | 2019-09-07 14:18 | 113 | 11kV | 1017 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194681 interrupt to remove tree on OHM at pole GV-97009 Excluded oms 1686051 | September | 2019 | 2020Q1 | 2020 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2019-09-07 | N | 113 | N | 18 | N | N | 1.1101 | 39.4971 | 743.1936
[7 empty] | 5147 | 18580 | 1685910 | 2019-09-07 06:44 | 2019-09-07 15:15 | 511 | 11kV | 39391 | 172 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194670 2 fault operations Tree brought mains down Excluded OMS 1685913 | September | 2019 | 2020Q1 | 2020 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2019-09-07 | N | 229.0174 | N | 18 | N | N | 1.1101 | 39.4971 | 28785.781
[7 empty] | 5310 | 19946 | 1685914 | 2019-09-07 06:40 | 2019-09-07 15:45 | 545 | 11kV | 101310 | 342 | HV | Vandalism | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | 11kV I/E with Access permits from LB572 to LB42 tee PT2328 Cobah Sunnyridge South Recloser CP3281 Tripped @ 0640 07/09/2019. Due to Vandalism Ausgrid Poles Cut Down. Abnormal Switching:CP340 Open, CP2063 Closed See OMS 1687215 1687216 1687218 1687220 16787223 also refer to previous event ZN35370 Galston Panel 8 Recloser CP554 Arcadia Rosscommon tripped, reclosed tripped and locked out on A phase OC, Reclose lockout Cause: Tree branch brought down OH om Cobah and Sunnyridge CC1: 22-"Refer to SOp" | September | 2019 | 2020Q1 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2019-09-07 | N | 296.2281 | N | 18 | N | N | 1.1101 | 39.4971 | 74034.3599
[7 empty] | 3400 | 986 | 1686096 | 2019-09-07 11:14 | 2019-09-07 16:10 | 296 | 11kV | 296 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194682 Broken Live Line lead Excluded OMS 1686096 | September | 2019 | 2020Q1 | 2020 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2019-09-07 | N | 296 | N | 18 | N | N | 1.1101 | 39.4971 | 216.3081
[7 empty] | 4232 | 9571 | 1686203 | 2019-09-07 15:48 | 2019-09-07 16:15 | 27 | 11kV | 1755 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194684 No Protection, Wire off pin P. FP-50453 Pole FP50453 -aerial 11k has come off insulator - DW hanging low | September | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-09-07 | N | 27 | N | 18 | N | N | 1.1101 | 39.4971 | 1282.5022
[7 empty] | 4419 | 11236 | 1686054 | 2019-09-07 15:58 | 2019-09-07 16:41 | 43 | 11kV | 989 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194683 Tree resting against 11kV mains, no protection operations BURLEY, TED small tree has uprooted and fallen on dw in paddock to the right in 1071 property. | September | 2019 | 2020Q1 | 2020 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2019-09-07 | N | 43 | N | 18 | N | N | 1.1101 | 39.4971 | 722.732
[7 empty] | 4863 | 15628 | 1686255 | 2019-09-07 15:30 | 2019-09-07 17:27 | 117 | 11kV | 234 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194688 Broken Live Line Lead Excluded OMS 1686255 | September | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-09-07 | N | 117 | N | 18 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 3897 | 5936 | 1686273 | 2019-09-07 16:22 | 2019-09-07 18:32 | 130 | 11kV | 130 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194716 Inital LID 194690 report missing. No details in switching sheet. | September | 2019 | 2020Q1 | 2020 |  |  |  | LAKE MACQUARIE | OH | Veg | 2019-09-07 | N | 130 | N | 18 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 3583 | 2692 | 1686058 | 2019-09-07 16:04 | 2019-09-07 18:45 | 161 | 11kV | 46529 | 289 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Wind Strong | N | LID 194689 interrupt to repair crossarm brace at pole JU-41900 Excluded oms 1686058 | September | 2019 | 2020Q1 | 2020 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | Unknown | Not Veg | 2019-09-07 | N | 161 | N | 18 | N | N | 1.1101 | 39.4971 | 34002.0208
[7 empty] | 5230 | 19311 | 1686138 | 2019-09-07 12:21 | 2019-09-07 19:30 | 429 | 11kV | 201630 | 470 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | 11kV Bond Off on 11kV UGOH to S10143 Wollongong Earle Abnormal Switching S10879 SW/A - CP30099 - S10143 Cause: 11kV Bond off on 11kV UGOH to S10143 See OMS 1686949 16867947 1686138 1686191 1686204 1686210 | September | 2019 | 2020Q1 | 2020 | ZN10999:PA17 | ZN10998:PA3 | ZN10998/000003 | BAYSIDE | Unknown | Unknown | 2019-09-07 | N | 429 | N | 18 | N | N | 1.1101 | 39.4971 | 147345.2569
[7 empty] | 3534 | 2342 | 1686306 | 2019-09-07 19:45 | 2019-09-07 23:10 | 204.8333 | 11kV | 45473 | 222 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194718 11kV Overcurrent at IV-80965 | September | 2019 | 2020Q1 | 2020 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2019-09-07 | N | 204.8333 | N | 18 | N | N | 1.1101 | 39.4971 | 33230.3272
[7 empty] | 5101 | 18240 | 1685414 | 2019-09-06 17:41 | 2019-09-07 23:20 | 1779 | 11kV | 742089 | 1259 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN1673 Turramurra - Panel 18 tripped, reclosed, tripped and locked out on Relays: IOC a and b phase Abnormal Switching: AB2209 Closed, LB3019 Cause: Section of 11kV feeder fromLB238 to CP2209 tee PT1334 Tree has brought down two bays of 11kV outside 117 Comenarra Parkway. Dop reports HV into LV EMSO to check for safety. A/P and CTW on transfer. See OMS 1686820 1686822 1685414 1685457 1685851 1685872 | September | 2019 | 2020Q1 | 2020 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2019-09-06 | N | 589.4273 | N | 15 | N | N | 1.1101 | 39.4971 | 542296.7533
[7 empty] | 4397 | 11019 | 1685392 | 2019-09-06 17:14 | 2019-09-08 13:07 | 2633 | 11kV | 356638 | 636 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston Panel 4 tripped on Relays: B and C phase IOC, EFI, Reclose Lockout Section of 11kV defective from LB3343 to LB493 - Abnormal Switching: CP340 Open CP62158 Closed Outside Rural fire station, address could be known as 127 Arcadia Road, tree has come down and taken down DW. No sparking seen HV CCT down, HV arms look ok. LV 19/2cu down, 3 broken LV arms - 2 straight thrus and 1 termo. See OMS 1686775 1686776 1685874 1685392 | September | 2019 | 2020Q1 | 2020 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2019-09-06 | N | 560.7516 | N | 15 | N | N | 1.1101 | 39.4971 | 260620.5314
[7 empty] | 4596 | 13126 | 1685373 | 2019-09-06 17:13 | 2019-09-08 17:00 | 2867 | 11kV | 208289 | 192 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN35370 Galston Panel 10 Recloser CP50015 Quarry Old Northern tripped and locked out on O/C Cause: Weather related - trees brought down 11kV OH from LLC to PT77201 LB62156 Open due to Gully Crossing and not patrolled. See OMS 1687093 1687096 1687097 1686512 1686263 1685416 1685373 | September | 2019 | 2020Q1 | 2020 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2019-09-06 | N | 1084.8385 | N | 15 | N | N | 1.1101 | 39.4971 | 152211.4577
[7 empty] | 4342 | 10537 | 1685766 | 2019-09-08 10:52 | 2019-09-08 17:05 | 373 | 11kV | 7087 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S12650 West Gosford LB47645 to PT11779 to PT14550 Isolated for safety Cause: Supply isolated to remove tree See OMS 1686434 1686401 | September | 2019 | 2020Q1 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2019-09-08 | N | 373 | N | 5 | N | N | 1.1101 | 39.4971 | 5178.9706
[7 empty] | 4507 | 12128 | 1686525 | 2019-09-08 17:33 | 2019-09-08 18:55 | 82 | 11kV | 6232 | 76 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT11856 Suncrest Gleddon - Roadside 63k HVDO operated Cause: Birds on OH mains See OMS 1686616 1686526 1686525 | September | 2019 | 2020Q1 | 2020 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2019-09-08 | N | 82 | N | 5 | N | N | 1.1101 | 39.4971 | 4554.1618
[7 empty] | 5059 | 17917 | 1686539 | 2019-09-08 18:34 | 2019-09-08 19:34 | 60 | 11kV | 109920 | 2090 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S9700 Kirrawee Pa20 the cook Glencoe tripped reclosed tripped and locked out on B phase IOC, Reclose Lockout and Time Delay Cause: Animals/Birds on UGOH to SB9093 See OMS 1686686 1686687 1686539 | September | 2019 | 2020Q1 | 2020 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | Unknown | Unknown | 2019-09-08 | N | 52.5933 | N | 5 | N | N | 1.1101 | 39.4971 | 80326.2939
[7 empty] | 3792 | 4960 | 1686555 | 2019-09-08 19:30 | 2019-09-08 22:30 | 180 | 11kV | 1610 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex 12630 Peats Ridge Panel 10 Section of 11kV Feeder isolated between CP43055 and CP44594 Tree resting on 11CCT adj PT14595 Isolated between LB43055 and AB44594 See separate interruption on PT49311 distributor 2 (OMS 1686614) See OMS 1686555 1686614 | September | 2019 | 2020Q1 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2019-09-08 | N | 134.1667 | N | 5 | N | N | 1.1101 | 39.4971 | 1176.5405
[7 empty] | 3461 | 1617 | 1686693 | 2019-09-09 10:47 | 2019-09-09 11:53 | 66 | 11kV | 92664 | 1404 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow Pnl.3 - Footpath phase bond burnt off load side of AB44327 | September | 2019 | 2020Q1 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2019-09-09 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 67716.1181
[7 empty] | 4085 | 8030 | 1685308 | 2019-09-06 15:35 | 2019-09-09 12:00 | 4105 | 11kV | 12260 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 194711 OHM on ground near sub 71678. Excluded OMS 1685308 | September | 2019 | 2020Q1 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-09-06 | N | 1114.5455 | N | 15 | N | N | 1.1101 | 39.4971 | 8959.2464
[7 empty] | 3409 | 1076 | 1686543 | 2019-09-08 18:40 | 2019-09-09 13:30 | 1130 | 11kV | 14626 | 78 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn167 Auburn - Pnl.19 tripped on: O/C and Earth Fault no Field EFIs Possum on UGOH near AB3287 | September | 2019 | 2020Q1 | 2020 | ZN167:PA19 | ZN167:PA19 | ZN00167/000019 | PARRAMATTA | OH | Not Veg | 2019-09-08 | N | 187.5128 | N | 5 | N | N | 1.1101 | 39.4971 | 10688.2494
[7 empty] | 4176 | 9155 | 1686731 | 2019-09-09 12:10 | 2019-09-09 13:30 | 80 | 11kV | 720 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 194712 Broken dead end at L/F 40643 | September | 2019 | 2020Q1 | 2020 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2019-09-09 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 4089 | 8054 | 1685782 | 2019-09-09 14:00 | 2019-09-09 19:35 | 334.5833 | 11kV | 28774.1667 | 86 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Wind Strong | N | See S.Op Arrange NAR # 46379 - T1 - T2 - unable to confirm exact outage times, used event created by AOp AKA 7 HUNT AVE DURAL. LARGE TREE ON HV AND LV SUSPENDED ACROSS RD. URGENT HAZARD, TREE WILL FALL IF CONDUCTORS BREAK. SUPPLY IS STILL ON BETWEEN POLES DU 37001 AND DU 3943. NEAR HV LINKS 1556. WIRES ARE NOT BROKEN NEW STRAIGHT THROUGH HV ARM NEEDED FOR POLE DU 36944. RURAL RD SIGNS & SOME TC REQUIRED. HV CUTOUT AND CTW REQD. BORER OR CRANE REQUIRED. BARE LV CONDUCTOR, CCT HV CONDUCTOR. | September | 2019 | 2020Q1 | 2020 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2019-09-09 | N | 334.5833 | N | 3 | N | N | 1.1101 | 39.4971 | 21027.3123
[7 empty] | 5167 | 18726 | 1686919 | 2019-09-10 02:21 | 2019-09-10 03:53 | 92 | 11kV | 164889 | 1922 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2310 Punchbowl - Pnl.14 tripped on: C Phase IOC UG cable fault between S3528 Sw/B and S274 Sw/B See 1687229 1687230 | September | 2019 | 2020Q1 | 2020 | ZN2310:PA14 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-09-10 | N | 85.7903 | N | 1 | N | N | 1.1101 | 39.4971 | 120496.0178
[7 empty] | 4120 | 8377 | 1687369 | 2019-09-11 17:58 | 2019-09-11 18:40 | 42 | 11kV | 116 | 3 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Section of Panel 1 Dog Trap ex ZN12650 from USL43922 to PT61456 and PT]14453 11kV Feeder burnt off and Feeder hanging off pin insulator See OMS 1689187 1689186 | September | 2019 | 2020Q1 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | Unknown | Not Veg | 2019-09-11 | N | 38.6667 | N | 1 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 4204 | 9334 | 1687444 | 2019-09-12 09:16 | 2019-09-12 12:15 | 179 | 11kV | 179 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 194749 C Phase DOLF Posibly have been out for a week since last storm. Excluded OMS 1687444 | September | 2019 | 2020Q1 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-09-12 | N | 179 | N | 1 | N | N | 1.1101 | 39.4971 | 130.8079
[7 empty] | 4467 | 11644 | 1687638 | 2019-09-13 13:16 | 2019-09-13 14:40 | 84 | 11kV | 147868 | 1862 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2466 Flemington 11kV feeder No 30 tripped on Relays: Earth Fault, EFI, Fault Check Cause: UG fault in 11kV From SW/B @ S61613 to SW/A at S3488 to SWA @ S3487. See OMS 1689131 1689135 1687638 | September | 2019 | 2020Q1 | 2020 | ZN2466:PA30 | ZN36000:PA6 | ZN36000/000006 | STRATHFIELD | UG | Not Veg | 2019-09-13 | N | 79.4135 | N | 2 | N | N | 1.1101 | 39.4971 | 108057.573
[7 empty] | 3553 | 2519 | 1687656 | 2019-09-13 15:01 | 2019-09-13 16:06 | 65 | 11kV | 62075 | 955 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Section of 11kV panel 13 Recloser CP61133 Minnamurra tosca tripped onb SEF 11kV Roadside flicker blade left in previously at AB44405 | September | 2019 | 2020Q1 | 2020 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Not Veg | 2019-09-13 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 45362.5791
[7 empty] | 4245 | 9705 | 1687813 | 2019-09-15 07:58 | 2019-09-15 09:05 | 67 | 11kV | 134 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 194782 C Phase DOLF : 10 Amp Excluded OMS 1687813 | September | 2019 | 2020Q1 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2019-09-15 | N | 67 | N | 3 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 4518 | 12227 | 1687827 | 2019-09-15 12:04 | 2019-09-15 13:41 | 97 | 11kV | 24929 | 257 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.18 tripped on: O/C & E/F Field EFIs: S4337 S4257 (S36046 and CP 2319 EFI did not operate) UG cable fault between S4257 Sw/B and S7516 Pnl.16 tripped @ 1300 on B phase O/C on restoration attempt due to EFIs not operating. S7516 has nil customers in GIS and did not create an event. restored at 1500 16/9 See 1688219 1688220 | September | 2019 | 2020Q1 | 2020 | ZN1287:PA18 | ZN1287:PA18 | ZN01287/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-09-15 | N | 97 | N | 3 | N | N | 1.1101 | 39.4971 | 18217.3779
[7 empty] | 5115 | 18335 | 1687856 | 2019-09-15 18:49 | 2019-09-15 19:49 | 60 | 11kV | 95160 | 1586 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 57 tripped on Relays: B and C phase OC, Earth Fault and EFI. Relays: B and C hase IOC, Earth Fault, EFI Signals: 11kV Trip. Field EFI's Abnormal Switching: CP1557 Open, LB259 Closed Cause: Possum on UGOH adjacent to pt S.1847 Surada Av See OMS 1688311 1687856 858 | September | 2019 | 2020Q1 | 2020 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2019-09-15 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 69540.1213
[7 empty] | 4824 | 15266 | 1687906 | 2019-09-16 12:20 | 2019-09-16 13:25 | 65 | 11kV | 650 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194792 Mains came of 11kV pin insulator. Interruption required to reattach mains. No protection operations. Excluded OMS1687906 | September | 2019 | 2020Q1 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2019-09-16 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 4367 | 10753 | 1688028 | 2019-09-16 15:25 | 2019-09-16 16:25 | 60 | 11kV | 180 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194796 11kV main came of insulator at pole AJ80028. Excluded OMS 1688028 | September | 2019 | 2020Q1 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2019-09-16 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 3396 | 938 | 1688037 | 2019-09-16 15:42 | 2019-09-16 17:45 | 123 | 11kV | 93141 | 1247 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 194798 2 fault operations 3 phase Earth Fault UGOH fault SW-90319. Excluded OMS 1688037. | September | 2019 | 2020Q1 | 2020 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | Unknown | Unknown | 2019-09-16 | N | 74.6921 | N | 5 | N | N | 1.1101 | 39.4971 | 68064.6956
[7 empty] | 3981 | 6691 | 1688107 | 2019-09-16 21:05 | 2019-09-16 23:20 | 135 | 11kV | 7695 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | The 11kV feeder from S48427 Beaconsfield Crescent to LB63682 tee S16841 interrupted to remove tree from CCT Cause: Tree on OH mains | September | 2019 | 2020Q1 | 2020 | ZN15004:PA1 | ZN15004:PA1 | ZN15004/000001 | NORTHERN BEACHES | OH | Veg | 2019-09-16 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 5623.279
[7 empty] | 3925 | 6142 | 1688122 | 2019-09-16 21:59 | 2019-09-17 01:25 | 206 | 11kV | 388507 | 2574 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | Zn10999 Kogarah - Pnl.17 tripped, reclosed & locked out on: Earth Fault Abnormal: S10879 Sw/A Open, LB30099 open with Rockdale Pnl.3 closed due to defective UG cable Pole cap on UGOH outside 19 Wolli Creek Rd, Rockdale came off and lodged between B phase and earth. See 1688198 1688199 1688201 1688202 1688200 | September | 2019 | 2020Q1 | 2020 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2019-09-16 | N | 150.9351 | N | 5 | N | N | 1.1101 | 39.4971 | 283909.4566
[7 empty] | 3800 | 5017 | 1689184 | 2019-09-17 01:25 | 2019-09-17 02:26 | 61 | 11kV | 40748 | 668 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 11kV Intellirupter Tripped and reclosed on Relays: OC trip. Cause: Mains to patrol in daylight - cause not ascertained | September | 2019 | 2020Q1 | 2020 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | OH | Veg | 2019-09-17 | N | 61 | N | 12 | N | N | 1.1101 | 39.4971 | 29777.4365
[7 empty] | 3883 | 5767 | 1688149 | 2019-09-17 04:05 | 2019-09-17 06:30 | 145 | 11kV | 211792 | 1907 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn116 Leichhardt Panel 12 'Balmain Derby" feeder tripped on: Relays: OC + EF 51AB Field EFI's: S4829 Moore Balmain Remarks: Cause not ascertained. All supply restored | September | 2019 | 2020Q1 | 2020 | ZN116:PA12 | ZN116:PA12 | ZN00116/000012 | INNER WEST | OH | Veg | 2019-09-17 | N | 111.0603 | N | 12 | N | N | 1.1101 | 39.4971 | 154771.3468
[7 empty] | 4098 | 8173 | 1688195 | 2019-09-17 10:13 | 2019-09-17 10:52 | 39 | 11kV | 5295 | 169 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 194811 A Phase burnt tapping on UGOH IU-64023 interupted due to arcing. Excluded OMS 1688195 | September | 2019 | 2020Q1 | 2020 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2019-09-17 | N | 31.3314 | N | 12 | N | N | 1.1101 | 39.4971 | 3869.4298
[7 empty] | 4219 | 9456 | 1688316 | 2019-09-17 13:25 | 2019-09-17 15:24 | 119 | 11kV | 93191 | 868 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | aT zN14143 sOMERSBY PANEL 17 TRIPPED, reclosed, tripped and locked out on Relays: B and C phase IOC, Lockout and Timing Signals:11kV trip Field EFI's Nil Cause: Tree branch on 11kV Mains between AB40511 and LK44302 See OMS 1689177 1689179 1688316 | September | 2019 | 2020Q1 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2019-09-17 | N | 107.3629 | N | 12 | N | N | 1.1101 | 39.4971 | 68101.2341
[7 empty] | 5072 | 17990 | 1688383 | 2019-09-17 16:45 | 2019-09-17 17:46 | 61 | 11kV | 46908 | 1068 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 194817 A Phase burnt off tapping at pole JU-31583. dq Excluded OMS1688383 | September | 2019 | 2020Q1 | 2020 | 257:81985 | 257:81985 | ZN00257/081985 | NEWCASTLE | OH | Not Veg | 2019-09-17 | N | 43.9213 | N | 12 | N | N | 1.1101 | 39.4971 | 34278.9828
[7 empty] | 4676 | 13880 | 1688478 | 2019-09-17 23:55 | 2019-09-18 00:02 | 7 | 11kV | 1071 | 153 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 194820 Fdr interrupted to remove hazard. Wire entagled in crossarm & 11kV links 27220. | September | 2019 | 2020Q1 | 2020 | 528:83014 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2019-09-17 | N | 7 | N | 12 | N | N | 1.1101 | 39.4971 | 782.6552
[7 empty] | 5198 | 18931 | 1688507 | 2019-09-17 23:24 | 2019-09-18 01:39 | 135 | 11kV | 226162 | 1885 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 194819 3 fault operations B & C Phase Intellrupter; Overcurrent Tree branch on 11kV OHM adj. sub 20332. Excluded OMS No. 1688507 | September | 2019 | 2020Q1 | 2020 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2019-09-17 | N | 119.9798 | N | 12 | N | N | 1.1101 | 39.4971 | 165272.519
[7 empty] | 3507 | 2095 | 1688481 | 2019-09-17 21:46 | 2019-09-18 03:20 | 334 | 11kV | 197394 | 591 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn9245 Engadine Zn - Pnl.1L from S9116 Sw/A Bond burnt off roadside phase AB35715 | September | 2019 | 2020Q1 | 2020 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2019-09-17 | N | 334 | N | 12 | N | N | 1.1101 | 39.4971 | 144249.7131
[7 empty] | 3847 | 5471 | 1688480 | 2019-09-17 21:39 | 2019-09-18 04:12 | 393 | 11kV | 193834 | 1376 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN19*5 Pymble Panel 9 tripped, reclosed tripped and locked out on Relays: B phase timed, Timing relay, lockout,SEL. Fault Check, EFI Signals: 11kV trip. TX2 Group Earth and Zone Earth Cause: Tree brught down HV and LV mains. HV into LV. Emso to check for damage to customer installations.: Emso checked switchboards from 8 to 34 Northcote Ave. Visual checks ok. See OMS 168912 1689125 1689126 1688480 | September | 2019 | 2020Q1 | 2020 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Veg | 2019-09-17 | N | 140.8677 | N | 12 | N | N | 1.1101 | 39.4971 | 141648.1701
[7 empty] | 4472 | 11720 | 1688502 | 2019-09-17 22:54 | 2019-09-18 10:35 | 701.0333 | 11kV | 4907.2333 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | ZN14891 Wyong - Panel 5 labelled LB40065 Auto links 48568 Opened for safety Footpath phase HDO defective at PT48944 | September | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-09-17 | N | 701.0333 | N | 12 | N | N | 1.1101 | 39.4971 | 3586.0614
[7 empty] | 4841 | 15475 | 1688538 | 2019-09-18 02:28 | 2019-09-18 11:15 | 527 | 11kV | 704964 | 3136 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn35500 Top Ryde Panel 28 tripped , reclosed, tripped and locked out on Relays: 28R Basler 50TBC, EFI, Fault Check UF relay Signals: 11kV Trip, Group Earth Abnormal Switching: LB280 Open, SW/B at S4932 Closed Cause: Suspect Cable fault from S8724 to S5334 tee CP717 tee PT77643 See OMS 1689154 1689156 1689158 1688771 1688681 1688680 1688676 1688538 | September | 2019 | 2020Q1 | 2020 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | UG | Not Veg | 2019-09-18 | N | 224.7972 | N | 7 | N | N | 1.1101 | 39.4971 | 515166.8983
[7 empty] | 3828 | 5361 | 1688675 | 2019-09-18 09:40 | 2019-09-18 13:18 | 218 | 11kV | 4360 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194824 3 Fault operations, A, B, C Phase Pole Mounted RAGCB Tree on mains Pole KR-20084 | September | 2019 | 2020Q1 | 2020 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2019-09-18 | N | 218 | N | 7 | N | N | 1.1101 | 39.4971 | 3186.1594
[7 empty] | 3754 | 4573 | 1688562 | 2019-09-18 06:11 | 2019-09-18 16:35 | 624 | 11kV | 3120 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 194829 A, b, C 16 Amp fuses, substation DOLF, possible lightening strike Pt Sub - 48260 feeding 3411 Nelson Bay Rd and numerous customers has three blown HV fuses and possible blown HV arrester. The sub is located just south of Marrays Brewery and is five meters off Nelson Bay Rd 100Klms/h. EWP required with major traffic control wet conditions. Could supply be checked at address after supply restored. Thankyou | September | 2019 | 2020Q1 | 2020 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2019-09-18 | N | 624 | N | 7 | N | N | 1.1101 | 39.4971 | 2280.004
[7 empty] | 5242 | 19409 | 1688814 | 2019-09-18 13:46 | 2019-09-18 19:40 | 354 | 11kV | 221604 | 626 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 194831 1 Fault operations, A, B and C Phases Sensitive Earth Fault Tree on Mains KAUTER, PAUL C - Daniel Tree Trimming Contractor 0408 292 463 identified HV down on the deck off pole FT93175 and between FT93174. AOP advised by phone as no trip. | September | 2019 | 2020Q1 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2019-09-18 | N | 354 | N | 7 | N | N | 1.1101 | 39.4971 | 161941.667
[7 empty] | 3555 | 2533 | 1688706 | 2019-09-18 11:02 | 2019-09-18 23:15 | 733 | 11kV | 35257 | 255 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 194833 2 fault operations 3 phase Earth fault Broken x arm pole IQ-52859. 33 into 11kV. Excluded OMS 1688706. | September | 2019 | 2020Q1 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2019-09-18 | N | 138.2627 | N | 7 | N | N | 1.1101 | 39.4971 | 25764.7757
[7 empty] | 4739 | 14419 | 1688451 | 2019-09-17 20:00 | 2019-09-19 00:15 | 1695 | 11kV | 47280 | 157 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12630 Peats Ridge Panel 3 Recloser CP45071 Central Mangrove tripped, reclosed tripped and locked out on Relays: OC trip and Lockout Cause: Tree has brought down 11kV OH mains near LB41192 and Damaged LV40552 and AB44011 See OMS 1689417 1689418 1688547 1688475 1688451 | September | 2019 | 2020Q1 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2019-09-17 | N | 301.1465 | N | 12 | N | N | 1.1101 | 39.4971 | 34550.8295
[7 empty] | 4832 | 15374 | 1688534 | 2019-09-18 01:29 | 2019-09-19 02:00 | 1471 | 11kV | 513379 | 349 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn3154 St Ives Panel 23 11kV recloser CP527 tripped reclosed tripped and locked out on Relays: OC, IOC, Lockout Signals: Zone Earth TX3 Group Earth AB1388 Open and Defective, LB64433 Closed Cause: 11kV down near PT1335 Note: AB1388 Open and Defective, AB2081 Bypassed LB2081 bypassed. LB3334 would not open See OMS 1688527 1688533 1688534 1688535 | September | 2019 | 2020Q1 | 2020 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2019-09-18 | N | 1471 | N | 7 | N | N | 1.1101 | 39.4971 | 375162.2311
[7 empty] | 4399 | 11033 | 1688975 | 2019-09-19 02:01 | 2019-09-19 03:12 | 71 | 11kV | 71783 | 1081 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | 11kV Recloser CP41397 Karalta Rd Tripped and Locked out Relays: Earth fault trip and lockout Cause: 11KV fault from S14617 Bronzewing Jessie Riley to S14617 Bronzewind dawdawn See OMS 1689118 1689119 1688975 | September | 2019 | 2020Q1 | 2020 | ZN12570:PA21 | ZN12580:PA2 | ZN12580/000002 | CENTRAL COAST | UG | Not Veg | 2019-09-19 | N | 66.4043 | N | 5 | N | N | 1.1101 | 39.4971 | 52456.8992
[7 empty] | 3638 | 3240 | 1688986 | 2019-09-19 06:02 | 2019-09-19 08:10 | 128.35 | 11kV | 39275.1 | 306 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | At CP31410 link found open Cause: Vehicle Hit pole - Vehicle had already left when DOp arrived. | September | 2019 | 2020Q1 | 2020 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Not Veg | 2019-09-19 | N | 128.35 | N | 5 | N | N | 1.1101 | 39.4971 | 28701.0847
[7 empty] | 4938 | 16452 | 1688980 | 2019-09-19 03:54 | 2019-09-19 12:30 | 516 | 11kV | 65532 | 127 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 194839 B & C Phase : 40 Amp FAULTY 11KV ARRESTORS AT UGOH. Excluded OMS 1689008 , 1688980. | September | 2019 | 2020Q1 | 2020 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2019-09-19 | N | 516 | N | 5 | N | N | 1.1101 | 39.4971 | 47888.8527
[7 empty] | 4831 | 15337 | 1688505 | 2019-09-17 23:16 | 2019-09-19 12:55 | 2259 | 11kV | 26144 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC76763 Grants Keighley - tripped, relcosed & locked out on: Earth fault 11kV down beyond LK47842 See 1690502 1690503 1690505 | September | 2019 | 2020Q1 | 2020 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2019-09-17 | N | 450.7586 | N | 12 | N | N | 1.1101 | 39.4971 | 19105.2641
[7 empty] | 3625 | 3071 | 1688979 | 2019-09-19 03:08 | 2019-09-19 16:05 | 777 | 11kV | 17094 | 22 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | S5963 bass Hill Shopping CTR - Tx No.1 11kV fuses operated on B & C phase Suspect fuse fatigue. No fault present on Direct Distributor | September | 2019 | 2020Q1 | 2020 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-09-19 | N | 777 | N | 5 | N | N | 1.1101 | 39.4971 | 12491.791
[7 empty] | 4253 | 9826 | 1689223 | 2019-09-19 17:40 | 2019-09-19 18:37 | 57 | 11kV | 3306 | 58 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 194846 broken 11kv x-arm pole FT-33907 , section isolated for repair Excluded oms 1689223 | September | 2019 | 2020Q1 | 2020 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2019-09-19 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 2415.9273
[7 empty] | 5081 | 18130 | 1689345 | 2019-09-20 10:50 | 2019-09-20 12:50 | 120 | 11kV | 840 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | At CP42953 Wyong Panel 5 opened for safety Cause: To remove large tree of 11kV CCT adjacent to PT12758 Supply interruupted for safety reasone | September | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-09-20 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 4314 | 10341 | 1689346 | 2019-09-20 11:04 | 2019-09-20 13:25 | 141 | 11kV | 224296 | 2645 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1285 Greenacre Park 11kV Panel 31 tripped, reclosed tripped and locked out on Relays: B phase OC, earth fault, reclose and lockout and EFI Signals:TX4 Group Earth, Zone Earth, 11kV Trip Cause: UG fault - section of 11kv feeder from S4862 to S4867 Acacia Wilbur to LB2481 tee PT78849 is defective See OMS1690275 1690276 1690277 1690278 1689346 | September | 2019 | 2020Q1 | 2020 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-09-20 | N | 84.8 | N | 2 | N | N | 1.1101 | 39.4971 | 163908.9012
[7 empty] | 4200 | 9306 | 1688937 | 2019-09-18 18:56 | 2019-09-20 13:30 | 2554 | 11kV | 2554 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV/415 PT13176 Missing link George 0.9 interrupted for safety Open wire distributors taken down by tree between PT pole CM321 and CM320, cut away/ made safe. 'A' phase fuse on PT13176 found open (possibly from impact). 2 customers supplied from transformer. One adjacent PT has one phase down, customer off pole CM320 has had no supply since last night (start time of event amended to reflect this). Access to pole CM320 may be by ladder only and via property on Wisemans Ferry Rd. EWP and ladders required. No traffic control. EmSO Jamie 0407907136. | September | 2019 | 2020Q1 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2019-09-18 | N | 2554 | N | 7 | N | N | 1.1101 | 39.4971 | 1866.3879
[7 empty] | 3887 | 5827 | 1689501 | 2019-09-21 00:44 | 2019-09-21 02:32 | 108 | 11kV | 148952 | 1423 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2602 Clovelly Panel 18 tripped on Relays: Earth Fault and Fault Check. Signals: Zone and TX3 earth and 11kV trip. Cause: 11kV UG feeder fault from S32320 Rae Street to S2677 to S3439 EFI @ S3663 St Marks Chap rusted and defective EFI @ S3230 Rae Street unknown if operated See OMS 1690271 1690273 1689501 | September | 2019 | 2020Q1 | 2020 | ZN2602:PA18 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | UG | Not Veg | 2019-09-21 | N | 104.6746 | N | 4 | N | N | 1.1101 | 39.4971 | 108849.7283
[7 empty] | 3829 | 5365 | 1689506 | 2019-09-21 09:15 | 2019-09-21 14:45 | 330 | 11kV | 44880 | 136 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 194868 no protection operations. Car into pole VP-70064. Section isolated for repairs Excluded OMS 1689506 | September | 2019 | 2020Q1 | 2020 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2019-09-21 | N | 330 | N | 4 | N | N | 1.1101 | 39.4971 | 32796.9803
[7 empty] | 4666 | 13779 | 1689564 | 2019-09-21 12:34 | 2019-09-21 15:30 | 176 | 11kV | 23970 | 140 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Section of Panel 8 From S15012 Killarney Supply interrupted from LB77229 to SW/A at S17136 tee S17136 and PT15429 Cause: Supply interrupted to carry out repairs. See OMS 1689957 1689956 1689569 1689564 | September | 2019 | 2020Q1 | 2020 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | Unknown | Unknown | 2019-09-21 | N | 171.2143 | N | 4 | N | N | 1.1101 | 39.4971 | 17516.569
[7 empty] | 4701 | 14113 | 1689572 | 2019-09-21 13:28 | 2019-09-21 16:50 | 202.2667 | 11kV | 3438.5333 | 17 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 194871 C Phase DOLF : 20 Amps Cph Load side contacts on LF 74690 burnt up. LF replaced. | September | 2019 | 2020Q1 | 2020 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2019-09-21 | N | 202.2667 | N | 4 | N | N | 1.1101 | 39.4971 | 2512.7787
[7 empty] | 4470 | 11667 | 1689618 | 2019-09-22 05:09 | 2019-09-22 07:10 | 121 | 11kV | 114755 | 1025 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2635 Epping Panel 38 tripped, reclosed tripped and locked out on Relays: IOC a phase, Earth Faukltm, E/F check, Timing and Lcokout and EFI. Cause: Section of 11kV from SW/B at S4550 to LB1308 tee CP543 See OMS 1690051 1690052 1690053 1689618 | September | 2019 | 2020Q1 | 2020 | ZN2635:PA38 | ZN2635:PA38 | ZN02635/000038 | HORNSBY | UG | Not Veg | 2019-09-22 | N | 111.9561 | N | 2 | N | N | 1.1101 | 39.4971 | 83859.5693
[7 empty] | 4838 | 15414 | 1689644 | 2019-09-22 10:35 | 2019-09-22 16:03 | 328 | 11kV | 39590 | 587 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 194878 2 Fault Operations A & B phase Overcurrent Tree branch on OHM adj. pole FQ-52409 & repair damaged stranding 11kV OHM. Excluded OMS No. 1689644 | September | 2019 | 2020Q1 | 2020 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2019-09-22 | N | 67.4446 | N | 2 | N | N | 1.1101 | 39.4971 | 28931.2043
[7 empty] | 4031 | 7366 | 1689722 | 2019-09-23 00:44 | 2019-09-23 02:35 | 111 | 11kV | 122668 | 1195 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S965 Pennant Hill 11kV Panel 45 feeder tripped on Relays: Timed overcurrent A and C phase EFI. Signals: 11kV trip, TX2 Group Earth, Zon Earth Cause: UG cable fault from S965 Pennant Hills Pa42 to S4499 Keelendi Victoria tee S5370 See OMS 1690268 1690269 1689722 1678726 | September | 2019 | 2020Q1 | 2020 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | UG | Not Veg | 2019-09-23 | N | 102.651 | N | 1 | N | N | 1.1101 | 39.4971 | 89642.1563
[7 empty] | 4755 | 14526 | 1690031 | 2019-09-24 12:07 | 2019-09-24 14:30 | 143 | 11kV | 131306 | 922 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.5 tripped on: Timed O/C Field EFIs; S2886 S35515 S8195 S8196 S3430 UG cable fault See 1690517 1690518 | September | 2019 | 2020Q1 | 2020 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | UG | Not Veg | 2019-09-24 | N | 142.4143 | N | 3 | N | N | 1.1101 | 39.4971 | 95954.5519
[7 empty] | 3799 | 5008 | 1689961 | 2019-09-24 07:15 | 2019-09-24 16:09 | 534 | 11kV | 127092 | 238 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | AT CP61922 Pacific Bart Point - Supply lost All details assumed - no outage report provided by Sydney CR Confirmed outage times VIA SCADA trends | September | 2019 | 2020Q1 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2019-09-24 | N | 534 | N | 3 | N | N | 1.1101 | 39.4971 | 92875.085
[7 empty] | 4957 | 16679 | 1690138 | 2019-09-24 17:37 | 2019-09-24 18:29 | 52 | 11kV | 118508 | 2279 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.25 tripped on: A & B phase O/C Ibis bird into OH mains outside 11 makneken Ave Revesby | September | 2019 | 2020Q1 | 2020 | ZN2196:PA25 | ZN2196:PA25 | ZN02196/000025 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-09-24 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 86602.151
[7 empty] | 5309 | 19944 | 1690173 | 2019-09-25 00:21 | 2019-09-25 01:52 | 91 | 11kV | 78762 | 880 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.22 tripped on A phase IOC Cause not ascertained \See 1690528 1690530 | September | 2019 | 2020Q1 | 2020 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Veg | 2019-09-25 | N | 89.5023 | N | 2 | N | N | 1.1101 | 39.4971 | 57556.9465
[7 empty] | 3419 | 1150 | 1690382 | 2019-09-25 21:48 | 2019-09-25 23:08 | 80 | 11kV | 6560 | 82 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC45017 Whiteman tripped on Earth fault Cause not ascertained. Patrolled OK | September | 2019 | 2020Q1 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2019-09-25 | N | 80 | N | 2 | N | N | 1.1101 | 39.4971 | 4793.8545
[7 empty] | 3357 | 625 | 1690486 | 2019-09-26 12:59 | 2019-09-26 15:06 | 127 | 11kV | 114307 | 984 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 194950 A Phase Earth Fault UG cable hit by excavator Excluded OMS 1690482 DQ | September | 2019 | 2020Q1 | 2020 | 204:82699 | 204:82699 | ZN00204/082699 | NEWCASTLE | UG | Not Veg | 2019-09-26 | N | 116.1657 | N | 2 | N | N | 1.1101 | 39.4971 | 83532.1841
[7 empty] | 3995 | 6937 | 1690549 | 2019-09-26 15:49 | 2019-09-26 17:13 | 84 | 11kV | 50316 | 599 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP45180 Avoca Beach Tripped, Reclosed Tripped and Locked out on OC and IOC Cause: DOps removed large tree branch near LB49195 | September | 2019 | 2020Q1 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2019-09-26 | N | 84 | N | 2 | N | N | 1.1101 | 39.4971 | 36769.4487
[7 empty] | 3631 | 3168 | 1690754 | 2019-09-27 16:19 | 2019-09-27 18:07 | 108 | 11kV | 221204 | 2708 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35600 Kingsford - Pa1 'S2184 Yamba Stone etc, 'S4207 Strachen St' has tripped Signals: 11kv trip, EF/Right indication, OC/Right A+B+C Phase, protection trip, Pa 15 efi Relays: OC + EF 51ABC(Timed OC), fault check, EFI Field EFI's: S4207, S3020 Remarks: UG fault. Underground fault between S3020 Barker Zac Sw/B and S2822 Anzac Barket Sw/A | September | 2019 | 2020Q1 | 2020 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2019-09-27 | N | 81.6854 | N | 2 | N | N | 1.1101 | 39.4971 | 161649.3588
[7 empty] | 4740 | 14421 | 1690682 | 2019-09-27 12:55 | 2019-09-27 19:45 | 410 | 11kV | 10330 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12630 Peats Ridge Recloser CP44945 tripped on 2 phase overcurrent and earth fault Cause: S12630 Peats ridge feeder adjacent to Link 44128 branch brought down 11kV mains See OMS 1691310 1691311 1690682 1690683 1690711 | September | 2019 | 2020Q1 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-09-27 | N | 198.6538 | N | 2 | N | N | 1.1101 | 39.4971 | 7548.8593
[7 empty] | 3381 | 808 | 1690797 | 2019-09-28 00:44 | 2019-09-28 02:31 | 107 | 11kV | 49269 | 463 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At S8000 Macquarie Park Panel 1 tripped on Relays: IOC A and B phase 50TAB, EFI Signals: 11kV Trip EFI's NIL Cause not ascertained for outage See OMS1691133 1691134 1690767 | September | 2019 | 2020Q1 | 2020 | ZN8000:PA1 | ZN8000:PA2 | ZN08000/000002 | RYDE | UG | Not Veg | 2019-09-28 | N | 106.4125 | N | 3 | N | N | 1.1101 | 39.4971 | 36004.332
[7 empty] | 4080 | 7975 | 1690825 | 2019-09-28 09:34 | 2019-09-28 10:55 | 81 | 11kV | 81 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 194967 DOLF : 10 Amp Excluded OMS 1690825 | September | 2019 | 2020Q1 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-09-28 | N | 81 | N | 3 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 4195 | 9282 | 1690908 | 2019-09-28 23:24 | 2019-09-29 03:52 | 268 | 11kV | 130546 | 1237 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 36 tripped on Relays: A and C phase IOC Signals: 11kV Trip Cause: Bat on OH adjacent to PT1608 Charles Waterview. Fault current cause bond off on CNR of Mitchel and Phillip See OMS 1691319 1691321 1690908 | September | 2019 | 2020Q1 | 2020 | ZN129:PA36 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Not Veg | 2019-09-28 | N | 105.5344 | N | 3 | N | N | 1.1101 | 39.4971 | 95399.1663
[7 empty] | 3649 | 3368 | 1691136 | 2019-09-30 13:58 | 2019-09-30 14:35 | 37 | 11kV | 407 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 194988 Feeder found with broken insulator resting on x-arm at pole DP-10736. Repaired under AP. | September | 2019 | 2020Q1 | 2020 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2019-09-30 | N | 37 | N | 2 | N | N | 1.1101 | 39.4971 | 297.4236
[7 empty] | 4946 | 16565 | 1691194 | 2019-09-30 19:16 | 2019-09-30 20:08 | 52 | 11kV | 1560 | 30 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At Zn12570 Avoca Panel 37 at PT2545 Widenow Moores roadside 31.5A HDO operated Cause: Fuse Fatigue See OMS 1691195 1691194 | September | 2019 | 2020Q1 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2019-09-30 | N | 52 | N | 2 | N | N | 1.1101 | 39.4971 | 1140.002
[7 empty] | 4859 | 15601 | 1691273 | 2019-10-01 09:41 | 2019-10-01 11:10 | 89 | 11kV | 5073 | 57 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT13680 Wesley Hanlan 11kV Middle Pahse HDO has blown Cause: A bird has flown between phases below the 11 kV HDO causing a phase to short See OMS 1691292 1691283 1691279 1691273 CC1: 22-"Refer to SOp" | October | 2019 | 2020Q2 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2019-10-01 | N | 89 | N | 3 | N | N | 1.1101 | 39.4971 | 3707.1988
[7 empty] | 4693 | 14028 | 1691266 | 2019-10-01 09:30 | 2019-10-01 13:25 | 235 | 11kV | 47350 | 326 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 194992 section of 11kv feeder and LV u/ground mains isolated from sw 69612 to identify & repair LV cable on LVF 69625 . | October | 2019 | 2020Q2 | 2020 | 223:14395 | 223:14395 | ZN00223/014395 | LAKE MACQUARIE | UG | Not Veg | 2019-10-01 | N | 145.2454 | N | 3 | N | N | 1.1101 | 39.4971 | 34601.9834
[7 empty] | 3929 | 6168 | 1691415 | 2019-10-01 19:55 | 2019-10-01 23:03 | 188.3667 | 11kV | 3955.7 | 21 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195007 A & B Phase DOLF : 20 Amp Bat near pole HS-53309. | October | 2019 | 2020Q2 | 2020 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Not Veg | 2019-10-01 | N | 188.3667 | N | 3 | N | N | 1.1101 | 39.4971 | 2890.7089
[7 empty] | 3636 | 3228 | 1691568 | 2019-10-02 16:05 | 2019-10-02 16:50 | 45 | 11kV | 945 | 21 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195027 section isolated for tree trimming pole HS-53325 | October | 2019 | 2020Q2 | 2020 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2019-10-02 | N | 45 | N | 1 | N | N | 1.1101 | 39.4971 | 690.5781
[7 empty] | 4621 | 13446 | 1691768 | 2019-10-03 16:40 | 2019-10-03 18:20 | 100 | 11kV | 200 | 2 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195047 EMPTY FEED BAG IS WRAPPED AROUND D/WIRES Allegedly sparking grass fire yesterday extinguished by fire brigade | October | 2019 | 2020Q2 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2019-10-03 | N | 100 | N | 1 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 5325 | 20108 | 1691966 | 2019-10-04 15:42 | 2019-10-04 16:40 | 58 | 11kV | 60088 | 1036 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 195067 ABS 48570 burnt up - fluctuating supply Excluded OMS 1691970 | October | 2019 | 2020Q2 | 2020 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2019-10-04 | N | 58 | N | 3 | N | N | 1.1101 | 39.4971 | 43910.5381
[7 empty] | 3748 | 4468 | 1691991 | 2019-10-04 16:18 | 2019-10-04 18:10 | 112 | 11kV | 45536 | 458 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S3472 Sefton - 11kv No.11 CB "Marjorie St" tripped on: Relays: B & C phase OC (50TBC), EF, Fault check, lockout, EFI Signals: 11kv trip, Tx3 Group earth Remarks: animals/birds. Cockatoo at PT1906 Holmes Munro | October | 2019 | 2020Q2 | 2020 | ZN3472:PA11 | ZN3472:PA11 | ZN03472/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-10-04 | N | 99.4236 | N | 3 | N | N | 1.1101 | 39.4971 | 33276.3657
[7 empty] | 3519 | 2193 | 1692063 | 2019-10-05 09:06 | 2019-10-05 12:30 | 204 | 11kV | 2040 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Autolink CP44773 Chandlers Opened by DOp Cause: OH down between CP44773 and USL42507 See OMS 1692074 1692063 | October | 2019 | 2020Q2 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-10-05 | N | 204 | N | 3 | N | N | 1.1101 | 39.4971 | 1490.7718
[7 empty] | 3928 | 6162 | 1692083 | 2019-10-05 11:40 | 2019-10-05 12:55 | 75 | 11kV | 102276 | 1387 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12610 Long Jetty Panel 9 Opened on Earth Fault to B phase, Fault Check. See OMS 1692490 1692491 1692083 | October | 2019 | 2020Q2 | 2020 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | UG | Not Veg | 2019-10-05 | N | 73.739 | N | 3 | N | N | 1.1101 | 39.4971 | 74740.2842
[7 empty] | 4849 | 15545 | 1691942 | 2019-10-04 13:39 | 2019-10-05 16:10 | 1591 | 11kV | 71869 | 1327 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Wind Strong | N | At S14143 Somersby Panel 12 tripped on earth fault with EFI Cause: S12475 End Box failed See OMS 1692464 1692466 1691942 1691975 | October | 2019 | 2020Q2 | 2020 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2019-10-04 | N | 54.159 | N | 3 | N | N | 1.1101 | 39.4971 | 52519.7454
[7 empty] | 4553 | 12574 | 1692110 | 2019-10-05 13:57 | 2019-10-05 17:35 | 218 | 11kV | 1526 | 7 | HV | Equipment Failed in Service | Equipment Failure | Zone STS Transformer | Unplanned | No Weather Impact | N | At S4570 Carrington Fitz (Ex S2196 Milperra - Pnl 12 "Carrington Mar No.3") tripped on: Relays: Tx1 - A&C ph diff Tx2 - Parallel tripping Remarks: Transformer failure. At S4570 Carrington Fitz - 11kv/415v Tx1 has failed | October | 2019 | 2020Q2 | 2020 | ZN2196:PA12 | ZN2196:PA12 | ZN02196/000012 | CANTERBURY-BANKSTOWN | Exclude | Not Veg | 2019-10-05 | N | 218 | N | 3 | N | N | 1.1101 | 39.4971 | 1115.1558
[7 empty] | 5265 | 19572 | 1692154 | 2019-10-06 03:16 | 2019-10-06 03:58 | 42 | 11kV | 168 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195072 B Phase DOLF : 63 Amp Excluded OMS 1692154 | October | 2019 | 2020Q2 | 2020 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Veg | 2019-10-06 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 3844 | 5457 | 1692156 | 2019-10-06 03:19 | 2019-10-06 04:47 | 88 | 11kV | 37488 | 426 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S3425 Castle Cove Panel 7 has tripped on Signals: 11kV Trip Relays: OC/EF/EFI and Fault Check Cause: UG fault between SW/B @ S38674 to SW/D@ S7313 Orchard Albert to SW/B at S3450 Anderson Grace Bros | October | 2019 | 2020Q2 | 2020 | ZN3425:PA7 | ZN3425:PA7 | ZN03425/000007 | WILLOUGHBY | UG | Not Veg | 2019-10-06 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 27395.1247
[7 empty] | 3935 | 6225 | 1692212 | 2019-10-06 16:48 | 2019-10-06 18:20 | 92 | 11kV | 142876 | 1553 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT ZN36300 Balgowlad North Pa8 tripped, reclosed and locked out on B/C IOC, B phase PC and ef and efi Cause: Tree branch on OH mains O/S10 King St Manlt Vale | October | 2019 | 2020Q2 | 2020 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Veg | 2019-10-06 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 104409.5667
[7 empty] | 5190 | 18875 | 1692324 | 2019-10-07 23:38 | 2019-10-08 00:25 | 47 | 11kV | 49209 | 1047 | HV | Animal Possum | Animal | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn 9118 Cronulla Panel 17 'Sub 9303 etc' feeder has tripped Signals: 11kv trip, No1 GE, ZE Relays: A and B phase timed OC, EFI Field EFI's @ Subs: Nil At PT9428 yowie Waterview Roadside and center phase HDO 50A were blown Remarks: animals/birds. Possum located @ PT9428 | October | 2019 | 2020Q2 | 2020 | ZN9118:PA17 | ZN9118:PA17 | ZN09118/000017 | SUTHERLAND | OH | Not Veg | 2019-10-07 | N | 47 | N | 1 | N | N | 1.1101 | 39.4971 | 35960.4858
[7 empty] | 5248 | 19440 | 1692327 | 2019-10-08 02:08 | 2019-10-08 05:10 | 182.1667 | 11kV | 3643.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195075 1 fault operation Single phase Instantaneous Overcurrent Fuse saver 79531 found tripped. The instantanous operation lever was found 'down' on one phase. (suspect dropped open). Partner line DOLFS 79531 were NOT blown but replaced per DG 218A 2 x 10A. DQ | October | 2019 | 2020Q2 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2019-10-08 | N | 182.1667 | N | 5 | N | N | 1.1101 | 39.4971 | 2662.4405
[7 empty] | 3377 | 774 | 1692361 | 2019-10-08 09:20 | 2019-10-08 09:30 | 10 | 11kV | 70 | 7 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195077 A Phase DOLF : 10 Amp Dead bird found at bottom of pole Excluded oms 1692361 & 1692365 | October | 2019 | 2020Q2 | 2020 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2019-10-08 | N | 10 | N | 5 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 5269 | 19592 | 1692494 | 2019-10-08 15:43 | 2019-10-08 20:55 | 312.2 | 11kV | 11662 | 85 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 195083 A Phase LLC lead broken. LV interconnected until AP is ready. then interr due to LV pause. | October | 2019 | 2020Q2 | 2020 | 532:83301 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Not Veg | 2019-10-08 | N | 137.2 | N | 5 | N | N | 1.1101 | 39.4971 | 8522.2456
[7 empty] | 5287 | 19749 | 1692516 | 2019-10-08 20:15 | 2019-10-08 21:20 | 65 | 11kV | 8060 | 124 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 195084 Tree branches being blown into 11kV OHM between poles GQ-41578 & GQ-41577. Fdr isolated to remove branches. Excluded OMS 1692516 | October | 2019 | 2020Q2 | 2020 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2019-10-08 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 5890.0103
[7 empty] | 4770 | 14740 | 1692530 | 2019-10-08 19:00 | 2019-10-08 21:25 | 145 | 11kV | 5445 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195085 Single phase LL Lead off DOLF. Fdr interrupted for repairs to LL Lead within clearance to 11kV main line. Excluded OMS No. 1692530 + 1692549 | October | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-10-08 | N | 50.8879 | N | 5 | N | N | 1.1101 | 39.4971 | 3979.0454
[7 empty] | 4815 | 15178 | 1692607 | 2019-10-09 09:41 | 2019-10-09 10:40 | 59.2167 | 11kV | 1065.9 | 18 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 195089 3 phase mains off pin pole SM 40019 | October | 2019 | 2020Q2 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2019-10-09 | N | 59.2167 | N | 2 | N | N | 1.1101 | 39.4971 | 778.9283
[7 empty] | 4170 | 9090 | 1692688 | 2019-10-09 14:47 | 2019-10-09 17:10 | 143 | 11kV | 276761 | 2819 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S36100 Panel 27 tripped on Signals: 11kV Trip, TX2 Group Earth and Zone Earth Relays: EFI. EFC, OC Trip 51N Cause: Fault Located between SW/B and S193 and SW/A @ S7353 See OMS 1692871 1692872 1692873 See OMS 1692871 1692872 1692873 1692688 1692708 | October | 2019 | 2020Q2 | 2020 | ZN36100:PA27 | ZN36100:PA25 | ZN36100/000025 | WAVERLEY | UG | Not Veg | 2019-10-09 | N | 98.177 | N | 2 | N | N | 1.1101 | 39.4971 | 202248.7757
[7 empty] | 4454 | 11549 | 1692749 | 2019-10-10 03:32 | 2019-10-10 05:01 | 89 | 11kV | 179385 | 2039 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9118 Cronulla Panel 15 tripped on: Earth fault/Lockout/Group Earth and Zone Earth Cause: 11kV feeder fault from S9386 to S9757 Kurnell Flinders to S9290 Thomas St See OMS 1692775 1692776 1692749 | October | 2019 | 2020Q2 | 2020 | ZN9118:PA15 | ZN9118:PA15 | ZN09118/000015 | SUTHERLAND | UG | Not Veg | 2019-10-10 | N | 87.9769 | N | 3 | N | N | 1.1101 | 39.4971 | 131089.267
[7 empty] | 4862 | 15626 | 1692858 | 2019-10-10 11:36 | 2019-10-10 16:35 | 299 | 11kV | 897 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195119 A phase 16 Amp fuse Substation DOLF, no cause found, not storm conditions | October | 2019 | 2020Q2 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-10-10 | N | 299 | N | 3 | N | N | 1.1101 | 39.4971 | 655.5011
[7 empty] | 5143 | 18521 | 1692916 | 2019-10-10 14:57 | 2019-10-10 19:45 | 288 | 11kV | 126482 | 1884 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.15 was interrupted at the request of DOP due to AB63 burning up. Abnormal: LB99 Open with LB1447 Closed. LB2110 Closed with open bonds line side of LB63 above tee to S3878. See 1693730 1693731 1693732 | October | 2019 | 2020Q2 | 2020 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-10-10 | N | 67.1348 | N | 3 | N | N | 1.1101 | 39.4971 | 92429.315
[7 empty] | 3569 | 2619 | 1693056 | 2019-10-11 13:35 | 2019-10-11 14:00 | 25 | 11kV | 325 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 195131 11Kv wire off pin isolated to repair. | October | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-10-11 | N | 25 | N | 5 | N | N | 1.1101 | 39.4971 | 237.5004
[7 empty] | 4880 | 15768 | 1693039 | 2019-10-11 11:14 | 2019-10-11 16:09 | 294.8833 | 11kV | 5897.6667 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 195132 No protection operation as just open circult 11kV connection. Excluded OMS 1693031 CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | October | 2019 | 2020Q2 | 2020 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2019-10-11 | N | 294.8833 | N | 5 | N | N | 1.1101 | 39.4971 | 4309.8408
[7 empty] | 4916 | 16175 | 1693092 | 2019-10-11 15:47 | 2019-10-11 18:19 | 152 | 11kV | 16179 | 110 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 195137 Transformer defective at PT 70204 | October | 2019 | 2020Q2 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2019-10-11 | N | 147.0818 | N | 5 | N | N | 1.1101 | 39.4971 | 11823.136
[7 empty] | 3440 | 1384 | 1693104 | 2019-10-11 16:38 | 2019-10-11 19:05 | 147 | 11kV | 294 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 195139 A Phase DOLF : 10 Amp Excluded OMS 1693104 | October | 2019 | 2020Q2 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | UPPER HUNTER | OH | Veg | 2019-10-11 | N | 147 | N | 5 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 3685 | 3761 | 1693148 | 2019-10-12 01:00 | 2019-10-12 02:15 | 75 | 11kV | 56720 | 856 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Light | N | Ex Zn10994 Mortdale - Pnl.7 REC62226 Connells Terry tripped on: OC Birds nest on UGOH to S10802 See 1693749 1693752 1693754 | October | 2019 | 2020Q2 | 2020 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Not Veg | 2019-10-12 | N | 66.2617 | N | 5 | N | N | 1.1101 | 39.4971 | 41449.303
[7 empty] | 3579 | 2663 | 1693105 | 2019-10-11 16:26 | 2019-10-12 03:15 | 649 | 11kV | 6041 | 14 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 195141 3 fault operation Poles down 7H-90081 Excluded OMS 1693105 | October | 2019 | 2020Q2 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-10-11 | N | 431.5 | N | 5 | N | N | 1.1101 | 39.4971 | 4414.5846
[7 empty] | 3348 | 547 | 1693152 | 2019-10-12 03:44 | 2019-10-12 04:28 | 44 | 11kV | 88308 | 2007 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S35500 Top Ryde Panel 28 Tripped, reclosed, tripped and locked out Signals: 11kV trip Relays: OC A and B phase, Reclose, Lockout on Panel 28L Cause: Tree branch on OH mains Abnormal Switching: S8724 SW/B Open and defective See OMS 1693742 1693153 16693152 | October | 2019 | 2020Q2 | 2020 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2019-10-12 | N | 44 | N | 5 | N | N | 1.1101 | 39.4971 | 64532.8818
[7 empty] | 4043 | 7462 | 1693158 | 2019-10-12 07:07 | 2019-10-12 10:25 | 198 | 11kV | 396 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 195146/02 Single phase DOLF : 10 Amp Excluded OMS 1693158 | October | 2019 | 2020Q2 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-10-12 | N | 198 | N | 5 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 5229 | 19297 | 1693208 | 2019-10-12 12:41 | 2019-10-12 14:50 | 129 | 11kV | 258 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 195149 Single phase DOLF : 10 Amp 1 by blown HV arrestor and one by 10A dolf. Excluded OMS 1693208 | October | 2019 | 2020Q2 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2019-10-12 | N | 129 | N | 5 | N | N | 1.1101 | 39.4971 | 188.5388
[7 empty] | 3876 | 5722 | 1693215 | 2019-10-12 14:05 | 2019-10-13 02:03 | 718 | 11kV | 56722 | 79 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 195155 Section of 11kv isolated for pole fire including subs 48650 & 15268. see report 195147/OMS 1693398 Excluded OMS 1693215,1693217,1693227, | October | 2019 | 2020Q2 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | NEWCASTLE | OH | Not Veg | 2019-10-12 | N | 718 | N | 5 | N | N | 1.1101 | 39.4971 | 41450.7646
[7 empty] | 3445 | 1449 | 1693262 | 2019-10-13 00:10 | 2019-10-13 03:40 | 210.2167 | 11kV | 18499.0667 | 88 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195154 B & C Phase DOLF : 40 Amp Possum on transformer Excluded OMS 1693263/4 | October | 2019 | 2020Q2 | 2020 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Not Veg | 2019-10-13 | N | 210.2167 | N | 1 | N | N | 1.1101 | 39.4971 | 13518.5723
[7 empty] | 4685 | 13962 | 1693360 | 2019-10-14 01:34 | 2019-10-14 03:20 | 106 | 11kV | 48442 | 457 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.4 tripped & reclosed on Earth Fault Possum on HV UGOH outside 3 Milburn Rd. Fault current caused a bond to burn off UGOH. See 1693757 1693758 | October | 2019 | 2020Q2 | 2020 | ZN9037:PA4 | ZN9037:PA4 | ZN09037/000004 | SUTHERLAND | OH | Not Veg | 2019-10-14 | N | 106 | N | 1 | N | N | 1.1101 | 39.4971 | 35399.9848
[7 empty] | 4247 | 9753 | 1693877 | 2019-10-16 12:30 | 2019-10-16 13:43 | 73 | 11kV | 3212 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 195210 11kv links 7004 reported as broken. Excluded oms 1693877, 1693911 | October | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-10-16 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 2347.2349
[7 empty] | 3431 | 1352 | 1693956 | 2019-10-16 16:35 | 2019-10-16 17:10 | 35 | 11kV | 1750 | 50 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 195213 Loose & twisted crossarm at pole 8F-60125 reported by Ausgrid staff. Excluded OMS 1693971 & 1693985 | October | 2019 | 2020Q2 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-10-16 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 1278.8484
[7 empty] | 4808 | 15106 | 1693981 | 2019-10-16 18:23 | 2019-10-16 20:10 | 107 | 11kV | 1712 | 16 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195215 car hit pole, broken ties. Excluded OMS 1693981 | October | 2019 | 2020Q2 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2019-10-16 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 1251.0791
[7 empty] | 4404 | 11086 | 1693938 | 2019-10-16 15:22 | 2019-10-16 21:35 | 373 | 11kV | 7646 | 110 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 195211 2 fault operations A & C Phases - DOLF : 16 Amp Sensitive Earth Fault Lightning strike at sub 70179. LA's & Tx replaced. Excluded OMS 1693938 + 1693943 + 1693955 | October | 2019 | 2020Q2 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-10-16 | N | 69.5091 | N | 4 | N | N | 1.1101 | 39.4971 | 5587.4713
[7 empty] | 5015 | 17360 | 1694091 | 2019-10-17 12:35 | 2019-10-17 14:45 | 130 | 11kV | 130 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 195231 C Phase DOLF : 10 Amp water in DOLF Excluded oms 1694091 | October | 2019 | 2020Q2 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2019-10-17 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 4570 | 12805 | 1694172 | 2019-10-17 15:56 | 2019-10-17 16:42 | 46 | 11kV | 7958 | 173 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | CP22381 Lane Cove Walter tripped, reclosed and locked out on: IOC Tree branch on mains at pole TH3531 | October | 2019 | 2020Q2 | 2020 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2019-10-17 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 5815.4717
[7 empty] | 3662 | 3530 | 1694300 | 2019-10-17 17:02 | 2019-10-17 17:54 | 52 | 11kV | 1196 | 23 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 195234 broken tapping at 11kV links 41289. trip and relose also happened on feeder 33570 Excluded OMS 1694210 | October | 2019 | 2020Q2 | 2020 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2019-10-17 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 874.0015
[7 empty] | 4495 | 11972 | 1694132 | 2019-10-17 14:25 | 2019-10-17 21:35 | 430 | 11kV | 86015 | 890 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Zn14892 Charmhaven - Pnl.14 tripped on: O/C & E/F Cause not ascertained after patrol. Fault current burnt off bond @ AB44690 & AB41862. Repiared by PM Lineworker See 1694318 1694319 16943230 | October | 2019 | 2020Q2 | 2020 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2019-10-17 | N | 96.6461 | N | 4 | N | N | 1.1101 | 39.4971 | 62857.225
[7 empty] | 4490 | 11928 | 1694482 | 2019-10-18 20:24 | 2019-10-18 23:34 | 190.3 | 11kV | 73015.8 | 1619 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S16300 Balgowlah North 11kV Panel 8 Labelled S50695 tripped, reclosed tripped and locked out on Relays: SEL -IOC B and C phase, Lockout Signals: TX1 group earth, 11kV trip Cause: Possum on LB61274 Burn off 11kV bond to S65545 SW/A DOp reports no visible alarms on panel 8. Cause: See OMS1695497 1695498 1694482 | October | 2019 | 2020Q2 | 2020 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Veg | 2019-10-18 | N | 45.0993 | N | 1 | N | N | 1.1101 | 39.4971 | 53357.793
[7 empty] | 3906 | 5996 | 1694603 | 2019-10-19 18:25 | 2019-10-19 19:43 | 78 | 11kV | 37362 | 479 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195257 1 fault operation 3 phase Overcurrent crow at pole JU-33360 Bourke St Carington. Started pole fire. A PROT -ABC O/C B PROT ABC O/C FEEDER DID NOT RECLOSE PLEASE CHECK . Excluded oms 1694604,1694606. | October | 2019 | 2020Q2 | 2020 | 204:82703 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Not Veg | 2019-10-19 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 27303.0476
[7 empty] | 4422 | 11255 | 1694624 | 2019-10-19 21:30 | 2019-10-19 23:12 | 102 | 11kV | 125967 | 1331 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2310 Punchbowl - Pnl.24 tripped on C Phase IOC, Earth Fault Field EFIs: S65965 S964 S78173 S2106 S7044 S3712 UG cable fault between S3712 Sw/B and S61990 Sw/A and S2204 Sw/A See 1695474 1695476 | October | 2019 | 2020Q2 | 2020 | ZN2310:PA24 | ZN2310:PA24 | ZN02310/000024 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-10-19 | N | 94.6409 | N | 3 | N | N | 1.1101 | 39.4971 | 92052.9682
[7 empty] | 4769 | 14732 | 1694656 | 2019-10-20 01:56 | 2019-10-20 04:10 | 134 | 11kV | 100988 | 1028 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser CP20397 Pittwater Cabbage tripped on Relays: IOC trip, OC triup, Lockout EFI down at S16702 Mona Vale Bungalow Cause Not Ascertained for outage 11kV Isolated from AB20597 to SW/A At S15214 tee S16250 See OMS 1695523 1695526 1695524 1695525 1695527 | October | 2019 | 2020Q2 | 2020 | ZN15014:PA7 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2019-10-20 | N | 98.2374 | N | 4 | N | N | 1.1101 | 39.4971 | 73799.0518
[7 empty] | 5146 | 18572 | 1694700 | 2019-10-20 11:34 | 2019-10-20 12:28 | 54 | 11kV | 41172 | 948 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP62730 Manns Narara Creek Panel 13 tripped reclosed tripped and locked out on Relays OC Signals: 11kV Trip Burnt STick found on mains near bellbowie Ave See OMS 1695493 1695495 1694700 1694704 1694705 | October | 2019 | 2020Q2 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2019-10-20 | N | 43.4304 | N | 4 | N | N | 1.1101 | 39.4971 | 30087.2832
[7 empty] | 3344 | 501 | 1694679 | 2019-10-20 09:23 | 2019-10-20 13:10 | 227 | 11kV | 227 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 195262 Single phase Live Line Clamp burnt off Excluded OMS 1694679 | October | 2019 | 2020Q2 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2019-10-20 | N | 227 | N | 4 | N | N | 1.1101 | 39.4971 | 165.8849
[7 empty] | 4925 | 16328 | 1694607 | 2019-10-19 18:49 | 2019-10-20 18:50 | 1441 | 11kV | 104958 | 78 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 195258 Broken 11kV crossarm at sub 54601 and defective pole at links 41601 Events Initial trip O/C, Sw 42091 Reclosed 2nd Trip Earth Fault Sw 42091 Locked Out | October | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-10-19 | N | 1345.6154 | N | 3 | N | N | 1.1101 | 39.4971 | 76700.2107
[7 empty] | 4725 | 14339 | 1694644 | 2019-10-20 22:46 | 2019-10-21 12:00 | 794 | 11kV | 1588 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | The 11kV TX2 and TX3 RMCB tripped at S8723 Macquarie UNI No9. Cause: The battery chargert at S8723 Macquarie UNi failed causing the transformers to trip See OMS 1695488 1694644 | October | 2019 | 2020Q2 | 2020 | ZN2635:PA47 | ZN2635:PA47 | ZN02635/000047 | RYDE | Unknown | Unknown | 2019-10-20 | N | 794 | N | 4 | N | N | 1.1101 | 39.4971 | 1160.4636
[7 empty] | 5022 | 17451 | 1694947 | 2019-10-21 17:30 | 2019-10-21 17:50 | 20 | 11kV | 720 | 36 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195281 sub required isolated for application of earths on emerg job for faulty sw 35296 Karuah pump No1 sub. Excluded OMS 1694947 | October | 2019 | 2020Q2 | 2020 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2019-10-21 | N | 20 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 5293 | 19772 | 1694980 | 2019-10-21 20:48 | 2019-10-21 21:43 | 55 | 11kV | 71363 | 1453 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ayt S35500 Top Ryde Panel 16 Opened on C phase OC EFI and Fault Check. Signals: 11kV Trip. TX2 Group Earth TX3 AC Board Trip and Battery A charger fail Cause: Possum at thye base of UG LB1433 to S5311 Mount Clarke See OMS 1695482 1695487 1694980 1694981 1694982 | October | 2019 | 2020Q2 | 2020 | ZN35500:PA16 | ZN35500:PA16 | ZN35500/000016 | RYDE | Unknown | Unknown | 2019-10-21 | N | 49.1142 | N | 3 | N | N | 1.1101 | 39.4971 | 52149.9755
[7 empty] | 3384 | 835 | 1694977 | 2019-10-21 20:20 | 2019-10-21 21:45 | 85 | 11kV | 3892 | 46 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn14143 Somersby Panel 21 tripped Relays: IOC A B and C phase Signals: 11kV Trip Cause: UG cable fault. See OMS 1695087 1695088 1694977 | October | 2019 | 2020Q2 | 2020 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | UG | Not Veg | 2019-10-21 | N | 84.6087 | N | 3 | N | N | 1.1101 | 39.4971 | 2844.1588
[7 empty] | 4930 | 16416 | 1695022 | 2019-10-22 11:05 | 2019-10-22 11:56 | 51 | 11kV | 102 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195289 section isolated and branch removed from mains Excluded OMS 1695022 | October | 2019 | 2020Q2 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2019-10-22 | N | 51 | N | 3 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 5241 | 19400 | 1695045 | 2019-10-22 10:03 | 2019-10-22 12:09 | 126 | 11kV | 7056 | 56 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195291 reported from Ausgrid staff . White rot. | October | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-10-22 | N | 126 | N | 3 | N | N | 1.1101 | 39.4971 | 5156.3167
[7 empty] | 4068 | 7749 | 1695180 | 2019-10-22 22:12 | 2019-10-22 22:50 | 37.6667 | 11kV | 38909.6667 | 1033 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | LID 195301 1 fault operation A & B Phase Instantaneous Overcurrent possum at ugoh pole JU-61251 | October | 2019 | 2020Q2 | 2020 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | OH | Not Veg | 2019-10-22 | N | 37.6667 | N | 3 | N | N | 1.1101 | 39.4971 | 28434.0368
[7 empty] | 4921 | 16289 | 1695187 | 2019-10-23 02:24 | 2019-10-23 03:36 | 72.4167 | 11kV | 122529 | 1692 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 57 tripped on Signals: 11kV Trip Relays: A phase protection - OC trip ABC B protection: OC trip ABC phase Cause Not ascertained for outage | October | 2019 | 2020Q2 | 2020 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2019-10-23 | N | 72.4167 | N | 3 | N | N | 1.1101 | 39.4971 | 89540.5792
[7 empty] | 4037 | 7420 | 1695308 | 2019-10-23 13:55 | 2019-10-23 15:35 | 100 | 11kV | 200 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Section of feeder between LB44297 and LK44339 tee PT14152 interrupted to make emergency repairs to defective insulator and cross arm on pole GO-4770 | October | 2019 | 2020Q2 | 2020 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2019-10-23 | N | 100 | N | 3 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 4962 | 16762 | 1695386 | 2019-10-23 23:18 | 2019-10-24 00:50 | 92 | 11kV | 279036 | 3033 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 31 feeder has tripped and reclosed on Signals 11kV Trip,; Group Earth and Zone earth Cause: At recloser CP46117 Balaclava Vimiera a possum has bridged the surge arrestors and caught fire. See OMS 1695386 1695387 | October | 2019 | 2020Q2 | 2020 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2019-10-23 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 203911.2786
[7 empty] | 3548 | 2450 | 1695389 | 2019-10-24 01:02 | 2019-10-24 02:59 | 117 | 11kV | 140417 | 1387 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | At ZN36300 Balgowlah North Panel 19 has tripped on Signals: 11kV trip Relays: 50T AC, Fault Check, UF Field EFI's NIL Cause: Possum @ LB49832 See OMS 1697196 1697197 1695389 | October | 2019 | 2020Q2 | 2020 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2019-10-24 | N | 101.2379 | N | 2 | N | N | 1.1101 | 39.4971 | 102612.602
[7 empty] | 4959 | 16706 | 1695566 | 2019-10-24 17:48 | 2019-10-25 02:30 | 522 | 11kV | 13572 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN35370 Galston Panel 8 Was opened Cause: tree branch on OH mains. See OMS 1695597 1695566 | October | 2019 | 2020Q2 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-10-24 | N | 522 | N | 2 | N | N | 1.1101 | 39.4971 | 9918.0173
[7 empty] | 4593 | 13095 | 1695601 | 2019-10-25 02:39 | 2019-10-25 07:27 | 288 | 11kV | 84388 | 969 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.39 tripped on: B phase Inst O/C UG cable fault between S2443 Sw/B, S35508 Sw/A & S8246 Sw/A delayed restoration to S8247 due to no access from broken locks. See 1696887 1696888 | October | 2019 | 2020Q2 | 2020 | ZN2568:PA39 | ZN2568:PA39 | ZN02568/000039 | INNER WEST | UG | Not Veg | 2019-10-25 | N | 87.0877 | N | 9 | N | N | 1.1101 | 39.4971 | 61668.2614
[7 empty] | 4607 | 13256 | 1695606 | 2019-10-25 07:03 | 2019-10-25 08:34 | 91 | 11kV | 70013 | 857 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35500 Top Ryde Panel 27 Tripped, reclosed tripped and locked out on Signals: 11kV Trip, TX3 Group Earth Relays: Earth Fault, EFI and Lockout There is an 11kV UG cable fault between S35967 and S7905. Restoration was delayed due to a faulty MDI at S35967. See OMS 1697142 1697144 1697146 1697148 1695606 | October | 2019 | 2020Q2 | 2020 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | UG | Not Veg | 2019-10-25 | N | 81.6954 | N | 9 | N | N | 1.1101 | 39.4971 | 51163.4354
[7 empty] | 3331 | 390 | 1695632 | 2019-10-25 10:13 | 2019-10-25 11:34 | 81 | 11kV | 55809 | 689 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | The 11kV footpath phase bond was found burnt off at AB1718 Cause: AB switch also looked samaged and may need replacing See OMS 1696984 1695632 1695640 | October | 2019 | 2020Q2 | 2020 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2019-10-25 | N | 81 | N | 9 | N | N | 1.1101 | 39.4971 | 40783.5711
[7 empty] | 3886 | 5795 | 1695638 | 2019-10-25 10:19 | 2019-10-25 12:06 | 107 | 11kV | 73848 | 843 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood Panel 29 'Parramatta Esher' Relays: timedd E/F, EFI & fault check Signals: 11kv trip Remarks: UG fault. 11kv UG fault from S1758 Marmaduke St to S61010 Railway Burleigh No.2 | October | 2019 | 2020Q2 | 2020 | ZN2835:PA29 | ZN2835:PA29 | ZN02835/000029 | BURWOOD | UG | Not Veg | 2019-10-25 | N | 87.6014 | N | 9 | N | N | 1.1101 | 39.4971 | 53965.9403
[7 empty] | 3355 | 618 | 1695712 | 2019-10-25 14:15 | 2019-10-25 16:04 | 109 | 11kV | 52206 | 654 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | REC46673 Terrigal Penrose - tripped, reclosed & locked out on: O/C Field EFIs: S18071 S77564 S18289 Cause not ascertained See 1696976 1696977 1696978 | October | 2019 | 2020Q2 | 2020 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2019-10-25 | N | 79.8257 | N | 9 | N | N | 1.1101 | 39.4971 | 38150.605
[7 empty] | 5171 | 18738 | 1695768 | 2019-10-25 18:34 | 2019-10-25 20:21 | 107 | 11kV | 75468 | 1480 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn10993 Hurstville North - Pnl.33 tripped on B & C phase O/C Pnl.23 tripped on: B & C phase O/C upon restoration attempt. Field EFIs; S10664 only. Tree branch on OH mains between S10984 and S10117. Dop removed. See 1696915 1696917 1696921 | October | 2019 | 2020Q2 | 2020 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | OH | Veg | 2019-10-25 | N | 50.9919 | N | 9 | N | N | 1.1101 | 39.4971 | 55149.7885
[7 empty] | 3890 | 5840 | 1695781 | 2019-10-25 19:45 | 2019-10-25 22:20 | 155 | 11kV | 155 | 1 | HV | Animal Bird | Animal | Air Break Switch | Unplanned | No Weather Impact | N | LID 195346 interrupt to remove birds nest from ABS 42897 Excluded oms 1695781 | October | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2019-10-25 | N | 155 | N | 9 | N | N | 1.1101 | 39.4971 | 113.2694
[7 empty] | 3370 | 682 | 1695687 | 2019-10-25 12:52 | 2019-10-26 02:00 | 788 | 11kV | 788 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S4898 MWSand DB Coleman Park - HV fuse operated Transformer failure - customer connected MG to pumping station until normal supply restored. | October | 2019 | 2020Q2 | 2020 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-10-25 | N | 788 | N | 9 | N | N | 1.1101 | 39.4971 | 575.8472
[7 empty] | 4130 | 8493 | 1695715 | 2019-10-25 14:25 | 2019-10-26 02:00 | 695 | 11kV | 222470 | 1400 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S847 Hornsby Panel 46 tripped and locked out on Signals: Group Earth TX3, Zone Earth Relays: Earth Fault, Fault Check, EFI, Reclose and Lockout CauseL 11kV UGOH fault above S5185. See OMS1696969 1696972 1696975 1696974 1696973 1695715 | October | 2019 | 2020Q2 | 2020 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | Unknown | Unknown | 2019-10-25 | N | 158.9071 | N | 9 | N | N | 1.1101 | 39.4971 | 162574.5142
[7 empty] | 3717 | 4086 | 1695804 | 2019-10-26 05:37 | 2019-10-26 07:10 | 93 | 11kV | 74462 | 961 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.1 tripped on:Earth Leakage UG cable fault between S1963 Tee Tx 1 and S4428 See 1696893 1696895 | October | 2019 | 2020Q2 | 2020 | ZN188:PA1 | ZN188:PA1 | ZN00188/000001 | SYDNEY | UG | Not Veg | 2019-10-26 | N | 77.4839 | N | 27 | Y | Y | 1.1101 | 39.4971 | 54414.6333
[7 empty] | 4692 | 14014 | 1695829 | 2019-10-26 11:10 | 2019-10-26 12:55 | 105 | 11kV | 210 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195347 Broken Live Line Lead Excluded OMS 1695829 | October | 2019 | 2020Q2 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-10-26 | N | 105 | N | 27 | Y | Y | 1.1101 | 39.4971 | 153.4618
[7 empty] | 3869 | 5668 | 1696005 | 2019-10-26 11:25 | 2019-10-26 15:20 | 235 | 11kV | 253404 | 2139 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn10999 Kogarah - Pnl.2 tripped on Earth Fault Tripped again at 1327 on restoration attempt Field EFIs; S50796 S10451 UG fault in UGOH to S10397. S10397 and PT10764 restored via LV // See 1696928 1696929 1696931 | October | 2019 | 2020Q2 | 2020 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | UG | Not Veg | 2019-10-26 | N | 118.4684 | N | 27 | Y | Y | 1.1101 | 39.4971 | 185180.169
[7 empty] | 4212 | 9394 | 1696039 | 2019-10-26 13:17 | 2019-10-26 16:30 | 193 | 11kV | 21230 | 110 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 195349 B Phase Substation DOLF Excluded OMS 1696039 | October | 2019 | 2020Q2 | 2020 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2019-10-26 | N | 193 | N | 27 | Y | Y | 1.1101 | 39.4971 | 15514.2578
[7 empty] | 5031 | 17571 | 1696062 | 2019-10-26 14:00 | 2019-10-26 17:00 | 180 | 11kV | 53640 | 483 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195350 A & B Phase Overcurrent tree om ohm at pole SI-91111 Excluded oms 1696062 | October | 2019 | 2020Q2 | 2020 | 523:33509 | 523:33509 | ZN00523/033509 | SINGLETON | OH | Not Veg | 2019-10-26 | N | 111.0559 | N | 27 | Y | Y | 1.1101 | 39.4971 | 39198.5299
[7 empty] | 3766 | 4761 | 1696020 | 2019-10-26 13:06 | 2019-10-26 17:35 | 269 | 11kV | 1076 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 195438 A & B phase line fuses blown fdr patrolled fuses restored Excluded oms 1696020 | October | 2019 | 2020Q2 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-10-26 | N | 269 | N | 27 | Y | Y | 1.1101 | 39.4971 | 786.3091
[7 empty] | 4091 | 8076 | 1696016 | 2019-10-26 16:10 | 2019-10-26 17:45 | 95 | 11kV | 18240 | 192 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 195348 Broken/twisted Xarm Pole JU 61666 Light St.. Only LVF 67128 customers affected out of Light St sub 67125. Excluded OMS 1696016, 1696041, 1696231, 232 | October | 2019 | 2020Q2 | 2020 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2019-10-26 | N | 95 | N | 27 | Y | Y | 1.1101 | 39.4971 | 13329.254
[7 empty] | 5197 | 18927 | 1696007 | 2019-10-26 12:00 | 2019-10-26 17:47 | 347 | 11kV | 70966 | 276 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 195352 A & C Phase Overcurrent Broken pin insulator pole WT-20052 Excluded OMS 1696007 | October | 2019 | 2020Q2 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2019-10-26 | N | 257.1232 | N | 27 | Y | Y | 1.1101 | 39.4971 | 51859.8597
[7 empty] | 4407 | 11128 | 1696048 | 2019-10-26 13:23 | 2019-10-26 18:00 | 277 | 11kV | 16150 | 100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC44995 Kulnura - tripped, reclosed and tripped on O/C Tree on mains near AB44109 See 1696966 1696968 | October | 2019 | 2020Q2 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2019-10-26 | N | 161.5 | N | 27 | Y | Y | 1.1101 | 39.4971 | 11801.9437
[7 empty] | 4005 | 7060 | 1696008 | 2019-10-26 12:54 | 2019-10-26 18:48 | 354 | 11kV | 19762 | 113 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195355 section isolated to repair mains Excluded OMS 1696008 | October | 2019 | 2020Q2 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2019-10-26 | N | 174.885 | N | 27 | Y | Y | 1.1101 | 39.4971 | 14441.4867
[7 empty] | 4968 | 16811 | 1696194 | 2019-10-26 15:04 | 2019-10-26 19:10 | 246 | 11kV | 83878 | 783 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC45133 Macmasters Beach tripped on: O/C Tree branch on OH mains. See 1696964 1696963 | October | 2019 | 2020Q2 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2019-10-26 | N | 107.1239 | N | 27 | Y | Y | 1.1101 | 39.4971 | 61295.5684
[7 empty] | 4787 | 14860 | 1696196 | 2019-10-26 14:59 | 2019-10-26 19:55 | 296 | 11kV | 32187 | 342 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12690 Berkeley Vale - Pnl.16 tripped on: A, b & C phase O/C Tree on 11kV mains. See 1696982 1696983 | October | 2019 | 2020Q2 | 2020 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2019-10-26 | N | 94.114 | N | 27 | Y | Y | 1.1101 | 39.4971 | 23521.3102
[7 empty] | 4322 | 10401 | 1696142 | 2019-10-26 13:56 | 2019-10-26 20:15 | 379 | 11kV | 210341 | 701 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 195358 2 fault operations Remove tree from OHM DOP S Williams found no targets for Fdr 83593. Excluded OMS 1696142 | October | 2019 | 2020Q2 | 2020 | 270:83593 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Veg | 2019-10-26 | N | 300.0585 | N | 27 | Y | Y | 1.1101 | 39.4971 | 153710.9988
[7 empty] | 5039 | 17666 | 1696158 | 2019-10-26 14:40 | 2019-10-26 20:44 | 364 | 11kV | 222742.15 | 1291 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195356 Isolated to repair after roof sheeting blown into mains near ABS 40204 | October | 2019 | 2020Q2 | 2020 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Veg | 2019-10-26 | N | 172.5346 | N | 27 | Y | Y | 1.1101 | 39.4971 | 162773.3934
[7 empty] | 4574 | 12836 | 1696139 | 2019-10-26 14:22 | 2019-10-26 21:05 | 403 | 11kV | 11342 | 34 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195359 DOLF : 16 Amp Excluded OMS 1696139 | October | 2019 | 2020Q2 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2019-10-26 | N | 333.5882 | N | 27 | Y | Y | 1.1101 | 39.4971 | 8288.3991
[7 empty] | 4527 | 12279 | 1696252 | 2019-10-26 15:58 | 2019-10-26 21:20 | 322 | 11kV | 43470 | 135 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 195364 HV tapping at P TB-50086 Burnt off. Subs put into parallel to restore supply. Insufficient staff to complete on the night. Excluded OMS 1696252 | October | 2019 | 2020Q2 | 2020 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2019-10-26 | N | 322 | N | 27 | Y | Y | 1.1101 | 39.4971 | 31766.5939
[7 empty] | 3302 | 162 | 1696398 | 2019-10-26 21:19 | 2019-10-26 22:07 | 48 | 11kV | 1008 | 21 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 195360 3 phase section isolated for repairs to faulty x-arm Excluded oms 1696398 | October | 2019 | 2020Q2 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2019-10-26 | N | 48 | N | 27 | Y | Y | 1.1101 | 39.4971 | 736.6167
[7 empty] | 5041 | 17682 | 1696171 | 2019-10-26 19:30 | 2019-10-26 22:17 | 167 | 11kV | 79788 | 480 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | LID 195363 No protection operation. Blown tapping pole IU-40474, isolated fdr for repairs. Note: prior to this from 26/10/19 14:56, multiple customers called advising part supply and low volts, refer to related records for calls Excluded OMS 1696171 | October | 2019 | 2020Q2 | 2020 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2019-10-26 | N | 166.225 | N | 27 | Y | Y | 1.1101 | 39.4971 | 58306.7171
[7 empty] | 3556 | 2543 | 1696119 | 2019-10-26 18:25 | 2019-10-26 23:59 | 334 | 11kV | 4342 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195367 A Phase Broken Live Line Lead Excluded OMS 1696401 | October | 2019 | 2020Q2 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-10-26 | N | 334 | N | 27 | Y | Y | 1.1101 | 39.4971 | 3173.0055
[7 empty] | 3420 | 1169 | 1696108 | 2019-10-26 14:02 | 2019-10-27 00:05 | 603.25 | 11kV | 10858.5 | 18 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 195369 Tree on Mains Excluded OMS 1696185 | October | 2019 | 2020Q2 | 2020 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2019-10-26 | N | 603.25 | N | 27 | Y | Y | 1.1101 | 39.4971 | 7935.0715
[7 empty] | 4207 | 9351 | 1696179 | 2019-10-26 14:59 | 2019-10-27 00:35 | 576.2833 | 11kV | 29390.45 | 51 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 195370 B Phase DOLF : 32 Amp Removed tree banch pole GW-30348. | October | 2019 | 2020Q2 | 2020 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2019-10-26 | N | 576.2833 | N | 27 | Y | Y | 1.1101 | 39.4971 | 21477.674
[7 empty] | 4721 | 14279 | 1696464 | 2019-10-27 00:40 | 2019-10-27 03:08 | 148 | 11kV | 384698 | 3330 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood Panel 32 tripped, reclosed tripped and lockoed out on Signals: 11kV Trip Relays: Pa32R IOC, EFI, LO and Timing Cause: 11kV feeder from S6278 to S3890 to S653 to AB3237 (UG cable fault) See OMS 1696913 1696914 1696918 1696464 | October | 2019 | 2020Q2 | 2020 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | UG | Not Veg | 2019-10-27 | N | 115.5249 | N | 8 | N | N | 1.1101 | 39.4971 | 281125.9517
[7 empty] | 4193 | 9280 | 1696471 | 2019-10-27 03:00 | 2019-10-27 03:25 | 25 | 11kV | 1750 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Avoca - Pnl.21 taken out of service for emergency repairs. Abnormal: LB49826 to AB41357 out of service defective. 66kV 824 fdr Failure - OH earth wire down. 11kV FDR from S77326 to S14890 to S18439 to AB42870 taken out of service. See 1696471 1696472 | October | 2019 | 2020Q2 | 2020 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2019-10-27 | N | 25 | N | 8 | N | N | 1.1101 | 39.4971 | 1278.8484
[7 empty] | 5189 | 18873 | 1696480 | 2019-10-27 05:10 | 2019-10-27 06:09 | 59 | 11kV | 81951 | 1389 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North Panel 19 has tripped on Signals: 11kV Trip Relays: 50T A and C phase, EFI, Faul;t Check, Lockout, TX1 fault Check Cause: Possum found at LB49832 See OMS 1696480 1696484 | October | 2019 | 2020Q2 | 2020 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2019-10-27 | N | 59 | N | 8 | N | N | 1.1101 | 39.4971 | 59887.3737
[7 empty] | 5228 | 19290 | 1696018 | 2019-10-26 13:03 | 2019-10-27 09:20 | 1217 | 11kV | 18922 | 38 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC46228 Ravensdale tripped (scan fail) Tree branch on mains. 3 PTs beyond USL42868 could not be patrolled until sunday 26/10, behind locked gates. See1696985 1696986 | October | 2019 | 2020Q2 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2019-10-26 | N | 497.9474 | N | 27 | Y | Y | 1.1101 | 39.4971 | 13827.6395
[7 empty] | 3764 | 4746 | 1696273 | 2019-10-26 16:16 | 2019-10-27 10:20 | 1084.1333 | 11kV | 35776.4 | 33 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 195373 Broken Live Line Clamp | October | 2019 | 2020Q2 | 2020 | 512:83741 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2019-10-26 | N | 1084.1333 | N | 27 | Y | Y | 1.1101 | 39.4971 | 26144.3379
[7 empty] | 3585 | 2705 | 1696492 | 2019-10-27 07:25 | 2019-10-27 10:38 | 193 | 11kV | 386 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 195376 Broken LIVE LINE Clamp Excluded OMS 1696492 | October | 2019 | 2020Q2 | 2020 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2019-10-27 | N | 193 | N | 8 | N | N | 1.1101 | 39.4971 | 282.0774
[7 empty] | 4855 | 15573 | 1696113 | 2019-10-26 14:04 | 2019-10-27 12:25 | 1341 | 11kV | 2682 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195382 A & B Phase DOLF : 10 Amp Tree on OHM Excluded OMS 1696113 | October | 2019 | 2020Q2 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2019-10-26 | N | 1341 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1959.9265
[7 empty] | 3913 | 6044 | 1696557 | 2019-10-27 12:16 | 2019-10-27 12:28 | 12 | 11kV | 3936 | 328 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195389 SI 47792 operating error outage was from CB 82580. unplanned interuption occured to customers beyond ABS 26454. | October | 2019 | 2020Q2 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2019-10-27 | N | 12 | N | 8 | N | N | 1.1101 | 39.4971 | 2876.3127
[7 empty] | 4448 | 11467 | 1696121 | 2019-10-26 14:02 | 2019-10-27 13:00 | 1378 | 11kV | 141959 | 425 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | Wind Strong | N | LID 195372 No reclose due to total fire ban feeder. Replaced pole from pole top fire IU-27008 Excluded OMS 1696121, 1696448. | October | 2019 | 2020Q2 | 2020 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Not Veg | 2019-10-26 | N | 334.0212 | N | 27 | Y | Y | 1.1101 | 39.4971 | 103739.4501
[7 empty] | 4924 | 16327 | 1696116 | 2019-10-26 14:07 | 2019-10-27 14:55 | 1488 | 11kV | 107241 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195381 A Phase Sensitive Earth Fault Excluded oms 1696116,1696150,1696153,1696154 | October | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-10-26 | N | 1374.8846 | N | 27 | Y | Y | 1.1101 | 39.4971 | 78368.5597
[7 empty] | 4178 | 9178 | 1696571 | 2019-10-27 12:41 | 2019-10-27 16:45 | 244 | 11kV | 23721 | 1288 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 195394 11kV conductor off pin insulator pole OR-57001 | October | 2019 | 2020Q2 | 2020 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2019-10-27 | N | 18.4169 | N | 8 | N | N | 1.1101 | 39.4971 | 17334.6071
[7 empty] | 5036 | 17635 | 1696622 | 2019-10-27 16:34 | 2019-10-27 17:08 | 34 | 11kV | 14824 | 436 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.28 tripped on: B Phase timed O/C Cause not ascertained. Possible developing UG cable fault. | October | 2019 | 2020Q2 | 2020 | ZN711:PA28 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2019-10-27 | N | 34 | N | 8 | N | N | 1.1101 | 39.4971 | 10832.942
[7 empty] | 3450 | 1501 | 1696654 | 2019-10-27 21:55 | 2019-10-27 23:06 | 71 | 11kV | 97554 | 1374 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S195 Oymbkle Panel 9 tripped on Relays: Time OC, Fault Check, Timing and Lockout Cause: UG cable fault - PA9 to S47348 Pacific Cecil | October | 2019 | 2020Q2 | 2020 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2019-10-27 | N | 71 | N | 8 | N | N | 1.1101 | 39.4971 | 71289.5858
[7 empty] | 5161 | 18687 | 1696670 | 2019-10-28 05:57 | 2019-10-28 07:08 | 71 | 11kV | 22626 | 321 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195407 2 fault operations 3 phase Overcurrent stick blown onto OHM at pole GW-50285 Excluded oms 1696670 | October | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-10-28 | N | 70.486 | N | 6 | N | N | 1.1101 | 39.4971 | 16534.4134
[7 empty] | 4463 | 11608 | 1696693 | 2019-10-28 08:08 | 2019-10-28 08:50 | 42 | 11kV | 21252 | 506 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1648 Enfield - Pnl.21 tripped on: B phase O/C Field EFIs: S6831, S3734, S35724 (did not operate) UG cable fault between S3734 and S2617 and S46926 | October | 2019 | 2020Q2 | 2020 | ZN1648:PA21 | ZN4853:PA12 | ZN04853/000012 | STRATHFIELD | UG | Not Veg | 2019-10-28 | N | 42 | N | 6 | N | N | 1.1101 | 39.4971 | 15530.3348
[7 empty] | 4577 | 12911 | 1696666 | 2019-10-28 05:16 | 2019-10-28 12:15 | 419 | 11kV | 7542 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At ZN 14891 Wong Panel 12 CP44778 Lauffs - fuse fatigue See OMS 1697215 1696710 1696666 | October | 2019 | 2020Q2 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-10-28 | N | 419 | N | 6 | N | N | 1.1101 | 39.4971 | 5511.4711
[7 empty] | 4542 | 12476 | 1696924 | 2019-10-28 16:04 | 2019-10-28 16:52 | 48 | 11kV | 20689 | 436 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.28 tripped on: Timed earth fault Field EFIs: S5580 UG cable fault between S5580 Sw/B and S6576 Sw/A See 1697145 1697147 | October | 2019 | 2020Q2 | 2020 | ZN711:PA28 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2019-10-28 | N | 47.4518 | N | 6 | N | N | 1.1101 | 39.4971 | 15118.911
[7 empty] | 4856 | 15574 | 1696992 | 2019-10-28 19:04 | 2019-10-28 20:57 | 113 | 11kV | 565 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195421 A Phase DOLF : 10 Amp 10 amp line fuse replaced with 10 amp, syst diag shows 15 amp please rectify. irrigator found near mains Excluded OMS 1696992 | October | 2019 | 2020Q2 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2019-10-28 | N | 113 | N | 6 | N | N | 1.1101 | 39.4971 | 412.8853
[7 empty] | 5045 | 17759 | 1696111 | 2019-10-26 14:27 | 2019-10-28 22:00 | 3333 | 11kV | 243428 | 321 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195371 3 fault operations Overcurrent OHM down beyond GW-40235 Excluded OMS 1696111 etc | October | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2019-10-26 | N | 758.3427 | N | 27 | Y | Y | 1.1101 | 39.4971 | 177890.0025
[7 empty] | 3719 | 4111 | 1697018 | 2019-10-29 00:47 | 2019-10-29 02:42 | 115 | 11kV | 3220 | 28 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.6 tripped on: O/C UG cable fault in front line section of feeder between Pnl.6 and S7661 | October | 2019 | 2020Q2 | 2020 | ZN2466:PA6 | ZN36000:PA8 | ZN36000/000008 | PARRAMATTA | UG | Not Veg | 2019-10-29 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 2353.081
[7 empty] | 3846 | 5463 | 1696997 | 2019-10-28 19:31 | 2019-10-29 03:10 | 459 | 11kV | 109701 | 239 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.28 tripped on:earth leakage Abnormal: S6576 Sw/B closed with Sw/A open from previous fault. UG cable fault between S5580 Sw/B and S6576 Sw/A | October | 2019 | 2020Q2 | 2020 | ZN711:PA28 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2019-10-28 | N | 459 | N | 6 | N | N | 1.1101 | 39.4971 | 80166.2552
[7 empty] | 4520 | 12232 | 1697180 | 2019-10-29 13:02 | 2019-10-29 14:10 | 68 | 11kV | 340 | 5 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill - Pnl.14 tripped on: Earth Fault UG cable fault in frontline section of feeder from Pnl.14 to S7522 Sw/A | October | 2019 | 2020Q2 | 2020 | ZN35900:PA14 | ZN35900:PA14 | ZN35900/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-10-29 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 4187 | 9245 | 1697221 | 2019-10-29 14:30 | 2019-10-29 15:55 | 85 | 11kV | 11815 | 139 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 195443 Section isolated to replace 33kV rusted eye bolt pole IV-90029 Excluded 1697067 1697221 1697230 | October | 2019 | 2020Q2 | 2020 | 222:33597 | 222:33597 | ZN00222/033597 | LAKE MACQUARIE | OH | Not Veg | 2019-10-29 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 8634.0535
[7 empty] | 5144 | 18527 | 1697299 | 2019-10-29 18:41 | 2019-10-29 20:00 | 79 | 11kV | 4503 | 57 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195448 DOLF's knocked out by tree falling onto sub 8602. Damage to 11kv bushing shields & arrestor brackets please arrange repairs. Volts A-243 B-243 C-244 Load A-70 B-40 C-70 Excluded OMS 1697299, 1697301,1697312 | October | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-10-29 | N | 79 | N | 5 | N | N | 1.1101 | 39.4971 | 3290.6596
[7 empty] | 5333 | 20229 | 1697227 | 2019-10-29 14:58 | 2019-10-29 21:10 | 372 | 11kV | 26040 | 70 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | S9526 Central Kingsway - DOp open Tx switch after vehicle hit kiosk. | October | 2019 | 2020Q2 | 2020 | ZN9037:PA14 | ZN9037:PA14 | ZN09037/000014 | SUTHERLAND | Unknown | Not Veg | 2019-10-29 | N | 372 | N | 5 | N | N | 1.1101 | 39.4971 | 19029.264
[7 empty] | 4717 | 14262 | 1697324 | 2019-10-30 05:28 | 2019-10-30 06:54 | 86 | 11kV | 86 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | S76936 Anzac Sturt - RMCB "HVC Sydney Light Rail" tripped on B phase Earth Fault Cause not ascertained. Customer's switchroom adjoins sub - approx 4m run to customer board. No sign of failure. | October | 2019 | 2020Q2 | 2020 |  |  |  | RANDWICK | UG | Not Veg | 2019-10-30 | N | 86 | N | 2 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 5258 | 19508 | 1697326 | 2019-10-30 05:37 | 2019-10-30 08:15 | 158 | 11kV | 60230 | 875 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.26 tripped on: A Phase O/C Field EFIs: S35265 S35266 S35267 S3595 S3594 Endbox fault at S7853 Sw/B See 1697674 1697675 | October | 2019 | 2020Q2 | 2020 | ZN1788:PA26 | ZN1788:PA42 | ZN01788/000042 | RANDWICK | UG | Not Veg | 2019-10-30 | N | 68.8343 | N | 2 | N | N | 1.1101 | 39.4971 | 44014.3075
[7 empty] | 4597 | 13140 | 1697558 | 2019-10-31 01:09 | 2019-10-31 02:34 | 85 | 11kV | 62640 | 810 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Lightning Arrestor | Unplanned | No Weather Impact | N | At ZN36300 Balgowlah North Panel 17 tripped on Relays: B and Cphase IOC and EFI + Fault Check. TX1 Earth Check Signals: CB17 EFI, IOC B - C phase Trip Abnormal swithcing LB61274 Closed, SW/A at s65545 Open Cause: Damaged lightning/surge arrestor at Ugoh to pa 8 side of ULB61274 See OMS 1697660 1697662 1697663 1697558 | October | 2019 | 2020Q2 | 2020 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Veg | 2019-10-31 | N | 77.3333 | N | 6 | N | N | 1.1101 | 39.4971 | 45775.4644
[7 empty] | 3684 | 3755 | 1697617 | 2019-10-31 10:15 | 2019-10-31 14:10 | 235 | 11kV | 235 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195467 B Phase Lead to top of Bph DOLF burnt off. Excluded OMS No. 1697617 | October | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-10-31 | N | 235 | N | 6 | N | N | 1.1101 | 39.4971 | 171.7311
[7 empty] | 3822 | 5331 | 1697691 | 2019-10-31 14:23 | 2019-10-31 15:47 | 84 | 11kV | 192689 | 2535 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36100 Rose Bay - Pnl.19 tripped on: B & C phase IOC Field EFIs: S3357 S35137 S2312 S2406 UG cable fault See 1697818 1697819 | October | 2019 | 2020Q2 | 2020 | ZN36100:PA19 | ZN36100:PA19 | ZN36100/000019 | WAVERLEY | UG | Not Veg | 2019-10-31 | N | 76.0114 | N | 6 | N | N | 1.1101 | 39.4971 | 140811.4378
[7 empty] | 4290 | 10095 | 1697698 | 2019-10-31 14:44 | 2019-10-31 16:06 | 82 | 11kV | 91348 | 1114 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.16 tripped on: Earth Fault UG cable fault in frontline section of feeder. | October | 2019 | 2020Q2 | 2020 | ZN188:PA16 | ZN188:PA16 | ZN00188/000016 | SYDNEY | UG | Not Veg | 2019-10-31 | N | 82 | N | 6 | N | N | 1.1101 | 39.4971 | 66754.4241
[7 empty] | 3354 | 613 | 1697748 | 2019-10-31 17:25 | 2019-10-31 19:10 | 105 | 11kV | 890 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195473 SECTION ISOLATED TO REMOVE TREE NEAR MAINS AT POLE GW-40235. Excluded OMS REPORT 1697748. | October | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-10-31 | N | 89 | N | 6 | N | N | 1.1101 | 39.4971 | 650.3857
[7 empty] | 3452 | 1513 | 1697751 | 2019-10-31 20:00 | 2019-11-01 02:18 | 378 | 11kV | 47628 | 126 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | PT9425 National Sixth - 11kV interrupted for safety to repair broken cross arm. | October | 2019 | 2020Q2 | 2020 | ZN9252:PA22 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Not Veg | 2019-10-31 | N | 378 | N | 6 | N | N | 1.1101 | 39.4971 | 34805.1376
[7 empty] | 4476 | 11802 | 1697833 | 2019-11-01 10:18 | 2019-11-01 13:33 | 195 | 11kV | 136564 | 701 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S2400 Berow Rd Panel 11 tripped and locked out on Time OC, Recloser and Lockout Cause: Dop patrolled cause not found and all supply restored See OMS 1698535 1698537 1698538 1697833 | November | 2019 | 2020Q2 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2019-11-01 | N | 194.8131 | N | 3 | N | N | 1.1101 | 39.4971 | 99796.9432
[7 empty] | 5202 | 18982 | 1697920 | 2019-11-01 18:08 | 2019-11-01 19:26 | 78 | 11kV | 46656 | 643 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14144 Wamberal Panel 10 tripped and locked out on a phase OC and EF, reclose lockout and EFI Cause: Tree branch down causing 11kV to contact LV links near 40062 See OMS 1698568 1698569 1698570 1697920 1697933 | November | 2019 | 2020Q2 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2019-11-01 | N | 72.5599 | N | 3 | N | N | 1.1101 | 39.4971 | 34094.8287
[7 empty] | 3858 | 5577 | 1697770 | 2019-11-01 04:20 | 2019-11-01 21:40 | 1040 | 11kV | 8253 | 132 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S187 Crows Nest Panel 24 Tripped on Relays: Earth Fault Signals: Group earth with efi Cause: Cable fault at Sub between S49892 and S3754 to CP78500. See OMS 1698563 1698564 1697770 1697774 | November | 2019 | 2020Q2 | 2020 | ZN187:PA24 | ZN187:PA24 | ZN00187/000024 | NORTH SYDNEY | UG | Not Veg | 2019-11-01 | N | 62.5227 | N | 3 | N | N | 1.1101 | 39.4971 | 6031.049
[7 empty] | 3670 | 3636 | 1697951 | 2019-11-02 02:34 | 2019-11-02 04:20 | 106 | 11kV | 89752 | 1032 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195490 1 fault operation A & B Phase Overcurrent Excluded OMS 1697951 | November | 2019 | 2020Q2 | 2020 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | OH | Veg | 2019-11-02 | N | 86.969 | N | 8 | N | N | 1.1101 | 39.4971 | 65588.1144
[7 empty] | 4573 | 12833 | 1697974 | 2019-11-02 10:58 | 2019-11-02 14:00 | 181.9833 | 11kV | 4913.55 | 27 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 195492 Broken tapping at ABS 76831 | November | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-11-02 | N | 181.9833 | N | 8 | N | N | 1.1101 | 39.4971 | 3590.6774
[7 empty] | 4003 | 7055 | 1698014 | 2019-11-02 15:36 | 2019-11-02 16:48 | 72 | 11kV | 47312 | 672 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.15 tripped on: Earth Fault Abnormal: S3020 to S2822 - out of service DMA. S1074 Sw/C open and Sw/B closed at S7846. Translay Non Auto at Pnl.15 UG cable fault between S8482, S2679 and S8855 See 1698357 1698358 | November | 2019 | 2020Q2 | 2020 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2019-11-02 | N | 70.4048 | N | 8 | N | N | 1.1101 | 39.4971 | 34574.2141
[7 empty] | 5163 | 18692 | 1698034 | 2019-11-02 18:14 | 2019-11-02 20:32 | 138 | 11kV | 34762 | 418 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.11 tripped Field EFIs: S9520 S9079 S9798 Abnormal: S9896 Sw/A to S76817 Sw/A defective UG cable fault between S9798, S9686 & S9424 See 1698346 1698347 1698348 | November | 2019 | 2020Q2 | 2020 | ZN9550:PA11 | ZN9550:PA11 | ZN09550/000011 | SUTHERLAND | UG | Not Veg | 2019-11-02 | N | 83.1627 | N | 8 | N | N | 1.1101 | 39.4971 | 25403.0443
[7 empty] | 3593 | 2768 | 1698057 | 2019-11-02 21:40 | 2019-11-02 23:05 | 85 | 11kV | 425 | 5 | HV | Arcing | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 195496 Arcing on main line near bail clamp at PT 71293. Repaired undeer AP. | November | 2019 | 2020Q2 | 2020 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2019-11-02 | N | 85 | N | 8 | N | N | 1.1101 | 39.4971 | 310.5775
[7 empty] | 4719 | 14273 | 1698052 | 2019-11-02 20:05 | 2019-11-02 23:30 | 205 | 11kV | 138360 | 732 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.5 tripped on: Sensitive Earth Abnormal: AB1565, AB2362 & LB133 are open with S8011 Sw/A and CP318 closed - DMA Tx Failure @ PT1679 See 1698370 1698371 | November | 2019 | 2020Q2 | 2020 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-11-02 | N | 189.0164 | N | 8 | N | N | 1.1101 | 39.4971 | 101109.4071
[7 empty] | 3479 | 1814 | 1698065 | 2019-11-02 22:00 | 2019-11-03 00:20 | 140 | 11kV | 136400 | 1162 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195497 1 fault operation B & C phase Overcurrent Excluded OMS 1698061 | November | 2019 | 2020Q2 | 2020 | 204:82705 | 204:82705 | ZN00204/082705 | NEWCASTLE | OH | Veg | 2019-11-02 | N | 117.3838 | N | 8 | N | N | 1.1101 | 39.4971 | 99677.0969
[7 empty] | 3857 | 5575 | 1698078 | 2019-11-03 02:41 | 2019-11-03 04:11 | 90 | 11kV | 69591 | 774 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn12690 Wyong Panel 26 Feeder tripped on Signals: 11kV trip Relays: Pa26L Earth Fault and EFI. Abnormal SWitching: LB40053 Closed, Open Bonds on Load side of CP77831 Cause: UG cable fault - 11kV feeder from ZM12690 to S65857 to S49561 See OMS 16698642 1698078 | November | 2019 | 2020Q2 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | UG | Not Veg | 2019-11-03 | N | 89.9109 | N | 4 | N | N | 1.1101 | 39.4971 | 50855.0502
[7 empty] | 3753 | 4520 | 1698056 | 2019-11-02 20:38 | 2019-11-03 05:50 | 552 | 11kV | 15985 | 169 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 195495 1 fault operation A & C Phase Overcurrent 2038hrs Sw 34640 trip & reclose 2215hrs Sw 34640 opened by SO 11kV OHM down at FR-74766 small grass fire started ERC advised Blown tapping at FR-74767 Excluded OMS 1698056 1698059 | November | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2019-11-02 | N | 94.5858 | N | 8 | N | N | 1.1101 | 39.4971 | 11681.3665
[7 empty] | 3368 | 675 | 1698087 | 2019-11-03 07:32 | 2019-11-03 08:59 | 87 | 11kV | 8439 | 97 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn874 Concord - Pnl.12 tripped on: Translay IT/R @S5417 'A" CB - IT/S UG cable fault between Pnl.12 and S2834 | November | 2019 | 2020Q2 | 2020 | ZN874:PA12 | ZN874:PA12 | ZN00874/000012 | CANADA BAY | UG | Not Veg | 2019-11-03 | N | 87 | N | 4 | N | N | 1.1101 | 39.4971 | 6166.9723
[7 empty] | 5087 | 18159 | 1698116 | 2019-11-03 12:33 | 2019-11-03 15:02 | 149 | 11kV | 194296 | 1304 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9252 Jannali - Pnl.30 tripped on: IOC trip Field EFIs: S9825 S9805 S9604 S9662 S9553 First restoration attempt failed: tripped on Earth fault with no Field EFIs UG cable fault between Pnl.30 and S9825 and S9897. | November | 2019 | 2020Q2 | 2020 | ZN9252:PA30 | ZN9252:PA30 | ZN09252/000030 | SUTHERLAND | UG | Not Veg | 2019-11-03 | N | 149 | N | 4 | N | N | 1.1101 | 39.4971 | 141985.786
[7 empty] | 3307 | 189 | 1698226 | 2019-11-03 21:52 | 2019-11-03 23:52 | 120 | 11kV | 63120 | 639 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 195504 1 fault operation A Phase Earth fault Excluded OMS 1698226 | November | 2019 | 2020Q2 | 2020 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Veg | 2019-11-03 | N | 98.7793 | N | 4 | N | N | 1.1101 | 39.4971 | 46126.2343
[7 empty] | 5160 | 18686 | 1698312 | 2019-11-04 08:55 | 2019-11-04 18:10 | 555 | 11kV | 9429 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195506 3 fault operations 3 phase Overcurrent Head of pole on fire at 3I-20039. Pole fire at 3H-80067. Mains on ground caused 10sqm grassfire. Excluded OMS No. 1698267, 1698312 | November | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-11-04 | N | 496.2632 | N | 2 | N | N | 1.1101 | 39.4971 | 6890.4351
[7 empty] | 3673 | 3662 | 1698515 | 2019-11-04 23:13 | 2019-11-05 02:00 | 167 | 11kV | 1002 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195513 Single phase DOLF : 5 Amp Excluded OMS 1698515 | November | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2019-11-04 | N | 167 | N | 2 | N | N | 1.1101 | 39.4971 | 732.232
[7 empty] | 3397 | 946 | 1698524 | 2019-11-05 06:34 | 2019-11-05 07:42 | 68 | 11kV | 46716 | 687 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn15001 Brookvale Panel 8 Labelled Harbord Rd tripped on Relays: B and C phase IOC and EFI Signals: 11kV Trip Field EFI's nil Cause not ascertained for outage | November | 2019 | 2020Q2 | 2020 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Veg | 2019-11-05 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 34138.6749
[7 empty] | 4216 | 9434 | 1698743 | 2019-11-05 10:41 | 2019-11-05 10:48 | 7 | 11kV | 7 | 1 | HV | Customer Installation Fault | Customer Installation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195517 Earth Fault Anthony from Liddell called CR, had patrolled from RAGCB to first ABS, requested AG to re energise fdr | November | 2019 | 2020Q2 | 2020 |  |  |  | SINGLETON | Unknown | Unknown | 2019-11-05 | N | 7 | N | 5 | N | N | 1.1101 | 39.4971 | 5.1154
[7 empty] | 3472 | 1715 | 1698625 | 2019-11-05 11:50 | 2019-11-05 16:15 | 265.1833 | 11kV | 37656.0333 | 142 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 195526 C Phase Broken Bail clamp at sub 61748 | November | 2019 | 2020Q2 | 2020 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2019-11-05 | N | 265.1833 | N | 5 | N | N | 1.1101 | 39.4971 | 27517.9185
[7 empty] | 5056 | 17866 | 1698637 | 2019-11-05 18:15 | 2019-11-05 20:55 | 160 | 11kV | 9600 | 60 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195529 No protection operations. Tree cracked & overhanging pole HU-90168 removed under AP Excluded OMS 1698637. | November | 2019 | 2020Q2 | 2020 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2019-11-05 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 7015.3968
[7 empty] | 4346 | 10567 | 1698709 | 2019-11-05 21:33 | 2019-11-05 22:25 | 52 | 11kV | 2860 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 195534 B Phase DOLF : 31 Amp Suspect fatigued fuse Excluded OMS 1698709, 1678711 | November | 2019 | 2020Q2 | 2020 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2019-11-05 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 2090.0036
[7 empty] | 4359 | 10687 | 1698715 | 2019-11-06 02:16 | 2019-11-06 03:07 | 51 | 11kV | 69732 | 1502 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.14 tripped on: P14L O/C, E/F Field EFIs: S4794 UG cable fault between S4794 Sw/B and S8867 Sw/A See 1699018 1699019 | November | 2019 | 2020Q2 | 2020 | ZN2568:PA14 | ZN2568:PA14 | ZN02568/000014 | SYDNEY | UG | Not Veg | 2019-11-06 | N | 46.4261 | N | 4 | N | N | 1.1101 | 39.4971 | 50958.0889
[7 empty] | 4613 | 13331 | 1698801 | 2019-11-06 12:09 | 2019-11-06 15:00 | 171 | 11kV | 200402 | 2403 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood Panel 37R tripped on Relays: Eath Fault with fault check. Signals: 11kV Trip, EFI, TX13 Group Earh and Zone Earth. Abnormal Switching: SW/A Closed at S3850 and AB3237 Cable fault between S3037 Pacific Eric to S5214 to S611 NOTE: PT628 was in LV parallel (DMA) and backfed the fault separate interruption. See OMS 1699032 1699033 1698822 1698804 1698801 | November | 2019 | 2020Q2 | 2020 | ZN80:PA37 | ZN80:PA37 | ZN00080/000037 | LANE COVE | UG | Not Veg | 2019-11-06 | N | 83.3966 | N | 4 | N | N | 1.1101 | 39.4971 | 146447.8707
[7 empty] | 3944 | 6388 | 1698868 | 2019-11-06 16:04 | 2019-11-06 17:17 | 73 | 11kV | 177595 | 2636 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.42 tripped on: Fault check and EFI Field EFIs: S36072 S50120 S35187 S6787 S35439 S8951 UG cable fault between S8951, S7117 & S1178 See 1699016 1699017 | November | 2019 | 2020Q2 | 2020 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2019-11-06 | N | 67.3729 | N | 4 | N | N | 1.1101 | 39.4971 | 129781.1878
[7 empty] | 3920 | 6123 | 1698794 | 2019-11-06 16:40 | 2019-11-06 19:45 | 185 | 11kV | 32930 | 178 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 195546 Interruption to make safe blown 11kV UGOH at pole JR-97002 and commence repairs. there were two previous trip and recloses. See report 195537 Excluded OMS 1698794, 1698883. | November | 2019 | 2020Q2 | 2020 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | Unknown | Unknown | 2019-11-06 | N | 185 | N | 4 | N | N | 1.1101 | 39.4971 | 24064.2727
[7 empty] | 4671 | 13823 | 1699046 | 2019-11-07 13:20 | 2019-11-07 14:15 | 55 | 11kV | 165 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195564 No protection operation, isolation required to re attach 11kV main. Excluded OMS 1699046 | November | 2019 | 2020Q2 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2019-11-07 | N | 55 | N | 6 | N | N | 1.1101 | 39.4971 | 120.5771
[7 empty] | 4469 | 11657 | 1699051 | 2019-11-07 12:38 | 2019-11-07 14:39 | 121 | 11kV | 53361 | 441 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Wind Strong | N | LID 195560 1 fault operation Earth Fault At pole AH-20987 contractor damaged UGOH cable witha large slab of concrete, causing the feeder to trip on earth fault. Feeder was abnormala t the time of the fault with ABS 74102 closed and abs 64198 open. Refer NAR 48673. Staff advised the earth fault indicator at sub 59240 did not indicate and earth fault. Excluded OMS 1699051 | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2019-11-07 | N | 121 | N | 6 | N | N | 1.1101 | 39.4971 | 38994.6449
[7 empty] | 3706 | 4027 | 1698934 | 2019-11-07 06:30 | 2019-11-07 15:40 | 550 | 11kV | 67650 | 123 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor U/G | Unplanned | Wind Strong | N | LID 195568 section isolated to replace faulty hazemeyer gear Excluded oms # 1698934 | November | 2019 | 2020Q2 | 2020 | 217:33608 | 217:33608 | ZN00217/033608 | LAKE MACQUARIE | UG | Not Veg | 2019-11-07 | N | 550 | N | 6 | N | N | 1.1101 | 39.4971 | 49436.6247
[7 empty] | 5236 | 19367 | 1699104 | 2019-11-07 15:03 | 2019-11-07 16:34 | 91 | 33kV Distribution | 91 | 1 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Wind Strong | N | LID 195562 section isolated to repair ties at pole JT-91961 Excluded OMS 1699104 | November | 2019 | 2020Q2 | 2020 | 417:80507 | 417:80507 | ZN00417/080507 | NEWCASTLE | Unknown | Not Veg | 2019-11-07 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 66.5001
[7 empty] | 4772 | 14765 | 1699135 | 2019-11-07 16:53 | 2019-11-07 19:10 | 137 | 11kV | 194802 | 2000 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10991 Blakehurst - Pnl.8 tripped on: A Phase O/C Field EFIs: S10138, S10264 S78477 S49021 S10692 S10160 S78851 UG cable fault between S10177 to S10889 tee PT10506 See 170047 1700479 1700480 | November | 2019 | 2020Q2 | 2020 | ZN10991:PA8 | ZN10991:PA8 | ZN10991/000008 | GEORGES RIVER | UG | Not Veg | 2019-11-07 | N | 97.401 | N | 6 | N | N | 1.1101 | 39.4971 | 142355.5559
[7 empty] | 3597 | 2782 | 1699153 | 2019-11-07 19:29 | 2019-11-07 21:08 | 99 | 11kV | 200563 | 2117 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double bay - Pnl.44 tripped on: spaj 140c relay Field EFI S6008 Abnormal: S35572 to S3091 to S342 to P34 Paddington, out of service defective UG cable fault in front line section of feeder | November | 2019 | 2020Q2 | 2020 | ZN3155:PA44 | ZN3155:PA44 | ZN03155/000044 | WOOLLAHRA | UG | Not Veg | 2019-11-07 | N | 94.7393 | N | 6 | N | N | 1.1101 | 39.4971 | 146565.5248
[7 empty] | 5099 | 18228 | 1699259 | 2019-11-08 11:28 | 2019-11-08 12:51 | 83.3 | 11kV | 4331.6 | 52 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 195580 Generator on site after HV UGOH fault. See 195546. Gen tripped on low oil. | November | 2019 | 2020Q2 | 2020 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | Unknown | Unknown | 2019-11-08 | N | 83.3 | N | 5 | N | N | 1.1101 | 39.4971 | 3165.4055
[7 empty] | 5332 | 20227 | 1699296 | 2019-11-08 13:18 | 2019-11-08 16:06 | 168 | 11kV | 52578 | 315 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 Botany - Pnl.32 tripped on: C phase IOC Field EFIs: S6277 S78272 S8739 S7234 UG cable fault between S6277 and S78272 - pit lid blew off adj Pole MA4090 (opp 1374 Botany Rd) Almost landed on lady with a stroller See 1700426 1700428 | November | 2019 | 2020Q2 | 2020 | ZN340:PA32 | ZN340:PA32 | ZN00340/000032 | BAYSIDE | UG | Not Veg | 2019-11-08 | N | 166.9143 | N | 5 | N | N | 1.1101 | 39.4971 | 38422.4516
[7 empty] | 4591 | 13074 | 1699359 | 2019-11-08 16:05 | 2019-11-08 18:05 | 120 | 11kV | 120 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195589 No protection operated, LL clamps head came off top one a dolf. Excluded OMS 1699359 | November | 2019 | 2020Q2 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-11-08 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 4478 | 11816 | 1699407 | 2019-11-08 18:08 | 2019-11-08 18:55 | 47 | 11kV | 39997 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn12570 Avoca Panel 34 Tripped on Signals: 11kV Trip Relays: B and C phase IOC and OC Cause: Burnt tree branch found under 11kV near PT12383 See OMS 1699407 1699411 1699412 1699414 | November | 2019 | 2020Q2 | 2020 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2019-11-08 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 29228.6279
[7 empty] | 3959 | 6522 | 1699417 | 2019-11-08 18:50 | 2019-11-08 20:00 | 70 | 11kV | 21630 | 309 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 195593 interrupt to repair 11kV tapping TB-50086 and remove LV cross feeder interconections Excluded oms 1699417 | November | 2019 | 2020Q2 | 2020 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2019-11-08 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 15806.566
[7 empty] | 3512 | 2122 | 1699467 | 2019-11-09 00:39 | 2019-11-09 02:18 | 99 | 11kV | 84843 | 857 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | At S12580 Erina Panel 16 Tripped on Relays: 16L: IOC, EFI and Trip LED Cause Not asceratained for outage | November | 2019 | 2020Q2 | 2020 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2019-11-09 | N | 99 | N | 4 | N | N | 1.1101 | 39.4971 | 62000.762
[7 empty] | 4884 | 15815 | 1699508 | 2019-11-09 11:10 | 2019-11-09 12:00 | 50 | 11kV | 100 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Wind Strong | N | LID 195600 Single phase DOLF : 10 Amp Replaced burnt up DOLF Excluded OMS 1699508 | November | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-11-09 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 4038 | 7424 | 1699514 | 2019-11-09 11:42 | 2019-11-09 13:45 | 123 | 11kV | 123 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 195601 A & B Phase DOLF : 10 Amp Excluded OMS 1699514 | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-11-09 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 89.8848
[7 empty] | 4240 | 9654 | 1699538 | 2019-11-09 13:33 | 2019-11-10 02:00 | 747 | 11kV | 294158 | 676 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.39 tripped on: Earth Fault Field EFIs: S8141 Abnormal: S2443 Sw/B open with S549 Sw/A Closed and S2821 Sw/B closed - Defective UG cable UG cable fault between S8141 and S2973 - could not be restored due to existing cable fault and needed to be repaired. See 1700433 1700434 1700435 | November | 2019 | 2020Q2 | 2020 | ZN2568:PA39 | ZN2568:PA39 | ZN02568/000039 | INNER WEST | UG | Not Veg | 2019-11-09 | N | 435.145 | N | 4 | N | N | 1.1101 | 39.4971 | 214961.9902
[7 empty] | 5037 | 17653 | 1699601 | 2019-11-10 07:12 | 2019-11-10 08:35 | 83 | 11kV | 415 | 5 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195608 B Phase DOLF : 10 Amp Burnt Possum at base of pole Excluded OMS 1699601 | November | 2019 | 2020Q2 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-11-10 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 303.2698
[7 empty] | 4554 | 12589 | 1699594 | 2019-11-10 05:37 | 2019-11-10 08:41 | 184 | 11kV | 172389 | 1009 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S4545 Meadowbnak Panel 21 Tripped on Relays: NIL Signals: 11kV Trip Cause: S4545 Meadowbank Panel 21 - P120 Sensitive earth relay failed. Tripped and Latched 1600627 1700628 1700629 1700630 1700632 1700633 1699594 1699605 1699607 | November | 2019 | 2020Q2 | 2020 | ZN4545:PA21 | ZN4545:PA21 | ZN04545/000021 | RYDE | Unknown | Unknown | 2019-11-10 | N | 170.8513 | N | 4 | N | N | 1.1101 | 39.4971 | 125976.7966
[7 empty] | 4736 | 14383 | 1699658 | 2019-11-10 18:04 | 2019-11-10 19:12 | 68 | 11kV | 23800 | 350 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn10999 Kogarah - Pnl.22L - 11kV bond burnt off on UGOH pole (KO18118) UGOH between S10929 Sw/B and USL30484 | November | 2019 | 2020Q2 | 2020 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Not Veg | 2019-11-10 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 17392.338
[7 empty] | 3363 | 654 | 1699677 | 2019-11-11 02:31 | 2019-11-11 03:23 | 52 | 11kV | 9308 | 179 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1850 Bass Hill - Pnl.44 tripped on: C phase O/C UG cable fault between Pnl.44, S8525 tee S6475 See 1700448 1700449 | November | 2019 | 2020Q2 | 2020 | ZN1850:PA44 | ZN1850:PA44 | ZN01850/000044 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-11-11 | N | 52 | N | 1 | N | N | 1.1101 | 39.4971 | 6802.0119
[7 empty] | 4391 | 10948 | 1699616 | 2019-11-10 08:52 | 2019-11-11 19:45 | 2093.4667 | 11kV | 200972.8 | 96 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2400 Berowra Ex Pa18 Berowra Waters Recloser CP3227 Tripped Tree has fallen on 11kV mains at 53 Calabash Pt Berowra Waters see OMS 1699612 1699616 1699611 CC1: 22-"Refer to SOp" | November | 2019 | 2020Q2 | 2020 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2019-11-10 | N | 2093.4667 | N | 4 | N | N | 1.1101 | 39.4971 | 146864.9945
[7 empty] | 3509 | 2106 | 1700000 | 2019-11-12 12:09 | 2019-11-12 13:35 | 86 | 11kV | 160734 | 1869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At Zn35400 North Sydney Panel 110 Alfred Bray Tripped on Relays: A phase protection C phase E/F efi Signals: Trip Field EFI's Nil | November | 2019 | 2020Q2 | 2020 | ZN35400:PA110 | ZN35400:PA110 | ZN35400/000110 | NORTH SYDNEY | UG | Not Veg | 2019-11-12 | N | 86 | N | 11 | N | N | 1.1101 | 39.4971 | 117459.6663
[7 empty] | 4820 | 15226 | 1700055 | 2019-11-12 13:29 | 2019-11-12 14:40 | 71 | 11kV | 13064 | 184 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | At Berkeley Vale Open bond Road side phase of USL43204 See OMS 1700492 1700055 | November | 2019 | 2020Q2 | 2020 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2019-11-12 | N | 71 | N | 11 | N | N | 1.1101 | 39.4971 | 9546.7859
[7 empty] | 4694 | 14064 | 1700096 | 2019-11-12 15:00 | 2019-11-12 17:30 | 150 | 11kV | 600 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195632 Fdr patrolled, no cause found. Customer reported this was second outage recently. Possibly mains clashing in wind. Please investigate Excluded OMS 1700096 | November | 2019 | 2020Q2 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-11-12 | N | 150 | N | 11 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 5331 | 20207 | 1700033 | 2019-11-12 12:58 | 2019-11-12 18:20 | 322 | 11kV | 28658 | 89 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 195631 C Phase DOLF : 20 Amp Blown Surge Arrestor Excluded OMS 1700033 | November | 2019 | 2020Q2 | 2020 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2019-11-12 | N | 322 | N | 11 | N | N | 1.1101 | 39.4971 | 20942.4211
[7 empty] | 5089 | 18168 | 1700188 | 2019-11-12 20:43 | 2019-11-12 21:27 | 44 | 11kV | 60324 | 1371 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S15008 Harbord Panel 6 Triped, reclosed and locked out on Relays: OC trip, E/F Trip, EFI and E/F check. Tree branch on 11kV - footpath phase branch touching LV neutral conductors Junction of West Dalley, Wayne and Girade on Pole FF46663 Dop Johnston remove tree branch | November | 2019 | 2020Q2 | 2020 | ZN15008:PA6 | ZN15008:PA6 | ZN15008/000006 | NORTHERN BEACHES | OH | Veg | 2019-11-12 | N | 44 | N | 11 | N | N | 1.1101 | 39.4971 | 44082.9999
[7 empty] | 3802 | 5026 | 1700204 | 2019-11-12 21:47 | 2019-11-12 22:38 | 51 | 11kV | 39423 | 773 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Wind Strong | N | At ZN12690 Berkeley Vale Panel 26 Tripped on Relays: B phase OC, Trim alarm, EFI Signals: TX13 Group Earth, CB 26 Open, EFI Right, OC trip. Protection Trim Timer, Protectiopn Trip Latched Abnormal Switching: LB40053 Closed, Open Bonds Below CP77831 Cause: 11kV recloser CP47878 Caught Fire | November | 2019 | 2020Q2 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2019-11-12 | N | 51 | N | 11 | N | N | 1.1101 | 39.4971 | 28809.1656
[7 empty] | 3485 | 1859 | 1700164 | 2019-11-12 20:40 | 2019-11-12 22:50 | 130 | 11kV | 390 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 195634 11kV tie broken at pole AL-10133 Excluded OMS 1700164 | November | 2019 | 2020Q2 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-11-12 | N | 130 | N | 11 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 4244 | 9700 | 1700184 | 2019-11-12 22:40 | 2019-11-12 23:15 | 35 | 11kV | 70 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 195637 Broken Live Line Clamp Excluded OMS 1700184 | November | 2019 | 2020Q2 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2019-11-12 | N | 35 | N | 11 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 5049 | 17811 | 1700210 | 2019-11-12 22:08 | 2019-11-12 23:23 | 75 | 11kV | 50025 | 667 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn9037 Miranda - Pnl.7 tripped on: A phase IOC Abnormal: AB39346 Open Cause not ascertained. Reports of flashover at UGOH to AB39346 but DOp could not find evidence. | November | 2019 | 2020Q2 | 2020 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Veg | 2019-11-12 | N | 75 | N | 11 | N | N | 1.1101 | 39.4971 | 36556.7945
[7 empty] | 5121 | 18370 | 1700186 | 2019-11-12 20:44 | 2019-11-13 06:44 | 600 | 11kV | 4200 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | LID 195640 Replaced transformer 15773 Excluded OMS 1700186 | November | 2019 | 2020Q2 | 2020 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2019-11-12 | N | 600 | N | 11 | N | N | 1.1101 | 39.4971 | 3069.2361
[7 empty] | 4457 | 11564 | 1700117 | 2019-11-12 16:20 | 2019-11-13 06:50 | 870 | 11kV | 185952 | 602 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | Hot >35C | N | LID 195633 Bushfire damaged poles & wires Wine country Dr. Fdr opened before tripping. Excluded OMS 1700100 | November | 2019 | 2020Q2 | 2020 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2019-11-12 | N | 308.8904 | N | 11 | N | N | 1.1101 | 39.4971 | 135888.2369
[7 empty] | 4588 | 13059 | 1700224 | 2019-11-13 02:02 | 2019-11-13 11:45 | 583 | 11kV | 25069 | 43 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195642 1 fault operation 3 phase Overcurrent wires down, birds hit mains adjacent sub 14477, section isolated for repairs | November | 2019 | 2020Q2 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2019-11-13 | N | 583 | N | 2 | N | N | 1.1101 | 39.4971 | 18319.6858
[7 empty] | 3451 | 1504 | 1700450 | 2019-11-13 15:38 | 2019-11-13 16:49 | 71 | 11kV | 85842 | 1278 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.16 tripped on: Earth leakage UG cable fault between S9133 Sw/B and S9378 Sw/A See 1700579 1700580 | November | 2019 | 2020Q2 | 2020 | ZN9037:PA16 | ZN9037:PA16 | ZN09037/000016 | SUTHERLAND | UG | Not Veg | 2019-11-13 | N | 67.169 | N | 2 | N | N | 1.1101 | 39.4971 | 62730.8017
[7 empty] | 3402 | 989 | 1700540 | 2019-11-14 01:15 | 2019-11-14 02:05 | 50 | 11kV | 50 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S76936 Anzac Sturt - RMCB to HVC Sydney Light Rail tripped on Earth Fault 2nd trip in 2 days. Suspect grading issues with customer's equipment | November | 2019 | 2020Q2 | 2020 |  |  |  | RANDWICK | Unknown | Not Veg | 2019-11-14 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 4312 | 10314 | 1700870 | 2019-11-14 06:03 | 2019-11-14 06:50 | 47 | 11kV | 47 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S76936 Anzac Sturt - RMCB "HVC Syd Light Rail" tripped on Earth Fault Customer keeps tripping RMCB. | November | 2019 | 2020Q2 | 2020 |  |  |  | RANDWICK | Unknown | Not Veg | 2019-11-14 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 4531 | 12320 | 1700552 | 2019-11-14 06:59 | 2019-11-14 15:37 | 518.0333 | 11kV | 48499.7 | 115 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | At PT2037 Crana Karoo dupply interruoted on distributor 1 and 2 Cause: Approved interruption by Head of System Control. Emergency Interruption for Safety Purposes SRR49614 See OMS 1700813 1700553 | November | 2019 | 2020Q2 | 2020 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Not Veg | 2019-11-14 | N | 421.7365 | N | 5 | N | N | 1.1101 | 39.4971 | 35442.1503
[7 empty] | 4108 | 8270 | 1700681 | 2019-11-14 14:33 | 2019-11-14 18:50 | 257 | 11kV | 14649 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12570 Avoca Panel 33 - Tree on OH mains at PT14235 - Required the HV and LBV to be interrupted Network interrupoted beyond LB44320 | November | 2019 | 2020Q2 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2019-11-14 | N | 257 | N | 5 | N | N | 1.1101 | 39.4971 | 10705.0571
[7 empty] | 3641 | 3253 | 1700823 | 2019-11-14 23:37 | 2019-11-15 15:45 | 968.3167 | 11kV | 25176.2333 | 26 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | Section of 11kV Pa24 Berkeley Vale 11kV CCT down beyond CP42102 - Tree | November | 2019 | 2020Q2 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2019-11-14 | N | 968.3167 | N | 5 | N | N | 1.1101 | 39.4971 | 18398.0487
[7 empty] | 3661 | 3529 | 1700937 | 2019-11-15 17:21 | 2019-11-15 18:20 | 59 | 11kV | 531 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195678 C Phase DOLF : 20 Amp Excluded OMS 1700937 | November | 2019 | 2020Q2 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2019-11-15 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 388.0391
[7 empty] | 3686 | 3762 | 1700929 | 2019-11-15 16:40 | 2019-11-15 18:48 | 128 | 11kV | 4352 | 34 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 195675 Broken x-arm brace s. 50723. HV Dropper the only thing stopping it twisting and blacking out feeder. Excluded OMS 1700929 & 1700941 | November | 2019 | 2020Q2 | 2020 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2019-11-15 | N | 128 | N | 5 | N | N | 1.1101 | 39.4971 | 3180.3132
[7 empty] | 3297 | 115 | 1700897 | 2019-11-15 19:50 | 2019-11-15 21:10 | 80 | 11kV | 13360 | 167 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 195679 Broken cross arm at KU-13111 sub interrupted for repairs Excluded OMS 1700897 1700957 | November | 2019 | 2020Q2 | 2020 | 228:7487 | 228:85410 | ZN00228/085410 | NEWCASTLE | OH | Not Veg | 2019-11-15 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 9763.0939
[7 empty] | 3752 | 4504 | 1700924 | 2019-11-15 16:20 | 2019-11-16 00:30 | 490 | 11kV | 980 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 195680 sub isolated to replace faulty tx sub 26190. Excluded OMS 1700924 | November | 2019 | 2020Q2 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2019-11-15 | N | 490 | N | 5 | N | N | 1.1101 | 39.4971 | 716.1551
[7 empty] | 4266 | 9935 | 1700883 | 2019-11-15 13:41 | 2019-11-16 02:50 | 789 | 11kV | 147798 | 322 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195672 3 fault operations Earth Fault 2 span and the 3 phases of 11kV OHM on ground from pole GW-20160, approx half acre burnt from fire. Excluded OMS 1700883, 1700903, 1700922 | November | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2019-11-15 | N | 459 | N | 5 | N | N | 1.1101 | 39.4971 | 108006.4191
[7 empty] | 4101 | 8198 | 1701022 | 2019-11-16 12:43 | 2019-11-16 14:17 | 94 | 11kV | 18330 | 195 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 11kV Recloser 45013 Gunderman has tripped, reclosed and locked out on Signals: 11kV Trip Relays: Overcurrent trip and lockout | November | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-11-16 | N | 94 | N | 2 | N | N | 1.1101 | 39.4971 | 13395.0234
[7 empty] | 3602 | 2795 | 1701038 | 2019-11-16 14:44 | 2019-11-16 18:30 | 226 | 11kV | 55370 | 245 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn9245 Engadine - Pnl.1 - Bond burnt off AB35715 | November | 2019 | 2020Q2 | 2020 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2019-11-16 | N | 226 | N | 2 | N | N | 1.1101 | 39.4971 | 40462.7629
[7 empty] | 3549 | 2465 | 1701100 | 2019-11-17 09:29 | 2019-11-17 13:55 | 266 | 11kV | 18332 | 139 | HV | Animal Bird | Animal | Fuse Assembly | Unplanned | No Weather Impact | N | LID 195687 1 fault operation A & C Phase Overcurrent A ph LF 40643 found blown. Dead & smouldering crow found underneath. Steel crossarm on pole. A ph DOLF assy replaced under AP Excluded OMS 1701100. | November | 2019 | 2020Q2 | 2020 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2019-11-17 | N | 131.8849 | N | 3 | N | N | 1.1101 | 39.4971 | 13396.4849
[7 empty] | 3910 | 6011 | 1701133 | 2019-11-17 15:55 | 2019-11-17 17:40 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195690 C Phase No protection operations. Broken dropper on C ph tank bushing. Sub isolated to repair under AP Excluded OMS 1701133. | November | 2019 | 2020Q2 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2019-11-17 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 4502 | 12085 | 1701138 | 2019-11-17 22:50 | 2019-11-18 01:50 | 180 | 11kV | 8280 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston ex Panel 8 - supply interrupted beyond CP2920 Tree on 11kV Mains and also touching LV network Cran ge required to remove tree See OMS 1701814 1701159 1701138 | November | 2019 | 2020Q2 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-11-17 | N | 180 | N | 3 | N | N | 1.1101 | 39.4971 | 6050.7798
[7 empty] | 4775 | 14785 | 1701346 | 2019-11-18 17:47 | 2019-11-18 19:15 | 88 | 11kV | 704 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195697 B Phase DOLF : 16 Amp Tx Volts 240V Excluded OMS 1701346 | November | 2019 | 2020Q2 | 2020 | 238:34148 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2019-11-18 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 514.4624
[7 empty] | 5029 | 17517 | 1701330 | 2019-11-18 16:53 | 2019-11-18 21:35 | 282 | 11kV | 20868 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT12229 Empire Bay Kill Cresty Was interrupted to repair falled LV mains caused by tree See OMS 1701715 1701330 1701340 1701332 | November | 2019 | 2020Q2 | 2020 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Veg | 2019-11-18 | N | 282 | N | 3 | N | N | 1.1101 | 39.4971 | 15249.7189
[7 empty] | 4516 | 12220 | 1701367 | 2019-11-18 19:36 | 2019-11-18 22:35 | 179 | 11kV | 7160 | 40 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 195699 B & C Phase Sectionaliser Tree brought down 11kV OHM at L 5297. Repaired under AP Excluded OMS 1701367, 1701369, 1701370 | November | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-11-18 | N | 179 | N | 3 | N | N | 1.1101 | 39.4971 | 5232.3168
[7 empty] | 3489 | 1925 | 1701385 | 2019-11-19 04:32 | 2019-11-19 08:40 | 248 | 11kV | 162106 | 2082 | HV | Animal Possum | Animal | Bond | Unplanned | No Weather Impact | N | LID 195704 2 fault operation Possum IV-32099. Blown 11kv tapping repaired under AP Excluded OMS 1701385. | November | 2019 | 2020Q2 | 2020 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2019-11-19 | N | 77.8607 | N | 5 | N | N | 1.1101 | 39.4971 | 118462.2835
[7 empty] | 4876 | 15747 | 1701408 | 2019-11-19 08:13 | 2019-11-19 10:39 | 146 | 11kV | 55336 | 510 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12620 Noraville Panel 2 tripped on Signals: 44kV trip Relays: EFI, B phase OC Cause; Suspect UG fault between LB43124 to LB43627 to S18492 tee PT12652 See OMS 1701739 1701741 1701742 1701745 1701399 | November | 2019 | 2020Q2 | 2020 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | UG | Not Veg | 2019-11-19 | N | 108.502 | N | 5 | N | N | 1.1101 | 39.4971 | 40437.9167
[7 empty] | 4733 | 14374 | 1701409 | 2019-11-19 10:00 | 2019-11-19 12:15 | 135 | 11kV | 3240 | 24 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kV links from CP41467 to PT11181 and PT11481 were isolated for safety Cause: A large bamboo tree is touching the 11kV near PT11481 See OMS 1701434 1701409 | November | 2019 | 2020Q2 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2019-11-19 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 2367.6964
[7 empty] | 3825 | 5344 | 1701478 | 2019-11-19 12:10 | 2019-11-19 13:20 | 70 | 11kV | 43306 | 667 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.18 tripped on: O/C, Earth Fault Field EFIs: S62994 S814 S1306 UG cable fault between S1306 Sw/B and S48306 Sw/A See 1701799 1701800 | November | 2019 | 2020Q2 | 2020 | ZN384:PA81 | ZN384:PA81 | ZN00384/000081 | SYDNEY | UG | Not Veg | 2019-11-19 | N | 64.9265 | N | 5 | N | N | 1.1101 | 39.4971 | 31646.7475
[7 empty] | 4162 | 8979 | 1701541 | 2019-11-19 15:51 | 2019-11-19 18:20 | 149 | 11kV | 278630 | 3503 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.16 tripped on: B Phase timed O/C and Earth Fault Field EFIs: S77472 S77473 S48559 Abnormal: S8855 Sw/B Closed & Sw/A Open (DMA) UG cable fault between S48559, S7645 tee S4563 See 1701785 1701786 | November | 2019 | 2020Q2 | 2020 | ZN35600:PA16 | ZN35600:PA16 | ZN35600/000016 | SYDNEY | UG | Not Veg | 2019-11-19 | N | 79.5404 | N | 5 | N | N | 1.1101 | 39.4971 | 203614.5858
[7 empty] | 4656 | 13663 | 1701635 | 2019-11-20 00:49 | 2019-11-20 02:45 | 116 | 11kV | 126845 | 1212 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At ZN14144 Wamberal Oanel 1 tripped on Signals: 11kV Trip, Auto CLose lockout Relays: Earth Fault, EFI Cause: Possible UG fault 11kV feeder isolated from S14897 to AB43615 to AB43616 to PT138920 See OMS 1701770 1701771 1701772 1701773 1701635 | November | 2019 | 2020Q2 | 2020 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | UG | Not Veg | 2019-11-20 | N | 104.6576 | N | 3 | N | N | 1.1101 | 39.4971 | 92694.5847
[7 empty] | 5095 | 18196 | 1701805 | 2019-11-20 16:55 | 2019-11-20 17:45 | 50 | 11kV | 1200 | 24 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 195735 No prot operations. Wire off pin 4I-80155 repaired under AP Excluded OMS 1701805. | November | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-11-20 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 4011 | 7121 | 1701862 | 2019-11-20 18:25 | 2019-11-20 21:15 | 170 | 11kV | 75650 | 445 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195739 section isolated to make repairs Excluded oms 1701862 | November | 2019 | 2020Q2 | 2020 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2019-11-20 | N | 170 | N | 3 | N | N | 1.1101 | 39.4971 | 55282.7887
[7 empty] | 5330 | 20185 | 1701914 | 2019-11-21 08:00 | 2019-11-21 12:05 | 245 | 11kV | 1225 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 195752 C Phase Dolf did not blow. But was dropped when found. Line on ground near pole AK-83264. Wire alive through TX winding. | November | 2019 | 2020Q2 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-11-21 | N | 245 | N | 3 | N | N | 1.1101 | 39.4971 | 895.1939
[7 empty] | 4255 | 9836 | 1701998 | 2019-11-21 15:45 | 2019-11-21 17:20 | 95 | 11kV | 285 | 3 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Hot >35C | N | LID 195756 Pole MD-20159 split down centre. Pola has been bolted through crack as emergency repair. To be replaced when staff are available. Excluded OMS 1701998 | November | 2019 | 2020Q2 | 2020 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2019-11-21 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 208.2696
[7 empty] | 4889 | 15833 | 1701996 | 2019-11-21 11:43 | 2019-11-22 01:25 | 822 | 11kV | 270168 | 1216 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At ZN12660 Woy Woy 11kV panel 14 has tripped Signals 11kV Trip Relays: C phase Overcurrent and IOC Cause: Truch hit pole on Phegans Bay Rd near PT13006 Abnormal Switching: CP63089 Open, S64362 Closed See OMS 1709972 1709973 1709975 1701996 | November | 2019 | 2020Q2 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2019-11-21 | N | 222.1776 | N | 3 | N | N | 1.1101 | 39.4971 | 197430.8058
[7 empty] | 3873 | 5697 | 1702130 | 2019-11-22 07:32 | 2019-11-22 12:15 | 283 | 11kV | 1698 | 6 | HV | Animal Other | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195761 16 Amp B and C Fuses Substation DOLF Replaced two HV fuses on Pt Sub - 12366. 16amp elements, back on at 1215, 240v across all three phases, B and C phases, cause possible animal | November | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2019-11-22 | N | 283 | N | 6 | N | N | 1.1101 | 39.4971 | 1240.8483
[7 empty] | 3435 | 1366 | 1702190 | 2019-11-22 15:15 | 2019-11-22 16:28 | 73 | 11kV | 1533 | 21 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Hot >35C | N | LID 195766 X arm brace bolt fallen out at pole HR-80455. No trip. Excluded OMS 1702190 | November | 2019 | 2020Q2 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2019-11-22 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 1120.2712
[7 empty] | 3803 | 5036 | 1702338 | 2019-11-22 18:21 | 2019-11-22 20:22 | 121 | 11kV | 4961 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 195768 2 Fault Operations Pole Mounted RAGCB, Overcurrent Wire off pin at pole 41-40042 | November | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-11-22 | N | 121 | N | 6 | N | N | 1.1101 | 39.4971 | 3625.3525
[7 empty] | 5151 | 18598 | 1709965 | 2019-11-22 20:45 | 2019-11-22 21:45 | 60 | 11kV | 540 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Section of 11kV feeder from S18221 to AB43229 to Open Bonds tee S14386 and S12462 interrupted to repair pin insulator. | November | 2019 | 2020Q2 | 2020 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | OH | Not Veg | 2019-11-22 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 4944 | 16532 | 1702380 | 2019-11-22 20:05 | 2019-11-22 23:30 | 205 | 11kV | 2510 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195773 A and C 16 Amp Line DOLFs and Substation DOLFs oms 1702380 A & C line dolf, also ABC dolf at sub 70996 line dolf restored at 2300 sub dolfs restored at 2330 | November | 2019 | 2020Q2 | 2020 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2019-11-22 | N | 179.2857 | N | 6 | N | N | 1.1101 | 39.4971 | 1834.234
[7 empty] | 4388 | 10920 | 1702393 | 2019-11-22 21:57 | 2019-11-23 00:30 | 153 | 11kV | 218373 | 1557 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | At S12650 West Gosford Panel 20 Labelled Central Moore tripped on OC with EFI and Group Earth - 11kV Trip Cause not ascertained - Mains to check UGOHS in daylight See OMS 1709990 1709991 1709992 1709995 1709994 1702393 | November | 2019 | 2020Q2 | 2020 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | Unknown | Unknown | 2019-11-22 | N | 140.2524 | N | 6 | N | N | 1.1101 | 39.4971 | 159580.5475
[7 empty] | 4867 | 15682 | 1702489 | 2019-11-23 14:45 | 2019-11-23 15:30 | 45 | 11kV | 1260 | 28 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 195778 Fdr isolated to repair broken crossarm braces at pole 4G-40006. | November | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-11-23 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 4190 | 9271 | 1702502 | 2019-11-23 16:55 | 2019-11-23 19:47 | 172 | 11kV | 252543 | 1501 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn10996 Rockdale - Pnl.32 tripped on: A & B phase O/C, A & B Phase IOC Field EFIs: NIL Cause not ascertained. See 1709873 1709875 1709876 LV // 1709877 1709878 1702507 | November | 2019 | 2020Q2 | 2020 | ZN10998:PA32 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Veg | 2019-11-23 | N | 168.2498 | N | 7 | N | N | 1.1101 | 39.4971 | 184550.9756
[7 empty] | 5166 | 18715 | 1702497 | 2019-11-23 16:31 | 2019-11-23 20:59 | 268 | 11kV | 6920 | 26 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 195780 2 fault operations Single phase Earth Fault Replaced L/A at SW 74812 Excluded OMS 1702497 | November | 2019 | 2020Q2 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2019-11-23 | N | 266.1538 | N | 7 | N | N | 1.1101 | 39.4971 | 5056.9319
[7 empty] | 5010 | 17295 | 1702540 | 2019-11-23 20:46 | 2019-11-23 21:32 | 46 | 11kV | 10626 | 231 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195788 2 Fault operations, A Phase, Overcurrent Patrolled, no cause found | November | 2019 | 2020Q2 | 2020 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2019-11-23 | N | 46 | N | 7 | N | N | 1.1101 | 39.4971 | 7765.1674
[7 empty] | 4000 | 6987 | 1702545 | 2019-11-23 21:17 | 2019-11-23 22:10 | 53 | 11kV | 159 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195790 A phase 20 Amp fuse Line DOLF LF to isolating sub 64740 blown No cause found | November | 2019 | 2020Q2 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-11-23 | N | 53 | N | 7 | N | N | 1.1101 | 39.4971 | 116.1925
[7 empty] | 3658 | 3492 | 1702539 | 2019-11-23 20:37 | 2019-11-23 23:15 | 158 | 11kV | 316 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195791 A Phase, 10 Amp substation DOLF | November | 2019 | 2020Q2 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-11-23 | N | 158 | N | 7 | N | N | 1.1101 | 39.4971 | 230.9235
[7 empty] | 3698 | 3894 | 1702565 | 2019-11-24 01:53 | 2019-11-24 04:54 | 181 | 11kV | 95741 | 881 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North Panel 19 Tripped,reclosed tripped and locked out on Relays: IOC A B and C phase Cause: Possum on LB49832 - also centre phase bond burnt @ MO30908 Abnormal Switching SW/B Closed at S16916 and AB20826 Opened See OMS 1712688 1712689 1702481 1702565 | November | 2019 | 2020Q2 | 2020 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2019-11-24 | N | 108.6731 | N | 3 | N | N | 1.1101 | 39.4971 | 69964.6989
[7 empty] | 4812 | 15137 | 1702516 | 2019-11-23 17:51 | 2019-11-24 13:10 | 1159 | 11kV | 2318 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 195789 B phase 16 Amp fuse Substation DOLF Blown Lightning Arrestor | November | 2019 | 2020Q2 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2019-11-23 | N | 1159 | N | 7 | N | N | 1.1101 | 39.4971 | 1693.926
[7 empty] | 4804 | 15087 | 1702660 | 2019-11-24 18:21 | 2019-11-24 19:45 | 84 | 11kV | 252 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195799 A Phase, 10 Amp fuse Substation DOLF No Cause found, not storm conditions | November | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2019-11-24 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 3729 | 4229 | 1702910 | 2019-11-25 17:58 | 2019-11-25 18:52 | 54 | 11kV | 43159 | 1395 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Electrical Storm | N | Zn847 Hornsby - Pnl.46 tripped & reclosed on: A phase IOC Lightning has hit a bond on road side phase at pole MC1632 (cnr Yirra and pacific hwy) which has caused AB694 to fail. See 1710410 1710411 | November | 2019 | 2020Q2 | 2020 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Not Veg | 2019-11-25 | N | 30.9384 | N | 17 | N | N | 1.1101 | 39.4971 | 31539.3242
[7 empty] | 3611 | 2884 | 1702814 | 2019-11-25 18:00 | 2019-11-25 19:20 | 80 | 11kV | 3920 | 49 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | lid 195822 A Phase, Substation DOLF Broken DOLF assembly replaced | November | 2019 | 2020Q2 | 2020 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2019-11-25 | N | 80 | N | 17 | N | N | 1.1101 | 39.4971 | 2864.6204
[7 empty] | 4344 | 10558 | 1702912 | 2019-11-25 18:32 | 2019-11-25 19:53 | 81 | 11kV | 66024 | 904 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195840 2 Fault operations A phase, Overcurrent Electrical Storm | November | 2019 | 2020Q2 | 2020 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Veg | 2019-11-25 | N | 73.0354 | N | 17 | N | N | 1.1101 | 39.4971 | 48248.3918
[7 empty] | 3486 | 1890 | 1702928 | 2019-11-25 18:40 | 2019-11-25 20:17 | 97 | 11kV | 110095 | 1135 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195837 1 Fault operations A, B and C phase, Instaneous Overcurrent Electrical Storm | November | 2019 | 2020Q2 | 2020 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Veg | 2019-11-25 | N | 97 | N | 17 | N | N | 1.1101 | 39.4971 | 80454.1787
[7 empty] | 4233 | 9573 | 1702902 | 2019-11-25 18:15 | 2019-11-25 20:42 | 147.25 | 11kV | 1914.25 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195843 B and C Phase 20 Amp Line DOLF Electrical Storm | November | 2019 | 2020Q2 | 2020 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2019-11-25 | N | 147.25 | N | 17 | N | N | 1.1101 | 39.4971 | 1398.8774
[7 empty] | 4738 | 14417 | 1702562 | 2019-11-24 00:58 | 2019-11-25 21:10 | 2652 | 11kV | 161746 | 1321 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.43 tripped on: Earth Fault UG cable fault between AB1436 to LB96 tee S7209 (N//) and S6944 See 1710215 1710216 1710217 1710218 1710220 1710221 1710222 | November | 2019 | 2020Q2 | 2020 | ZN2635:PA43 | ZN2635:PA43 | ZN02635/000043 | PARRAMATTA | UG | Not Veg | 2019-11-24 | N | 122.4421 | N | 3 | N | N | 1.1101 | 39.4971 | 118199.2061
[7 empty] | 3776 | 4817 | 1702918 | 2019-11-25 18:37 | 2019-11-25 21:20 | 163 | 11kV | 72469 | 481 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195845 2 Fault operations A and phase, Instantaneous Overcurrent | November | 2019 | 2020Q2 | 2020 | 204:82703 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Veg | 2019-11-25 | N | 150.6632 | N | 17 | N | N | 1.1101 | 39.4971 | 52958.2077
[7 empty] | 4234 | 9583 | 1702920 | 2019-11-25 18:37 | 2019-11-25 22:00 | 203 | 11kV | 293491 | 1487 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195847 2 Fault operations A, B and C phase, Overcurrent Targets Required Electrical Storm Patrol Requested | November | 2019 | 2020Q2 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Veg | 2019-11-25 | N | 197.3712 | N | 17 | N | N | 1.1101 | 39.4971 | 214474.5663
[7 empty] | 3993 | 6902 | 1702942 | 2019-11-25 18:55 | 2019-11-25 22:40 | 225 | 11kV | 450 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195851 B Phase 10 Amp fuse, substation DOLF | November | 2019 | 2020Q2 | 2020 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2019-11-25 | N | 225 | N | 17 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 4810 | 15113 | 1702876 | 2019-11-25 17:20 | 2019-11-25 22:45 | 325 | 11kV | 15454 | 85 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 195818 Overcurrent OHM down near Pole 8M-90013 | November | 2019 | 2020Q2 | 2020 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2019-11-25 | N | 181.8118 | N | 17 | N | N | 1.1101 | 39.4971 | 11293.3274
[7 empty] | 3405 | 1048 | 1702914 | 2019-11-25 18:35 | 2019-11-25 23:35 | 300 | 11kV | 2100 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195849 A phase 5 Amp Line DOLF Electrical Storm | November | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2019-11-25 | N | 300 | N | 17 | N | N | 1.1101 | 39.4971 | 1534.6181
[7 empty] | 4629 | 13483 | 1703004 | 2019-11-25 21:51 | 2019-11-26 00:05 | 134 | 11kV | 216990 | 2085 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Lightning | N | Zn10995 Riverwood - Pnl.1 tripped & reclosed on: Earth fault, C phase O/C Field EFIs: S10758 S61175 S10947 S10231 S10418 S10108 Suspected UG cable fault between LB30588 and S10700 See 1709892 1709893 1709894 | November | 2019 | 2020Q2 | 2020 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | UG | Not Veg | 2019-11-25 | N | 104.0719 | N | 17 | N | N | 1.1101 | 39.4971 | 158569.8919
[7 empty] | 4373 | 10799 | 1703021 | 2019-11-25 22:52 | 2019-11-26 01:28 | 156 | 11kV | 32760 | 210 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Lightning | N | At S2400 Berowra Panel 13 Tripped on Relays: B and C pjhase IOC and EFI Signals: 11kV Trip Cause: Lightning - No fault found | November | 2019 | 2020Q2 | 2020 | ZN2400:PA13 | ZN2400:PA13 | ZN02400/000013 | HORNSBY | OH | Not Veg | 2019-11-25 | N | 156 | N | 17 | N | N | 1.1101 | 39.4971 | 23940.0417
[7 empty] | 3747 | 4464 | 1702897 | 2019-11-25 19:03 | 2019-11-26 02:33 | 450.1167 | 11kV | 8552.2167 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195853 1 Fault operations A and C phase, 63 Amp Line DOLF | November | 2019 | 2020Q2 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2019-11-25 | N | 450.1167 | N | 17 | N | N | 1.1101 | 39.4971 | 6249.7077
[7 empty] | 3798 | 5005 | 1712760 | 2019-11-26 02:43 | 2019-11-26 03:13 | 30 | 11kV | 30210 | 1007 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Wind Storm | Y | At S2400 Berowra Panel 22 Tripped on Relays: A and C phase IOC, EFI, TX1 Fault Check Signals: 11kV trip Cause: CKised at S8229 CP1442 Open Cause: Damaged insulators between CP642 and AB442 - Also damaged surge arrestors between S6045 and AB2785 and LB11 See OMS 1712760 1712746 1712755 1712756 | November | 2019 | 2020Q2 | 2020 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Not Veg | 2019-11-26 | Y | 30 | N | 7 | N | Y | 1.1101 | 39.4971 | 22076.577
[7 empty] | 5058 | 17882 | 1703014 | 2019-11-25 22:18 | 2019-11-26 06:09 | 471 | 11kV | 21666 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 195856 A Phase DOLF : 20 Amp blown DOLF supply restored 0609. Note: Unable to find a LID report entered by the control room - refer to notepad entries | November | 2019 | 2020Q2 | 2020 | 261:81886 | 261:81886 | ZN00261/081886 | LAKE MACQUARIE | OH | Veg | 2019-11-25 | N | 471 | N | 17 | N | N | 1.1101 | 39.4971 | 15832.8738
[7 empty] | 5020 | 17434 | 1702978 | 2019-11-25 19:58 | 2019-11-26 08:15 | 737 | 11kV | 2948 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195857 A Phase DOLF : 10 Amp Replaced 10 amp HV DOLF on Sub 16373. Supply restoreda at 8.15 am. Note: unable to find a LID record entered Excluded OMS 1702978 | November | 2019 | 2020Q2 | 2020 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2019-11-25 | N | 737 | N | 17 | N | N | 1.1101 | 39.4971 | 2154.3114
[7 empty] | 3927 | 6160 | 1702931 | 2019-11-25 18:39 | 2019-11-26 10:05 | 926 | 11kV | 33601 | 46 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 195854 2 fault operations B Phase Overcurrent; Earth Fault Blown tapping JS-80376. ABS 17575 could not be operated.. 2 phases 11kV down JS-80055 & JS-80409. Excluded OMS 1702931. | November | 2019 | 2020Q2 | 2020 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2019-11-25 | N | 730.4565 | N | 17 | N | N | 1.1101 | 39.4971 | 24554.6197
[7 empty] | 4459 | 11567 | 1703081 | 2019-11-26 08:59 | 2019-11-26 11:10 | 131 | 11kV | 131 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 195859 A Phase DOLF : 10 Amp Excluded OMS 1703081 | November | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2019-11-26 | Y | 131 | N | 7 | N | Y | 1.1101 | 39.4971 | 95.7309
[7 empty] | 4461 | 11572 | 1712746 | 2019-11-25 15:26 | 2019-11-26 13:37 | 1331 | 11kV | 552447 | 1917 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Electrical Storm | N | At S2400 Berowra Panel 22 Tripped on Relays: A and C phase IOC, EFI, TX1 Fault Check Signals: 11kV trip Cause: CKised at S8229 CP1442 Open Cause: Damaged insulators between CP642 and AB442 - Also damaged surge arrestors between S6045 and AB2785 and LB11 See OMS 1712760 1712746 1712755 1712756 | November | 2019 | 2020Q2 | 2020 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2019-11-25 | N | 288.1831 | N | 17 | N | N | 1.1101 | 39.4971 | 403711.9732
[7 empty] | 4474 | 11734 | 1703377 | 2019-11-26 12:57 | 2019-11-26 14:36 | 99 | 11kV | 247125 | 2510 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn10991 Blakehurst - Pnl.7 tripped, reclosed & tripped on: C phase IOC Abnormal: S65992 Sw/B closed with S10889 Sw/A Open Cause not ascertained. Likely storm related See 1709897 1709900 | November | 2019 | 2020Q2 | 2020 | ZN10991:PA7 | ZN10991:PA7 | ZN10991/000007 | GEORGES RIVER | OH | Not Veg | 2019-11-26 | N | 98.4562 | N | 7 | N | N | 1.1101 | 39.4971 | 180591.661
[7 empty] | 4643 | 13565 | 1703337 | 2019-11-26 12:55 | 2019-11-26 15:47 | 172 | 11kV | 312180 | 1815 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | ZN9245 ENGADINE 11kV CB Panel 13 'S9668 Cooper Street' tripped, reclosed and tripped Signals: 11kv trip Relays: EF, LO, IOC EFI: S9668 S9007 S9792 Cause: storm. Tree branch Adjacent PT9381 | November | 2019 | 2020Q2 | 2020 | ZN9245:PA13 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Veg | 2019-11-26 | Y | 172 | N | 7 | N | Y | 1.1101 | 39.4971 | 228131.9362
[7 empty] | 3609 | 2850 | 1706394 | 2019-11-26 11:47 | 2019-11-26 15:52 | 245 | 11kV | 40739 | 277 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195891 3 fault operations Excluded OMS 1703225 42009 tripped while backfeeding this job - see OMS 1706396 | November | 2019 | 2020Q2 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2019-11-26 | Y | 147.0722 | N | 7 | N | Y | 1.1101 | 39.4971 | 29770.8596
[7 empty] | 4376 | 10815 | 1704661 | 2019-11-26 15:05 | 2019-11-26 16:00 | 55 | 11kV | 15485 | 465 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Electrical Storm | Y | LID 195894 1 fault operation ABS 74509 struck by lightening. DMA. DE energised due to pole fire. Excluded OMS 1704661. | November | 2019 | 2020Q2 | 2020 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2019-11-26 | Y | 33.3011 | N | 7 | N | Y | 1.1101 | 39.4971 | 11315.9813
[7 empty] | 5004 | 17260 | 1703555 | 2019-11-26 13:08 | 2019-11-26 16:01 | 173 | 11kV | 209693 | 1216 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | Zn1290 Leightonfield - Pnl.11 - tripped on: A & C phase O/C Cause not ascertained See 1709842 1709843 | November | 2019 | 2020Q2 | 2020 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2019-11-26 | N | 172.4449 | N | 7 | N | N | 1.1101 | 39.4971 | 153237.4595
[7 empty] | 4339 | 10507 | 1704682 | 2019-11-26 14:02 | 2019-11-26 16:10 | 128 | 11kV | 1330 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195892 1 Fault operations, Pole Mounted RAGCB Nothing found | November | 2019 | 2020Q2 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2019-11-26 | Y | 83.125 | N | 7 | N | Y | 1.1101 | 39.4971 | 971.9248
[7 empty] | 3576 | 2656 | 1703863 | 2019-11-26 13:22 | 2019-11-26 16:26 | 184 | 11kV | 141379 | 1246 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | t S12660 Woy Woy Panel 14 Opened on A phase IOC and Timed OC with EFI Cause: Weather Related See OMS 1709961 1709963 1703863 | November | 2019 | 2020Q2 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2019-11-26 | Y | 113.4663 | N | 7 | N | Y | 1.1101 | 39.4971 | 103315.6032
[7 empty] | 5252 | 19464 | 1704575 | 2019-11-26 13:04 | 2019-11-26 16:55 | 231 | 11kV | 222915 | 965 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S2400 Berowra Pa26 tripped, reclosed, tripped and locked out on Relays: 50TBC, IOC B and Cphase Cause: Trees on OH | November | 2019 | 2020Q2 | 2020 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2019-11-26 | Y | 231 | N | 7 | N | Y | 1.1101 | 39.4971 | 162899.7071
[7 empty] | 4414 | 11201 | 1703225 | 2019-11-26 14:14 | 2019-11-26 16:56 | 162 | 11kV | 11340 | 70 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195889 1 fault operation Tree branch on mains AN-90042. Tripped while being backfed on outage of 48067. See OMS 1706394. Excluded OMS 1705092 | November | 2019 | 2020Q2 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2019-11-26 | Y | 162 | N | 7 | N | Y | 1.1101 | 39.4971 | 8286.9375
[7 empty] | 4805 | 15090 | 1704212 | 2019-11-26 13:50 | 2019-11-26 17:33 | 223 | 11kV | 121312 | 544 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S14891 Wyong - Panel 20 tripped, reclosed, tripped and locked out on Timing relays and Prohibition Relay. Cause: Tree branch on OH mains - near link 42103 Tree removed by DOp | November | 2019 | 2020Q2 | 2020 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2019-11-26 | Y | 223 | N | 7 | N | Y | 1.1101 | 39.4971 | 88651.2315
[7 empty] | 4350 | 10594 | 1703936 | 2019-11-26 13:33 | 2019-11-26 17:55 | 262 | 11kV | 133067 | 1542 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 195870 Trees into mains Excluded OMS 1703936 | November | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-11-26 | N | 86.2951 | N | 7 | N | N | 1.1101 | 39.4971 | 97241.4388
[7 empty] | 3563 | 2593 | 1705475 | 2019-11-26 16:23 | 2019-11-26 18:30 | 127 | 11kV | 127 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 195897 DOLF : 10 Amp Excluded OMS 1705475 | November | 2019 | 2020Q2 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2019-11-26 | Y | 127 | N | 7 | N | Y | 1.1101 | 39.4971 | 92.8079
[7 empty] | 5074 | 18058 | 1704801 | 2019-11-26 18:20 | 2019-11-26 19:15 | 55 | 11kV | 17985 | 327 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 195922 broken crossarm at pole FS-92855 Excluded OMS 1704801 | November | 2019 | 2020Q2 | 2020 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2019-11-26 | Y | 55 | N | 7 | N | Y | 1.1101 | 39.4971 | 13142.9075
[7 empty] | 4020 | 7194 | 1705105 | 2019-11-26 16:16 | 2019-11-26 19:30 | 194 | 11kV | 148410 | 765 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | ZN35900 POTTS HILL 11kV CB Panel 3 'S6760 Rookwood Wedlock no1' fdr tripped on Relays: A+B Phase OC Signals: 11kv trip Abnormal: S5605SwB closed, AB2496 open Cause: lighting surge/arrestor Damaged surge arrestor on 11kv UGOH near S5369 waterloo como N.01 see DMA See 1709744 ex 1705105 | November | 2019 | 2020Q2 | 2020 | ZN35900:PA3 | ZN35900:PA3 | ZN35900/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2019-11-26 | N | 194 | N | 7 | N | N | 1.1101 | 39.4971 | 108453.6506
[7 empty] | 3637 | 3238 | 1704775 | 2019-11-26 15:15 | 2019-11-26 19:50 | 275 | 11kV | 1100 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195921 DOLF : 20 Amp Excluded OMS 1704775 | November | 2019 | 2020Q2 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2019-11-26 | N | 275 | N | 7 | N | N | 1.1101 | 39.4971 | 803.8476
[7 empty] | 4061 | 7687 | 1704542 | 2019-11-26 14:25 | 2019-11-26 20:40 | 375 | 11kV | 88867 | 916 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 195924 11kV crossarm broken pole FS-51328 11kV into LV Excluded OMS 1704542 | November | 2019 | 2020Q2 | 2020 | 524:33572 | 524:33572 | ZN00524/033572 | CESSNOCK | OH | Not Veg | 2019-11-26 | Y | 97.0164 | N | 7 | N | Y | 1.1101 | 39.4971 | 64941.3825
[7 empty] | 5134 | 18468 | 1704751 | 2019-11-26 15:09 | 2019-11-26 20:45 | 336 | 11kV | 672 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 195901 Single phase DOLF : 10 Amp this OMS job not sent to control Queue. Tx replaced and SAO required. Excluded OMS 1704751, | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-11-26 | Y | 336 | N | 7 | N | Y | 1.1101 | 39.4971 | 491.0778
[7 empty] | 4995 | 17159 | 1704005 | 2019-11-26 13:37 | 2019-11-26 21:20 | 463 | 11kV | 35808 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | REC45026 Fountaindale - tripped on: O/C Tree brought down OH mains See 1709914 1709915 | November | 2019 | 2020Q2 | 2020 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2019-11-26 | Y | 331.5556 | N | 7 | N | Y | 1.1101 | 39.4971 | 26167.4302
[7 empty] | 4948 | 16582 | 1705292 | 2019-11-26 16:54 | 2019-11-26 21:30 | 276 | 11kV | 828 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 195907 DOLF : 6 Amp Excluded OMS 1705292 | November | 2019 | 2020Q2 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-11-26 | Y | 276 | N | 7 | N | Y | 1.1101 | 39.4971 | 605.078
[7 empty] | 3986 | 6766 | 1705915 | 2019-11-26 16:36 | 2019-11-26 22:00 | 324 | 11kV | 5508 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195903 not this OMS job was common to many jobs in the same area. Line patrolled and A and C line fuses replaced. Note 40A fuses blew but crew only had 31.5 A fuses, so fuses size should be corrected one day. Excluded OMS 1705915, | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-11-26 | Y | 324 | N | 7 | N | Y | 1.1101 | 39.4971 | 4025.0839
[7 empty] | 3879 | 5746 | 1706586 | 2019-11-26 21:30 | 2019-11-26 22:00 | 30 | 11kV | 330 | 11 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195900 no protection operation, isolated to allow repairs and to make safe. | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2019-11-26 | Y | 30 | N | 7 | N | Y | 1.1101 | 39.4971 | 241.1543
[7 empty] | 4524 | 12248 | 1705050 | 2019-11-26 16:07 | 2019-11-26 22:30 | 383 | 11kV | 22214 | 58 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | Y | LID 195904 No protection ops. B ph LL driopper broken. Replaced under AP Excluded OMS 1705050. | November | 2019 | 2020Q2 | 2020 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | OH | Not Veg | 2019-11-26 | N | 383 | N | 7 | N | N | 1.1101 | 39.4971 | 16233.336
[7 empty] | 3446 | 1451 | 1704663 | 2019-11-26 14:52 | 2019-11-26 23:00 | 487.8167 | 11kV | 11707.6 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195909 A phase 40 Amp Line DOLF Electrical Storm | November | 2019 | 2020Q2 | 2020 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2019-11-26 | Y | 487.8167 | N | 7 | N | Y | 1.1101 | 39.4971 | 8555.5688
[7 empty] | 4922 | 16298 | 1709477 | 2019-11-26 13:01 | 2019-11-26 23:50 | 649 | 11kV | 306403 | 1103 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn9037 Miranda - Panel 2 tripped, reclosed, tripped and locked out on A phhase IOC, Timed and Lockout Cause: Tree branch on OH adjacent to LB35840 See OMS 1709477 1709483 1709482 1709481 1709480 1709479 | November | 2019 | 2020Q2 | 2020 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2019-11-26 | Y | 277.7906 | N | 7 | N | Y | 1.1101 | 39.4971 | 223910.275
[7 empty] | 4610 | 13301 | 1705093 | 2019-11-26 19:38 | 2019-11-26 23:50 | 252 | 11kV | 4788 | 19 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195905/01 & 02 Sub 7530 A phase DOLF blown Along with Spur fuse 6905 Restored together | November | 2019 | 2020Q2 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2019-11-26 | Y | 252 | N | 7 | N | Y | 1.1101 | 39.4971 | 3498.9292
[7 empty] | 5201 | 18949 | 1705491 | 2019-11-26 17:45 | 2019-11-26 23:55 | 370 | 11kV | 2220 | 6 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | Y | LID 195912 Main cause blown llc at pole AJ 20591. See switching for more detail. Excluded oms 1705491 | November | 2019 | 2020Q2 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2019-11-26 | Y | 370 | N | 7 | N | Y | 1.1101 | 39.4971 | 1622.3105
[7 empty] | 4220 | 9477 | 1705743 | 2019-11-26 19:29 | 2019-11-27 00:05 | 276 | 11kV | 552 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 195911 A and B Phase 20Amp Line DOLF Stick on mains removed by a better stick | November | 2019 | 2020Q2 | 2020 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2019-11-26 | Y | 276 | N | 7 | N | Y | 1.1101 | 39.4971 | 403.3853
[7 empty] | 4535 | 12375 | 1705295 | 2019-11-26 16:54 | 2019-11-27 01:00 | 486 | 11kV | 1458 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 195915 Single phase DOLF : 10 Amp Excluded OMS 1705295 | November | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | SINGLETON | OH | Veg | 2019-11-26 | Y | 486 | N | 7 | N | Y | 1.1101 | 39.4971 | 1065.4634
[7 empty] | 4415 | 11202 | 1705539 | 2019-11-26 18:03 | 2019-11-27 01:10 | 426.9667 | 11kV | 5123.6 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195918 A and C Phase 16 Amp LIine DOLF Feeder patrolled | November | 2019 | 2020Q2 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2019-11-26 | Y | 426.9667 | N | 7 | N | Y | 1.1101 | 39.4971 | 3744.1758
[7 empty] | 4169 | 9068 | 1705205 | 2019-11-26 16:37 | 2019-11-27 01:20 | 523.5333 | 11kV | 5235.3333 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 195914 Blown sub DOLF @ 70026 and LF 10381 Restored similtaneously Excluded OMS 1705369 | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-11-26 | Y | 523.5333 | N | 7 | N | Y | 1.1101 | 39.4971 | 3825.8272
[7 empty] | 4326 | 10424 | 1705596 | 2019-11-26 18:23 | 2019-11-27 03:30 | 547.0167 | 11kV | 254662.4667 | 568 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Section of Panel 41 beyond Recloser CP46120 Russel Tripped and locked out on OC 11kV Down near PT2248 See OMS 1705596 1706062 | November | 2019 | 2020Q2 | 2020 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2019-11-26 | N | 448.3494 | N | 7 | N | N | 1.1101 | 39.4971 | 186099.8194
[7 empty] | 3372 | 721 | 1706063 | 2019-11-27 02:03 | 2019-11-27 04:28 | 145 | 11kV | 1885 | 13 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | the 10A HDO fuse operated at PT13127 Peats Cooks 0.6 Cause: Weather related - Storm See OMS 1706497 1706063 | November | 2019 | 2020Q2 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2019-11-27 | N | 145 | N | 8 | N | N | 1.1101 | 39.4971 | 1377.5024
[7 empty] | 4899 | 15962 | 1706069 | 2019-11-27 03:07 | 2019-11-27 10:30 | 443 | 11kV | 64532 | 166 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 195919 Tree inbetween sub 52426 & 54163 Excluded OMS 1706069 | November | 2019 | 2020Q2 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2019-11-27 | N | 388.747 | N | 8 | N | N | 1.1101 | 39.4971 | 47158.0822
[7 empty] | 4699 | 14093 | 1706077 | 2019-11-27 05:22 | 2019-11-27 10:40 | 318.2 | 11kV | 3182 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 195931 A Phase DOLF : 20 Amp | November | 2019 | 2020Q2 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2019-11-27 | N | 318.2 | N | 8 | N | N | 1.1101 | 39.4971 | 2325.3117
[7 empty] | 4157 | 8874 | 1703793 | 2019-11-26 12:59 | 2019-11-27 10:53 | 1314 | 11kV | 92001 | 91 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN15013 Terrey Hills Panel 10 from recloser CP20852 tripped and reclosed with CP49122 Sectionliser found tripped on A B and C with OC flags Cause: DOp cut tree off 11kV Mains and patrolled feeder See OMS 1711434 1711436 1703793 1704051 | November | 2019 | 2020Q2 | 2020 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 1011 | N | 7 | N | Y | 1.1101 | 39.4971 | 67231.6172
[7 empty] | 4447 | 11456 | 1704920 | 2019-11-26 15:05 | 2019-11-27 11:00 | 1195 | 11kV | 31464 | 420 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Wind Storm | Y | EX Zn14891 Wyong Pa5 CP40082 Jilliby Tripped and Reclosed on OC CP44781 Dunks Lane Auto Linkls Operated Cause: Patrolled - All Clear by DOp - Auto links defective? See OMS 1709953 1709955 1706096 | November | 2019 | 2020Q2 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-11-26 | Y | 74.9143 | N | 7 | N | Y | 1.1101 | 39.4971 | 22992.9632
[7 empty] | 4907 | 16013 | 1706070 | 2019-11-27 03:14 | 2019-11-27 11:00 | 466 | 11kV | 3262 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 195927 DOLF : 5 Amp Excluded OMS 1706070 | November | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2019-11-27 | N | 466 | N | 8 | N | N | 1.1101 | 39.4971 | 2383.7734
[7 empty] | 4078 | 7937 | 1703406 | 2019-11-26 13:05 | 2019-11-27 12:10 | 1385.4833 | 11kV | 225483.7833 | 163 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ex S2400 Berowra Panel 18 CP3281 Bay Cooper Tripped Abnormal Switching: CP62158 Closed, AB340 Open See OMS 1703406 1706530 1706683 | November | 2019 | 2020Q2 | 2020 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2019-11-26 | Y | 1383.3361 | N | 7 | N | Y | 1.1101 | 39.4971 | 164776.8982
[7 empty] | 5108 | 18278 | 1706454 | 2019-11-27 11:00 | 2019-11-27 12:45 | 105 | 11kV | 1050 | 10 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 195930 A Phase DOLF : 10 Amp arrestor blown at sub 70421. dolfs also replaced at sub 70421. Excluded oms 1706454 | November | 2019 | 2020Q2 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2019-11-27 | N | 105 | N | 8 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 5214 | 19175 | 1706607 | 2019-11-27 13:09 | 2019-11-27 13:55 | 46.1333 | 11kV | 415.2 | 9 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 195934 Replace crossarm brace straps @ pole AK-61922 | November | 2019 | 2020Q2 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2019-11-27 | N | 46.1333 | N | 8 | N | N | 1.1101 | 39.4971 | 303.4159
[7 empty] | 4697 | 14081 | 1703336 | 2019-11-26 12:49 | 2019-11-27 14:05 | 1516 | 11kV | 2972364 | 2096 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2635 Epping - Pnl.58 tripped on: ABC O/C Tree branch on mains. See 1710242 1710243 | November | 2019 | 2020Q2 | 2020 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Veg | 2019-11-26 | Y | 1418.1126 | N | 7 | N | Y | 1.1101 | 39.4971 | 2172115.9413
[7 empty] | 4967 | 16803 | 1703851 | 2019-11-26 13:02 | 2019-11-27 14:08 | 1506 | 11kV | 95572 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC21799 Oxford Brooker tripped on: IOC and OC Tree on mains in multiple locations. S78681-1 interrupted to remove tree in conjunction See 1710359 1710363 1710364 | November | 2019 | 2020Q2 | 2020 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 1426.4478 | N | 7 | N | Y | 1.1101 | 39.4971 | 69841.1987
[7 empty] | 4039 | 7438 | 1706592 | 2019-11-27 12:52 | 2019-11-27 15:00 | 128 | 11kV | 512 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong Pa5 PT12926 - A phase HDO Operated Cause: Weather Related. See OMS 1709949 1706592 | November | 2019 | 2020Q2 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2019-11-27 | N | 128 | N | 8 | N | N | 1.1101 | 39.4971 | 374.1545
[7 empty] | 5210 | 19086 | 1704814 | 2019-11-26 15:36 | 2019-11-27 16:00 | 1464 | 11kV | 250344 | 171 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | S36190 Wyong Killarney - TX HV switch opened at SOp request due to customer receving shocks and EMOS didn't know how/ wasn't willing to open LV Dist fuse. Customer's service cut away. | November | 2019 | 2020Q2 | 2020 | ZN180:PA30 | ZN180:PA30 | ZN00180/000030 | MOSMAN | OH | Not Veg | 2019-11-26 | Y | 1464 | N | 7 | N | Y | 1.1101 | 39.4971 | 182944.0113
[7 empty] | 3781 | 4879 | 1703428 | 2019-11-26 12:53 | 2019-11-27 18:42 | 1789 | 11kV | 211267 | 119 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC61097 Wise Ferry Lavender 10.2 tripped on O/C Tree branch brought down OH mains near USL40442 See 1709967 1709968 | November | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-11-26 | Y | 1775.3529 | N | 7 | N | Y | 1.1101 | 39.4971 | 154387.6923
[7 empty] | 4360 | 10695 | 1703374 | 2019-11-26 12:59 | 2019-11-27 19:10 | 1811 | 11kV | 1088859 | 1729 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn9252 Jannali - Pnl.27 tripped, reclosed and tripped on: O/C Field EFIs: S63053, S9690, S9558, UGOH Box Rd Abnormal: Open bonds to PT9713 Ingrid Rd. Fault 1: Open bond adjacent LB35850 Fault 2: 5 bays of 11kV & 415 down near PT9713. See1709858 1709859 1709861 1709862 1709863 | November | 2019 | 2020Q2 | 2020 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2019-11-26 | Y | 629.7623 | N | 7 | N | Y | 1.1101 | 39.4971 | 795706.0413
[7 empty] | 5284 | 19721 | 1703999 | 2019-11-26 13:37 | 2019-11-27 23:15 | 2018 | 11kV | 30934 | 67 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC44994 Mangrove Creek - tripped on: O/C 27/11 2145 - LB46388 was interrupted to repair lightning arrestor at PT46387 Kyola Mangrove which caused HDO to blown during storm. Weather related See 1709978 1709979 1709981 1709982 | November | 2019 | 2020Q2 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2019-11-26 | Y | 461.7015 | N | 7 | N | Y | 1.1101 | 39.4971 | 22605.6548
[7 empty] | 4243 | 9699 | 1707005 | 2019-11-27 12:07 | 2019-11-28 00:40 | 753 | 11kV | 1860120 | 2620 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn15006 Dee WHy West Panel 9 Signals: 11Kv tri, Zone Earth Cause nopt ascertained for outage. Possible UG fault See OMS 1712642 1707005 1712644 1703240 1712643 | November | 2019 | 2020Q2 | 2020 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2019-11-27 | N | 709.9695 | N | 8 | N | N | 1.1101 | 39.4971 | 1359320.8317
[7 empty] | 4305 | 10262 | 1707277 | 2019-11-28 11:21 | 2019-11-28 13:05 | 104 | 11kV | 56264 | 541 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN874 CONCORD 11kV CB Panel 15 'Station George' fdr tripped Relays: EF, Zone Earth, Group Earth Signals: 11kv trip EFI: Nil Cause: UG Cable damaged by contractor Cantractor dug thorugh cable @ 39 george st, Concord. Cable from Zn874 Concord to S719 See 1707277 ex 1707350 | November | 2019 | 2020Q2 | 2020 | ZN874:PA15 | ZN874:PA15 | ZN00874/000015 | CANADA BAY | UG | Not Veg | 2019-11-28 | N | 104 | N | 3 | N | N | 1.1101 | 39.4971 | 41116.0717
[7 empty] | 3403 | 991 | 1703901 | 2019-11-26 17:35 | 2019-11-28 13:59 | 2664.15 | 11kV | 546150.75 | 205 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Major Storm | November | 2019 | 2020Q2 | 2020 | ZN3425:PA15 | ZN3425:PA15 | ZN03425/000015 | WILLOUGHBY | OH | Not Veg | 2019-11-26 | Y | 2664.15 | N | 7 | N | Y | 1.1101 | 39.4971 | 399110.8594
[7 empty] | 3536 | 2350 | 1707397 | 2019-11-28 14:00 | 2019-11-28 14:30 | 30 | 11kV | 360 | 12 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 195956 Broken tie on pole JQ-60003 repaired under emergency switching T0116. | November | 2019 | 2020Q2 | 2020 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2019-11-28 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 5002 | 17233 | 1703372 | 2019-11-26 12:57 | 2019-11-28 15:12 | 3015 | 11kV | 285357 | 751 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Wind Storm | Y | At S15005 Belrose Panel 10 tripped Signals: 11kV Trip Relays: OC, Earth fault, EFI, Fault Check Cause: Section of OH down on Gullyside of recloser247232 and 11kV Recloser CP24772 Damaged See OMS 1713723 1713726 1703372 | November | 2019 | 2020Q2 | 2020 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2019-11-26 | Y | 379.9694 | N | 7 | N | Y | 1.1101 | 39.4971 | 208530.479
[7 empty] | 3678 | 3705 | 1707621 | 2019-11-28 21:07 | 2019-11-28 21:50 | 43 | 11kV | 3397 | 79 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 195957 A Phase DOLF : 31 Amp POSSUM FOUND AT SUB POLE. B PROT FAULT FLAG OPERATED. Excluded OMS 1707621. CC1: 22-"Refer to SOp" | November | 2019 | 2020Q2 | 2020 | 270:83590 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Not Veg | 2019-11-28 | N | 43 | N | 3 | N | N | 1.1101 | 39.4971 | 2482.4274
[7 empty] | 4984 | 16986 | 1707855 | 2019-11-29 11:58 | 2019-11-29 15:00 | 182 | 11kV | 139708 | 1028 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1673 Turramurra - pnl.7 tripped on: Earth Fault, B phase O/C UG cable fault between S1673 to S727 to S49736 tee PT1059 See 1713425 1713426 1713427 | November | 2019 | 2020Q2 | 2020 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | UG | Not Veg | 2019-11-29 | N | 135.9027 | N | 5 | N | N | 1.1101 | 39.4971 | 102094.4857
[7 empty] | 4182 | 9216 | 1707873 | 2019-11-29 12:45 | 2019-11-29 18:00 | 315 | 11kV | 315 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 195976 11kV Mains on the ground, beyond Line Fuse 63833. No fuse operation, or SEF operation Excavator backed into tree bringing down HV Mains at pole - GS44564. Opened Line Fuses - 63833 and tested dead danger tag applied. Crew required for repairs | November | 2019 | 2020Q2 | 2020 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2019-11-29 | N | 315 | N | 5 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 3968 | 6627 | 1707968 | 2019-11-29 19:00 | 2019-11-29 19:30 | 30 | 11kV | 60 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 195977 Single Phase Fuse Temp replaced LV Fuses, bruce to arrange replacement to under slung fuse | November | 2019 | 2020Q2 | 2020 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2019-11-29 | N | 30 | N | 5 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 4366 | 10733 | 1708064 | 2019-11-29 20:43 | 2019-11-29 22:40 | 117 | 11kV | 253136 | 2295 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.1 tripped on: Pnl.1L Earth leakage Abnormal: S8482 Sw/B open DMA UG cable fault between S36061 Sw/B and S2684 Sw/A See 1709507 1709508 | November | 2019 | 2020Q2 | 2020 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2019-11-29 | N | 110.2989 | N | 5 | N | N | 1.1101 | 39.4971 | 184984.3226
[7 empty] | 4983 | 16983 | 1703339 | 2019-11-26 12:56 | 2019-11-30 08:20 | 5484 | 11kV | 547212 | 381 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S1193 Lindfield Panel 17 feeder tripped, reclosed tripped and locked out on Relays: B and C phase IOC, fault Check, Lockout and EFI. Cause: feeder patrolled by DOp and Hazards checked before closing See OMS 1711554 1711555 1711557 1703339 1706470 | November | 2019 | 2020Q2 | 2020 | ZN1193:PA17 | ZN1193:PA17 | ZN01193/000017 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 1436.252 | N | 7 | N | Y | 1.1101 | 39.4971 | 399886.3896
[7 empty] | 4283 | 10029 | 1704463 | 2019-11-26 12:55 | 2019-11-30 10:30 | 5615 | 11kV | 325670 | 58 | HV | Overload | Utility Process Issue | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At PT92 Coopernook Wellington supply lost to A B and C phase of distributior 1 and 2. PA 27 impacted see control room report see OMS 171181 1707247 Cause: Major Storm Cause: See OMS 1711716/720/721/722/723/724/725/726/727/728/729/730 1703365 1703429 1706481 1706828 1707812 1707813 /1708209 1708210 1708211 1708213 1708214 1708547 | November | 2019 | 2020Q2 | 2020 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 5615 | N | 7 | N | Y | 1.1101 | 39.4971 | 237990.0304
[7 empty] | 3494 | 1969 | 1703383 | 2019-11-26 12:58 | 2019-11-30 12:15 | 5717 | 11kV | 1715380 | 540 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Wind Storm | Y | iR49520 Keldie Brown - tripped & reclosed on: O/C Tree on 11kV mains near PT15338 and tree on CCT near iR49520 | November | 2019 | 2020Q2 | 2020 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 3176.6296 | N | 7 | N | Y | 1.1101 | 39.4971 | 1253549.1089
[7 empty] | 4578 | 12915 | 1704273 | 2019-11-26 13:21 | 2019-11-30 13:05 | 5743.8167 | 11kV | 470992.9667 | 82 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Storm | November | 2019 | 2020Q2 | 2020 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 5743.8167 | N | 7 | N | Y | 1.1101 | 39.4971 | 344187.7681
[7 empty] | 3743 | 4415 | 1707408 | 2019-11-26 12:51 | 2019-11-30 13:40 | 5809 | 11kV | 4241617 | 1706 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | AT S2400 Berowra Panel 22 feeder tripped , reclosed tripped and lockedout on Relays: B and C phase OC, Reclose Relay and timing relay See OMS 1712797 1712804 17128051712806 1712807 1712808 1712809 1712810 1712811 1712812 1712813 1712814 1712815 1712816 1712817 | November | 2019 | 2020Q2 | 2020 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2019-11-26 | Y | 2486.2937 | N | 7 | N | Y | 1.1101 | 39.4971 | 3099648.5971
[7 empty] | 4027 | 7278 | 1703527 | 2019-11-26 12:59 | 2019-11-30 13:45 | 5806 | 11kV | 624990 | 237 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC64824 Deepwater Holly - tripped HV and LV down between REC64824 and LB3103 tee S1720 Castle Cove Golf. A/P & CTW issued 30/11/19 @1100 See 1711547 1711548 | November | 2019 | 2020Q2 | 2020 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2019-11-26 | Y | 2637.0886 | N | 7 | N | Y | 1.1101 | 39.4971 | 456724.2579
[7 empty] | 4029 | 7324 | 1708328 | 2019-11-30 13:56 | 2019-11-30 15:10 | 74 | 11kV | 1480 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 195986 B phase 20 Amp Line DOLF Replaced HV fuse on spur line 10755. Restored at 1510pm 20amp fuse. Liaised with SO3 | November | 2019 | 2020Q2 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2019-11-30 | N | 74 | N | 6 | N | N | 1.1101 | 39.4971 | 1081.5403
[7 empty] | 4139 | 8577 | 1703270 | 2019-11-26 12:49 | 2019-11-30 15:20 | 5911 | 11kV | 680634 | 789 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.18 tripped on: A Phase IOC Abnormal: LB65298 closed with AB277 Open Tree brought down OH mains outside 25 Montview Rde, Hornsby Heights. HV into LV, customers checked by EMSO, refer to related records for details See 1710436 1710438 1710439 | November | 2019 | 2020Q2 | 2020 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2019-11-26 | Y | 862.654 | N | 7 | N | Y | 1.1101 | 39.4971 | 497387.2519
[7 empty] | 4687 | 13969 | 1708350 | 2019-11-30 14:47 | 2019-11-30 16:00 | 73 | 11kV | 365 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 195996 On call reattached LL clamp No Cause Found not storm conditions | November | 2019 | 2020Q2 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2019-11-30 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 266.7312
[7 empty] | 5106 | 18255 | 1708370 | 2019-11-30 15:38 | 2019-11-30 17:09 | 91 | 11kV | 101789 | 1233 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 196001 1 Fault operations, overcurrent Fdr reclose function non auto due to total fire ban. Full patrol, fdr went back in. | November | 2019 | 2020Q2 | 2020 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Veg | 2019-11-30 | N | 82.5539 | N | 6 | N | N | 1.1101 | 39.4971 | 74384.3989
[7 empty] | 3704 | 4007 | 1703386 | 2019-11-26 13:00 | 2019-11-30 17:52 | 6052 | 11kV | 3229904 | 1163 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | S15012 Killarney - Pnl.8 tripped on: C phase IOC Large tree on 11kV OH between S16846Sw/B to LB20560 to LB77298. Tree on mains @ 651 Warringah Rd. Multiple trees on mains and mains down on LV. See 1711502 1711505 1711506 1711507 1711508 1711509 1711510 | November | 2019 | 2020Q2 | 2020 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2019-11-26 | Y | 2777.2175 | N | 7 | N | Y | 1.1101 | 39.4971 | 2360318.5772
[7 empty] | 4903 | 15984 | 1703260 | 2019-11-26 12:45 | 2019-11-30 18:20 | 6095 | 11kV | 486351.1 | 744 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S35370 Galstonb Panel 8 tripped, reclosed tripped and locked out on B and C phase OC, Fault Check, Lockout and EFI Cause: Tree on OH near AB 1237 See OM S 1711492 1711496 1711497 1711498 1711499 1711500 1711503 1703260 1706284 1706683 1707193 1708502 1710537 | November | 2019 | 2020Q2 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-11-26 | Y | 653.6977 | N | 7 | N | Y | 1.1101 | 39.4971 | 355411.039
[7 empty] | 4475 | 11753 | 1703450 | 2019-11-26 13:01 | 2019-11-30 19:17 | 6136 | 11kV | 3953320 | 2010 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | Zn15011 Beacon Hill - Pnl.2 tripped on: B & C phase IOC Anormal: LB22843 Closed with USL 22935 Open Large tree on PT15164 Darmour Ave. Unable to isolate PT. See 1710369 1710370 1710372 1710373 | November | 2019 | 2020Q2 | 2020 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 1966.8259 | N | 7 | N | Y | 1.1101 | 39.4971 | 2888969.6528
[7 empty] | 3499 | 2026 | 1708391 | 2019-11-30 18:00 | 2019-11-30 19:30 | 90 | 11kV | 180 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 196002 A Phase Substation DOLF Replaced high voltage arrestor. Co-ordinated with control room. | November | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-11-30 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 4888 | 15828 | 1703034 | 2019-11-26 13:00 | 2019-11-30 19:40 | 6160 | 11kV | 359536 | 125 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ex S15013 Terrey Hills CP21350 Booralie Kulgoa Tripped on OC Cause: OH Storm Related Trees down beyond CP26216 See OMS 1711340 1711341 1711344 1711345 1708425 1706884 1706727 1706726 1703034 1703029 | November | 2019 | 2020Q2 | 2020 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 2876.288 | N | 7 | N | Y | 1.1101 | 39.4971 | 262738.3043
[7 empty] | 4887 | 15826 | 1703495 | 2019-11-26 13:08 | 2019-11-30 20:17 | 6189.0167 | 11kV | 683429.9 | 114 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn15013 Terrey Hills Panel 6 from recloser CP20828 Tripped on OC Cause: Trees down on OH beyond CP28211 See OMS 1703495 1708250 1708476 | November | 2019 | 2020Q2 | 2020 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 5994.9991 | N | 7 | N | Y | 1.1101 | 39.4971 | 499430.4132
[7 empty] | 5206 | 19010 | 1708467 | 2019-11-30 19:31 | 2019-11-30 21:00 | 89 | 11kV | 267 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 196004 Replaced blown 10A, A phase DOLF on PT Sub 5058. Supply restored 2100 hrs. | November | 2019 | 2020Q2 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2019-11-30 | N | 89 | N | 6 | N | N | 1.1101 | 39.4971 | 195.1157
[7 empty] | 4497 | 12021 | 1708454 | 2019-11-30 18:51 | 2019-11-30 23:06 | 254.6 | 11kV | 51121.5167 | 203 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 196006 A, B and C Phase Electrical Storm 11kV interrupted for saFety as 33kV 720 feeder was down in vicintiy see LID 196000 LVF 15093 Vidor Eng sub also interrupted | November | 2019 | 2020Q2 | 2020 | 204:82691 | 204:82691 | ZN00204/082691 | NEWCASTLE | OH | Not Veg | 2019-11-30 | N | 251.8301 | N | 6 | N | N | 1.1101 | 39.4971 | 37358.0966
[7 empty] | 4558 | 12676 | 1708511 | 2019-12-01 05:06 | 2019-12-01 08:48 | 222 | 11kV | 229852 | 1212 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn12690 berkeley Vale - Pnl.19 tripped on: IOC Cause not ascertained See 1709916 1709917 1709919 1709920 | December | 2019 | 2020Q2 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2019-12-01 | N | 189.6469 | N | 5 | N | N | 1.1101 | 39.4971 | 167969.0621
[7 empty] | 4532 | 12328 | 1708524 | 2019-12-01 07:25 | 2019-12-01 10:49 | 204 | 11kV | 115709 | 773 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12690 Berkeley vale - Pnl.26 tripped on: SEL 26R Abnormal: LB40053 Closed with open bonds below LB77831 Bond burnt off above AB41094 See 1709925 1709927 | December | 2019 | 2020Q2 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2019-12-01 | N | 149.6882 | N | 5 | N | N | 1.1101 | 39.4971 | 84556.7244
[7 empty] | 4534 | 12365 | 1703690 | 2019-11-26 14:31 | 2019-12-01 12:20 | 7069 | 11kV | 721038 | 102 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | At S16533 Belrose Aux No2 - Supply lost to distributors Based on customer calls - assumed distributor 1 and 2 were impaced (distributor 3 nil customers) Switching Tag Lef on Dist #1 (Suspect Cable fault on Dist #1 Prince Charles Rd only B Phase Coming out). LV// 25783. Closed. All other dists Healthy. CC1: 12-"Urgent refer to mains" | November | 2019 | 2020Q2 | 2020 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | UG | Not Veg | 2019-11-26 | Y | 7069 | N | 7 | N | Y | 1.1101 | 39.4971 | 526913.3034
[7 empty] | 4057 | 7656 | 1704063 | 2019-11-26 12:57 | 2019-12-01 14:10 | 7273 | 11kV | 6947983 | 1486 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3425 Castle Cove - Pnl.30 - tripped on: C phase IOC and OC Storm - 11kV restored first with Sub Tx links opened then LV patrolled/repaired and restored after See 1711797 1711799 1711801 1711802 1711803 1711804 1711805 1711806 1711807 1711808 1711809 1711810 1711811 1711812 1711813 1711814 1711815 | November | 2019 | 2020Q2 | 2020 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | WILLOUGHBY | OH | Not Veg | 2019-11-26 | Y | 4675.6279 | N | 7 | N | Y | 1.1101 | 39.4971 | 5077381.0456
[7 empty] | 4034 | 7388 | 1708637 | 2019-12-01 14:18 | 2019-12-01 16:00 | 102 | 11kV | 204 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196010 10 Amp substation DOLF | December | 2019 | 2020Q2 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2019-12-01 | N | 102 | N | 5 | N | N | 1.1101 | 39.4971 | 149.0772
[7 empty] | 4154 | 8808 | 1708667 | 2019-12-01 15:50 | 2019-12-01 17:30 | 100 | 11kV | 300 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 196013 Power on at 1730hrs, one 10A DOLF replaced at single phase sub, no cause provided. Matt from Despatch called and relocated job from the Singleton queue to the Control queue. PD | December | 2019 | 2020Q2 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2019-12-01 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 4523 | 12244 | 1703842 | 2019-11-26 13:26 | 2019-12-01 17:39 | 7453 | 11kV | 499351 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Full distributor out, multiple customers affected. Will require Tree trimmers to remove multiple branches on LV mains Treedown on Mains, pole snapped at base Pole and mains to be replaced large tree to be removed 4 BAYS down, from PY58900-PY58886 Note: Distributor fuses found pulled not live. Pole has been down for days blocking the street, customers cant drive out, they understand delay issues but if possible request linesman to cut away distributor pole to allow vehicular access, pole is at 45degrees across street, thanks. | November | 2019 | 2020Q2 | 2020 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Veg | 2019-11-26 | Y | 7453 | N | 7 | N | Y | 1.1101 | 39.4971 | 364910.9824
[7 empty] | 3894 | 5885 | 1703106 | 2019-11-26 13:00 | 2019-12-01 18:40 | 7540 | 11kV | 1110192 | 1983 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ATt Zn15005 Belrose Panel 2 tripped on] Signals: 11kV Trip relays: Earth Fault Cause: Section of 11kV feeder from LB77809 to LB24825 to LB20287 - Tree on OH mains See P<S 1713694 17134706 1713707 1713708 1713709 1703106 1705938 1706108 1706835 | November | 2019 | 2020Q2 | 2020 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Veg | 2019-11-26 | Y | 559.8548 | N | 7 | N | Y | 1.1101 | 39.4971 | 811295.5685
[7 empty] | 5152 | 18616 | 1712631 | 2019-11-26 12:57 | 2019-12-01 19:45 | 7608 | 11kV | 2528831 | 1522 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S1193 Lindfield Panel 26 tripped and locked out on Relays: B and C phase IOC, Fault Check and EFI Cause: PT25 Isolated - wires down | November | 2019 | 2020Q2 | 2020 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2019-11-26 | Y | 1661.5184 | N | 7 | N | Y | 1.1101 | 39.4971 | 1847995.1069
[7 empty] | 4343 | 10539 | 1703396 | 2019-11-26 13:02 | 2019-12-02 01:30 | 7948 | 11kV | 4295289 | 1237 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S15005 Belrose Panel 4 tripped on Signals: 11kV trip Relays: SEF, Fault Check and EFI See OM S1713626 /29/30/31/32/33/34/35/36/37/38/77/78 Cause: Tree branch on OH mains - Major Stiorm | November | 2019 | 2020Q2 | 2020 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2019-11-26 | Y | 3472.3436 | N | 7 | N | Y | 1.1101 | 39.4971 | 3138870.5116
[7 empty] | 3617 | 2977 | 1703324 | 2019-11-26 12:53 | 2019-12-02 07:52 | 8339 | 11kV | 151442 | 196 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | REC420 Reynolds Crosslands - tripped on: O/C Tree on mains outside 75 Crosslands Rd, Galston PT1851 - Dist #1 - B & C phase fuses found blown See 1710420 1710422 1710425 | November | 2019 | 2020Q2 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-11-26 | Y | 772.6633 | N | 7 | N | Y | 1.1101 | 39.4971 | 110669.3468
[7 empty] | 4249 | 9768 | 1708805 | 2019-12-02 08:30 | 2019-12-02 09:00 | 30 | 11kV | 90 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 196016 C Phase Broken LLC | December | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-12-02 | N | 30 | N | 8 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 4565 | 12778 | 1703367 | 2019-11-26 12:56 | 2019-12-02 11:25 | 8549.4 | 11kV | 4792018.3333 | 1141 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3425 Castle Cove - Pnl.12 tripped on: A & B phase IOC Various trees on mains and wires down along 11kV and LV See 1711531 1711532 1711533 1711535 1711536 1711537 1711538 1711539 1711543 | November | 2019 | 2020Q2 | 2020 | ZN3425:PA12 | ZN3425:PA12 | ZN03425/000012 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 4199.8408 | N | 7 | N | Y | 1.1101 | 39.4971 | 3501865.6574
[7 empty] | 4616 | 13367 | 1708844 | 2019-12-02 08:18 | 2019-12-02 12:00 | 222 | 11kV | 888 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 196018 A Phase Burnt off lug on A Phase LV TX tail | December | 2019 | 2020Q2 | 2020 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2019-12-02 | N | 222 | N | 8 | N | N | 1.1101 | 39.4971 | 648.9242
[7 empty] | 3309 | 196 | 1708852 | 2019-12-02 11:44 | 2019-12-02 13:20 | 96 | 11kV | 384 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Wind Strong | N | LID 196020 10 Amp C Phase substation DOLF C Phase LA replaced | December | 2019 | 2020Q2 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2019-12-02 | N | 96 | N | 8 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 3851 | 5520 | 1703468 | 2019-11-26 12:59 | 2019-12-02 13:50 | 8691 | 11kV | 3193292.1667 | 859 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | AT S1193 Lindfield Panel 16 Tripped, reclosed tripped, reclosed tripped and locked out on Relays: A and B phhase OC, Fault checke and lockout and EFI. 1712014/015/016/017/018/019/020/021/022/054 1703468/6220/6302/7477/7700/7711/7750/8127/8252/9005 | November | 2019 | 2020Q2 | 2020 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 3717.453 | N | 7 | N | Y | 1.1101 | 39.4971 | 2333563.7292
[7 empty] | 4473 | 11732 | 1703346 | 2019-11-26 16:22 | 2019-12-02 16:30 | 8648 | 11kV | 1580766 | 597 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ex Z3154 St Ives Recloser CP1622 Eastern Arterial tripped on OC Cause: Section of 11kV feeder OOS for NAR48870 and 45668 DOp advised that PT1625 LV distributor2 was cut away and made safet See OMS 1710388 1710394 1710398 1710401 1710402 1710403 1710404 1710405 1710406 1708773/749/735/891/890/889/867/866/865/615/546/912/346 | November | 2019 | 2020Q2 | 2020 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 2647.8492 | N | 7 | N | Y | 1.1101 | 39.4971 | 1155177.1681
[7 empty] | 4165 | 9046 | 1707357 | 2019-11-29 22:21 | 2019-12-02 16:32 | 3971 | 11kV | 199587 | 1091 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn4545 Meadowbanks Panel 25 Tripped Cause: A phase OC , Fault Check and EFI Cause: Kids letting off fireworks have come into contact with PT1479 Consitution Mns causing flash over. Section of feedewr from SW C at CP337 Meadowbank Park to SW @ at S35736 is isolated. Distributor 1 @ PT1479 is Isolated due to HV into LV See OMS 1710210 17102136 1710214 | November | 2019 | 2020Q2 | 2020 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Not Veg | 2019-11-29 | N | 182.9395 | N | 5 | N | N | 1.1101 | 39.4971 | 145852.2928
[7 empty] | 4630 | 13506 | 1703294 | 2019-11-26 12:58 | 2019-12-02 16:40 | 8862 | 11kV | 1814543 | 699 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn195 Pymble - Pnl.22 tripped on: O/C & E/F Tree branch brought down 11kV mains and multiple LV mains along feeder. Abnormal switching: S2542 Closed with S373478 Open (Pnl. 9 interruptions captured under Pnl.9 OMS event) See 1712585 1712587 1712588 1712589 1712590 1712591 | November | 2019 | 2020Q2 | 2020 | ZN195:PA22 | ZN195:PA10 | ZN00195/000010 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 2595.9127 | N | 7 | N | Y | 1.1101 | 39.4971 | 1326014.5044
[7 empty] | 3703 | 3992 | 1709212 | 2019-12-02 16:01 | 2019-12-02 16:50 | 49.2833 | 11kV | 8181.0333 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14144 Wamberal CP44946 Kunarra Rd tripped, reclosed, tripped and locked out on Relays: OC trip and lockout Cause: Tree branch on OH mains See OMS 1709212 1709218 1709219 1709227 1709238 | December | 2019 | 2020Q2 | 2020 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2019-12-02 | N | 49.2833 | N | 8 | N | N | 1.1101 | 39.4971 | 5978.4579
[7 empty] | 4675 | 13873 | 1708795 | 2019-12-01 23:16 | 2019-12-02 17:23 | 1087 | 11kV | 90014 | 461 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.44 tripped on: B & C phase O/C Field EFIs: S49499 Tree on mains between LB2752 to LB78032 tee PT1693 See 1710030 1710031 1710033 | December | 2019 | 2020Q2 | 2020 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Veg | 2019-12-01 | N | 195.2581 | N | 5 | N | N | 1.1101 | 39.4971 | 65779.5762
[7 empty] | 4515 | 12199 | 1709119 | 2019-12-02 14:49 | 2019-12-02 17:27 | 158 | 11kV | 346902 | 2633 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn847 Hornsby - Pnl.21 tripped on: A Phase IOC, C phase OC (relays not reset from previous trip and reclose) Abnormal: LB321 Closed with AB694 Open Defective Burnt tree branch on mains found near LB331 and also AB739 See 1711370 1711371 1711372 | December | 2019 | 2020Q2 | 2020 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2019-12-02 | N | 131.7516 | N | 8 | N | N | 1.1101 | 39.4971 | 253505.7497
[7 empty] | 4790 | 14920 | 1709254 | 2019-12-02 16:01 | 2019-12-02 17:28 | 87 | 11kV | 78648 | 904 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | AT S3154 St Ives Panel 12 tripped, reclosed tripped and locked out on Signals: 11kV trip Relays: A phase IOC, A phase timed, lockout and Timing Abnormal Switching: CP63181 is closed, CP63174 is open Cause: tree branch on OH conductor adjacent to LB64868 See OMS 1710638 1709216 1709224 1709236 1709254 | December | 2019 | 2020Q2 | 2020 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2019-12-02 | N | 87 | N | 8 | N | N | 1.1101 | 39.4971 | 57473.6387
[7 empty] | 4745 | 14459 | 1703304 | 2019-11-26 12:52 | 2019-12-02 19:42 | 9050 | 11kV | 2284791 | 929 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.47 tripped on: A phase O/C Storm PT61557 - Dist #1 - C phase fuse blown S7305 - Dist #2 - A, & B Phase fuses blown PT1803 - Dist #1 - A, B & Cphase fuses blown See 1710391 1710393 1710395 1710396 LV 1710397 1710399 1710400 | November | 2019 | 2020Q2 | 2020 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2019-11-26 | Y | 2459.409 | N | 7 | N | Y | 1.1101 | 39.4971 | 1669657.8729
[7 empty] | 4853 | 15559 | 1703429 | 2019-11-26 12:55 | 2019-12-02 19:58 | 9063 | 11kV | 5153065 | 1135 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S1193 Lindfield Panel 27 Tryon Slade tripped, reclosed, tripped and locked out on Relays: B and C phase OC, A phase IOC, Fault Check and EFI Cause: Major Storm Cause: See OMS 1711716/720/721/722/723/724/725/726/727/728/729/730 1703365 1703429 1706481 1706828 1707812 1707813 /1708209 1708210 1708211 1708213 1708214 1708547 | November | 2019 | 2020Q2 | 2020 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2019-11-26 | Y | 4540.1454 | N | 7 | N | Y | 1.1101 | 39.4971 | 3765707.9123
[7 empty] | 3718 | 4088 | 1709203 | 2019-12-02 16:03 | 2019-12-02 23:50 | 467 | 11kV | 38549 | 184 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 196026 Pole Mounted RAGCB Overcurrent Cause of Fault, 11kV main of B phase insulator at pole IQ-12715 | December | 2019 | 2020Q2 | 2020 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2019-12-02 | N | 209.5054 | N | 8 | N | N | 1.1101 | 39.4971 | 28170.4722
[7 empty] | 4208 | 9360 | 1709366 | 2019-12-02 20:29 | 2019-12-03 00:22 | 233 | 11kV | 5126 | 22 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 196029 Single Phase Tapping broken off at DOLF | December | 2019 | 2020Q2 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2019-12-02 | N | 233 | N | 8 | N | N | 1.1101 | 39.4971 | 3745.9296
[7 empty] | 4433 | 11322 | 1709463 | 2019-12-03 09:55 | 2019-12-03 12:37 | 162 | 11kV | 162 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 196037 A Phase 10 Amp, substation DOLF | December | 2019 | 2020Q2 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2019-12-03 | N | 162 | N | 5 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 4055 | 7625 | 1709898 | 2019-12-03 13:27 | 2019-12-03 15:40 | 133 | 11kV | 133 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196054 Single Phase 10Amp fuse substation DOLF | December | 2019 | 2020Q2 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2019-12-03 | N | 133 | N | 5 | N | N | 1.1101 | 39.4971 | 97.1925
[7 empty] | 5338 | 20289 | 1703513 | 2019-11-26 12:59 | 2019-12-03 17:00 | 10321 | 11kV | 6971427 | 1271 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn15005 Belrose Panel 6 tripped Cause: Section of 111kV isolated from panel 6 @ Belorse to S16965 - OH down Additional Major storm damage across belrose panel 6 See OMS 1713521/522/523/524/526/29/32/34/35/37/40/42/43/44/47/48/59/50/51 | November | 2019 | 2020Q2 | 2020 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2019-11-26 | Y | 5484.9937 | N | 7 | N | Y | 1.1101 | 39.4971 | 5094513.2293
[7 empty] | 4501 | 12082 | 1709596 | 2019-12-03 16:35 | 2019-12-03 18:00 | 85 | 11kV | 12835 | 151 | HV | 3rd Party Vehicle | 3rd Party Impact | Stay Wire | Unplanned | No Weather Impact | N | LID 196056 Car hit stay wire on pole HR-72410. Section isolated for safety CONSTABLE SENIOR BAILEY CESSNOCK POLICE Car has gone through the earthing pointcausing bushfire. Bush fire out pole check required.On leggets drive Pole number 72401. Driver of vehicle is deceased, road is blocked off, police advised will be delayed access probably for another hour. | December | 2019 | 2020Q2 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2019-12-03 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 9379.4394
[7 empty] | 3652 | 3393 | 1709653 | 2019-12-03 15:00 | 2019-12-03 18:45 | 225 | 11kV | 1125 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 196052 A phase 16 Amp Line DOLF mains down pole 4k-40025 section isolated for repair | December | 2019 | 2020Q2 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2019-12-03 | N | 225 | N | 5 | N | N | 1.1101 | 39.4971 | 822.1168
[7 empty] | 3515 | 2178 | 1709786 | 2019-12-04 02:23 | 2019-12-04 04:12 | 109 | 11kV | 97664 | 896 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196060 1 fault operation A & B Phase Instantaneous Overcurrent Please patrol | December | 2019 | 2020Q2 | 2020 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2019-12-04 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 71369.9706
[7 empty] | 3610 | 2869 | 1709782 | 2019-12-04 01:17 | 2019-12-04 07:30 | 373 | 11kV | 21261 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 196061 C Phase DOLF : 31 Amp Excluded OMS 1709785 | December | 2019 | 2020Q2 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2019-12-04 | N | 373 | N | 7 | N | N | 1.1101 | 39.4971 | 15536.9117
[7 empty] | 4714 | 14239 | 1709731 | 2019-12-03 18:16 | 2019-12-04 14:41 | 1225 | 11kV | 7350 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12660 WOY WOY section of 11kV Panel 14 RE45093 Wondabyne has tripped Relays: Overcurrent Trip and Lockout Cause: Tree/Branch brought down HV OH. LK40638 CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | December | 2019 | 2020Q2 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2019-12-03 | N | 1225 | N | 5 | N | N | 1.1101 | 39.4971 | 5371.1632
[7 empty] | 4393 | 10959 | 1709841 | 2019-12-04 14:15 | 2019-12-04 15:12 | 57 | 11kV | 1083 | 19 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 196076 Repair broken stay wire at sub 70554. Excluded OMS No. 1709841, 1710009 | December | 2019 | 2020Q2 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2019-12-04 | N | 57 | N | 7 | N | N | 1.1101 | 39.4971 | 791.4245
[7 empty] | 4601 | 13195 | 1710032 | 2019-12-04 15:07 | 2019-12-04 16:11 | 64 | 11kV | 106048 | 1657 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12580 ERINA 11kV CB Panel 10 'S13682 Erina High Ernest' tripped on: Relays C Phase OC Signals: 11kv trip EFI: Nil Cause: tree/branch on OH Mains below S14225 Christle Sun Valley See 1710032 Ex 1710040,4,7,8,55,62 | December | 2019 | 2020Q2 | 2020 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2019-12-04 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 77496.7505
[7 empty] | 4401 | 11058 | 1710096 | 2019-12-04 18:13 | 2019-12-04 19:20 | 67 | 11kV | 73058 | 1165 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn4545 Meadowbanks Panel 41 tripped on Relays: Earth Fault with Fault Check Signals: 11kV Trip, TX3 Group and Zone Earth Cause: Cable fault between S35110 - S8530 - S7890 See OMS 1711015 1711016 1711017 1710096 | December | 2019 | 2020Q2 | 2020 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | UG | Not Veg | 2019-12-04 | N | 62.7107 | N | 7 | N | N | 1.1101 | 39.4971 | 53388.6316
[7 empty] | 4647 | 13586 | 1710109 | 2019-12-04 18:34 | 2019-12-04 19:24 | 50 | 11kV | 20550 | 411 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Ex Pa8 Galston -HR connection on footpath phase Note: Fire Start event - Arcing joint on Hv air break caused damage. Assist DOP to switch and take out of service. POLE ALIGHT CAUSING GRASS FIRES See OMS1711024 1710128 1710126 1710125 1710122 1710121 1710120 1710115 1710116 1710114 1710113 1710112 1710111 1710110 1710109 1710108 1710106 | December | 2019 | 2020Q2 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2019-12-04 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 15017.3339
[7 empty] | 4307 | 10291 | 1709910 | 2019-12-04 11:22 | 2019-12-04 21:30 | 608 | 11kV | 28712 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 12 RE45015 Brush Creek tripped, reclosed and locked out on: Relays: IOC & Locked out EFI: Nil Cause: tree branch contact - HV into LV PT 11492 Tree on mains, section of 11kv mains from LB40081 to AB40934 tee PT11492, PT11841 isolated to make repairs See 1710447 ex 1709910,10448,9 | December | 2019 | 2020Q2 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2019-12-04 | N | 522.0364 | N | 7 | N | N | 1.1101 | 39.4971 | 20981.8827
[7 empty] | 4056 | 7653 | 1710156 | 2019-12-05 05:39 | 2019-12-05 07:40 | 121 | 11kV | 85605 | 933 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Sub14892 Charmhaven Panel No.1 opened on: O/C & earth fault, efi, fault check efi fault check Abnormal: Panel No.1 Non Auto on reclose for bush fire Remarks: cause not ascertained. NB S79680 was commissioned 4/11 was not on Dops IPAD as yet. 11kv fault in section of feeder from S79680 sw/B to S65768 sw/A. S79680 commisioned last evening | December | 2019 | 2020Q2 | 2020 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | OH | Veg | 2019-12-05 | N | 91.7524 | N | 11 | N | N | 1.1101 | 39.4971 | 62557.6091
[7 empty] | 3830 | 5367 | 1710168 | 2019-12-05 06:52 | 2019-12-05 07:50 | 58 | 11kV | 47328 | 816 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN342 Paddington 11kv feeder Panel No.35 "Clement Waratah etc" tripped on: Relays: C phase O/C, EFI Field EFI's: Nil Remarks: UG fault. 11kv feeder fault in section from ZN342 Paddington Panel No.35 to S1681 New South Rushcutters (Sw/F) to S4371 Clement Waratah (Sw/A) | December | 2019 | 2020Q2 | 2020 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2019-12-05 | N | 58 | N | 11 | N | N | 1.1101 | 39.4971 | 34585.9065
[7 empty] | 4304 | 10256 | 1710155 | 2019-12-05 05:28 | 2019-12-05 11:05 | 337 | 11kV | 319882 | 1236 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15005 Belrose - Pnl.4 tripped on: B PHase O/C Abnormal: REC21801 non auto reclose due to fire ban @ 0746 - Pnl.6 tripped on SEL Dead bird found on ground at 115 Prahran Ave. Bond damaged near AB21076 (Pole FF31529) Bond off ajd UGOH near LB24314 Major damage along feeder from recent storm See 1712719 1712720 | December | 2019 | 2020Q2 | 2020 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2019-12-05 | N | 258.8042 | N | 11 | N | N | 1.1101 | 39.4971 | 233760.3307
[7 empty] | 3480 | 1834 | 1710353 | 2019-12-05 13:13 | 2019-12-05 14:30 | 77 | 11kV | 20039 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn129 Hunters Hill - Ex Pnl.64 section of 11kV feeder from AB1560 to LB3240 to S8020 isolated to remove tree branch from mains PT335 Monash Thompson - dist #3 - also interrupted See 1712057 1712058 | December | 2019 | 2020Q2 | 2020 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2019-12-05 | N | 71.8244 | N | 11 | N | N | 1.1101 | 39.4971 | 14643.9101
[7 empty] | 5208 | 19076 | 1710202 | 2019-12-05 12:30 | 2019-12-05 17:10 | 280 | 11kV | 23520 | 84 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | LID 196097 interrupt to repair damaged kiosk - replace LV board Excluded oms 1710202 | December | 2019 | 2020Q2 | 2020 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | UG | Not Veg | 2019-12-05 | N | 280 | N | 11 | N | N | 1.1101 | 39.4971 | 17187.7223
[7 empty] | 3580 | 2685 | 1710444 | 2019-12-05 17:30 | 2019-12-05 19:15 | 105 | 11kV | 7980 | 76 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT2448 Bonefin Rd No.53 interrupted for safety to remove tree from mains. | December | 2019 | 2020Q2 | 2020 | ZN129:PA39 | ZN129:PA39 | ZN00129/000039 | HUNTERS HILL | OH | Veg | 2019-12-05 | N | 105 | N | 11 | N | N | 1.1101 | 39.4971 | 5831.5486
[7 empty] | 4961 | 16747 | 1710523 | 2019-12-05 19:45 | 2019-12-05 20:48 | 63 | 11kV | 16293 | 411 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn5868 Gore Hill - Pnl.10 tripped on: Earth fault Abnormal: S3809 Sw/B closed with Sw/A open UG cable fault between S8964 Sw/B and S1402 Sw/A See 1712072 1712073 | December | 2019 | 2020Q2 | 2020 | ZN5868:PA10 | ZN5868:PA10 | ZN05868/000010 | WILLOUGHBY | UG | Not Veg | 2019-12-05 | N | 39.6423 | N | 11 | N | N | 1.1101 | 39.4971 | 11906.4438
[7 empty] | 4409 | 11152 | 1710529 | 2019-12-05 20:14 | 2019-12-05 23:07 | 173 | 11kV | 15532 | 332 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196101 & 196102 4 Fault Operations Overcurrent OMS 1710529 & 1710531 Sw 82580 Brandy Hill. Trip/Close /Trip Possibly 4 ops Sw 43101 Clarence Town Rd. RAGCB T/C/T. Possibly 1 op only? Not sure if reclosed properly. refer to LID # 196102 | December | 2019 | 2020Q2 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2019-12-05 | N | 46.7831 | N | 11 | N | N | 1.1101 | 39.4971 | 11350.3275
[7 empty] | 4978 | 16907 | 1710542 | 2019-12-05 23:16 | 2019-12-06 00:33 | 77 | 11kV | 59936 | 838 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.33 tripped, reclosed and tripped on: Earth Fault UG cable fault between S7816 and S7814 See 1712076 1712075 | December | 2019 | 2020Q2 | 2020 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | UG | Not Veg | 2019-12-05 | N | 71.5227 | N | 11 | N | N | 1.1101 | 39.4971 | 43799.461
[7 empty] | 4756 | 14534 | 1710560 | 2019-12-06 07:07 | 2019-12-06 09:14 | 127 | 11kV | 287189 | 2317 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12600 Lisarow Panel 11 "Wyoming" feeder tripped on: overcurrent only Abnormal: LB44430 opeb LB77492 closed (panel 3) Remarks: bird on 11kv near tee off to PT12985 sheet 3 B9 | December | 2019 | 2020Q2 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2019-12-06 | N | 123.9486 | N | 7 | N | N | 1.1101 | 39.4971 | 209869.2506
[7 empty] | 4489 | 11891 | 1710537 | 2019-12-05 21:37 | 2019-12-06 11:34 | 837 | 11kV | 9207 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | PT1752 Quarry Eloura Rserve - Roadside phase HDO operated Cause not ascertained | December | 2019 | 2020Q2 | 2020 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2019-12-05 | N | 837 | N | 11 | N | N | 1.1101 | 39.4971 | 6728.204
[7 empty] | 4651 | 13624 | 1710575 | 2019-12-06 10:25 | 2019-12-06 14:25 | 240 | 11kV | 27120 | 113 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S12600 Lisarow ex Panel 3 "S12399 Lisarow High Taylor" section of 11kv feeder from LB42056 to LB44024 to USL41622 tee to PT12985 Angus Dougall. De-energised to allow emergency repairs Remarks: interrupted for isolation for emergency repairs | December | 2019 | 2020Q2 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2019-12-06 | N | 240 | N | 7 | N | N | 1.1101 | 39.4971 | 19818.4961
[7 empty] | 3768 | 4764 | 1710705 | 2019-12-06 08:38 | 2019-12-06 14:40 | 362 | 11kV | 19548 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 196119 A Phase DOLF : 40 Amp Excluded OMS 1710705 | December | 2019 | 2020Q2 | 2020 | 513:83497 | 513:83497 | ZN00513/083497 | SINGLETON | OH | Veg | 2019-12-06 | N | 362 | N | 7 | N | N | 1.1101 | 39.4971 | 14285.1018
[7 empty] | 4327 | 10430 | 1710610 | 2019-12-06 15:50 | 2019-12-06 16:45 | 55 | 11kV | 13035 | 257 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S12600 Lisarow ex Panel 3 "S12399 Lisarow High Taylor" section of 11kv feeder is isolated from LB47774 to AB44430 tee to S14378 Pierce Northview to Pt47773 Newling Parsons. To allow emergency repairs. Abnormal: AB44327 is open and defective. LV in // between PT47773, S14378 and S12859 Remarks: bird on 11kv near tee off to PT12985 sht 3 B9 Lisarow | December | 2019 | 2020Q2 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2019-12-06 | N | 50.7198 | N | 7 | N | N | 1.1101 | 39.4971 | 9525.5935
[7 empty] | 4874 | 15736 | 1711040 | 2019-12-06 21:34 | 2019-12-06 22:45 | 71 | 11kV | 1420 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 11kv roadside 31.5A HDO operated at PT14619 Davistown Coomal Section of 11kv Panel 40 'Davistown' feeder at ZN12570 Avoca Remarks: cause not ascertained | December | 2019 | 2020Q2 | 2020 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2019-12-06 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 1037.6941
[7 empty] | 4980 | 16927 | 1712567 | 2019-12-07 03:59 | 2019-12-07 05:49 | 110 | 11kV | 140643 | 1287 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN12570 Avoca, 11kv Panel No.26 'Avoca Aux No.11" feeder tripped Relays: 'B' phase O/C, efi Signals: trip Remarks: UG fault. | December | 2019 | 2020Q2 | 2020 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | UG | Not Veg | 2019-12-07 | N | 109.2797 | N | 7 | N | N | 1.1101 | 39.4971 | 102777.7561
[7 empty] | 4504 | 12096 | 1711072 | 2019-12-07 08:45 | 2019-12-07 08:55 | 10 | 11kV | 360 | 36 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kv feeder from S.65159 bellevue Bakali No.2 Sw/B to LK44641 tee PT1815 4 Bellvue Bakali tee PT14389 Kyte Bellvue interrupted for safety, to remove a possum Remarks: possum on LK42048, 11kv interrupted to remove safely | December | 2019 | 2020Q2 | 2020 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2019-12-07 | N | 10 | N | 7 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 4028 | 7316 | 1710737 | 2019-12-06 15:50 | 2019-12-07 11:58 | 1208 | 11kV | 119502 | 99 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 196122 OHM down between poles 9T-50058 & 9T-50057. J Frazer patrolled the line prior to restoring supply. Excluded OMS 1710737, 1710745, 1710750, 1710743, 1710748. | December | 2019 | 2020Q2 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-12-06 | N | 1207.0909 | N | 7 | N | N | 1.1101 | 39.4971 | 87328.5369
[7 empty] | 5272 | 19610 | 1710525 | 2019-12-05 19:58 | 2019-12-07 13:10 | 2472 | 11kV | 115704 | 71 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Hot >35C | N | At S12630 Peats Ridge, Ex 11kv Panel 3 "Mangrove Mountain", recloser 49206 Mangrove MTN West has tripped on overcurrent Remarks: Bushfire has brought down wires beyond AB43940. Beyond USL42143 interrupted to remake 11kv bonds 1030 on 07/12/19 | December | 2019 | 2020Q2 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2019-12-05 | N | 1629.6338 | N | 11 | N | N | 1.1101 | 39.4971 | 84553.0705
[7 empty] | 4278 | 10004 | 1710527 | 2019-12-06 04:51 | 2019-12-07 16:45 | 2154 | 11kV | 34950 | 45 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196113 1 fault operation 3 phase Earth Fault Recloser 42089 tripped before fuse saver 41292 operated. wires on the ground at CV-23663. Tree branch has bought wires down to ground. RFS crews in area. Active fires in area but currently access to site. Excluded oms 1710549. | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-12-06 | N | 776.6667 | N | 7 | N | N | 1.1101 | 39.4971 | 25540.4291
[7 empty] | 4802 | 15066 | 1711047 | 2019-12-07 03:34 | 2019-12-07 16:58 | 804 | 11kV | 15569 | 29 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | iR44316 Wisemans Ferry tripped on: OC Bushfire damaged section of feeder from USL43964 to LB45074 tee PT18717 Note: Wisemans Ferry road is closed at Mill Crk due to fire. Patches of heavy smoke. Pole # MR 10 is 2 bays from PT 18717 and 4 bays from ferry. Access may be accessible from Wisemans Ferry- if ferry is operating. Unsafe to procede alone See 1713887 1713888 1713889 | December | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-12-07 | N | 536.8621 | N | 7 | N | N | 1.1101 | 39.4971 | 11377.366
[7 empty] | 3664 | 3562 | 1711154 | 2019-12-07 17:44 | 2019-12-07 18:36 | 52 | 11kV | 69680 | 1340 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196126 B & C Phase Overcurrent targets = 51BC tree branch blown clear at pole MW-40063 | December | 2019 | 2020Q2 | 2020 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2019-12-07 | N | 52 | N | 7 | N | N | 1.1101 | 39.4971 | 50920.0888
[7 empty] | 4749 | 14502 | 1711071 | 2019-12-07 18:30 | 2019-12-07 21:15 | 165 | 11kV | 990 | 6 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | Hot >35C | N | The 11kv LK44006 was opened for safety reasons Remarks: The pole at PT.11993 Mangrove Ck Dam No.1 was found badly damaged by the bushfire. Interrupted to allow lineworkers to break 11kv bonds to PT.11993 Mangrove Ck Dam No.1. See seperate interruption for PT.11993 | December | 2019 | 2020Q2 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2019-12-07 | N | 165 | N | 7 | N | N | 1.1101 | 39.4971 | 723.4628
[7 empty] | 5266 | 19573 | 1711219 | 2019-12-08 12:49 | 2019-12-08 13:43 | 54 | 11kV | 216 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 196132 B Phase DOLF : 63 Amp fuse fatigue. B phase load 63A. Excluded oms 1711219. | December | 2019 | 2020Q2 | 2020 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2019-12-08 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 157.8464
[7 empty] | 3501 | 2034 | 1711231 | 2019-12-08 14:41 | 2019-12-08 20:25 | 344 | 11kV | 688 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 196136 Single phase sub isolated for repairs Excluded oms 1711231 | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-12-08 | N | 344 | N | 4 | N | N | 1.1101 | 39.4971 | 502.7701
[7 empty] | 4750 | 14512 | 1711261 | 2019-12-08 19:09 | 2019-12-08 22:28 | 199 | 11kV | 27158 | 427 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196135 tree on mains adj sub 50999, switch 3978 opened. section isolated for repairs Excluded oms 1711261 & 1711265 | December | 2019 | 2020Q2 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2019-12-08 | N | 63.6019 | N | 4 | N | N | 1.1101 | 39.4971 | 19846.2654
[7 empty] | 3650 | 3371 | 1711267 | 2019-12-08 20:24 | 2019-12-09 00:10 | 226 | 11kV | 10634 | 97 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196137 11kv isolated from abs 42181 to make repairs to LLC 54117 Excluded oms 1711267 | December | 2019 | 2020Q2 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2019-12-08 | N | 109.6289 | N | 4 | N | N | 1.1101 | 39.4971 | 7771.0136
[7 empty] | 3482 | 1842 | 1711284 | 2019-12-09 03:37 | 2019-12-09 04:36 | 59 | 11kV | 39926 | 684 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.20 tripped UG cable fault between S3821 Sw/A and S7864 Sw/A See 1712734 1712735 | December | 2019 | 2020Q2 | 2020 | ZN901:PA20 | ZN901:PA29 | ZN00901/000029 | SYDNEY | UG | Not Veg | 2019-12-09 | N | 58.3713 | N | 4 | N | N | 1.1101 | 39.4971 | 29176.7432
[7 empty] | 4352 | 10664 | 1711519 | 2019-12-09 14:29 | 2019-12-09 15:35 | 66 | 11kV | 528 | 8 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196148 C Phase DOLF : 20 Amp Bird at sub 70794. C ph DOLF replaced. LF 74551 C ph LF replaced. Excluded OMS 1711519. | December | 2019 | 2020Q2 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2019-12-09 | N | 66 | N | 4 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 4405 | 11090 | 1711679 | 2019-12-07 19:46 | 2019-12-09 18:16 | 2790 | 11kV | 98296 | 54 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | No Weather Impact | N | LID 196150 B & C Phase Overcurrent carry over from initial fire see report 196125/OMS 1711675 fault beyond abs 40652, poles down Top burnt off pole 8U-60014 Poles burnt down 8U-90026, 8U-90028, 8u-90029 | December | 2019 | 2020Q2 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-12-07 | N | 1820.2963 | N | 7 | N | N | 1.1101 | 39.4971 | 71831.8176
[7 empty] | 5071 | 17986 | 1711114 | 2019-12-07 12:20 | 2019-12-09 18:34 | 3254 | 11kV | 167550 | 99 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196125 Tree on mains at pole 8U-60020 potentially caused by previous bushfire feeder only had power restored at 1158hrs following being repaired for fire damage earlier today. second outage. See lid report 196122 Excluded oms 1711118, 1711114, 1711155, 1711168 | December | 2019 | 2020Q2 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-12-07 | N | 1692.4242 | N | 7 | N | N | 1.1101 | 39.4971 | 122440.5981
[7 empty] | 4215 | 9410 | 1711286 | 2019-12-09 08:05 | 2019-12-10 00:10 | 965 | 11kV | 60897 | 119 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC61097 Wise Ferry Lavendar 10.2 tripped on: O/C After previous bushfire damage, tree branch fell on 11kV mains near LK43530, OH mains twisted together and crossarm damage. Six bays of 11kV down See 1713890 1713891 1713893 1713894 1713895 1713896 | December | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-12-09 | N | 511.7395 | N | 4 | N | N | 1.1101 | 39.4971 | 44501.7314
[7 empty] | 3816 | 5215 | 1711652 | 2019-12-10 03:33 | 2019-12-10 04:35 | 62 | 11kV | 558 | 9 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP1835 Caravan Plassey - HDO blown on footpath and middle phase Bat found below mains | December | 2019 | 2020Q2 | 2020 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2019-12-10 | N | 62 | N | 16 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 3361 | 641 | 1711653 | 2019-12-10 04:37 | 2019-12-10 07:18 | 161 | 11kV | 170831 | 1329 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196154 3 phase Instantaneous Overcurrent Excluded OMS 1711653 | December | 2019 | 2020Q2 | 2020 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2019-12-10 | N | 128.541 | N | 16 | N | N | 1.1101 | 39.4971 | 124838.2561
[7 empty] | 3836 | 5395 | 1711624 | 2019-12-09 19:11 | 2019-12-10 10:10 | 899 | 11kV | 38925 | 45 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196151 Tree on mains adjacent to links 41293 Excluded OMS 1711624 | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-12-09 | N | 865 | N | 4 | N | N | 1.1101 | 39.4971 | 28445.2419
[7 empty] | 4051 | 7564 | 1711741 | 2019-12-10 09:21 | 2019-12-10 11:01 | 100 | 11kV | 44816 | 465 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Sub 2835 Burwood Panel No.9 "George Mary No.3" feeder opened on Relays: earth fault, EFI Signals: Zone earth, No.4 Group Earth Remarks: UG fault. 11kv feeder failed from S220 Burwood Road to S79254 Railway Burleigh No.4 | December | 2019 | 2020Q2 | 2020 | ZN2835:PA9 | ZN2835:PA9 | ZN02835/000009 | BURWOOD | UG | Not Veg | 2019-12-10 | N | 96.3785 | N | 16 | N | N | 1.1101 | 39.4971 | 32750.211
[7 empty] | 3430 | 1336 | 1712062 | 2019-12-10 13:20 | 2019-12-10 14:39 | 79 | 11kV | 6636 | 84 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 196157 B Phase DOLF : 40 Amp DOLF Fuse fatigue Excluded OMS 1712062 | December | 2019 | 2020Q2 | 2020 | 270:83584 | 270:83584 | ZN00270/083584 | LAKE MACQUARIE | OH | Not Veg | 2019-12-10 | N | 79 | N | 16 | N | N | 1.1101 | 39.4971 | 4849.3931
[7 empty] | 4661 | 13730 | 1712069 | 2019-12-10 14:20 | 2019-12-10 16:10 | 110 | 11kV | 1320 | 12 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | On Panel 12 "Yarramelong" section of feeder from USL41520 interrupted Remarks: OH resting on cross arm. feeder isolated from LK41520 tee PT18094, PT13441, PT18673, PT13228 | December | 2019 | 2020Q2 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-12-10 | N | 110 | N | 16 | N | N | 1.1101 | 39.4971 | 964.6171
[7 empty] | 3853 | 5551 | 1712052 | 2019-12-10 13:13 | 2019-12-10 18:17 | 304 | 11kV | 4864 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Fuse failure At 9900 Menai Zn P10 the illawarra barry no2 fdr interrupted for safety Remarks: interrupted for safety reasons. ABB switchgear safety issue per stuart donaldson to de-energise rmi for fuse replacement oms 1712052 | December | 2019 | 2020Q2 | 2020 | ZN9900:PA10 | ZN9900:PA10 | ZN09900/000010 | SUTHERLAND | OH | Not Veg | 2019-12-10 | N | 304 | N | 16 | N | N | 1.1101 | 39.4971 | 3554.4677
[7 empty] | 4586 | 13045 | 1712378 | 2019-12-10 18:18 | 2019-12-10 19:05 | 47 | 11kV | 20257 | 431 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At 9900 Menai Zn P10 the illawarra barry no2 fdr interrupted for safety Remarks: interrupted for safety reasons. ABB switchgear safety issue per stuart donaldson to de-energise rmi for fuse replacement oms 1712052 | December | 2019 | 2020Q2 | 2020 | ZN9900:PA10 | ZN9900:PA10 | ZN09900/000010 | SUTHERLAND | Unknown | Not Veg | 2019-12-10 | N | 47 | N | 16 | N | N | 1.1101 | 39.4971 | 14803.2181
[7 empty] | 4022 | 7205 | 1712175 | 2019-12-10 18:33 | 2019-12-10 19:48 | 75 | 11kV | 75781 | 1055 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | LID 196163 UGOH at pole AH-61438 arrestor exploded UGOH fault. Possibly only LA's. 3 phase IOC. Excluded OMS 1712175 | December | 2019 | 2020Q2 | 2020 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2019-12-10 | N | 71.8303 | N | 16 | N | N | 1.1101 | 39.4971 | 55378.5196
[7 empty] | 5303 | 19886 | 1712151 | 2019-12-10 16:56 | 2019-12-10 21:06 | 250 | 11kV | 26000 | 104 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Hot >35C | N | LID 196164 Burnt off Live Line Clamp Excluded OMS 1712151 | December | 2019 | 2020Q2 | 2020 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2019-12-10 | N | 250 | N | 16 | N | N | 1.1101 | 39.4971 | 19000.0331
[7 empty] | 4127 | 8451 | 1712208 | 2019-12-10 21:13 | 2019-12-10 22:00 | 47 | 11kV | 6909 | 147 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | ZN12610 Long Jetty Pa16 'S14918 Entrance SBS B1 etc' was interrupted: Interruption was due to operating restriction on ABB and Andelec SD type 11kv RMI's Remarks: insulator failed. 11kv OH mains come away from pin insulator between S14918 Sw/B and LK43537 isolation extended due to RMI operating restriction. Job deemed emergency by lineworker | December | 2019 | 2020Q2 | 2020 | ZN12610:PA16 | ZN12610:PA16 | ZN12610/000016 | CENTRAL COAST | OH | Not Veg | 2019-12-10 | N | 47 | N | 16 | N | N | 1.1101 | 39.4971 | 5048.8934
[7 empty] | 4277 | 10003 | 1712218 | 2019-12-10 21:37 | 2019-12-11 00:40 | 183 | 11kV | 366 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 196167 Single phase LLC burnt off at sub 52712. DQ Excluded OMS 1712218 | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-12-10 | N | 183 | N | 16 | N | N | 1.1101 | 39.4971 | 267.462
[7 empty] | 3526 | 2256 | 1712226 | 2019-12-10 22:16 | 2019-12-11 02:36 | 260 | 11kV | 271118 | 1044 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 196169 2 fault operations 3 phase Instantaneous Overcurrent Excluded OMS 1712226 | December | 2019 | 2020Q2 | 2020 | 224:80326 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Veg | 2019-12-10 | N | 259.6916 | N | 16 | N | N | 1.1101 | 39.4971 | 198125.0378
[7 empty] | 3870 | 5677 | 1712211 | 2019-12-10 23:45 | 2019-12-11 03:03 | 198 | 11kV | 30692 | 234 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 196165 3 phase interupted to repair LV broken x arm arcing and HV pin insulator cracked and tracking pole sw-30839. DQ Excludedoms 1712232 | December | 2019 | 2020Q2 | 2020 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2019-12-10 | N | 131.1624 | N | 16 | N | N | 1.1101 | 39.4971 | 22428.8083
[7 empty] | 4635 | 13527 | 1712252 | 2019-12-11 00:33 | 2019-12-11 05:10 | 277 | 11kV | 125692 | 728 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | REC40425 Kurrawyba Cadell - Pnl.26 tripped on: Earth Fault and O/C Broken Cross arm caused footpath phase 11kV wire to come down Note: Operating ban on ABB and Andelec SD type RMIs - each restoration step required isolation at the REC to close open switches See 1712749 1712751 1712752 1712754 1712759 1712753 1712757 | December | 2019 | 2020Q2 | 2020 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2019-12-11 | N | 172.6538 | N | 2 | N | N | 1.1101 | 39.4971 | 91852.0063
[7 empty] | 4854 | 15563 | 1712238 | 2019-12-10 23:43 | 2019-12-11 09:52 | 609 | 11kV | 67095 | 851 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | Zn12570 Avoca - Pnl.34 tripped, reclosed and tripped on: OC + EF B phase insulator failed on pole AV1434. HV into LV. HV into LV inspections completed at m/b in the immediate vicinity and no damage found. See 1712763 1712764 | December | 2019 | 2020Q2 | 2020 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2019-12-10 | N | 78.8425 | N | 16 | N | N | 1.1101 | 39.4971 | 49031.047
[7 empty] | 4218 | 9455 | 1712767 | 2019-12-10 23:48 | 2019-12-11 13:05 | 797 | 11kV | 272576 | 1250 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | N | Zn12660 Woy Woy - Pnl.14 tripped on: O/C Note: REC48036 did not trip on original fault then tripped when re-energised Bird found at PT12095 See 1712767 1712768 1712769 1712770 1712771 1712772 1712773 1712774 1712775 1712776 1712777 1712779 | December | 2019 | 2020Q2 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2019-12-10 | N | 218.0608 | N | 16 | N | N | 1.1101 | 39.4971 | 199190.5012
[7 empty] | 4368 | 10762 | 1712612 | 2019-12-12 09:40 | 2019-12-12 10:55 | 75 | 11kV | 26700 | 356 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP42701 Scotland Island - interrupted to remove tree branch from OH mains. (11kV) | December | 2019 | 2020Q2 | 2020 | ZN15014:PA10 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Veg | 2019-12-12 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 19511.5725
[7 empty] | 4273 | 9987 | 1712586 | 2019-12-12 09:10 | 2019-12-12 13:30 | 260 | 11kV | 5460 | 21 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 196180 Replaced pole FL-10042 which was at 25% strength. NAR 50767 | December | 2019 | 2020Q2 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2019-12-12 | N | 260 | N | 4 | N | N | 1.1101 | 39.4971 | 3990.007
[7 empty] | 4851 | 15551 | 1712819 | 2019-12-12 15:44 | 2019-12-12 17:09 | 84.9333 | 11kV | 14098.9333 | 166 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | No Weather Impact | N | LID 196197 NAR 50796 Hot joint repaired at SW 3528. Urgent repair required after thermal inspection. See M Judge Luke watters to switch. Hot Joint at Sw 3528. Found by thermovision. | December | 2019 | 2020Q2 | 2020 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | Unknown | Not Veg | 2019-12-12 | N | 84.9333 | N | 4 | N | N | 1.1101 | 39.4971 | 10303.0846
[7 empty] | 4261 | 9893 | 1712548 | 2019-12-11 20:50 | 2019-12-12 19:15 | 1345 | 11kV | 59180 | 44 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Section of 11kv feeder interrupted from S79254 Railway Burley #4 to S49738 Shaftsbury Clarence See NAR #50764-T1 Remarks: interrupted for safety reasons. Damaged 11kv cable. | December | 2019 | 2020Q2 | 2020 | ZN2835:PA9 | ZN2835:PA9 | ZN02835/000009 | BURWOOD | UG | Not Veg | 2019-12-11 | N | 1345 | N | 2 | N | N | 1.1101 | 39.4971 | 43246.9985
[7 empty] | 5182 | 18819 | 1713461 | 2019-12-13 10:16 | 2019-12-13 10:30 | 14 | 11kV | 4018 | 287 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | The 11kv feeder from R45050 Magenta to extent of feeder Ex S12620 Noraville Panel 11 "Noral head" interrupted for safety Remarks: interrupted to operate ABB RMI for NAR 5022 | December | 2019 | 2020Q2 | 2020 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | Unknown | Not Veg | 2019-12-13 | N | 14 | N | 4 | N | N | 1.1101 | 39.4971 | 2936.2359
[7 empty] | 3459 | 1598 | 1712940 | 2019-12-13 09:53 | 2019-12-13 17:45 | 472 | 11kV | 472 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 196214 Substation DOLF Broken DOLF assembly replaced under AP | December | 2019 | 2020Q2 | 2020 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2019-12-13 | N | 472 | N | 4 | N | N | 1.1101 | 39.4971 | 344.9237
[7 empty] | 3911 | 6027 | 1713035 | 2019-12-13 17:10 | 2019-12-13 19:55 | 165 | 11kV | 85445 | 540 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 196225 ABS 41020 Faulty. Will be bridged out. Requires replacement. M Judge aware. Hv lead pulled out while operating | December | 2019 | 2020Q2 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2019-12-13 | N | 158.2315 | N | 4 | N | N | 1.1101 | 39.4971 | 62440.6858
[7 empty] | 4383 | 10859 | 1713053 | 2019-12-13 21:21 | 2019-12-14 00:20 | 179 | 11kV | 59512 | 652 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196229 1 Fault operations, A Phase, Overcurrent FEEDER DIPPED, HV MAIN DOWN ALIVE ON BACKFEED. POSSIBLE HV INTO LV, CHECKED BY EMSO ALL OK. POSSIBLY A POSSUM HAS COME IN CONTACT WITH NETWORK - DISTRIBUTION WIRE HANGING ON FENCE - HALF THE STREET HAS NO POWER - STREETLIGHTS OUT See also OMS ## OMS REPORT NO 1713053, 1713060, 1713054 and LID 196228 (OMS 1713920) | December | 2019 | 2020Q2 | 2020 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2019-12-13 | N | 91.2761 | N | 4 | N | N | 1.1101 | 39.4971 | 43489.6143
[7 empty] | 3806 | 5091 | 1713074 | 2019-12-14 09:10 | 2019-12-14 15:03 | 353 | 11kV | 3177 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196231 Single phase Tree fallen on mains pole CT-20001, ABS 31427 isolated for repairs Note: Outage time began at 9:10 as per control room switching sheet | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2019-12-14 | N | 353 | N | 4 | N | N | 1.1101 | 39.4971 | 2321.6579
[7 empty] | 5267 | 19580 | 1713651 | 2019-12-12 12:00 | 2019-12-14 16:45 | 3165 | 11kV | 75960 | 24 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Panel No.1 "ex Sub12630 Peats Ridge" USL43712 to USL43692 Remarks: bushfire | December | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-12-12 | N | 3165 | N | 4 | N | N | 1.1101 | 39.4971 | 55509.3276
[7 empty] | 5259 | 19521 | 1713131 | 2019-12-14 16:49 | 2019-12-14 21:15 | 266 | 11kV | 9006 | 45 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196233 11kv mains down pole WB-72928 Sw 42523 section isolated for repairs from 11kV links 8912. Feeder originally opened from SW 45253 until links 8912 were opened | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-12-14 | N | 200.1333 | N | 4 | N | N | 1.1101 | 39.4971 | 6581.3192
[7 empty] | 5256 | 19501 | 1713160 | 2019-12-14 22:54 | 2019-12-14 23:39 | 45 | 11kV | 46350 | 1030 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC20397 Pitwater Cabbage tree - tripped on: IOC & OC Abnormal: AB20597 open with S15214 Sw.B Closed (S16251 S16250 S15214 S16242 were in LV //) Bat on 11kV mains outside 40 Rednal St | December | 2019 | 2020Q2 | 2020 | ZN15014:PA7 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Not Veg | 2019-12-14 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 33871.2129
[7 empty] | 4690 | 14005 | 1713147 | 2019-12-14 19:33 | 2019-12-15 00:20 | 287 | 11kV | 7462 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196235 B phase 6 Amp Line DOLF tree removed from mains, supply restored 0020 | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2019-12-14 | N | 287 | N | 4 | N | N | 1.1101 | 39.4971 | 5453.0095
[7 empty] | 5283 | 19716 | 1713169 | 2019-12-15 03:30 | 2019-12-15 21:05 | 1055 | 11kV | 143390 | 714 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | @S9534 Kurnell Sth Panel 17 'Captain Cook Solander" fdr tripped and locked out on: A & C phase overcurrent reclose time delay lockout Remarks: vehicle hit pole. Car hit LB35399 pole | December | 2019 | 2020Q2 | 2020 | ZN9534:PA17 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2019-12-15 | N | 200.8263 | N | 3 | N | N | 1.1101 | 39.4971 | 104785.1827
[7 empty] | 5011 | 17319 | 1713242 | 2019-12-15 15:39 | 2019-12-15 21:05 | 326 | 11kV | 2282 | 7 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 196240 B Phase LLC broken, Replaced under AP AT MSB, F/L A1-N= O/C A2-N=1043 OHMS A3-N=0.09 OHMS,FED DIRECTLY OF TX POLE HR22216, REPEATED TEST AT POINT OF ATTATCHMENT, FOUND SAME RESULTS, BAD CONNECTIONS FOUND AT LINE SIDE OF SERVICE WIRE, RECEIVED URGENT JOB AT ANNA BAY, REQUIRED TO LEAVE SITE, OH CREW TO PLEASE ATTEND AND REPLACE LINE SIDE CONNECTIONS AND CONFIRM SUPPLY TO AT CUSTOMERS MSB | December | 2019 | 2020Q2 | 2020 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2019-12-15 | N | 326 | N | 3 | N | N | 1.1101 | 39.4971 | 1667.6183
[7 empty] | 4019 | 7191 | 1713713 | 2019-12-16 02:14 | 2019-12-16 04:05 | 111 | 11kV | 7409 | 1029 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At ZN14144 Wamberal Panel 4 "S18823" feeder has tripped and reclosed Signals: 11kv trip Relays: A & C OC At PT12362 hastings Aspen 63amp HDO's operate foot path side and centre phase Abnormal: S18343 Sw/B closed and Sw/A open Remarks: animals/birds. At PT12362 Hastings Aspen DOP has found 2x HDOs blown and a possum tail | December | 2019 | 2020Q2 | 2020 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Not Veg | 2019-12-16 | N | 7.2002 | N | 4 | N | N | 1.1101 | 39.4971 | 5414.2787
[7 empty] | 4937 | 16448 | 1714525 | 2019-12-15 22:53 | 2019-12-16 08:35 | 582 | 11kV | 44620 | 140 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S2400 Berowra Panel 13 from S6731 to Ab1262 Bond Off at UGIOH See OMS 1714525 1713299 1713274 | December | 2019 | 2020Q2 | 2020 | ZN2400:PA13 | ZN2400:PA13 | ZN02400/000013 | HORNSBY | OH | Not Veg | 2019-12-15 | N | 318.7143 | N | 3 | N | N | 1.1101 | 39.4971 | 32606.9799
[7 empty] | 4491 | 11946 | 1713290 | 2019-12-16 04:06 | 2019-12-16 09:20 | 314 | 11kV | 85161 | 644 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 22 has tripped Signals; 11kV trip, Zone earth and Tx3 Group Earth Abnormal Swithcing:11kV UG fault between S5844 Goodlannds and S7816 The Santuary SW/A open Cause: 11kV UG fault between S5844 goodlands Esplanade to S7816 The Sanctury See OMS 1714496 1714497 1713290 1313291 | December | 2019 | 2020Q2 | 2020 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | UG | Not Veg | 2019-12-16 | N | 132.2376 | N | 4 | N | N | 1.1101 | 39.4971 | 62233.147
[7 empty] | 4539 | 12442 | 1713383 | 2019-12-16 11:06 | 2019-12-16 15:10 | 244 | 11kV | 244 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 196246 LLC burnt loose, no protection operated Note: start time changed to match the first NS call received, refer to related record | December | 2019 | 2020Q2 | 2020 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2019-12-16 | N | 244 | N | 4 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 4840 | 15441 | 1713433 | 2019-12-16 13:40 | 2019-12-16 17:50 | 250 | 11kV | 250 | 1 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196250 B phase 31 Amp fuse, substation DOLF refer to OMS 1713433 and 1713479 Sub 72123 NOT 72604 | December | 2019 | 2020Q2 | 2020 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Not Veg | 2019-12-16 | N | 250 | N | 4 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 3940 | 6299 | 1713581 | 2019-12-17 05:48 | 2019-12-17 08:10 | 142 | 11kV | 31240 | 220 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | The 11kv R.35260 Pacific Cres East Ex. S9118 Cronulla Panel 3 "Binaville Av, etc" tripped Remarks: cause not ascertained. Dop patrolled feeder, no cause found | December | 2019 | 2020Q2 | 2020 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Veg | 2019-12-17 | N | 142 | N | 4 | N | N | 1.1101 | 39.4971 | 22829.2706
[7 empty] | 5324 | 20103 | 1713662 | 2019-12-17 10:40 | 2019-12-17 13:05 | 145 | 11kV | 290 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196261 Single Phase 10 Amp substation DOLF No Cause found, not storm conditions Replaced 10 amp HV Fuse on Sub 19264, Supply restored at 1305. | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2019-12-17 | N | 145 | N | 4 | N | N | 1.1101 | 39.4971 | 211.9234
[7 empty] | 4519 | 12230 | 1713735 | 2019-12-17 14:10 | 2019-12-17 16:25 | 135 | 11kV | 16065 | 119 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | AT ZN1648 Enfield, Ex Panel 15 "S2013" feeder Abnormal: sw/B open @ S1840 with Sw/A closed @ S48456 blight st Remarks: interrupted for safety reasons. Due to ABB operating ban at S8988. Was required to open and earth Sw/B @ S8988 | December | 2019 | 2020Q2 | 2020 | ZN690:PA34 | ZN690:PA34 | ZN00690/000034 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2019-12-17 | N | 135 | N | 4 | N | N | 1.1101 | 39.4971 | 11739.8282
[7 empty] | 4776 | 14790 | 1713812 | 2019-12-17 19:54 | 2019-12-17 21:50 | 116 | 11kV | 52416 | 511 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN187 panel 23 tripped on Relay trip alarm, earth fault, EFI, EF Check flag Signals: 11kV trip, group earth Abnormal Switchimh: SW/A closed at S8592 SW/B open Cause: 11kV feeder fault from S6594 Mitchell Pacific to S5623 Herbert St Leonards Station See OMS 1714487 1714489 1713812 | December | 2019 | 2020Q2 | 2020 | ZN187:PA23 | ZN187:PA23 | ZN00187/000023 | NORTH SYDNEY | UG | Not Veg | 2019-12-17 | N | 102.5753 | N | 4 | N | N | 1.1101 | 39.4971 | 38304.0668
[7 empty] | 4033 | 7376 | 1713833 | 2019-12-18 00:19 | 2019-12-18 02:25 | 126 | 11kV | 130488 | 1128 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC45092 Mannering Park Opened (Scan Fail) Abnormal: LB40955 closed with LB40566 open (DMA AB43916) Bird likely made contact See 1713875 1713876 | December | 2019 | 2020Q2 | 2020 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2019-12-18 | N | 115.6809 | N | 2 | N | N | 1.1101 | 39.4971 | 95356.7817
[7 empty] | 3811 | 5119 | 1712492 | 2019-12-10 09:01 | 2019-12-18 17:00 | 11999 | 11kV | 2258934 | 454 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12630 Peats Ridge - Pnl.1 - multiple trips & interruptions along the feeder due to bushfire activitiy with trees and mains down. Note: 11kV line being damaged by falling branches off burnt trees. Too hazardous for staff to remain on site. Staff will return Wed 11/12/19 12/12/19 19:28 t44658: Feeder ZN12630:PA1 De-energised for safety due to multiple hazards on the feeder. Multiple trees down due to bushfire. See 1717348/ 349/ 351/ 352/ 353/ 354/ 355/ 356/ 357/ 358/ 362/ 363/ 365 | December | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-12-10 | N | 4975.6256 | N | 16 | N | N | 1.1101 | 39.4971 | 1650762.3399
[7 empty] | 4288 | 10073 | 1713980 | 2019-12-18 18:00 | 2019-12-18 18:35 | 35 | 11kV | 1015 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | CP40827 interrupted for safety to put 11kV CCT back onto pin Dan Craft from Ausgrid Contracts reports 11kV CCT cable come away from insulator and resting on crossarm on pole CB58. PT14636 BRUSH CK YARRA 5.8 also located on pole. | December | 2019 | 2020Q2 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2019-12-18 | N | 35 | N | 2 | N | N | 1.1101 | 39.4971 | 741.7321
[7 empty] | 3991 | 6879 | 1714082 | 2019-12-19 | 2019-12-19 03:10 | 190 | 11kV | 147828 | 1141 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 33612 B and C phases Over current Feeder patrolled all OK No cause found, not storm conditions | December | 2019 | 2020Q2 | 2020 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2019-12-19 | N | 129.56 | N | 11 | N | N | 1.1101 | 39.4971 | 108028.3422
[7 empty] | 4952 | 16623 | 1714096 | 2019-12-19 05:04 | 2019-12-19 07:30 | 146 | 11kV | 44508 | 554 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1193 Lindfield Panel 10 Highfield Pacific feede rtripped Relays: Earth Fault C phase, EFI Signals 11kV trip, Group Earth Cause: UG cable fault from S5125 to S5126 tee PT780 See OMS 1714516 1714518 1714519 1714096 | December | 2019 | 2020Q2 | 2020 | ZN1193:PA10 | ZN1193:PA10 | ZN01193/000010 | KU-RING-GAI | UG | Not Veg | 2019-12-19 | N | 80.3394 | N | 11 | N | N | 1.1101 | 39.4971 | 32525.1336
[7 empty] | 4107 | 8267 | 1714085 | 2019-12-19 02:39 | 2019-12-19 07:59 | 320 | 11kV | 73564 | 557 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ex S1300 Lake Munmorah ex 11kV panel 10 Recloser Cp40178 Elizabeth Bay Anthony has tripped on overcurrent Abnormal Switching: CP40214 Closed, CP43627 Open 'Cause not ascertained for outage See OMS 1714507 1714508 1714085 1714101 1714089 | December | 2019 | 2020Q2 | 2020 | ZN13000:PA10 | ZN13000:PA10 | ZN13000/000010 | CENTRAL COAST | OH | Veg | 2019-12-19 | N | 132.0718 | N | 11 | N | N | 1.1101 | 39.4971 | 53758.4014
[7 empty] | 3614 | 2941 | 1714437 | 2019-12-19 08:45 | 2019-12-19 10:10 | 85 | 11kV | 425 | 5 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Panel 5 ex S12630 Peats Ridge CP44097 Interrupted to clear trees after bush fire | December | 2019 | 2020Q2 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2019-12-19 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 310.5775
[7 empty] | 5191 | 18884 | 1714117 | 2019-12-19 08:04 | 2019-12-19 11:01 | 177 | 11kV | 307197 | 2277 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN2196 Milperra 11kV panel No25 tripped on Relays: C phase OC and EF with fault check Cause: 11kV feeder fault from S6133 to S1269 See OMS 1714433 1714434 1714435 1714117 | December | 2019 | 2020Q2 | 2020 | ZN2196:PA25 | ZN2196:PA25 | ZN02196/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-12-19 | N | 134.913 | N | 11 | N | N | 1.1101 | 39.4971 | 224490.5068
[7 empty] | 4668 | 13815 | 1714097 | 2019-12-19 05:33 | 2019-12-19 13:05 | 452 | 11kV | 11268 | 99 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196301 3 Phase 5 Amp, Line DOLF HV reported down Pole burnt out and fell Note: Start time has been amended to first NS customer call received | December | 2019 | 2020Q2 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2019-12-19 | N | 113.8182 | N | 11 | N | N | 1.1101 | 39.4971 | 8234.3221
[7 empty] | 3915 | 6076 | 1714197 | 2019-12-19 12:20 | 2019-12-19 14:00 | 100 | 11kV | 75600 | 1204 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | ZN4545 MEADOWBANK 11kV CB Panel 44 'S1575 Park Ave' tripped on: Re;ays: A Phase IOC, A Phase OC, Earth Fault, EFI and Fault check Signals: Zone Earth, Tx3 Group Earth, 11kv trip EFI: S61092 Cause: UGOH fault short circuit 11kv fdr from S61092 Sw/B to LB61232 tee pt2230. UGOH damaged See 1715581,2 ex 1714197,206 | December | 2019 | 2020Q2 | 2020 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | Unknown | Unknown | 2019-12-19 | N | 62.7907 | N | 11 | N | N | 1.1101 | 39.4971 | 55246.2502
[7 empty] | 4500 | 12078 | 1714250 | 2019-12-19 14:25 | 2019-12-19 15:52 | 87 | 11kV | 91953 | 1105 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN3425 CASTLE COVE 11kV CB Panel 22 'S8007 Gibbes Victoria' fdr tripped on Signals: 11kv trip, No.4 Tx Group Earth Relays: B Phase O/C, Earth Fault, Fault CHeck, EFI EFI: S8007 Cause: UG Fault between S8007Swb to S3884SwA See 1715584,6,7 ex 1714250 | December | 2019 | 2020Q2 | 2020 | ZN3425:PA22 | ZN3425:PA22 | ZN03425/000022 | WILLOUGHBY | UG | Not Veg | 2019-12-19 | N | 83.2154 | N | 11 | N | N | 1.1101 | 39.4971 | 67196.5402
[7 empty] | 4458 | 11565 | 1714249 | 2019-12-19 14:24 | 2019-12-19 18:34 | 250 | 11kV | 50210 | 208 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | ZN12610 LONG JETTY 11kV CB Panel 5 'Bay Village Shopping Complex' tripped on: Realys: C Phase IOC, EFI, Fault Check Signals: 11kv trip, Tx1 Group EArth, Zone Earth EFI: Nil Cause: UGOH fault short circuit above S14747 failed See 1715526,7,8 Ex 1714249,333 | December | 2019 | 2020Q2 | 2020 | ZN12610:PA5 | ZN12610:PA5 | ZN12610/000005 | CENTRAL COAST | Unknown | Unknown | 2019-12-19 | N | 241.3942 | N | 11 | N | N | 1.1101 | 39.4971 | 36691.9871
[7 empty] | 5008 | 17285 | 1714424 | 2019-12-19 19:36 | 2019-12-19 20:32 | 56 | 11kV | 74013 | 1358 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | At S262 Marrickville Panel 31 "Ohara Calvert"' feeder tripped on: earth leakage, efi, fault check Remarks: UG fault in section of 11kv S7989 sw/B to S2244 Sw/A to S49534 sw/A | December | 2019 | 2020Q2 | 2020 | ZN262:PA31 | ZN262:PA31 | ZN00262/000031 | INNER WEST | UG | Not Veg | 2019-12-19 | N | 54.5015 | N | 11 | N | N | 1.1101 | 39.4971 | 54086.5174
[7 empty] | 4083 | 7996 | 1714322 | 2019-12-19 16:29 | 2019-12-19 20:48 | 259 | 11kV | 122158 | 1049 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn35370 Galston - Pnl.4 tripped on: C phase O/C & Earth Fault Abnormal: LB62158 Closed with AB340 Open (DMA), CP62159 Closed with CO1237 Open (DMA) tree branch on mains between LB2603 and CP2604 See 1721471 1721472 | December | 2019 | 2020Q2 | 2020 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2019-12-19 | N | 116.4519 | N | 11 | N | N | 1.1101 | 39.4971 | 89269.4633
[7 empty] | 4761 | 14618 | 1714532 | 2019-12-20 13:27 | 2019-12-20 14:00 | 32.6167 | 11kV | 1728.6833 | 53 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex ZN14143 SOMERSBY section of 11kV Panel 12 section of 11kv OH isolated from LB44475 to LB45416 to LB46579 due to operating ban on andealect fuse switch @ S12155 & Links 42677 (Ferro) Cause: OH resting on cross arm. Interrupted to allow repairs | December | 2019 | 2020Q2 | 2020 | ZN14143:PA12 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | OH | Not Veg | 2019-12-20 | N | 32.6167 | N | 2 | N | N | 1.1101 | 39.4971 | 1263.2708
[7 empty] | 5118 | 18343 | 1714493 | 2019-12-20 08:44 | 2019-12-21 06:50 | 1326 | 11kV | 3117 | 7 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2466 Flemington 11kv panel 21, "S44444 Hill Carter No1 "feeder tripped on relays: Timed earth fault, EFI, fault check Signals: 11kv trip, Tx4 group earth, zone earth At S3620 Tooheys Lidcombe Sw/B tripped on: Relays: feeder protection relay (C phase, earth fault, IDMT, directional trip) remarks: UG fault. 11kv UG cable fault from S4444 Hill Carter No1 to S48233 Paramatta John No2 to S3620 Tooheys Lidcombe tee S3298 Nyrang Par No. (S3298 Non//, interrupted) | December | 2019 | 2020Q2 | 2020 | ZN2466:PA21 | ZN2466:PA21 | ZN02466/000021 | PARRAMATTA | UG | Not Veg | 2019-12-20 | N | 445.2857 | N | 2 | N | N | 1.1101 | 39.4971 | 2277.8117
[7 empty] | 3595 | 2773 | 1714676 | 2019-12-21 03:34 | 2019-12-21 07:30 | 236 | 11kV | 349892 | 2304 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S9700 Kirrawee Panel 17 tripped reclosed tripped and locked out Relays - C phase IOC, C phase, overcurrent SEL EFI Signals - 11kV Zone Earth Tx3 Group. Bond failed below CP35835 See OMS 1721542 1721543 1721544 1721547 1714676 | December | 2019 | 2020Q2 | 2020 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2019-12-21 | N | 151.8628 | N | 11 | N | N | 1.1101 | 39.4971 | 255690.7535
[7 empty] | 4632 | 13520 | 1714712 | 2019-12-21 08:58 | 2019-12-21 11:10 | 132 | 11kV | 3564 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196313 C Phase 40 Amp fuse, substation DOLF No cause found, not storm conditions OMS 1714712. C phase dolf. All 3 replaced. V = 238 Left 50/80/70 right 80/100/80 | December | 2019 | 2020Q2 | 2020 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2019-12-21 | N | 132 | N | 11 | N | N | 1.1101 | 39.4971 | 2604.4661
[7 empty] | 5251 | 19463 | 1714758 | 2019-12-21 14:22 | 2019-12-21 16:22 | 120 | 11kV | 167626 | 1562 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | @ZN 3472 Sefton 11kv Panel 28 fdr tripped, reclosed and locked out Remarks: suspected 11kv ug fault from S4349 Neville St to S6254 Olympic Velodome to S8525 Cameron Thornton | December | 2019 | 2020Q2 | 2020 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2019-12-21 | N | 107.315 | N | 11 | N | N | 1.1101 | 39.4971 | 122496.1367
[7 empty] | 4999 | 17191 | 1714856 | 2019-12-21 18:24 | 2019-12-21 19:35 | 71 | 11kV | 1065 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 196316 B Phase 63Amp substation DOLF | December | 2019 | 2020Q2 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Veg | 2019-12-21 | N | 71 | N | 11 | N | N | 1.1101 | 39.4971 | 778.2706
[7 empty] | 3415 | 1136 | 1714757 | 2019-12-21 14:14 | 2019-12-21 20:00 | 346 | 11kV | 345472 | 1497 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S10994 Mortdale Panel 7 tripped on A and B phase IOC earth fault and SEL Abnormal Switching: LB30094 Open SW CLosed at S10133 Cause: UG fault - between S499593 to S49349 to S49509 See OMS 1721444 1721446 1714757 1714760 | December | 2019 | 2020Q2 | 2020 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | UG | Not Veg | 2019-12-21 | N | 230.7762 | N | 11 | N | N | 1.1101 | 39.4971 | 252460.7479
[7 empty] | 4505 | 12112 | 1714905 | 2019-12-21 18:56 | 2019-12-21 20:50 | 114 | 11kV | 8276 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC559 Cobah Rd - tripped/ reclosed and tripped on : A & B Phase OC Cause not ascertained. LB3342 to AB2063 requires patrolling. PT63876 restored via LV // See 1721475 1721476 1721479 | December | 2019 | 2020Q2 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-12-21 | N | 86.2083 | N | 11 | N | N | 1.1101 | 39.4971 | 6047.8567
[7 empty] | 3721 | 4135 | 1714880 | 2019-12-21 19:22 | 2019-12-21 21:35 | 133.2833 | 11kV | 8530.1333 | 64 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | At PT10442 Ogilvy Ulister HDO and surge arrestors blown DOp suspects faulty TX. Sub placed in LV parallel See OMS 1714929 1714897 1714880 | December | 2019 | 2020Q2 | 2020 | ZN10995:PA13 | ZN10995:PA13 | ZN10995/000013 | GEORGES RIVER | OH | Not Veg | 2019-12-21 | N | 133.2833 | N | 11 | N | N | 1.1101 | 39.4971 | 6233.5698
[7 empty] | 4276 | 9993 | 1714945 | 2019-12-21 19:30 | 2019-12-21 23:58 | 268 | 11kV | 14696 | 67 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 8 RE44994 Mangrove Creek tripped Cause: not ascertained. DOps patrolled found nil See 1715515,6 ex 1714945 | December | 2019 | 2020Q2 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2019-12-21 | N | 219.3433 | N | 11 | N | N | 1.1101 | 39.4971 | 10739.4033
[7 empty] | 4691 | 14013 | 1715099 | 2019-12-22 01:27 | 2019-12-22 02:36 | 69 | 11kV | 4623 | 67 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 196325 Dead possum at sub pole, A & B phase 31 Amp DOLF replaced supply on 0236hrs. | December | 2019 | 2020Q2 | 2020 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | OH | Not Veg | 2019-12-22 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 3378.352
[7 empty] | 3727 | 4200 | 1715082 | 2019-12-22 00:37 | 2019-12-22 04:53 | 256 | 11kV | 512 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 196327 no protection operation isolated for clearance 33kV xarm change, 11kV System was abnormal with open taps pole KT-70082. See report 196326 for 33kV outage | December | 2019 | 2020Q2 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2019-12-22 | N | 256 | N | 4 | N | N | 1.1101 | 39.4971 | 374.1545
[7 empty] | 4795 | 14988 | 1715010 | 2019-12-21 20:31 | 2019-12-22 06:50 | 619 | 11kV | 17485 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 1969322 2 Fault operations, earth fault Tree brought down 11kV OHM from Pole FU-72554 | December | 2019 | 2020Q2 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2019-12-21 | N | 336.25 | N | 11 | N | N | 1.1101 | 39.4971 | 12777.5223
[7 empty] | 3522 | 2226 | 1715080 | 2019-12-22 00:08 | 2019-12-22 08:40 | 512 | 11kV | 383025 | 1516 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 196329 11kV cross arm burnt throughat pole JV-40004. 33kV into LV OHM Excluded OMS 1715074 | December | 2019 | 2020Q2 | 2020 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2019-12-22 | N | 252.655 | N | 4 | N | N | 1.1101 | 39.4971 | 279903.3727
[7 empty] | 4801 | 15061 | 1715033 | 2019-12-21 21:27 | 2019-12-22 11:25 | 838 | 11kV | 38741 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 196330 1 Fault operations Single Phase, Sensitive Earth Fault Trees blown onto mains, near Pole CT-23997 | December | 2019 | 2020Q2 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2019-12-21 | N | 596.0154 | N | 11 | N | N | 1.1101 | 39.4971 | 28310.7801
[7 empty] | 4464 | 11611 | 1715170 | 2019-12-22 12:26 | 2019-12-22 13:57 | 91 | 11kV | 203896 | 2276 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.42 tripped on: A phase IOC Abnormal: S7117 Sw/B open with S4005 Sw/A Closed UG cable fault between S36072 and S50120 to 78890 See 1720640 1720641 | December | 2019 | 2020Q2 | 2020 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2019-12-22 | N | 89.5852 | N | 4 | N | N | 1.1101 | 39.4971 | 149001.1829
[7 empty] | 3795 | 4997 | 1715497 | 2019-12-23 15:53 | 2019-12-23 16:49 | 56 | 11kV | 56 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196338 1 Fault operations No cause found, not storm conditions Prot=IOE OPER TRIP REQ | December | 2019 | 2020Q2 | 2020 |  |  |  | NEWCASTLE | OH | Veg | 2019-12-23 | N | 56 | N | 1 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 3770 | 4776 | 1715463 | 2019-12-24 05:47 | 2019-12-24 12:05 | 378.4333 | 11kV | 756.8667 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 196341 Single Phase Found 11kv dropper at TX62513 to top of 11kv Dolf detached from live line clamp on 11kv main. Opened and DT'd HV and LV Fuses at TX 62513 as instructed by SO. DO and line crew required CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | December | 2019 | 2020Q2 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2019-12-24 | N | 378.4333 | N | 2 | N | N | 1.1101 | 39.4971 | 553.0958
[7 empty] | 4260 | 9890 | 1715734 | 2019-12-24 20:41 | 2019-12-24 22:41 | 120 | 11kV | 5066 | 187 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | REC420 Reynolds Croswslands tripped & reclosed on: OC REC705 Knights Chad tripped on Earth Fault Abnormal: AB2440 open with LB1767 Closed Cause not ascertained. Grading issue between REC421 and REC420 and REC705 See 1721397 1721398 | December | 2019 | 2020Q2 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2019-12-24 | N | 27.0909 | N | 2 | N | N | 1.1101 | 39.4971 | 3702.0834
[7 empty] | 3487 | 1893 | 1715808 | 2019-12-25 04:39 | 2019-12-25 09:25 | 286 | 11kV | 91535 | 648 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 1969345 2 Fault operations A and B phases, Overcurrent Wire off pins pole VP-10099 repaired under AP | December | 2019 | 2020Q2 | 2020 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | OH | Not Veg | 2019-12-25 | N | 141.2577 | N | 2 | N | N | 1.1101 | 39.4971 | 66891.0782
[7 empty] | 3380 | 803 | 1715922 | 2019-12-26 04:18 | 2019-12-26 05:36 | 78 | 11kV | 122304 | 1568 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15009 Manly Pnl.7 tripped, reclosed and locked out on: O/C & E/F Bat found on ground below 11kV | December | 2019 | 2020Q2 | 2020 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Not Veg | 2019-12-26 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 89376.1558
[7 empty] | 4762 | 14624 | 1715976 | 2019-12-26 14:30 | 2019-12-26 15:00 | 30 | 11kV | 60 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196349 single phase Service reattched. Supply interrupted at 1430hrs & restored at 1500hrs. | December | 2019 | 2020Q2 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2019-12-26 | N | 30 | N | 5 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 3931 | 6179 | 1715831 | 2019-12-25 07:08 | 2019-12-26 17:10 | 2042 | 11kV | 13756 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | CP24720 Cromer Fitness - 11kV Fuses operated UG cable fault between S16970 and S17023 See 1715831 1715907 | December | 2019 | 2020Q2 | 2020 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | UG | Not Veg | 2019-12-25 | N | 1719.5 | N | 2 | N | N | 1.1101 | 39.4971 | 10052.4791
[7 empty] | 3645 | 3313 | 1715996 | 2019-12-26 16:20 | 2019-12-26 17:10 | 50 | 11kV | 496 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berekeley Vale - Pnl.4 tripped on Earth Fault UG cable fault between S18446 Sw/B to S183232 Sw/A and S14766 Sw/A See 1717429 1717430 | December | 2019 | 2020Q2 | 2020 | ZN12690:PA4 | ZN12690:PA4 | ZN12690/000004 | CENTRAL COAST | UG | Not Veg | 2019-12-26 | N | 49.6 | N | 5 | N | N | 1.1101 | 39.4971 | 362.4622
[7 empty] | 3444 | 1443 | 1716026 | 2019-12-26 19:58 | 2019-12-26 21:20 | 82 | 11kV | 656 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT13310 Reeves Wirrinda 0.5 - footpath phase HOD found blown Fatigue | December | 2019 | 2020Q2 | 2020 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2019-12-26 | N | 82 | N | 5 | N | N | 1.1101 | 39.4971 | 479.3855
[7 empty] | 3552 | 2513 | 1716025 | 2019-12-26 19:40 | 2019-12-26 21:30 | 110 | 11kV | 5610 | 51 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | No Weather Impact | N | LID 196351 B phase line fuse 5254 found blown with 3.15A fuse, replaced with 31.5A(correct size)supply on 2130. Only 1 x 3 phase sub 78756 on spur affected | December | 2019 | 2020Q2 | 2020 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2019-12-26 | N | 110 | N | 5 | N | N | 1.1101 | 39.4971 | 4099.6225
[7 empty] | 3759 | 4669 | 1716043 | 2019-12-27 00:50 | 2019-12-27 01:25 | 35 | 11kV | 2835 | 81 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | No Weather Impact | N | LID 196352 Sub isolated to repoair hot joint at top of DOLF.supply restored 0125. | December | 2019 | 2020Q2 | 2020 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | Unknown | Not Veg | 2019-12-27 | N | 35 | N | 3 | N | N | 1.1101 | 39.4971 | 2071.7344
[7 empty] | 4581 | 12967 | 1716047 | 2019-12-27 01:15 | 2019-12-27 02:19 | 64 | 11kV | 33792 | 528 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn1673 Turramurra - Pnl.19 tripped on: C phase IOC Possum caused flashover at PT1809 | December | 2019 | 2020Q2 | 2020 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | OH | Not Veg | 2019-12-27 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 24694.1969
[7 empty] | 5232 | 19340 | 1716056 | 2019-12-27 06:36 | 2019-12-27 07:17 | 41.45 | 11kV | 23875.2 | 576 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | IR50096 Tonkiss Pacific - tripped Abnormal: LB40053 closed with Open bonds near LB77831 Tree branch on mains near PT12862 | December | 2019 | 2020Q2 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2019-12-27 | N | 41.45 | N | 3 | N | N | 1.1101 | 39.4971 | 17447.292
[7 empty] | 3859 | 5585 | 1716231 | 2019-12-28 04:04 | 2019-12-28 04:52 | 48 | 11kV | 74112 | 1544 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S9550 Gwawley Bay Panel 3 tripped on Relays: A and B phase Earth Fauklt and IOC Signals; CB3 Open 11kV trip, TX3 Group Earth Abnormal Switching: S9669 SW/B Closed, S9875 SWA open Cause:Fresh dead bat found in Endeavour St Near Evelyn. See OMS 1721287 1716230/231/232/233/234/235/236/237 | December | 2019 | 2020Q2 | 2020 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | OH | Not Veg | 2019-12-28 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 54158.8637
[7 empty] | 5148 | 18588 | 1716251 | 2019-12-28 14:43 | 2019-12-28 16:04 | 80.8833 | 11kV | 485.3 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 196365 Interrupt to repair broken tie wires LOCATION IS POLE NUMBERS OR60768 AND OR60672 KNOWN AS B63 NELSON BAY ROAD TIE WIRES ARE BROKEN ON 11 KV DIST WIRES NEAREST HOUSE WHICH IS OPPOSITE LOCATION IS 5082 NELSON BAY ROAD | December | 2019 | 2020Q2 | 2020 | 242:81533 | 242:81533 | ZN00242/081533 | PORT STEPHENS | OH | Not Veg | 2019-12-28 | N | 80.8833 | N | 5 | N | N | 1.1101 | 39.4971 | 354.6429
[7 empty] | 3813 | 5144 | 1714688 | 2019-12-21 07:14 | 2019-12-28 17:23 | 10689 | 11kV | 90971 | 560 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill - Pnl.25 tripped on: 50NT, 51N EFIs: S8713 CP396 S5107 UG cable fault between S5107, S6570 tee S77801 & S1604 Note: Jointers couldn't get access to site to repair hence long duration for tee off subs. See 1720591 1720592 | December | 2019 | 2020Q2 | 2020 | ZN35900:PA25 | ZN3472:PA7 | ZN03472/000007 | CUMBERLAND | UG | Not Veg | 2019-12-21 | N | 162.4482 | N | 11 | N | N | 1.1101 | 39.4971 | 66478.9236
[7 empty] | 4156 | 8870 | 1716342 | 2019-12-28 19:56 | 2019-12-28 20:35 | 39.05 | 11kV | 3084.95 | 79 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 196367 Aaron Richardson assigned replaced C phase 40 amp hv fuse power restored 2035 | December | 2019 | 2020Q2 | 2020 | 513:83503 | 513:83503 | ZN00513/083503 | SINGLETON | OH | Not Veg | 2019-12-28 | N | 39.05 | N | 5 | N | N | 1.1101 | 39.4971 | 2254.3905
[7 empty] | 4143 | 8636 | 1716358 | 2019-12-28 22:04 | 2019-12-28 23:00 | 56 | 11kV | 280 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196368 B phase 10 Amp Fuse, substation DOLF. Fuse replaced has been replaced and supply restored | December | 2019 | 2020Q2 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2019-12-28 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 4379 | 10835 | 1716360 | 2019-12-28 22:26 | 2019-12-29 00:18 | 112 | 11kV | 185672 | 1820 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1648 Enfield 11kV Panel 8 tripped on Relays: Earth Fault and EFI Signals: 11kV CB.8 Open, TX1 Group Earth Cause: 11kV UG fault from SW/A @ S46336 to SW/B @ S136 Sum Ave See OMS 1721290 1721291 1716362 1716360 | December | 2019 | 2020Q2 | 2020 | ZN1648:PA8 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2019-12-28 | N | 102.0176 | N | 5 | N | N | 1.1101 | 39.4971 | 135683.6212
[7 empty] | 3708 | 4031 | 1716370 | 2019-12-29 01:13 | 2019-12-29 05:50 | 277 | 11kV | 10614 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196369 1 Fault operations Pole Mounted RAGCB, Sensitive Earth Fault No Cause found, not storm conditions | December | 2019 | 2020Q2 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2019-12-29 | N | 196.5556 | N | 5 | N | N | 1.1101 | 39.4971 | 7756.3981
[7 empty] | 3378 | 779 | 1716426 | 2019-12-29 17:20 | 2019-12-29 17:45 | 25.5 | 11kV | 4411.5 | 173 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 196370 C phase 40 Amp Substation DOLF No cuase found, not storm conditions | December | 2019 | 2020Q2 | 2020 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Veg | 2019-12-29 | N | 25.5 | N | 5 | N | N | 1.1101 | 39.4971 | 3223.7941
[7 empty] | 3714 | 4068 | 1716423 | 2019-12-29 19:07 | 2019-12-29 19:13 | 6 | 11kV | 360 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn2400 Berowra - Pnl.11 - CP1238 interrupted to remove tree branch from OH mains | December | 2019 | 2020Q2 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2019-12-29 | N | 6 | N | 5 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 5138 | 18497 | 1716440 | 2019-12-29 19:15 | 2019-12-29 20:25 | 70 | 11kV | 136034 | 2013 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Zn14892 - Charmhaven - Pnl.16 tripped on; SEL Centre phase bond burnt off LK41517 See 1717421 1717422 | December | 2019 | 2020Q2 | 2020 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2019-12-29 | N | 67.5777 | N | 5 | N | N | 1.1101 | 39.4971 | 99409.6349
[7 empty] | 4890 | 15834 | 1716461 | 2019-12-29 23:32 | 2019-12-30 03:06 | 214 | 11kV | 427294 | 2419 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn10995 Riverwood Panel 2 tripped reclosed tripped and lockedout on Relays: C phase IOC, Earth Fauklt, EFI, Timing and Lockout Cause: Section of 11kV feeder from AB30068 to S10987 tee PT10828 is defective See OMS1721525 1721526 1721527 1721532 1751533 1717137 1716461 1716463 | December | 2019 | 2020Q2 | 2020 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | UG | Not Veg | 2019-12-29 | N | 176.6408 | N | 5 | N | N | 1.1101 | 39.4971 | 312253.8522
[7 empty] | 4513 | 12194 | 1716523 | 2019-12-30 11:16 | 2019-12-30 14:34 | 198 | 11kV | 103380 | 1188 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3922 Drummoyne - Pnl.17 tripped on: B Phase O/C UG cable fault from S8369 to S49979 Note: EFI @ S49979 Flair 21D type. Due to being at an open point, not enough charge current to keep it working hence no indication. Open point has been moved See 1720550 1720551 1720553 1720552 | December | 2019 | 2020Q2 | 2020 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2019-12-30 | N | 87.0202 | N | 3 | N | N | 1.1101 | 39.4971 | 75547.0548
[7 empty] | 3470 | 1684 | 1716563 | 2019-12-30 14:57 | 2019-12-30 15:33 | 36 | 11kV | 35388 | 983 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.7 tripped on: O/C Abnormal: LB61759 closed with AB40372 Open & Defective Tree branch removed by DOp | December | 2019 | 2020Q2 | 2020 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2019-12-30 | N | 36 | N | 3 | N | N | 1.1101 | 39.4971 | 25860.5066
[7 empty] | 5282 | 19710 | 1716658 | 2019-12-31 09:18 | 2019-12-31 10:58 | 100 | 11kV | 132958 | 1585 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35555 Croydon - Pnl.16 tripped on: A Phase O/C UG cable fault between S3259 and S7997 See 1720506 1720508 | December | 2019 | 2020Q2 | 2020 | ZN35555:PA16 | ZN35555:PA16 | ZN35555/000016 | INNER WEST | UG | Not Veg | 2019-12-31 | N | 83.8852 | N | 9 | N | N | 1.1101 | 39.4971 | 97161.7848
[7 empty] | 3466 | 1654 | 1716659 | 2019-12-31 09:24 | 2019-12-31 12:20 | 176 | 11kV | 528 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT12629 Goolara Niclins - roadside HDO fuse mech failed | December | 2019 | 2020Q2 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2019-12-31 | N | 176 | N | 9 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 4530 | 12318 | 1716733 | 2019-12-31 14:25 | 2019-12-31 16:18 | 113 | 11kV | 10848 | 96 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | REC559 Cobah Rd tripped on : OC Abnormal: AB1237 open with LB62159 closed Tree branch clashed mains at pole AR95097 (Bloodwood Rd and Cobah) Tree branch caused grass fire which was put out by RFS | December | 2019 | 2020Q2 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2019-12-31 | N | 113 | N | 9 | N | N | 1.1101 | 39.4971 | 7927.3984
[7 empty] | 3395 | 934 | 1716762 | 2019-12-31 15:35 | 2019-12-31 17:32 | 117 | 11kV | 198783 | 1699 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn12640 Umina - Pnl.10 tripped on: A Phase IOC UG cable fault between Pnl.10 and S18775 Sw/A | December | 2019 | 2020Q2 | 2020 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | UG | Not Veg | 2019-12-31 | N | 117 | N | 9 | N | N | 1.1101 | 39.4971 | 145264.7533
[7 empty] | 3837 | 5398 | 1716819 | 2019-12-31 17:15 | 2019-12-31 17:50 | 35 | 11kV | 210 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 196382 Tree leaning against mains at pole BQ80004 | December | 2019 | 2020Q2 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2019-12-31 | N | 35 | N | 9 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 4929 | 16405 | 1716796 | 2019-12-31 16:06 | 2019-12-31 19:50 | 224 | 11kV | 224 | 1 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Hot >35C | N | LID 196383 Substation DOLF 3rd Outage this month Removed bird from L/A and repaired insulation to prevent future animal issues. | December | 2019 | 2020Q2 | 2020 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Not Veg | 2019-12-31 | N | 224 | N | 9 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 4395 | 11010 | 1716769 | 2019-12-31 15:50 | 2019-12-31 20:19 | 269 | 11kV | 432525 | 2192 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn195 pymble - Pnl.22 tripped on: Earth Fault Field EFIs: S8187 S7031 (S35973 S2333 S35667 S8711 - Did not operate and should have) Abnormal: DMA on Pnl.9 and Pnl.12 (S2542 Sw/B closed with S47348 Sw/A Open + LB224 Closed with LB79087 Open) UG cable fault between S8711 Sw/B and S5985 Sw/A. End box damage at S5985. See 1717454 1717456 1717458 1717460 | December | 2019 | 2020Q2 | 2020 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2019-12-31 | N | 197.3198 | N | 9 | N | N | 1.1101 | 39.4971 | 316076.5127
[7 empty] | 4551 | 12560 | 1716909 | 2019-12-31 19:43 | 2019-12-31 20:19 | 36 | 11kV | 30636 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12570 Avoca - Pnl.34 tripped on A & B phase IOC Tree branch on mains outside 29 Francis St North Avoca. | December | 2019 | 2020Q2 | 2020 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2019-12-31 | N | 36 | N | 9 | N | N | 1.1101 | 39.4971 | 22387.8852
[7 empty] | 4241 | 9693 | 1716891 | 2019-12-31 19:07 | 2019-12-31 21:07 | 120 | 11kV | 102600 | 855 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Recloser Cp62226 Connells Terry Opened on OC CauseL: Tree branch on OH near PT78744 See OMS 1716891 1716917 1716894 | December | 2019 | 2020Q2 | 2020 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2019-12-31 | N | 120 | N | 9 | N | N | 1.1101 | 39.4971 | 74977.0538
[7 empty] | 4575 | 12889 | 1717060 | 2020-01-01 12:09 | 2020-01-01 12:56 | 47 | 11kV | 37689 | 1335 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | No Weather Impact | N | LID 206394 2 fault operations 3 phase Instantaneous Overcurrent 11kV wires down and pole burnt due to bushfire pole HW-30394. dq Excluded OMS 1717059 | January | 2020 | 2020Q3 | 2020 | 239:82133 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Veg | 2020-01-01 | N | 28.2315 | N | 6 | N | N | 1.1101 | 39.4971 | 27542.0096
[7 empty] | 3850 | 5494 | 1716553 | 2019-12-30 13:47 | 2020-01-01 17:10 | 3083 | 11kV | 5207 | 26 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn167 Auburn - Pnl.15 tripped on: IOC Field EFIs: S46634 & S46633 - No EFI @ S2421 UG cable fault between S46633 Sw/A to S6166 to S2421 tee S4213 Note: S4213 is non // - delayed restoration until cable repaired See 1720500 1720501 | December | 2019 | 2020Q2 | 2020 | ZN167:PA15 | ZN167:PA15 | ZN00167/000015 | PARRAMATTA | UG | Not Veg | 2019-12-30 | N | 200.2692 | N | 3 | N | N | 1.1101 | 39.4971 | 3805.122
[7 empty] | 3324 | 324 | 1717106 | 2020-01-01 18:19 | 2020-01-01 19:45 | 86 | 11kV | 86 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206396 A Phase 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-01 | N | 86 | N | 6 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 5296 | 19811 | 1717100 | 2020-01-01 17:38 | 2020-01-01 20:15 | 156.5333 | 11kV | 3600.2667 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206397 A and B Phase 31.5 Amp Line DOLFS CC1: 22-"Refer to SOp" | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-01 | N | 156.5333 | N | 6 | N | N | 1.1101 | 39.4971 | 2630.9687
[7 empty] | 4972 | 16825 | 1717120 | 2020-01-01 20:24 | 2020-01-01 21:20 | 56 | 11kV | 56 | 1 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV Panel 22 PT18326 JAMES DUNLOP FIGTREE 11kv HDO roadside phase 16S fuse blown Tree bark on surge arrestor See 1719026 ex 1717120 | January | 2020 | 2020Q3 | 2020 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2020-01-01 | N | 56 | N | 6 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 5026 | 17499 | 1717135 | 2020-01-01 21:41 | 2020-01-01 22:40 | 59 | 11kV | 88698 | 1608 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.30 tripped on: Earth Fault UG cable fault between S5548 Sw/B and S255 Sw/C See 1719036 1719037 | January | 2020 | 2020Q3 | 2020 | ZN2835:PA30 | ZN2835:PA30 | ZN02835/000030 | CANADA BAY | UG | Not Veg | 2020-01-01 | N | 55.1604 | N | 6 | N | N | 1.1101 | 39.4971 | 64817.8823
[7 empty] | 5336 | 20249 | 1717145 | 2020-01-01 22:13 | 2020-01-01 22:58 | 45.2167 | 11kV | 1537.3667 | 34 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206399 B Phase 20 Amp substation DOLF Dead possum found at sub pole Readings as left 246V 75A, 95A, 135A | January | 2020 | 2020Q3 | 2020 | 206:34438 | 206:34438 | ZN00206/034438 | LAKE MACQUARIE | OH | Not Veg | 2020-01-01 | N | 45.2167 | N | 6 | N | N | 1.1101 | 39.4971 | 1123.4622
[7 empty] | 4428 | 11298 | 1717310 | 2020-01-02 10:00 | 2020-01-02 10:34 | 34 | 11kV | 5474 | 161 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 206416 Broken Live Line Clamp at Sub 51526 | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-01-02 | N | 34 | N | 10 | N | N | 1.1101 | 39.4971 | 4000.2377
[7 empty] | 4443 | 11426 | 1717419 | 2020-01-02 13:10 | 2020-01-02 16:50 | 220 | 11kV | 21340 | 97 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 206420 faulty xarm IU-80507 section isolated Repairs completed Excluded oms 1717419 1717423 | January | 2020 | 2020Q3 | 2020 | 224:80332 | 224:80332 | ZN00224/080332 | LAKE MACQUARIE | OH | Not Veg | 2020-01-02 | N | 220 | N | 10 | N | N | 1.1101 | 39.4971 | 15594.6426
[7 empty] | 4743 | 14451 | 1717202 | 2020-01-02 03:00 | 2020-01-02 17:15 | 855 | 11kV | 83288 | 1615 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 206401 2 fault operations, A Phase, Earth Fault Broken xarm pole IU-50003 and 33kV into LV at pole IU-80343, isolated at sub 21671 RH LVF (see OMS 1718996) for repairs. Fire brigade extinguised pole top fire pole IU-80246 33kV Frd 735 & 11Kv Fdr 80346 on pole Excluded OMS 1717202 | January | 2020 | 2020Q3 | 2020 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2020-01-02 | N | 51.5715 | N | 10 | N | N | 1.1101 | 39.4971 | 60864.4138
[7 empty] | 4111 | 8296 | 1717168 | 2020-01-02 01:05 | 2020-01-02 17:40 | 995 | 33kV Distribution | 5907 | 17 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 206400 pole fire which brought 33kV mains into LV at pole IU-80343. No 1 prot = A phase to earth, Multi trip No 2 prot = 51N, multi trip Excluded OMS 1717168 | January | 2020 | 2020Q3 | 2020 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Not Veg | 2020-01-02 | N | 347.4706 | N | 10 | N | N | 1.1101 | 39.4971 | 4316.6614
[7 empty] | 4645 | 13579 | 1717498 | 2020-01-02 16:35 | 2020-01-02 17:45 | 70 | 11kV | 26238 | 421 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Pacquarie Park Panel 10 Tripped Cause: 11kV UG cable fault from S64450 to S7979 to S7889 See OMS 1720601 1720602 1717498 | January | 2020 | 2020Q3 | 2020 | ZN8000:PA10 | ZN8000:PA10 | ZN08000/000010 | RYDE | UG | Not Veg | 2020-01-02 | N | 62.323 | N | 10 | N | N | 1.1101 | 39.4971 | 19173.9565
[7 empty] | 4796 | 14991 | 1717233 | 2020-01-02 07:16 | 2020-01-02 19:15 | 719 | 11kV | 52439 | 73 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 206413 Fire Brigade reports: CAD-001501 pole on fire at top X-arm replaced Pole IU-20949 | January | 2020 | 2020Q3 | 2020 | 216:10724 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2020-01-02 | N | 718.3425 | N | 10 | N | N | 1.1101 | 39.4971 | 38320.8745
[7 empty] | 5186 | 18854 | 1718971 | 2020-01-02 16:28 | 2020-01-02 20:40 | 252 | 11kV | 77364 | 307 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206411 33kV pole fire IU-80343 33kV into LV - refer to OMS 1718944 and LID 206411 for 33kV event Sw 80255 A prot = inst E/F B prot = L1 E/F 3.3km Sw 34412 | January | 2020 | 2020Q3 | 2020 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2020-01-02 | N | 252 | N | 10 | N | N | 1.1101 | 39.4971 | 56535.3293
[7 empty] | 4345 | 10565 | 1717478 | 2020-01-02 15:54 | 2020-01-02 22:30 | 396 | 11kV | 19008 | 48 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 206424 33kV crossarm broken at pole JS-46015. See also #206424 for associated 11kV Fdr outage. Targets Sw 83241 Tomago Sw Stn: Aprot - Line Diff L1-L2 Bprot - Dist. Z1 A/Bph (no distance available) Sw 81204 Raymond Terrace Z/S: Aprot - Line Diff L1-L2 Bprot - L/O Fdr Rcl relay. | January | 2020 | 2020Q3 | 2020 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2020-01-02 | N | 396 | N | 10 | N | N | 1.1101 | 39.4971 | 13890.4858
[7 empty] | 5279 | 19685 | 1720400 | 2020-01-03 00:05 | 2020-01-03 00:41 | 36 | 11kV | 72 | 2 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 206430 Broken 33kV insulator pole BM-20059. Isolated to repair But job cancelled due to no access to 33kv ABS 32112 | January | 2020 | 2020Q3 | 2020 | 514:18156 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2020-01-03 | N | 36 | N | 7 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 4768 | 14730 | 1717369 | 2020-01-02 11:22 | 2020-01-03 01:38 | 856 | 11kV | 69336 | 81 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 206418 11kV Fdr isolated to repair broken 33kV crossarm at pole KT-20007. See also report #206405. | January | 2020 | 2020Q3 | 2020 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2020-01-02 | N | 856 | N | 10 | N | N | 1.1101 | 39.4971 | 50668.7037
[7 empty] | 4338 | 10495 | 1717525 | 2020-01-02 18:53 | 2020-01-03 15:23 | 1230 | 11kV | 173430 | 141 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206428 1 fault operation Overcurrent Mains down between poles TC-20025 & TC -20026. Fallen tree following recent fires | January | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-01-02 | N | 1230 | N | 10 | N | N | 1.1101 | 39.4971 | 126737.5287
[7 empty] | 3839 | 5426 | 1717722 | 2020-01-03 13:52 | 2020-01-03 15:35 | 103 | 11kV | 103 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206435 Single phase DOLF : 10 Amp Excluded OMS 1717722 | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-01-03 | N | 103 | N | 7 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 4145 | 8640 | 1717697 | 2020-01-03 14:29 | 2020-01-03 16:05 | 96 | 11kV | 96 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 206436 3 phase DOLF : 10 Amp Melted LV mains between trans & LVFs. | January | 2020 | 2020Q3 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2020-01-03 | N | 96 | N | 7 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 5213 | 19159 | 1717726 | 2020-01-03 13:58 | 2020-01-03 18:04 | 246 | 11kV | 135766 | 1146 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.5 tripped, reclosed & tripped on: O/C Field EFIs: S6360, S6525 S709 S4954 S4663 S4559 Pole fire on UGOH PT64853 See 1718908 1718909 1718910 1718914 | January | 2020 | 2020Q3 | 2020 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-01-03 | N | 118.4695 | N | 7 | N | N | 1.1101 | 39.4971 | 99213.7884
[7 empty] | 4119 | 8372 | 1717799 | 2020-01-03 18:26 | 2020-01-03 19:33 | 67 | 11kV | 30765 | 466 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.17 tripped on: Earth fault Field EFIs: S62021 S5050 S7662 UG cable fault between S7662 Sw/B and S49793 Sw/B (N/O) and S5115 Sw/B (N/O) See 1718936 1718937 1718938 | January | 2020 | 2020Q3 | 2020 | ZN2466:PA17 | ZN36000:PA10 | ZN36000/000010 | STRATHFIELD | UG | Not Veg | 2020-01-03 | N | 66.0193 | N | 7 | N | N | 1.1101 | 39.4971 | 22482.1546
[7 empty] | 4918 | 16222 | 1717811 | 2020-01-03 19:33 | 2020-01-03 20:21 | 48 | 11kV | 4907 | 119 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.8 tripped on: IOC UG cable fault between S9411 Sw/D to S9413 Sw/A See 1721508 1721509 | January | 2020 | 2020Q3 | 2020 | ZN9035:PA8 | ZN9035:PA8 | ZN09035/000008 | SUTHERLAND | UG | Not Veg | 2020-01-03 | N | 41.2353 | N | 7 | N | N | 1.1101 | 39.4971 | 3585.8909
[7 empty] | 4001 | 7019 | 1717840 | 2020-01-03 23:13 | 2020-01-04 00:41 | 88 | 11kV | 2288 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206441 C Phase DOLF : 31 Amp loose earth wire touched HV dropper. sub maintenance required. Excluded oms 1717840 | January | 2020 | 2020Q3 | 2020 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Veg | 2020-01-03 | N | 88 | N | 7 | N | N | 1.1101 | 39.4971 | 1672.0029
[7 empty] | 4378 | 10831 | 1717843 | 2020-01-04 01:16 | 2020-01-04 02:44 | 88 | 11kV | 172480 | 1960 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN1673 Turramurra Panel 13 tripped on Relays: OC, EF, FC, UF, EFI Abnormal Switching: SW/B Closed at S8688, Turramurra Pa7 Front line feeder fault Cause: Possum found at the base of PT1561 Derwent Dalley B Phase HVDO Operated See OMS 1720113 1717844 1717843 | January | 2020 | 2020Q3 | 2020 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2020-01-04 | N | 88 | N | 17 | N | N | 1.1101 | 39.4971 | 126043.2967
[7 empty] | 4096 | 8142 | 1717924 | 2020-01-04 13:36 | 2020-01-04 15:34 | 118 | 11kV | 100165 | 1062 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At ZN 14892 Charmhaven 11kv feeder Panel No : 1 "Mataram Haven" feeder TRIPPED and RECLOSED and locked out on: RELAYS : B & C phase timed O/C , C phase O/C, minor alarm, reclose timing and lock out EFI and E/F check SIGNALS : Zone earth and Tx 1 group earth Cause UGOH Fault short circuit. Section of 11kV feeder from 11kV USL 42035 to S.18212 Woodcutters Tuckaroo to S. 18378 Hiawatha Mataram. UGOH fault. NOTE: Dop Reports HV into LV. impact was at Link Switch off pole DD8. Customers close to HV into LV dist checked and all ok. Dop advised safe to restore supply. | January | 2020 | 2020Q3 | 2020 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | Unknown | Unknown | 2020-01-04 | N | 94.3173 | N | 17 | N | N | 1.1101 | 39.4971 | 73197.6276
[7 empty] | 3807 | 5097 | 1717933 | 2020-01-04 14:04 | 2020-01-04 16:08 | 124 | 11kV | 334143 | 2790 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN13000 LAKE MUNMORAH 11kV CB Panel 5 tripped, reclosed and locked out on: Relays: 5Righ: Earth Fault, EFI, Timing and lockout Signals: 11kv trip Abnormal: LB40566 open, LB40955 closed LB49620 Closed Fdr 680 Vales Point open Cause: UG Fault from S14743 to S18069 EFI @ S18069 down See 1720198,9 ex 1717939,72 | January | 2020 | 2020Q3 | 2020 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | UG | Not Veg | 2020-01-04 | N | 119.7645 | N | 17 | N | N | 1.1101 | 39.4971 | 244181.8488
[7 empty] | 4579 | 12931 | 1717971 | 2020-01-04 14:46 | 2020-01-04 16:45 | 119 | 11kV | 3213 | 27 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | PT12059 Glenrock Brisbane Water - Roadside HDO blown Transformer failure. Restored via LV // | January | 2020 | 2020Q3 | 2020 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2020-01-04 | N | 119 | N | 17 | N | N | 1.1101 | 39.4971 | 2347.9656
[7 empty] | 4970 | 16817 | 1718136 | 2020-01-04 18:46 | 2020-01-04 18:58 | 12 | 11kV | 7020 | 585 | HV | Overload | Utility Process Issue | O/H Conductor Unknown | Unplanned | Hot >35C | N | REC78525 Opened due to overload on OH mains. Abnormal: S18470 Sw/A Closed with USL41517 Open and Defective | January | 2020 | 2020Q3 | 2020 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2020-01-04 | N | 12 | N | 17 | N | N | 1.1101 | 39.4971 | 5130.0089
[7 empty] | 4953 | 16632 | 1718053 | 2020-01-04 17:36 | 2020-01-04 19:05 | 89 | 11kV | 209756 | 2600 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN690 Campsie 11kV Panel 4 tripped on Relays: C phase Overload, EFI, Fault Check Signals: 11kV CB4 Open, 11kV Trip, TX2 Group Earth Abnromal Switching: Closed SW/A @ S2740 Charleston Ave, Open SW/D @ S310 Cause: Cable fault between S2532 - CP1555 - S310 See OMS 1720424 1718053 1718057 1718107 | January | 2020 | 2020Q3 | 2020 | ZN690:PA4 | ZN690:PA4 | ZN00690/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-01-04 | N | 80.6754 | N | 17 | N | N | 1.1101 | 39.4971 | 153283.498
[7 empty] | 4308 | 10294 | 1718080 | 2020-01-04 17:58 | 2020-01-04 19:51 | 113 | 11kV | 192790 | 1867 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN847 Hornsby Panel 7 tripped on Relays: Earth Fault, EFI, Trip Signals: Zone Earth, TX2 Group Earth 11kV Trip. Abnormal Switching: CP875 Closed, SW/B at S8841 Nursery Frederick Open Cause: Front line feeder fault from Pa7 at Hornsby to SW/A @ S8497 See OMS 1720216 1720217 1720218 1718080 1718081 | January | 2020 | 2020Q3 | 2020 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | UG | Not Veg | 2020-01-04 | N | 103.2619 | N | 17 | N | N | 1.1101 | 39.4971 | 140885.2457
[7 empty] | 4201 | 9313 | 1718083 | 2020-01-04 18:19 | 2020-01-04 20:56 | 157.4167 | 11kV | 51475.25 | 327 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 206450 broken tapping cph ABS 64202 Excluded broken tapping cph ABS 64202 oms 1718083oms 1718083 CC1: 22-"Refer to SOp" | January | 2020 | 2020Q3 | 2020 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2020-01-04 | N | 157.4167 | N | 17 | N | N | 1.1101 | 39.4971 | 37616.5944
[7 empty] | 5042 | 17689 | 1718090 | 2020-01-04 18:07 | 2020-01-04 22:20 | 253 | 11kV | 44712 | 219 | HV | Overload LV Parallel | Utility Process Issue | O/H Link | Unplanned | Hot >35C | N | At PT6175 Hart Felton 400A fuse blown on B phase of distributor 1 At S2525 Mobray Girraween 400A fuse blown on A and B phase of distributor 2 At S8488 Hatfield Mobray 400A fuse blown on B phase of distributor 3 At PT1953 Beaconsfield Mooney - PT OOS and defective. Supplied via LV parallel Cause: LV parallel failed on Hot day See OMS 1719873 1719870 1719868 1719866 1718236 1718114 1718095 1718090 | January | 2020 | 2020Q3 | 2020 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Not Veg | 2020-01-04 | N | 204.1644 | N | 17 | N | N | 1.1101 | 39.4971 | 32674.2108
[7 empty] | 4468 | 11656 | 1718159 | 2020-01-04 19:49 | 2020-01-04 22:30 | 161 | 11kV | 188814 | 1251 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | LID 206454 1 fault operation Earth Fault Cable fault between Sw28714/29424/28329 Prot A-E Excluded OMS 1718159 | January | 2020 | 2020Q3 | 2020 | 213:33773 | 213:33773 | ZN00213/033773 | NEWCASTLE | UG | Not Veg | 2020-01-04 | N | 150.9305 | N | 17 | N | N | 1.1101 | 39.4971 | 137979.7021
[7 empty] | 3957 | 6485 | 1718204 | 2020-01-04 21:58 | 2020-01-04 23:48 | 110 | 11kV | 89430 | 813 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex 9118 Cronulla Panel 11 Recloser CP35756 Bundeena tripped, reclosed tripped and locked out on OC and Lockout Cause: Branch fallen through 11kV NO Ab35236 - No damage caused | January | 2020 | 2020Q3 | 2020 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2020-01-04 | N | 110 | N | 17 | N | N | 1.1101 | 39.4971 | 65352.8063
[7 empty] | 4010 | 7105 | 1718129 | 2020-01-04 18:57 | 2020-01-05 00:45 | 348 | 11kV | 22272 | 64 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 206456 B Phase interrupt to repair Bph RH LVF to bundle connection Excluded oms 1718129 | January | 2020 | 2020Q3 | 2020 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2020-01-04 | N | 348 | N | 17 | N | N | 1.1101 | 39.4971 | 16275.7207
[7 empty] | 5299 | 19829 | 1718300 | 2020-01-04 23:16 | 2020-01-05 01:00 | 104 | 11kV | 119506 | 1736 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12600 Lisarow - Pnl.3 tripped on: Timed Earth Fault OH connection came away from UGOH between LB44819 and LB45174 to Sw/A 14262 tee PT11072. See 1719881 1719882 1719883 179886 | January | 2020 | 2020Q3 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2020-01-04 | N | 68.8399 | N | 17 | N | N | 1.1101 | 39.4971 | 87331.46
[7 empty] | 5086 | 18158 | 1718265 | 2020-01-04 22:40 | 2020-01-05 01:19 | 159 | 11kV | 138012 | 868 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S9252 Jannali Panel 25 Woronora Tripped, reclosed tripped and locked out on Cause; Tree on OH adjacent CP35362 See OMS 1718265 1718286 | January | 2020 | 2020Q3 | 2020 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Veg | 2020-01-04 | N | 159 | N | 17 | N | N | 1.1101 | 39.4971 | 100855.0989
[7 empty] | 3352 | 601 | 1718283 | 2020-01-04 22:59 | 2020-01-05 01:23 | 144 | 11kV | 193152 | 1516 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S10991 Blakehurst Panel 1 Tripped, reclosed tripped and locked out on Relays: C phase OC, Lockout and Timing Signals: 11kV Trip Cause: possible tree branch on 11kv OH due to strong winds.DOP patroled nothing found. See OMS 1718946 1718947 1718306 1718292 1718289 1718283 | January | 2020 | 2020Q3 | 2020 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Veg | 2020-01-04 | N | 127.409 | N | 17 | N | N | 1.1101 | 39.4971 | 141149.7846
[7 empty] | 3737 | 4341 | 1718344 | 2020-01-04 22:53 | 2020-01-05 04:06 | 313 | 11kV | 482637 | 2781 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At S10999 Kogarah Panel 10 tripped and reclosed on RelaysL A and B phase OC, Trip and Lockout Cause: Bond burnt off at LB62011- Dop patrolled feeder fandf nothing found | January | 2020 | 2020Q3 | 2020 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Not Veg | 2020-01-04 | N | 173.548 | N | 17 | N | N | 1.1101 | 39.4971 | 352696.8842
[7 empty] | 4528 | 12302 | 1717842 | 2020-01-05 00:11 | 2020-01-05 04:49 | 278 | 11kV | 562265 | 2118 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | ZN12610 LONG JETTY 11kV CB Panel 13 'Blue Bay' tripped and locked out on Relays: SEF EFI: Nil Cause: UG Fault Fault UG OC in section of UG from UGOH to S18424 All cust volts checked ok See 1720212,3,4 ex 1718353 | January | 2020 | 2020Q3 | 2020 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | UG | Not Veg | 2020-01-05 | N | 265.4698 | N | 13 | N | N | 1.1101 | 39.4971 | 410886.678
[7 empty] | 4658 | 13672 | 1718403 | 2020-01-05 01:25 | 2020-01-05 06:30 | 305 | 11kV | 73505 | 241 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN12690 BERKELEY VALE section of 11kV Panel 3 RE41630 Keren Bundilla Opened & locked out Removed tree/branch from OH mains adjacent to AB44498 | January | 2020 | 2020Q3 | 2020 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Veg | 2020-01-05 | N | 305 | N | 13 | N | N | 1.1101 | 39.4971 | 53715.286
[7 empty] | 5290 | 19761 | 1718445 | 2020-01-05 07:00 | 2020-01-05 08:25 | 85 | 11kV | 6970 | 82 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | At S9097 Large Tree branch on HV and LV mains adjacent to PT9963 Willarong Waring. Feeder Isolated top remove tree and make repairs see OMS 1719005 1718446 1718445 | January | 2020 | 2020Q3 | 2020 | ZN9118:PA17 | ZN9118:PA17 | ZN09118/000017 | SUTHERLAND | OH | Not Veg | 2020-01-05 | N | 85 | N | 13 | N | N | 1.1101 | 39.4971 | 5093.4704
[7 empty] | 5114 | 18333 | 1718567 | 2020-01-05 12:16 | 2020-01-05 13:23 | 67 | 11kV | 719 | 11 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.4 tripped on 3 Phase O/C UG cable fault in front line section of feeder from Pnl.4 to S3376 to S4802 | January | 2020 | 2020Q3 | 2020 | ZN2466:PA4 | ZN36000:PA6 | ZN36000/000006 | PARRAMATTA | UG | Not Veg | 2020-01-05 | N | 65.3636 | N | 13 | N | N | 1.1101 | 39.4971 | 525.424
[7 empty] | 3565 | 2610 | 1718583 | 2020-01-05 13:53 | 2020-01-05 15:09 | 76 | 11kV | 16213 | 217 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.27 tripped on: B Phase Earth Fault UG cable fault between S8640, S5154 and S76931 | January | 2020 | 2020Q3 | 2020 | ZN188:PA27 | ZN188:PA27 | ZN00188/000027 | SYDNEY | UG | Not Veg | 2020-01-05 | N | 74.7143 | N | 13 | N | N | 1.1101 | 39.4971 | 11847.9822
[7 empty] | 3423 | 1226 | 1718260 | 2020-01-04 22:36 | 2020-01-05 16:30 | 1074 | 11kV | 2148 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S62659 Coward kent No.5 - 2 x 80Amps HV fuses operated Transformer failed | January | 2020 | 2020Q3 | 2020 | ZN630:PA19 | ZN630:PA19 | ZN00630/000019 | BAYSIDE | UG | Not Veg | 2020-01-04 | N | 1074 | N | 17 | N | N | 1.1101 | 39.4971 | 1569.695
[7 empty] | 4766 | 14700 | 1718577 | 2020-01-05 13:14 | 2020-01-05 17:35 | 261 | 11kV | 5481 | 21 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Ex Zn12580 Erina - Pnl.12 - Tree brought down mains between USL42282 and PT12035 (on Erina Valley Rd) | January | 2020 | 2020Q3 | 2020 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2020-01-05 | N | 261 | N | 13 | N | N | 1.1101 | 39.4971 | 4005.3531
[7 empty] | 3976 | 6668 | 1718613 | 2020-01-05 15:35 | 2020-01-05 17:38 | 123 | 11kV | 25629 | 228 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 206464 2 fault operations A & B Phase Overcurrent Fdr patrolled, no obvious signs of fault Prot A-Bph O/C 3041A Excluded oms 1718613 | January | 2020 | 2020Q3 | 2020 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-01-05 | N | 112.4079 | N | 13 | N | N | 1.1101 | 39.4971 | 18728.9173
[7 empty] | 4224 | 9507 | 1718661 | 2020-01-05 18:15 | 2020-01-05 19:44 | 89 | 11kV | 70036 | 1121 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 206465 1 fault operation C Phase Instantaneous Overcurrent Not sure if reclose is initiated from Instantanious protection but there did not appear to be a reclose on this occassion. No Fault was found after a complete patrol of the feeder. Excluded OMS 1718661 | January | 2020 | 2020Q3 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Veg | 2020-01-05 | N | 62.4764 | N | 13 | N | N | 1.1101 | 39.4971 | 51180.2431
[7 empty] | 5142 | 18511 | 1718682 | 2020-01-05 19:37 | 2020-01-05 21:28 | 111 | 11kV | 8658 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 206466 1 fault operation 3 phase Overcurrent Reclose disabled due to a Bushfire defect beyond it. FI flashing at pole AI-50031 Excluded OMS 1718682 | January | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-01-05 | N | 92.1064 | N | 13 | N | N | 1.1101 | 39.4971 | 6327.011
[7 empty] | 4667 | 13793 | 1718671 | 2020-01-05 21:05 | 2020-01-05 21:35 | 30.3167 | 11kV | 151.5833 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 206469 B & C Phase DOLF : 20 Amp Stick on mains adjacent sub 72998 Excluded OMS 1718671 | January | 2020 | 2020Q3 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-01-05 | N | 30.3167 | N | 13 | N | N | 1.1101 | 39.4971 | 110.7726
[7 empty] | 3505 | 2062 | 1718724 | 2020-01-05 22:16 | 2020-01-06 03:12 | 296 | 33kV Distribution | 4184 | 17 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 206471 interrupt to repair pole KT-70899 Excluded oms 1718724 | January | 2020 | 2020Q3 | 2020 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Not Veg | 2020-01-05 | N | 246.1176 | N | 13 | N | N | 1.1101 | 39.4971 | 3057.5438
[7 empty] | 3954 | 6471 | 1718703 | 2020-01-05 21:12 | 2020-01-06 04:10 | 418 | 11kV | 21758 | 332 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206481 1 fault operation Sensitive Earth Fault Wire down near pole IQ-61333 Excluded OMS 1718703 | January | 2020 | 2020Q3 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2020-01-05 | N | 65.5361 | N | 13 | N | N | 1.1101 | 39.4971 | 15900.1046
[7 empty] | 4592 | 13091 | 1718699 | 2020-01-05 22:10 | 2020-01-06 04:50 | 400 | 11kV | 55461 | 529 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | N | LID 206472 interrupt to repair burnt pole IU-70524 Excluded oms 1718699 | January | 2020 | 2020Q3 | 2020 | 224:80332 | 224:80332 | ZN00224/080332 | LAKE MACQUARIE | OH | Not Veg | 2020-01-05 | N | 104.8412 | N | 13 | N | N | 1.1101 | 39.4971 | 40529.263
[7 empty] | 3375 | 753 | 1718784 | 2020-01-06 08:40 | 2020-01-06 10:15 | 95 | 11kV | 570 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206478 A Phase DOLF : 10 Amp Excluded OMS 1718784 | January | 2020 | 2020Q3 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-01-06 | N | 95 | N | 12 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 3406 | 1059 | 1718894 | 2020-01-06 11:16 | 2020-01-06 12:52 | 96 | 11kV | 72704 | 768 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn195 Pymble - Pnl.25 tripped on: Earth Fault UG cable fault between S5239 and S7058 See 1721406 1721407 | January | 2020 | 2020Q3 | 2020 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | UG | Not Veg | 2020-01-06 | N | 94.6667 | N | 12 | N | N | 1.1101 | 39.4971 | 53129.9388
[7 empty] | 4584 | 13024 | 1718940 | 2020-01-06 12:27 | 2020-01-06 13:57 | 90 | 11kV | 3690 | 41 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35700 Port Botany -Pnl.13 tripped on: B phase O/C and Earth Fault UG cable fault in front line section of feeder from Pnl.13 to S49323 Sw/A | January | 2020 | 2020Q3 | 2020 | ZN35700:PA13 | ZN35700:PA13 | ZN35700/000013 | RANDWICK | UG | Not Veg | 2020-01-06 | N | 90 | N | 12 | N | N | 1.1101 | 39.4971 | 2696.5432
[7 empty] | 3567 | 2616 | 1718889 | 2020-01-06 14:00 | 2020-01-06 17:42 | 222 | 11kV | 47952 | 216 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 206496 interrupt sub 9532 & RH LVF sub 65023 to repair broken 33kV x-arm pole Jw-32000 Excluded oms 1718889 | January | 2020 | 2020Q3 | 2020 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2020-01-06 | N | 222 | N | 12 | N | N | 1.1101 | 39.4971 | 35041.9073
[7 empty] | 4248 | 9765 | 1719140 | 2020-01-06 18:08 | 2020-01-06 18:35 | 27 | 11kV | 216 | 8 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Lightning | N | PT12965 Teralba Wallarah 0.3 - Centre phase fuse operated Tree branch on PT between HV bushing and earthed tank | January | 2020 | 2020Q3 | 2020 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2020-01-06 | N | 27 | N | 12 | N | N | 1.1101 | 39.4971 | 157.8464
[7 empty] | 4807 | 15105 | 1719136 | 2020-01-06 17:58 | 2020-01-06 19:26 | 88 | 11kV | 174334 | 2124 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Epping - Pnl.31 tripped on: 50TN UG cable fault between S77441, S65872 and S4627 See 1721427 172428 | January | 2020 | 2020Q3 | 2020 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2020-01-06 | N | 82.0782 | N | 12 | N | N | 1.1101 | 39.4971 | 127398.1452
[7 empty] | 5334 | 20234 | 1719166 | 2020-01-06 18:53 | 2020-01-06 20:10 | 77 | 11kV | 4878 | 850 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn14144 Wamberal - Pnl.4 tripped & recloased on: 3 phase IOC @ PT12112 Wycombe Hastings - HDO blown Tree branch on PT12112 See 1720045 1720047 | January | 2020 | 2020Q3 | 2020 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2020-01-06 | N | 5.7388 | N | 12 | N | N | 1.1101 | 39.4971 | 3564.6985
[7 empty] | 4013 | 7157 | 1719088 | 2020-01-06 19:01 | 2020-01-06 21:55 | 174 | 11kV | 184859 | 2183 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | ZN12620 NORAVILLE 11kV CB Panel 7 'Main Brisbane' Relays: EF and EFI Signals: 11kv trip EFI: S14590 S14589 S48014 S14588 S14587 S14695 S14397 S14694 S14693 Cause: UG Fault from S14693 to S14692 Rain and lightning in the area DOp patrolled fdr and reset EFI See 1720203,5,6,7,8 Ex 1719088,323,420 | January | 2020 | 2020Q3 | 2020 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | UG | Not Veg | 2020-01-06 | N | 84.6812 | N | 12 | N | N | 1.1101 | 39.4971 | 135089.5048
[7 empty] | 4206 | 9346 | 1718735 | 2020-01-06 00:04 | 2020-01-06 22:53 | 1369 | 11kV | 38450 | 144 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206483 Pole fire IT-10453 and pole JS-70053 Excluded OMS 1718735 & 1719087 | January | 2020 | 2020Q3 | 2020 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2020-01-06 | N | 267.0139 | N | 12 | N | N | 1.1101 | 39.4971 | 28098.1259
[7 empty] | 4313 | 10331 | 1719658 | 2020-01-07 02:30 | 2020-01-07 02:45 | 15 | 11kV | 1155 | 77 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206502 interrupt to disconnect faulty service Excluded oms 1719507 | January | 2020 | 2020Q3 | 2020 | 214:8667 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Not Veg | 2020-01-07 | N | 15 | N | 20 | Y | Y | 1.1101 | 39.4971 | 844.0399
[7 empty] | 4291 | 10099 | 1719581 | 2020-01-07 01:16 | 2020-01-07 02:51 | 95.3667 | 11kV | 101851.6 | 1068 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn9037 Miranda Panel 2 Silvania heights tripped off on B and C phase OC timing and lockout Field EFI's NIL Cause Not ascertained Dop patrolled and nothing found. | January | 2020 | 2020Q3 | 2020 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2020-01-07 | N | 95.3667 | N | 20 | Y | Y | 1.1101 | 39.4971 | 74430.1452
[7 empty] | 3849 | 5487 | 1719576 | 2020-01-07 01:06 | 2020-01-07 03:00 | 114 | 11kV | 228451 | 2262 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At S10999 Kogarah Panel 11 tripped on Relays: B and C phase with earth fault check Cause: Suspect storm - mains to patrol see OMS 1720621 1720623 1719576 | January | 2020 | 2020Q3 | 2020 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Veg | 2020-01-07 | N | 100.9951 | N | 20 | Y | Y | 1.1101 | 39.4971 | 166945.2526
[7 empty] | 4981 | 16929 | 1719422 | 2020-01-06 22:50 | 2020-01-07 06:30 | 460 | 11kV | 95680 | 208 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 206499 Fdr de energised on request from EMSO after embers were falling off pole onto grass. Defective insulators on pole IV-50246 Section isolated for repairs. Excluded oms 1719422 | January | 2020 | 2020Q3 | 2020 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2020-01-06 | N | 460 | N | 12 | N | N | 1.1101 | 39.4971 | 69920.1219
[7 empty] | 5128 | 18421 | 1719546 | 2020-01-07 00:41 | 2020-01-07 07:50 | 429 | 11kV | 160810 | 1138 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 206505 interrupt 33 and 11kV broken crossarm/fire pole JU-55168 Excluded oms 1719546 | January | 2020 | 2020Q3 | 2020 | 256:80641 | 256:80641 | ZN00256/080641 | NEWCASTLE | OH | Not Veg | 2020-01-07 | N | 141.3093 | N | 20 | Y | Y | 1.1101 | 39.4971 | 117515.2049
[7 empty] | 3503 | 2053 | 1719760 | 2020-01-07 01:07 | 2020-01-07 10:18 | 551 | 11kV | 142763 | 837 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 206527 2 fault operations 3 phase Earth Fault broken x arm at pole JT 50343 Excluded OMS 1719575## dq | January | 2020 | 2020Q3 | 2020 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | OH | Not Veg | 2020-01-07 | N | 170.5651 | N | 20 | Y | Y | 1.1101 | 39.4971 | 104326.9896
[7 empty] | 4842 | 15483 | 1719974 | 2020-01-07 10:56 | 2020-01-07 12:20 | 84 | 11kV | 137360 | 1710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven - Pnl.6 tripped on: Earth Fault UG cable fault between Pnl.6 and S14890 Sw/B | January | 2020 | 2020Q3 | 2020 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2020-01-07 | N | 80.3275 | N | 20 | Y | Y | 1.1101 | 39.4971 | 100378.6366
[7 empty] | 5082 | 18135 | 1719718 | 2020-01-07 07:58 | 2020-01-07 13:10 | 312 | 33kV Distribution | 2531 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 206528 A & C phase tappings burnt off at ABS 61209. Fdr 80504 interupted by Sop at 0758hrs (see also LID 206530 for ABS 2747 fault) Excluded OMS 1719718 & 1719725##. | January | 2020 | 2020Q3 | 2020 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Not Veg | 2020-01-07 | N | 281.2222 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1849.5801
[7 empty] | 4403 | 11085 | 1720063 | 2020-01-07 12:45 | 2020-01-07 13:45 | 60 | 11kV | 180 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206521 B Phase DOLF : 10 Amp Excluded OMS 1720063 | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-01-07 | N | 60 | N | 20 | Y | Y | 1.1101 | 39.4971 | 131.5387
[7 empty] | 5247 | 19439 | 1719334 | 2020-01-06 21:03 | 2020-01-07 14:45 | 1062 | 11kV | 80712 | 76 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | PT11659 St james Blenheim - 3 HDO Operated Lightning arrestors failed | January | 2020 | 2020Q3 | 2020 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2020-01-06 | N | 1062 | N | 12 | N | N | 1.1101 | 39.4971 | 58981.949
[7 empty] | 4075 | 7891 | 1719842 | 2020-01-07 08:54 | 2020-01-07 14:45 | 351 | 11kV | 351 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 206522 Single phase DOLF : 10 Amp Lightning strike, LA s replaced 200A LVFs blown & also replaced | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-01-07 | N | 351 | N | 20 | Y | Y | 1.1101 | 39.4971 | 256.5004
[7 empty] | 3606 | 2812 | 1719817 | 2020-01-07 08:20 | 2020-01-07 15:45 | 445 | 11kV | 445 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206523 Aphase dropepr lead open curcuit at connection. Excluded OMS 1719817 | January | 2020 | 2020Q3 | 2020 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2020-01-07 | N | 445 | N | 20 | Y | Y | 1.1101 | 39.4971 | 325.1929
[7 empty] | 5120 | 18364 | 1719295 | 2020-01-07 11:05 | 2020-01-07 16:41 | 336 | 11kV | 45360 | 135 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 206509 No protecttion operation, all devices opened for safety or to allow repairs.. Excluded OMS 1719295 & 1719983. | January | 2020 | 2020Q3 | 2020 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2020-01-07 | N | 336 | N | 20 | Y | Y | 1.1101 | 39.4971 | 33147.7501
[7 empty] | 3945 | 6396 | 1720246 | 2020-01-07 15:14 | 2020-01-07 18:00 | 166 | 11kV | 37184 | 224 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 206532 2 fault operations Earth Fault Truck hit OHM adj sub 72687 | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-01-07 | N | 166 | N | 20 | Y | Y | 1.1101 | 39.4971 | 27172.9705
[7 empty] | 4732 | 14369 | 1719717 | 2020-01-07 06:40 | 2020-01-07 18:09 | 689 | 33kV Distribution | 3276 | 8 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | LID 206530 ABS 2747 tracking section of fdr interupted from ABS 48197 for safety due to defective abs 2747. Excluded OMS 1719743## see also LID report 206528 | January | 2020 | 2020Q3 | 2020 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Not Veg | 2020-01-07 | N | 409.5 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2394.0042
[7 empty] | 4836 | 15400 | 1720059 | 2020-01-07 14:00 | 2020-01-07 19:45 | 345 | 11kV | 22170 | 66 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206525 high into low sub 14223. HV dropper cable touching B phase LV at sub 14223 section isolated for repairs, Paul Lee check installations power restored Excluded OMS 1720081 AND 1720059 | January | 2020 | 2020Q3 | 2020 | 235:2728 | 235:2728 | ZN00235/002728 | NEWCASTLE | OH | Not Veg | 2020-01-07 | N | 335.9091 | N | 20 | Y | Y | 1.1101 | 39.4971 | 16201.1821
[7 empty] | 3318 | 251 | 1720234 | 2020-01-07 17:00 | 2020-01-07 20:20 | 200 | 11kV | 7400 | 37 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 206531 No protection opeation loose 11kV x arm spotted before it fell. Excluded OMS 1719902 | January | 2020 | 2020Q3 | 2020 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Not Veg | 2020-01-07 | N | 200 | N | 20 | Y | Y | 1.1101 | 39.4971 | 5407.7017
[7 empty] | 4560 | 12700 | 1720309 | 2020-01-07 21:44 | 2020-01-07 23:04 | 80 | 11kV | 5447 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206539 3 phase Instantaneous Overcurrent; Earth Fault sw 35200 prot IOC A & B PH, TIMED OC C PH. EF | January | 2020 | 2020Q3 | 2020 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2020-01-07 | N | 77.8143 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3980.5069
[7 empty] | 4806 | 15102 | 1719728 | 2020-01-07 01:20 | 2020-01-07 23:59 | 1359 | 11kV | 5553 | 44 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | At S9534 Kurnell Panel; 18 opened by DOp Cause: Cross arm on fire - conductior on crossarm See OMS 1721513 1721517 1721519 | January | 2020 | 2020Q3 | 2020 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2020-01-07 | N | 126.2045 | N | 20 | Y | Y | 1.1101 | 39.4971 | 4057.9686
[7 empty] | 3572 | 2631 | 1720289 | 2020-01-07 21:00 | 2020-01-08 | 180 | 11kV | 26820 | 149 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 206540 Section isolated to enable repairs at JU50114 | January | 2020 | 2020Q3 | 2020 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2020-01-07 | N | 180 | N | 20 | Y | Y | 1.1101 | 39.4971 | 19599.2649
[7 empty] | 4843 | 15491 | 1720336 | 2020-01-07 23:59 | 2020-01-08 01:45 | 106 | 11kV | 100416 | 976 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 Botany pnl.40 tripped on: B phase O.C UG cable fault between S3693 Sw/B (Haz) to S746 Sw/B to S6095 Sw/A See 1720607 1720608 | January | 2020 | 2020Q3 | 2020 | ZN340:PA40 | ZN340:PA40 | ZN00340/000040 | BAYSIDE | UG | Not Veg | 2020-01-07 | N | 102.8852 | N | 20 | Y | Y | 1.1101 | 39.4971 | 73381.051
[7 empty] | 3306 | 186 | 1720292 | 2020-01-07 20:40 | 2020-01-08 04:00 | 440.4333 | 11kV | 5285.2 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206541 A & B Phase DOLF : 20 Amp | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-07 | N | 440.4333 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3862.2683
[7 empty] | 4300 | 10222 | 1720353 | 2020-01-08 01:03 | 2020-01-08 10:45 | 582 | 11kV | 153696 | 1069 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Lightning | N | Zn847 Hornsby - Pnl.47 tripped, reclosed and locked out on: Earth Fault Abnormal: S6371 to AB1262 DMA with LB160 Closed Severe lightning damage to HAZ @ S4882. UGOHs broken away and restored via LV // See 1721366 1721369 | January | 2020 | 2020Q3 | 2020 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | UG | Not Veg | 2020-01-08 | N | 143.7755 | N | 13 | N | N | 1.1101 | 39.4971 | 112316.5035
[7 empty] | 4086 | 8032 | 1720569 | 2020-01-08 12:31 | 2020-01-08 14:50 | 139 | 11kV | 278 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206554 A Phase DOLF : 10 Amp Excluded oms 1720596,1720569 Note: start time amended to reflect first No Supply call received | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-08 | N | 139 | N | 13 | N | N | 1.1101 | 39.4971 | 203.1542
[7 empty] | 3564 | 2605 | 1719701 | 2020-01-06 22:45 | 2020-01-08 17:00 | 2535 | 11kV | 5172 | 4 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn14891 Wyong - Pnl.19 tripped on: Earth Fault Abnormal: S18164 Sw/B closed with AB40001 Closed UGOH fault to PT14979 (N//) See 1721016 1721017 | January | 2020 | 2020Q3 | 2020 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | Unknown | Unknown | 2020-01-06 | N | 1293 | N | 12 | N | N | 1.1101 | 39.4971 | 3779.5451
[7 empty] | 3751 | 4486 | 1720634 | 2020-01-08 14:36 | 2020-01-08 18:15 | 219 | 11kV | 7359 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206573 Earth Fault Sensitive Earth Fault fdr patrolled nothing found power restored Excluded oms 1720634 | January | 2020 | 2020Q3 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2020-01-08 | N | 159.9783 | N | 13 | N | N | 1.1101 | 39.4971 | 5377.7401
[7 empty] | 3868 | 5667 | 1720694 | 2020-01-08 17:56 | 2020-01-08 21:00 | 184 | 11kV | 184 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206578 Single pgase DOLF : 10 Amp Excluded OMS 1720694 | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-08 | N | 184 | N | 13 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 3780 | 4845 | 1720701 | 2020-01-08 17:59 | 2020-01-08 22:10 | 251 | 11kV | 12801 | 51 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206563 Transformer 54463 Faulty and requires replacement. Excluded oms 1720697 | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-01-08 | N | 251 | N | 13 | N | N | 1.1101 | 39.4971 | 9354.5932
[7 empty] | 3647 | 3323 | 1720708 | 2020-01-08 18:20 | 2020-01-08 22:15 | 235 | 11kV | 2350 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206591 B Phase DOLF : 20 Amp Excluded OMS 1720708 1720720 | January | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-01-08 | N | 235 | N | 13 | N | N | 1.1101 | 39.4971 | 1717.3107
[7 empty] | 4398 | 11031 | 1720693 | 2020-01-08 17:43 | 2020-01-08 22:41 | 298 | 11kV | 20540 | 93 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206583 74497 Locked out LF 74742 blown : 10 Amp | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-08 | N | 220.8602 | N | 13 | N | N | 1.1101 | 39.4971 | 15010.0262
[7 empty] | 4335 | 10483 | 1720700 | 2020-01-08 22:40 | 2020-01-08 23:50 | 70 | 11kV | 1540 | 22 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 206590 Burnt off tapping at Line Fuse 40759 Excluded OMS 1720700 | January | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-01-08 | N | 70 | N | 13 | N | N | 1.1101 | 39.4971 | 1125.3866
[7 empty] | 3975 | 6663 | 1720658 | 2020-01-08 14:14 | 2020-01-08 23:59 | 585 | 11kV | 585 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | Rain Light | N | Order 1700176873 LID 206557 | January | 2020 | 2020Q3 | 2020 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2020-01-08 | N | 585 | N | 13 | N | N | 1.1101 | 39.4971 | 427.5007
[7 empty] | 3733 | 4295 | 1720834 | 2020-01-09 00:14 | 2020-01-09 09:23 | 549 | 11kV | 167605 | 1520 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 206595 2 fault operation Earth Fault faulty xarm pole JU-52774 Excluded oms 1720834 ,1720894 | January | 2020 | 2020Q3 | 2020 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Not Veg | 2020-01-09 | N | 110.2664 | N | 18 | N | N | 1.1101 | 39.4971 | 122480.7905
[7 empty] | 3908 | 6006 | 1732075 | 2020-01-09 04:56 | 2020-01-09 09:40 | 284 | 11kV | 143136 | 504 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206606 B Phase DOLF : 10 Amp Excluded OMS 1720859 | January | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-01-09 | N | 284 | N | 18 | N | N | 1.1101 | 39.4971 | 104599.567
[7 empty] | 4354 | 10671 | 1720770 | 2020-01-08 21:16 | 2020-01-09 11:00 | 824.1 | 11kV | 4944.6 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206600 Overcurrent Patrolled feeder no cause found. | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-01-08 | N | 824.1 | N | 13 | N | N | 1.1101 | 39.4971 | 3613.3678
[7 empty] | 4587 | 13049 | 1720923 | 2020-01-09 08:51 | 2020-01-09 11:35 | 163.6 | 11kV | 2944.8 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206602 A Phase DOLF : 16 Amp | January | 2020 | 2020Q3 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2020-01-09 | N | 163.6 | N | 18 | N | N | 1.1101 | 39.4971 | 2151.973
[7 empty] | 4865 | 15669 | 1720882 | 2020-01-09 07:05 | 2020-01-09 12:00 | 295 | 11kV | 885 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206601 B Phase DOLF : 10 Amp Excluded OMS 1720882 | January | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-01-09 | N | 295 | N | 18 | N | N | 1.1101 | 39.4971 | 646.7319
[7 empty] | 4695 | 14065 | 1720697 | 2020-01-08 17:59 | 2020-01-09 12:05 | 1086 | 11kV | 1086 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 206614 Transformer 54463 Faulty and requires replacement. Excluded oms 1720697 | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-01-08 | N | 1086 | N | 13 | N | N | 1.1101 | 39.4971 | 793.6168
[7 empty] | 4533 | 12358 | 1720836 | 2020-01-09 00:27 | 2020-01-09 12:10 | 703 | 11kV | 1406 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206604 A Phase DOLF Excluded OMS 1720836 | January | 2020 | 2020Q3 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2020-01-09 | N | 703 | N | 18 | N | N | 1.1101 | 39.4971 | 1027.4633
[7 empty] | 4264 | 9929 | 1720988 | 2020-01-09 06:53 | 2020-01-09 12:15 | 322.3167 | 11kV | 644.6333 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 206605 3 Phase DOLF : 10 Amp REPLACED LIGHTNING ARRESTORS CC1: 06-"Urgent - O.H Mains - No others" | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-01-09 | N | 322.3167 | N | 18 | N | N | 1.1101 | 39.4971 | 471.079
[7 empty] | 4180 | 9196 | 1720682 | 2020-01-08 17:21 | 2020-01-09 12:20 | 1139 | 11kV | 10823 | 62 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206581 3 phase Sensitive Earth Fault Found blown transformer at sub 70700 | January | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2020-01-08 | N | 174.5645 | N | 13 | N | N | 1.1101 | 39.4971 | 7909.1292
[7 empty] | 4945 | 16557 | 1720870 | 2020-01-09 06:34 | 2020-01-09 12:30 | 356 | 11kV | 356 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206609 C Phase DOLF : 10 Amp Excluded OMS 1720870 | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-09 | N | 356 | N | 18 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 3884 | 5773 | 1720954 | 2020-01-09 09:29 | 2020-01-09 13:30 | 241 | 11kV | 8676 | 36 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206612 Overcurrent Feeder patroleld no cause found. | January | 2020 | 2020Q3 | 2020 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2020-01-09 | N | 241 | N | 18 | N | N | 1.1101 | 39.4971 | 6340.1649
[7 empty] | 3413 | 1102 | 1720893 | 2020-01-09 07:46 | 2020-01-09 14:00 | 374 | 11kV | 1122 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 206615 A Phase DOLF : 10 Amp Excluded OMS 1720893 | January | 2020 | 2020Q3 | 2020 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2020-01-09 | N | 374 | N | 18 | N | N | 1.1101 | 39.4971 | 819.9245
[7 empty] | 5131 | 18438 | 1720925 | 2020-01-09 08:53 | 2020-01-09 14:15 | 322 | 11kV | 644 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206616 A Phase DOLF : 10 Amp Excluded OMS 1720925 | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-01-09 | N | 322 | N | 18 | N | N | 1.1101 | 39.4971 | 470.6162
[7 empty] | 4012 | 7122 | 1721142 | 2020-01-09 14:05 | 2020-01-09 14:45 | 40 | 11kV | 840 | 21 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206621 sub isolated for tap change on sub 70848. changed for tap 4 to tap 5 volts= 243v | January | 2020 | 2020Q3 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2020-01-09 | N | 40 | N | 18 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 5188 | 18865 | 1720790 | 2020-01-08 22:55 | 2020-01-09 15:36 | 1001 | 11kV | 81836 | 1660 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn12620 Noraville - Pnl.11 tripped on: A & B phase O/C Abnormal: REC450550 Bypassed Prior to DOp attending broken cross arm at UGOH pole below PT18414, NSWFS pulsed water at burning cross arm and tripped feeder off. See 1721336 1721337 | January | 2020 | 2020Q3 | 2020 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2020-01-08 | N | 49.2988 | N | 13 | N | N | 1.1101 | 39.4971 | 59803.335
[7 empty] | 4652 | 13628 | 1720847 | 2020-01-09 02:11 | 2020-01-09 17:00 | 889 | 11kV | 91148 | 465 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 206624 pole fire @ pole FO-40347. Section isolated for repairs. Excluded oms 1720931 | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-01-09 | N | 196.0172 | N | 18 | N | N | 1.1101 | 39.4971 | 66608.27
[7 empty] | 3538 | 2374 | 1721191 | 2020-01-09 16:00 | 2020-01-09 17:35 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 206627 Single phase DOLF : 3 Amp Excluded OMS 1721191 | January | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2020-01-09 | N | 95 | N | 18 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 5199 | 18934 | 1721059 | 2020-01-09 12:15 | 2020-01-09 18:40 | 385 | 11kV | 42195 | 542 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC45053 Norah Head tripped on: O/C 11kV came off pin. HV into LV See 172342 1721343 | January | 2020 | 2020Q3 | 2020 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2020-01-09 | N | 77.8506 | N | 18 | N | N | 1.1101 | 39.4971 | 30834.8615
[7 empty] | 4720 | 14277 | 1721211 | 2020-01-09 17:30 | 2020-01-09 19:10 | 100 | 11kV | 1800 | 18 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 206629 section isolated to repair broken ties pole HR-83420 | January | 2020 | 2020Q3 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2020-01-09 | N | 100 | N | 18 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 4708 | 14171 | 1720844 | 2020-01-09 02:16 | 2020-01-09 19:35 | 1039 | 11kV | 630974 | 2379 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 206598 1 fault operation B & C Phase Overcurrent faulty xarm at pole JU-61266 HV into LV & tapping blown at pole KU-41182 Excluded oms 1720844, 1721137, 1721138, 1721139 | January | 2020 | 2020Q3 | 2020 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2020-01-09 | N | 265.2266 | N | 18 | N | N | 1.1101 | 39.4971 | 461097.1886
[7 empty] | 4337 | 10494 | 1720673 | 2020-01-09 16:40 | 2020-01-09 22:00 | 320 | 11kV | 44037 | 141 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206592 Earth Fault recorded 71 amps. Region staff requested reclose be left NA at Sw 2389 for safety due to the number of trees falling near the line. Excluded OMS 1720673. | January | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-01-09 | N | 312.3191 | N | 18 | N | N | 1.1101 | 39.4971 | 32180.9407
[7 empty] | 5319 | 20030 | 1720719 | 2020-01-09 18:45 | 2020-01-09 22:15 | 210 | 11kV | 630 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206585 A & B phase DOLF : 10 Amp Excluded OMS 1720719 | January | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-01-09 | N | 210 | N | 18 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 5227 | 19288 | 1721274 | 2020-01-10 02:18 | 2020-01-10 04:22 | 124 | 11kV | 201946 | 2242 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | LID 206633 3 fault operations B Phase Earth Fault Possum at 61912 | January | 2020 | 2020Q3 | 2020 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2020-01-10 | N | 90.074 | N | 7 | N | N | 1.1101 | 39.4971 | 147576.1804
[7 empty] | 3980 | 6686 | 1722263 | 2020-01-10 11:52 | 2020-01-10 12:27 | 35 | 11kV | 2170 | 62 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Hot >35C | N | LID 206638 A phase replaced broken Pin insulator Aph on pole BK-80087 | January | 2020 | 2020Q3 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2020-01-10 | N | 35 | N | 7 | N | N | 1.1101 | 39.4971 | 1585.772
[7 empty] | 3716 | 4081 | 1721486 | 2020-01-10 14:13 | 2020-01-10 15:12 | 59 | 11kV | 590 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT S12690 Berkeley Vale the 11kV panel 11 tripped on Relays: EF, EFI Signals: TX13 Group Earth Field EFI's NIL Cause: 11kV UG fault Berkeley Vale Panel 11 and S14772 | January | 2020 | 2020Q3 | 2020 | ZN12690:PA11 | ZN12690:PA11 | ZN12690/000011 | CENTRAL COAST | UG | Not Veg | 2020-01-10 | N | 59 | N | 7 | N | N | 1.1101 | 39.4971 | 431.1546
[7 empty] | 4203 | 9333 | 1721586 | 2020-01-10 19:34 | 2020-01-10 20:20 | 46 | 11kV | 4416 | 96 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206646 A Phase DOLF : 31 Amp A Phase DOLF on fire Excluded OMS 1721586 | January | 2020 | 2020Q3 | 2020 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2020-01-10 | N | 46 | N | 7 | N | N | 1.1101 | 39.4971 | 3227.0826
[7 empty] | 5162 | 18689 | 1721540 | 2020-01-10 19:50 | 2020-01-10 20:30 | 40 | 11kV | 80 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 206645 DOLF carrier Broken | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-10 | N | 40 | N | 7 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 3977 | 6676 | 1721607 | 2020-01-10 20:39 | 2020-01-10 21:45 | 66.3 | 11kV | 1657.5 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 206647 C Phase DOLF : 10 Amp | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-10 | N | 66.3 | N | 7 | N | N | 1.1101 | 39.4971 | 1211.2521
[7 empty] | 5012 | 17324 | 1721618 | 2020-01-10 22:26 | 2020-01-10 23:54 | 88 | 11kV | 148430 | 1745 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 29 tripped on Relays: Earth Fault, A and Cphase timed OC, Fault Check and EFI Signals: 11kV Trip, TX2 Group Earth with Zone Earth Cause: Possum on 11kV UGOH near PT1194 North Woorang See OMS 1722300 1722301 1721618 | January | 2020 | 2020Q3 | 2020 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2020-01-10 | N | 85.0602 | N | 7 | N | N | 1.1101 | 39.4971 | 108468.2661
[7 empty] | 5067 | 17951 | 1721656 | 2020-01-11 03:32 | 2020-01-11 05:59 | 147 | 11kV | 23228 | 170 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 206650 2 fault operation 3 phase Overcurrent Excluded OMS 1721656 | January | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-01-11 | N | 136.6353 | N | 9 | N | N | 1.1101 | 39.4971 | 16974.3373
[7 empty] | 3677 | 3691 | 1723302 | 2020-01-11 13:54 | 2020-01-11 14:45 | 51 | 33kV Distribution | 51 | 1 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 206656 Pole fire at JT-41017 | January | 2020 | 2020Q3 | 2020 |  |  |  | NEWCASTLE | OH | Not Veg | 2020-01-11 | N | 51 | N | 9 | N | N | 1.1101 | 39.4971 | 37.2693
[7 empty] | 3709 | 4035 | 1721864 | 2020-01-11 14:00 | 2020-01-11 14:45 | 45 | 11kV | 5445 | 121 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 206658 & 206659 Pole fire at JT-41017 Excluded OMS 1721864 | January | 2020 | 2020Q3 | 2020 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2020-01-11 | N | 45 | N | 9 | N | N | 1.1101 | 39.4971 | 3979.0454
[7 empty] | 5127 | 18415 | 1721817 | 2020-01-11 12:18 | 2020-01-11 17:30 | 312 | 11kV | 135862 | 1283 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 206655 11kV crossarm burning through pole JT-81244 replaced under AP. Excluded OMS 1721817 | January | 2020 | 2020Q3 | 2020 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Not Veg | 2020-01-11 | N | 105.894 | N | 9 | N | N | 1.1101 | 39.4971 | 99283.9423
[7 empty] | 3605 | 2810 | 1721871 | 2020-01-11 15:56 | 2020-01-11 22:10 | 374 | 11kV | 74084 | 1003 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 206660 Pole Fire JT-80327 Feeder Dumped from ABS 15998. sub 14378 interconnected. at 1825. Excluded OMS 1721889 | January | 2020 | 2020Q3 | 2020 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | OH | Not Veg | 2020-01-11 | N | 73.8624 | N | 9 | N | N | 1.1101 | 39.4971 | 54138.4021
[7 empty] | 4348 | 10580 | 1721812 | 2020-01-11 11:09 | 2020-01-11 23:15 | 726 | 33kV Distribution | 726 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Light | N | LID 206662 A Phase Earth Fault Sw 43064 found open. Incoming links 43065 welded shut.. Possibly following TR earlier on fdr? See report 206652 Links replaced Excluded OMS 1721815. | January | 2020 | 2020Q3 | 2020 |  |  |  | NEWCASTLE | OH | Not Veg | 2020-01-11 | N | 726 | N | 9 | N | N | 1.1101 | 39.4971 | 530.5394
[7 empty] | 5312 | 19960 | 1721801 | 2020-01-11 11:10 | 2020-01-12 01:00 | 830 | 11kV | 9960 | 12 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 206666 No Protection operation Pole fire SW-50177. Excluded OMS 1721801 | January | 2020 | 2020Q3 | 2020 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2020-01-11 | N | 830 | N | 9 | N | N | 1.1101 | 39.4971 | 7278.4742
[7 empty] | 4541 | 12474 | 1721911 | 2020-01-11 18:48 | 2020-01-12 02:50 | 482 | 11kV | 21934 | 167 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 206663 2 fault operations Sw 80652 = 50TN Xarm burnt off pole JU-22066, repairs completed Excluded OMS 1721911 | January | 2020 | 2020Q3 | 2020 | 256:80652 | 256:80652 | ZN00256/080652 | NEWCASTLE | OH | Not Veg | 2020-01-11 | N | 131.3413 | N | 9 | N | N | 1.1101 | 39.4971 | 16028.7203
[7 empty] | 3918 | 6095 | 1721910 | 2020-01-11 23:10 | 2020-01-12 03:00 | 230 | 11kV | 690 | 3 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 206665 Tree grown into mains Excluded OMS 1721910 | January | 2020 | 2020Q3 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2020-01-11 | N | 230 | N | 9 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 4024 | 7220 | 1722040 | 2020-01-12 15:29 | 2020-01-12 16:20 | 51 | 11kV | 9741 | 191 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn35370 Galston Panel 10 Recloser CP50015 Tripped, Lockout out tripped and locked out under fault Cause: Abnormal Switching: AB1192 Opened Due to DMA, Recloser CP2691 Duneba Drive Closed Tree brancgh removed from 11kV Overhead mains outside 67 Quarry Rd Dural See OMS 1722344 1722057 1722040 | January | 2020 | 2020Q3 | 2020 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2020-01-12 | N | 51 | N | 1 | N | N | 1.1101 | 39.4971 | 7118.4355
[7 empty] | 3772 | 4793 | 1722156 | 2020-01-13 07:10 | 2020-01-13 09:05 | 115 | 11kV | 230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 206673 A Phase DOLF : 5 Amp Excluded OMS 1722156 | January | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2020-01-13 | N | 115 | N | 6 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 5043 | 17730 | 1722427 | 2020-01-13 14:40 | 2020-01-13 19:30 | 290 | 11kV | 1740 | 6 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206679 Single phase tree on 11kV OHM pole MG77002 | January | 2020 | 2020Q3 | 2020 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2020-01-13 | N | 290 | N | 6 | N | N | 1.1101 | 39.4971 | 1271.5407
[7 empty] | 5179 | 18799 | 1722394 | 2020-01-13 17:30 | 2020-01-13 20:20 | 170 | 11kV | 31450 | 185 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 206676 A Pople asigned. Truck hit pole DP 30360 Kelso St dislodged 11kv insulator. section isolated for repair. Excluded oms 1722394. 1722460 see report 206674 for associated T & R | January | 2020 | 2020Q3 | 2020 | 513:83493 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Not Veg | 2020-01-13 | N | 170 | N | 6 | N | N | 1.1101 | 39.4971 | 22982.7324
[7 empty] | 3725 | 4191 | 1722455 | 2020-01-13 20:40 | 2020-01-13 21:45 | 65 | 11kV | 650 | 10 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 206680 car accient at IR21162 NO protection. Interr by dop Excluded OMS 1722481, 1722455 | January | 2020 | 2020Q3 | 2020 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2020-01-13 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 4538 | 12418 | 1722495 | 2020-01-14 00:09 | 2020-01-14 01:25 | 76 | 11kV | 684 | 9 | HV | Vandalism | 3rd Party Impact | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 206682 interrupt to repair stolen earth at L/A on CCT pole AK60416 Excluded OMS 1722495 | January | 2020 | 2020Q3 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2020-01-14 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 4417 | 11222 | 1722503 | 2020-01-13 23:55 | 2020-01-14 03:40 | 225 | 11kV | 63615 | 609 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 206683 1 fault operation C Phase Earth Fault A prot - Inst EF B prot - o/c & EF C-E faulty arrestor UGOH HR-61203 AR off for planned SI 51052 Excluded oms 1722503 | January | 2020 | 2020Q3 | 2020 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2020-01-13 | N | 104.4581 | N | 6 | N | N | 1.1101 | 39.4971 | 46487.9657
[7 empty] | 3854 | 5568 | 1722497 | 2020-01-13 21:43 | 2020-01-14 06:30 | 527 | 11kV | 112251 | 213 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN21400 Berowra Panel 11 - Bond Burnt off @ AB1304 See OMS 1723367 1722497 1722636 | January | 2020 | 2020Q3 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2020-01-13 | N | 527 | N | 6 | N | N | 1.1101 | 39.4971 | 82029.72
[7 empty] | 3960 | 6536 | 1722553 | 2020-01-14 09:23 | 2020-01-14 10:30 | 67 | 11kV | 134 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206687 B Phase DOLF : 10 Amp Excluded OMS 1722553 | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-01-14 | N | 67 | N | 3 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 3669 | 3613 | 1722743 | 2020-01-14 17:52 | 2020-01-14 20:14 | 142.1 | 11kV | 191 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At PT47388 Springs Finna 11kV roadside 63A ABB HDO Operated Cause not ascertained See OMS 1722749 1722748 1722743 | January | 2020 | 2020Q3 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2020-01-14 | N | 95.5 | N | 3 | N | N | 1.1101 | 39.4971 | 139.5772
[7 empty] | 4050 | 7556 | 1723003 | 2020-01-15 18:35 | 2020-01-15 21:05 | 150 | 11kV | 24750 | 165 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Section of 11kV Feeder (Ex Noraville panel 3) from LB40958 to S11948 Interrupted of safety Cause: Interrupted to repair cross arm which had spun 180 degrees and about to fall See OMS 1723021 1723013 1723004 | January | 2020 | 2020Q3 | 2020 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2020-01-15 | N | 150 | N | 1 | N | N | 1.1101 | 39.4971 | 18086.57
[7 empty] | 5196 | 18904 | 1723046 | 2020-01-16 03:51 | 2020-01-16 04:45 | 54 | 11kV | 91638 | 1697 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn129 Hunters Holl Panel 57 tripped on Signals: 11kV Trip Relays: B and C phase IOC Field efi's @ Sub - As expected Cause: Bat across mains near LB7 | January | 2020 | 2020Q3 | 2020 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2020-01-16 | N | 54 | N | 28 | Y | Y | 1.1101 | 39.4971 | 66966.3475
[7 empty] | 3966 | 6611 | 1723052 | 2020-01-16 06:04 | 2020-01-16 09:55 | 231 | 11kV | 9397 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 206721 A, B, and C Phase Sensitive Earth Fault No Cause found, not storm conditions Fdr patrolled no fault found, fdr restored | January | 2020 | 2020Q3 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2020-01-16 | N | 187.94 | N | 28 | Y | Y | 1.1101 | 39.4971 | 6867.0504
[7 empty] | 3731 | 4275 | 1723127 | 2020-01-16 08:50 | 2020-01-16 10:30 | 100 | 11kV | 84895 | 1174 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At ZN9037 Miranda Panel 2 "Sylvania Heights" feeder has tripped Signal: 11kv trip Relays: C phase IOC, EF relay, LO Abnormal: LB3549 closed defective with AB35609 open Remarks: lightning. Insulator on corner pole 2 poles out (265 Princes Hwy, Syvania) from PT9982 has been hit by lightning, destroying an insulator. Located electrically between AB35195 and AB35010 Tee PT9982 Princes Young | January | 2020 | 2020Q3 | 2020 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2020-01-16 | N | 72.3126 | N | 28 | Y | Y | 1.1101 | 39.4971 | 62038.762
[7 empty] | 3904 | 5988 | 1723106 | 2020-01-16 10:30 | 2020-01-16 12:10 | 100 | 11kV | 100 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 206732 B Phase DOLF Burnt up Excluded OMS 1723106 | January | 2020 | 2020Q3 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2020-01-16 | N | 100 | N | 28 | Y | Y | 1.1101 | 39.4971 | 73.0771
[7 empty] | 3756 | 4612 | 1723236 | 2020-01-16 11:00 | 2020-01-16 12:55 | 115 | 11kV | 230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206734 Single Phase 10 Amp fuse, substation DOLF replaced 2 x 10 amp DOLFS | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-01-16 | N | 115 | N | 28 | Y | Y | 1.1101 | 39.4971 | 168.0772
[7 empty] | 5224 | 19280 | 1723205 | 2020-01-16 11:10 | 2020-01-16 13:08 | 118 | 11kV | 1888 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206740 A and C phase 20Amp Line DOLF and Substation DOLF Line fuse 74388 A & C ph 20 amp fuses replaced also sub 48062 10 amp dolf replaced. power restored 1308.mdv | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-16 | N | 118 | N | 28 | Y | Y | 1.1101 | 39.4971 | 1379.6947
[7 empty] | 3992 | 6897 | 1723225 | 2020-01-16 13:15 | 2020-01-16 13:35 | 20 | 11kV | 260 | 13 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 206739 3 phase Pole Mounted RAGCB, Earth Fault sw 74439 tripped while trying dolf back at sub 70790, sub isolated for replace lightning arrestor, power restored sw 74439 at 1335. power restored to sub 70790 at 1400. see report LID 206737 (OMS 1724558) | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-01-16 | N | 20 | N | 28 | Y | Y | 1.1101 | 39.4971 | 190.0003
[7 empty] | 5110 | 18302 | 1724541 | 2020-01-16 13:30 | 2020-01-16 13:44 | 14 | 33kV Distribution | 14 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206746 Sw 80497 A prot - trip AB B prot - trip 50 TAB no targets found Sw 33730 | January | 2020 | 2020Q3 | 2020 |  |  |  | NEWCASTLE | OH | Veg | 2020-01-16 | N | 14 | N | 28 | Y | Y | 1.1101 | 39.4971 | 10.2308
[7 empty] | 5140 | 18509 | 1723276 | 2020-01-16 13:12 | 2020-01-16 13:45 | 33 | 11kV | 1320 | 40 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 206743 3 Phase Poles hit by lightning section isolated for repairs | January | 2020 | 2020Q3 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2020-01-16 | N | 33 | N | 28 | Y | Y | 1.1101 | 39.4971 | 964.6171
[7 empty] | 3694 | 3835 | 1723117 | 2020-01-16 11:53 | 2020-01-16 13:45 | 112 | 11kV | 112 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 206737 3 Phase 10 Amp Pole Mounted RAGCB, substation DOLF sw 74439 tripped while trying dolf back at sub 70790, sub isolated for replace lightning arrestor, power restored sw 74439 at 1335. power restored to sub 70790 at 1345 | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-01-16 | N | 112 | N | 28 | Y | Y | 1.1101 | 39.4971 | 81.8463
[7 empty] | 3543 | 2418 | 1723327 | 2020-01-16 13:30 | 2020-01-16 14:15 | 45 | 11kV | 225 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206755 Substation DOLF : 10 Amp Excluded OMS 1723327 | January | 2020 | 2020Q3 | 2020 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2020-01-16 | N | 45 | N | 28 | Y | Y | 1.1101 | 39.4971 | 164.4234
[7 empty] | 4372 | 10787 | 1723272 | 2020-01-16 13:08 | 2020-01-16 14:25 | 77 | 11kV | 111178 | 1473 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 206744 2 fault operations A & B phase Overcurrent 1 blown disc out of 3 at pole JT-93110. supply restored but further work required at pole. Excluded OMS 1723277, 1723298 | January | 2020 | 2020Q3 | 2020 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | OH | Not Veg | 2020-01-16 | N | 75.4773 | N | 28 | Y | Y | 1.1101 | 39.4971 | 81245.6032
[7 empty] | 5225 | 19284 | 1723256 | 2020-01-16 12:58 | 2020-01-16 17:16 | 258 | 11kV | 236128 | 933 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206759 2 fault operations A Phase Overcurrent Excluded OMS 1723256 | January | 2020 | 2020Q3 | 2020 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Veg | 2020-01-16 | N | 253.0847 | N | 28 | Y | Y | 1.1101 | 39.4971 | 172555.3778
[7 empty] | 3422 | 1210 | 1723425 | 2020-01-16 13:37 | 2020-01-16 17:47 | 250 | 11kV | 184154 | 1572 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 206757 2 fault operations B & C Phase Overcurrent Sw 82697 B & C O/C, Fault detector A. Blown insulator pole JT-91416 Excluded OMS 1723291 | January | 2020 | 2020Q3 | 2020 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2020-01-16 | N | 117.1463 | N | 28 | Y | Y | 1.1101 | 39.4971 | 134574.3116
[7 empty] | 3607 | 2831 | 1723420 | 2020-01-16 13:00 | 2020-01-16 18:10 | 310 | 11kV | 310 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206763 Single phase DOLF : 50 Amp Excluded OMS 1723420 | January | 2020 | 2020Q3 | 2020 | 507:80920 | 507:80920 | ZN00507/080920 | CESSNOCK | OH | Veg | 2020-01-16 | N | 310 | N | 28 | Y | Y | 1.1101 | 39.4971 | 226.5389
[7 empty] | 4334 | 10471 | 1723286 | 2020-01-16 13:30 | 2020-01-16 19:10 | 339.75 | 11kV | 24122.25 | 71 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206764 A & B Phase DOLF : 31 Amp Excluded OMS 1723412 | January | 2020 | 2020Q3 | 2020 | 213:33775 | 213:33775 | ZN00213/033775 | NEWCASTLE | OH | Veg | 2020-01-16 | N | 339.75 | N | 28 | Y | Y | 1.1101 | 39.4971 | 17627.8288
[7 empty] | 4477 | 11812 | 1723269 | 2020-01-16 13:08 | 2020-01-16 19:34 | 386 | 11kV | 354574 | 1391 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | UGOH | Unplanned | Electrical Storm | N | LID 206745 2 fault operation Earth Fault Possible faulty pot head Excluded OMS 1723269 | January | 2020 | 2020Q3 | 2020 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2020-01-16 | N | 254.9058 | N | 28 | Y | Y | 1.1101 | 39.4971 | 259112.221
[7 empty] | 3903 | 5981 | 1723164 | 2020-01-16 09:34 | 2020-01-16 19:50 | 616 | 11kV | 668148 | 2097 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | At ZN10993 Hurstville North Panel 22L 'Barnards Av' feeder has tripped. Signals: 11kv trip, 22L OC Relays: 51 ABC, EFI, LO Field EFI's @ Subs : nil Relays: after 3 min trip OC A and B phases Remarks: OH resting on cross arm. Cross arm snapped on pole KO-14171. Located electrically between LB30036, LB62012 and AB31213 tee PT10243 Edward Laycock and S10456 St Kilda Staples. Second fault: AB30011 has blown insulators on footpath and center phases | January | 2020 | 2020Q3 | 2020 | ZN10993:PA22 | ZN10993:PA22 | ZN10993/000022 | BAYSIDE | OH | Not Veg | 2020-01-16 | N | 318.6209 | N | 28 | Y | Y | 1.1101 | 39.4971 | 488262.8514
[7 empty] | 3987 | 6823 | 1723263 | 2020-01-16 13:04 | 2020-01-16 20:20 | 436 | 11kV | 294834 | 1299 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206738 2 fault operations 50T BC excluded OMS 1723263 | January | 2020 | 2020Q3 | 2020 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Veg | 2020-01-16 | N | 226.97 | N | 28 | Y | Y | 1.1101 | 39.4971 | 215455.9911
[7 empty] | 4301 | 10225 | 1723341 | 2020-01-16 14:11 | 2020-01-16 20:31 | 380 | 11kV | 36480 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 206765 A Phase DOLF : 40 Amp Aph L/A cut away - replace asap Excluded oms 1723331 | January | 2020 | 2020Q3 | 2020 | 216:10723 | 216:10723 | ZN00216/010723 | LAKE MACQUARIE | OH | Veg | 2020-01-16 | N | 380 | N | 28 | Y | Y | 1.1101 | 39.4971 | 26658.508
[7 empty] | 5328 | 20155 | 1724461 | 2020-01-16 12:58 | 2020-01-16 20:47 | 469 | 11kV | 119975 | 362 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206742 A & B phase Overcurrent Excluded OMS 1723261 Sw 81240 50 TAB Sw 2108 oc ef | January | 2020 | 2020Q3 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-01-16 | N | 331.4227 | N | 28 | Y | Y | 1.1101 | 39.4971 | 87674.1913
[7 empty] | 5193 | 18893 | 1723297 | 2020-01-16 13:37 | 2020-01-16 23:50 | 613 | 11kV | 570168 | 937 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206769 Overcurrent Excluded OMS 1723297 prot - 51B, 51N no fault found | January | 2020 | 2020Q3 | 2020 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2020-01-16 | N | 608.5037 | N | 28 | Y | Y | 1.1101 | 39.4971 | 416661.9573
[7 empty] | 4992 | 17081 | 1723257 | 2020-01-16 12:59 | 2020-01-16 23:50 | 651 | 11kV | 266544 | 843 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 206741 2 fault operation C Phase Overcurrent Mains down JR 54417 & JR 54427. Fed from Fdr 81232 but usually Fdr 81240. Also outage from Sw 2108 to complicate matters as well. Sorry Excluded OMS 1723257 Complicated | January | 2020 | 2020Q3 | 2020 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Not Veg | 2020-01-16 | N | 316.1851 | N | 28 | Y | Y | 1.1101 | 39.4971 | 194782.4935
[7 empty] | 4909 | 16039 | 1723547 | 2020-01-16 22:26 | 2020-01-17 00:25 | 119 | 11kV | 1309 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206770 A phase 10 Amp Line DOLF | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-01-16 | N | 119 | N | 28 | Y | Y | 1.1101 | 39.4971 | 956.5786
[7 empty] | 5326 | 20133 | 1723545 | 2020-01-16 22:25 | 2020-01-17 00:30 | 125 | 11kV | 250 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206771 A Phase 10Amp fuse substation DOLF | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-01-16 | N | 125 | N | 28 | Y | Y | 1.1101 | 39.4971 | 182.6926
[7 empty] | 3676 | 3685 | 1723482 | 2020-01-16 23:45 | 2020-01-17 00:45 | 60 | 11kV | 120 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206773 Interrupted to repair LV cables between LVF and Tx | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-01-16 | N | 60 | N | 28 | Y | Y | 1.1101 | 39.4971 | 87.6925
[7 empty] | 4881 | 15770 | 1723266 | 2020-01-16 13:00 | 2020-01-17 01:49 | 769 | 11kV | 137082 | 313 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 206772 2 fault operations A & B phases Overcurrent broken insulator pole JS-45265 Excluded oms 1723266 | January | 2020 | 2020Q3 | 2020 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2020-01-16 | N | 437.9617 | N | 28 | Y | Y | 1.1101 | 39.4971 | 100175.4824
[7 empty] | 3893 | 5879 | 1723438 | 2020-01-16 17:42 | 2020-01-17 04:30 | 648 | 11kV | 148272 | 702 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S9900 menai 11kv Panel 19 "S9768 menai Exchange" has tripped on Relays: A and B phase overcurrent, reclose and lockout, efi Tx2 earth fault check frame leakage Signals: Zone earth , Tx2 grp earth, 11kv trip Remarks: tree on OH mains outside 113 Prices CCT Woronora. LB35364 is open and defective | January | 2020 | 2020Q3 | 2020 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | OH | Veg | 2020-01-16 | N | 211.2137 | N | 28 | Y | Y | 1.1101 | 39.4971 | 108352.8043
[7 empty] | 3796 | 4999 | 1723580 | 2020-01-17 06:30 | 2020-01-17 07:50 | 80 | 11kV | 320 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206774 B Phase DOLF : 10 Amp Excluded OMS 1723580 | January | 2020 | 2020Q3 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-01-17 | N | 80 | N | 17 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 4879 | 15760 | 1723597 | 2020-01-17 07:09 | 2020-01-17 08:39 | 90 | 11kV | 91980 | 1022 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn10994 Mortdale Pa 21 'S10364' feeder has tripped Remarks: tree/branch on OH mains. Branch @ LB 31154 removed by Dop | January | 2020 | 2020Q3 | 2020 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2020-01-17 | N | 90 | N | 17 | N | N | 1.1101 | 39.4971 | 67216.271
[7 empty] | 4071 | 7791 | 1723605 | 2020-01-17 07:48 | 2020-01-17 09:43 | 115 | 11kV | 105893 | 925 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.26 tripped, reclosed and locked out on: IOC Pnl.26 tripped again at 0907 during restoration Tree branch on mains near LB78030 See 1729796 1729797 1729798 | January | 2020 | 2020Q3 | 2020 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2020-01-17 | N | 114.4789 | N | 17 | N | N | 1.1101 | 39.4971 | 77383.4811
[7 empty] | 4124 | 8418 | 1723659 | 2020-01-17 08:54 | 2020-01-17 10:47 | 113 | 11kV | 122492 | 1084 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At ST Ives Panel 17 Shindfield feeder tripped, reclosed tripped and locked out on Relays: A phase OC, Timing, Abnormal Swithcing: LB64433 Closed, AB2082 Open and Defective DOp patrolled and all clear. See OMS 1725477 1723659 1723999 | January | 2020 | 2020Q3 | 2020 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2020-01-17 | N | 113 | N | 17 | N | N | 1.1101 | 39.4971 | 89513.5407
[7 empty] | 4627 | 13476 | 1723718 | 2020-01-17 10:15 | 2020-01-17 11:05 | 50 | 11kV | 4250 | 85 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | PT612 Copeland Hull - B phase HDO operated. Tree branch on PT | January | 2020 | 2020Q3 | 2020 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Veg | 2020-01-17 | N | 50 | N | 17 | N | N | 1.1101 | 39.4971 | 3105.7746
[7 empty] | 4847 | 15532 | 1723730 | 2020-01-17 10:23 | 2020-01-17 12:00 | 97 | 11kV | 45193 | 609 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | At ZN12600 Lisarow 11kv Panel No.1 "LB42050, etc" tripped under fault. Protection operations at Zone sub: Timed earth fault, efi, recloser timing, recloser lockout Remarks: UGOH fault short circuit. 11kv UGOH fault between S14727 Hillgrove Finlay (Sw/B) and AB41098 tee PT14303 Walmsley Finlay | January | 2020 | 2020Q3 | 2020 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | Unknown | Unknown | 2020-01-17 | N | 74.2085 | N | 17 | N | N | 1.1101 | 39.4971 | 33025.7114
[7 empty] | 3941 | 6308 | 1723591 | 2020-01-17 06:57 | 2020-01-17 12:20 | 323 | 11kV | 625492 | 2677 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN10998 Rockdale Panel 17 "Sub 10957" feeder has tripped Signals: 11kv trip Relays: A phase IOC Field EFI's @ Subs: Nil Abnormal: AB30069 closed, LB62011 open Remarks: tree branch near PT78135. Blown surge arrestor assembly at UGOH between Sw/B @ S10224 Delmaine New Illawarra and Sw/A @ S48119 Shaw West | January | 2020 | 2020Q3 | 2020 | ZN10998:PA17 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Veg | 2020-01-17 | N | 233.6541 | N | 17 | N | N | 1.1101 | 39.4971 | 457091.1047
[7 empty] | 4059 | 7674 | 1723720 | 2020-01-17 09:57 | 2020-01-17 12:30 | 153 | 11kV | 3673 | 1393 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN36200 Empire Bay, 11kv Panel No.1 tripped under fault and reclosed Remarks: weather related. Footpath and centre phase 31.5A HDO's found operated at PT14676 'Empire bay School'. HDO's replaced, and supply restored | January | 2020 | 2020Q3 | 2020 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Veg | 2020-01-17 | N | 2.6368 | N | 17 | N | N | 1.1101 | 39.4971 | 2684.1201
[7 empty] | 4125 | 8444 | 1723768 | 2020-01-17 11:11 | 2020-01-17 13:50 | 159 | 11kV | 477 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN12600 Lisarow 11kv panel 2 "Holgate feeder" @ PT14479 The Ridgeway Paroo 1.2-16A HVDO operated road and middle phase Remarks: tree branch contact- other. Stringy bark on 11kv @ PT14479 | January | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-01-17 | N | 159 | N | 17 | N | N | 1.1101 | 39.4971 | 348.5775
[7 empty] | 5302 | 19874 | 1723764 | 2020-01-17 11:07 | 2020-01-17 14:15 | 188 | 11kV | 188 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 206784 B Phase substation DOLF B phase DOLF & 3 LAs replaced | January | 2020 | 2020Q3 | 2020 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2020-01-17 | N | 188 | N | 17 | N | N | 1.1101 | 39.4971 | 137.3849
[7 empty] | 4942 | 16520 | 1725540 | 2020-01-17 14:47 | 2020-01-17 14:58 | 11 | 11kV | 11013 | 1963 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At 1287 Revesby ZN P6 tripped and reclosed on B phase time oc, lockout and timing relay, efi, fault check Abnormal: Sw/B @ S4106 Wrona Burra closed, Sw/A S6525 Davies Banks no1 open defective Remarks: cause not ascertained. Patrolled by dop | January | 2020 | 2020Q3 | 2020 | ZN1287:PA6 | ZN1287:PA6 | ZN01287/000006 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-01-17 | N | 5.6103 | N | 17 | N | N | 1.1101 | 39.4971 | 8047.9756
[7 empty] | 3675 | 3674 | 1723818 | 2020-01-17 12:25 | 2020-01-17 15:40 | 195 | 11kV | 195 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 206786 Single phase substation DOLF Blown Lighting arrestor @ sub 72891 | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-01-17 | N | 195 | N | 17 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 4633 | 13523 | 1723638 | 2020-01-17 14:38 | 2020-01-17 16:50 | 131.5833 | 11kV | 15526.8333 | 118 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 206793 Isolated sub to repair hot joint B phase 11kV bushing. Excluded OMS 1723638 | January | 2020 | 2020Q3 | 2020 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2020-01-17 | N | 131.5833 | N | 17 | N | N | 1.1101 | 39.4971 | 11346.5518
[7 empty] | 3757 | 4629 | 1724174 | 2020-01-17 17:10 | 2020-01-17 18:05 | 55 | 11kV | 165 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 206799 3 Phase B and C Phase wiring from Transformer to LVF's shorted | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-01-17 | N | 55 | N | 17 | N | N | 1.1101 | 39.4971 | 120.5771
[7 empty] | 3528 | 2277 | 1723726 | 2020-01-17 00:18 | 2020-01-17 18:18 | 1080 | 11kV | 14040 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 206792 B Phase DOLF : 10 Amp Excluded OMS 1723726 | January | 2020 | 2020Q3 | 2020 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2020-01-17 | N | 1080 | N | 17 | N | N | 1.1101 | 39.4971 | 10260.0179
[7 empty] | 4973 | 16832 | 1724023 | 2020-01-17 23:15 | 2020-01-18 00:12 | 57 | 11kV | 15390 | 270 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN12600 Lisarow ex Panel 2 "Holgate", rec 41845 North Erina has tripped Relays: OC tirp and LO remarks: tree/branch on OH mains. Branch found and removed adj AB42109 | January | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-01-17 | N | 57 | N | 17 | N | N | 1.1101 | 39.4971 | 11246.5581
[7 empty] | 4741 | 14441 | 1724017 | 2020-01-17 23:00 | 2020-01-18 00:29 | 89 | 11kV | 75650 | 850 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At Zn12570 Avoca, ex Panel 40 'Davistown', Rec 41778 Amy Kincumber has tripped Relays: OC trip and LO Remarks: cause not ascertained. Nothing found at UGOH in report either | January | 2020 | 2020Q3 | 2020 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2020-01-17 | N | 89 | N | 17 | N | N | 1.1101 | 39.4971 | 55282.7887
[7 empty] | 4032 | 7372 | 1724065 | 2020-01-18 07:59 | 2020-01-18 11:20 | 200.8667 | 11kV | 3013 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S13326 Milina Coachwood B phase 31 amp HDO operated Section of Panel No.10L "Wamberal Aux No.2" ex Sub 14144 Wamberal Remarks: tree branch on OH mains removed by Dop | January | 2020 | 2020Q3 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-01-18 | N | 200.8667 | N | 6 | N | N | 1.1101 | 39.4971 | 2201.8115
[7 empty] | 4620 | 13399 | 1724045 | 2020-01-18 06:29 | 2020-01-18 12:23 | 354 | 11kV | 64980 | 857 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | At S12600 Lisarow Panel No.13 "LB 41044 etc" feeder opened on B phase OC with EFI Remarks: UGOH fault open circuit. B phase OC on UGOH to S14776 Old Farm Shirley | January | 2020 | 2020Q3 | 2020 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | Unknown | Unknown | 2020-01-18 | N | 75.8226 | N | 6 | N | N | 1.1101 | 39.4971 | 47485.4674
[7 empty] | 4192 | 9278 | 1724160 | 2020-01-18 13:54 | 2020-01-18 15:19 | 85 | 11kV | 68850 | 810 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At S3154 St Ives Panel 11 Ellaomhg Rd tripped on C phase OC Cause: Tree branch on 11kV near S35365 - Tree branch contact other | January | 2020 | 2020Q3 | 2020 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2020-01-18 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 50313.5493
[7 empty] | 3786 | 4905 | 1724082 | 2020-01-18 08:53 | 2020-01-18 17:20 | 507 | 11kV | 2028 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | The 11kv 16Amp Right side HDO was found to have operated at PT13748 Oystershell Wise 3.4 Remarks: cause not ascertained | January | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-01-18 | N | 507 | N | 6 | N | N | 1.1101 | 39.4971 | 1482.0026
[7 empty] | 3491 | 1930 | 1724231 | 2020-01-18 22:52 | 2020-01-19 00:45 | 113 | 11kV | 110127 | 1023 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Zn965 Pennant Hills - Pnl.43 tripped Cause not ascertained See 1729823 1729824 | January | 2020 | 2020Q3 | 2020 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Veg | 2020-01-18 | N | 107.651 | N | 6 | N | N | 1.1101 | 39.4971 | 80477.5634
[7 empty] | 4103 | 8211 | 1724238 | 2020-01-19 02:27 | 2020-01-19 04:24 | 117 | 11kV | 61659 | 527 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | At ZN15005 Belrose Panel 4 Recloser CP51818 Prahran John Oxley tripped on EF trip and lockout Cause: Two lightning arrestors burnt up at recloser CP21802 Abnormal Switching:CP21076 Open DMA, Recloser 21801 Open DMA, CP24314 Open, CP25623 Closed, CP22588 Closed See OMS 1725694 1724238 1724240 | January | 2020 | 2020Q3 | 2020 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2020-01-19 | N | 117 | N | 3 | N | N | 1.1101 | 39.4971 | 45058.5786
[7 empty] | 5047 | 17786 | 1724330 | 2020-01-19 09:09 | 2020-01-19 14:51 | 342 | 11kV | 82080 | 240 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Section of Panel 17 "Somersby fall" feeder at ZN14143 Somersby Rec 61922 "Pacific Bar point" tripped & locked out Remarks: tree/branch brought down OH. Vicinity #13 cheero point rd. Rec 61922 in scan fail. | January | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-01-19 | N | 342 | N | 3 | N | N | 1.1101 | 39.4971 | 59981.643
[7 empty] | 5255 | 19493 | 1724350 | 2020-01-19 15:04 | 2020-01-19 16:37 | 93 | 11kV | 93 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 206804 Single phase DOLF : 10 Amp | January | 2020 | 2020Q3 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2020-01-19 | N | 93 | N | 3 | N | N | 1.1101 | 39.4971 | 67.9617
[7 empty] | 4380 | 10838 | 1724405 | 2020-01-20 04:51 | 2020-01-20 07:13 | 142 | 11kV | 82646 | 1712 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | Y | Zn1193 Lindfield - Pnl.27 tripped & relcosed on: B & C phase O/C Abnormal: AB576 Open with LB244 Closed, iR49996 Open with LB62192 Closed, LB79087 Open with LB224 Closed (DMA) Bond burnt off LB46265 (Pole PY00006) See 1729842 1729843 | January | 2020 | 2020Q3 | 2020 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2020-01-20 | N | 48.2745 | N | 13 | N | N | 1.1101 | 39.4971 | 60395.2592
[7 empty] | 4439 | 11413 | 1724416 | 2020-01-20 06:04 | 2020-01-20 09:40 | 216 | 11kV | 432 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 206816 A Phase DOLF : 10 Amp Excluded OMS 1724416 | January | 2020 | 2020Q3 | 2020 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2020-01-20 | N | 216 | N | 13 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 4811 | 15123 | 1724404 | 2020-01-20 04:59 | 2020-01-20 09:56 | 297 | 11kV | 594 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 206817 Single phase DOLF : 10 Amp Excluded OMS 1724404 | January | 2020 | 2020Q3 | 2020 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2020-01-20 | N | 297 | N | 13 | N | N | 1.1101 | 39.4971 | 434.0777
[7 empty] | 4894 | 15899 | 1724428 | 2020-01-20 06:44 | 2020-01-20 10:45 | 241 | 11kV | 241 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 206819 B Phase DOLF : 10 Amp Excluded OMS 1724428 | January | 2020 | 2020Q3 | 2020 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2020-01-20 | N | 241 | N | 13 | N | N | 1.1101 | 39.4971 | 176.1157
[7 empty] | 5329 | 20183 | 1724459 | 2020-01-20 08:58 | 2020-01-20 12:00 | 182 | 11kV | 182 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 206823 Single phase DOLF : 10 Amp Excluded OMS 1724459 | January | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-01-20 | N | 182 | N | 13 | N | N | 1.1101 | 39.4971 | 133.0002
[7 empty] | 3581 | 2687 | 1725570 | 2020-01-20 13:18 | 2020-01-20 13:25 | 7 | 11kV | 532 | 76 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 206833 1 fault operation Overcurrent | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-01-20 | Y | 7 | N | 13 | N | Y | 1.1101 | 39.4971 | 388.7699
[7 empty] | 4696 | 14072 | 1724564 | 2020-01-20 13:36 | 2020-01-20 14:05 | 29 | 11kV | 87 | 3 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | Y | LID 206828 Garbage truck hit sub pole Excluded OMS 1724564 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-20 | N | 29 | N | 13 | N | N | 1.1101 | 39.4971 | 63.577
[7 empty] | 4046 | 7516 | 1724396 | 2020-01-20 00:21 | 2020-01-20 14:15 | 834 | 11kV | 48621 | 646 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At ZN12640 Umina 11kv feeder Panel No.1 "LB47844" feeder tripped and locked out on: Relays: E/f and efi Remarks: OH earth wire down. On cnr railway st and Nagari Rd, dislodged earth wire on No830 feeder coming into contact/tripping 66kv no830 feeder and Panel No1 ex ZN12640 Umina. | January | 2020 | 2020Q3 | 2020 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2020-01-20 | Y | 75.2647 | N | 13 | N | Y | 1.1101 | 39.4971 | 35530.7927
[7 empty] | 3632 | 3177 | 1724674 | 2020-01-20 15:21 | 2020-01-20 15:44 | 23 | 11kV | 23 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 206838 A Phase DOLF : 10 Amp Excluded OMS 1724674 | January | 2020 | 2020Q3 | 2020 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2020-01-20 | N | 23 | N | 13 | N | N | 1.1101 | 39.4971 | 16.8077
[7 empty] | 4537 | 12412 | 1724642 | 2020-01-20 14:35 | 2020-01-20 16:50 | 135 | 11kV | 7290 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 206849 DOLF : 20 Amp Excluded OMS 1724642 | January | 2020 | 2020Q3 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-01-20 | Y | 135 | N | 13 | N | Y | 1.1101 | 39.4971 | 5327.317
[7 empty] | 5183 | 18829 | 1724703 | 2020-01-20 16:05 | 2020-01-20 17:33 | 88 | 11kV | 792 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 206853 C Phase DOLF : 16 Amp Excluded OMS 1724703 | January | 2020 | 2020Q3 | 2020 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2020-01-20 | N | 88 | N | 13 | N | N | 1.1101 | 39.4971 | 578.7702
[7 empty] | 4628 | 13480 | 1725701 | 2020-01-20 14:58 | 2020-01-20 18:20 | 202 | 11kV | 2936 | 323 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Heavy | Y | Recloser CP20112 Kaland Rd Panel 2 L tripped and reclosed on Signals: Zone Earth Relays: OC trip Anormal Switching: LB20518 Closed, AB77332 Open Cause: Lightning strike at PT15862 See OMS 1725701 1725703 | January | 2020 | 2020Q3 | 2020 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2020-01-20 | N | 9.0898 | N | 13 | N | N | 1.1101 | 39.4971 | 2145.5422
[7 empty] | 5044 | 17738 | 1724627 | 2020-01-20 14:10 | 2020-01-20 18:35 | 265 | 11kV | 193343 | 1314 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 206859 A Phase Earth Fault Arresters pole NR-50182 replaced under AP | January | 2020 | 2020Q3 | 2020 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2020-01-20 | N | 147.1408 | N | 13 | N | N | 1.1101 | 39.4971 | 141289.3617
[7 empty] | 4908 | 16027 | 1724670 | 2020-01-20 15:11 | 2020-01-20 20:01 | 290 | 11kV | 72138 | 613 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | AT 14143 Somersby ZN section of P17 from CP45202 Pacific Ashbrooke 2.0 tirpped, reclosed and locked out on OC and lockout relays Remarks: tree/branch brought down OH near PT61530 | January | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-01-20 | N | 117.6803 | N | 13 | N | N | 1.1101 | 39.4971 | 52716.3227
[7 empty] | 4985 | 16995 | 1724745 | 2020-01-20 17:18 | 2020-01-20 20:20 | 182 | 11kV | 182 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 206861 Single phase DOLF : 10 Amp Replaced blown arrestor. Excluded OMS 1724745 | January | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2020-01-20 | Y | 182 | N | 13 | N | Y | 1.1101 | 39.4971 | 133.0002
[7 empty] | 3626 | 3075 | 1724898 | 2020-01-20 17:08 | 2020-01-20 20:40 | 212 | 11kV | 421946 | 2096 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9700 Kirrawee Panel 20 tripped on SEF with fault check Cause: Weather related See OMS 1726287 1726288 1724898 | January | 2020 | 2020Q3 | 2020 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2020-01-20 | Y | 201.3101 | N | 13 | N | Y | 1.1101 | 39.4971 | 308345.6915
[7 empty] | 3814 | 5183 | 1725130 | 2020-01-20 18:58 | 2020-01-20 21:15 | 137 | 11kV | 137339 | 1739 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | Y | Recloser CP63175 Griffin Adam Panel 7 tripped, reclosed and locked out on Signals: Zone Earth, CB open Cause: DOp reports blown surge arrestor on tee off UGOH to S16274 See OMS 1726253 1726254 1726255 1725130 1725246 | January | 2020 | 2020Q3 | 2020 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2020-01-20 | N | 78.9758 | N | 13 | N | N | 1.1101 | 39.4971 | 100363.2904
[7 empty] | 4552 | 12567 | 1725057 | 2020-01-20 18:26 | 2020-01-20 21:35 | 189 | 11kV | 189 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 206868 Single phase DOLF : 10 Amp Excluded OMS 1725057 | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-01-20 | Y | 189 | N | 13 | N | Y | 1.1101 | 39.4971 | 138.1156
[7 empty] | 4777 | 14793 | 1725175 | 2020-01-20 19:31 | 2020-01-21 00:53 | 321.25 | 11kV | 333136.25 | 1037 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Recloser 63641 Manchester View - Locked Out Abniormal Switching: Cause: SW/A closed at S47084, LB35855 Open Cause: Weather Related | January | 2020 | 2020Q3 | 2020 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2020-01-20 | Y | 321.25 | N | 13 | N | Y | 1.1101 | 39.4971 | 243446.1456
[7 empty] | 5170 | 18735 | 1725287 | 2020-01-20 21:26 | 2020-01-21 01:28 | 242 | 11kV | 7502 | 31 | HV | Fire (Non Ausgrid) | UNKNOWN | OTHER - REFER COMMENTS | Unplanned | Electrical Storm | Y | S65927 werrina Blue Dist No.1 "Werrina Pde N OH" Phase: ABC Fuse: 400A Remarks: fire. LV linkbox caught fire and required replacement. | January | 2020 | 2020Q3 | 2020 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | Unknown | Not Veg | 2020-01-20 | N | 242 | N | 13 | N | N | 1.1101 | 39.4971 | 5482.2403
[7 empty] | 5098 | 18221 | 1725332 | 2020-01-21 01:59 | 2020-01-21 03:37 | 98 | 11kV | 12103 | 172 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | zn14891 wyong panel 19 '12636 Pacific Howarth' has tripped and reclosed Signals: CB 19 Open, CB 19 Closed Remarks: animals/birds. Possum on mains at pole WY-1337 has caused a bond to burn off at Pole WY-1523 | January | 2020 | 2020Q3 | 2020 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | OH | Not Veg | 2020-01-21 | N | 70.3663 | N | 7 | N | N | 1.1101 | 39.4971 | 8844.5154
[7 empty] | 5217 | 19216 | 1725337 | 2020-01-20 17:03 | 2020-01-21 08:05 | 902 | 11kV | 413986 | 459 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | Y | Section of 11kV ex Panel 4 Miranda beyond LB35612 11kV bond burn off on UGOH Corner Milburn Rd and The Boulevarde See OMS 1729993 Note: customer calls advise part power had been occuring since the storm went thru on the evening of the 20th. Start date/time amended to 20/01/20 17:03 after the T&R on PA 4 during the storm and feeder patrol was requested 1725410 1725406 1725407 1725337 | January | 2020 | 2020Q3 | 2020 | ZN9037:PA4 | ZN9037:PA4 | ZN09037/000004 | SUTHERLAND | OH | Not Veg | 2020-01-20 | Y | 901.9303 | N | 13 | N | Y | 1.1101 | 39.4971 | 302528.7583
[7 empty] | 4045 | 7515 | 1725441 | 2020-01-21 07:50 | 2020-01-21 10:50 | 180 | 11kV | 1260 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 206875 B Phase DOLF : 31 Amp Excluded OMS 1725441 | January | 2020 | 2020Q3 | 2020 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Veg | 2020-01-21 | N | 180 | N | 7 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 4136 | 8546 | 1725498 | 2020-01-21 09:09 | 2020-01-21 11:00 | 111 | 11kV | 111 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 206874 B Phase DOLF : 10 Amp B ph 10 Amp hvf replaced. power restored 1100 Excluded oms1725498 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-21 | N | 111 | N | 7 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 3550 | 2495 | 1724043 | 2020-01-18 06:20 | 2020-01-21 11:05 | 4605 | 11kV | 225647 | 1156 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 206797 2 fault operations B & C phase Overcurrent HAZ switch failure. Excluded OMS 1724043 etc. | January | 2020 | 2020Q3 | 2020 | 213:33775 | 213:33775 | ZN00213/033775 | NEWCASTLE | Unknown | Not Veg | 2020-01-18 | N | 195.1964 | N | 6 | N | N | 1.1101 | 39.4971 | 164896.1721
[7 empty] | 5347 | 20413 | 1725594 | 2020-01-21 10:55 | 2020-01-21 12:00 | 65 | 11kV | 650 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 206880 B Phase DOLF : 10 Amp B PH 10 amp hvf replaced power restored 1200. Excluded OMS 1725594 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-21 | N | 65 | N | 7 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 4698 | 14084 | 1725363 | 2020-01-21 10:25 | 2020-01-21 12:05 | 100 | 11kV | 20600 | 206 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 206887 3 SUBS INTERRUPTED TO REPLACE 3 DOLF AT SUB 16118 Excluded OMS 1725363 | January | 2020 | 2020Q3 | 2020 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2020-01-21 | N | 100 | N | 7 | N | N | 1.1101 | 39.4971 | 15053.8724
[7 empty] | 4328 | 10433 | 1725267 | 2020-01-20 22:19 | 2020-01-21 12:45 | 866 | 11kV | 7794 | 9 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | Y | PT48466 Scenic Bounty Hill foot path side 11kv HDO 31.5A operated REmarks: lightning/surge arrestor footpath side damaged | January | 2020 | 2020Q3 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2020-01-20 | Y | 866 | N | 13 | N | Y | 1.1101 | 39.4971 | 5695.6253
[7 empty] | 3351 | 592 | 1725342 | 2020-01-20 18:12 | 2020-01-21 18:30 | 1458.4667 | 11kV | 192517.6 | 132 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At S9027 Bulwarra Willarong 40A C phase HV fuse blown Cause: Weather related | January | 2020 | 2020Q3 | 2020 | ZN9118:PA26 | ZN9118:PA26 | ZN09118/000026 | SUTHERLAND | OH | Not Veg | 2020-01-20 | Y | 1458.4667 | N | 13 | N | Y | 1.1101 | 39.4971 | 140686.1838
[7 empty] | 5091 | 18172 | 1725827 | 2020-01-21 21:27 | 2020-01-22 03:15 | 348 | 11kV | 9733 | 55 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 206897 4 fault operations Earth Fault 11kV OHM down at pole 8J-50007. Excluded OMS No. 1725827 | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-01-21 | N | 176.9636 | N | 7 | N | N | 1.1101 | 39.4971 | 7112.5893
[7 empty] | 4310 | 10309 | 1725832 | 2020-01-21 23:13 | 2020-01-22 07:55 | 522 | 11kV | 3132 | 6 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206899 B Phase DOLF : 16 Amp Dead Possom found on ground Excluded OMS 1725832 | January | 2020 | 2020Q3 | 2020 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2020-01-21 | N | 522 | N | 7 | N | N | 1.1101 | 39.4971 | 2288.7732
[7 empty] | 3624 | 3050 | 1725484 | 2020-01-20 18:21 | 2020-01-22 15:40 | 2719 | 11kV | 2719 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | NEW 3 PHASE SERVICE CONNECTED.RF11 COMPLETED AND CUSTOMER RE ENERGISED. | January | 2020 | 2020Q3 | 2020 | ZN9035:PA7 | ZN9035:PA7 | ZN09035/000007 | SUTHERLAND | OH | Veg | 2020-01-20 | Y | 2719 | N | 13 | N | Y | 1.1101 | 39.4971 | 1986.965
[7 empty] | 5327 | 20146 | 1724888 | 2020-01-20 17:12 | 2020-01-22 15:50 | 2798 | 11kV | 1347492 | 1752 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9037 Miranda Panel 8 tripped on earth fault with EFI, Timing and Lockout. Zone and No1 Group Earth Cause: DMA 1: 11kV Feeder S78680 to AB35181 tee PT9438 DMA 2: S9490 All distributors interrupted on CTW See OMS 1729136 1729138 1729140 1729142 1729141 | January | 2020 | 2020Q3 | 2020 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2020-01-20 | Y | 769.1164 | N | 13 | N | Y | 1.1101 | 39.4971 | 984707.4093
[7 empty] | 5017 | 17404 | 1725955 | 2020-01-22 13:09 | 2020-01-22 17:50 | 281 | 11kV | 1124 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Previous Storm | N | LID 206909 Pole 8k-30006 hit by lightning Low 11kV mains Insulator failed on pole 8K-30006 Blown Lightning arrestor sub 46670 Excluded OMS 1725955 | January | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-01-22 | N | 281 | N | 3 | N | N | 1.1101 | 39.4971 | 821.386
[7 empty] | 4848 | 15542 | 1725752 | 2020-01-21 16:35 | 2020-01-22 18:00 | 1525 | 11kV | 6100 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 206895 3 phase pole fire sub 51894 solar farm, sub fallen to ground and wires down, section isolated for repairs. Excluded oms 1725771 | January | 2020 | 2020Q3 | 2020 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2020-01-21 | N | 1525 | Y | 7 | N | Y | 1.1101 | 39.4971 | 4457.7001
[7 empty] | 4025 | 7261 | 1725327 | 2020-01-20 17:08 | 2020-01-22 19:30 | 3022 | 11kV | 1095412 | 1780 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | At S9700 Kirrawee Panel 16 tripped on A and C phase OC with fault check and EFI Abnormal Switching: DMA on PA17 CP35835 Open, LB35674 Closed LB35855 Open S47084 Closed Cause: UG cable fault @ Kirrawee Pa16. See OMS 1730008 1730010 1730011 | January | 2020 | 2020Q3 | 2020 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | UG | Not Veg | 2020-01-20 | Y | 615.4 | N | 13 | N | Y | 1.1101 | 39.4971 | 800494.7804
[7 empty] | 4703 | 14132 | 1724737 | 2020-01-20 17:12 | 2020-01-22 21:00 | 3108 | 11kV | 545784 | 666 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S9037 Miranda Panel 7 tripped on Zone and NO1 group earth Relays: Earth Leakage,EFI Cause: Tree branch brought down OH 0 AP left on section of 11kVa feeder from LB35779 to CP 35498 tee S9907 See OMS 1729567 1729569 1729570 1729571 1724737 14725331 176206 1726207 1726208 | January | 2020 | 2020Q3 | 2020 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Veg | 2020-01-20 | Y | 819.4955 | N | 13 | N | Y | 1.1101 | 39.4971 | 398842.8493
[7 empty] | 5077 | 18099 | 1726152 | 2020-01-22 18:18 | 2020-01-22 21:46 | 208 | 11kV | 102336 | 492 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | Wind Strong | N | At S9118 Cronulla ex Panel 3 CP35555 Opened Cause: AN 9118 Cronulla Panel 3 large tree branch has come down and snapped operating arm causing CB to oped. See OMS 1729553 1726179 1726164 1726161 1726152 CC1: 22-"Refer to SOp" | January | 2020 | 2020Q3 | 2020 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Veg | 2020-01-22 | N | 208 | N | 3 | N | N | 1.1101 | 39.4971 | 74784.1304
[7 empty] | 4492 | 11964 | 1726131 | 2020-01-22 16:59 | 2020-01-23 03:00 | 601 | 11kV | 17055 | 70 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 206912 2 fault operations A & B Phase Overcurrent; Earth Fault 66kV crossarm broke into 11kV Targets: A/Bph OC & EF | January | 2020 | 2020Q3 | 2020 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2020-01-22 | N | 243.6429 | N | 3 | N | N | 1.1101 | 39.4971 | 12463.291
[7 empty] | 4340 | 10519 | 1726230 | 2020-01-23 02:09 | 2020-01-23 08:43 | 394 | 11kV | 9222 | 41 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | Y | LID 206919 B Phase Burnt up B phase tapping at 11kV Link 40717. Excluded OMS 1726230. | January | 2020 | 2020Q3 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2020-01-23 | Y | 224.9268 | N | 7 | N | Y | 1.1101 | 39.4971 | 6739.1656
[7 empty] | 3667 | 3585 | 1726270 | 2020-01-23 08:34 | 2020-01-23 11:15 | 161 | 11kV | 2254 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | LID 206923 B Phase DOLF : 16 Amp Excluded OMS 1726270 | January | 2020 | 2020Q3 | 2020 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2020-01-23 | N | 161 | N | 7 | N | N | 1.1101 | 39.4971 | 1647.1567
[7 empty] | 5124 | 18400 | 1727305 | 2020-01-23 11:06 | 2020-01-23 14:40 | 214 | 11kV | 54133 | 326 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Hot >35C | Y | LID 206927 2 fault operation B Phase wire off pin on pole HY-30072 | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-01-23 | Y | 166.0521 | N | 7 | N | Y | 1.1101 | 39.4971 | 39558.7997
[7 empty] | 5316 | 20002 | 1728861 | 2020-01-23 16:30 | 2020-01-23 16:35 | 5 | 11kV | 340 | 68 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | Y | Zn3460 Sefton - Pnl.30 from S48418 Sw/A interrupted due to overload Interrupted to transfer load to Bass Hill zone (cross power source) | January | 2020 | 2020Q3 | 2020 | ZN3472:PA30 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2020-01-23 | N | 5 | N | 7 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 3540 | 2397 | 1726402 | 2020-01-23 11:55 | 2020-01-23 16:37 | 282 | 11kV | 199126 | 868 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | At S9252 jannali 11kV feeder Panel 25 tripped and locked out Cayse: Vegetation Normally Clear. See OMS 1731924 1731925 1726402 | January | 2020 | 2020Q3 | 2020 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Veg | 2020-01-23 | N | 229.4078 | N | 7 | N | N | 1.1101 | 39.4971 | 145515.4076
[7 empty] | 3292 | 52 | 1726635 | 2020-01-23 15:57 | 2020-01-23 17:13 | 76 | 11kV | 35832 | 477 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | Zn8000 Macquairie Park - Pnl.25 tripped on: Earth Fault UG cable fault between S5423 and S7739 See 1729882 1729883 | January | 2020 | 2020Q3 | 2020 | ZN8000:PA25 | ZN35500:PA26 | ZN35500/000026 | RYDE | UG | Not Veg | 2020-01-23 | Y | 75.1195 | N | 7 | N | Y | 1.1101 | 39.4971 | 26184.9687
[7 empty] | 3746 | 4461 | 1726484 | 2020-01-23 13:09 | 2020-01-23 18:06 | 297 | 11kV | 80828 | 277 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 206933 Targets needed Excluded OMS 1726484 | January | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2020-01-23 | Y | 291.7978 | N | 7 | N | Y | 1.1101 | 39.4971 | 59066.7184
[7 empty] | 3510 | 2114 | 1726883 | 2020-01-23 20:56 | 2020-01-23 22:35 | 99.4667 | 11kV | 1591.4667 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 206935 C Phase DOLF : 20 Amp | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-23 | N | 99.4667 | N | 7 | N | N | 1.1101 | 39.4971 | 1162.9969
[7 empty] | 4562 | 12705 | 1727118 | 2020-01-23 22:48 | 2020-01-24 00:47 | 119 | 11kV | 176486 | 1551 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | LID 206940 3 phase Earth Fault Excluded OMS 1727118 | January | 2020 | 2020Q3 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-01-23 | N | 113.7885 | N | 7 | N | N | 1.1101 | 39.4971 | 128970.7633
[7 empty] | 4411 | 11169 | 1726906 | 2020-01-23 21:15 | 2020-01-24 03:15 | 360 | 11kV | 19889 | 128 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 206939 A Phase Earth Fault Excluded OMS 1726896 | January | 2020 | 2020Q3 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2020-01-23 | N | 155.3828 | N | 7 | N | N | 1.1101 | 39.4971 | 14534.2946
[7 empty] | 3629 | 3109 | 1727232 | 2020-01-24 04:58 | 2020-01-24 06:20 | 82 | 11kV | 195884 | 2707 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn35600 Kingsford - Pnl.1 tripped on: Earth Fault UG cable fault between S36061 and S2684 See 1728702 1728703 | January | 2020 | 2020Q3 | 2020 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2020-01-24 | N | 72.362 | N | 23 | Y | Y | 1.1101 | 39.4971 | 143146.2496
[7 empty] | 3969 | 6629 | 1726935 | 2020-01-23 22:04 | 2020-01-24 07:55 | 591 | 11kV | 1182 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 206942 Single phase DOLF : 10 Amp Excluded OMS 1726935 | January | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-01-23 | N | 591 | N | 7 | N | N | 1.1101 | 39.4971 | 863.7707
[7 empty] | 3970 | 6630 | 1727249 | 2020-01-24 06:05 | 2020-01-24 08:25 | 140 | 11kV | 280 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 206944 A Phase DOLF : 10 Amp Excluded OMS 1727249 | January | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-01-24 | N | 140 | N | 23 | Y | Y | 1.1101 | 39.4971 | 204.6157
[7 empty] | 4522 | 12235 | 1726784 | 2020-01-23 18:49 | 2020-01-24 08:50 | 841 | 11kV | 192442 | 1228 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | Zn1610 Homebush Bay - Pnl.1 tripped on: Earth Fault Field EFIs; S8593, S7703 (many failed to operate) Abnormal: S4799 Sw/F closed with Flemington Pnl.41 open for load relief due to defective Tap Changer. UG cable fault between S7742 Sw/B and S8323 Sw/B. Delayed restoration due to no access to S7742 See 1728737 1728738 | January | 2020 | 2020Q3 | 2020 | ZN2466:PA41 | ZN36000:PA24 | ZN36000/000024 | CUMBERLAND | UG | Not Veg | 2020-01-23 | Y | 156.7117 | N | 7 | N | Y | 1.1101 | 39.4971 | 140630.9375
[7 empty] | 3691 | 3788 | 1727290 | 2020-01-24 07:16 | 2020-01-24 10:32 | 196 | 11kV | 392 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 206946 C Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-01-24 | N | 196 | N | 23 | Y | Y | 1.1101 | 39.4971 | 286.462
[7 empty] | 3353 | 610 | 1726652 | 2020-01-23 16:04 | 2020-01-24 11:17 | 1153.3333 | 11kV | 214673 | 2550 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | LID 206930 B Phase Earth Fault Excluded OMS 1726652 | January | 2020 | 2020Q3 | 2020 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Veg | 2020-01-23 | Y | 84.1855 | N | 7 | N | Y | 1.1101 | 39.4971 | 156876.6966
[7 empty] | 4823 | 15265 | 1728579 | 2020-01-24 09:45 | 2020-01-24 11:45 | 120 | 11kV | 1080 | 9 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Previous Storm | N | LID 206951 OMS 1727249 pole 7m 60131 split from lightening. | January | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-01-24 | N | 120 | N | 23 | Y | Y | 1.1101 | 39.4971 | 789.2321
[7 empty] | 4316 | 10343 | 1726604 | 2020-01-23 15:07 | 2020-01-24 12:00 | 1253 | 11kV | 11227 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 206938 Earth Fault Excluded OMS 1726604 | January | 2020 | 2020Q3 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-01-23 | Y | 193.569 | N | 7 | N | Y | 1.1101 | 39.4971 | 8204.3605
[7 empty] | 3554 | 2526 | 1727491 | 2020-01-24 11:57 | 2020-01-24 13:01 | 64 | 11kV | 1664 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 206954 X-arm brace bolt fallen out pole SI-60729 Excluded OMS 1727495 | January | 2020 | 2020Q3 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-01-24 | N | 64 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1216.0021
[7 empty] | 3659 | 3510 | 1727553 | 2020-01-24 12:49 | 2020-01-24 13:55 | 66 | 11kV | 132 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 206955 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 66 | N | 23 | Y | Y | 1.1101 | 39.4971 | 96.4617
[7 empty] | 3988 | 6849 | 1726641 | 2020-01-23 16:05 | 2020-01-24 14:30 | 1344.5167 | 11kV | 49747.1167 | 37 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | Y | S6999 Tennyson Victoria - RMCB operated Transformer failure | January | 2020 | 2020Q3 | 2020 | ZN35500:PA31 | ZN35500:PA31 | ZN35500/000031 | RYDE | UG | Not Veg | 2020-01-23 | Y | 1344.5167 | N | 7 | N | Y | 1.1101 | 39.4971 | 36353.7256
[7 empty] | 3612 | 2885 | 1727629 | 2020-01-24 15:16 | 2020-01-24 15:50 | 34 | 11kV | 34 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206974 B Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 34 | N | 23 | Y | Y | 1.1101 | 39.4971 | 24.8462
[7 empty] | 3342 | 483 | 1727357 | 2020-01-24 08:32 | 2020-01-24 16:05 | 453 | 11kV | 21693 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206979 1 fault operations 3 phases, overcurrent No further infomation provided in LID or in related records | January | 2020 | 2020Q3 | 2020 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2020-01-24 | N | 387.375 | N | 23 | Y | Y | 1.1101 | 39.4971 | 15852.6046
[7 empty] | 3373 | 724 | 1727657 | 2020-01-24 16:09 | 2020-01-24 18:45 | 156 | 11kV | 156 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206987 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 156 | N | 23 | Y | Y | 1.1101 | 39.4971 | 114.0002
[7 empty] | 3498 | 2011 | 1727658 | 2020-01-24 16:11 | 2020-01-24 19:40 | 209 | 11kV | 209 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206992 C Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 209 | N | 23 | Y | Y | 1.1101 | 39.4971 | 152.731
[7 empty] | 4655 | 13655 | 1727695 | 2020-01-24 17:01 | 2020-01-24 19:43 | 162.35 | 11kV | 2759.95 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206990 C Phase, 31 Amp Line DOLF SAO required, Sys diagram shows 40A Line Fuse 75433 31.5 Amp | January | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 162.35 | N | 23 | Y | Y | 1.1101 | 39.4971 | 2016.8901
[7 empty] | 3905 | 5994 | 1727600 | 2020-01-24 17:05 | 2020-01-24 20:10 | 185 | 11kV | 555 | 3 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 206980 no prptection operation 11kV section isolated to remove tree Excluded oms 1727600 & 1727682 | January | 2020 | 2020Q3 | 2020 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Veg | 2020-01-24 | N | 185 | N | 23 | Y | Y | 1.1101 | 39.4971 | 405.5776
[7 empty] | 4684 | 13958 | 1727638 | 2020-01-24 15:39 | 2020-01-24 20:45 | 306 | 11kV | 1761 | 6 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Electrical Storm | N | LID 206988 4 Amp Line DOLF Insulators damaged at pole 3J-10017 & 2J-30032 Sub 70744 went back on at 2045 | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-01-24 | N | 293.5 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1286.8869
[7 empty] | 4066 | 7743 | 1727708 | 2020-01-24 17:47 | 2020-01-24 21:05 | 198 | 11kV | 198 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206995 A Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 198 | N | 23 | Y | Y | 1.1101 | 39.4971 | 144.6926
[7 empty] | 4568 | 12791 | 1727727 | 2020-01-24 18:46 | 2020-01-24 21:08 | 142.4 | 11kV | 2278.4 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206993 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-24 | N | 142.4 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1664.9875
[7 empty] | 4058 | 7670 | 1727747 | 2020-01-24 19:37 | 2020-01-24 21:30 | 113 | 11kV | 226 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206996 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-24 | N | 113 | N | 23 | Y | Y | 1.1101 | 39.4971 | 165.1541
[7 empty] | 4837 | 15405 | 1727726 | 2020-01-24 18:45 | 2020-01-24 22:20 | 215 | 11kV | 430 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 206994 Single phase DOLF : 20 Amp Blown L/F 48165 Blown Dolf @ S 13228 & 19983.Faulty L/A cut away @ sub 13228. Excluded OMS 1727726 | January | 2020 | 2020Q3 | 2020 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2020-01-24 | N | 215 | N | 23 | Y | Y | 1.1101 | 39.4971 | 314.2313
[7 empty] | 4402 | 11078 | 1727782 | 2020-01-24 21:39 | 2020-01-24 22:35 | 56 | 11kV | 112 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207001 3 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-24 | N | 56 | N | 23 | Y | Y | 1.1101 | 39.4971 | 81.8463
[7 empty] | 4794 | 14986 | 1726951 | 2020-01-23 21:57 | 2020-01-24 22:48 | 1491 | 11kV | 562429 | 419 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | At ZN12630 Peats Ridge, 11kv panel 3 "Mangrove Mtn" tripped on: Relays: B & C O/C, reclose & lockout Signals: 11kv trip Rec46935 T&R at 21:52, then tripped and locked out 21:55 Remarks: storm. patrolled/repaired/restored | January | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2020-01-23 | Y | 1342.3126 | Y | 7 | N | Y | 1.1101 | 39.4971 | 411006.5244
[7 empty] | 4250 | 9786 | 1727739 | 2020-01-24 19:05 | 2020-01-24 23:25 | 259.5 | 11kV | 259.5 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207002 Single Phase, 10 Amp substation DOLF Suspect Lightning strike | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2020-01-24 | N | 259.5 | N | 23 | Y | Y | 1.1101 | 39.4971 | 189.6349
[7 empty] | 4144 | 8639 | 1727699 | 2020-01-24 17:30 | 2020-01-24 23:50 | 379.8167 | 11kV | 379.8167 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207000 Blown Lightning Arrestor Substation DOLF | January | 2020 | 2020Q3 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2020-01-24 | N | 379.8167 | N | 23 | Y | Y | 1.1101 | 39.4971 | 277.5588
[7 empty] | 4435 | 11362 | 1727705 | 2020-01-24 17:41 | 2020-01-25 00:30 | 409 | 11kV | 409 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207003 Tx leaking oil and service wire repair. Excluded OMS 1727705 DQ | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-01-24 | N | 409 | N | 23 | Y | Y | 1.1101 | 39.4971 | 298.8851
[7 empty] | 4605 | 13229 | 1727711 | 2020-01-24 17:53 | 2020-01-25 01:00 | 427 | 11kV | 1281 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 206989 A Phase, 10 Amp substation DOLF Blown Lightning Arrestor | January | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-01-24 | N | 427 | N | 23 | Y | Y | 1.1101 | 39.4971 | 936.117
[7 empty] | 5051 | 17833 | 1727022 | 2020-01-23 22:14 | 2020-01-25 11:00 | 2206 | 11kV | 1019454 | 1290 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12640 Umina - Pnl.12 tripped on SEF Tree branch on links 41466 See 1729655 1729656 1729658 1729659 1729660 | January | 2020 | 2020Q3 | 2020 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Veg | 2020-01-23 | Y | 790.2744 | Y | 7 | N | Y | 1.1101 | 39.4971 | 744986.9144
[7 empty] | 4199 | 9305 | 1726954 | 2020-01-23 21:57 | 2020-01-25 11:35 | 2258 | 11kV | 216156 | 242 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | At ZN12630 Peats Ridge, 11kv Panel 11 'Central mangrove' tripped on: Relays: BC O/C EFI, Timing and Lockout Signals: 11kv Trip Remarks: tree/branch on OH mains. Tree on mains between LB 40831 and Rec 46803 | January | 2020 | 2020Q3 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2020-01-23 | Y | 893.2066 | Y | 7 | N | Y | 1.1101 | 39.4971 | 157960.4293
[7 empty] | 5176 | 18779 | 1727894 | 2020-01-25 11:27 | 2020-01-25 12:20 | 53.2833 | 11kV | 53.2833 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207008 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-25 | N | 53.2833 | N | 14 | N | N | 1.1101 | 39.4971 | 38.9379
[7 empty] | 4674 | 13855 | 1727105 | 2020-01-23 22:01 | 2020-01-25 13:35 | 2374 | 11kV | 1398885 | 1729 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12650 west Gosford - Pnl.1 tripped on SEF Various storm damage along feeder. See 1729678 1729680 1729681 1729682 1729683 1729684 1729685 1729686 | January | 2020 | 2020Q3 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2020-01-23 | Y | 809.0717 | Y | 7 | N | Y | 1.1101 | 39.4971 | 1022263.8979
[7 empty] | 4333 | 10463 | 1727678 | 2020-01-24 16:57 | 2020-01-25 13:50 | 1253 | 11kV | 5215 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 207004 3 fault operations 3 phase Earth Fault Replaced damaged transformer. Excluded oms 1727678 | January | 2020 | 2020Q3 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2020-01-24 | N | 651.875 | Y | 23 | N | Y | 1.1101 | 39.4971 | 3810.9682
[7 empty] | 3392 | 882 | 1726986 | 2020-01-23 22:12 | 2020-01-25 14:15 | 2403.15 | 11kV | 181827.6 | 824 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12580 Erina - Pnl.8 tripped on SEL OH mains down near PT14717 See 1726986 1727339 | January | 2020 | 2020Q3 | 2020 | ZN12580:PA8 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2020-01-23 | Y | 220.6646 | N | 7 | N | Y | 1.1101 | 39.4971 | 132874.2471
[7 empty] | 5129 | 18429 | 1727913 | 2020-01-25 15:15 | 2020-01-25 15:20 | 5 | 11kV | 30 | 6 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | AB43135 Arcing on roadside phase. Opened and PT12835 interrupted to stop arcing. See 1729620 | January | 2020 | 2020Q3 | 2020 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2020-01-25 | N | 5 | N | 14 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 3588 | 2712 | 1727866 | 2020-01-25 10:53 | 2020-01-25 15:35 | 282.3667 | 11kV | 61273.5667 | 217 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kv feeder Pa.5 "Dooralong" IR.62705 Jilliby Durren tripped Remarks: tree branch contact - other. Bark on PT.14839 mandalong Dooralong 1.02 2X 10 HDO's also replaced | January | 2020 | 2020Q3 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2020-01-25 | N | 282.3667 | N | 14 | N | N | 1.1101 | 39.4971 | 44776.9153
[7 empty] | 4590 | 13072 | 1727935 | 2020-01-25 13:29 | 2020-01-25 15:35 | 126 | 11kV | 252 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207012 Single Phase substation DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-25 | N | 126 | N | 14 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 5068 | 17959 | 1727802 | 2020-01-25 06:38 | 2020-01-25 15:45 | 547 | 11kV | 1094 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 207011 B & C Phase DOLF : 10 Amp Replaced blown arrestors Excluded OMS 1727802 | January | 2020 | 2020Q3 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2020-01-25 | N | 547 | Y | 14 | N | Y | 1.1101 | 39.4971 | 799.4629
[7 empty] | 5062 | 17927 | 1726945 | 2020-01-23 22:02 | 2020-01-25 15:55 | 2513 | 11kV | 1453332 | 2052 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn12640 Umina - Pnl.13tripped on: B & C phase IOC Tree branch brought down mains outside 118 Brisbane Ave Umina. See 1729642 1729643 1729645 1729646 1729647 1729648 | January | 2020 | 2020Q3 | 2020 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2020-01-23 | Y | 708.2515 | Y | 7 | N | Y | 1.1101 | 39.4971 | 1062052.1596
[7 empty] | 4873 | 15732 | 1727948 | 2020-01-25 14:16 | 2020-01-25 16:20 | 124 | 11kV | 13268 | 107 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT10934 Gooroa Carwar centre phase HDO failed See OMS 1729935 1727948 | January | 2020 | 2020Q3 | 2020 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2020-01-25 | N | 124 | N | 14 | N | N | 1.1101 | 39.4971 | 9695.8631
[7 empty] | 4529 | 12306 | 1727954 | 2020-01-25 16:08 | 2020-01-25 17:38 | 89.4333 | 11kV | 3309.0333 | 37 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S6999 Tennyson Victoria - Interrupted for safety to remove generator and phase and restore transformer after failure | January | 2020 | 2020Q3 | 2020 | ZN35500:PA31 | ZN35500:PA31 | ZN35500/000031 | RYDE | UG | Not Veg | 2020-01-25 | N | 89.4333 | N | 14 | N | N | 1.1101 | 39.4971 | 2418.144
[7 empty] | 3688 | 3771 | 1726991 | 2020-01-23 21:55 | 2020-01-25 17:40 | 2625 | 11kV | 91654 | 94 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN12630 peats Ridge, 11kv Panel 13 tripped, reclosed and locked out on: Relays: B + C O/C, reclose and lockout Signals: 11kv trip Remarks: storm damage | January | 2020 | 2020Q3 | 2020 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2020-01-23 | Y | 975.0426 | Y | 7 | N | Y | 1.1101 | 39.4971 | 66978.0399
[7 empty] | 4858 | 15593 | 1727640 | 2020-01-24 17:00 | 2020-01-25 18:00 | 1500 | 11kV | 147000 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv Rec44607 Matcham North was opened for the removal of a tree off the 11kv OH. Section of 11kv Panel 10L "Wamebral Aux No.2" feeder at Zn14144 Wamberal Remarks: Tree/branch on OH mains. Tree branch on OH 24/01/20 17:00 CASS: A and B phase down between poles #WL2795 and #WL2794. EMSO spoke to AOP and isolated Dist #1 at PT13453. EMSO danger tagged PT and LV link #31938 then tested phases to prove deenergised. Multiple customers affected that rely on power for sewer and water. O/H please attend to make repairs | January | 2020 | 2020Q3 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-01-24 | N | 1500 | N | 23 | Y | Y | 1.1101 | 39.4971 | 107423.2642
[7 empty] | 4282 | 10028 | 1727966 | 2020-01-25 15:52 | 2020-01-25 18:00 | 128 | 11kV | 7040 | 55 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 207016 A Phase DOLF : 31 Amp faulty trans to be replaced next day, closed LVL 22074 to back feed Excluded oms 1727966 & 1727969 | January | 2020 | 2020Q3 | 2020 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Not Veg | 2020-01-25 | N | 128 | N | 14 | N | N | 1.1101 | 39.4971 | 5144.6244
[7 empty] | 4311 | 10312 | 1726477 | 2020-01-23 13:06 | 2020-01-25 18:05 | 3179 | 11kV | 265839 | 323 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | At ZN12630 Peats Ridge 11kv Panel '10', labelled 'Peats Ridge', tripped, reclosed and locked out on: Relays: B & C Phase, IOC, reclose and lockout Signals: 11kv trip iR61083 Bushells Peats 0.1 tripped, reclosed and locked out on: OC Trip. 13129 Kilpa Peats Ridge tee PT13989 Barakee Peats 0.9 tee PT18546 peats Ridge Barakee is defective. IR61083 tripped at 1609, 1.5 hours after first restoration. Section of 11kv feeder from LB47036 tee pT14881 Colong Barnes tee PT13923 Barn Remarks: tree brought down HV mains outside 1583 peats Ridge Rd. Section of 11kv feeder from LB44187 to LB45002 tee PT13923 is defectiv | January | 2020 | 2020Q3 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-01-23 | Y | 823.031 | Y | 7 | N | Y | 1.1101 | 39.4971 | 194267.3003
[7 empty] | 4598 | 13144 | 1727941 | 2020-01-25 13:39 | 2020-01-25 19:50 | 371 | 11kV | 371 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207018 Single Phase substation DOLF 10 Amp Fuse Replace Blown L/A | January | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2020-01-25 | N | 371 | N | 14 | N | N | 1.1101 | 39.4971 | 271.1159
[7 empty] | 4237 | 9615 | 1727990 | 2020-01-25 17:23 | 2020-01-25 21:30 | 247 | 11kV | 641 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207027 10 Amp Line DOLF Replaced Blown L/A at S64741 - 5 Amp fuse Line Fuse 65145 also blown | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2020-01-25 | N | 213.6667 | N | 14 | N | N | 1.1101 | 39.4971 | 468.4239
[7 empty] | 4279 | 10007 | 1727927 | 2020-01-25 19:45 | 2020-01-25 21:50 | 125 | 11kV | 375 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 207019 Blown Lightning Arrestor Excluded OMS 1727927 | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-01-25 | N | 125 | N | 14 | N | N | 1.1101 | 39.4971 | 274.0389
[7 empty] | 4242 | 9695 | 1728025 | 2020-01-25 20:46 | 2020-01-25 22:20 | 94 | 11kV | 188 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207029 C Phase substation DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-01-25 | N | 94 | N | 14 | N | N | 1.1101 | 39.4971 | 137.3849
[7 empty] | 3570 | 2620 | 1728024 | 2020-01-25 20:32 | 2020-01-25 22:39 | 127 | 11kV | 1137 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207026 1 Fault operations, Sectionaliser Patroled to visable areas, no fault found | January | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-01-25 | N | 126.3333 | N | 14 | N | N | 1.1101 | 39.4971 | 830.8861
[7 empty] | 3965 | 6600 | 1728010 | 2020-01-25 19:05 | 2020-01-25 23:20 | 255 | 11kV | 255 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207030 C Phase substation DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-01-25 | N | 255 | N | 14 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 3478 | 1812 | 1727794 | 2020-01-25 12:05 | 2020-01-26 02:20 | 855 | 11kV | 17955 | 21 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 207005 interupted to replace defective x arm pole JT92126 dq | January | 2020 | 2020Q3 | 2020 | 204:82689 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Not Veg | 2020-01-25 | N | 855 | N | 14 | N | N | 1.1101 | 39.4971 | 13120.9844
[7 empty] | 3790 | 4931 | 1728046 | 2020-01-26 07:17 | 2020-01-26 08:55 | 98 | 11kV | 98 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207032 Single Phase substation DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-01-26 | N | 98 | N | 30 | Y | Y | 1.1101 | 39.4971 | 71.6155
[7 empty] | 4559 | 12688 | 1728080 | 2020-01-26 08:37 | 2020-01-26 10:18 | 101 | 11kV | 122444 | 1590 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.13 tripped onL O/C & E/F Abnormal: S16559 Sw/B closed with Sw/A Open Customer reports flock of birds flying into 11kV on Suffolk Ave. Tee off UGOH to S16045 damaged. See 1728900 1728901 1728906 LV// 1728080 1728074 | January | 2020 | 2020Q3 | 2020 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2020-01-26 | N | 77.0088 | N | 30 | Y | Y | 1.1101 | 39.4971 | 89478.4637
[7 empty] | 4625 | 13472 | 1728052 | 2020-01-26 08:55 | 2020-01-26 11:10 | 135 | 11kV | 1620 | 12 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Nil operation of protection. Remarks: interrupted for safety reasons. 11kv OH off the pins and resting on the 11kv cross arm. A/P on issue @ 0940 | January | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2020-01-26 | N | 135 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 3640 | 3250 | 1728028 | 2020-01-25 20:55 | 2020-01-26 11:20 | 865 | 11kV | 6055 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207036 A and C phase 10 Amp, Substation DOLF | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-01-25 | N | 865 | Y | 14 | N | Y | 1.1101 | 39.4971 | 4424.8154
[7 empty] | 3301 | 161 | 1728062 | 2020-01-26 08:45 | 2020-01-26 12:10 | 205 | 11kV | 11275 | 55 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 207034 A Phase DOLF : 31 Amp Transformer changed Excluded OMS 1728062 | January | 2020 | 2020Q3 | 2020 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Not Veg | 2020-01-26 | N | 205 | N | 30 | Y | Y | 1.1101 | 39.4971 | 8239.4374
[7 empty] | 3934 | 6200 | 1726929 | 2020-01-23 21:51 | 2020-01-26 15:00 | 3909 | 11kV | 710965 | 257 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | @Sub 12630 Peats Ridge Ex Panel #1 Recloser 45189 Cooks Peats Ridge 0.5 tripped and locked out on OC trip Remarks: tree/branch brought down OH. See DMA from AB40602 to CP44945 | January | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-01-23 | Y | 2766.4008 | Y | 7 | N | Y | 1.1101 | 39.4971 | 519552.2521
[7 empty] | 3856 | 5574 | 1728129 | 2020-01-26 14:11 | 2020-01-26 15:00 | 49 | 11kV | 22442 | 458 | HV | Animal Goanna | Animal | O/H Conductor Unknown | Unplanned | Hot >35C | N | At ZN12690 Panel 24 'LB49474, LB49513' feeder has tripped Signals: 11kv trip Relays: IOC A ph, EFI Abnormal: open bonds below LB77831 Remarks: animals/birds. Goana came in contact with 11kv @ UGOH near LLB49474 and started a graass fire, RFS put it under control | January | 2020 | 2020Q3 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2020-01-26 | N | 49 | N | 30 | Y | Y | 1.1101 | 39.4971 | 16399.9517
[7 empty] | 3310 | 198 | 1728112 | 2020-01-26 13:00 | 2020-01-26 15:13 | 133 | 11kV | 7049 | 53 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 207037 33kV OHM off insulator at pole DF-90135. | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2020-01-26 | N | 133 | N | 30 | Y | Y | 1.1101 | 39.4971 | 5151.2013
[7 empty] | 5158 | 18662 | 1728135 | 2020-01-26 14:46 | 2020-01-26 16:05 | 79 | 11kV | 79 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207043 A and C, substation DOLF 10 Amp Fuses | January | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-01-26 | N | 79 | N | 30 | Y | Y | 1.1101 | 39.4971 | 57.7309
[7 empty] | 4048 | 7539 | 1728117 | 2020-01-26 13:35 | 2020-01-26 16:30 | 175 | 11kV | 5950 | 34 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | Zn12600 Lisarow Panel 2 "Holgate" interrupted from AB42920 to AB44993 Remarks: interrupted for safety reasons. See interruption @ Wamberal Panel 2 tree on N/O LB 43440 | January | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2020-01-26 | N | 175 | N | 30 | Y | Y | 1.1101 | 39.4971 | 4348.0845
[7 empty] | 3983 | 6721 | 1728156 | 2020-01-26 16:02 | 2020-01-26 18:30 | 148 | 11kV | 73089 | 898 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207051 1 fault operation A & C phase Overcurrent Excluded OMS 1728156 | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-01-26 | N | 81.3909 | N | 30 | Y | Y | 1.1101 | 39.4971 | 53411.2854
[7 empty] | 4731 | 14366 | 1728192 | 2020-01-26 17:49 | 2020-01-26 18:40 | 51 | 11kV | 255 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207068 DOLF : 10 Amp Excluded OMS 1728192 | January | 2020 | 2020Q3 | 2020 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2020-01-26 | N | 51 | N | 30 | Y | Y | 1.1101 | 39.4971 | 186.3465
[7 empty] | 4126 | 8450 | 1728151 | 2020-01-26 16:14 | 2020-01-26 20:02 | 228 | 11kV | 194816 | 990 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207067 2 Fault Operations Overcurrent; Earth Fault Feeder went back on after patrol Excluded OMS 1728151 | January | 2020 | 2020Q3 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2020-01-26 | N | 196.7838 | N | 30 | Y | Y | 1.1101 | 39.4971 | 142365.7867
[7 empty] | 4818 | 15206 | 1728183 | 2020-01-26 17:20 | 2020-01-26 20:43 | 203 | 11kV | 90745 | 497 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207069 1 fault operation Overcurrent Excluded OMS 1728183 | January | 2020 | 2020Q3 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-01-26 | N | 182.5855 | N | 30 | Y | Y | 1.1101 | 39.4971 | 66313.7695
[7 empty] | 3432 | 1354 | 1728186 | 2020-01-26 17:40 | 2020-01-26 21:41 | 241 | 11kV | 233529 | 969 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207074 1 fault operation Overcurrent Branch on OHM | January | 2020 | 2020Q3 | 2020 | 532:83293 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Veg | 2020-01-26 | N | 241 | N | 30 | Y | Y | 1.1101 | 39.4971 | 170656.1053
[7 empty] | 3598 | 2784 | 1728248 | 2020-01-26 19:13 | 2020-01-26 22:02 | 169 | 11kV | 3042 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207075 1 Fault operations Targets Required | January | 2020 | 2020Q3 | 2020 | 813:89058 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Veg | 2020-01-26 | N | 169 | N | 30 | Y | Y | 1.1101 | 39.4971 | 2223.0039
[7 empty] | 3323 | 323 | 1728205 | 2020-01-26 18:05 | 2020-01-26 22:25 | 260 | 11kV | 260 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207070 Single Phase substation DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-01-26 | N | 260 | N | 30 | Y | Y | 1.1101 | 39.4971 | 190.0003
[7 empty] | 3734 | 4297 | 1728235 | 2020-01-26 18:46 | 2020-01-26 23:15 | 269 | 11kV | 31000 | 293 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 207071 10 Amp fuse, Intellirupter Recloser locked out but 3 subs had blon dolfs. See emergency SI S 53478 A ph 10 Amp S 53479 B Ph 10 Amp S 51535 A ph 10 Amp. Blown L/A Tx Faulty as well. Put in LV parallel. via LVL 49507 & 49626 | January | 2020 | 2020Q3 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2020-01-26 | N | 105.802 | N | 30 | Y | Y | 1.1101 | 39.4971 | 22653.8857
[7 empty] | 3443 | 1440 | 1728141 | 2020-01-26 17:30 | 2020-01-26 23:57 | 387 | 11kV | 424960 | 1290 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 207089 A Phase tapping burnt off at pole IR32807 Excluded oms 1728141## DQ | January | 2020 | 2020Q3 | 2020 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2020-01-26 | N | 329.4264 | N | 30 | Y | Y | 1.1101 | 39.4971 | 310548.2338
[7 empty] | 3573 | 2632 | 1728236 | 2020-01-26 18:51 | 2020-01-27 01:26 | 395 | 11kV | 7110 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207088 B Phase, Line DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-26 | N | 395 | N | 30 | Y | Y | 1.1101 | 39.4971 | 5195.7783
[7 empty] | 3722 | 4136 | 1728265 | 2020-01-26 19:47 | 2020-01-27 01:54 | 367 | 11kV | 5872 | 16 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207101 C Phase, 10 Amp substation DOLF Customer reported seeing Lightning strike | January | 2020 | 2020Q3 | 2020 | 526:34641 | 526:34641 | ZN00526/034641 | SINGLETON | OH | Not Veg | 2020-01-26 | N | 367 | N | 30 | Y | Y | 1.1101 | 39.4971 | 4291.0844
[7 empty] | 3484 | 1858 | 1732157 | 2020-01-26 18:50 | 2020-01-27 02:36 | 466 | 11kV | 6058 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207091 B and C Phases, LINE DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-26 | N | 466 | N | 30 | Y | Y | 1.1101 | 39.4971 | 4427.0077
[7 empty] | 3345 | 503 | 1728166 | 2020-01-26 16:46 | 2020-01-27 02:41 | 595 | 11kV | 1190 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207094 C Phase DOLF : 10 Amp Excluded OMS 1728166 | January | 2020 | 2020Q3 | 2020 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2020-01-26 | N | 595 | N | 30 | Y | Y | 1.1101 | 39.4971 | 869.6169
[7 empty] | 5344 | 20371 | 1728319 | 2020-01-26 21:33 | 2020-01-27 02:45 | 312 | 11kV | 13640 | 137 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207076 OMS 1728319 & 1728319 No Protection Operation Wires alive on the ground at pole 5I-10002 Mountain Staion Rd | January | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2020-01-26 | N | 99.562 | N | 30 | Y | Y | 1.1101 | 39.4971 | 9967.7097
[7 empty] | 3530 | 2292 | 1728159 | 2020-01-26 16:14 | 2020-01-27 03:20 | 666 | 11kV | 20431 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207092 3 phase Overcurrent; Earth Fault Excluded OMS 1728159 | January | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-01-26 | N | 475.1395 | N | 30 | Y | Y | 1.1101 | 39.4971 | 14930.3722
[7 empty] | 4726 | 14341 | 1728322 | 2020-01-26 21:45 | 2020-01-27 03:35 | 350 | 11kV | 350 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207093 C Phase 10 Amp Substation DOLF | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-26 | N | 350 | N | 30 | Y | Y | 1.1101 | 39.4971 | 255.7697
[7 empty] | 4044 | 7502 | 1728280 | 2020-01-26 02:50 | 2020-01-27 04:50 | 1560 | 11kV | 10626 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207096 Single Phase substation DOLF 5 Amp Fuse Defective Lightning Arrestor sub 70774 | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-01-26 | N | 1518 | Y | 30 | N | Y | 1.1101 | 39.4971 | 7765.1674
[7 empty] | 3682 | 3738 | 1728191 | 2020-01-26 17:49 | 2020-01-27 06:10 | 741 | 11kV | 741 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207098 Single phase sub isolated to replace arrestor. Excluded oms 1728191 | January | 2020 | 2020Q3 | 2020 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2020-01-26 | N | 741 | N | 30 | Y | Y | 1.1101 | 39.4971 | 541.5009
[7 empty] | 3441 | 1388 | 1728325 | 2020-01-26 22:10 | 2020-01-27 07:15 | 545 | 11kV | 2180 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 207102 Single Phase sub isolated to replace LVF assembly | January | 2020 | 2020Q3 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2020-01-26 | N | 545 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1593.0797
[7 empty] | 4320 | 10380 | 1728359 | 2020-01-27 06:55 | 2020-01-27 07:30 | 35 | 11kV | 245 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207103 B Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2020-01-27 | N | 35 | N | 16 | N | N | 1.1101 | 39.4971 | 179.0388
[7 empty] | 4926 | 16334 | 1728307 | 2020-01-26 15:23 | 2020-01-27 08:30 | 1027 | 11kV | 5135 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207107 B Phase DOLF : 10 Amp Excluded OMS 1728307 | January | 2020 | 2020Q3 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-01-26 | N | 1027 | Y | 30 | N | Y | 1.1101 | 39.4971 | 3752.5065
[7 empty] | 4877 | 15752 | 1728374 | 2020-01-27 07:53 | 2020-01-27 08:45 | 52 | 11kV | 52 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207110 20 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-01-27 | N | 52 | N | 16 | N | N | 1.1101 | 39.4971 | 38.0001
[7 empty] | 5107 | 18277 | 1728368 | 2020-01-27 07:25 | 2020-01-27 09:05 | 99.8167 | 11kV | 598.9 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207106 B Phase , 10 Amp LINE DOLF also found blown dolf at sub 52550 and 52549, both B phase | January | 2020 | 2020Q3 | 2020 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2020-01-27 | N | 99.8167 | N | 16 | N | N | 1.1101 | 39.4971 | 437.6585
[7 empty] | 4431 | 11311 | 1728369 | 2020-01-27 07:34 | 2020-01-27 09:55 | 141 | 11kV | 423 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207108 C Phase substation DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2020-01-27 | N | 141 | N | 16 | N | N | 1.1101 | 39.4971 | 309.1159
[7 empty] | 3383 | 826 | 1732169 | 2020-01-27 10:37 | 2020-01-27 11:03 | 26 | 11kV | 6344 | 244 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207132 A, B and C phases Ple Mounted RAGCB Sensitive Earth Fault Recloser operated when staff tried back DOLF to faulty arrestor @ sub 51246 | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-27 | N | 26 | N | 16 | N | N | 1.1101 | 39.4971 | 4636.0081
[7 empty] | 4662 | 13741 | 1728241 | 2020-01-26 20:05 | 2020-01-27 11:33 | 928.7333 | 11kV | 33434.4 | 36 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | no futher information supplied assumed information from field is correct Nev Smith assigned 2 x 10 line fuses replaced power restored 1030. mdv | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-01-26 | N | 928.7333 | N | 30 | Y | Y | 1.1101 | 39.4971 | 24432.8734
[7 empty] | 4964 | 16768 | 1728308 | 2020-01-26 21:07 | 2020-01-27 12:10 | 903 | 11kV | 4515 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207115 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2020-01-26 | N | 903 | N | 30 | Y | Y | 1.1101 | 39.4971 | 3299.4288
[7 empty] | 4609 | 13292 | 1732161 | 2020-01-27 06:30 | 2020-01-27 13:20 | 410 | 11kV | 5330 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207126 Single phase DOLF : 10 Amp Kane Colburt assigned to replace line dolf | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-27 | N | 410 | N | 16 | N | N | 1.1101 | 39.4971 | 3895.0068
[7 empty] | 3360 | 640 | 1729119 | 2020-01-26 17:10 | 2020-01-27 13:25 | 1215 | 11kV | 53573 | 145 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207097 4 fault operations 3 phase Overcurrent mains down pole IP-95072 Excluded OMS 1728180 | January | 2020 | 2020Q3 | 2020 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2020-01-26 | N | 369.469 | N | 30 | Y | Y | 1.1101 | 39.4971 | 39149.5683
[7 empty] | 4438 | 11410 | 1728160 | 2020-01-27 08:51 | 2020-01-27 13:48 | 297.1667 | 11kV | 26745 | 90 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Region to follow up reairs 0830 Monday , region to submit papers , LV// fail for existing DMA , Zn Tx No2 @ epping made manual at top of range to assist volts . | January | 2020 | 2020Q3 | 2020 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Not Veg | 2020-01-27 | N | 297.1667 | N | 16 | N | N | 1.1101 | 39.4971 | 19544.4572
[7 empty] | 4604 | 13215 | 1726921 | 2020-01-23 21:57 | 2020-01-27 16:42 | 5445 | 11kV | 1702425 | 869 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S14143 Somersby Panel 17 tripped on A and B phase IOC Signals: 11kV Tip, Field EFi's NIL Cause: Tree on HV adjacent to Link 41695 See OMS 1729829/831/835/837/838/840/850/834/854/833/836/851/855/856/852/853 excluded OMS 1726921/7169/7471/7760/7761/7762/7763/7774/7976/7977/7984/7985/8051/8977 | January | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-01-23 | Y | 1959.0621 | Y | 7 | N | Y | 1.1101 | 39.4971 | 1244081.977
[7 empty] | 3551 | 2502 | 1728491 | 2020-01-27 15:17 | 2020-01-27 17:00 | 103 | 11kV | 412 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207147 Single Phase, 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2020-01-27 | N | 103 | N | 16 | N | N | 1.1101 | 39.4971 | 301.0774
[7 empty] | 4185 | 9234 | 1728426 | 2020-01-27 10:24 | 2020-01-27 17:20 | 416 | 11kV | 3328 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 207140 section isolated to repair burnt off tapping to lf 40879 Excluded oms 1728426 | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-01-27 | N | 416 | N | 16 | N | N | 1.1101 | 39.4971 | 2432.0042
[7 empty] | 3892 | 5870 | 1728215 | 2020-01-26 16:58 | 2020-01-27 17:50 | 1492 | 11kV | 283358 | 254 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207072 1 fault operation Tree on OHM pole IP-82410 Possible high into Low Excluded OMS 1728179, 1728180 | January | 2020 | 2020Q3 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2020-01-26 | N | 1115.5827 | Y | 30 | N | Y | 1.1101 | 39.4971 | 207069.6688
[7 empty] | 3841 | 5436 | 1728477 | 2020-01-27 14:36 | 2020-01-27 17:50 | 194 | 11kV | 2522 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207146 C Phase DOLF : 31 Amp Excluded OMS 1728477 | January | 2020 | 2020Q3 | 2020 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2020-01-27 | N | 194 | N | 16 | N | N | 1.1101 | 39.4971 | 1843.0032
[7 empty] | 4132 | 8503 | 1729304 | 2020-01-27 17:20 | 2020-01-27 18:30 | 70 | 11kV | 73080 | 1044 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207144 Open for clearance for 33kV OHM repair No further information supplied, no related records to be found | January | 2020 | 2020Q3 | 2020 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2020-01-27 | N | 70 | N | 16 | N | N | 1.1101 | 39.4971 | 53404.7085
[7 empty] | 3616 | 2969 | 1728504 | 2020-01-27 16:40 | 2020-01-27 19:40 | 180 | 11kV | 1080 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207150 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-01-27 | N | 180 | N | 16 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 4323 | 10404 | 1728452 | 2020-01-27 12:02 | 2020-01-27 20:00 | 478 | 11kV | 1434 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207152 Substation DOLF Faulty arrestors replaced at sub 54114 under AP. All other subs checked for supply OK. | January | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-01-27 | N | 478 | N | 16 | N | N | 1.1101 | 39.4971 | 1047.9249
[7 empty] | 3305 | 181 | 1728526 | 2020-01-27 18:31 | 2020-01-27 20:27 | 116 | 11kV | 10324 | 89 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207148 63 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 238:34148 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-01-27 | N | 116 | N | 16 | N | N | 1.1101 | 39.4971 | 7544.4747
[7 empty] | 4135 | 8523 | 1728226 | 2020-01-26 18:39 | 2020-01-27 21:01 | 1582.4333 | 11kV | 124928.2667 | 776 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | LID 207073 1 Fault operations A, B and C phases, Sensitive Earth Fault Refer to OMS 1728318/1728226. Fdr tripped on SEF at approx same time report of explosion at 9309 Pflug sub with blown Bph dolf due to surge arrestors. Fdr patrolled OK please check relay events for correct operation. Dop Williams DQ | January | 2020 | 2020Q3 | 2020 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2020-01-26 | N | 160.99 | N | 30 | Y | Y | 1.1101 | 39.4971 | 91293.8925
[7 empty] | 4420 | 11239 | 1728407 | 2020-01-27 09:19 | 2020-01-27 21:10 | 711 | 11kV | 4266 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207151 Line DOLF 10 Amp Fuse | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-27 | N | 711 | N | 16 | N | N | 1.1101 | 39.4971 | 3117.467
[7 empty] | 4826 | 15273 | 1728410 | 2020-01-27 09:30 | 2020-01-27 22:10 | 759.9833 | 11kV | 28879.3667 | 38 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Previous Storm | N | LID 207155 Single Phase 10 Amp substation DOLF Arrestors and transformer replaced under AP | January | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-01-27 | N | 759.9833 | N | 16 | N | N | 1.1101 | 39.4971 | 21104.1894
[7 empty] | 4440 | 11415 | 1728594 | 2020-01-28 08:49 | 2020-01-28 11:20 | 151 | 11kV | 302 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207166 A Phase DOLF : 16 Amp Excluded OMS 1728594 | January | 2020 | 2020Q3 | 2020 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2020-01-28 | N | 151 | N | 34 | Y | Y | 1.1101 | 39.4971 | 220.6927
[7 empty] | 3730 | 4242 | 1728590 | 2020-01-28 08:33 | 2020-01-28 12:15 | 222 | 11kV | 444 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 207171 Single phase DOLF : 10 Amp Excluded OMS 1728590 | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-01-28 | N | 222 | N | 34 | Y | Y | 1.1101 | 39.4971 | 324.4621
[7 empty] | 3763 | 4742 | 1728585 | 2020-01-28 08:23 | 2020-01-28 12:25 | 242 | 11kV | 484 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207170 B Phase DOLF : 10 Amp Excluded OMS 1728585 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-28 | N | 242 | N | 34 | Y | Y | 1.1101 | 39.4971 | 353.6929
[7 empty] | 3657 | 3491 | 1728636 | 2020-01-28 09:49 | 2020-01-28 12:57 | 188 | 11kV | 3264 | 277 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Previous Storm | N | LID 207173 11kV Link 40839 burning up. Excluded OMS 1728636/ 1728701/ 1728587 | January | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-01-28 | N | 11.7834 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2385.2349
[7 empty] | 5032 | 17573 | 1728688 | 2020-01-28 11:21 | 2020-01-28 13:25 | 124 | 11kV | 47968 | 494 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.26 tripped on: O/C & E/F Anormal: S1161 Sw/B Closed with S7739 Sw/D Open UG cable fault between S35394 and S6171 See 1729786 1729788 1729789 | January | 2020 | 2020Q3 | 2020 | ZN8000:PA25 | ZN35500:PA26 | ZN35500/000026 | RYDE | UG | Not Veg | 2020-01-28 | N | 97.1012 | N | 34 | Y | Y | 1.1101 | 39.4971 | 35053.5996
[7 empty] | 5292 | 19765 | 1728837 | 2020-01-28 14:13 | 2020-01-28 15:34 | 81 | 11kV | 112539 | 1449 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 paddington - Pnl.18 tripped on: A Phase O/C UG cable fault between S935 Sw/B, S7468 Sw/A, S6816 Sw/A and S3692 Sw/A See 1729555 1729556 | January | 2020 | 2020Q3 | 2020 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2020-01-28 | N | 77.6667 | N | 34 | Y | Y | 1.1101 | 39.4971 | 82240.1819
[7 empty] | 4608 | 13269 | 1728931 | 2020-01-28 15:30 | 2020-01-28 17:00 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207179 Single phase DOLF : 10 Amp Excluded OMS 1728931 | January | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2020-01-28 | N | 90 | N | 34 | Y | Y | 1.1101 | 39.4971 | 65.7693
[7 empty] | 4931 | 16417 | 1728952 | 2020-01-28 16:16 | 2020-01-28 17:13 | 57 | 11kV | 2565 | 45 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 207180 Isolated section of 11kV & LV OHM to remove tree branch Excluded OMS 1728757, 1728865, 1728952 | January | 2020 | 2020Q3 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-01-28 | N | 57 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1874.4263
[7 empty] | 4113 | 8315 | 1728970 | 2020-01-28 17:18 | 2020-01-28 18:52 | 94 | 11kV | 57622 | 613 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Recloser CP45202 PAcific Ashbrook 2.0 tripped on Relays: OC trip/ Lockout Cause: Tree hit 111kV OH near PT61530 See OMS 1729776 1728970 Abnormal: CP43276 open and Defective (Customers Interrupted) | January | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-01-28 | N | 94 | N | 34 | Y | Y | 1.1101 | 39.4971 | 42108.458
[7 empty] | 4481 | 11831 | 1728965 | 2020-01-28 16:09 | 2020-01-28 19:24 | 195 | 11kV | 835 | 59 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | 11kv Rec.45083 Durren tripped the recloser Relays: IOC trip, EF trip Section of 11kv Panel 5 'Wyong' feeder at ZN14891 Wyong Remarks: lightning/ surge arrestor. Arrestor blown at PT13701 Smiths Durren 1.1 | January | 2020 | 2020Q3 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2020-01-28 | N | 14.1525 | N | 34 | Y | Y | 1.1101 | 39.4971 | 610.1934
[7 empty] | 4757 | 14536 | 1728916 | 2020-01-28 15:20 | 2020-01-28 20:00 | 280 | 11kV | 38718 | 141 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207195 Overcurrent Excluded OMS 1728916 | January | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-01-28 | N | 274.5957 | N | 34 | Y | Y | 1.1101 | 39.4971 | 28293.9724
[7 empty] | 4094 | 8128 | 1729003 | 2020-01-28 19:09 | 2020-01-28 20:15 | 66 | 11kV | 726 | 11 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | PT18856 Abundance Scenic - Footpath phase HDO operated Lightning | January | 2020 | 2020Q3 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2020-01-28 | N | 66 | N | 34 | Y | Y | 1.1101 | 39.4971 | 530.5394
[7 empty] | 4642 | 13564 | 1729027 | 2020-01-28 19:39 | 2020-01-28 20:29 | 50 | 11kV | 7250 | 145 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207191 3 fault operations 3 phase Intellirupter; Overcurrent Bark on mains pole GS-51319 | January | 2020 | 2020Q3 | 2020 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2020-01-28 | N | 50 | N | 34 | Y | Y | 1.1101 | 39.4971 | 5298.0862
[7 empty] | 5088 | 18162 | 1729033 | 2020-01-28 19:55 | 2020-01-28 20:44 | 49 | 11kV | 245 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207194 A Phase DOLF : 10 Amp Excluded OMS 1729033 | January | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-01-28 | N | 49 | N | 34 | Y | Y | 1.1101 | 39.4971 | 179.0388
[7 empty] | 3812 | 5120 | 1729019 | 2020-01-28 19:36 | 2020-01-28 21:25 | 109 | 11kV | 109 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207198 Single phase DOLF : 10 Amp Excluded OMS 1729019 | January | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-01-28 | N | 109 | N | 34 | Y | Y | 1.1101 | 39.4971 | 79.654
[7 empty] | 3562 | 2587 | 1729013 | 2020-01-28 19:00 | 2020-01-28 22:00 | 180 | 11kV | 3240 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207207 3 phase DOLF : 10 Amp Excluded OMS 1729013 | January | 2020 | 2020Q3 | 2020 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2020-01-28 | N | 180 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2367.6964
[7 empty] | 5063 | 17931 | 1729043 | 2020-01-28 20:19 | 2020-01-28 22:05 | 105.5667 | 11kV | 422.2667 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207203 A & B Phase DOLF : 20 Amp | January | 2020 | 2020Q3 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2020-01-28 | N | 105.5667 | N | 34 | Y | Y | 1.1101 | 39.4971 | 308.58
[7 empty] | 4883 | 15814 | 1729009 | 2020-01-28 19:00 | 2020-01-28 22:10 | 190 | 11kV | 190 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207206 Single phase DOLF : 10 Amp | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-01-28 | N | 190 | N | 34 | Y | Y | 1.1101 | 39.4971 | 138.8464
[7 empty] | 3321 | 311 | 1729040 | 2020-01-28 19:31 | 2020-01-29 01:00 | 329 | 11kV | 1974 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207220 3 phase DOLF : 10 Amp Excluded OMS 1729040 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-28 | N | 329 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1442.541
[7 empty] | 3819 | 5256 | 1729034 | 2020-01-28 20:00 | 2020-01-29 01:05 | 305 | 11kV | 610 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207216 Arrestors changed under AP Excluded OMS 1729034. | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-28 | N | 305 | N | 34 | Y | Y | 1.1101 | 39.4971 | 445.77
[7 empty] | 4412 | 11174 | 1729012 | 2020-01-28 19:35 | 2020-01-29 01:30 | 355 | 11kV | 35221 | 112 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207209 4 fault operations A & B Phases Overcurrent Tree on mains FN-20057 Excluded oms 1729012. | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-28 | N | 314.4732 | N | 34 | Y | Y | 1.1101 | 39.4971 | 25738.468
[7 empty] | 3874 | 5713 | 1729066 | 2020-01-28 21:18 | 2020-01-29 02:20 | 302 | 11kV | 400884 | 1898 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 207303 1 fault operation A Phase Overcurrent ELB 2444 damaged by lightning. Excluded OMS 1729067. | January | 2020 | 2020Q3 | 2020 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2020-01-28 | N | 211.2139 | N | 34 | Y | Y | 1.1101 | 39.4971 | 292954.2031
[7 empty] | 3404 | 1011 | 1732026 | 2020-01-28 21:18 | 2020-01-29 02:20 | 302 | 11kV | 247628 | 1348 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 207304 1 fault operation A Phase Overcurrent ELB 2444 damaged by lightning. Excluded OMS 1729066. | January | 2020 | 2020Q3 | 2020 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2020-01-28 | N | 183.7003 | N | 34 | Y | Y | 1.1101 | 39.4971 | 180959.2386
[7 empty] | 4727 | 14342 | 1729108 | 2020-01-28 19:31 | 2020-01-29 02:20 | 409 | 11kV | 409 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207221 A Phase DOLF : 10 Amp Arrestor changed under AP | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-28 | N | 409 | N | 34 | Y | Y | 1.1101 | 39.4971 | 298.8851
[7 empty] | 5073 | 17994 | 1729078 | 2020-01-29 00:55 | 2020-01-29 02:23 | 88 | 11kV | 13200 | 150 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207218 no protection operations. Loose earth wire pole KR-90066 repaired under AP | January | 2020 | 2020Q3 | 2020 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2020-01-29 | N | 88 | N | 14 | N | N | 1.1101 | 39.4971 | 9646.1707
[7 empty] | 5132 | 18442 | 1729016 | 2020-01-28 19:31 | 2020-01-29 02:40 | 429 | 11kV | 4290 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207222 Single phase DOLF : 20 Amp Excluded OMS 1729016 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-28 | N | 429 | N | 34 | Y | Y | 1.1101 | 39.4971 | 3135.0055
[7 empty] | 3997 | 6945 | 1729054 | 2020-01-28 20:58 | 2020-01-29 04:15 | 437 | 11kV | 437 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207219 B & C Phase DOLF : 10 Amp Arrestors replaced under AP Excluded OMS 1729054. | January | 2020 | 2020Q3 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2020-01-28 | N | 437 | N | 34 | Y | Y | 1.1101 | 39.4971 | 319.3467
[7 empty] | 3948 | 6428 | 1729087 | 2020-01-28 22:41 | 2020-01-29 04:50 | 369 | 11kV | 178030 | 1640 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 207204 1 fault operation 3 phase Sensitive Earth Fault 11kV cross arm broken pole NR-60093 replaced under AP Excluded OMS 81440. | January | 2020 | 2020Q3 | 2020 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2020-01-28 | N | 108.5549 | N | 34 | Y | Y | 1.1101 | 39.4971 | 130099.073
[7 empty] | 4456 | 11560 | 1729105 | 2020-01-29 04:37 | 2020-01-29 05:32 | 55 | 11kV | 56265 | 1023 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.43 tripped on : B & C phase O/C Bat caused flashover near PT2338 | January | 2020 | 2020Q3 | 2020 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2020-01-29 | N | 55 | N | 14 | N | N | 1.1101 | 39.4971 | 41116.8025
[7 empty] | 4106 | 8221 | 1729048 | 2020-01-28 20:32 | 2020-01-29 07:40 | 668 | 11kV | 1336 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207234 Single Phase 10 Amp substation DOLF | January | 2020 | 2020Q3 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2020-01-28 | N | 668 | N | 34 | Y | Y | 1.1101 | 39.4971 | 976.3094
[7 empty] | 5275 | 19636 | 1732046 | 2020-01-29 05:29 | 2020-01-29 09:40 | 251 | 11kV | 1757 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207235 C Phase DOLF : 10 Amp L/F not sub | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-01-29 | N | 251 | N | 14 | N | N | 1.1101 | 39.4971 | 1283.9638
[7 empty] | 4774 | 14781 | 1729130 | 2020-01-29 07:39 | 2020-01-29 09:58 | 139 | 11kV | 301320 | 2270 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Kogarah Panel 11 tripped on 50TBC 1.3.1 Fault 1: UG cable fault from S10005 tio S63035 to LB31199 Fault 2: 11kV Bond arcing beyond CP30157 Pa11 interrupted by AOp See OMS 1730024 1730025 1730027 17300287 1729254 1729252 1729212 | January | 2020 | 2020Q3 | 2020 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | UG | Not Veg | 2020-01-29 | N | 132.7401 | N | 14 | N | N | 1.1101 | 39.4971 | 220195.7686
[7 empty] | 3817 | 5239 | 1729116 | 2020-01-29 07:19 | 2020-01-29 10:58 | 219 | 11kV | 1095 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207239 C Phase DOLF : 10 Amp Excluded OMS 1729116 | January | 2020 | 2020Q3 | 2020 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2020-01-29 | N | 219 | N | 14 | N | N | 1.1101 | 39.4971 | 800.1937
[7 empty] | 3666 | 3569 | 1729044 | 2020-01-28 19:57 | 2020-01-29 11:22 | 925 | 11kV | 66600 | 72 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207214 3 phase Sensitive Earth Fault | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-28 | N | 925 | N | 34 | Y | Y | 1.1101 | 39.4971 | 48669.3156
[7 empty] | 4076 | 7901 | 1729212 | 2020-01-29 10:53 | 2020-01-29 12:09 | 76 | 11kV | 74770 | 1420 | HV | Arcing | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Kogarah Panel 11 tripped on 50TBC 1.3.1 Fault 1: UG cable fault from S10005 tio S63035 to LB31199 Fault 2: 11kV Bond arcing beyond CP30157 Pa11 interrupted by AOp See OMS 1730024 1730025 1730027 17300287 1729254 1729252 1729212 | January | 2020 | 2020Q3 | 2020 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Not Veg | 2020-01-29 | N | 52.6549 | N | 14 | N | N | 1.1101 | 39.4971 | 54639.7107
[7 empty] | 4778 | 14821 | 1729120 | 2020-01-29 07:16 | 2020-01-29 12:30 | 314 | 11kV | 1570 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207244 A Phase DOLF Excluded OMS 1729120 | January | 2020 | 2020Q3 | 2020 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2020-01-29 | N | 314 | N | 14 | N | N | 1.1101 | 39.4971 | 1147.3097
[7 empty] | 3679 | 3717 | 1729011 | 2020-01-28 19:24 | 2020-01-29 12:50 | 1046 | 11kV | 3138 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207249 Single phase DOLF : 10 Amp Excluded OMS 1729011 | January | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-01-28 | N | 1046 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2293.1578
[7 empty] | 5295 | 19807 | 1729006 | 2020-01-28 19:13 | 2020-01-29 13:40 | 1107 | 11kV | 3647 | 183 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 207313 DOLF : 10 Amp At 1913 dolfs 53026 blows 28/1/20, interr from ABS 79420 for clearance at 1236 29/1/20. ABS back on at 1320 and Sub 53026 on at 1340 on the 29/1/20. Excluded OMS 1729006, 1729239 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-28 | N | 19.929 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2665.12
[7 empty] | 3933 | 6190 | 1729114 | 2020-01-29 06:57 | 2020-01-29 14:00 | 423 | 11kV | 846 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207251 C Phase DOLF : 10 Amp Excluded OMS 1729114 | January | 2020 | 2020Q3 | 2020 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2020-01-29 | N | 423 | N | 14 | N | N | 1.1101 | 39.4971 | 618.2318
[7 empty] | 3956 | 6484 | 1728972 | 2020-01-28 17:22 | 2020-01-29 14:14 | 1252 | 11kV | 7512 | 6 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | REC45093 Wdabyne tripped on: OC PT13935 - HDO Operated Recloser was one shot at request of Linesman due to condition of pole Lightning | January | 2020 | 2020Q3 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2020-01-28 | N | 1252 | N | 34 | Y | Y | 1.1101 | 39.4971 | 5489.548
[7 empty] | 5239 | 19385 | 1729264 | 2020-01-29 15:30 | 2020-01-29 16:00 | 30 | 11kV | 390 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 207258 Damaged Insulator Excluded OMS 1729264 | January | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-01-29 | N | 30 | N | 14 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 3448 | 1472 | 1729372 | 2020-01-29 15:36 | 2020-01-29 17:20 | 104 | 11kV | 416 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207260 Single phase DOLF : 16 Amp Excluded OMS 1729372 | January | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-01-29 | N | 104 | N | 14 | N | N | 1.1101 | 39.4971 | 304.0005
[7 empty] | 5240 | 19390 | 1729069 | 2020-01-28 21:39 | 2020-01-29 17:48 | 1209 | 11kV | 58032 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207261 B Phase DOLF : 10 Amp Excluded OMS 1729069 | January | 2020 | 2020Q3 | 2020 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2020-01-28 | N | 1209 | N | 34 | Y | Y | 1.1101 | 39.4971 | 42408.0739
[7 empty] | 3428 | 1328 | 1729424 | 2020-01-29 17:04 | 2020-01-29 19:05 | 120.6333 | 11kV | 8444.3333 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 207266 C Phase : 40 Amp CC1: 22-"Refer to SOp" | January | 2020 | 2020Q3 | 2020 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2020-01-29 | N | 120.6333 | N | 14 | N | N | 1.1101 | 39.4971 | 6170.8697
[7 empty] | 3545 | 2439 | 1729449 | 2020-01-29 19:25 | 2020-01-29 21:49 | 144 | 11kV | 3168 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 207263 Outage to replace insulators at pole JS-70479. | January | 2020 | 2020Q3 | 2020 | 235:2121 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2020-01-29 | N | 144 | N | 14 | N | N | 1.1101 | 39.4971 | 2315.081
[7 empty] | 3971 | 6638 | 1729050 | 2020-01-28 20:37 | 2020-01-29 23:45 | 1628 | 11kV | 9768 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 207267 A & B phase DOLF : 10 Amp Faulty transformer replaced BLOWN 10 AMP A AND B PHASE DOLF 11190, TRYBACK OF B PHASE FAILED, OPENED REMOVED AND DT DOLF 11190, DOLFS LEFT AT BASE OF POLE, ADVISED SOP, NO VISUAL SIGNS OF A FAILED TANK OR ARRESTOR, PLEASE HAVE CREWS ATTEND TO REPLACED FAILED COMPONANTS AND RESTORE SUPPLY. DUPLICATE JOB OMS # 1729050, 1729128 AND 1729106 | January | 2020 | 2020Q3 | 2020 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2020-01-28 | N | 1628 | N | 34 | Y | Y | 1.1101 | 39.4971 | 7138.1663
[7 empty] | 4799 | 15015 | 1729092 | 2020-01-29 23:24 | 2020-01-29 23:55 | 31 | 11kV | 682 | 22 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 207215 33kV insulator cracked pole JS-70479. Fdr de energised to extinguish fire. | January | 2020 | 2020Q3 | 2020 | 235:2121 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2020-01-29 | N | 31 | N | 14 | N | N | 1.1101 | 39.4971 | 498.3855
[7 empty] | 4734 | 14378 | 1729476 | 2020-01-30 06:00 | 2020-01-30 06:40 | 40 | 11kV | 2640 | 66 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 207275 A & B Phase : 40 Amp dop suspects 11kv LAs, please investigate Excluded oms 1729476 1729477 | January | 2020 | 2020Q3 | 2020 | 261:81876 | 261:81876 | ZN00261/081876 | NEWCASTLE | OH | Not Veg | 2020-01-30 | N | 40 | N | 8 | N | N | 1.1101 | 39.4971 | 1929.2341
[7 empty] | 4603 | 13212 | 1729494 | 2020-01-30 07:38 | 2020-01-30 08:50 | 72 | 11kV | 47160 | 655 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby All Centres beyond CP43780 Interrupted when opened for NAR51145 Abnormal Switching: AB40597 found open, CP43276 Open Due to previous DMA Cause: Links CP40597 found open after recent storms - Staff Error See OMS 1729791 1729494 | January | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | Unknown | Not Veg | 2020-01-30 | N | 72 | N | 8 | N | N | 1.1101 | 39.4971 | 34463.137
[7 empty] | 4184 | 9225 | 1729488 | 2020-01-30 07:12 | 2020-01-30 08:55 | 103 | 11kV | 103 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207283 A & C Phase DOLF : 20 Amp Excluded OMS 1729488 | January | 2020 | 2020Q3 | 2020 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2020-01-30 | N | 103 | N | 8 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 3557 | 2557 | 1729439 | 2020-01-29 18:00 | 2020-01-30 10:52 | 1012 | 11kV | 1012 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207278 A Phase DOLF : 16 Amp Replaced blown arrestor. Excluded OMS No. 1729439 | January | 2020 | 2020Q3 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-01-29 | N | 1012 | N | 14 | N | N | 1.1101 | 39.4971 | 739.5398
[7 empty] | 5083 | 18147 | 1729530 | 2020-01-30 08:26 | 2020-01-30 15:08 | 402 | 11kV | 402 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 207288 AA & C Phase Overcurrent Excluded OMS 1729530 | January | 2020 | 2020Q3 | 2020 |  |  |  | CESSNOCK | Unknown | Not Veg | 2020-01-30 | N | 402 | N | 8 | N | N | 1.1101 | 39.4971 | 293.7697
[7 empty] | 5097 | 18213 | 1729894 | 2020-01-30 17:34 | 2020-01-30 18:32 | 58 | 11kV | 116 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207301 Single phase DOLF : 10 Amp Excluded OMS 1729894 | January | 2020 | 2020Q3 | 2020 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Veg | 2020-01-30 | N | 58 | N | 8 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 4298 | 10207 | 1729900 | 2020-01-30 18:16 | 2020-01-30 19:26 | 70 | 11kV | 138294 | 2177 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland -Pnl.10 tripped on Earth Fault UG cable fault between Pnl.10, S7628 and S65738 | January | 2020 | 2020Q3 | 2020 | ZN188:PA10 | ZN188:PA10 | ZN00188/000010 | SYDNEY | UG | Not Veg | 2020-01-30 | N | 63.525 | N | 8 | N | N | 1.1101 | 39.4971 | 101061.1762
[7 empty] | 4833 | 15375 | 1729931 | 2020-01-30 22:10 | 2020-01-31 00:10 | 120 | 11kV | 8421 | 91 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn15013 Terrey Hills PAnel 10 Recloser CP20852 tripped and reclosed on OC and IOC Cp49122 Sectionaliser Tripped on on A and B phase OC Tree branch on OH mains See OMS 1732290 1732291 1729931 | January | 2020 | 2020Q3 | 2020 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2020-01-30 | N | 92.5385 | N | 8 | N | N | 1.1101 | 39.4971 | 6153.8184
[7 empty] | 3439 | 1381 | 1729915 | 2020-01-30 20:21 | 2020-01-31 09:51 | 810 | 11kV | 92340 | 114 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 207308 3 fault operations 3 phase Overcurrent | January | 2020 | 2020Q3 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2020-01-30 | N | 810 | N | 8 | N | N | 1.1101 | 39.4971 | 67479.3484
[7 empty] | 3386 | 856 | 1730084 | 2020-01-31 12:07 | 2020-01-31 14:10 | 123 | 11kV | 123 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207314 A Phase DOLF : 10 Amp Excluded OMS 1730084 | January | 2020 | 2020Q3 | 2020 | 508:82579 | 508:82579 | ZN00508/082579 | DUNGOG | OH | Veg | 2020-01-31 | N | 123 | N | 8 | N | N | 1.1101 | 39.4971 | 89.8848
[7 empty] | 4493 | 11970 | 1730149 | 2020-01-31 14:18 | 2020-01-31 15:55 | 97 | 11kV | 141776 | 1476 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.6 tripped on: Earth Fault and O/C Abnormal: S65499 Sw/A closed with S35426 Sw/A Open, S4430 Sw/A Closed with S63 Sw/E Open (NAR51822) UG cable fault between S8528 Sw/A and S7242 Sw/A and S7187 Sw/A See1731912 1731913 | January | 2020 | 2020Q3 | 2020 | ZN7900:PA6 | ZN7900:PA6 | ZN07900/000006 | SYDNEY | UG | Not Veg | 2020-01-31 | N | 96.0542 | N | 8 | N | N | 1.1101 | 39.4971 | 103605.7191
[7 empty] | 4644 | 13570 | 1730004 | 2020-01-31 09:07 | 2020-01-31 17:25 | 498 | 11kV | 498 | 1 | HV | Vandalism | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207318 LV CCT 16176 busbar & cables removed from LV Board. Repairs done under AP. Excluded oms 1730004 | January | 2020 | 2020Q3 | 2020 |  |  |  | NEWCASTLE | OH | Not Veg | 2020-01-31 | N | 498 | N | 8 | N | N | 1.1101 | 39.4971 | 363.9237
[7 empty] | 4321 | 10395 | 1730147 | 2020-01-31 14:19 | 2020-01-31 17:25 | 186 | 11kV | 143482 | 1016 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S1673 Turramurra panel 14 has tripped on Relays: B phase IOC, earth fault, fault check EFI and UNder frequency Signals TX 3 group Earth, ZOne Earth Cause: UG cable fault between S8332 and S3554 See OMS 1732268 1732269 1732270 1730147 | January | 2020 | 2020Q3 | 2020 | ZN1673:PA14 | ZN1673:PA14 | ZN01673/000014 | KU-RING-GAI | UG | Not Veg | 2020-01-31 | N | 141.2224 | N | 8 | N | N | 1.1101 | 39.4971 | 104852.4136
[7 empty] | 4622 | 13465 | 1730193 | 2020-01-31 18:45 | 2020-01-31 19:02 | 17 | 11kV | 1278 | 163 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT13625 Wise Ferry Lavender 9.6 Customer is reporting 3 phase supply is reversed See NAR45927 For Work @1854 CP61097 Wise Ferry Lavender 10.2 Opened @1900 AB43179 Opened Network REstored from Endeavour energy (LB45074) to LB43179 Appears there has been a cross in the HV feeder at some stage after numerous repairs to sections of panel 1 @ Peats Ridge See OMS 1732294 1732295 1730193 | January | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-01-31 | N | 7.8405 | N | 8 | N | N | 1.1101 | 39.4971 | 933.9247
[7 empty] | 4450 | 11490 | 1730236 | 2020-01-31 18:16 | 2020-01-31 19:26 | 70 | 11kV | 210 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207321 A Phase DOLF : 10 Amp Excluded OMS 1730236 | January | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-01-31 | N | 70 | N | 8 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 4172 | 9098 | 1730191 | 2020-01-31 15:30 | 2020-01-31 19:40 | 250 | 11kV | 250 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 207319 C Phase DOLF : 10 Amp SUB ISOLATED FO REPLACE LA Excluded OMS 170191 | January | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-01-31 | N | 250 | N | 8 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 4235 | 9584 | 1730253 | 2020-01-31 18:45 | 2020-02-01 00:23 | 338 | 11kV | 11011 | 33 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 207322 A Phase open tapping at pole 6K-60099 No Operations of switch Excluded OMS 1730253 | January | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2020-01-31 | N | 333.6667 | N | 8 | N | N | 1.1101 | 39.4971 | 8046.514
[7 empty] | 4453 | 11537 | 1730294 | 2020-02-01 01:13 | 2020-02-01 03:15 | 122 | 11kV | 6544 | 56 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn14143 Somwerby Panel 6 tripped on Signals: 11kV Trip EFI Relays: A and C phase OC, E/F and EFI Cause: UG cable fault between S18084 Pile Australian Fee and S76982 Old Pacific Pile 0.3 See OMS 1732296 1732297 1730294 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2020-02-01 | N | 116.8571 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4782.1622
[7 empty] | 3521 | 2210 | 1730443 | 2020-02-01 14:08 | 2020-02-01 15:15 | 67 | 11kV | 73055 | 1165 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2568 St Peters - Pnl.9 tripped on Earth leakage Ug cable fault between S47256 and S3160 See 1731932 1731933 | February | 2020 | 2020Q3 | 2020 | ZN2568:PA9 | ZN2568:PA9 | ZN02568/000009 | INNER WEST | UG | Not Veg | 2020-02-01 | N | 62.7082 | N | 21 | Y | Y | 1.1101 | 39.4971 | 53386.4392
[7 empty] | 5322 | 20052 | 1730368 | 2020-02-01 14:13 | 2020-02-01 15:17 | 64 | 11kV | 3904 | 61 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Hot >35C | N | LID 207333 11 kV of pins at pole 9k90237 Excluded OMS oms 1730368 | February | 2020 | 2020Q3 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2020-02-01 | N | 64 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2852.9281
[7 empty] | 3924 | 6141 | 1730484 | 2020-02-01 15:20 | 2020-02-01 15:53 | 33 | 11kV | 52224 | 4640 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Zn10999 Kogarah - Pnl.12 opened due to overloading Abnormal: S10157 Sw/A Closed with S10158 Sw/A Open (DMA) See 1732136 1732137 | February | 2020 | 2020Q3 | 2020 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Not Veg | 2020-02-01 | N | 11.2552 | N | 21 | Y | Y | 1.1101 | 39.4971 | 38163.7589
[7 empty] | 3490 | 1926 | 1730466 | 2020-02-01 14:44 | 2020-02-01 15:56 | 72 | 11kV | 46908 | 855 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn262 Marrickville - Pnl.32 tripped on: A Phase O/C UG cable fault between S36 Sw/B and S7164 Sw/A See 1732275 1732276 | February | 2020 | 2020Q3 | 2020 | ZN262:PA32 | ZN262:PA32 | ZN00262/000032 | INNER WEST | UG | Not Veg | 2020-02-01 | N | 54.8632 | N | 21 | Y | Y | 1.1101 | 39.4971 | 34278.9828
[7 empty] | 4594 | 13101 | 1730501 | 2020-02-01 15:35 | 2020-02-01 16:57 | 82 | 11kV | 63042 | 810 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN4545 Meadowbank Panel 24 tripped on Signals: 11kV trip Relays: B phase EF, and EFI Field EFI's NIl Abnormal Switching: S47941 Closed abd S5311 Open Cause: 11kV Feeder fault from S1835 Herbot Linton to S6451 Parkes Hortaculture SW/A to S47941 Faulkner Parkes See OMS 1732229 17322230 | February | 2020 | 2020Q3 | 2020 | ZN4545:PA24 | ZN4545:PA24 | ZN04545/000024 | RYDE | UG | Not Veg | 2020-02-01 | N | 77.8296 | N | 21 | Y | Y | 1.1101 | 39.4971 | 46069.2342
[7 empty] | 5035 | 17634 | 1730524 | 2020-02-01 16:16 | 2020-02-01 17:47 | 91 | 11kV | 79198 | 894 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn1673 Turramurra Panel 21 tripped on Signals : 11kV Trip, Group Earth Relays: IOC, B phase, Timed OC, Earth Fault with EFI Cause: UG cable fault from S36184 to S48366 Abnormal Switching: Load Relief switching SW/A Open at S49740, CP373 Closed (Load relief required due to additional load placed onto TX3 due to Panel 7 failure) See OMS 1732177 1732178 1730524 | February | 2020 | 2020Q3 | 2020 | ZN1673:PA21 | ZN1673:PA21 | ZN01673/000021 | KU-RING-GAI | UG | Not Veg | 2020-02-01 | N | 88.5884 | N | 21 | Y | Y | 1.1101 | 39.4971 | 57875.5625
[7 empty] | 5250 | 19461 | 1730378 | 2020-02-01 16:32 | 2020-02-01 18:15 | 103 | 11kV | 97028 | 1076 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN12650 West Gosford Panel 6 tripped on Signals: 11kV trip Relays: Earth Fault and WFI Abnormal Switching: SW/A closed at S18568, CP44911 Open, CP41355 Closed, CP62730 Open Cause: 11kV Cable fault from S18054 to S18568 See OMS 1732300 1732301 1732302 1730532 1730533 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | UG | Not Veg | 2020-02-01 | N | 90.1747 | N | 21 | Y | Y | 1.1101 | 39.4971 | 70905.2006
[7 empty] | 3300 | 160 | 1730641 | 2020-02-01 18:09 | 2020-02-01 19:22 | 73 | 11kV | 130920 | 1860 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S187 Crows Nest Panel 13 Tripped on overcurrent E/F efi Cause: UG cable fault in section of 11kv feeder from S5440 to S3383 See OMS 1732171 1732173 1730641 | February | 2020 | 2020Q3 | 2020 | ZN187:PA30 | ZN187:PA30 | ZN00187/000030 | WILLOUGHBY | UG | Not Veg | 2020-02-01 | N | 70.3871 | N | 21 | Y | Y | 1.1101 | 39.4971 | 95672.4745
[7 empty] | 3628 | 3083 | 1730649 | 2020-02-01 18:16 | 2020-02-01 19:42 | 86 | 11kV | 94084 | 1094 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S180 Mosman Panel 24 tripped on B phase OC with efi Cause: underground cable fault in section of feeder from Mosman Panel 24 to S1340 | February | 2020 | 2020Q3 | 2020 | ZN180:PA24 | ZN180:PA24 | ZN00180/000024 | WILLOUGHBY | UG | Not Veg | 2020-02-01 | N | 86 | N | 21 | Y | Y | 1.1101 | 39.4971 | 68753.8122
[7 empty] | 4641 | 13559 | 1730638 | 2020-02-01 18:09 | 2020-02-01 20:05 | 116 | 11kV | 12528 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 207337 B Phase DOLF : 40 Amp Excluded OMS 1730638, 1730689 CC1: 22-"Refer to SOp" | February | 2020 | 2020Q3 | 2020 | 502:48008 | 502:48001 | ZN00502/048001 | MAITLAND | OH | Veg | 2020-02-01 | N | 116 | N | 21 | Y | Y | 1.1101 | 39.4971 | 9155.0929
[7 empty] | 4664 | 13767 | 1730790 | 2020-02-01 19:50 | 2020-02-01 20:31 | 41 | 11kV | 83435 | 2035 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Upon restoration of Pnl.1L @ Potts Hill from S6596 Sw/B - Pnl.23 tripped on overload due to abnormal switching | February | 2020 | 2020Q3 | 2020 | ZN1285:PA23 | ZN37100:PA33 | ZN37100/000033 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2020-02-01 | N | 41 | N | 21 | Y | Y | 1.1101 | 39.4971 | 60971.8371
[7 empty] | 3308 | 195 | 1730708 | 2020-02-01 19:00 | 2020-02-01 21:00 | 120 | 11kV | 95760 | 798 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex Jannali - Pnl.24 - Bond burnt off AB35778 Note: Actual restore time 21/02/20 @ 2100. Confirmed on DNMS via load trend S.Edwards | February | 2020 | 2020Q3 | 2020 | ZN9252:PA24 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2020-02-01 | N | 120 | N | 21 | Y | Y | 1.1101 | 39.4971 | 69978.5836
[7 empty] | 4173 | 9105 | 1730570 | 2020-02-01 16:59 | 2020-02-01 21:05 | 246 | 11kV | 228861 | 2113 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | At ZN12640 Umina Panel 14 tripped Signals: 11kV trip Abnormal Switching: SW/B closedat S14488, SW/A open at S18026 Relays: IOC, SEF, EFI, Reclose, Timing and Lockout Cause: 11PG clamp has come off and hit adjacent mains on the cnr of Memorial and Bourke 11kV feeder isolated from LB44942 to LV40712 to LB47457 tee POT12778 See OMS 1732308 1732311 1732312 1730575/576/582/570 | February | 2020 | 2020Q3 | 2020 | ZN12640:PA14 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2020-02-01 | N | 108.3109 | N | 21 | Y | Y | 1.1101 | 39.4971 | 167244.8685
[7 empty] | 4979 | 16921 | 1730594 | 2020-02-01 17:24 | 2020-02-01 21:30 | 246 | 11kV | 334440 | 1836 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | Zn35900 Potts Hill - Pnl.1L tripped on: Earth Fault Abnormal: LB586 open with S5096 Sw/A End box fault at HAZ S5221 Woodbine St. See 1732237 1732239 1732240 | February | 2020 | 2020Q3 | 2020 | ZN35900:PA1 | ZN35900:PA1 | ZN35900/000001 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-02-01 | N | 182.1569 | N | 21 | Y | Y | 1.1101 | 39.4971 | 244398.8877
[7 empty] | 4358 | 10686 | 1730770 | 2020-02-01 19:55 | 2020-02-01 21:40 | 105 | 11kV | 144475 | 1451 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn262 marrickville - Pnl.5 tripped on: Earth Fault UG cable fault between S7658 Sw/B and S5771 Sw/A See 1732277 1732278 | February | 2020 | 2020Q3 | 2020 | ZN262:PA5 | ZN262:PA5 | ZN00262/000005 | INNER WEST | UG | Not Veg | 2020-02-01 | N | 99.5693 | N | 21 | Y | Y | 1.1101 | 39.4971 | 105578.0687
[7 empty] | 3477 | 1802 | 1730640 | 2020-02-01 18:08 | 2020-02-01 22:30 | 262 | 11kV | 52924 | 202 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Ex Turramurra Panel 13 11kV S.4711 Carrington Eastern SW/B Openm Abnormal Switching: SW/B Closed @ 8688 with SW/A open @49736 Cause: Load Shedding due to overload (Abnormal Switching) | February | 2020 | 2020Q3 | 2020 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | Unknown | Not Veg | 2020-02-01 | N | 262 | N | 21 | Y | Y | 1.1101 | 39.4971 | 38675.2982
[7 empty] | 5339 | 20296 | 1730760 | 2020-02-01 19:43 | 2020-02-01 23:50 | 247 | 11kV | 22477 | 91 | HV | Overload | Utility Process Issue | Fuse | Unplanned | Hot >35C | N | At S965 Pennant Hills Panel 35 tripped on Protection relay: SEF Signals: Nil Cause: Sensitive earth operated when energising section of feeder from S4960 At S4960 Kungala Murray Farm 40A HV fuse operated due to overload See OMS 1732123 1732116 1730760 | February | 2020 | 2020Q3 | 2020 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | PARRAMATTA | OH | Not Veg | 2020-02-01 | N | 247 | N | 21 | Y | Y | 1.1101 | 39.4971 | 16425.5286
[7 empty] | 4036 | 7419 | 1730428 | 2020-02-01 12:07 | 2020-02-02 02:30 | 863 | 11kV | 173488 | 1906 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At ZN12650 West Gosford 11kV Panel 13 tripped reclosed tripped and locked out on Relays: C phase IOC, earth fault, EFI and Lockout Cause: UGOH fault between CP44151 - S414116 tee S14017 See OMS 1732319 1732320 1732320 1732321 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Unknown | Unknown | 2020-02-01 | N | 91.022 | N | 21 | Y | Y | 1.1101 | 39.4971 | 126779.9134
[7 empty] | 4665 | 13769 | 1730630 | 2020-02-01 17:56 | 2020-02-02 04:09 | 613 | 11kV | 127504 | 208 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Ex Greenacre Park - Pnl.24L - LB1447 opened due to overloading on Pnl.24 and Pnl.27 Abnormal: LB1447 closed with AP99 Open (DMA), LB73 Closed with LB2481 open (DMA) | February | 2020 | 2020Q3 | 2020 | ZN35800:PA15 | ZN35800:PA15 | ZN35800/000015 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2020-02-01 | N | 613 | N | 21 | Y | Y | 1.1101 | 39.4971 | 93176.1625
[7 empty] | 4556 | 12598 | 1730605 | 2020-02-01 17:32 | 2020-02-02 04:40 | 668 | 11kV | 110758 | 1836 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | LID 207342 A Phase DOLF : 31 Amp faulty trans also see report # 207341 section 5625/6846 isolated to change trans Excluded oms 1730605 & 1730905 | February | 2020 | 2020Q3 | 2020 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2020-02-01 | N | 60.3257 | N | 21 | Y | Y | 1.1101 | 39.4971 | 80938.6796
[7 empty] | 4825 | 15268 | 1730934 | 2020-02-02 06:30 | 2020-02-02 07:50 | 80 | 11kV | 70080 | 1000 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.24 tripped on: Earth fault Field EFIs: S4300 S35027 UG cable fault between S35027 and S8273 See 1732425 1732426 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | UG | Not Veg | 2020-02-02 | N | 70.08 | N | 12 | N | N | 1.1101 | 39.4971 | 51212.397
[7 empty] | 3862 | 5618 | 1731023 | 2020-02-02 13:46 | 2020-02-02 15:14 | 88 | 11kV | 55370 | 640 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn8000 MaCQUARIE Park tripped on Relays: Earth Fault, Fault check and EFI Signals: 11kV Trip, TX 3 Group earth Cause: UG cable fauklt from S7753 to S7225 Abnormal Switcing: S63297 SW/B is closed, SW/A is open See OMS 1732182 1732183 1731023 | February | 2020 | 2020Q3 | 2020 | ZN8000:PA38 | ZN8000:PA38 | ZN08000/000038 | RYDE | UG | Not Veg | 2020-02-02 | N | 86.5156 | N | 12 | N | N | 1.1101 | 39.4971 | 40462.7629
[7 empty] | 4711 | 14210 | 1731046 | 2020-02-02 14:52 | 2020-02-02 16:48 | 116 | 11kV | 37236 | 321 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 207360 2 Fault operation Tree on mains GW-10019 Excluded OMS 1731050 | February | 2020 | 2020Q3 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-02-02 | N | 116 | N | 12 | N | N | 1.1101 | 39.4971 | 27210.9705
[7 empty] | 4496 | 11974 | 1732422 | 2020-02-02 16:19 | 2020-02-02 17:38 | 79 | 11kV | 39606 | 514 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S14892 Charmhaven Panel 17 Tripped on Earth fault, EFI and timing relay Cause: UG cable fault from S14814 to S18225 See OMS 1732422 1732427 1731079 1731200 | February | 2020 | 2020Q3 | 2020 | ZN14892:PA17 | ZN14892:PA17 | ZN14892/000017 | CENTRAL COAST | UG | Not Veg | 2020-02-02 | N | 77.0545 | N | 12 | N | N | 1.1101 | 39.4971 | 28942.8966
[7 empty] | 3852 | 5530 | 1731158 | 2020-02-02 19:45 | 2020-02-02 21:40 | 115 | 11kV | 21965 | 191 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | S35370 Galston Panel 10L Intellirupter has tripped on Signals Cause: Tree branch across 2 phases of 11kV in laneway behind 152. Branch caught fire a couple of times. Abnormal Switching: AB1192 Oped CP2691 Defective | February | 2020 | 2020Q3 | 2020 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2020-02-02 | N | 115 | N | 12 | N | N | 1.1101 | 39.4971 | 16051.3741
[7 empty] | 4915 | 16159 | 1731171 | 2020-02-02 19:53 | 2020-02-02 22:25 | 152 | 11kV | 213184 | 1694 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.7 tripped, reclosed & tripped on: IOC and Earth Fault Field EFIs: S10200 & S10425 UGOH defective outside 38 Frederick St See 1732093 1732095 1732096 | February | 2020 | 2020Q3 | 2020 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | Unknown | Unknown | 2020-02-02 | N | 125.8465 | N | 12 | N | N | 1.1101 | 39.4971 | 155788.5793
[7 empty] | 4238 | 9634 | 1731138 | 2020-02-02 19:30 | 2020-02-02 22:31 | 181 | 11kV | 438414 | 3094 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn1285 Greenacre Park - Pnl.23 tripped on: A & C phase O/C Abnormal: S63510 Sw/B closed with S4027 Sw/A Open, S6569 Sw/B closed with S6513 Sw/A Open, S5096 Sw/B with LB586 11kV hit by lightning, mains down adjacent to PT1114 See 1732162 1732163 | February | 2020 | 2020Q3 | 2020 | ZN1285:PA23 | ZN37100:PA33 | ZN37100/000033 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-02-02 | N | 141.6981 | N | 12 | N | N | 1.1101 | 39.4971 | 320380.0202
[7 empty] | 4082 | 7985 | 1731200 | 2020-02-02 20:41 | 2020-02-02 22:58 | 137 | 11kV | 79207 | 684 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | At Zn14892 Charmhaven Panel 19 tripped on Earth fault, EFI, Fault Check, Timing relay and AR lockout Abnormal Switching: AB40127 Open, CP44110 Closed Cause: 11kV feeder fault from S14809 S/W B to CP63042 to CP41422 to S14816 See OMS 1732439 1732440 | February | 2020 | 2020Q3 | 2020 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | UG | Not Veg | 2020-02-02 | N | 115.7997 | N | 12 | N | N | 1.1101 | 39.4971 | 57882.1394
[7 empty] | 5070 | 17976 | 1731178 | 2020-02-02 20:06 | 2020-02-02 23:09 | 183 | 11kV | 18398 | 132 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 207367 3 fault operations Excluded OMS 1731178 | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-02-02 | N | 139.3788 | N | 12 | N | N | 1.1101 | 39.4971 | 13444.7158
[7 empty] | 4788 | 14882 | 1731055 | 2020-02-02 15:14 | 2020-02-02 23:59 | 525 | 11kV | 14639 | 51 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 207369 A & B Phase DOLF : 31 Amp tree on ohm adjacent sub 881 Excluded oms 1731055 | February | 2020 | 2020Q3 | 2020 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2020-02-02 | N | 287.0392 | N | 12 | N | N | 1.1101 | 39.4971 | 10697.7494
[7 empty] | 4365 | 10729 | 1731199 | 2020-02-02 20:40 | 2020-02-03 00:25 | 225 | 11kV | 199799 | 1326 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Lightning | N | Zn15008 Harbord - Pnl.5 tripped on: B & C phase O/C Field EFIs: S16800 S77556 S1752 S65754 11kV Insulator failed on pole between USL23562 and S17060 See 1732435 1732436 1732437 1732438 | February | 2020 | 2020Q3 | 2020 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2020-02-02 | N | 150.678 | N | 12 | N | N | 1.1101 | 39.4971 | 146007.2161
[7 empty] | 4302 | 10236 | 1730648 | 2020-02-02 19:30 | 2020-02-03 00:48 | 318 | 11kV | 310572 | 2288 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn35800 Bankstown Pnl.1 tripped on: O/C Abnormal: REC50006 Closed with S4343 Sw/A Open, S5096 Sw/A Closed with LB586 S5908 Dutton Glassop - dist 31 - Interrupted to allow repairs Lightning damage to 11kV feeder sEE 1732219 1732220 | February | 2020 | 2020Q3 | 2020 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-02-02 | N | 135.7395 | N | 12 | N | N | 1.1101 | 39.4971 | 226956.8573
[7 empty] | 3462 | 1628 | 1731270 | 2020-02-03 02:29 | 2020-02-03 03:56 | 87 | 11kV | 138268 | 1609 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 207370 1 fault operation Sensitive Earth Fault Excluded OMS 1731270 | February | 2020 | 2020Q3 | 2020 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2020-02-03 | N | 85.9341 | N | 11 | N | N | 1.1101 | 39.4971 | 101042.1762
[7 empty] | 3974 | 6661 | 1731307 | 2020-02-03 08:21 | 2020-02-03 10:10 | 109 | 11kV | 981 | 9 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Heavy | N | Ex ZN14891 WYONG section of 11kV Panel 20 PT13341 HUE HUE DICKSON 0.6 blew footpath side 10A HDO Branch fell on Tx Tank. no apparant damage See 1757528 ex 1731307 | February | 2020 | 2020Q3 | 2020 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2020-02-03 | N | 109 | N | 11 | N | N | 1.1101 | 39.4971 | 716.8859
[7 empty] | 4754 | 14523 | 1731362 | 2020-02-03 09:11 | 2020-02-03 10:19 | 68 | 11kV | 147764 | 2173 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN12580 ERINA 11kV CB Panel 4 'Springfield' fdr tripped on Relays: A&C Phase IOC and Timed OC Cause: Tree/Branch on OH Mains Small branch on OH adj AB43779 Note: Panel 4 recloser was auto at time of trip but CB did not reclose additionally RE49612 did not trip (existing DMA on RE49612) See 1731335 ex 1731362 | February | 2020 | 2020Q3 | 2020 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2020-02-03 | N | 68 | N | 11 | N | N | 1.1101 | 39.4971 | 107981.5729
[7 empty] | 5184 | 18831 | 1731402 | 2020-02-03 11:00 | 2020-02-03 11:45 | 45 | 11kV | 45 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207377 C Phase DOLF : 10 Amp Excluded OMS 1721402 | February | 2020 | 2020Q3 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2020-02-03 | N | 45 | N | 11 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 4324 | 10406 | 1731328 | 2020-02-03 09:15 | 2020-02-03 12:40 | 205 | 11kV | 9225 | 45 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 207378 SECTION ISOLATED FOR EMERG POLE CV-23665 REPLACEMENT Excluded OMS 1731328 | February | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-02-03 | N | 205 | N | 11 | N | N | 1.1101 | 39.4971 | 6741.3579
[7 empty] | 5215 | 19178 | 1731272 | 2020-02-03 02:54 | 2020-02-03 12:50 | 596 | 11kV | 86244 | 379 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn9550 Gwawley Bay Panel 36 Tripped on Relays: 150TN (Earth Fault), 51N EFI Signals: 11kV Field EFI's Nil Abnormal Switching: S9669 Closed, CP35551 Open Cause: 11kV has come into contact with LV. Between LB35614 to LB35499 tee S9675 See OMS 1750864 1750865 1750867 1750868 1731272 1731521 1731280 | February | 2020 | 2020Q3 | 2020 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2020-02-03 | N | 227.5567 | N | 11 | N | N | 1.1101 | 39.4971 | 63024.5714
[7 empty] | 3655 | 3446 | 1731602 | 2020-02-03 19:27 | 2020-02-03 20:26 | 59 | 11kV | 28548 | 488 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At S847 Horbsy Panel 45 tripped Cause: 11kV Bond burnt off at LB490 Swee OMS 1732031 1732032 1731602 1731603 1731612 | February | 2020 | 2020Q3 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2020-02-03 | N | 58.5 | N | 11 | N | N | 1.1101 | 39.4971 | 20862.0364
[7 empty] | 3794 | 4979 | 1731546 | 2020-02-03 16:24 | 2020-02-03 20:50 | 266 | 11kV | 266 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207394 C Phase DOLF : 10 Amp Excluded OMS 1731541 | February | 2020 | 2020Q3 | 2020 | 508:82574 | 508:82574 | ZN00508/082574 | SINGLETON | OH | Veg | 2020-02-03 | N | 266 | N | 11 | N | N | 1.1101 | 39.4971 | 194.385
[7 empty] | 4174 | 9128 | 1731527 | 2020-02-03 15:54 | 2020-02-03 21:10 | 316 | 11kV | 948 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 207393 Single phase DOLF : 10 Amp Blown arrestor caused fuse to blow Excluded OMS 1731527 | February | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-02-03 | N | 316 | N | 11 | N | N | 1.1101 | 39.4971 | 692.7704
[7 empty] | 5280 | 19692 | 1731671 | 2020-02-03 21:38 | 2020-02-03 23:06 | 88 | 11kV | 251330 | 3725 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn2635 Epping - Pnl.58 tripped on B & C phase O.C Abnormals: S5604 Closed with S2933 Open. LB1659 Closed, S4550 Sw/B Open. S61095 Closed. CP916 Open. LB1903 Closed with AB1906 Open. S5702 Closed with S5271 Sw/A Open. S46890 Sw/B Closed with S4627 Sw/A Open. Multiple DMAs + Load relief switching Tree contacted mains near PT1387 See 1756965 1756964 | February | 2020 | 2020Q3 | 2020 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Veg | 2020-02-03 | N | 67.4711 | N | 11 | N | N | 1.1101 | 39.4971 | 183664.551
[7 empty] | 5111 | 18304 | 1731637 | 2020-02-03 20:04 | 2020-02-04 00:30 | 266.2333 | 11kV | 266.2333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207398 A Phase DOLF : 10 Amp Excluded OMS 1731667 | February | 2020 | 2020Q3 | 2020 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2020-02-03 | N | 266.2333 | N | 11 | N | N | 1.1101 | 39.4971 | 194.5555
[7 empty] | 4227 | 9536 | 1731742 | 2020-02-04 06:03 | 2020-02-04 07:00 | 57 | 11kV | 11400 | 200 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S62354 Dunkerley Bourke No.1 - 11kV/415V Tx failed. DOp could not access to check fuses due to operating restriction. | February | 2020 | 2020Q3 | 2020 | ZN188:PA2 | ZN188:PA2 | ZN00188/000002 | SYDNEY | UG | Not Veg | 2020-02-04 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 8330.7838
[7 empty] | 4386 | 10881 | 1731828 | 2020-02-04 10:30 | 2020-02-04 11:36 | 66 | 11kV | 12210 | 185 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN12690 BERKELEY VALE section of 11kV Panel 12 LK43204 went High resistance on B Phase See 1752193 ex 1731828,9 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2020-02-04 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 8922.7079
[7 empty] | 4329 | 10441 | 1731874 | 2020-02-04 12:33 | 2020-02-04 14:55 | 142 | 11kV | 21342 | 291 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT Zn1648 Enfield Panel 1 Tripped on Relays: A phase IOC, Timed and EFI Note: Panel 8 @ Enfield Tripped on restoration - Assumed front line feeder fault due to EFI lack of indication See OMS 1755107 1755149 1755156 1731874 | February | 2020 | 2020Q3 | 2020 | ZN1648:PA1 | ZN4853:PA2 | ZN04853/000002 | BURWOOD | UG | Not Veg | 2020-02-04 | N | 73.3402 | N | 3 | N | N | 1.1101 | 39.4971 | 15596.1041
[7 empty] | 4949 | 16585 | 1732088 | 2020-02-05 11:23 | 2020-02-05 13:30 | 127 | 11kV | 12954 | 102 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 207421 low mains between poles is-82016 & is-82017 Excluded oms 1732088 | February | 2020 | 2020Q3 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2020-02-05 | N | 127 | N | 4 | N | N | 1.1101 | 39.4971 | 9466.4011
[7 empty] | 3399 | 960 | 1732099 | 2020-02-05 12:00 | 2020-02-05 13:50 | 110 | 11kV | 550 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 207422 broken xarm pole jr-60039 Excluded oms 1732023 | February | 2020 | 2020Q3 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2020-02-05 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 401.9238
[7 empty] | 3436 | 1368 | 1751700 | 2020-02-05 14:25 | 2020-02-05 14:32 | 7 | 11kV | 2513 | 359 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Supply lost to S7119 and S2863 due to staff operating error. Network was abnormally switched at the time. | February | 2020 | 2020Q3 | 2020 | ZN2568:PA26 | ZN2568:PA26 | ZN02568/000026 | INNER WEST | Unknown | Not Veg | 2020-02-05 | N | 7 | N | 4 | N | N | 1.1101 | 39.4971 | 1836.4263
[7 empty] | 3325 | 333 | 1732353 | 2020-02-06 03:24 | 2020-02-06 05:01 | 97 | 11kV | 139620 | 1450 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn15002 narrabeen - Pnl.8 tripped on C phase O/C Abnormal: S16686 Sw/B with LB24376 Open DMA Cause not ascertained See 1750836 1750837 | February | 2020 | 2020Q3 | 2020 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Veg | 2020-02-06 | N | 96.2897 | N | 9 | N | N | 1.1101 | 39.4971 | 102030.1779
[7 empty] | 3842 | 5445 | 1732391 | 2020-02-06 06:36 | 2020-02-06 07:57 | 81 | 11kV | 5252 | 65 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 207430 3 fault operations B Phase Overcurrent Bph LA between Sw 49180 & Reg 49181 blown. Malgrade between Sw 49175 & Sw49180 caused wider outage. Excluded OMS 1732391 | February | 2020 | 2020Q3 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2020-02-06 | N | 80.8 | N | 9 | N | N | 1.1101 | 39.4971 | 3838.0067
[7 empty] | 3643 | 3290 | 1732340 | 2020-02-05 23:25 | 2020-02-06 08:34 | 549 | 11kV | 174981 | 395 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 207426 1 fault operation C Phase Instantaneous Overcurrent; Earth Fault Excluded OMS 1732340 | February | 2020 | 2020Q3 | 2020 | 202:34259 | 202:34259 | ZN00202/034259 | NEWCASTLE | UG | Not Veg | 2020-02-05 | N | 442.9899 | N | 4 | N | N | 1.1101 | 39.4971 | 127870.9537
[7 empty] | 5341 | 20320 | 1732420 | 2020-02-06 07:58 | 2020-02-06 09:44 | 106 | 11kV | 28856 | 323 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC20112 Kalang Rd - tripped, relcosed & tripped on: O/C Abnormal: LB20518 Closed with LB77332 Open Cause not ascertained See 1750834 1750834 | February | 2020 | 2020Q3 | 2020 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2020-02-06 | N | 89.3375 | N | 9 | N | N | 1.1101 | 39.4971 | 21087.1137
[7 empty] | 4074 | 7862 | 1732485 | 2020-02-06 09:30 | 2020-02-06 09:57 | 27 | 11kV | 29511 | 1093 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn14144 wamberal - Pnl.10 tripped on: A & B phase IOC Abnormal: LB40973 Closed with AB43615 Open Tree on mains outside 40 Brush Rd See 1757566 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-02-06 | N | 27 | N | 9 | N | N | 1.1101 | 39.4971 | 21565.7684
[7 empty] | 3488 | 1917 | 1732556 | 2020-02-06 11:33 | 2020-02-06 13:35 | 122 | 11kV | 6222 | 51 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At S12610 Long Jetty ex panel 6 PT12548 Sutton Kitchener had a blown centre phase 31.5 amp HDO. Batch Number was 1023 Remarks: fuse fatigue | February | 2020 | 2020Q3 | 2020 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2020-02-06 | N | 122 | N | 9 | N | N | 1.1101 | 39.4971 | 4546.8541
[7 empty] | 5141 | 18510 | 1732611 | 2020-02-06 14:18 | 2020-02-06 17:23 | 185 | 11kV | 8510 | 46 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | LID 207438 Earth Fault See prev reports for sw 42005 T&Rs Broken crossarm pole LI-81073 | February | 2020 | 2020Q3 | 2020 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2020-02-06 | N | 185 | N | 9 | N | N | 1.1101 | 39.4971 | 6218.857
[7 empty] | 4900 | 15966 | 1732602 | 2020-02-06 14:00 | 2020-02-06 18:35 | 275 | 11kV | 154341 | 1400 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 207441 4 fault operations B Phase Overcurrent, Sensitive Earth Fault faulty LA at ABS 74639 Network abnormal....ABS 75089 CLOSED, Sw 74122 OPEN....also lost all of fdr 74122 Excluded OMS 1732602 | February | 2020 | 2020Q3 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2020-02-06 | N | 110.2436 | N | 9 | N | N | 1.1101 | 39.4971 | 112787.8505
[7 empty] | 3574 | 2648 | 1732613 | 2020-02-06 14:50 | 2020-02-06 19:00 | 250 | 11kV | 4535 | 144 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Heavy | N | LID 207440 2 fault operations 3 phase Overcurrent fire at pole AJ-60061 Excluded OMS 1732613 | February | 2020 | 2020Q3 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2020-02-06 | N | 31.4931 | N | 9 | N | N | 1.1101 | 39.4971 | 3314.0442
[7 empty] | 4223 | 9497 | 1732748 | 2020-02-06 21:34 | 2020-02-07 03:10 | 336 | 11kV | 1344 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 207450 C Phase DOLF : 16 Amp Excluded OMS 1732748 | February | 2020 | 2020Q3 | 2020 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2020-02-06 | N | 336 | N | 9 | N | N | 1.1101 | 39.4971 | 982.1556
[7 empty] | 4064 | 7724 | 1732935 | 2020-02-07 08:52 | 2020-02-07 10:23 | 91 | 11kV | 65936 | 779 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn965 Pennant Hills - Pnl38 tripped on: O/C UG cable fault between S6109 Sw.B and S5927 Sw/B See 1756595 1756596 | February | 2020 | 2020Q3 | 2020 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | UG | Not Veg | 2020-02-07 | N | 84.6418 | N | 14 | N | N | 1.1101 | 39.4971 | 48184.084
[7 empty] | 4377 | 10822 | 1732810 | 2020-02-07 02:59 | 2020-02-07 10:30 | 451 | 11kV | 196563 | 965 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Rain Heavy | N | Zn35370 Galston - Pnl.8 tripped on: O/C & E/F Abnormal: LB62109 Closed with REC421 Open DMA Blown surge arrestor found between USL92 and PT1868. Fuse carrier failed at PT1868 (second fault) See 1755100 1755103 1755105 1755108 1755109 1755110 1755112 1755114 1755117 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2020-02-07 | N | 203.6922 | N | 14 | N | N | 1.1101 | 39.4971 | 143642.4428
[7 empty] | 4026 | 7271 | 1732850 | 2020-02-07 06:03 | 2020-02-07 12:15 | 372 | 11kV | 59974 | 659 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 207454 2 fault operations 3 phase Earth Fault Arrestor pole GW-97043 changed under AP Excluded OMS 1732850 | February | 2020 | 2020Q3 | 2020 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2020-02-07 | N | 91.0076 | N | 14 | N | N | 1.1101 | 39.4971 | 43827.2303
[7 empty] | 5117 | 18339 | 1732989 | 2020-02-07 10:17 | 2020-02-07 12:17 | 120 | 11kV | 160434 | 1447 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Zn15005 Belrose - Pnl.12 tripped on: B & C phase O/C & E/F Footpath phase bond burnt off LK21843 See 1750351 1750354 | February | 2020 | 2020Q3 | 2020 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Not Veg | 2020-02-07 | N | 110.8735 | N | 14 | N | N | 1.1101 | 39.4971 | 117240.4352
[7 empty] | 4866 | 15675 | 1742738 | 2020-02-07 07:39 | 2020-02-07 13:40 | 361 | 11kV | 586 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 207461 Sub 72059 faulty transformer Section isolated for safety clearance Excluded OMS 1732883 | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-02-07 | N | 146.5 | N | 14 | N | N | 1.1101 | 39.4971 | 428.2315
[7 empty] | 4547 | 12523 | 1733184 | 2020-02-07 15:27 | 2020-02-07 17:30 | 123 | 11kV | 113316 | 1174 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Zn3154 St Ives - Pnl.5 tripped on: A phase O.C Field EFIs: S4263 S7319 S61479 S8717 S8276 Flashover at UGOH between between S8276 and AB2514 tee PT1291 See 1752049 1752050 1752051 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | Unknown | Unknown | 2020-02-07 | N | 96.5213 | N | 14 | N | N | 1.1101 | 39.4971 | 82807.9905
[7 empty] | 4624 | 13468 | 1732969 | 2020-02-07 09:49 | 2020-02-07 18:05 | 496 | 11kV | 18136 | 51 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 11kv Rec 44945 Lower mangrove Ex Peats Ridge Panel 1 "Gunderman" tripped Remarks: tree/branch on OH mains. Small branch on mains adj PT13729 | February | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-02-07 | N | 355.6078 | N | 14 | N | N | 1.1101 | 39.4971 | 13253.2539
[7 empty] | 3508 | 2099 | 1733314 | 2020-02-07 17:36 | 2020-02-07 19:40 | 124 | 11kV | 9889 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | REC3280 Hunt Ave - tripped on: O/C Tree on OH mains in Gully crossing See 1754498 1754499 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-02-07 | N | 123.6125 | N | 14 | N | N | 1.1101 | 39.4971 | 7226.5895
[7 empty] | 3618 | 2994 | 1733358 | 2020-02-07 19:02 | 2020-02-07 20:31 | 89 | 11kV | 2492 | 28 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 207470 B PhaseLoose Bph 'D' conection on 11kV OHM to sub 46190. Excluded OMS No. 1733358 | February | 2020 | 2020Q3 | 2020 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-02-07 | N | 89 | N | 14 | N | N | 1.1101 | 39.4971 | 1821.0801
[7 empty] | 3683 | 3744 | 1733347 | 2020-02-07 18:38 | 2020-02-07 21:00 | 142 | 11kV | 5992 | 63 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kv rec 45035 Mangrove Mountain Ex Peats Ridge Panel 3 "Mangrove Mountain" tripped, reclosed, tripped and locked out Remarks: UG fault. 11kv UG fault beyond UGOH between LB42637 and LB44642 Ex. Peats Ridge Panel 3 | February | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | UG | Not Veg | 2020-02-07 | N | 95.1111 | N | 14 | N | N | 1.1101 | 39.4971 | 4378.7769
[7 empty] | 3793 | 4961 | 1733319 | 2020-02-07 21:55 | 2020-02-07 22:30 | 35 | 11kV | 315 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Section of 11kv feeder from LB4336 to AB3335 tee PT12069 Silvester Gore 3516 tee PT13777 Elwyns Wise ferry 1.0 interrupted to allow for tree removal Ex ZN12630 Peats Ridge 11kv feeder Panel No11 "Somersby" Remarks: tree/branch on OH mains. Tree on 11kv mains O/S 93 Elwins Rd Somersby, interrupted to allow repairs | February | 2020 | 2020Q3 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2020-02-07 | N | 35 | N | 14 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 3909 | 6008 | 1733431 | 2020-02-07 23:32 | 2020-02-08 03:22 | 230 | 11kV | 230 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Ex ZN14143 SOMERSBY section of 11kV Panel 12 PT13828 MT PENANG PACIFIC NO 1 centre phase HDO operated 63amp Cause: fuse failure. Fuse replaced, supply checked OK See 1756168 ex 1733431 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA12 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | OH | Not Veg | 2020-02-07 | N | 230 | N | 14 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 4637 | 13543 | 1733443 | 2020-02-08 05:18 | 2020-02-08 12:18 | 420 | 11kV | 94784 | 312 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | At Zn12630 Peats Ridge 11kv feeder Panel No.10: "Peats Ridge" feeder tripped on: Relays: ABC phase O/C on A & B protection Signals: 11kv trip Field EFI's: nil Abnormal: LK40550 OPEN DMA beyond Rec Panel no10 N/A Remarks: tree on 11kv mains between AB44636 to AB40559 | February | 2020 | 2020Q3 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 303.7949 | N | 4 | N | Y | 1.1101 | 39.4971 | 69265.3515
[7 empty] | 4646 | 13580 | 1733342 | 2020-02-07 18:27 | 2020-02-08 13:26 | 1139 | 11kV | 124171 | 323 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge - Pnl.10 tripped on SEF Bond Failed from LK40550 See 1757589 1757591 1757592 1757593 1757594 | February | 2020 | 2020Q3 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2020-02-07 | N | 384.4303 | N | 14 | N | N | 1.1101 | 39.4971 | 90740.5044
[7 empty] | 4639 | 13547 | 1733451 | 2020-02-08 07:56 | 2020-02-08 14:04 | 368 | 11kV | 163032 | 544 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | ZN14891 WYONG 11kV CB Panel 20 'Warnervale' fdr tripped Signals: Tx2 Group Earth, EFI, Left Relays: Minor Alarm, trip, EF Check, Reclose timer, Lockout, 51N, EFI<Tx2 EF Check Field EFI's: RE45203 Butt Gass Generator tripped Cause: tree branch brought down OH See 1757538,9,40 ex 1733484 | February | 2020 | 2020Q3 | 2020 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 299.6912 | N | 4 | N | Y | 1.1101 | 39.4971 | 119138.977
[7 empty] | 5050 | 17831 | 1757301 | 2020-02-08 14:10 | 2020-02-08 14:17 | 7 | 11kV | 231 | 33 | HV | Customer Installation Fault | Customer Installation | Recloser / Sectionaliser | Unplanned | No Weather Impact | Y | Ex Zn12630 peats Ridge 11kv VCB panel 3 Abnormal: LK41124 open, LB47448 closed Remarks: customer's installation. @S18020 Wisemans Inghams fault located on customers installation. Dop isolated and left warning tag. Customer will contact Ausgrid when electrician organised and CTW required. | February | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | Unknown | Unknown | 2020-02-08 | Y | 7 | N | 4 | N | Y | 1.1101 | 39.4971 | 168.808
[7 empty] | 5078 | 18117 | 1733583 | 2020-02-08 09:53 | 2020-02-08 15:10 | 317 | 11kV | 2318 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 1 'Dog Trap Rd' RE44602 Ourimbah Crrek rd tripped and reclosed on Signals: EF trip Cause Mains to Patrol. Patrol Clear. Tree Fallen on DW 100 metres away from ourimbah creek rd See 1756682,3 Ex 1733583 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 21.8679 | N | 4 | N | Y | 1.1101 | 39.4971 | 1693.926
[7 empty] | 3711 | 4064 | 1733400 | 2020-02-08 15:10 | 2020-02-08 16:35 | 85 | 11kV | 1530 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Heavy | Y | Autolink 44778 interrupted to remove very large tree from CCT | February | 2020 | 2020Q3 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 85 | N | 4 | N | Y | 1.1101 | 39.4971 | 1118.0789
[7 empty] | 3500 | 2032 | 1733619 | 2020-02-08 12:41 | 2020-02-08 16:41 | 240 | 11kV | 10800 | 45 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 207476 Earth Fault tree on mains | February | 2020 | 2020Q3 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-02-08 | N | 240 | N | 4 | N | N | 1.1101 | 39.4971 | 7892.3215
[7 empty] | 4090 | 8068 | 1733607 | 2020-02-08 14:30 | 2020-02-08 17:00 | 150 | 11kV | 7600 | 102 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Rain Heavy | Y | Section of Panel 18 Surry Hills Zn. Section of 11kV UG interrupted from S36057 Turner Pitt to S1016 PMG Redfern St via S5240 Rachel Forster. S5240 interrupted due to excavation at a construction site has caused S5240 to collapse into excavation due to heavy rain. See 1733681, 1751892 | February | 2020 | 2020Q3 | 2020 | ZN901:PA18 | ZN901:PA38 | ZN00901/000038 | SYDNEY | UG | Not Veg | 2020-02-08 | N | 74.5098 | N | 4 | N | N | 1.1101 | 39.4971 | 5553.8558
[7 empty] | 3418 | 1149 | 1733715 | 2020-02-08 15:35 | 2020-02-08 17:08 | 93 | 11kV | 21948 | 236 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | REC3202 Pacific South Cowan - Tripped on: O/C Tree on mains near PT834 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2020-02-08 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 16038.951
[7 empty] | 3693 | 3824 | 1733688 | 2020-02-08 15:02 | 2020-02-08 17:41 | 159 | 11kV | 135786 | 854 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex ZN12580 ERINA section of 11kV Panel 4 RE49613 Marana Tulip tripped and locked out on OC Cause: tree branch on oh mains. Tree Brought down 11kv near AB40506 | February | 2020 | 2020Q3 | 2020 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 159 | N | 4 | N | Y | 1.1101 | 39.4971 | 99228.4038
[7 empty] | 4882 | 15775 | 1733606 | 2020-02-08 12:08 | 2020-02-08 19:45 | 457 | 11kV | 74542 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | @ZN14144 Wamberal Panel 2 11kv recloser 44946 Kunarra Rd tripped on Signals: OC trip Remarks; tree brought down 11kv near REC 44946. Dop restored PT18847 via LV// lk.no36221 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 449.0482 | N | 4 | N | Y | 1.1101 | 39.4971 | 54473.095
[7 empty] | 3898 | 5953 | 1733706 | 2020-02-08 15:04 | 2020-02-08 19:46 | 282 | 11kV | 36996 | 184 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | LID 207475 Fault flag indication on fault detector B sw 83126 Tree brought down 11lkV OHM adjacent sub 27272. Excluded OMS 1733694, 1733731, 1733706 | February | 2020 | 2020Q3 | 2020 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2020-02-08 | N | 201.0652 | N | 4 | N | N | 1.1101 | 39.4971 | 27035.5856
[7 empty] | 4974 | 16833 | 1733771 | 2020-02-08 17:33 | 2020-02-08 23:40 | 367 | 11kV | 19802 | 206 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Ex ZN12600 LISAROW section of 11kV Panel 2 'Holgate' fdr RE41845 North Erina tripped reclosed tripped and locked out on overcurrent Abnormal: LB44993 defective and open; RE40239 closed Cause: tree/branch brought down 11kV OH near PT11410. AP issued to Linesman @20:45 See 1755912,3 ex 1733771,8,83,4,810,1,4 | February | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-02-08 | Y | 96.1262 | N | 4 | N | Y | 1.1101 | 39.4971 | 14470.7175
[7 empty] | 4161 | 8960 | 1733551 | 2020-02-08 10:16 | 2020-02-09 01:08 | 892 | 11kV | 314341 | 669 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Rain Wind Storm | Y | Ex ZN14143 SOMERSBY section of 11kV Panel 17 'Wise Ferry Somersby 2.0 & etc' RE48437 Peats Ridge Cooks 1.35 tripped on Signals: OC trip, Lockout Cause: not ascertained Possible fault in CCT between LB43212 to RE45202 tee PT14915 PT14995 PT46444 PT18481 PT13348 still out Bypass AB @ RE44961 closed for duration to be opened on completion Major Storm See 1756531,2,3,49,50,1,2,3,4,7,8 2nd 1756534,41,2,6,7,8 Ex 1733551,634,926,63,4480,9351,2,41029,2160 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-02-08 | Y | 469.867 | N | 4 | N | Y | 1.1101 | 39.4971 | 229711.1313
[7 empty] | 5085 | 18151 | 1733932 | 2020-02-09 04:07 | 2020-02-09 06:08 | 121 | 11kV | 13915 | 115 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12600 LISAROW section of 11kV Panel 2 CP41020 Wattle Tree Rd North trippedon OC trip Fault btwn CP44336 to CP45186 tee PT64478. PT64478 LV// to PT11864 See 1755995 ex 1733929,32 | February | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 121 | N | 3 | N | Y | 1.1101 | 39.4971 | 10168.6716
[7 empty] | 4239 | 9650 | 1733951 | 2020-02-09 06:13 | 2020-02-09 09:22 | 189 | 11kV | 127575 | 675 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12600 LISAROW 11kV CB Panel 2 'Chamberlain Taylor 0.1' tripped on Relays: B phase high limit Abnormal: CP44993 Defective open; CP40239 closed Tree on OH mains See 1733951 ex 1733964 | February | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 189 | N | 3 | N | Y | 1.1101 | 39.4971 | 93228.0472
[7 empty] | 4095 | 8131 | 1733991 | 2020-02-09 06:51 | 2020-02-09 10:16 | 205 | 11kV | 58870 | 290 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC427 Arcadia Fagan Park - tripped on: O/C Abnormal: LB62109 Closed with REC421 Open DMA Storm See 1755136 1755137 1755138 | February | 2020 | 2020Q3 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2020-02-09 | Y | 203 | N | 3 | N | Y | 1.1101 | 39.4971 | 43020.4596
[7 empty] | 3938 | 6285 | 1734061 | 2020-02-09 07:40 | 2020-02-09 11:24 | 224 | 11kV | 234403 | 1221 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 207483 2 fault operation A Phase Overcurrent Branch found on 11kV OHM one span past ABS 5508 removed by Dop Excluded OMS 1734061 1734035 1734094 | February | 2020 | 2020Q3 | 2020 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Veg | 2020-02-09 | Y | 191.9762 | N | 3 | N | Y | 1.1101 | 39.4971 | 171294.7987
[7 empty] | 4886 | 15819 | 1734400 | 2020-02-09 09:27 | 2020-02-09 13:21 | 234 | 11kV | 197965 | 906 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Long Jetty panel 20 Relays: E/F check, EFI, SEF Abnormal: no remarks: restored | February | 2020 | 2020Q3 | 2020 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 218.5044 | N | 3 | N | Y | 1.1101 | 39.4971 | 144666.983
[7 empty] | 4617 | 13384 | 1735424 | 2020-02-09 12:47 | 2020-02-09 13:40 | 53 | 11kV | 106 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 207485 B & C Phase Line DOLF : 10 Amp Line Fuse 40855 not in model Excluded OMS 1735424 | February | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-02-09 | N | 53 | N | 3 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 5003 | 17259 | 1735214 | 2020-02-09 12:12 | 2020-02-09 14:39 | 147 | 11kV | 10101 | 69 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn3472 Sefton - Pnl16 tripped UG cable fault between S6641 and S77857 See 1749957 1749958 | February | 2020 | 2020Q3 | 2020 | ZN3472:PA16 | ZN3472:PA16 | ZN03472/000016 | CUMBERLAND | UG | Not Veg | 2020-02-09 | Y | 146.3913 | N | 3 | N | Y | 1.1101 | 39.4971 | 7381.5129
[7 empty] | 3843 | 5455 | 1734296 | 2020-02-09 09:05 | 2020-02-09 14:40 | 335 | 11kV | 388705 | 1685 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | Rain Wind Storm | Y | ZN14891 WYONG 11kV CB Panel 10 'Wyongah' tripped on Reclose lockout, Reclose time, Fault Check, O/C, E/F, S/BC Cause: Tree near LK40745 removed by DOp See 1757517,8,9 Ex 1734296 | February | 2020 | 2020Q3 | 2020 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 230.6855 | N | 3 | N | Y | 1.1101 | 39.4971 | 284054.1491
[7 empty] | 3804 | 5049 | 1735197 | 2020-02-09 12:04 | 2020-02-09 14:50 | 166 | 11kV | 31710 | 277 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | LID 207487 3 fault operations C Phase Earth Fault Suspect UGM Fault at Sw 82710 Suspect directional protection at Port Waratah Coal Loader sub faulty ( looking the wrong way ) Sw 91144 Remained Closed Sw 90800 Tripped Dir E/F Sw 91577 Tripped Dir E/F Excluded OMS 1735197 1735198 1735265 | February | 2020 | 2020Q3 | 2020 | 204:82710 | 204:82703 | ZN00204/082703 | NEWCASTLE | UG | Not Veg | 2020-02-09 | Y | 114.4765 | N | 3 | N | Y | 1.1101 | 39.4971 | 23172.7327
[7 empty] | 3899 | 5954 | 1734071 | 2020-02-09 07:38 | 2020-02-09 14:51 | 433 | 11kV | 22949 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 207486 Overcurrent Tree on mains between pole GU 54301 and GU 54310 | February | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-02-09 | N | 433 | N | 3 | N | N | 1.1101 | 39.4971 | 16770.4523
[7 empty] | 3516 | 2179 | 1734173 | 2020-02-09 08:22 | 2020-02-09 16:05 | 463 | 11kV | 296158 | 824 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12580 ERINA 11kV CB Panel 8 tripped EFI, SEF timmed 11kv trip Major Storm 11kv down adj LB45143 AP left at PT11688 See 1755285,8,9,90,1 Ex 1734173,6958,9 | February | 2020 | 2020Q3 | 2020 | ZN12580:PA8 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 359.415 | N | 3 | N | Y | 1.1101 | 39.4971 | 216423.5312
[7 empty] | 4462 | 11604 | 1734239 | 2020-02-09 08:09 | 2020-02-09 16:45 | 516 | 11kV | 195225 | 974 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn9550 Gwawley Bay Panel 42 tripped on A and B phase OC Abnormal SwitchingL LB35469 Closed, AB35609 Opened Cause: Tree brought down OHG 139 Corea St Miranda from AB39348 to LB35642 to Ab35609 tee PT9638 See OMS 1750878 1750879 1734146 1734379 1734245 | February | 2020 | 2020Q3 | 2020 | ZN9550:PA42 | ZN9550:PA42 | ZN09550/000042 | SUTHERLAND | OH | Veg | 2020-02-09 | Y | 200.4363 | N | 3 | N | Y | 1.1101 | 39.4971 | 142664.6718
[7 empty] | 3311 | 207 | 1733949 | 2020-02-09 05:55 | 2020-02-09 16:45 | 650 | 11kV | 90716 | 184 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 207491 2 fault operations Tree on mains at pole GT53357. Excluded OMS 1733949 | February | 2020 | 2020Q3 | 2020 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2020-02-09 | Y | 493.0217 | N | 3 | N | Y | 1.1101 | 39.4971 | 66292.5771
[7 empty] | 4730 | 14363 | 1736829 | 2020-02-09 16:02 | 2020-02-09 17:03 | 61 | 11kV | 61 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | Y | LID 207492 C Phase DOLF : 16 Amp Excluded OMS 1736829 | February | 2020 | 2020Q3 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2020-02-09 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 4852 | 15556 | 1755394 | 2020-02-09 13:29 | 2020-02-09 17:10 | 221 | 11kV | 164912 | 906 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Wind Storm | Y | Long Jetty Panel 20 Relays: SEF Details: 2 HVDO's operated footpath + roadside phase @ PIT 12118 suspect defective Tx remarks: PT12118 restored via LV// LK no.31941. A/P to Ausgrid Authorised person @ 18:00 | February | 2020 | 2020Q3 | 2020 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 182.0221 | N | 3 | N | Y | 1.1101 | 39.4971 | 120512.8255
[7 empty] | 3878 | 5743 | 1734588 | 2020-02-09 10:08 | 2020-02-09 17:45 | 457 | 11kV | 48877 | 335 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Zn35900 Potts Hill - Pnl.6 tripped on: E/F & O/C UGOH failed. Broken away and earthed to restore S2527 See 1747077 1747078 | February | 2020 | 2020Q3 | 2020 | ZN35900:PA6 | ZN35900:PA6 | ZN35900/000006 | CUMBERLAND | Unknown | Unknown | 2020-02-09 | Y | 145.9015 | N | 3 | N | Y | 1.1101 | 39.4971 | 35717.87
[7 empty] | 4751 | 14515 | 1733940 | 2020-02-09 05:34 | 2020-02-09 18:00 | 746 | 11kV | 93536 | 408 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | Y | LID 207495 1 fault operation Tree on mains KR-30533 Abercrombie Rd. Six spans damaged. Excluded OMS 1733940/3944/4028/4049 | February | 2020 | 2020Q3 | 2020 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2020-02-09 | Y | 229.2549 | N | 3 | N | Y | 1.1101 | 39.4971 | 68353.35
[7 empty] | 3382 | 809 | 1737520 | 2020-02-09 18:29 | 2020-02-09 18:53 | 24 | 11kV | 42864 | 1786 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At 12610 long jetty zn p6 the lng jetty fdr open for safety "Rhodes Drive' fdr Remarks: OH down. O/S 54 Sth Pacific St made safe | February | 2020 | 2020Q3 | 2020 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 24 | N | 3 | N | Y | 1.1101 | 39.4971 | 31323.7469
[7 empty] | 4186 | 9242 | 1733989 | 2020-02-09 06:57 | 2020-02-09 19:30 | 753 | 11kV | 514348 | 1500 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | Y | LID 207496 1 fault operation 3 phase Overcurrent Broken X-arm KT-40531 and bond burnt off KT-40814. Excluded OMS 1733989/3998/4002 | February | 2020 | 2020Q3 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2020-02-09 | Y | 342.8987 | N | 3 | N | Y | 1.1101 | 39.4971 | 375870.3477
[7 empty] | 5092 | 18176 | 1734109 | 2020-02-09 07:47 | 2020-02-09 20:25 | 758 | 11kV | 32594 | 43 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | Y | LID 207499 1 fault operation 3 Phase Overcurrent; Earth Fault Tree on mains near PT.11399 Excluded OMS 1734109/656 | February | 2020 | 2020Q3 | 2020 | 217:33607 | 217:33607 | ZN00217/033607 | LAKE MACQUARIE | OH | Veg | 2020-02-09 | Y | 758 | Y | 3 | N | Y | 1.1101 | 39.4971 | 23818.7338
[7 empty] | 4351 | 10641 | 1734953 | 2020-02-09 11:20 | 2020-02-09 20:38 | 558 | 11kV | 1074156 | 1978 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | ZN12580 ERINA 11kV CB Panel 14 tripped on B & C Phase overcurrent, lockout, reclose, timer Major Storm No cause ascertained. DOp patrolled See 1755308,9 ex 1734953 1734956,9421 | February | 2020 | 2020Q3 | 2020 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 543.0516 | Y | 3 | N | Y | 1.1101 | 39.4971 | 784961.5226
[7 empty] | 4413 | 11194 | 1736683 | 2020-02-09 15:37 | 2020-02-09 21:15 | 338 | 11kV | 457678 | 1751 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35900 Potts Hill - Pnl.2 tripped on B & Cphase O.C Abnormal: S7213 Sw/B closed with S8241 Sw/A Open Storm S4397 - Dist #2 - LV mains down See1747082 1747083 | February | 2020 | 2020Q3 | 2020 | ZN35900:PA2 | ZN35900:PA2 | ZN35900/000002 | CUMBERLAND | OH | Not Veg | 2020-02-09 | Y | 261.3809 | N | 3 | N | Y | 1.1101 | 39.4971 | 334457.5832
[7 empty] | 3313 | 216 | 1734510 | 2020-02-09 12:13 | 2020-02-09 21:41 | 568 | 11kV | 297064 | 523 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra -Pnl.15 tripped on SEF Abnormal: S49939 sw/B Open. See Pnl.22 outage for other abnormals | February | 2020 | 2020Q3 | 2020 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 568 | Y | 3 | N | Y | 1.1101 | 39.4971 | 217085.6093
[7 empty] | 4364 | 10722 | 1734213 | 2020-02-09 08:40 | 2020-02-09 22:30 | 830 | 11kV | 660118 | 1532 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | LID 207503 1 fault operation C Phase Overcurrent; Earth Fault PT. 27851 and 3 span of mains down from tree. Excluded OMS 1734213/5677 | February | 2020 | 2020Q3 | 2020 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Veg | 2020-02-09 | Y | 430.8864 | N | 3 | N | Y | 1.1101 | 39.4971 | 482394.7642
[7 empty] | 3978 | 6682 | 1734999 | 2020-02-09 11:30 | 2020-02-10 02:15 | 885 | 11kV | 531000 | 600 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12570 AVOCA section of 11kV Panel 37 RE45180 Avoca Beach opened for safety to remove branch near 11kv LB77912 OH See 1750543 ex 1734999,5301 | February | 2020 | 2020Q3 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 885 | Y | 3 | N | Y | 1.1101 | 39.4971 | 388039.1382
[7 empty] | 4508 | 12136 | 1734536 | 2020-02-09 09:59 | 2020-02-10 02:54 | 1015 | 11kV | 1788830 | 1778 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | ZN12570 AVOCA 11kV CB Panel 24 tripped on IOC B+C Phase, Reclose See 1750418 1750422 ex 1734536 | February | 2020 | 2020Q3 | 2020 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1006.0911 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1307224.2024
[7 empty] | 4997 | 17179 | 1738341 | 2020-02-09 21:44 | 2020-02-10 05:24 | 460 | 11kV | 689540 | 1499 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At Zn9550 Gwawley Bay panel 43 tripped on A and B phase OC EFI Abnormal Switching: CP35327 Closed, CP35010 Open Cause: Tree on PT9939 See OMS 1750843 1750844 1750845 1738341 | February | 2020 | 2020Q3 | 2020 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Veg | 2020-02-09 | Y | 460 | N | 3 | N | Y | 1.1101 | 39.4971 | 503895.494
[7 empty] | 3362 | 651 | 1738794 | 2020-02-10 05:27 | 2020-02-10 07:50 | 143 | 11kV | 1287 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | Y | LID 207509 A & B Phase DOLF : 16 Amp excluded OMS 1738794 | February | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-02-10 | N | 143 | N | 11 | N | N | 1.1101 | 39.4971 | 940.5016
[7 empty] | 3364 | 658 | 1738908 | 2020-02-10 06:59 | 2020-02-10 08:25 | 86 | 11kV | 86 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Heavy | Y | LIS 207507 A Phase Live Line Clamp came away | February | 2020 | 2020Q3 | 2020 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2020-02-10 | N | 86 | N | 11 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 4369 | 10763 | 1738102 | 2020-02-09 20:29 | 2020-02-10 12:30 | 961 | 11kV | 922959 | 1219 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12690 BERKELEY VALE 11kV CB Panel 19 tripped A&B Phase IOC See 1752759,60,1 Ex 1738102,53,977,9371 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 757.1444 | Y | 3 | N | Y | 1.1101 | 39.4971 | 674471.2145
[7 empty] | 4303 | 10253 | 1734102 | 2020-02-09 07:52 | 2020-02-10 12:34 | 1722 | 11kV | 1092399 | 646 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Wind Storm | Y | Umina Panel 1 Relays: OC Recloser locked out Remarks: tree branch removed top of PT12085 | February | 2020 | 2020Q3 | 2020 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1691.0201 | Y | 3 | N | Y | 1.1101 | 39.4971 | 798292.9689
[7 empty] | 3896 | 5921 | 1742026 | 2020-02-10 11:00 | 2020-02-10 12:40 | 100 | 11kV | 200 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | Y | LID 207511 A Phase DOLF : 10 Amp Excluded OMS 1738969 | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-02-10 | N | 100 | N | 11 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 3578 | 2662 | 1738631 | 2020-02-09 12:14 | 2020-02-10 14:00 | 1545.5 | 11kV | 284372 | 184 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3472 Sefton - Pnl.28 - tree brought 11kV mains down beyond LB2594 | February | 2020 | 2020Q3 | 2020 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-02-09 | Y | 1545.5 | N | 3 | N | Y | 1.1101 | 39.4971 | 207810.67
[7 empty] | 4258 | 9879 | 1738120 | 2020-02-09 20:34 | 2020-02-10 14:25 | 1071 | 11kV | 356679 | 1307 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn1850 Bass Hills - Pnl.32 tripped on: B & Cphase IOC Abnormal: LB49711 Closed with S5963 Sw/F Open DMA Flood, beyond LB2594 & AB373 - 11kV down HV into LV at PT47411 See 1746931 1746934 1746935 | February | 2020 | 2020Q3 | 2020 | ZN1850:PA32 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-02-09 | Y | 272.899 | N | 3 | N | Y | 1.1101 | 39.4971 | 260650.493
[7 empty] | 3923 | 6140 | 1738684 | 2020-02-10 02:12 | 2020-02-10 15:00 | 768 | 11kV | 2083584 | 2713 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN10999 Kogarah Panel 12 tripped Abnormal Switching : SW/A Closed @ S48506, CP62384 Open Confirmed outage on DNMS trends See OMS 1752907 1738684 | February | 2020 | 2020Q3 | 2020 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Not Veg | 2020-02-10 | Y | 768 | N | 11 | N | Y | 1.1101 | 39.4971 | 1522621.7319
[7 empty] | 4140 | 8582 | 1740395 | 2020-02-10 14:44 | 2020-02-10 15:43 | 59 | 11kV | 62658 | 1062 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Previous Storm | Y | AT Zn10994 Mortdale - Panel 3 Tripped Cause: UGOH fault Note: Trip and Restoration time taken from DNMS | February | 2020 | 2020Q3 | 2020 | ZN10994:PA3 | ZN10994:PA3 | ZN10994/000003 | GEORGES RIVER | Unknown | Unknown | 2020-02-10 | N | 59 | N | 11 | N | N | 1.1101 | 39.4971 | 45788.6183
[7 empty] | 3326 | 335 | 1738665 | 2020-02-10 01:26 | 2020-02-10 17:32 | 966 | 11kV | 168380 | 305 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | Y | LID 207513 1 fault operation Earth Fault 3 bays of mains on the ground from pole GW-10013 Excluded OMS 1733668, 1738665 | February | 2020 | 2020Q3 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2020-02-10 | Y | 552.0656 | Y | 11 | N | Y | 1.1101 | 39.4971 | 123047.1376
[7 empty] | 5123 | 18391 | 1740044 | 2020-02-10 12:45 | 2020-02-10 17:40 | 295 | 11kV | 243909 | 2153 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Wind Storm | Y | At Zn36100 Rose Bay Panel 6 - Feeder has tripped Signals: 11kV trip Relays: 50T A, B & C. EFI, Fault Check Field EFI's: S36181 Rose Bay Aux No.1 The 11kV end box (Sw B) at S.2774 SIMPSON O'BRIEN has exploded (Ex Zn.36100 Rose Bay - Panel 6) 1751636, 1751637, 1751641, 1751642, 1751643, 1740044 (withdrawn) | February | 2020 | 2020Q3 | 2020 | ZN36100:PA6 | ZN36100:PA6 | ZN36100/000006 | WAVERLEY | UG | Not Veg | 2020-02-10 | N | 113.288 | N | 11 | N | N | 1.1101 | 39.4971 | 178241.5031
[7 empty] | 3293 | 65 | 1736003 | 2020-02-09 16:21 | 2020-02-10 17:52 | 1531 | 11kV | 494513 | 323 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC20112 tripped on: O/C Abnormal: LB20518 closed with LB77332 Open DMA Storm | February | 2020 | 2020Q3 | 2020 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2020-02-09 | Y | 1531 | Y | 3 | N | Y | 1.1101 | 39.4971 | 361375.5147
[7 empty] | 5204 | 18992 | 1736276 | 2020-02-09 13:44 | 2020-02-10 18:00 | 1696 | 11kV | 983664 | 762 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZM10993 Hurstville North Panel 33 tripped Cause: Tree on OH mains @ PT10233 - Isolated and AP issued for removal See OMS 1735447 1739623 | February | 2020 | 2020Q3 | 2020 | ZN10993:PA33 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | OH | Veg | 2020-02-09 | Y | 1290.8976 | Y | 3 | N | Y | 1.1101 | 39.4971 | 718832.638
[7 empty] | 4040 | 7444 | 1734203 | 2020-02-09 08:36 | 2020-02-10 18:00 | 2004 | 11kV | 2257476 | 1218 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN14892 CHARMHAVEN section of 11kV Panel 16 IR78525 Sane Remo tripped on lockout OC trip Tree on 11kv between S46911SwB to LB41807 to CP41808 Tree on 11kv between LB48507 to CP43626 to S18470SwA 11kV Hanging low near USL 41808 See 1753490,2,3 Ex 1734203,40478,513 | February | 2020 | 2020Q3 | 2020 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1853.4286 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1649696.8765
[7 empty] | 4917 | 16196 | 1734546 | 2020-02-09 10:03 | 2020-02-10 18:00 | 1917 | 11kV | 828815 | 575 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Long Jetty REC50249 Kilpling Shakespear Remarks: tree on 11kv beyond LK's 41444 A/P's issued to tree trimmers @ 1150am. burnt off bond. Also near UGOH ex LB47175. | February | 2020 | 2020Q3 | 2020 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 1441.4174 | Y | 3 | N | Y | 1.1101 | 39.4971 | 605673.5561
[7 empty] | 4712 | 14222 | 1740685 | 2020-02-10 16:43 | 2020-02-10 18:23 | 100 | 11kV | 30820 | 313 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207515 1 fault operation C Phase Overcurrent | February | 2020 | 2020Q3 | 2020 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Veg | 2020-02-10 | N | 98.4665 | N | 11 | N | N | 1.1101 | 39.4971 | 22522.347
[7 empty] | 5125 | 18401 | 1740611 | 2020-02-10 16:20 | 2020-02-10 18:34 | 134 | 11kV | 127552 | 1040 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207514 1 fault operation Overcurrent fdr patrolled and restored Excluded oms 1740611 | February | 2020 | 2020Q3 | 2020 | 532:83301 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2020-02-10 | N | 122.6462 | N | 11 | N | N | 1.1101 | 39.4971 | 93211.2395
[7 empty] | 4939 | 16455 | 1735146 | 2020-02-09 11:59 | 2020-02-10 18:40 | 1841 | 11kV | 4150562 | 2350 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra - Pnl.22 tripped on: B & C phase O/C Abnormal: LB116 Closed with LB1442 open. S46651 Sw/A Closed with S66077 Sw/A Open. AB1019 Closed with S49943 Sw/A Open. AB1161 Closed with S64281 Sw/A Open Storm damage. See 1754349 1754350 1754351 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 1766.1966 | Y | 3 | N | Y | 1.1101 | 39.4971 | 3033108.2887
[7 empty] | 4177 | 9158 | 1740840 | 2020-02-10 18:00 | 2020-02-10 19:45 | 104.7667 | 11kV | 12152.9333 | 116 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Zn1287 Revesby - Pnl.4 - 11kV feeder interrupted from LB1626 to allow tree to be removed from mains in Sandy Pt | February | 2020 | 2020Q3 | 2020 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | SUTHERLAND | OH | Veg | 2020-02-10 | N | 104.7667 | N | 11 | N | N | 1.1101 | 39.4971 | 8881.0052
[7 empty] | 3337 | 451 | 1741038 | 2020-02-10 20:03 | 2020-02-10 20:34 | 31 | 11kV | 5456 | 176 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | Y | LID 207520 Wire off pin GW-50288 repaired uinder AP | February | 2020 | 2020Q3 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2020-02-10 | N | 31 | N | 11 | N | N | 1.1101 | 39.4971 | 3987.0839
[7 empty] | 4197 | 9303 | 1740360 | 2020-02-10 21:00 | 2020-02-10 22:40 | 100 | 11kV | 7900 | 79 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 207531 cracked insulator & wire off pin pole KT 70117 Excluded OMS 1740360 | February | 2020 | 2020Q3 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | NEWCASTLE | OH | Not Veg | 2020-02-10 | N | 100 | N | 11 | N | N | 1.1101 | 39.4971 | 5773.087
[7 empty] | 3546 | 2440 | 1740688 | 2020-02-10 16:45 | 2020-02-10 22:46 | 361 | 11kV | 25417 | 144 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 207517 1 fault operation A phase Overcurrent Excluded OMS 1740688 | February | 2020 | 2020Q3 | 2020 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Veg | 2020-02-10 | N | 176.5069 | N | 11 | N | N | 1.1101 | 39.4971 | 18573.9939
[7 empty] | 4960 | 16736 | 1734908 | 2020-02-09 11:14 | 2020-02-11 01:45 | 2311 | 11kV | 2405089 | 1299 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN10999 Kogarah Panel 10 tripped Cause: Tree branch on AB30059 DOp unable to remove. OH required to assist Abnormal Switching: SW/A Open @ S10158 11kV Feeder from AB30059 to AB31078 tee PT10201 ISolated and AP left for mains to remove tree branch See OMS 1752884 1752886 1752887 1734908 1740781 | February | 2020 | 2020Q3 | 2020 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Veg | 2020-02-09 | Y | 1851.4927 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1757568.1031
[7 empty] | 4487 | 11880 | 1738984 | 2020-02-10 07:38 | 2020-02-11 07:04 | 1406 | 11kV | 137788 | 98 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12600 LISAROW section of 11kV Panel 2 RE41066 MacDonalds Rd tripped on OC, SEF, Lockout OH 11kV wires down Major Storm | February | 2020 | 2020Q3 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2020-02-10 | Y | 1406 | N | 11 | N | Y | 1.1101 | 39.4971 | 100691.4063
[7 empty] | 5345 | 20380 | 1734543 | 2020-02-09 10:04 | 2020-02-11 08:50 | 2806 | 11kV | 261212 | 194 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | CP24703 Plateau Palmgrove Sw/C - HV Fuse blown 11kV Feeder from S47056 Sw/B interrupted to replace fuses at CP24703 Storm see 1751306 1751307 | February | 2020 | 2020Q3 | 2020 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | OH | Not Veg | 2020-02-09 | Y | 1346.4536 | Y | 3 | N | Y | 1.1101 | 39.4971 | 190886.0252
[7 empty] | 5168 | 18730 | 1734226 | 2020-02-09 08:44 | 2020-02-11 09:02 | 2898 | 11kV | 1126390 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal - Pnl.2 tripped on: IOC Tree on PT12362 See 1757546 1757550 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1323.6075 | Y | 3 | N | Y | 1.1101 | 39.4971 | 823132.5891
[7 empty] | 5028 | 17516 | 1741238 | 2020-02-11 06:31 | 2020-02-11 09:06 | 155 | 11kV | 96389 | 686 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Zn15001 Brookvale - Pnl.8 tripped on: B & C phase O/C Cause not ascertained See 1750400 1750401 1750403 1750404 | February | 2020 | 2020Q3 | 2020 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Veg | 2020-02-11 | N | 140.5087 | N | 5 | N | N | 1.1101 | 39.4971 | 70438.2382
[7 empty] | 3723 | 4167 | 1734480 | 2020-02-09 09:47 | 2020-02-11 10:15 | 2908 | 11kV | 383414 | 198 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN14143 SOMERSBY 11kV CB Panel 17 'Wise Ferry Somersby 2.0 & etc' tripped Signals: SEF Abnormal: LB43212 to RE45202 tee PT14915 PT14995 PT46444 PT18481 PT13348 DMA/out at time of fault Multiple Trees on 11kv mains in various locations Major Storm See 1756531,2,3,49,50,1,2,3,4,7,8 2nd 1756534,41,2,6,7,8 Ex 1733551,634,926,63,4480,9351,2,41029,2160 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1936.4343 | Y | 3 | N | Y | 1.1101 | 39.4971 | 280187.6424
[7 empty] | 3453 | 1517 | 1739449 | 2020-02-10 09:54 | 2020-02-11 12:29 | 1594.8833 | 11kV | 196156.65 | 123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Interrupted to remove tree from 11kV See 1739449 1740139 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2020-02-10 | Y | 1594.7695 | N | 11 | N | Y | 1.1101 | 39.4971 | 143345.4942
[7 empty] | 3827 | 5360 | 1735408 | 2020-02-09 12:43 | 2020-02-11 12:34 | 2871 | 11kV | 488070 | 170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12570 AVOCA section of 11kV Panel 35 IR61952 Ballorok Avoga tripped on OC trip, lockout, alarm Branch removed from PT12687 by DOp Dabovic | February | 2020 | 2020Q3 | 2020 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 2871 | Y | 3 | N | Y | 1.1101 | 39.4971 | 356667.1604
[7 empty] | 4099 | 8193 | 1740435 | 2020-02-10 19:45 | 2020-02-11 13:50 | 1085 | 11kV | 8585 | 40 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC24722 interrupted at request of DOP due to large tree on AB20623 See 1750381 1750382 | February | 2020 | 2020Q3 | 2020 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2020-02-10 | Y | 214.625 | N | 11 | N | Y | 1.1101 | 39.4971 | 6273.6648
[7 empty] | 3985 | 6765 | 1741651 | 2020-02-11 03:48 | 2020-02-11 13:56 | 608 | 11kV | 8512 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex ZN14143 SOMERSBY section of 11kV Panel 6 interrupted for safety. Suspect Damage to OH. DNMS recorded switch open and close Previous Major Storm | February | 2020 | 2020Q3 | 2020 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2020-02-11 | N | 608 | Y | 5 | N | Y | 1.1101 | 39.4971 | 6220.3185
[7 empty] | 4384 | 10864 | 1756542 | 2020-02-09 02:02 | 2020-02-11 14:15 | 3613 | 11kV | 154564 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Rain Wind Storm | Y | Ex ZN14143 SOMERSBY section of 11kV Panel 17 'Wise Ferry Somersby 2.0 & etc' RE48437 Peats Ridge Cooks 1.35 tripped on Signals: OC trip, Lockout Cause: not ascertained Possible fault in CCT between LB43212 to RE45202 tee PT14915 PT14995 PT46444 PT18481 PT13348 still out Bypass AB @ RE44961 closed for duration to be opened on completion Major Storm See 1756531,2,3,49,50,1,2,3,4,7,8 2nd 1756534,41,2,6,7,8 Ex 1733551,634,926,63,4480,9351,2,41029,2160 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 2664.8966 | Y | 3 | N | Y | 1.1101 | 39.4971 | 112950.8123
[7 empty] | 5019 | 17422 | 1742102 | 2020-02-11 15:19 | 2020-02-11 15:45 | 26 | 11kV | 390 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 207542 A Phase DOLF : 50 Amp HV Fuse Element Fatigue Excluded OMS 1742102 | February | 2020 | 2020Q3 | 2020 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-02-11 | N | 26 | N | 5 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 3401 | 988 | 1736804 | 2020-02-09 15:56 | 2020-02-11 15:56 | 2880 | 11kV | 1327680 | 461 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills - Pnl.44 tripped on: B & C phase O/C Storm | February | 2020 | 2020Q3 | 2020 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 2880 | Y | 3 | N | Y | 1.1101 | 39.4971 | 970229.3841
[7 empty] | 4479 | 11826 | 1739524 | 2020-02-10 03:02 | 2020-02-11 16:55 | 2273 | 11kV | 361407 | 159 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12570 AVOCA section of 11kV Panel 37 LB41682 to LB41670 Isolated due to damage on OH mains See 1750548 ex 1739524 | February | 2020 | 2020Q3 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2020-02-10 | Y | 2273 | N | 11 | N | Y | 1.1101 | 39.4971 | 264105.5759
[7 empty] | 3919 | 6110 | 1756692 | 2020-02-09 09:37 | 2020-02-11 17:10 | 3333 | 11kV | 116194 | 36 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Rec45189 Cooks Peats Ridge Relays: OC trip, lockout Abnormal: suspect yes Remarks: not patrolled (in scan fail) reclosers still auto | February | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 3227.6111 | Y | 3 | N | Y | 1.1101 | 39.4971 | 84911.1481
[7 empty] | 3761 | 4680 | 1740832 | 2020-02-10 17:55 | 2020-02-11 18:30 | 1475 | 11kV | 216945 | 1687 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | Y | At Zn9700 Kirrawee Panel 16 tripped on B phase OC, EF and EFI Abnormal Switching: LB35674 Closed, SW/A At S9881 Open, LB35855 Open Cause: 11kV Cable fault from S9013 to S9837 See OMS 1750709 1750710 1750711 1740832 1740999 | February | 2020 | 2020Q3 | 2020 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | UG | Not Veg | 2020-02-10 | Y | 128.5981 | N | 11 | N | Y | 1.1101 | 39.4971 | 158537.0072
[7 empty] | 4168 | 9064 | 1734176 | 2020-02-09 11:32 | 2020-02-11 19:00 | 3328 | 11kV | 258048 | 86 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC44582 Erina - tripped on SEF Storm damage See 1757542 1757544 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 3000.5581 | Y | 3 | N | Y | 1.1101 | 39.4971 | 188573.8673
[7 empty] | 4839 | 15416 | 1737980 | 2020-02-09 19:53 | 2020-02-11 19:30 | 2857 | 11kV | 279098.4 | 338 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Wind Storm | Y | Zn35800 Bankstown Pnl.21 tripped Area between S46109 Sw/B to S8720 Sw/B to S2468 Sw/B flooded See 1757193 1757194 1757195 | February | 2020 | 2020Q3 | 2020 | ZN35800:PA21 | ZN35800:PA21 | ZN35800/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-02-09 | Y | 825.7349 | N | 3 | N | Y | 1.1101 | 39.4971 | 203956.8787
[7 empty] | 4709 | 14193 | 1734444 | 2020-02-09 09:40 | 2020-02-11 19:30 | 3470 | 11kV | 14556 | 31 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Wind Strong | Y | LID 207506 Transformer 2 faulty Excluded OMS 1734444 | February | 2020 | 2020Q3 | 2020 | 258:80781 | 258:80781 | ZN00258/080781 | NEWCASTLE | UG | Not Veg | 2020-02-09 | Y | 469.5484 | N | 3 | N | Y | 1.1101 | 39.4971 | 10637.0955
[7 empty] | 4827 | 15289 | 1734294 | 2020-02-09 09:08 | 2020-02-11 20:40 | 3572.3333 | 11kV | 1233516.6667 | 386 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN14891 WYONG section of 11kV Panel 20 RE50560 Hue Hue Sandra tripped on OC PT12681 LV OOS | February | 2020 | 2020Q3 | 2020 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 3195.639 | Y | 3 | N | Y | 1.1101 | 39.4971 | 901417.5974
[7 empty] | 5318 | 20011 | 1742326 | 2020-02-11 18:04 | 2020-02-11 21:07 | 183 | 11kV | 1098 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207549 A Phase DOLF : 5 Amp Excluded OMS 1742326 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-11 | N | 183 | N | 5 | N | N | 1.1101 | 39.4971 | 802.386
[7 empty] | 5307 | 19936 | 1734896 | 2020-02-09 11:10 | 2020-02-11 21:30 | 3500 | 11kV | 210450 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC21799 Oxford Brooker tripped on: OC Storm | February | 2020 | 2020Q3 | 2020 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Veg | 2020-02-09 | Y | 3188.6364 | Y | 3 | N | Y | 1.1101 | 39.4971 | 153790.6528
[7 empty] | 4748 | 14484 | 1742160 | 2020-02-09 09:37 | 2020-02-11 21:43 | 3606 | 11kV | 1545432 | 445 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12630 PEATS RIDGE section of 11kV Panel 1 tripped Abnormal: ZN14143 Somersby section of 11kv Panel 17 CP61925 closed CP45012 Open, CP45202 Open at time of trip Please see outage Zn12630:Pa1 @ 9/2/20 0937 Separate outage created for ZN14143 Somersby section of 11kv Panel 17 CP61925 to CP45012 to CP45202 as restored from ZN14143 Somersby Panel 17 Major Storm See 1756531,2,3,49,50,1,2,3,4,7,8 2nd 1756534,41,2,6,7,8 Ex 1733551,634,926,63,4480,9351,2,41029,2160 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 3472.8809 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1129356.1231
[7 empty] | 4896 | 15938 | 1734518 | 2020-02-09 09:58 | 2020-02-11 22:50 | 3652 | 11kV | 412424 | 230 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15013 Terrey Hills - Pnl.6 tripped on: O/C PT15908 - dist #1 - A, B 7& c phase fuses blown Mains down between LB26242 and LB48729 (HV & LV) See 1751371 1751372 1751373 1751375 1751376 | February | 2020 | 2020Q3 | 2020 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2020-02-09 | Y | 1793.1478 | Y | 3 | N | Y | 1.1101 | 39.4971 | 301387.2948
[7 empty] | 3791 | 4935 | 1742384 | 2020-02-11 18:42 | 2020-02-12 02:00 | 438 | 11kV | 23734 | 198 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207554 1 fault operation Sensitive Earth Fault sub 70709 damaged LAS Excluded oms 1742384 | February | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2020-02-11 | N | 119.8687 | N | 5 | N | N | 1.1101 | 39.4971 | 17344.1072
[7 empty] | 3338 | 454 | 1733981 | 2020-02-09 14:34 | 2020-02-12 02:35 | 3601 | 11kV | 3228158 | 1378 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.44 tripped on A & C phase O/C Abnormal: S46651 Sw/A closed with S66077 Sw/A Open. AB1019 Closed with S49943 Sw/A open HV UGOH beyond S4837 failed See 1757455 1757457 1757458 | February | 2020 | 2020Q3 | 2020 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | Unknown | Unknown | 2020-02-09 | Y | 2342.6401 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2359042.6519
[7 empty] | 5069 | 17969 | 1742552 | 2020-02-11 21:16 | 2020-02-12 03:03 | 347 | 11kV | 281070 | 810 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.17 tripped on B & C phase IOC Abnormal: LB61274 Closed with S65545 Sw/A open Bat across B & C phase | February | 2020 | 2020Q3 | 2020 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2020-02-11 | N | 347 | N | 5 | N | N | 1.1101 | 39.4971 | 205397.6658
[7 empty] | 3749 | 4473 | 1742448 | 2020-02-11 19:58 | 2020-02-12 06:00 | 602 | 11kV | 10836 | 18 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 207556 3 phase DOLF : 16 Amp faulty xarm pole 3J-90169 Excluded oms 1742448 | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-02-11 | N | 602 | Y | 5 | N | Y | 1.1101 | 39.4971 | 7918.6292
[7 empty] | 3953 | 6468 | 1734030 | 2020-02-09 07:20 | 2020-02-12 11:01 | 4541 | 11kV | 2973470 | 753 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12570 AVOCA section of 11kV Panel 33 IR50407 The Scenic Bounty tripped on Lock Out, OC trip, SEF Trip, EFI Fault between LB50717 & LB50716 See 1750513 2nd 1750515,20,2 Ex 1734030,7901,8888,50446,88,9 | February | 2020 | 2020Q3 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 3948.8313 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2172924.1735
[7 empty] | 3742 | 4414 | 1738547 | 2020-02-09 23:27 | 2020-02-12 12:00 | 3633 | 11kV | 773771 | 213 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | Y | Sectio of Pnl.11 Berowra - AB2423 opened for emergency pole replacement. Pole shared used between Ausgrid and Sydney Trains fell during storm into rail corridor. See 1753747 1753749 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 3632.7277 | Y | 3 | N | Y | 1.1101 | 39.4971 | 565449.0244
[7 empty] | 4830 | 15323 | 1741487 | 2020-02-11 09:39 | 2020-02-12 12:00 | 1581 | 11kV | 207111 | 131 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | At ZN9035 - Panel 4 - 11kV Bond burnt off @ CP35376 Supply restored at 1200 on 12/02/2020 (Confirmed on DNMS trends) See OMS 1750007 1741487 | February | 2020 | 2020Q3 | 2020 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | OH | Not Veg | 2020-02-11 | N | 1581 | Y | 5 | N | Y | 1.1101 | 39.4971 | 151350.6101
[7 empty] | 4746 | 14465 | 1734216 | 2020-02-09 08:37 | 2020-02-12 12:50 | 4573 | 11kV | 276888 | 131 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC21350 Booralie Kulgoa - tripped on Earth Fault @ 08:57, 12:06 & 2030 (9/2) Tree on 11kV mains - HV & LV down on Booralie Rd between AB26216 and AB26217 See 1751960 17518959 1751958 1751948 | February | 2020 | 2020Q3 | 2020 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2020-02-09 | Y | 2113.6489 | Y | 3 | N | Y | 1.1101 | 39.4971 | 202341.5836
[7 empty] | 4813 | 15166 | 1734249 | 2020-02-09 08:51 | 2020-02-12 15:17 | 4706 | 11kV | 1255826 | 1009 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn1610 Homebush Bay - Pnl.29 tripped on: Earth Fault Flooding and no access to S63482 Hill Half No.3. Suspect UG cable fault between Pnl.21, S63482 and S4800 | February | 2020 | 2020Q3 | 2020 | ZN1610:PA29 | ZN1610:PA29 | ZN01610/000029 | PARRAMATTA | UG | Not Veg | 2020-02-09 | Y | 1244.6244 | N | 3 | N | Y | 1.1101 | 39.4971 | 917720.6002
[7 empty] | 3833 | 5382 | 1734148 | 2020-02-09 10:09 | 2020-02-12 16:05 | 4676 | 11kV | 1133482 | 323 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Peats Ridge Panel 10 relays: AB , OC Abnormal: LB62765 closed to LB4336(looks like a typo) Remarks: TREES FALLEN EVERYWHERE | February | 2020 | 2020Q3 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 3509.2322 | Y | 3 | N | Y | 1.1101 | 39.4971 | 828315.2135
[7 empty] | 5016 | 17397 | 1735556 | 2020-02-09 13:08 | 2020-02-12 18:00 | 4611.8167 | 11kV | 484240.75 | 105 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Wind Storm | Y | Pt 15857 is defective. It has failed test. Pt 15857 is in LV//. See DMA database. | February | 2020 | 2020Q3 | 2020 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Not Veg | 2020-02-09 | Y | 4611.8167 | Y | 3 | N | Y | 1.1101 | 39.4971 | 353868.8574
[7 empty] | 5126 | 18407 | 1740171 | 2020-02-09 10:32 | 2020-02-12 18:10 | 4778 | 11kV | 653974 | 2969 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn2835 Burwood - Pnl.15 tripped on: Fault check UG cable fault between S65173 Sw/B and S7907 Sw/A S2032 Underwood Pom - dist #4 - A, B & Cphase fuses previoulsy blown due to flooding. See 1746963 1746965 1746962 | February | 2020 | 2020Q3 | 2020 | ZN2835:PA15 | ZN2835:PA15 | ZN02835/000015 | STRATHFIELD | UG | Not Veg | 2020-02-09 | Y | 220.2674 | N | 3 | N | Y | 1.1101 | 39.4971 | 477904.9102
[7 empty] | 5135 | 18470 | 1735107 | 2020-02-09 11:52 | 2020-02-12 19:00 | 4748 | 11kV | 2946528 | 838 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills - Pnl33 tripped on Earth Fault Storm damage to mains between LB77215 and AB2830 See 1756575 1756576 1756577 | February | 2020 | 2020Q3 | 2020 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 3516.1432 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2153235.7545
[7 empty] | 4444 | 11434 | 1743510 | 2020-02-12 19:05 | 2020-02-12 19:15 | 10 | 11kV | 520 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 207565 stick on mains. interr to get it off Excluded oms 1743510 | February | 2020 | 2020Q3 | 2020 | 532:83295 | 532:83295 | ZN00532/083295 | MAITLAND | OH | Veg | 2020-02-12 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 380.0007
[7 empty] | 4759 | 14542 | 1734003 | 2020-02-09 07:06 | 2020-02-12 19:32 | 5066 | 11kV | 630963 | 158 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Rain Wind Storm | Y | Suspect by ION and customer comments that Rec 45071 tripped at 09/02/2020 07:06 Remarks on outage reports received suggests no abnormal switching, however this incident received no paperwork. | February | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | Unknown | Unknown | 2020-02-09 | Y | 3993.4367 | Y | 3 | N | Y | 1.1101 | 39.4971 | 461089.1501
[7 empty] | 3810 | 5118 | 1735925 | 2020-02-09 14:04 | 2020-02-12 20:45 | 4721 | 11kV | 387122 | 82 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | CP1617 Church St No.1 - A phase HV fuse operated, sub isolated Put up a low voltage spreader on LV mains going up the laneway & trimmed some trees near the low voltage mains. More tree trimming near 13 Lyndhurst Cres, Hunters Hill NSW 2110 as the trees in this backyard are too close to the mains . At present S1961 transformer is isolated, so all three distributors have no supply. We expect him to be able to restore supply at the sub to all 3 distributors. This will get supply back on to Hunters Hill Public School. Note: sub also affected by wider area sub-trans outage on the 9th refer to OMS 1735257 | February | 2020 | 2020Q3 | 2020 | ZN129:PA35 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Veg | 2020-02-09 | Y | 4721 | N | 3 | N | Y | 1.1101 | 39.4971 | 282897.3394
[7 empty] | 3544 | 2421 | 1743436 | 2020-02-12 17:14 | 2020-02-12 20:55 | 221 | 11kV | 221 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207567 B Phase DOLF : 10 Amp Excluded OMS 1743436 | February | 2020 | 2020Q3 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-02-12 | N | 221 | N | 3 | N | N | 1.1101 | 39.4971 | 161.5003
[7 empty] | 4919 | 16238 | 1739897 | 2020-02-10 01:00 | 2020-02-12 21:30 | 4110 | 11kV | 2495379 | 2454 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10999 Kogarah Panel 36 tripped Cause: Major Raiun wind storm See OMS 1754261 1754263 1754266 1754270 1754271 1754272 | February | 2020 | 2020Q3 | 2020 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | OH | Not Veg | 2020-02-10 | Y | 1016.8619 | N | 11 | N | Y | 1.1101 | 39.4971 | 1823549.372
[7 empty] | 5061 | 17925 | 1733725 | 2020-02-08 15:52 | 2020-02-12 23:25 | 6213 | 11kV | 6213 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Heavy | Y | S65412 Hilly Edwin No.2 - DOp opened Transformer switch to isolate TV board which suffered a flashover | February | 2020 | 2020Q3 | 2020 | ZN874:PA4 | ZN874:PA4 | ZN00874/000004 | CANADA BAY | UG | Not Veg | 2020-02-08 | Y | 6213 | N | 4 | N | Y | 1.1101 | 39.4971 | 4540.2771
[7 empty] | 4910 | 16072 | 1743644 | 2020-02-13 01:39 | 2020-02-13 03:15 | 96 | 11kV | 960 | 10 | HV | Arcing | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | Ex ZN14143 SOMERSBY section of 11kV Panel 17 'Somersby Falls' PT18484 PACIFIC ASHBROOKE 1.2 Roadside HDO fuse operated Cause: not ascertained. DOp reports PT shroud on Tx appears H/R. Region to investigate See 1756664 ex 1743644 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-02-13 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 3475 | 1747 | 1734177 | 2020-02-09 08:22 | 2020-02-13 08:30 | 5768 | 11kV | 314928 | 291 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14144 Wamberal - Pnl.5 tripped on A & B phase OC Storm See 1757554 1757556 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 1082.2268 | Y | 3 | N | Y | 1.1101 | 39.4971 | 230140.0936
[7 empty] | 3529 | 2281 | 1734845 | 2020-02-09 11:03 | 2020-02-13 09:25 | 5662 | 11kV | 1744742 | 896 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3154 St Ives - Pnl.12 tripped Abnormal: LB63181 Closed with iR63174 Open (DMA) Storm See 1752100 1752101 1752102 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Not Veg | 2020-02-09 | Y | 1947.2567 | N | 3 | N | Y | 1.1101 | 39.4971 | 1275005.9924
[7 empty] | 5254 | 19471 | 1735987 | 2020-02-09 14:12 | 2020-02-13 11:55 | 5623 | 11kV | 2779603 | 1368 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Beacon Hill Pnl.4 - REC21685 tripped 11kV mains down beyond S17079. HV into LV See 1750171 1750172 1750173 | February | 2020 | 2020Q3 | 2020 | ZN15011:PA4 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | OH | Not Veg | 2020-02-09 | Y | 2031.8735 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2031251.888
[7 empty] | 4636 | 13542 | 1736226 | 2020-02-09 23:50 | 2020-02-13 12:00 | 5050 | 11kV | 277750 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At PT48159 Waratah Cambrah Supply interrupted to remove tree and SW for customers at 10 Waratah Rd transferred to western side of LV Link at EN-17 & supply restored (13/2/20). SPOTTER BERTRAM REPORTS-OH MAINS CUT AWAY BY OTHERS. AREA TAPED OFF & MADE SAFE. NEUTRAL CONDUCTOR VERY LOW OVER INTERSECTION BUT BEING SUPPORTED BY SERVICE.URGENT EWP REQ'D TO CUT AWAY MAINS. OH MAINS APPEAR TO BE DE-ENERGISED | February | 2020 | 2020Q3 | 2020 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Veg | 2020-02-09 | Y | 5050 | Y | 3 | N | Y | 1.1101 | 39.4971 | 202971.5078
[7 empty] | 3613 | 2902 | 1734526 | 2020-02-09 10:00 | 2020-02-13 12:45 | 5925 | 11kV | 794361 | 856 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35500 - Top ryde - Pnl.27 tripped on SEL HV & LV down + Tree on OH near UGOH near tee off to S4676 See 1756397 1756398 | February | 2020 | 2020Q3 | 2020 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Veg | 2020-02-09 | Y | 927.9918 | N | 3 | N | Y | 1.1101 | 39.4971 | 580495.5891
[7 empty] | 4488 | 11882 | 1734539 | 2020-02-09 09:50 | 2020-02-13 12:48 | 5938 | 11kV | 378644 | 98 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC44607 Matcham North - tripped on OC Storm damage beyond LK41490 See 1757535 1757536 | February | 2020 | 2020Q3 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 3863.7143 | Y | 3 | N | Y | 1.1101 | 39.4971 | 276701.8671
[7 empty] | 3630 | 3133 | 1744258 | 2020-02-13 13:19 | 2020-02-13 13:27 | 8 | 11kV | 5936 | 742 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Zn3500 Top Ryde - Pnl.27 tripped on: SEF 11kV air break switch flicker blade welded on (AB1901) | February | 2020 | 2020Q3 | 2020 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Not Veg | 2020-02-13 | N | 8 | N | 5 | N | N | 1.1101 | 39.4971 | 4337.8537
[7 empty] | 4349 | 10587 | 1735255 | 2020-02-09 12:20 | 2020-02-13 14:00 | 5860 | 11kV | 416000 | 83 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Zn3154 St Ives - Pnl.19 - Section of 11kV feeder between LB1831 to S484 tee pT49602 & PT1401 isolated for removal of trees from HV & LV mains See 1752075 1752076 1752077 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2020-02-09 | Y | 5012.0482 | N | 3 | N | Y | 1.1101 | 39.4971 | 304000.5301
[7 empty] | 4965 | 16776 | 1734057 | 2020-02-09 07:14 | 2020-02-13 14:03 | 6169 | 11kV | 7654752 | 2052 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Umina Panel 13 Relays: A + C phase O/C, EFI + lockout relay Remarks: storm Abnormal: No | February | 2020 | 2020Q3 | 2020 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 3730.386 | Y | 3 | N | Y | 1.1101 | 39.4971 | 5593866.9846
[7 empty] | 4499 | 12073 | 1744240 | 2020-02-13 12:59 | 2020-02-13 14:50 | 111 | 11kV | 111 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207578 Single phase DOLG : 10 Amp Excluded OMS 1744240 | February | 2020 | 2020Q3 | 2020 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2020-02-13 | N | 111 | N | 5 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 4362 | 10719 | 1733224 | 2020-02-07 15:34 | 2020-02-13 14:56 | 8602 | 11kV | 786680 | 576 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex ZN12690 BERKELEY VALE section of 11kV Panel 26 IR50096 Tonkiss Pacific tripped Abnormal: LB40053 closed; beyond LB77831 open bonds; IR50096 SCADA defect at time of outage. No access due to Bridge Flooded & flooding in area. Flooding receding slightly. Patrol required, unable to patrol due to floodwater. Major Storm See 1753215,7,8,20,1,2 2nd 1753219,23,4,5 Ex 1733224,371,2,3,4,922,43944 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2020-02-07 | N | 1365.7639 | N | 14 | N | N | 1.1101 | 39.4971 | 574882.5409
[7 empty] | 4786 | 14850 | 1744420 | 2020-02-13 15:06 | 2020-02-13 16:39 | 93 | 11kV | 69146 | 790 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | AT ZN9118 Cronulla Panel 2 triipped on Earth fault, EFI, C phase OC, Timing and Lockout Cause:UG cable fault See OMS 1750105 1744420 | February | 2020 | 2020Q3 | 2020 | ZN9118:PA2 | ZN9118:PA2 | ZN09118/000002 | SUTHERLAND | UG | Not Veg | 2020-02-13 | N | 87.5266 | N | 5 | N | N | 1.1101 | 39.4971 | 50529.8573
[7 empty] | 4155 | 8836 | 1735592 | 2020-02-09 14:29 | 2020-02-13 17:30 | 5941 | 11kV | 1909402 | 1024 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills - Pnl.43 tripped on B & C phase O/C PT2073 LV isolated S4492 - Dist #2 - Isolated Storm damage. Mains down See 1756523 1756524 1756525 1756529 1756530 | February | 2020 | 2020Q3 | 2020 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 1864.6504 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1395334.6638
[7 empty] | 4870 | 15714 | 1734206 | 2020-02-09 08:39 | 2020-02-13 17:30 | 6291 | 11kV | 509571 | 81 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S10345 Watkin Frederick 400A fuse blown on A B and C phase of distributor 1 Cause: Major Rain Wind storm See OMS 1734270 1734206 1742674 | February | 2020 | 2020Q3 | 2020 | ZN10999:PA29 | ZN10999:PA29 | ZN10999/000029 | BAYSIDE | OH | Not Veg | 2020-02-09 | Y | 6291 | Y | 3 | N | Y | 1.1101 | 39.4971 | 372379.457
[7 empty] | 3635 | 3205 | 1734467 | 2020-02-09 15:35 | 2020-02-13 17:31 | 5876 | 11kV | 1699564 | 1326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | ZN14143 SOMERSBY 11kV CB Panel 12 'Philips Gindurra' tripped Relays: A&B Phase OVercurrent EFI's down to S18495Swb Major Storm. Its raining sideways Cause: Tree on 11kv between AB445274 to LB44475. LB45416 closed See 1756482,3,4,5,6,7 Ex 1734467,9329,30,1,41336 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1281.7225 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1241991.2425
[7 empty] | 4986 | 17005 | 1734387 | 2020-02-09 12:08 | 2020-02-13 17:45 | 6097 | 11kV | 1092262 | 468 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Recloser / Sectionaliser | Unplanned | Previous Storm | Y | WOY WOY Panel 10R Brisbane Water Lara IR49684 Relays: OC trip, lockout Remarks: near PT11221 One phase 11kv off insulator hanging close to LV. Not sure if contacted LV | February | 2020 | 2020Q3 | 2020 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 2333.8932 | Y | 3 | N | Y | 1.1101 | 39.4971 | 798192.8533
[7 empty] | 4254 | 9832 | 1744524 | 2020-02-13 17:05 | 2020-02-13 20:30 | 205 | 11kV | 1230 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 207582 broken tapping at AL-10021 Excluded oms 1744524. | February | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-02-13 | N | 205 | N | 5 | N | N | 1.1101 | 39.4971 | 898.8477
[7 empty] | 3767 | 4763 | 1734090 | 2020-02-09 12:51 | 2020-02-13 21:15 | 6264 | 11kV | 1012922 | 1603 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12570 AVOCA 11kV CB Panel 22 tripped on Relays: EFI, B+C Overload, E/fault, Reclose/Timer 6 Bays LV Down between S18419 figrtree Boor Boora & AB40388. AP left Ausgrid authorised person @ 2200 3 Bays LV Down beyond LK41557 See 1750286,9,90 2nd 1750292,8 Exclude 1734090,9260,354,514,44357,551,4 | February | 2020 | 2020Q3 | 2020 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 631.8915 | Y | 3 | N | Y | 1.1101 | 39.4971 | 740213.5215
[7 empty] | 4015 | 7170 | 1737040 | 2020-02-09 16:29 | 2020-02-13 21:45 | 6076 | 11kV | 1643208 | 1013 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN10994 Mortdale - Panel 1 tripped on B and C phase IOC IOC and EF trip Reclose Lockout relays EFI Cause: Branch on OH mainns - PT10126 removed See OMS 1751208 1751210 1751211 1737040 1739023 1739073 1740987 | February | 2020 | 2020Q3 | 2020 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | OH | Veg | 2020-02-09 | Y | 1622.1204 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1200807.94
[7 empty] | 3663 | 3554 | 1742824 | 2020-02-12 08:42 | 2020-02-13 21:45 | 2223 | 11kV | 6669 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Wind Storm | N | S62215 Muir Dasea No.2 - RMCB tripped with no indication Water in relay | February | 2020 | 2020Q3 | 2020 | ZN35900:PA22 | ZN35900:PA10 | ZN35900/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-02-12 | N | 2223 | N | 3 | N | N | 1.1101 | 39.4971 | 4873.5085
[7 empty] | 4116 | 8342 | 1734784 | 2020-02-09 10:50 | 2020-02-13 21:50 | 6420 | 11kV | 2810084 | 808 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3154 St ives - Pnl.22 tripped on; C phase IOC S5538 - Dist #2 - A, B & C phase fuses blown Storm See 1752832 1752835 1752837 1752838 1752839 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Not Veg | 2020-02-09 | Y | 3477.8267 | N | 3 | N | Y | 1.1101 | 39.4971 | 2053526.5038
[7 empty] | 5180 | 18801 | 1738651 | 2020-02-09 19:45 | 2020-02-13 23:00 | 5955 | 11kV | 143536 | 157 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Wind Storm | Y | Zn262 Marrickville - Pnl.28 tripped on: O/C Abnormal: S8880 Sw/A to phased or proven after fault S4653 flooded, Sw/A endbox blew up. Unable to restore S7775 & S8880 due to abnormal. While waiting for restoration of S7775 & S8880... Tx 3A (Pnl.36) was incorrectly opened by DOp during switching to return 91X feeder to service. This interrupted the back (blue ) bar at Marrickville See 1747061 1747062 1747064 - SE 1747063 | February | 2020 | 2020Q3 | 2020 | ZN262:PA28 | ZN262:PA28 | ZN00262/000028 | INNER WEST | UG | Not Veg | 2020-02-09 | Y | 914.242 | N | 3 | N | Y | 1.1101 | 39.4971 | 104891.8752
[7 empty] | 3916 | 6089 | 1744684 | 2020-02-14 03:38 | 2020-02-14 04:28 | 50 | 11kV | 46964 | 1210 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn128 Hunters Hill - Pnl38 tripped on A & B phase O.C UG cable fault between S49203 Sw/B and S7579 Sw/A See 1756666 1756667 | February | 2020 | 2020Q3 | 2020 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | UG | Not Veg | 2020-02-14 | N | 38.8132 | N | 7 | N | N | 1.1101 | 39.4971 | 34319.906
[7 empty] | 4306 | 10280 | 1735584 | 2020-02-09 05:07 | 2020-02-14 07:44 | 7357 | 11kV | 1913343 | 368 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Section of Panel 8 suspected of tripping (Combined events below) - 11kv rec 44995 Kulnura tripped and reclosed to lockout. Section of 11kv feeder Panel No.8 "Kulnura" Ex ZN:12630 Peats Ridge Relays: IOC trip, O/C trip - Rec63734 George Downes Blood Relays: OC trip, lockout, Aux supply Remarks: not patrolled -Rec44994 Mangrove Creek Relays: lockout, OC, trip EF trip Remarks: not patrolled Rec49506 Springs Rd Relays: OC trip, lockout, | February | 2020 | 2020Q3 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 5199.3016 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1398214.6303
[7 empty] | 5018 | 17407 | 1734648 | 2020-02-09 10:16 | 2020-02-14 09:30 | 7154 | 11kV | 1394165 | 871 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12690 BERKELEY VALE 11kV CB Panel 12 tripped Relays: Earth Fault, EFI, Reclose, Timmer, Lock out Tx13 Group Earth, EFI, 26R See 1752259,63,6,7,9 Ex 1734648,9390,41767,8 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1600.6487 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1018814.6611
[7 empty] | 3877 | 5733 | 1756668 | 2020-02-14 05:24 | 2020-02-14 10:32 | 308 | 11kV | 195580 | 635 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Pnl.38 - Bond burnt off tee off to PT1170 Abnormal: S49386 Sw/B closed with S7579 Sw/A Open (DMA) | February | 2020 | 2020Q3 | 2020 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2020-02-14 | N | 308 | N | 7 | N | N | 1.1101 | 39.4971 | 142924.0954
[7 empty] | 3724 | 4177 | 1735018 | 2020-02-09 18:09 | 2020-02-14 11:00 | 6771 | 11kV | 1792302 | 297 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 13 IR62730 Manns Narara Creek tripped on Lock out, OC trip Not patrolled. Branch removed by DOP near PT11336 LB44907 11kV bond burnt off PT14318 REEVES MANN interrupted for safety. ROP checked. OK all fuses in service LB44907 to AB44366 tee PT12218 & PT14318 interrupted by DOp for safety In conjunction with PT18846 Dist 2 for repairs Tree Brought down OH See 1756724,5,6,7,8 Ex 1734039,6881,7426,42221,603,711,2,3,3413,5287 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 6034.6869 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1309761.4376
[7 empty] | 3942 | 6328 | 1734786 | 2020-02-09 12:31 | 2020-02-14 11:45 | 7154 | 11kV | 2767093 | 1132 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | Y | At S10994 Mortdale Panel 10 Tripped on A B and C pphase OC/ IOC, EF trip, Reclose and Lockout EFI Cause: Extensive Storm Damage Lorraine St Peakhurst 2 HV Poles snapped and on ground x arms snapped distributors down, 2 more HV poles cracked at base Note: HV into LV many premises to be checked for possible damage See OMS 1751295 1751296 1751298 1751299 1735323 1739439 1744679 | February | 2020 | 2020Q3 | 2020 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Not Veg | 2020-02-09 | Y | 2444.4284 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2022109.949
[7 empty] | 4146 | 8651 | 1734046 | 2020-02-09 11:20 | 2020-02-14 12:40 | 7280 | 11kV | 770288 | 862 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.18 - tripped on: Earth Fault Abnormal: AB227 Open with LB65298 Closed (DMA). CP2919 Closed with CP468 Open (DMA) HV & LV mains down during storm. See 1759936 1755937 1755938 1755935 1755934 1744814 | February | 2020 | 2020Q3 | 2020 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2020-02-09 | Y | 893.6056 | Y | 3 | N | Y | 1.1101 | 39.4971 | 562903.7508
[7 empty] | 5291 | 19763 | 1734053 | 2020-02-09 07:37 | 2020-02-14 13:05 | 7528 | 11kV | 1069953 | 1262 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn195 Pymble - Pnl.10 tripped on: Earth Fault & C Phase O/C Abnormal: S35422 Sw/B closed with S5985 Sw/A Open. S2542 Sw/B Closed with S4297 Sw/A Open Sealing ends failed at PT1260 S35144 - Dist #1 - B phase fuse blown - Tree on mains. See 1756429 1756430 1756431 1756432 1756433 | February | 2020 | 2020Q3 | 2020 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Not Veg | 2020-02-09 | Y | 847.8233 | N | 3 | N | Y | 1.1101 | 39.4971 | 781890.0941
[7 empty] | 4382 | 10852 | 1734795 | 2020-02-09 10:53 | 2020-02-14 13:15 | 7342 | 11kV | 1877530 | 1022 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | Y | At S10994 Mortdale Panel 21 tripped on A B and C phase OC, IOC,EF Trip, Reclose and Lockout relays: EFI Cause: Extensive strom damage in Lorraine Sr Peakurst. See OMS 1751261 1751263 1751264 1751265 1734795 1739471 1740887 1740888 1744691 | February | 2020 | 2020Q3 | 2020 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Not Veg | 2020-02-09 | Y | 1837.1135 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1372043.5462
[7 empty] | 3455 | 1556 | 1734572 | 2020-02-09 11:18 | 2020-02-14 14:35 | 7397 | 11kV | 3962675 | 1162 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn965 Pennant Hills - Pnl.17 tripped on: A Phase O.C Storm PT1685 - Dist #1 & #2 - A, B & C phase fuses blown See 1756569 1756570 1756571 1756572 1756573 | February | 2020 | 2020Q3 | 2020 | ZN965:PA17 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 3410.2194 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2895806.0109
[7 empty] | 4494 | 11971 | 1744999 | 2020-02-14 13:38 | 2020-02-14 15:46 | 128 | 11kV | 135948 | 1560 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn195 Pymble - Pnl.11 tripped on: A & B phase OC Abnormal: S35850 Sw/B Closed with S48366 Sw/A Open (DMA) UG cable fault between S5055 Sw/B, S4143 Sw/B and S35850 Sw/B See 1756494 1756495 1756496 | February | 2020 | 2020Q3 | 2020 | ZN1673:PA21 | ZN1673:PA21 | ZN01673/000021 | KU-RING-GAI | UG | Not Veg | 2020-02-14 | N | 87.1462 | N | 7 | N | N | 1.1101 | 39.4971 | 99346.7886
[7 empty] | 3385 | 843 | 1745079 | 2020-02-14 15:17 | 2020-02-14 16:50 | 93 | 11kV | 186 | 2 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.4 - LB65370 found open suspect by phanton operator | February | 2020 | 2020Q3 | 2020 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | SUTHERLAND | OH | Not Veg | 2020-02-14 | N | 93 | N | 7 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 4683 | 13949 | 1734766 | 2020-02-09 10:46 | 2020-02-14 17:25 | 7599 | 11kV | 610187 | 826 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35370 Galston - Pnl.10 - @1046 - REC50015 tripped @1312 - Pnl.10 tripped Storm. Trees on mains and mains down along feeder See 1754574 1754575 1754576 1754579 1754580 1754582 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2020-02-09 | Y | 738.7252 | Y | 3 | N | Y | 1.1101 | 39.4971 | 445906.6621
[7 empty] | 3880 | 5748 | 1753460 | 2020-02-13 19:18 | 2020-02-14 17:35 | 1337 | 11kV | 20055 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | PT12149 BERKELEY CORONA 0.4 Dist 1 'BERKELEY RD W' fuses failed due to OH wires down Ex ZN12690 BERKELEY VALE section of 11kV Panel 24 LB65389 to LB40032 tee PT64873, PT1249 interrupted due to emergency repairs to 11kv OH damage See 1753459 2nd 1753460 Ex 1735020,44811 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2020-02-13 | N | 1337 | Y | 5 | N | Y | 1.1101 | 39.4971 | 14655.6025
[7 empty] | 3826 | 5356 | 1734044 | 2020-02-09 11:14 | 2020-02-14 17:57 | 7603 | 11kV | 2231954 | 970 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 17R 'Fagans Bay' IR63069 Coolarn Wendy tripped on OC trip, Lockout Not patrolled, Tree/Branch on OH Mains. Wires Down Major Storm See 1756673,4 Ex 1734044,5583,41136 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 2300.9835 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1631046.1517
[7 empty] | 5084 | 18150 | 1734288 | 2020-02-09 10:00 | 2020-02-14 18:10 | 7690 | 11kV | 2278210 | 702 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | CP46116 tripped on OC trip + Lockout See OMS 1757132 1757133 1757135 Cause: Tree on OH mains @ S4666 See OMS 1757132 1757133 1757135OMS 1734288 1741703 | February | 2020 | 2020Q3 | 2020 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Veg | 2020-02-09 | Y | 3245.3134 | N | 3 | N | Y | 1.1101 | 39.4971 | 1664848.6722
[7 empty] | 5261 | 19535 | 1734876 | 2020-02-09 10:06 | 2020-02-14 18:20 | 7694 | 11kV | 1527677 | 373 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35370 Galston - Pnl.2 @10:55 - REC3280 tripped on: B phase O/C @11:06 - Pnl.2 tripped on: B Phase O/C PT1515 - Dist #1 - A, B & C phase fuses blown Tree on mains outside 411 Galston Rd & 427 Galston Rd See 1754507 1754508 1754510 1754505 1754511 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-02-09 | Y | 4095.6488 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1116381.2928
[7 empty] | 3982 | 6700 | 1735419 | 2020-02-09 12:46 | 2020-02-14 19:20 | 7594 | 11kV | 1511853 | 1718 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15004 Newport - pnl.1 tripped on: O/C Abnormal S50118 Sw/A Closed with SwB open S16755 - Dist #3 - A, b & C phase fuses blown Storm See 1751285 1751287 1751288 | February | 2020 | 2020Q3 | 2020 | ZN15004:PA1 | ZN15004:PA1 | ZN15004/000001 | NORTHERN BEACHES | OH | Not Veg | 2020-02-09 | Y | 880.0076 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1104817.5803
[7 empty] | 3745 | 4444 | 1745202 | 2020-02-14 19:15 | 2020-02-14 20:05 | 50 | 11kV | 50 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 207591 Fuse fatigue Single phase DOLF : 10 Amp Excluded OMS 1745202 | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-02-14 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 3511 | 2115 | 1745161 | 2020-02-14 17:34 | 2020-02-14 20:50 | 196 | 11kV | 39830 | 500 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 207588 3 fault operations Broken 11Kv underslung disc at pole JT-47007. repairs complete Excluded OMS 1745161 | February | 2020 | 2020Q3 | 2020 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2020-02-14 | N | 79.66 | N | 7 | N | N | 1.1101 | 39.4971 | 29106.5892
[7 empty] | 5112 | 18325 | 1745249 | 2020-02-14 22:10 | 2020-02-14 23:59 | 109 | 11kV | 91342 | 838 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills Pnl.33 tripped on Earth Fault UG cable fault between Pnl.33 and S4493, LB1022, S4613 | February | 2020 | 2020Q3 | 2020 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | UG | Not Veg | 2020-02-14 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 66750.0395
[7 empty] | 4686 | 13963 | 1733910 | 2020-02-08 23:10 | 2020-02-15 08:30 | 9200 | 11kV | 2523414 | 637 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35370 - Galston Pnl.4 tripped @ 2310 (8/2) & 1111 (9/2) Cause 1st trip: Tree brought down OH mains in Manfield Rd with HV into LV (PT1616 & PT2214 remained out of service) Cause 2nd Trip: Broken cross arm during storm at pole AR33209 LV interruptions @ PT658, PT1616 & PT61993 Abnormal: AB340 open DMA with LB62158 Closed See 1755261 1755263 1755264 1755266 1755268 1755269 1755270 1755271 1755272 1755273 1755274 1755275 1755278 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2020-02-08 | Y | 3961.4035 | N | 4 | N | Y | 1.1101 | 39.4971 | 1844036.5231
[7 empty] | 4093 | 8127 | 1736045 | 2020-02-09 14:17 | 2020-02-15 10:20 | 8403 | 11kV | 3886503 | 1137 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Lindfield Panel 27 Relays: OC + EF - efi, f/c, U/f, lockout relay, IOC, C phase, Group earth Tx4 Abnormal: LB244 closed, LB46265 open | February | 2020 | 2020Q3 | 2020 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2020-02-09 | Y | 3418.2084 | N | 3 | N | Y | 1.1101 | 39.4971 | 2840141.76
[7 empty] | 4536 | 12405 | 1734870 | 2020-02-09 11:07 | 2020-02-15 14:30 | 8843 | 11kV | 3332405 | 1386 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN36200 EMPIRE BAY 11kV CB Panel 8 tripped, reclosed and locked out Relays: EF trip, A&B Ph OCm OC trip EFI: not recorded Tree on 11kv mains between LB48657 to LB48645 tee PT13952, PT13455 PT14571 Stanly Owanda Dist 1 ABC phases fuses affected due to tree on LV Dist See 1753478,9 Ex 1734870,41262,3 | February | 2020 | 2020Q3 | 2020 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 2404.3326 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2435223.2847
[7 empty] | 5133 | 18452 | 1733963 | 2020-02-09 06:03 | 2020-02-15 14:32 | 9149 | 11kV | 1518734 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN14143 SOMERSBY section of 11kV Panel 17 'Wise Ferry Somersby 2.0 & etc' RE45012 Bar Point reclosed and tripped on Signals: Relays: E/Fault, Lockout Cause: tree/branch brought down HV OH Mains Major Storm See 1756531,2,3,49,50,1,2,3,4,7,8 2nd 1756534,41,2,6,7,8 Ex 1733551,634,926,63,4480,9351,2,41029,2160 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 9149 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1109846.0121
[7 empty] | 4626 | 13475 | 1745422 | 2020-02-15 12:40 | 2020-02-15 15:44 | 183.9833 | 11kV | 15270.6167 | 83 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Suspected storm damage/tree brought down mains | February | 2020 | 2020Q3 | 2020 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Not Veg | 2020-02-15 | N | 183.9833 | N | 3 | N | N | 1.1101 | 39.4971 | 11159.3163
[7 empty] | 4623 | 13466 | 1756711 | 2020-02-09 09:06 | 2020-02-15 16:23 | 9077 | 11kV | 2594401 | 351 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Section of Panel 1 beyond Rec45189 Remarks: LB40596 open, AB 43179 open(questionable as restoration step conflicts with this info) | February | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 7391.4558 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1895911.7289
[7 empty] | 3882 | 5763 | 1733702 | 2020-02-09 20:16 | 2020-02-15 16:30 | 8414 | 11kV | 1034922 | 123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Customer report NS. Multiple trees down on 11kv & 415V OH Mains CP41559 to CP40506 tee PT12614, PT11573 isolated due to tree on 11kv Mains See 1756706,7 Ex 1733702,9301,41011,124,56702 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 8414 | Y | 3 | N | Y | 1.1101 | 39.4971 | 756290.4726
[7 empty] | 3967 | 6618 | 1734255 | 2020-02-09 08:55 | 2020-02-15 17:00 | 9125 | 11kV | 3939172 | 965 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra - Pnl.26 tripped on A & C phase IOC PT1601 - Dist #2 - B phase fuse blown S50340 - Dist #4 -A, B & C phase fuses blown S72323 - Dist #4 & #2 - A, B & C phase fuses blown Storm. Trees brought down mains See 1753804 1753806 1753800 1753801 1753802 1753803 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2020-02-09 | Y | 4082.0435 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2878630.7117
[7 empty] | 4798 | 15011 | 1735139 | 2020-02-09 12:01 | 2020-02-15 17:51 | 8990 | 11kV | 1258600 | 140 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Berowra -pnl.13 interrupted from S6731 Sw/B after storm activity Note: PT1138 was also affected by OMS 1755639 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA13 | ZN2400:PA13 | ZN02400/000013 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 8990 | Y | 3 | N | Y | 1.1101 | 39.4971 | 919747.7576
[7 empty] | 3788 | 4912 | 1735034 | 2020-02-09 11:34 | 2020-02-15 18:00 | 9026 | 11kV | 151520 | 124 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | iR78712 - tripped on : OC Storm damage between LK44469 and AB44347 See 1757523 1757524 1757525 | February | 2020 | 2020Q3 | 2020 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 1221.9355 | Y | 3 | N | Y | 1.1101 | 39.4971 | 110726.3469
[7 empty] | 4047 | 7525 | 1734039 | 2020-02-09 07:23 | 2020-02-15 19:25 | 9362 | 11kV | 982472 | 949 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 13 IR62730 Manns Narara Creek tripped on Lock out, OC trip Not patrolled. Branch removed by DOP near PT11336 LB44907 11kV bond burnt off PT14318 REEVES MANN interrupted for safety. ROP checked. OK all fuses in service LB44907 to AB44366 tee PT12218 & PT14318 interrupted by DOp for safety In conjunction with PT18846 Dist 2 for repairs Tree Brought down OH See 1756724,5,6,7,8 Ex 1734039,6881,7426,42221,603,711,2,3,3413,5287 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1035.2708 | Y | 3 | N | Y | 1.1101 | 39.4971 | 717961.5596
[7 empty] | 4660 | 13728 | 1745287 | 2020-02-15 08:18 | 2020-02-15 19:25 | 667 | 11kV | 71369 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex ZN12650 WEST GOSFORD section of 11kV Panel 13 IR62730 Manns Narara Creek tripped on Lock out, OC trip Not patrolled. Branch removed by DOP near PT11336 LB44907 11kV bond burnt off PT14318 REEVES MANN interrupted for safety. ROP checked. OK all fuses in service LB44907 to AB44366 tee PT12218 & PT14318 interrupted by DOp for safety In conjunction with PT18846 Dist 2 for repairs Tree Brought down OH See 1756724,5,6,7,8 Ex 1734039,6881,7426,42221,603,711,2,3,3413,5287 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2020-02-15 | N | 667 | N | 3 | N | N | 1.1101 | 39.4971 | 52154.3602
[7 empty] | 3740 | 4377 | 1734732 | 2020-02-09 10:40 | 2020-02-15 19:30 | 9170 | 11kV | 2996402 | 1209 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3154 - St Ives - Pnl.4 tripped Storm S48465 - Dist #1 - Isolated to remove trees See 1752889 1752890 1752891 1752893 1752894 1752898 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA4 | ZN3154:PA4 | ZN03154/000004 | KU-RING-GAI | OH | Not Veg | 2020-02-09 | Y | 2478.4136 | N | 3 | N | Y | 1.1101 | 39.4971 | 2189682.2027
[7 empty] | 4763 | 14639 | 1734113 | 2020-02-09 07:59 | 2020-02-15 21:05 | 9426 | 11kV | 2127074 | 524 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 6 'SCC Racecourse' RE44824 Wyoming tripped on OC trip, Lockout, Aux Supply, IOC Trip Tree/Branch on OH Mains AB41629 to AB41674 tee PT14102 damaged due to tree/branch. Also PT13728 Dist 1 damaged due to tree/branch Major Storm See 1756693,7,8,9 Ex 1734113,42146,5566 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 4059.3015 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1554402.9411
[7 empty] | 5165 | 18704 | 1733972 | 2020-02-09 06:40 | 2020-02-15 21:28 | 9528 | 11kV | 881111 | 1524 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra - Pnl.21 tripped on A & C phase O.C PT1165 - Dist #2 - A, B & Cphase fuses blown - Storm damage Tree branch on mains near LB1803 See 1754370 1754372 1754373 1754374 1754377 1754379 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2020-02-09 | Y | 578.1568 | Y | 3 | N | Y | 1.1101 | 39.4971 | 643889.9304
[7 empty] | 3523 | 2232 | 1745601 | 2020-02-15 19:38 | 2020-02-15 22:35 | 177 | 11kV | 177 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 207613 Single phase DOLF : 10 Amp Replace 11kV L/A Excluded OMS 1745601 | February | 2020 | 2020Q3 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2020-02-15 | N | 177 | N | 3 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 3601 | 2794 | 1734317 | 2020-02-09 09:06 | 2020-02-16 03:20 | 9734 | 11kV | 502444 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Section of Panel 13 restoration Section of 11kv feeder beyond Rec46763 | February | 2020 | 2020Q3 | 2020 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 8662.8276 | Y | 3 | N | Y | 1.1101 | 39.4971 | 367171.2556
[7 empty] | 4141 | 8629 | 1745687 | 2020-02-16 01:51 | 2020-02-16 03:30 | 99 | 11kV | 1782 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207617 A Phase DOLF : 10 Amp Also replaced damaged DOLF carrier Excluded OMS 1745687 | February | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-02-16 | N | 99 | N | 8 | N | N | 1.1101 | 39.4971 | 1302.233
[7 empty] | 3864 | 5628 | 1745741 | 2020-02-16 06:28 | 2020-02-16 07:40 | 72 | 11kV | 864 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207618 A Phase DOLF : 10 Amp branches removed from mains 10 amp A ph HVF replaced power restored 0740. Excluded OMS 1745741 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-16 | N | 72 | N | 8 | N | N | 1.1101 | 39.4971 | 631.3857
[7 empty] | 4857 | 15575 | 1745719 | 2020-02-16 04:21 | 2020-02-16 08:25 | 244 | 11kV | 1464 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207619 B Phase DOLF : 31 Amp B ph 31.5 spur fuse replaced power restored . Excluded OMS 1745719 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-16 | N | 244 | N | 8 | N | N | 1.1101 | 39.4971 | 1069.848
[7 empty] | 4370 | 10767 | 1745754 | 2020-02-16 07:42 | 2020-02-16 10:40 | 178 | 11kV | 534 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207620 C Phase DOLF : 10 Amp replaced C ph 10 amp HVF power restored 1040 Excluded OMS 1745754 | February | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-02-16 | N | 178 | N | 8 | N | N | 1.1101 | 39.4971 | 390.2314
[7 empty] | 4544 | 12493 | 1745786 | 2020-02-16 08:59 | 2020-02-16 11:05 | 126 | 11kV | 252 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207621 Single phase DOLF : 10 Amp Excluded OMS 1745786 | February | 2020 | 2020Q3 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-02-16 | N | 126 | N | 8 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 4498 | 12054 | 1734353 | 2020-02-09 09:15 | 2020-02-16 12:25 | 10270 | 11kV | 3181671 | 1413 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl22 tripped on C phase O/C Abnormal: LB65298 Closed with AB277 Open LV interruptions at PT1742 & S5600 Storm See 1755672 1755675 1755671 1755670 | February | 2020 | 2020Q3 | 2020 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 2251.7134 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2325071.3234
[7 empty] | 4589 | 13068 | 1745838 | 2020-02-16 10:25 | 2020-02-16 12:30 | 125 | 11kV | 375 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207622 3 phase DOLF : 10 Amp replaced B & C PH hvf and A ph lvf. 2 dead birds found at sub. Excluded oms 1745838 | February | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-02-16 | N | 125 | N | 8 | N | N | 1.1101 | 39.4971 | 274.0389
[7 empty] | 4100 | 8194 | 1744460 | 2020-02-12 14:13 | 2020-02-16 12:55 | 5681.6333 | 11kV | 34089.8 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | At 12660 Woy Woy Zn section of p14 from Cp45093 Remarks: Oh down. Deso advised 1 phase PT13935 only 140v adviced from customer. Aop Manoukian opened Rec 45093. Possible 11kv on ground. (Confirmed 11kv on ground) Dop Dabovic | February | 2020 | 2020Q3 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2020-02-12 | N | 5681.6333 | Y | 3 | N | Y | 1.1101 | 39.4971 | 24911.8204
[7 empty] | 5053 | 17839 | 1734318 | 2020-02-09 09:10 | 2020-02-16 13:30 | 10340 | 11kV | 2310096 | 878 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.47 tripped Abnormal: AB2919 Closed with AB1474 Open, LB160 Closed with LB3358 Open (DMA) LV Interruptions at S4843 7 S4485 Storm See 1755638 1755639 1755636 1755637 | February | 2020 | 2020Q3 | 2020 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Veg | 2020-02-09 | Y | 2631.0888 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1688150.0205
[7 empty] | 4904 | 15991 | 1734488 | 2020-02-09 09:50 | 2020-02-16 13:45 | 10315 | 11kV | 9594604 | 4852 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12600 LISAROW 11kV CB Panel 3 'Lisarow High Taylor' tripped Tree brought down HV & LV beyond CP41622 Major Storm See 1756113,20,2,3,5,8 2nd 1756114,5,6,7,8 Ex 1734488,670,757,5684,6793,9294,5,40224,461,1005,311,92,407,36 | February | 2020 | 2020Q3 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 1977.4534 | Y | 3 | N | Y | 1.1101 | 39.4971 | 7011453.6103
[7 empty] | 4114 | 8328 | 1734390 | 2020-02-09 05:00 | 2020-02-16 15:05 | 10685 | 11kV | 1077039 | 212 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Rec45035 Mangrove Mountain, 46935 Ironbark Kirks 0.8 Relays: EF trip, lockout Remarks: not patrolled, but multiple damage reported from the field. 11kV on the ground at PT12523. Moved from over the road with operator stick and area taped off. Damage to cross arm, fuse holder & insulators at PT and 3 bays of LV 7/2-8.0 down between pole KE26-KE32, pulled fuses at pt18734 and pulled pararel 35874 as per control room instructions to make safe | February | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 5080.3726 | Y | 3 | N | Y | 1.1101 | 39.4971 | 787068.3339
[7 empty] | 5289 | 19756 | 1734060 | 2020-02-09 07:40 | 2020-02-16 15:55 | 10575 | 11kV | 222075 | 21 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12580 ERINA section of 11kV Panel 12 CP42282 isolated for safety Tree on 11kv CTW & AP issued to lineworker See 1755315 ex 1744546 | February | 2020 | 2020Q3 | 2020 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 10575 | Y | 3 | N | Y | 1.1101 | 39.4971 | 162285.8599
[7 empty] | 3622 | 3037 | 1734504 | 2020-02-09 09:51 | 2020-02-16 17:00 | 10509 | 11kV | 1806230 | 180 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC3281 Bay Cooper - Tripped Storm See 1755295 1755297 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2020-02-09 | Y | 10034.6111 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1319939.6092
[7 empty] | 5027 | 17514 | 1734066 | 2020-02-09 07:42 | 2020-02-16 17:40 | 10678 | 11kV | 2865884 | 718 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn14891 - Wyong - Pnl.12 tripped Storm damage along feeder and LV See 1757484 486 487 488 489 493 497 498 499 500 501 504 507 508 510 | February | 2020 | 2020Q3 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2020-02-09 | Y | 3991.4819 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2094303.4979
[7 empty] | 4004 | 7059 | 1742440 | 2020-02-09 12:55 | 2020-02-16 18:39 | 10424.2833 | 11kV | 221759.9667 | 31 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | S48016 - dist #2 - A, B & C phase fuses blown Storm Section of Dist#2 is still interrupted. There is a boken pole in Otaki Pl, approx. 12 residences affected. Assigned to Hung Chau for Spotting | February | 2020 | 2020Q3 | 2020 | ZN3154:PA4 | ZN3154:PA4 | ZN03154/000004 | KU-RING-GAI | OH | Veg | 2020-02-09 | Y | 7153.5473 | N | 3 | N | Y | 1.1101 | 39.4971 | 162055.6428
[7 empty] | 4424 | 11267 | 1733967 | 2020-02-09 06:31 | 2020-02-16 19:20 | 10849 | 11kV | 1406086 | 242 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | @ZN12630 Peats Ridge 11kv Panel 11 "somersby" reclosed and tripped on Section of 11kv feeder from AB40754 to LK42943 tee PT12219, tee PT18875, tee PT12239, tee PT13539, tee PT14436, Ex ZN12630 Peats Ridge, Panel 11 'Central Mangrove' Remarks: tree/branch on OH mains. Tree on 11kv mains | February | 2020 | 2020Q3 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 5810.2727 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1027526.1763
[7 empty] | 3541 | 2399 | 1745870 | 2020-02-16 12:46 | 2020-02-16 19:30 | 404 | 11kV | 79992 | 198 | HV | Staff Operation | Utility Process Issue | O/H Link | Unplanned | Previous Storm | N | Panel 32 @ LB1733 Remarks: interrupted by dops Restored Tx's at PT1854 & S6984 | February | 2020 | 2020Q3 | 2020 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Not Veg | 2020-02-16 | N | 404 | N | 8 | N | N | 1.1101 | 39.4971 | 58455.7942
[7 empty] | 4982 | 16982 | 1735846 | 2020-02-09 13:54 | 2020-02-16 20:00 | 10446.3667 | 11kV | 616335.6333 | 59 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | Y | PT1893 Dist No.2 Phase: ABC Fuse: 400A Spotter Comments:" 150 abc needs replacing for 2 bays Lv TERMO xarm needed on 59505 Everything cutaway Services to houses 22,3,1 need replacing " | February | 2020 | 2020Q3 | 2020 | ZN1193:PA10 | ZN1193:PA10 | ZN01193/000010 | KU-RING-GAI | OH | Not Veg | 2020-02-09 | Y | 10446.3667 | N | 3 | N | Y | 1.1101 | 39.4971 | 450399.902
[7 empty] | 5007 | 17280 | 1734052 | 2020-02-09 07:01 | 2020-02-16 22:25 | 11004 | 11kV | 3390983 | 915 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | @ 0701- REC559 Tripped @1238- REC554 Tripped @1303- REC705 Tripped @1303- Pnl.8 Galston Tripped LV interruptions @ PT1598, PT2144, PT787, PT2112, PT1967, PT1135, PT627 Major storm damage along feeder See 1755154 1755155 1755157 1755159 1755160 1755161 1755162 1755163 1755165 1755166 1755167 1755168 1755169 1755170 1755173 1755176 1755177 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2020-02-09 | Y | 3705.9923 | Y | 3 | N | Y | 1.1101 | 39.4971 | 2478030.3593
[7 empty] | 4681 | 13933 | 1746067 | 2020-02-16 19:52 | 2020-02-16 22:55 | 183 | 11kV | 2562 | 14 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 207633 A Phase DOLF : 10 Amp Replace complete DOLF wedge as old wedge broken. Excluded OMS 1746067 | February | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2020-02-16 | N | 183 | N | 8 | N | N | 1.1101 | 39.4971 | 1872.234
[7 empty] | 4226 | 9523 | 1746114 | 2020-02-17 06:49 | 2020-02-17 09:20 | 151 | 11kV | 1510 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207649 Single phase DOLF : 10 Amp Excluded OMS 1746114 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 151 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1103.4635
[7 empty] | 4729 | 14358 | 1746916 | 2020-02-17 08:48 | 2020-02-17 09:35 | 47 | 11kV | 188 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207660 Single phase DOLF : 10 Amp | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 47 | N | 32 | Y | Y | 1.1101 | 39.4971 | 137.3849
[7 empty] | 3298 | 118 | 1746120 | 2020-02-17 07:13 | 2020-02-17 11:35 | 262 | 11kV | 9292 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207643 1 Fault Operation Earth Fault Excluded OMS 1746120 | February | 2020 | 2020Q3 | 2020 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2020-02-17 | N | 232.3 | N | 32 | Y | Y | 1.1101 | 39.4971 | 6790.3195
[7 empty] | 4049 | 7554 | 1746240 | 2020-02-17 10:14 | 2020-02-17 11:50 | 96 | 11kV | 192 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207685 B & C Phase DOLF : 10 Amp Excluded OMS 1746240 | February | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 96 | N | 32 | Y | Y | 1.1101 | 39.4971 | 140.3079
[7 empty] | 4442 | 11419 | 1751900 | 2020-02-17 09:00 | 2020-02-17 12:00 | 180 | 11kV | 6120 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207678 A & B phase DOLF : 20 Amp Sub 72700 2x 10A DOLFs also replaced | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-02-17 | N | 180 | N | 32 | Y | Y | 1.1101 | 39.4971 | 4472.3155
[7 empty] | 3696 | 3889 | 1746276 | 2020-02-17 10:57 | 2020-02-17 13:00 | 123 | 11kV | 246 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207692 Single phase DOLF : 10 Amp Excluded OMS 1746276 | February | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 123 | N | 32 | Y | Y | 1.1101 | 39.4971 | 179.7695
[7 empty] | 4724 | 14319 | 1746329 | 2020-02-17 11:47 | 2020-02-17 13:10 | 83 | 11kV | 83 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207694 Single phase DOLF : 10 Amp Excluded OMS 1746329 | February | 2020 | 2020Q3 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2020-02-17 | N | 83 | N | 32 | Y | Y | 1.1101 | 39.4971 | 60.654
[7 empty] | 4410 | 11161 | 1748268 | 2020-02-17 09:59 | 2020-02-17 13:20 | 201 | 11kV | 1206 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207707 Single phase DOLF : 5 Amp Excluded OMS 1746225 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-17 | N | 201 | N | 32 | Y | Y | 1.1101 | 39.4971 | 881.3092
[7 empty] | 3623 | 3040 | 1746695 | 2020-02-17 11:10 | 2020-02-17 13:31 | 141 | 11kV | 153266 | 1338 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207683 2 fault operations Overcurrent nothing found 33kV feeder 80255 T&R at the same time see Lid 207684 Excluded oms 1746291 | February | 2020 | 2020Q3 | 2020 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Veg | 2020-02-17 | N | 114.5486 | N | 32 | Y | Y | 1.1101 | 39.4971 | 112002.2722
[7 empty] | 4394 | 11001 | 1746251 | 2020-02-17 10:27 | 2020-02-17 13:35 | 188 | 11kV | 3760 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207711 Single phase DOLF : 20 Amp Excluded OMS 1746251 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 188 | N | 32 | Y | Y | 1.1101 | 39.4971 | 2747.6971
[7 empty] | 4546 | 12519 | 1748926 | 2020-02-17 07:14 | 2020-02-17 13:38 | 384 | 11kV | 2304 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207713 Single phase DOLF : 20 Amp | February | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-02-17 | N | 384 | N | 32 | Y | Y | 1.1101 | 39.4971 | 1683.6952
[7 empty] | 5139 | 18502 | 1746342 | 2020-02-17 11:57 | 2020-02-17 13:50 | 113 | 11kV | 452 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207687 A Phase DOLF : 10 Amp excluded OMS 1746342 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-02-17 | N | 113 | N | 32 | Y | Y | 1.1101 | 39.4971 | 330.3083
[7 empty] | 4147 | 8656 | 1746124 | 2020-02-17 07:34 | 2020-02-17 13:56 | 382 | 11kV | 187848 | 649 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 207645 11kV on ground between poles AI-90039 & AI-90042 Possible high into Low J Byfield advised possible high to low A Regan arranging service checks prior to re energising. Excluded OMS 1746124 | February | 2020 | 2020Q3 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2020-02-17 | N | 289.4422 | N | 32 | Y | Y | 1.1101 | 39.4971 | 137273.7778
[7 empty] | 5207 | 19046 | 1746225 | 2020-02-17 09:49 | 2020-02-17 14:53 | 304 | 11kV | 5168 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207699 Line DOLF Single phase DOLF : 5 Amp Excluded OMS 1746225 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-17 | N | 304 | N | 32 | Y | Y | 1.1101 | 39.4971 | 3776.622
[7 empty] | 3808 | 5101 | 1746458 | 2020-02-17 14:23 | 2020-02-17 15:13 | 50 | 11kV | 28574 | 649 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207700 1 fault operation Overcurrent autom reclose lockout alarm not reset from prev fdr trip[ | February | 2020 | 2020Q3 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 44.0277 | N | 32 | Y | Y | 1.1101 | 39.4971 | 20881.0364
[7 empty] | 3329 | 371 | 1746345 | 2020-02-17 11:58 | 2020-02-17 15:45 | 227 | 11kV | 5211.6667 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Pnl.2 Galston - LB77358 to LB 1548 interrupted to remove tree from mains See 1746345 1746346 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-02-17 | N | 226.5942 | N | 32 | Y | Y | 1.1101 | 39.4971 | 3808.5323
[7 empty] | 4914 | 16149 | 1746383 | 2020-02-17 12:53 | 2020-02-17 15:47 | 174 | 11kV | 348 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207714 C Phase DOLF : 10 Amp Excluded OMS 1746383 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-02-17 | N | 174 | N | 32 | Y | Y | 1.1101 | 39.4971 | 254.3081
[7 empty] | 3999 | 6975 | 1746388 | 2020-02-17 13:01 | 2020-02-17 16:05 | 184 | 11kV | 920 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207717 C Phase DOLF : 10 Amp Excluded OMS 1746388 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-02-17 | N | 184 | N | 32 | Y | Y | 1.1101 | 39.4971 | 672.3089
[7 empty] | 4390 | 10945 | 1734438 | 2020-02-09 09:19 | 2020-02-17 16:15 | 11936 | 11kV | 586495 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC1238 tripped on: SEF LB64398 isolated fror repairs Tree branch on mains during storm. Milson's Passage difficult access See 1753730 1753732 1753733 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2020-02-09 | Y | 9774.9167 | Y | 3 | N | Y | 1.1101 | 39.4971 | 428593.2473
[7 empty] | 4933 | 16436 | 1746261 | 2020-02-17 10:44 | 2020-02-17 16:25 | 341 | 11kV | 6820 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207720 B Phase DOLF : 63 Amp Excluded OMS 1746261 | February | 2020 | 2020Q3 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2020-02-17 | N | 341 | N | 32 | Y | Y | 1.1101 | 39.4971 | 4983.8548
[7 empty] | 5195 | 18902 | 1746295 | 2020-02-17 11:25 | 2020-02-17 17:08 | 342.8333 | 11kV | 8913.6667 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207722 3 phase DOLF : 10 Amp Excluded OMS 1746295 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-02-17 | N | 342.8333 | N | 32 | Y | Y | 1.1101 | 39.4971 | 6513.8447
[7 empty] | 4503 | 12094 | 1746440 | 2020-02-17 14:02 | 2020-02-17 18:13 | 251.1 | 11kV | 9792.9 | 39 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 207718 FUSE : 80 Amp | February | 2020 | 2020Q3 | 2020 | 206:34441 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | UG | Not Veg | 2020-02-17 | N | 251.1 | N | 32 | Y | Y | 1.1101 | 39.4971 | 7156.3625
[7 empty] | 4042 | 7461 | 1746228 | 2020-02-17 10:02 | 2020-02-17 19:05 | 543 | 11kV | 543 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207735 Single phase DOLF : 10 Amp Excluded OMS 1746228 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 543 | Y | 32 | N | Y | 1.1101 | 39.4971 | 396.8084
[7 empty] | 3330 | 374 | 1746395 | 2020-02-17 13:08 | 2020-02-17 20:10 | 422 | 11kV | 22078 | 59 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 207739 Broken taps pole 9L-40811 | February | 2020 | 2020Q3 | 2020 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2020-02-17 | N | 374.2034 | N | 32 | Y | Y | 1.1101 | 39.4971 | 16133.9512
[7 empty] | 5314 | 19995 | 1746477 | 2020-02-17 14:51 | 2020-02-17 20:25 | 334 | 11kV | 668 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207742 Single phase DOLF : 10 Amp Excluded OMS 1746477 | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-02-17 | N | 334 | N | 32 | Y | Y | 1.1101 | 39.4971 | 488.1547
[7 empty] | 3594 | 2769 | 1746515 | 2020-02-17 15:49 | 2020-02-17 20:40 | 291.2333 | 11kV | 4950.9667 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207746 Single phase DOLF : 5 Amp | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-17 | N | 291.2333 | N | 32 | Y | Y | 1.1101 | 39.4971 | 3618.0204
[7 empty] | 3660 | 3528 | 1746602 | 2020-02-17 19:27 | 2020-02-17 21:20 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207747 Single phase DOLF : 5 Amp Excluded OMS 1746602 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-17 | N | 113 | N | 32 | Y | Y | 1.1101 | 39.4971 | 82.5771
[7 empty] | 4225 | 9515 | 1751984 | 2020-02-17 20:45 | 2020-02-17 21:45 | 60 | 11kV | 540 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 207752 Blown lightning arrestor sub 73094 | February | 2020 | 2020Q3 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 60 | N | 32 | Y | Y | 1.1101 | 39.4971 | 394.6161
[7 empty] | 4128 | 8459 | 1746456 | 2020-02-17 14:24 | 2020-02-17 21:45 | 441 | 11kV | 441 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207751 Single phase DOLF : 10 Amp Excluded OMS 1746456 | February | 2020 | 2020Q3 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 441 | N | 32 | Y | Y | 1.1101 | 39.4971 | 322.2698
[7 empty] | 4911 | 16137 | 1746315 | 2020-02-17 11:36 | 2020-02-17 21:55 | 619 | 11kV | 18138 | 178 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 207733 11kV tappings blown at pole GQ-57475 towards pole GQ-55301. Excluded OMS No. 1746315 + 1746564 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2020-02-17 | N | 101.8989 | N | 32 | Y | Y | 1.1101 | 39.4971 | 13254.7154
[7 empty] | 4152 | 8752 | 1746773 | 2020-02-17 17:30 | 2020-02-17 21:55 | 265 | 11kV | 530 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207732 C Phase DOLF : 10 Amp No OMS No. found by staff | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-02-17 | N | 265 | N | 32 | Y | Y | 1.1101 | 39.4971 | 387.3084
[7 empty] | 4567 | 12789 | 1746267 | 2020-02-17 10:49 | 2020-02-17 22:45 | 716 | 11kV | 9737 | 46 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 207743 1 fault operation Sensitive Earth Fault Replaced damaged tx @ sub 50230. Excluded OMS No. 1746267 | February | 2020 | 2020Q3 | 2020 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2020-02-17 | N | 211.6739 | N | 32 | Y | Y | 1.1101 | 39.4971 | 7115.5124
[7 empty] | 4576 | 12901 | 1746595 | 2020-02-17 19:02 | 2020-02-17 23:20 | 258 | 11kV | 774 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207754 Single phase DOLF : 10 Amp Excluded OMS 1746595 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 258 | N | 32 | Y | Y | 1.1101 | 39.4971 | 565.6164
[7 empty] | 4615 | 13338 | 1746628 | 2020-02-17 23:14 | 2020-02-18 00:48 | 94 | 11kV | 282 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207756 A Phase DOLF : 16 Amp Cut away blown 11kV arrestor, requires replacement Excluded OMS 1746628 | February | 2020 | 2020Q3 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2020-02-17 | N | 94 | N | 32 | Y | Y | 1.1101 | 39.4971 | 206.0773
[7 empty] | 3398 | 953 | 1746619 | 2020-02-17 20:20 | 2020-02-18 09:00 | 760 | 11kV | 760 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207763 B Phase DOLF : 10 Amp Excluded OMS 1746619 | February | 2020 | 2020Q3 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 760 | Y | 32 | N | Y | 1.1101 | 39.4971 | 555.3856
[7 empty] | 5294 | 19791 | 1746663 | 2020-02-18 07:52 | 2020-02-18 09:05 | 73 | 11kV | 146 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207766 A Phase DOLF : 10 Amp Excluded OMS 1746663 | February | 2020 | 2020Q3 | 2020 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2020-02-18 | N | 73 | N | 7 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 3831 | 5370 | 1746616 | 2020-02-17 20:06 | 2020-02-18 09:25 | 799 | 11kV | 799 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207760 DOLF : 10 Amp Excluded OMS 1746616 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-02-17 | N | 799 | Y | 32 | N | Y | 1.1101 | 39.4971 | 583.8856
[7 empty] | 3449 | 1488 | 1746668 | 2020-02-17 09:00 | 2020-02-18 10:25 | 1525 | 11kV | 1525 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207767 Single phase DOLF : 10 Amp Blown Lightning Arrestor Excluded OMS 1746668 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-02-17 | N | 1525 | Y | 32 | N | Y | 1.1101 | 39.4971 | 1114.425
[7 empty] | 5181 | 18814 | 1746603 | 2020-02-17 19:33 | 2020-02-18 10:35 | 902 | 11kV | 1804 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 207777 Single phase DOLF : 10 Amp | February | 2020 | 2020Q3 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2020-02-17 | N | 902 | Y | 32 | N | Y | 1.1101 | 39.4971 | 1318.31
[7 empty] | 3294 | 69 | 1746716 | 2020-02-18 09:24 | 2020-02-18 10:35 | 70.7333 | 11kV | 70.7333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 207770 C Phase DOLF : 10 Amp Excluded OMS 1746718 | February | 2020 | 2020Q3 | 2020 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2020-02-18 | N | 70.7333 | N | 7 | N | N | 1.1101 | 39.4971 | 51.6898
[7 empty] | 4885 | 15817 | 1746503 | 2020-02-17 15:33 | 2020-02-18 10:50 | 1157 | 11kV | 1157 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 207755 Single phase DOLF : 10 Amp replace faulty transformer Excluded OMS 1746503 | February | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2020-02-17 | N | 1157 | Y | 32 | N | Y | 1.1101 | 39.4971 | 845.5015
[7 empty] | 3514 | 2172 | 1746605 | 2020-02-17 19:38 | 2020-02-18 11:30 | 951.5167 | 11kV | 24739.4333 | 26 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 207769 Single phase DOLF : 20 Amp Replaced Lightning Arrestors Sub 70334 | February | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2020-02-17 | N | 951.5167 | Y | 32 | N | Y | 1.1101 | 39.4971 | 18078.8482
[7 empty] | 3989 | 6853 | 1746703 | 2020-02-18 08:55 | 2020-02-18 13:10 | 255 | 11kV | 255 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207779 A Phase DOLF : 10 Amp related to LID 207778 & OMS 1746789. excluded OMS 1746703 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-18 | N | 255 | N | 7 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 4670 | 13821 | 1746789 | 2020-02-18 12:00 | 2020-02-18 13:10 | 70 | 11kV | 8750 | 125 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207778 Termination grip let go pole AI-80183 No Protection. Found by field staff. related to LID 20779 & OMS 1746703 Excluded OMS 1746789 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-18 | N | 70 | N | 7 | N | N | 1.1101 | 39.4971 | 6394.2419
[7 empty] | 4996 | 17163 | 1746798 | 2020-02-18 11:51 | 2020-02-18 13:56 | 125.5167 | 11kV | 29998.4833 | 239 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | LB61922 Bypass interrupted for safety. DNMS recorded open and close Abnormal: IR61922 Paciifc Bar Point DMA unable to close locally/remotely | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-02-18 | Y | 125.5167 | N | 7 | N | Y | 1.1101 | 39.4971 | 21922.0068
[7 empty] | 5157 | 18660 | 1750450 | 2020-02-18 13:15 | 2020-02-18 14:05 | 50 | 11kV | 750 | 15 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Previous Storm | Y | Ex ZN12570 AVOCA section of 11kV Panel 33 RE44797 Bouddi to LB44320interrupted for emergency repairs LB50212 switfch unable to be locked closed or open, interrupted for emergency repairs | February | 2020 | 2020Q3 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2020-02-18 | Y | 50 | N | 7 | N | Y | 1.1101 | 39.4971 | 548.0779
[7 empty] | 4484 | 11870 | 1746860 | 2020-02-18 13:19 | 2020-02-18 14:30 | 71 | 11kV | 213 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207783 B Phase DOLF : 10 Amp Excluded OMS 1746860 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-18 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 155.6541
[7 empty] | 4263 | 9924 | 1746803 | 2020-02-18 11:55 | 2020-02-18 14:33 | 158 | 11kV | 50718 | 321 | HV | Equipment Failed in Service | Equipment Failure | Tap Changer | Unplanned | No Weather Impact | Y | Ex ZN12630 peats Ridge, Panel '1', labelled 'Gunderman' 11kv intelliruptor 61375 Wise Ferry Biara 1.30, tripped, reclosed, reclosed and locked out on: Relays: Nil (iR in scan fail) Remarks: transformer tap changer. Regulator 61374 Wise Ferry Biara 1.27 has failed, smoke seen from footpath side can. | February | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | Unknown | Not Veg | 2020-02-18 | Y | 158 | N | 7 | N | Y | 1.1101 | 39.4971 | 37063.2185
[7 empty] | 4270 | 9974 | 1756722 | 2020-02-18 14:00 | 2020-02-18 16:20 | 140 | 11kV | 980 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | Y | Section of 11kv feeder from LK44820 to AB43713 interrupted for emergency repairs. Ex Zn12630 Peats Ridge, Panel 1 'Gunderman' Remarks: bond. Emergency repairs to PT13484 Wise Ferry Oyster 4.4, HV bond off | February | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-02-18 | Y | 140 | N | 7 | N | Y | 1.1101 | 39.4971 | 716.1551
[7 empty] | 5346 | 20387 | 1738018 | 2020-02-09 08:55 | 2020-02-18 18:54 | 13559.25 | 11kV | 5944254 | 1720 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12650 WEST GOSFORD 11kV CB Panel 1 'Dog Trap Rd' tripped on Relays: Cause: Multiple Tree on OH Mains in various locations AP Issued. CP42941 Defective Autlink AP Issued. Suspect DMA from CP49777 to CP44637 tee pt12676 pt14603 AP Issued. Suspect DMA from CP44637 to CP44391 AP Issued. OH mains beyond CP43922 damaged by Storm. Crew Working on repairs See 1734253,42347,8,64,890,1,5022,80 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-02-09 | Y | 3455.9616 | Y | 3 | N | Y | 1.1101 | 39.4971 | 4343885.4974
[7 empty] | 4792 | 14962 | 1747105 | 2020-02-18 22:15 | 2020-02-19 00:13 | 118 | 11kV | 56535 | 492 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Darling Harbour Zn - Panel 19 Relays: Tx12 Group Earth, 11kV trip EFIs: S6421, S3044 UG cable fault located between S3044, S6488 and S3092 See 1753789, 1753788 | February | 2020 | 2020Q3 | 2020 | ZN7481:PA19 | ZN7481:PA19 | ZN07481/000019 | SYDNEY | UG | Not Veg | 2020-02-18 | N | 114.9085 | N | 7 | N | N | 1.1101 | 39.4971 | 41314.1105
[7 empty] | 4198 | 9304 | 1747627 | 2020-02-19 00:01 | 2020-02-19 02:16 | 135 | 11kV | 206955 | 1533 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 207804 2 fault operations A Phase Overcurrent Tree on mains pole CH-10211 Excluded OMS 1747696 | February | 2020 | 2020Q3 | 2020 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Veg | 2020-02-19 | Y | 135 | N | 6 | N | Y | 1.1101 | 39.4971 | 151236.6099
[7 empty] | 3517 | 2180 | 1747577 | 2020-02-18 23:45 | 2020-02-19 04:14 | 269 | 11kV | 287976 | 1124 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | ZN12620 NORAVILLE 11kV CB Panel 10 'Diamond Head Kailua' tripped on Relays: ABC phase OC & EF No cause found Storm See 1753505,6,7,8 Ex 1747577 | February | 2020 | 2020Q3 | 2020 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2020-02-18 | Y | 256.2064 | N | 7 | N | Y | 1.1101 | 39.4971 | 210444.3669
[7 empty] | 4648 | 13599 | 1747348 | 2020-02-18 23:02 | 2020-02-19 04:33 | 331 | 11kV | 450491 | 1361 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3154 St Ives - Pnl.11 interrupted to remove large tree from mains S35365 Sw/A Closed with AB2514 Open | February | 2020 | 2020Q3 | 2020 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2020-02-18 | Y | 331 | N | 7 | N | Y | 1.1101 | 39.4971 | 329205.5356
[7 empty] | 4465 | 11617 | 1747149 | 2020-02-18 22:46 | 2020-02-19 06:05 | 439 | 11kV | 592571 | 1897 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2196 Milperra - Pnl.5 tripped on: A Phae O/C Abnormal: S8011 Sw/A Closed with LB133 Open 11kV mains down between S8990 Sw/B, S8239 Sw/A to LB3265 to LB2801 See 1750256 1750255 | February | 2020 | 2020Q3 | 2020 | ZN2196:PA3 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-02-18 | N | 312.3727 | N | 7 | N | N | 1.1101 | 39.4971 | 433033.4089
[7 empty] | 4069 | 7759 | 1747810 | 2020-02-19 01:47 | 2020-02-19 07:53 | 366 | 11kV | 186117 | 1390 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 207814 A Phase Overcurrent Tapping blown pole IU-61337 repaired under AP Excluded OMS 1747810. | February | 2020 | 2020Q3 | 2020 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | OH | Not Veg | 2020-02-19 | Y | 133.8971 | N | 6 | N | Y | 1.1101 | 39.4971 | 136008.8141
[7 empty] | 3493 | 1947 | 1747532 | 2020-02-18 23:30 | 2020-02-19 08:12 | 522 | 11kV | 513648 | 984 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | Ex ZN12620 NORAVILLE section of 11kV Panel 1 RE47818 isolated from LK47818X to LK47818Y Surge Arrestors at RE47818 have failed | February | 2020 | 2020Q3 | 2020 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2020-02-18 | Y | 522 | N | 7 | N | Y | 1.1101 | 39.4971 | 375358.8083
[7 empty] | 3608 | 2839 | 1748093 | 2020-02-18 23:10 | 2020-02-19 08:14 | 544 | 11kV | 359040 | 660 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC630 tripped on: OC Abnormal: REC630 Closed with S47772 Sw/A Open, LB1590 Closed with LB1276 Open Storm See 1756399 1756400 | February | 2020 | 2020Q3 | 2020 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2020-02-18 | Y | 544 | N | 7 | N | Y | 1.1101 | 39.4971 | 262375.8421
[7 empty] | 3366 | 672 | 1747338 | 2020-02-18 22:57 | 2020-02-19 08:27 | 570 | 11kV | 868623 | 1545 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15009 Manly - Pnl.5 tripped on: A phase O/C Tree on HV and LV between S16427 Sw/B and S15095 Sw/A See 1750817 1750818 | February | 2020 | 2020Q3 | 2020 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Veg | 2020-02-18 | Y | 562.2155 | Y | 7 | N | Y | 1.1101 | 39.4971 | 634764.0684
[7 empty] | 4913 | 16140 | 1748445 | 2020-02-19 08:19 | 2020-02-19 08:43 | 24 | 11kV | 257 | 119 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At S9035 Caringbah Panel 8 tripped on Relays: Timed OC, E/F and EFI Signals: Zone Earth and Tx2 Group Earth and 11kV Trip Cause: 11kV UG feeder fault from S9411 Kareena Hospital No1 to S9017 Kereena SW/B See OMS 1750096 1750099 1748445 | February | 2020 | 2020Q3 | 2020 | ZN9035:PA8 | ZN9035:PA8 | ZN09035/000008 | SUTHERLAND | UG | Not Veg | 2020-02-19 | N | 2.1597 | N | 6 | N | N | 1.1101 | 39.4971 | 187.808
[7 empty] | 3912 | 6041 | 1748144 | 2020-02-19 07:07 | 2020-02-19 08:45 | 98 | 11kV | 1274 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207815 Single phase DOLF : 20 Amp Excluded OMS 1748144 & 1747848 | February | 2020 | 2020Q3 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-02-19 | Y | 98 | N | 6 | N | Y | 1.1101 | 39.4971 | 931.0016
[7 empty] | 3726 | 4192 | 1748020 | 2020-02-19 06:22 | 2020-02-19 09:10 | 168 | 11kV | 3024 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207818 DOLF : 20 Amp Excluded OMS 1748020 & others. in Singleton Queue | February | 2020 | 2020Q3 | 2020 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-02-19 | Y | 168 | N | 6 | N | Y | 1.1101 | 39.4971 | 2209.85
[7 empty] | 3473 | 1736 | 1747956 | 2020-02-19 05:33 | 2020-02-19 09:10 | 217 | 11kV | 217 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207817 B Phase DOLF : 31 Amp Excluded OMS 1747956 | February | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-02-19 | Y | 217 | N | 6 | N | Y | 1.1101 | 39.4971 | 158.5772
[7 empty] | 4087 | 8037 | 1747503 | 2020-02-18 23:26 | 2020-02-19 09:25 | 599 | 11kV | 185458 | 329 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex ZN12690 BERKELEY VALE section of 11kV Panel 12 RE44999 Warner tripped due to storm Relays: OC trip, IOC trip See 1752737,9,40 Ex 1747503,8573,4 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2020-02-18 | Y | 563.7021 | N | 7 | N | Y | 1.1101 | 39.4971 | 135527.2363
[7 empty] | 4285 | 10046 | 1747108 | 2020-02-18 22:38 | 2020-02-19 09:38 | 660 | 11kV | 1226212 | 1861 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn965 Pennant Hills - Pnl.43 tripped on C phase O/L Abnormal: LB2664 Closed with S4493 Sw/A Open Lightning storm See 1756535 1756536 | February | 2020 | 2020Q3 | 2020 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2020-02-18 | Y | 658.8995 | N | 7 | N | Y | 1.1101 | 39.4971 | 896079.5625
[7 empty] | 4021 | 7198 | 1747250 | 2020-02-18 22:57 | 2020-02-19 09:43 | 645.5833 | 11kV | 215624.8333 | 334 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn2400 Berowra - Pnl.23 tripped on: OC trip Tree branch removed near LB573 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | OH | Veg | 2020-02-18 | Y | 645.5833 | N | 7 | N | Y | 1.1101 | 39.4971 | 157572.2683
[7 empty] | 5065 | 17942 | 1748395 | 2020-02-19 08:11 | 2020-02-19 09:45 | 94 | 11kV | 188 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207831 A Phase DOLF : 10 Amp Excluded OMS 1748395 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 94 | N | 6 | N | Y | 1.1101 | 39.4971 | 137.3849
[7 empty] | 3340 | 475 | 1748223 | 2020-02-19 07:31 | 2020-02-19 10:00 | 149 | 11kV | 596 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207821 C Phase DOLF : 10 Amp Excluded OMS 1748223 | February | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-02-19 | Y | 149 | N | 6 | N | Y | 1.1101 | 39.4971 | 435.5392
[7 empty] | 4905 | 15998 | 1748408 | 2020-02-19 08:15 | 2020-02-19 10:10 | 115 | 11kV | 690 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207822 3 Phase DOLF : 20 Amp Excluded OMS 1748408 | February | 2020 | 2020Q3 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2020-02-19 | Y | 115 | N | 6 | N | Y | 1.1101 | 39.4971 | 504.2316
[7 empty] | 5226 | 19286 | 1747463 | 2020-02-18 23:17 | 2020-02-19 10:20 | 663 | 11kV | 209508 | 316 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | Y | At ZN10997 Sans Souci Panel 2 section beyond CP30838 Burnt off Cause: 11kV USL 30838 | February | 2020 | 2020Q3 | 2020 | ZN10997:PA2 | ZN10997:PA2 | ZN10997/000002 | BAYSIDE | OH | Not Veg | 2020-02-18 | Y | 663 | N | 7 | N | Y | 1.1101 | 39.4971 | 153102.267
[7 empty] | 3506 | 2091 | 1747176 | 2020-02-18 22:51 | 2020-02-19 10:37 | 706.2 | 11kV | 1074130.2 | 1521 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Previous Storm | Y | Lindfield P26 Relays: 50TBC, IOC B+C trip Remarks: branch remove from PT2415 | February | 2020 | 2020Q3 | 2020 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2020-02-18 | Y | 706.2 | N | 7 | N | Y | 1.1101 | 39.4971 | 784942.6687
[7 empty] | 4289 | 10090 | 1747685 | 2020-02-19 00:29 | 2020-02-19 10:41 | 612 | 11kV | 858088 | 1432 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Ex ZN13000 LAKE MUNMORAH section of 11kV Panel 7 RE45061 Chain Valley Bay Mulloway tripped on OC trip and Lockout 11kv fdr isolated from Zn13000 Panel 7 to RE45061 to LB40169 11kV Bond off at RE45061 11kV UGOH has failed See 1753531,2,3 Ex 1747685,8599,843 | February | 2020 | 2020Q3 | 2020 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | Unknown | Unknown | 2020-02-19 | Y | 599.2235 | N | 6 | N | Y | 1.1101 | 39.4971 | 627065.4011
[7 empty] | 5212 | 19105 | 1751129 | 2020-02-19 07:31 | 2020-02-19 10:41 | 190 | 11kV | 380 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207823 DOLF : 20 Amp | February | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-02-19 | Y | 190 | N | 6 | N | Y | 1.1101 | 39.4971 | 277.6928
[7 empty] | 3596 | 2777 | 1747567 | 2020-02-18 23:28 | 2020-02-19 10:50 | 682 | 11kV | 131209 | 200 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | Y | Zn14891 Wyong - Pnl.10 tripped on: O/C UGOH to S18743 failed See 1757520 1757521 | February | 2020 | 2020Q3 | 2020 | ZN14891:PA6 | ZN14891:PA6 | ZN14891/000006 | CENTRAL COAST | Unknown | Unknown | 2020-02-18 | Y | 656.045 | N | 7 | N | Y | 1.1101 | 39.4971 | 95883.6672
[7 empty] | 4653 | 13630 | 1747786 | 2020-02-19 01:26 | 2020-02-19 10:55 | 569 | 11kV | 85354 | 160 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 207851 C Phase Earth Fault; Overcurrent Excluded OMS 1747786 | February | 2020 | 2020Q3 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 533.4625 | Y | 6 | N | Y | 1.1101 | 39.4971 | 62374.1857
[7 empty] | 5262 | 19549 | 1748115 | 2020-02-18 22:44 | 2020-02-19 11:03 | 739 | 11kV | 1441096 | 2301 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Rain Wind Storm | Y | Epping P35 Relays: 50 TC, ISOTN, Trip EFI Abnormal: Sw/B closed @ S5604, LB2933 open | February | 2020 | 2020Q3 | 2020 | ZN2635:PA35 | ZN2635:PA35 | ZN02635/000035 | RYDE | Unknown | Unknown | 2020-02-18 | Y | 626.2912 | N | 7 | N | Y | 1.1101 | 39.4971 | 1053110.4517
[7 empty] | 4371 | 10785 | 1748327 | 2020-02-19 07:55 | 2020-02-19 11:05 | 190 | 11kV | 570 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207879 Single phase DOLF : 10 Amp Excluded OMS 1748327 | February | 2020 | 2020Q3 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2020-02-19 | Y | 190 | N | 6 | N | Y | 1.1101 | 39.4971 | 416.5392
[7 empty] | 4385 | 10866 | 1747805 | 2020-02-19 01:43 | 2020-02-19 11:16 | 573 | 11kV | 7854 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207810 3 fault operations B & C Phase Overcurrent Excluded OMS 1747805 | February | 2020 | 2020Q3 | 2020 | 813:89058 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 436.3333 | N | 6 | N | Y | 1.1101 | 39.4971 | 5739.4715
[7 empty] | 3972 | 6642 | 1747639 | 2020-02-19 00:08 | 2020-02-19 11:20 | 672 | 11kV | 2688 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12690 BERKELEY VALE section of 11kV Panel 24 PT13809 BRUSH ANDERSON 16Amp Footpath HDO operated Weather: Storm See 1753245 ex 1747639 1748191 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2020-02-19 | Y | 672 | N | 6 | N | Y | 1.1101 | 39.4971 | 1964.3111
[7 empty] | 4067 | 7744 | 1747844 | 2020-02-19 02:35 | 2020-02-19 11:35 | 540 | 11kV | 1080 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207835 Single phase DOLF : 10 Amp Excluded OMS 1747844 | February | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 540 | Y | 6 | N | Y | 1.1101 | 39.4971 | 789.2321
[7 empty] | 4872 | 15731 | 1748823 | 2020-02-19 10:26 | 2020-02-19 11:35 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207860 A Phase Distribution fuse : 100 Amp Excluded OMS 1748823 | February | 2020 | 2020Q3 | 2020 | 526:34635 | 526:34635 | ZN00526/034635 | SINGLETON | OH | Veg | 2020-02-19 | Y | 69 | N | 6 | N | Y | 1.1101 | 39.4971 | 50.4232
[7 empty] | 3866 | 5654 | 1747166 | 2020-02-18 22:50 | 2020-02-19 11:40 | 770 | 11kV | 1010510 | 1359 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | Zn195 - Pymble - Pnl.28 tripped on B & C phase O/C Abnormal: S6931 Sw/B Closed with AB241 Open (DMA) Storm See 1756579 1756580 | February | 2020 | 2020Q3 | 2020 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | OH | Not Veg | 2020-02-18 | Y | 743.5688 | N | 7 | N | Y | 1.1101 | 39.4971 | 738450.903
[7 empty] | 4221 | 9486 | 1747831 | 2020-02-19 02:16 | 2020-02-19 11:40 | 564 | 11kV | 454468 | 1119 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207857 A & B Phase Overcurrent; Earth Fault Excluded OMS 1747831 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-02-19 | Y | 406.1376 | N | 6 | N | Y | 1.1101 | 39.4971 | 332111.8099
[7 empty] | 4935 | 16445 | 1748635 | 2020-02-19 09:19 | 2020-02-19 11:45 | 146 | 11kV | 2628 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207828 3 Phase DOLF : 10 Amp Excluded OMS 1748635 | February | 2020 | 2020Q3 | 2020 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2020-02-19 | Y | 146 | N | 6 | N | Y | 1.1101 | 39.4971 | 1920.4649
[7 empty] | 4783 | 14836 | 1748734 | 2020-02-19 09:46 | 2020-02-19 11:50 | 124 | 11kV | 372 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207862 A Phase DOLF : 10 Amp Excluded OMS 1748734 | February | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-02-19 | N | 124 | N | 6 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 3532 | 2324 | 1747818 | 2020-02-19 02:03 | 2020-02-19 12:06 | 602.6167 | 11kV | 21091.5833 | 35 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207830 C Phase DOLF : 20 Amp | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-02-19 | Y | 602.6167 | N | 6 | N | Y | 1.1101 | 39.4971 | 15413.107
[7 empty] | 5064 | 17933 | 1750519 | 2020-02-19 08:16 | 2020-02-19 12:15 | 239 | 11kV | 1673 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207845 B & C phase DOLF : 10 Amp Excluded OMS 1748412 | February | 2020 | 2020Q3 | 2020 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 239 | N | 6 | N | Y | 1.1101 | 39.4971 | 1222.5791
[7 empty] | 3750 | 4482 | 1747820 | 2020-02-19 01:53 | 2020-02-19 12:40 | 647 | 11kV | 30264 | 184 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 207812 2 fault operations Faulty Transformer Excluded OMS 1747820 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 164.4783 | N | 6 | N | Y | 1.1101 | 39.4971 | 22116.0386
[7 empty] | 5320 | 20032 | 1748989 | 2020-02-19 11:46 | 2020-02-19 12:40 | 53.75 | 11kV | 2633.75 | 49 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 207837 Wire off Pin at AH-42112 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-02-19 | Y | 53.75 | N | 6 | N | Y | 1.1101 | 39.4971 | 1924.6668
[7 empty] | 3350 | 566 | 1747216 | 2020-02-18 23:11 | 2020-02-19 12:51 | 820 | 11kV | 192532 | 237 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Rec64824 Deepwater Holly lock out + O/C trip Remarks: tree on mains patrol required. | February | 2020 | 2020Q3 | 2020 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Veg | 2020-02-18 | Y | 812.3713 | N | 7 | N | Y | 1.1101 | 39.4971 | 140696.7069
[7 empty] | 4817 | 15198 | 1748972 | 2020-02-19 11:39 | 2020-02-19 12:55 | 76 | 11kV | 228 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207842 C Phase DOLF : 20 Amp Excluded OMS 1748972 | February | 2020 | 2020Q3 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 76 | N | 6 | N | Y | 1.1101 | 39.4971 | 166.6157
[7 empty] | 5348 | 20430 | 1747587 | 2020-02-18 23:49 | 2020-02-19 13:06 | 797 | 11kV | 3985 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | PT14341 REEVES DAWSON Defective Surge Arrestor See 1756588,9 Ex 1747587 Note: customers then affected by OMS 1757602 and had continual outage until 19/02/20 14:00 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2020-02-18 | Y | 797 | N | 7 | N | Y | 1.1101 | 39.4971 | 2912.1205
[7 empty] | 5233 | 19347 | 1747157 | 2020-02-18 23:01 | 2020-02-19 13:28 | 867 | 11kV | 247337 | 421 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Rec45189 Cook Peats Ridge 0.5 Remarks: 11kv down between AB43966 & LK43962 PT49014 also associated. AP & CTW issued at 04:00 also appears from SAP records that TX PT14007 Wiseferry Oyster 3.9 was replaced also | February | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-02-18 | Y | 587.4988 | N | 7 | N | Y | 1.1101 | 39.4971 | 180746.5844
[7 empty] | 3339 | 457 | 1747213 | 2020-02-18 22:52 | 2020-02-19 13:37 | 885 | 11kV | 414048 | 544 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn3154 St Ives - Pnl.5 tripped on: A phase O/C Abnormal: S8276 Sw/B open with S35365 Closed Tree down near PT995 See 1752060 1752061 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2020-02-18 | Y | 761.1176 | N | 7 | N | Y | 1.1101 | 39.4971 | 302574.0661
[7 empty] | 4580 | 12933 | 1756589 | 2020-02-19 13:06 | 2020-02-19 14:00 | 54 | 11kV | 1944 | 36 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | Ex ZN14143 SOMERSBY section of 11kV Panel 17 RE45037 Reeves Somersby tripped on OC trip, IOC Trip No EFI's operated PT14341 has Defective Surge Arrestor All PT's beyond RE45037 have blown HV HDO Fuses See 1756588,9 Ex 1747587 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2020-02-19 | Y | 54 | N | 6 | N | Y | 1.1101 | 39.4971 | 1420.6179
[7 empty] | 4861 | 15622 | 1747882 | 2020-02-19 03:30 | 2020-02-19 14:07 | 637 | 11kV | 45227 | 71 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 207840 Broken tapping at pole GQ-14614 Excluded OMS 1747882 1748730 | February | 2020 | 2020Q3 | 2020 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 637 | Y | 6 | N | Y | 1.1101 | 39.4971 | 33050.5576
[7 empty] | 4211 | 9390 | 1747970 | 2020-02-19 05:50 | 2020-02-19 14:08 | 498 | 11kV | 7968 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207838 A Phase DOLF : 20 Amp Excluded OMS 1747970 | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 498 | N | 6 | N | Y | 1.1101 | 39.4971 | 5822.7794
[7 empty] | 4294 | 10132 | 1747840 | 2020-02-19 02:59 | 2020-02-19 14:25 | 686 | 11kV | 203858 | 573 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 207881 Associated with 33kV KU4 outage Excluded oms 1747884, 1748733 | February | 2020 | 2020Q3 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2020-02-19 | Y | 355.7731 | N | 6 | N | Y | 1.1101 | 39.4971 | 148973.4136
[7 empty] | 3615 | 2942 | 1747135 | 2020-02-18 22:43 | 2020-02-19 14:30 | 947 | 11kV | 863951 | 1092 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At S1673 Turramurr Panel 6 tripped Cause: OH wind related See OMS 1756301 1756304 1756303 1747135 1749027 | February | 2020 | 2020Q3 | 2020 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Not Veg | 2020-02-18 | Y | 791.1639 | N | 7 | N | Y | 1.1101 | 39.4971 | 631349.9086
[7 empty] | 4213 | 9403 | 1747282 | 2020-02-18 22:56 | 2020-02-19 14:55 | 959 | 11kV | 115320 | 158 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | Y | Rec 45071 Relays: OC trip at 22:56 Abnormal: no Weather: storm | February | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2020-02-18 | Y | 729.8734 | N | 7 | N | Y | 1.1101 | 39.4971 | 84272.4546
[7 empty] | 3568 | 2618 | 1749189 | 2020-02-19 13:55 | 2020-02-19 15:00 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207865 Single phase DOLF : 10 Amp excluded OMS 1749189 | February | 2020 | 2020Q3 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2020-02-19 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 4599 | 13151 | 1747173 | 2020-02-18 23:43 | 2020-02-19 15:23 | 940 | 11kV | 825500 | 1013 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | AT S4545 Meadowbanks Panel 21 Tripped on Relays: A and C phase IOC and time doC Cause: HV found twisted together between S65523 and LB2813 Above Church St Meadowbank Abnormal Switching: CP62837 Open, CP1937 Closed See OMS 1756908 1756909 1749278/200/173 | February | 2020 | 2020Q3 | 2020 | ZN4545:PA21 | ZN4545:PA21 | ZN04545/000021 | RYDE | OH | Not Veg | 2020-02-18 | Y | 814.9062 | N | 7 | N | Y | 1.1101 | 39.4971 | 603251.0519
[7 empty] | 4137 | 8547 | 1747502 | 2020-02-18 23:27 | 2020-02-19 15:32 | 965 | 11kV | 2895 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | Ex ZN14143 SOMERSBY section of 11kV Panel 17 PT79078 GOLDSMITH REEVES HV HDO Fuse blown See 1756611 ex 1747502,29 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2020-02-18 | Y | 965 | N | 7 | N | Y | 1.1101 | 39.4971 | 2115.5806
[7 empty] | 3881 | 5754 | 1751310 | 2020-02-19 14:52 | 2020-02-19 16:02 | 70 | 11kV | 420 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207887 A & B Phase DOLF :: 10 Amp OMS NUMBER NOT PROVIDED APAPRENTLY IN DEPOT QUEUE. | February | 2020 | 2020Q3 | 2020 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 70 | N | 6 | N | Y | 1.1101 | 39.4971 | 306.9236
[7 empty] | 3535 | 2349 | 1749188 | 2020-02-19 13:54 | 2020-02-19 16:05 | 131 | 11kV | 262 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | Y | LID 207868 Broken Live Lione Clamp Excluded OMS 1749188 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 131 | N | 6 | N | Y | 1.1101 | 39.4971 | 191.4619
[7 empty] | 4713 | 14223 | 1747129 | 2020-02-18 22:42 | 2020-02-19 16:40 | 1078 | 11kV | 757834 | 703 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Wind Storm | Y | At CP46116 Lancaster Andrew - SEF O/C trip, Lockout and Aux supply Cause:Recloser CP46116 Lancaster Andrew - Centre phase line side link welded closed. Isolations needed to be extended in order to repair DMA Clearance received from Endeavour Energy @ 1828 to restore via their network. See OMS 1747147 1757145 1747129 1749219 | February | 2020 | 2020Q3 | 2020 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Not Veg | 2020-02-18 | Y | 1078 | N | 7 | N | Y | 1.1101 | 39.4971 | 553802.7349
[7 empty] | 4347 | 10577 | 1749138 | 2020-02-19 13:12 | 2020-02-19 16:40 | 208 | 11kV | 624 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207880 A Phase DOLF : 16 Amp Excluded OMS 1749138 | February | 2020 | 2020Q3 | 2020 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2020-02-19 | N | 208 | N | 6 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 3715 | 4073 | 1747823 | 2020-02-19 02:13 | 2020-02-19 16:55 | 882 | 11kV | 91970 | 277 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 207813 1 fault operation Sensitive Earth Fault Patrolled complete fdr to Sw 61200. LF 40759 x 2 blown dolfs S 51073 x 1 blown dolf Excluded OMS 1747823 | February | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 332.0217 | N | 6 | N | Y | 1.1101 | 39.4971 | 67208.9633
[7 empty] | 3867 | 5659 | 1748644 | 2020-02-19 09:21 | 2020-02-19 17:58 | 517 | 11kV | 656759 | 1770 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Previous Storm | Y | Epping Panel 58 Relays: trip, 50TAC, locked Abnormal: Sw/A open @ S5271, Sw/B closed @ S5702. AB1906 open, LB1903 closed, Sw/B @ S46890 closed, Sw/A @ S.4627, Sw/B open @ S6139 Sw/B closed @ S5142 | February | 2020 | 2020Q3 | 2020 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | Unknown | Unknown | 2020-02-19 | N | 371.0503 | N | 6 | N | N | 1.1101 | 39.4971 | 479940.1061
[7 empty] | 3558 | 2559 | 1748959 | 2020-02-19 07:36 | 2020-02-19 18:00 | 624 | 11kV | 3744 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207890 B & C Phase DOLF : 10 Amp excluded OMS 1748959 | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-02-19 | Y | 624 | Y | 6 | N | Y | 1.1101 | 39.4971 | 2736.0048
[7 empty] | 5100 | 18232 | 1747777 | 2020-02-19 00:55 | 2020-02-19 18:15 | 1040 | 11kV | 402337 | 815 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 207798 3 fault operations Instantaneous Overcurrent 4 span of mains on ground either side of ABS 10615 Excluded OMS 1747740 | February | 2020 | 2020Q3 | 2020 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Not Veg | 2020-02-19 | Y | 493.665 | N | 6 | N | Y | 1.1101 | 39.4971 | 294016.0127
[7 empty] | 4035 | 7402 | 1747999 | 2020-02-19 06:09 | 2020-02-19 20:05 | 836 | 11kV | 3344 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 207891 C Phase DOLF : 10 Amp Faulty Transformer Excluded OMS 1747999 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 836 | Y | 6 | N | Y | 1.1101 | 39.4971 | 2443.6966
[7 empty] | 3735 | 4302 | 1747898 | 2020-02-19 03:55 | 2020-02-19 20:45 | 1010 | 11kV | 326230 | 323 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC20112 tripped Abnormal: LB20518 closed with LB77332 open DMA Storm Note: customers lost supply prior to this refer to OMS 1750803 18/02/2020 23:05 | February | 2020 | 2020Q3 | 2020 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2020-02-19 | Y | 1010 | N | 6 | N | Y | 1.1101 | 39.4971 | 238399.2618
[7 empty] | 3835 | 5389 | 1747421 | 2020-02-18 23:03 | 2020-02-19 20:50 | 1307 | 11kV | 68767 | 121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | Peats Ridge Rec46803 Relays: OC trip, IOC trip at 2303 Remarks: 11kv fdr isolated from AB 40526 to LK 42860 tee PT12951 tee PT12263 tee PT14429 Remarks: tree on 11kv at PT12263 | February | 2020 | 2020Q3 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2020-02-18 | Y | 568.3223 | N | 7 | N | Y | 1.1101 | 39.4971 | 50252.8953
[7 empty] | 4030 | 7361 | 1749407 | 2020-02-19 17:17 | 2020-02-19 21:00 | 223 | 11kV | 446 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 207894 Single phase DOLF : 10 Amp Excluded OMS 1749407 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-19 | Y | 223 | N | 6 | N | Y | 1.1101 | 39.4971 | 325.9236
[7 empty] | 4649 | 13611 | 1749443 | 2020-02-19 18:09 | 2020-02-19 21:00 | 171 | 11kV | 204599 | 1528 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn1285 Greenacre Park - Pnl.20 tripped on: Earth fault Abnormal: S4189 Sw/A closed with LB1469 Open. S50484 Sw/B closed with S4867 Sw/A Open LV // in place between S1250, S49680 & PT1433 Suspect UG cable fault between S4409 Sw/B and S3965 Sw/A tee PT1203 See 1750052 1750553 LV// 1750058 1750059 | February | 2020 | 2020Q3 | 2020 | ZN1285:PA20 | ZN1285:PA20 | ZN01285/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-02-19 | N | 133.8999 | N | 6 | N | N | 1.1101 | 39.4971 | 149514.9146
[7 empty] | 4265 | 9933 | 1749420 | 2020-02-19 20:59 | 2020-02-19 21:39 | 40 | 11kV | 1960 | 49 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 207893 Mains off pin insulator at pole 4J-50062. Interruption to allow repairs and make site safe. Excluded OMS 1749420 | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-02-19 | Y | 40 | N | 6 | N | Y | 1.1101 | 39.4971 | 1432.3102
[7 empty] | 4987 | 17016 | 1747264 | 2020-02-18 22:57 | 2020-02-19 22:58 | 1441 | 11kV | 2367563 | 1643 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | AT Zn10999 Kogarah Panel 4 tripped and reclosed on ABC IOC - Earth Fault EFI Cause: Feeder to be patrolled | February | 2020 | 2020Q3 | 2020 | ZN10999:PA4 | ZN10999:PA4 | ZN10999/000004 | GEORGES RIVER | OH | Veg | 2020-02-18 | Y | 1441 | N | 7 | N | Y | 1.1101 | 39.4971 | 1730145.2091
[7 empty] | 4771 | 14750 | 1749589 | 2020-02-19 23:03 | 2020-02-20 00:34 | 91 | 11kV | 44135 | 485 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | Y | ZN14892 CHARMHAVEN 11kV CB Panel 17 'Matarami Arizona & Plane Tree Apple Gum' tripped 50T ABC Earth Fault, Recloser, Lockout, Timer, FC, 11kv frame leakage prohibition Abnormal: S18225 SwB closed, S14814 SwA Open (DMA) Possum fried @ UGOH between S14678 & S18155 See 1753494 ex 1749589 | February | 2020 | 2020Q3 | 2020 | ZN14892:PA17 | ZN14892:PA17 | ZN14892/000017 | CENTRAL COAST | Unknown | Unknown | 2020-02-19 | Y | 91 | N | 6 | N | Y | 1.1101 | 39.4971 | 32252.5562
[7 empty] | 3358 | 626 | 1749306 | 2020-02-19 15:48 | 2020-02-20 01:45 | 597 | 11kV | 1194 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 207884 Blown transformer Excluded OMS 1749306 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2020-02-19 | Y | 597 | N | 6 | N | Y | 1.1101 | 39.4971 | 872.54
[7 empty] | 4789 | 14912 | 1747142 | 2020-02-18 22:45 | 2020-02-20 02:30 | 1665 | 11kV | 367141 | 858 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.18 tripped on A Phase SEL Abnormal: CP65298 Closed with AB277 Open (DMA). LB2919 Closed with LB468 Open (DMA) Tree on mains outside 22 Sydney Rd See 175955 1755957 1755960 1755962 | February | 2020 | 2020Q3 | 2020 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2020-02-18 | Y | 427.9033 | N | 7 | N | Y | 1.1101 | 39.4971 | 268295.814
[7 empty] | 4164 | 9010 | 1749605 | 2020-02-20 00:52 | 2020-02-20 02:30 | 98 | 11kV | 102069 | 1143 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 931 Darlinghurst - 11kV Panel 25 feeder trip Relays: Earth Fault, EFI Signals: 11kV trip, Zone Earth, No.2 Group Earth EFI's: S3369, S3567, S6162, S6296, S7278, S1565, S4310 11kV UG Fault from S4310 Lincoln Cowper to S1393 Naval Pump. See 1754298, 1754297 | February | 2020 | 2020Q3 | 2020 | ZN931:PA25 | ZN931:PA25 | ZN00931/000025 | SYDNEY | UG | Not Veg | 2020-02-20 | N | 89.2992 | N | 10 | N | N | 1.1101 | 39.4971 | 74589.0147
[7 empty] | 4104 | 8216 | 1747219 | 2020-02-18 22:54 | 2020-02-20 02:42 | 1667.5667 | 11kV | 218451.2333 | 131 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC21350 Booralie Kalgoa tripped on: O/C Tree on mains | February | 2020 | 2020Q3 | 2020 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2020-02-18 | Y | 1667.5667 | Y | 7 | N | Y | 1.1101 | 39.4971 | 159637.7181
[7 empty] | 4267 | 9948 | 1747205 | 2020-02-18 22:50 | 2020-02-20 04:25 | 1775 | 11kV | 1460482 | 1816 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn36300 Balgowlah North - pnl.5 tripped on: B & C phase IOC Abnormal: S16916 Sw/B closed with LB20826 Open Storm S16505 Princes Alan - dist #1 - A, B & C phase fuses blown - Tree on mains See 1750241 1750242 1750243 1750244 | February | 2020 | 2020Q3 | 2020 | ZN36300:PA5 | ZN36300:PA5 | ZN36300/000005 | NORTHERN BEACHES | OH | Not Veg | 2020-02-18 | Y | 804.2302 | Y | 7 | N | Y | 1.1101 | 39.4971 | 1067277.1687
[7 empty] | 3765 | 4754 | 1747295 | 2020-02-18 23:02 | 2020-02-20 08:09 | 1987.2833 | 11kV | 421304.0667 | 212 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | No further information supplied, RDO created by Control Room after NS calls logged by customers Major storm 20/02/20 08:09 t44817: Phoned customers and on 20/02 | February | 2020 | 2020Q3 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2020-02-18 | Y | 1987.2833 | N | 7 | N | Y | 1.1101 | 39.4971 | 307876.5856
[7 empty] | 4582 | 12968 | 1749626 | 2020-02-20 06:06 | 2020-02-20 08:16 | 130 | 11kV | 249968 | 2188 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman - Pnl.41 tripped on: O/C and E/F UG cable fault in frontline section of feeder from Pnl.41 to S8299 Sw/A See 1751150 1751153 | February | 2020 | 2020Q3 | 2020 | ZN180:PA41 | ZN180:PA41 | ZN00180/000041 | WILLOUGHBY | UG | Not Veg | 2020-02-20 | N | 114.245 | N | 10 | N | N | 1.1101 | 39.4971 | 182669.2416
[7 empty] | 3963 | 6591 | 1749226 | 2020-02-19 14:34 | 2020-02-20 10:50 | 1216 | 11kV | 3648 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | Y | LID 207905 Substation DOLF Blown HV Lightning arrestors Excluded OMS 1749226 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-02-19 | Y | 1216 | Y | 6 | N | Y | 1.1101 | 39.4971 | 2665.8508
[7 empty] | 5130 | 18432 | 1751361 | 2020-02-20 06:54 | 2020-02-20 11:30 | 276 | 11kV | 552 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 207918 B Phase DOLF : 20 Amp Excluded OMS 1749643 | February | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-02-20 | N | 276 | N | 10 | N | N | 1.1101 | 39.4971 | 403.3853
[7 empty] | 3316 | 236 | 1749863 | 2020-02-20 11:24 | 2020-02-20 12:30 | 66 | 11kV | 23166 | 351 | HV | 3rd Party Vehicle | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | LID 207916 ABS 17126 operating handle damaged by MVA ABS left half open Excluded OMS 1749863 | February | 2020 | 2020Q3 | 2020 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Not Veg | 2020-02-20 | N | 66 | N | 10 | N | N | 1.1101 | 39.4971 | 16929.0295
[7 empty] | 4400 | 11051 | 1747345 | 2020-02-18 23:06 | 2020-02-20 12:40 | 2254 | 11kV | 69798 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex ZN12650 WEST GOSFORD section of 11kV Panel 1 RE44602 Ourimbah Ck Rd tripped on OC trip, Lockout Cause: 11kv fdr isolated from LK43922 to PT61456 to PT14453 See 1747345 1748627 | February | 2020 | 2020Q3 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-02-18 | Y | 658.4717 | N | 7 | N | Y | 1.1101 | 39.4971 | 51006.3197
[7 empty] | 5173 | 18752 | 1747167 | 2020-02-18 22:44 | 2020-02-20 13:00 | 2296 | 11kV | 868944 | 1748 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At 4545 Meadowbank Panel 29 tripped on 50TBC - IOC B and Cphase, 11kV Trip, Group Earth No2 Cause: Large Tree branch on OH - Section isolated between LB1044 to LV332 to LB2425 tee PT168 See OMS 1757116 1757117 1757118 1747167 1747937 | February | 2020 | 2020Q3 | 2020 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Veg | 2020-02-18 | Y | 497.1076 | N | 7 | N | Y | 1.1101 | 39.4971 | 634998.6457
[7 empty] | 3604 | 2798 | 1749634 | 2020-02-20 06:30 | 2020-02-20 13:20 | 410 | 11kV | 1640 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At PT11404 Wise Ferry George 0.4 11kv roadside HDO operated Remarks: cause not ascertained | February | 2020 | 2020Q3 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-02-20 | N | 410 | N | 10 | N | N | 1.1101 | 39.4971 | 1198.4636
[7 empty] | 4392 | 10950 | 1749903 | 2020-02-20 12:28 | 2020-02-20 13:49 | 81 | 11kV | 80290 | 1066 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN14892 CHARMHAVEN 11kV CB Panel 1 'Mataram Haven' tripped, reclosed and locked out on: Relays: EF, EFI, Fault Check, Reclose, Timing, Lock Out Signals: 11kv trip, Tx1 Group Earth EFI: Nil Frontline fault. Cause: UG Fault between Zn14892 Pa1 to S18361SwB See 1753496,7 ex 1749903 | February | 2020 | 2020Q3 | 2020 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | UG | Not Veg | 2020-02-20 | N | 75.3189 | N | 10 | N | N | 1.1101 | 39.4971 | 58673.5638
[7 empty] | 3990 | 6877 | 1748790 | 2020-02-19 10:12 | 2020-02-20 14:10 | 1678 | 11kV | 4138 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 207889 Single phase DOLF : 5 Amp Excluded OMS 1748790 | February | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-02-19 | Y | 689.6667 | Y | 6 | N | Y | 1.1101 | 39.4971 | 3023.9283
[7 empty] | 5343 | 20354 | 1747117 | 2020-02-18 22:40 | 2020-02-20 14:20 | 2380 | 11kV | 296057 | 374 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35370 Galston - Pnl.2 tripped on: B & Cphase IOC Storm. Large tree has brought down HV into LV, PT808 Dist #1 between Poles DU42163 and DU42162 affected. Switchboard checks ok. See 1756886 1756887 1756888 1756889 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-02-18 | Y | 791.5963 | N | 7 | N | Y | 1.1101 | 39.4971 | 216349.7234
[7 empty] | 3474 | 1740 | 1747188 | 2020-02-18 22:49 | 2020-02-20 15:30 | 2441 | 11kV | 806886 | 1413 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.22 tripped on C phase O/C S8018 - dist #2 - A, B & C phase fuses blown Storm See 1755683 1755684 1755687 | February | 2020 | 2020Q3 | 2020 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2020-02-18 | Y | 571.0446 | N | 7 | N | Y | 1.1101 | 39.4971 | 589648.4897
[7 empty] | 4966 | 16784 | 1747106 | 2020-02-18 22:39 | 2020-02-20 16:05 | 2486 | 11kV | 1225334 | 1014 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn35370 Galston - Pnl.8 tripped & reclosed on: A & C phase O/C REC554 Arcadia Rosscommon tripped and locked out. Abnormal:AB2063 Closed with AB340 Open (DMA). LB62159 Closed with LB3211 Open (DMA) Storm damage along feeder See 1756912 1756913 1756915 1756916 1756917 1756920 1756921 1756922 1756923 | February | 2020 | 2020Q3 | 2020 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2020-02-18 | Y | 1208.4162 | N | 7 | N | Y | 1.1101 | 39.4971 | 895437.946
[7 empty] | 4281 | 10023 | 1750023 | 2020-02-20 16:30 | 2020-02-20 17:30 | 60 | 11kV | 1440 | 24 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 207938 Broken pin insulator at pole FU-72559 | February | 2020 | 2020Q3 | 2020 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2020-02-20 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 4955 | 16666 | 1750092 | 2020-02-20 17:11 | 2020-02-20 19:10 | 119 | 11kV | 119 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207941 A Phase DOLF : 10 Amp Excluded OMS 1750092 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-20 | N | 119 | N | 10 | N | N | 1.1101 | 39.4971 | 86.9617
[7 empty] | 4007 | 7081 | 1749971 | 2020-02-20 14:34 | 2020-02-20 19:40 | 306 | 11kV | 999 | 131 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207939 A Phase DOLF : 16 Amp Excluded OMS 1749971 | February | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2020-02-20 | N | 7.626 | N | 10 | N | N | 1.1101 | 39.4971 | 730.0397
[7 empty] | 5001 | 17201 | 1749999 | 2020-02-20 15:14 | 2020-02-21 10:10 | 1136 | 11kV | 11355.05 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | PT2086 isolated due to tree resting on mains CC1: 06-"Urgent - O.H Mains - No others" CC2: 06-"Urgent - O.H Mains - No others" CC3: 18-"Complete - Customer phoned from vehicle" FRC1: 300-"Specify details by voice" FRC2: 371-"Tree across Service Lines or Distributors - Unable to remove tree" FRC3: 300-"Specify details by voice" | February | 2020 | 2020Q3 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2020-02-20 | N | 1135.505 | N | 10 | N | N | 1.1101 | 39.4971 | 8297.9356
[7 empty] | 3496 | 1996 | 1747478 | 2020-02-18 22:15 | 2020-02-21 12:38 | 3743 | 11kV | 222102 | 138 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Zn15013 Terrey Hills - Pnl.8 tripped, reclosed & tripped on: IOC, O/C C phase Tree branch brought down 11kV into LV at S16760 Bundaleer Covenant School Dist #2 See 1751383 1751384 1751385 | February | 2020 | 2020Q3 | 2020 | ZN15013:PA8 | ZN15013:PA8 | ZN15013/000008 | NORTHERN BEACHES | OH | Veg | 2020-02-18 | Y | 1609.4348 | Y | 7 | N | Y | 1.1101 | 39.4971 | 162305.5907
[7 empty] | 4408 | 11135 | 1750383 | 2020-02-21 11:17 | 2020-02-21 13:30 | 133 | 11kV | 931 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | at 12630 Peats Ridge Z section of p8 from pt13323 george downs colli 1.2 fppt[atj 16a hdo operated Remarks: fuse failure | February | 2020 | 2020Q3 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-02-21 | N | 133 | N | 3 | N | N | 1.1101 | 39.4971 | 680.3473
[7 empty] | 4295 | 10171 | 1747707 | 2020-02-19 00:29 | 2020-02-21 16:30 | 3841 | 11kV | 1006539 | 1770 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN13000 LAKE MUNMORAH 11kV CB Panel 4 'LB62014' tripped Relays: A+B phase OC, L/O, EFI Abnormal: RE45139 closed, S18069 SwA Open 11kv fdr isolated from LB46170 to PT11177 to PT64431 NAR53565 PT13391 Multiple bays of 11kv down See 1753524,5,6,7,8 Ex 1747707,15,8544,765,831 | February | 2020 | 2020Q3 | 2020 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2020-02-19 | Y | 568.6661 | N | 6 | N | Y | 1.1101 | 39.4971 | 735549.0133
[7 empty] | 4230 | 9558 | 1750565 | 2020-02-21 17:50 | 2020-02-21 18:45 | 55 | 11kV | 330 | 6 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 207968 Tree on mains near sub 70802 No protection operation, interruption for safety to issue access permit and remove tree from mains. Excluded OMS 1750565 | February | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-02-21 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 5172 | 18742 | 1750592 | 2020-02-21 18:25 | 2020-02-21 20:24 | 119 | 11kV | 1428 | 12 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 207970 Broken X arm pole AL-20002. Excluded OMS 1750592 | February | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-02-21 | N | 119 | N | 3 | N | N | 1.1101 | 39.4971 | 1043.5403
[7 empty] | 3642 | 3268 | 1750655 | 2020-02-22 06:35 | 2020-02-22 08:20 | 105 | 11kV | 1260 | 12 | HV | Animal Flying Fox | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 207972 B Phase DOLF : 30 Amp Bat on LA Excluded OMS 1750655 | February | 2020 | 2020Q3 | 2020 | 204:82701 | 204:82701 | ZN00204/082701 | NEWCASTLE | OH | Not Veg | 2020-02-22 | N | 105 | N | 1 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 4902 | 15979 | 1734219 | 2020-02-09 14:46 | 2020-02-22 19:30 | 19004.2 | 11kV | 1881415.8 | 99 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Storm - Water access only - Long outage | February | 2020 | 2020Q3 | 2020 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2020-02-09 | Y | 19004.2 | Y | 3 | N | Y | 1.1101 | 39.4971 | 1374883.1743
[7 empty] | 5200 | 18935 | 1750931 | 2020-02-23 03:42 | 2020-02-23 18:00 | 858 | 11kV | 743013 | 1903 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S10993 Hurstville Panel 35 tripped on Relays: C phase IOC, EF and EFI Signals: Tx12 Group Earth and Zone Earth Abnormal Switching: SW/B Closed at S10876, AB30068 Open Cause: UG cable fault between S10703 King Georges Norfolk to S10818 Stoney Cambridge See OMS 1754950 1754953 1754955 1754957 1750942/941/940/933/932/931 | February | 2020 | 2020Q3 | 2020 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | UG | Not Veg | 2020-02-23 | N | 390.443 | N | 3 | N | N | 1.1101 | 39.4971 | 542971.9852
[7 empty] | 3577 | 2659 | 1750876 | 2020-02-23 18:20 | 2020-02-24 10:52 | 991.6167 | 11kV | 164608.3667 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex ZN14143 SOMERSBY section of 11kV Panel 17 RE45012 Bar Point opened for safety due to tree on 11kv OH mains @ Pole SP558 Cause: interrupted for safety. See Relay OCB Operations section of report | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-02-23 | N | 991.6167 | N | 3 | N | N | 1.1101 | 39.4971 | 120290.9392
[7 empty] | 3964 | 6599 | 1751188 | 2020-02-24 10:02 | 2020-02-24 11:30 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 207984 A & B Phase DOLF : 10 Amp Excluded OMS 1751188 | February | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-02-24 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 4016 | 7175 | 1751020 | 2020-02-23 14:39 | 2020-02-24 12:15 | 1296 | 11kV | 36505 | 290 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @Wamberal Panel 5 'USL 41596 etc' fdr tripped, reclosed, tripped & locked out on Relays: A & B phase IOC, sef, lockout Signals: 11kv trip Remarks: tree/branch brought down OH. In Serpenine Drive Erina HTS large tree has fallen bringing down 2 bays of 11kv OH mains | February | 2020 | 2020Q3 | 2020 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2020-02-23 | N | 125.8793 | N | 3 | N | N | 1.1101 | 39.4971 | 26676.7773
[7 empty] | 4436 | 11400 | 1751426 | 2020-02-24 15:37 | 2020-02-24 20:20 | 283 | 11kV | 31785 | 384 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 17 tripped on A B and C phase IOC, EFI, Reclose, time delay lockout Cause: Top of pole HV contacted LV @ 35 Gladstone See OMS 1756108 1756109 1756134 1751426 1751429 1751430 1751432 1751465 | February | 2020 | 2020Q3 | 2020 | ZN1193:PA17 | ZN1193:PA17 | ZN01193/000017 | KU-RING-GAI | OH | Not Veg | 2020-02-24 | N | 82.7734 | N | 4 | N | N | 1.1101 | 39.4971 | 23227.5405
[7 empty] | 3412 | 1095 | 1751359 | 2020-02-24 17:30 | 2020-02-24 20:25 | 175 | 11kV | 27650 | 158 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 207989 MVA at IU20828 Excluded 1751359 | February | 2020 | 2020Q3 | 2020 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2020-02-24 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 20205.8045
[7 empty] | 3332 | 399 | 1751207 | 2020-02-24 10:29 | 2020-02-24 21:10 | 641 | 11kV | 28120 | 76 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | LID 207988 Replace Transformer Excluded OMS 1751207 | February | 2020 | 2020Q3 | 2020 | 261:81885 | 261:81885 | ZN00261/081885 | LAKE MACQUARIE | OH | Not Veg | 2020-02-24 | N | 370 | N | 4 | N | N | 1.1101 | 39.4971 | 20549.2666
[7 empty] | 4569 | 12804 | 1751540 | 2020-02-25 02:18 | 2020-02-25 03:17 | 59 | 11kV | 34731 | 684 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC3154 St Ives - Pnl. 16 tripped, reclosed & tripped on: O.C Abnormal: AB1853 Closed with REC231 Open Possum found adjacent to LB62190 See 1752953 1752954 | February | 2020 | 2020Q3 | 2020 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2020-02-25 | N | 50.7763 | N | 9 | N | N | 1.1101 | 39.4971 | 25380.3904
[7 empty] | 4455 | 11557 | 1751543 | 2020-02-25 03:30 | 2020-02-25 06:10 | 160 | 11kV | 31686 | 298 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1648 Enfield Panel 1 tripped on C phase IOC and Timed, EFI Signals: Zone Earth TX2 Group Earth, 11kV Trip, CB1 Open Cause: UG fault section of feeder from S/A@ b36263 to SW/B36264 NOTE: Panel 8 @ Enfield Tripped on Restoration due to NO EFI indication on Panel 8 See OMS 1755175 1755183 1755184 1751543 | February | 2020 | 2020Q3 | 2020 | ZN1648:PA1 | ZN4853:PA2 | ZN04853/000002 | BURWOOD | UG | Not Veg | 2020-02-25 | N | 106.3289 | N | 9 | N | N | 1.1101 | 39.4971 | 23155.1942
[7 empty] | 5159 | 18681 | 1751544 | 2020-02-25 03:54 | 2020-02-25 08:32 | 278 | 11kV | 14734 | 53 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 207992 C Phase DOLF : 31 Amp Excluded OMS 1751544 | February | 2020 | 2020Q3 | 2020 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Veg | 2020-02-25 | N | 278 | N | 9 | N | N | 1.1101 | 39.4971 | 10767.1726
[7 empty] | 3937 | 6283 | 1751623 | 2020-02-25 10:33 | 2020-02-25 11:26 | 53 | 11kV | 67619 | 1411 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S9700 Kirrawee Panel 24 tripped on Relays: Earth Fault, B phase timed Overcurrent, Timing relay, Lockout EFI and Fault Check Cause: UG cable fault from S9536 to S66086 - Plumbing Contractor hit Cable with back hoe outside No1 Magnolia Ave Kirrawee See OMS 1755331 1755332 1751623 1751629 | February | 2020 | 2020Q3 | 2020 | ZN9700:PA24 | ZN9700:PA24 | ZN09700/000024 | SUTHERLAND | UG | Not Veg | 2020-02-25 | N | 47.9227 | N | 9 | N | N | 1.1101 | 39.4971 | 49413.9708
[7 empty] | 3710 | 4041 | 1751592 | 2020-02-25 11:00 | 2020-02-25 12:40 | 100 | 11kV | 8400 | 84 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 207998 Wire on crossarm pole HW-70702. CC1: 22-"Refer to SOp" | February | 2020 | 2020Q3 | 2020 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2020-02-25 | N | 100 | N | 9 | N | N | 1.1101 | 39.4971 | 6138.4722
[7 empty] | 5178 | 18791 | 1751644 | 2020-02-25 11:00 | 2020-02-25 14:14 | 193.6833 | 11kV | 387.3667 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 208006 Single phase DOLF : 20 Amp sub 13228 isolated for LA replacement. replaced 20 amp LF 48165 | February | 2020 | 2020Q3 | 2020 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2020-02-25 | N | 193.6833 | N | 9 | N | N | 1.1101 | 39.4971 | 283.0761
[7 empty] | 3895 | 5919 | 1751721 | 2020-02-25 14:17 | 2020-02-25 15:23 | 66 | 11kV | 122826 | 1861 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Zn965 Pennant Hills -Pnl.43 tripped : SEL Pole snapped in section of 11kV form S4727 sw.B to LB564 tee S4099 (Hornsby Sewer Works) S4099 remained isolated and on other supply | February | 2020 | 2020Q3 | 2020 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2020-02-25 | N | 66 | N | 9 | N | N | 1.1101 | 39.4971 | 89757.618
[7 empty] | 4092 | 8087 | 1751667 | 2020-02-25 11:56 | 2020-02-26 10:05 | 1329 | 11kV | 147957 | 694 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S9700 Kirrawee Panel 11 tripped on Relays: B phase overcurrent Abnormal Switching: SW/B closed at S9811, SW/A open at S66086 Cause: UG cable damaged by contractor between S9794 to S66085 See OMS 1755084 1755085 1755086 1751677/1751676/ 1751667/1751629/1751623 | February | 2020 | 2020Q3 | 2020 | ZN9700:PA21 | ZN9700:PA21 | ZN09700/000021 | SUTHERLAND | UG | Not Veg | 2020-02-25 | N | 213.1945 | N | 9 | N | N | 1.1101 | 39.4971 | 108122.6116
[7 empty] | 5104 | 18253 | 1752096 | 2020-02-26 14:37 | 2020-02-26 15:45 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 208035 A Phase DOLF : 10 Amp | February | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-02-26 | N | 68 | N | 30 | Y | Y | 1.1101 | 39.4971 | 99.3848
[7 empty] | 4209 | 9365 | 1752282 | 2020-02-26 16:50 | 2020-02-26 18:00 | 70 | 11kV | 210 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 208053 A Phase DOLF : 10 Amp Excluded OMS 1752282 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-26 | N | 70 | N | 30 | Y | Y | 1.1101 | 39.4971 | 153.4618
[7 empty] | 3834 | 5385 | 1752174 | 2020-02-26 15:46 | 2020-02-26 18:01 | 135 | 11kV | 240165 | 1779 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208042 Earth Fault No Fault found | February | 2020 | 2020Q3 | 2020 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Veg | 2020-02-26 | N | 135 | N | 30 | Y | Y | 1.1101 | 39.4971 | 175505.4983
[7 empty] | 4767 | 14714 | 1752128 | 2020-02-26 15:28 | 2020-02-26 18:12 | 164 | 11kV | 191880 | 1170 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 208043 2 fault operations 3 Phase Overcurrent Disk insulator blown at JU-30867 | February | 2020 | 2020Q3 | 2020 | 204:82705 | 204:82705 | ZN00204/082705 | NEWCASTLE | OH | Not Veg | 2020-02-26 | N | 164 | N | 30 | Y | Y | 1.1101 | 39.4971 | 140220.2445
[7 empty] | 3394 | 925 | 1752878 | 2020-02-26 16:00 | 2020-02-26 18:20 | 140 | 11kV | 980 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208055 C Phase DOLF : 16 Amp | February | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-02-26 | N | 140 | N | 30 | Y | Y | 1.1101 | 39.4971 | 716.1551
[7 empty] | 4315 | 10342 | 1752320 | 2020-02-26 17:21 | 2020-02-26 19:30 | 129 | 11kV | 37038 | 672 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14143 SOMERSBY section of 11kV Panel 17 IR61921 Somersby Falls Vitsalo has tripped on OC (Scan Fail) from OMS Reports RE45202 Pacific Ashbrook0.2 tripped & reclosed on OC Cause: tree branch brought down OH in Ashbrooke st beyond CP40579 See 1752320,99 Ex 1752328,34 | February | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-02-26 | N | 55.1161 | N | 30 | Y | Y | 1.1101 | 39.4971 | 27066.278
[7 empty] | 4989 | 17045 | 1752176 | 2020-02-26 15:40 | 2020-02-26 19:41 | 241 | 11kV | 186157 | 1197 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 208044 A Phase Earth Fault Blown arrestor pole IU-70738 Excluded OMS 1752155 | February | 2020 | 2020Q3 | 2020 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2020-02-26 | N | 155.5196 | N | 30 | Y | Y | 1.1101 | 39.4971 | 136038.0449
[7 empty] | 4540 | 12473 | 1752203 | 2020-02-26 15:56 | 2020-02-26 20:10 | 254 | 11kV | 432308 | 1702 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208057 Earth Fault Hazard checked & Cleared 1752205 | February | 2020 | 2020Q3 | 2020 | 256:80646 | 256:80646 | ZN00256/080646 | NEWCASTLE | OH | Veg | 2020-02-26 | N | 254 | N | 30 | Y | Y | 1.1101 | 39.4971 | 315917.9355
[7 empty] | 5187 | 18862 | 1752436 | 2020-02-26 19:44 | 2020-02-26 20:14 | 30 | 11kV | 300 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12690 BERKELEY VALE 11kV CB Panel 11 fdr trippe don Relays: EF, EFI, Prot Trip Signals: 11kv trip, Tx13GE No field EFI operations Cause: UG Fault from Pa11 to S14772 | February | 2020 | 2020Q3 | 2020 | ZN12690:PA11 | ZN12690:PA11 | ZN12690/000011 | CENTRAL COAST | UG | Not Veg | 2020-02-26 | N | 30 | N | 30 | Y | Y | 1.1101 | 39.4971 | 219.2312
[7 empty] | 3845 | 5460 | 1752185 | 2020-02-26 15:56 | 2020-02-26 20:27 | 271 | 11kV | 328181 | 1211 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208056 Overcurrent No Fault found | February | 2020 | 2020Q3 | 2020 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Veg | 2020-02-26 | N | 271 | N | 30 | Y | Y | 1.1101 | 39.4971 | 239824.9951
[7 empty] | 4054 | 7623 | 1751862 | 2020-02-26 03:52 | 2020-02-26 20:40 | 1008 | 11kV | 159406 | 904 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn15014 Mona Vale - Pnl.22 tripped on: A & B phase OC Car hit pole near 1621 Pittwater Rd. PT15955 Dist #1 restored via LV // See 1757183 1757184 1757185 | February | 2020 | 2020Q3 | 2020 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Not Veg | 2020-02-26 | N | 176.3341 | N | 30 | Y | Y | 1.1101 | 39.4971 | 116489.2031
[7 empty] | 4251 | 9798 | 1752796 | 2020-02-26 15:53 | 2020-02-26 20:53 | 300 | 33kV Distribution | 6600 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208045 2 fault operations 3 phase Overcurrent DOP patrol nothing found, detailed patrol required. Sw 43064 was feed from Fdr 80500 as ABS 49576 N/O Sw 80500 A prot = ABC O/C, Multi trip . B prot - %!ABC Sw 90700 = A & C O/C | February | 2020 | 2020Q3 | 2020 | 417:80500 | 417:80500 | ZN00417/080500 | NEWCASTLE | OH | Veg | 2020-02-26 | N | 300 | N | 30 | Y | Y | 1.1101 | 39.4971 | 4823.0853
[7 empty] | 3502 | 2038 | 1752165 | 2020-02-26 15:39 | 2020-02-26 21:00 | 321 | 11kV | 171084 | 909 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 208047 2 fault operations C Phase Overcurrent Sw 80791 = 51C Repaired wires down pole JT-70189 Excluded OMS 1752169 | February | 2020 | 2020Q3 | 2020 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Not Veg | 2020-02-26 | N | 188.2112 | N | 30 | Y | Y | 1.1101 | 39.4971 | 125023.1411
[7 empty] | 4252 | 9817 | 1752183 | 2020-02-26 15:53 | 2020-02-26 21:11 | 318 | 11kV | 170177 | 667 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 208046 2 fault operations C phase Overcurrent; Earth Fault pole JU43790 11kV main on ground, repairs complete Timed E/F, C phase O/C Excluded OMS 1752183 | February | 2020 | 2020Q3 | 2020 | 205:12203 | 205:12203 | ZN00205/012203 | NEWCASTLE | OH | Not Veg | 2020-02-26 | N | 255.1379 | N | 30 | Y | Y | 1.1101 | 39.4971 | 124360.3322
[7 empty] | 3460 | 1599 | 1752065 | 2020-02-26 13:48 | 2020-02-26 22:10 | 502 | 11kV | 69276 | 138 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208025 Overcurrent | February | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-02-26 | N | 502 | N | 30 | Y | Y | 1.1101 | 39.4971 | 50624.8575
[7 empty] | 5218 | 19217 | 1752161 | 2020-02-26 15:42 | 2020-02-26 22:29 | 407 | 11kV | 495627 | 1497 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 208052 Mains wrapped together at pole IU-60117, seperated conductors, Daylight inspection required Excluded OMS 1752161 | February | 2020 | 2020Q3 | 2020 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2020-02-26 | N | 331.0802 | N | 30 | Y | Y | 1.1101 | 39.4971 | 362189.5931
[7 empty] | 4418 | 11234 | 1752241 | 2020-02-26 16:25 | 2020-02-26 22:50 | 385 | 11kV | 2695 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 208058 ? Phase DOLF : 40 Amp Excluded OMS 1752241, 1752279 | February | 2020 | 2020Q3 | 2020 | 256:80652 | 256:80652 | ZN00256/080652 | NEWCASTLE | OH | Veg | 2020-02-26 | N | 385 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1969.4265
[7 empty] | 3600 | 2791 | 1752152 | 2020-02-26 15:40 | 2020-02-26 23:17 | 457 | 11kV | 629073 | 1389 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208060 2 fault operation Earth Fault | February | 2020 | 2020Q3 | 2020 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | OH | Veg | 2020-02-26 | N | 452.8963 | N | 30 | Y | Y | 1.1101 | 39.4971 | 459707.9939
[7 empty] | 5009 | 17294 | 1752019 | 2020-02-26 12:00 | 2020-02-26 23:40 | 700 | 11kV | 66825 | 1499 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208023 Fdr interrupted due to pole 33kV fdr on fire at pole HR-50495. See LID # 208022. Excluded OMS No. 1752019, 1752062 | February | 2020 | 2020Q3 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2020-02-26 | N | 44.5797 | N | 30 | Y | Y | 1.1101 | 39.4971 | 48833.739
[7 empty] | 3732 | 4293 | 1752311 | 2020-02-26 17:17 | 2020-02-26 23:40 | 383 | 11kV | 1532 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 208066 A Phase DOLF : 10 Amp Excluded OMS 1752311 | February | 2020 | 2020Q3 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2020-02-26 | N | 383 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1119.5404
[7 empty] | 3434 | 1362 | 1752189 | 2020-02-26 15:53 | 2020-02-27 00:30 | 517 | 11kV | 333239 | 879 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 208061 Earth Fault Blown arrestor pole JU-13368 | February | 2020 | 2020Q3 | 2020 | 210:83474 | 210:83474 | ZN00210/083474 | NEWCASTLE | OH | Not Veg | 2020-02-26 | N | 379.1115 | N | 30 | Y | Y | 1.1101 | 39.4971 | 243521.2323
[7 empty] | 3437 | 1369 | 1752414 | 2020-02-26 19:04 | 2020-02-27 02:00 | 416 | 11kV | 1664 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 208073 A Phase DOLF : 16 Amp Excluded OMS 1752414 | February | 2020 | 2020Q3 | 2020 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2020-02-26 | N | 416 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1216.0021
[7 empty] | 5054 | 17860 | 1752250 | 2020-02-26 16:31 | 2020-02-27 02:15 | 584 | 11kV | 64392 | 177 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Electrical Storm | N | LID 208059 Lightning hit pole JU-51267. Blown tapping on 11kV Excluded OMS 1752250 | February | 2020 | 2020Q3 | 2020 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Not Veg | 2020-02-26 | N | 363.7966 | N | 30 | Y | Y | 1.1101 | 39.4971 | 47055.7744
[7 empty] | 5305 | 19929 | 1754539 | 2020-02-26 17:06 | 2020-02-27 03:40 | 634 | 11kV | 1268 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 208161 see previous unplanned outage 208160. Isolated subs to extend outage area to replace 11kV Sw 35541 | February | 2020 | 2020Q3 | 2020 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2020-02-26 | N | 634 | N | 30 | Y | Y | 1.1101 | 39.4971 | 926.617
[7 empty] | 4941 | 16513 | 1752598 | 2020-02-26 19:50 | 2020-02-27 05:00 | 550 | 11kV | 237015 | 1019 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN10999 Kogarah Panel 7 tripped on Relays: Overcurrent ABC 51 ABC, Reclose Lockout, Earth Fault Check, EFI Wind has blown sheet metal into CP61465 causing wire to come down, also HV into LV PT61736 Dist 1 Durham St corner of Botany St 1754355 1754357 1754358 1754359 1752439 1752450 1752455 1752458 | February | 2020 | 2020Q3 | 2020 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | GEORGES RIVER | OH | Veg | 2020-02-26 | N | 232.5957 | N | 30 | Y | Y | 1.1101 | 39.4971 | 173203.5712
[7 empty] | 3699 | 3905 | 1752526 | 2020-02-26 20:40 | 2020-02-27 08:20 | 700 | 11kV | 2100 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 208112 Single phase DOLF : 10 Amp Excluded OMS 1752526 | February | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2020-02-26 | N | 700 | N | 30 | Y | Y | 1.1101 | 39.4971 | 1534.6181
[7 empty] | 3560 | 2578 | 1752626 | 2020-02-27 06:43 | 2020-02-27 10:15 | 212 | 11kV | 424 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 208124 A & B Phase DOLF 10 Amp Excluded OMS 1752626 | February | 2020 | 2020Q3 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-02-27 | N | 212 | N | 6 | N | N | 1.1101 | 39.4971 | 309.8467
[7 empty] | 3359 | 632 | 1752738 | 2020-02-27 10:02 | 2020-02-27 11:45 | 103 | 11kV | 206 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 208130 Single phase DOLF : 10 Amp Excluded OMS 1752738 | February | 2020 | 2020Q3 | 2020 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2020-02-27 | N | 103 | N | 6 | N | N | 1.1101 | 39.4971 | 150.5387
[7 empty] | 3713 | 4066 | 1752806 | 2020-02-27 11:45 | 2020-02-27 12:58 | 73 | 11kV | 1095 | 15 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 208145 subs 65474 & 26042 isolated to make 33kV repairs at pole IU-41267 see report # 208138 Excluded oms 1752806 & 1752809 | February | 2020 | 2020Q3 | 2020 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2020-02-27 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 800.1937
[7 empty] | 5286 | 19748 | 1752618 | 2020-02-26 14:22 | 2020-02-27 13:05 | 1363 | 11kV | 109778 | 272 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 208029 1 Fault operation Sensitive Earth Fault Mains down pole FU-33131 Excluded OMS 1752083 | February | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-02-26 | N | 403.5956 | N | 30 | Y | Y | 1.1101 | 39.4971 | 80222.5245
[7 empty] | 4517 | 12222 | 1752098 | 2020-02-26 14:39 | 2020-02-27 15:45 | 1506 | 11kV | 9115 | 61 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 208036 Sensitive Earth Fault Blown transformer sub 62212 Excluded 1752098 | February | 2020 | 2020Q3 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2020-02-26 | N | 149.4262 | N | 30 | Y | Y | 1.1101 | 39.4971 | 6660.9732
[7 empty] | 5090 | 18169 | 1752180 | 2020-02-26 15:54 | 2020-02-27 17:30 | 1536 | 11kV | 508246 | 1570 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 208075 2 fault operations Earth Fault 11Kv main into LV neutral' repairs to 11kV complete, Emso still to check customer switch boards, LVF left open sub 4608. On 11kV restoration found sub 4608 Tx faulty requires replacement. Excluded OMS 1752180 | February | 2020 | 2020Q3 | 2020 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2020-02-26 | N | 323.7236 | N | 30 | Y | Y | 1.1101 | 39.4971 | 371411.1861
[7 empty] | 4640 | 13552 | 1752608 | 2020-02-27 02:31 | 2020-02-27 17:35 | 904 | 11kV | 32544 | 36 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 208148 B Phase Fuse : 63 Amp sub isolated to replace HV fuse Excluded oms 1752608 & 1752905 | February | 2020 | 2020Q3 | 2020 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | UG | Not Veg | 2020-02-27 | N | 904 | N | 6 | N | N | 1.1101 | 39.4971 | 23782.1953
[7 empty] | 4723 | 14308 | 1752691 | 2020-02-27 09:08 | 2020-02-27 17:59 | 530.7 | 11kV | 4776.3 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 208154 A Phase DOLF : 40 Amp CC1: 23-"Mains Required" FRC1: 329-"High Voltage Fuse - Requires replacement" | February | 2020 | 2020Q3 | 2020 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2020-02-27 | N | 530.7 | N | 6 | N | N | 1.1101 | 39.4971 | 3490.3792
[7 empty] | 4779 | 14823 | 1751854 | 2020-02-25 23:31 | 2020-02-27 18:15 | 2564 | 11kV | 415528 | 477 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.18 tripped on: O/C and E/F Abnormal: S3223 Sw/B closed with S935 Sw/B Open. S7468 Sw/A Open with Sw/F Closed (DMA UG Cable) UG cable fault in front line section of feeder. Lengthy outage for S935 due to existing DMA See 1757285 1757286 | February | 2020 | 2020Q3 | 2020 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2020-02-25 | N | 871.1279 | N | 9 | N | N | 1.1101 | 39.4971 | 303655.6064
[7 empty] | 3665 | 3565 | 1752980 | 2020-02-27 17:01 | 2020-02-27 19:05 | 124 | 11kV | 248 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208158 A Phase DOLF : 10 Amp Excluded OMS 1752980 | February | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-02-27 | N | 124 | N | 6 | N | N | 1.1101 | 39.4971 | 181.2311
[7 empty] | 4869 | 15694 | 1752307 | 2020-02-26 16:06 | 2020-02-27 21:30 | 1764 | 11kV | 22467 | 46 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 208160 11Kv OHM down pole JS-80453 to JS-80455, faulty Sw 35541 & private switch gear Excluded OMS1752200. | February | 2020 | 2020Q3 | 2020 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2020-02-26 | N | 488.413 | N | 30 | Y | Y | 1.1101 | 39.4971 | 16418.2209
[7 empty] | 3429 | 1333 | 1753043 | 2020-02-28 07:00 | 2020-02-28 07:40 | 40 | 11kV | 47800 | 1195 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208162 2 fault operations A & B Phase Overcurrent Bird on mains pole IV-90139 | February | 2020 | 2020Q3 | 2020 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2020-02-28 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 34930.8301
[7 empty] | 4210 | 9385 | 1754450 | 2020-02-28 08:30 | 2020-02-28 09:00 | 30 | 11kV | 60 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 208163 Single Phase DOLF : 10 Amp Staff found LF blown. | February | 2020 | 2020Q3 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-02-28 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 4545 | 12505 | 1753230 | 2020-02-28 15:25 | 2020-02-28 18:50 | 205 | 11kV | 410 | 2 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 208174 Single phase DOLF : 10 Amp - Bird on arrestor removed and dolf replaced Excluded OMS 1753230 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-02-28 | N | 205 | N | 4 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 3823 | 5340 | 1753307 | 2020-02-28 23:41 | 2020-02-29 01:03 | 82 | 11kV | 181336 | 2434 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.25 tripped on C phase IOC and OC UG cable fault in front line section of UG cable | February | 2020 | 2020Q3 | 2020 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-02-28 | N | 74.5012 | N | 4 | N | N | 1.1101 | 39.4971 | 132515.0003
[7 empty] | 5192 | 18886 | 1753309 | 2020-02-29 01:34 | 2020-02-29 04:00 | 146 | 11kV | 21334 | 147 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn167 Auburn - Pnl.12 tripped on: Earth Fault UG cable fault between S5717, S6583 and S8296 See 1757239 1757240 | February | 2020 | 2020Q3 | 2020 | ZN167:PA12 | ZN167:PA12 | ZN00167/000012 | CUMBERLAND | UG | Not Veg | 2020-02-29 | N | 145.1293 | N | 5 | N | N | 1.1101 | 39.4971 | 15590.258
[7 empty] | 4014 | 7162 | 1753320 | 2020-02-29 07:17 | 2020-02-29 08:50 | 93 | 11kV | 372 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse Assembly | Unplanned | No Weather Impact | N | LID 208176 A Phase A phase LVF fell open, contacts cleaned & reset. Excluded oms 1753320 | February | 2020 | 2020Q3 | 2020 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2020-02-29 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 4932 | 16418 | 1753389 | 2020-02-29 13:32 | 2020-02-29 13:36 | 4 | 11kV | 5160 | 1290 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn15014 Mona vale - Pnl.7 tripped on: B phase O/C Abnormal: USL24463 Open with S16893 Sw/B Closed (DMA) After repairs to defective UGOH, DOp energised section and the same UGOH failed. | February | 2020 | 2020Q3 | 2020 | ZN15014:PA7 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | Unknown | Unknown | 2020-02-29 | N | 4 | N | 5 | N | N | 1.1101 | 39.4971 | 3770.7758
[7 empty] | 4878 | 15756 | 1753402 | 2020-02-29 15:20 | 2020-02-29 16:30 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 208179 A Phase DOLF : 10 Amp Excluded OMS 1753402 | February | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-02-29 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 3932 | 6183 | 1753430 | 2020-02-29 21:00 | 2020-02-29 23:05 | 125 | 11kV | 23927 | 1401 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 208180 burnt up tapping ABS 74910 section isolated for repair Excluded oms 1753430 | February | 2020 | 2020Q3 | 2020 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2020-02-29 | N | 17.0785 | N | 5 | N | N | 1.1101 | 39.4971 | 17485.1459
[7 empty] | 3789 | 4930 | 1753554 | 2020-03-01 20:08 | 2020-03-01 21:24 | 76 | 11kV | 219868 | 2893 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10995 Riverwood - pnl.7 tripped on: A Phase timed O/C Abnormal: S10236 Sw/B Closed with S10717 Sw/A Open Bat across 2 phases of 11kV near PT10518 See 1759035 1759307 | March | 2020 | 2020Q3 | 2020 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2020-03-01 | N | 76 | N | 1 | N | N | 1.1101 | 39.4971 | 160673.0494
[7 empty] | 4785 | 14843 | 1753607 | 2020-03-02 01:01 | 2020-03-02 02:01 | 60 | 11kV | 73080 | 1218 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S12690 Berkeley Vale Panel 19 has tripped Signals 11kV Trip Relays: CB19 Right A and B phase OC and protection trip timer Cause Not ascertained | March | 2020 | 2020Q3 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2020-03-02 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 53404.7085
[7 empty] | 3644 | 3295 | 1753809 | 2020-03-02 13:55 | 2020-03-02 14:52 | 57 | 11kV | 684 | 12 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208190 Wire off pin at pole AI-80065 | March | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-03-02 | N | 57 | N | 10 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 4257 | 9874 | 1762996 | 2020-03-02 17:23 | 2020-03-02 18:45 | 82 | 11kV | 69864 | 852 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14144 Wamberal Panel 4 has tripped , reclosed tripped and locked out on Signals - 11kV trip Relays: IOC, EFI, Recloser Lockout Cause: Palm Tree has fallen on HV mains outside 29 Cheryl Ave Terrigal See OMS 1762996 1762997 1754011 | March | 2020 | 2020Q3 | 2020 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2020-03-02 | N | 82 | N | 10 | N | N | 1.1101 | 39.4971 | 51054.5506
[7 empty] | 5340 | 20299 | 1754049 | 2020-03-02 15:20 | 2020-03-02 18:50 | 210 | 11kV | 464102 | 3566 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Zn10994 mortdale - Pnl.12 tripped, reclosed & locked out on: A Phase IOC Abnormal: S10425 Sw/B Open with AB31292 Closed (DMA) UGOH flashed over between S10018 Sw/A, AB31296 and LB63034 tee PT61898 See 1759043 1759044 | March | 2020 | 2020Q3 | 2020 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | Unknown | Unknown | 2020-03-02 | N | 130.1464 | N | 10 | N | N | 1.1101 | 39.4971 | 339152.0529
[7 empty] | 4510 | 12152 | 1753981 | 2020-03-02 17:06 | 2020-03-02 21:45 | 279 | 11kV | 84430 | 646 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12640 Umina - Panel 1 tripped on Signals: 11kV trip Relays: E/F, IOC, L/O and efi Cause: Tree branch brought down HV into LV near pole WW1031. Emso required to check installations and give clearance to energise.All boards checked in area, no visible damage found. Dop advised, and has now restored supply. See OMS 1763259 1763260 1763261 1753981 | March | 2020 | 2020Q3 | 2020 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Veg | 2020-03-02 | N | 130.6966 | N | 10 | N | N | 1.1101 | 39.4971 | 61698.9537
[7 empty] | 4256 | 9847 | 1754054 | 2020-03-02 17:52 | 2020-03-02 22:21 | 269 | 11kV | 20982 | 78 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | Ex Engadine Zn Pnl.3 - AB35720 contact went open circuit | March | 2020 | 2020Q3 | 2020 | ZN9245:PA3 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2020-03-02 | N | 269 | N | 10 | N | N | 1.1101 | 39.4971 | 15333.0267
[7 empty] | 3994 | 6928 | 1754219 | 2020-03-02 22:56 | 2020-03-03 00:45 | 109 | 11kV | 1090 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Wind Strong | N | 11kV 20K centre phase HDO operated at PT18484 Pacific Ashbrook 1.2 Caused: Fise failure @ PT18484 | March | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-03-02 | N | 109 | N | 10 | N | N | 1.1101 | 39.4971 | 796.5399
[7 empty] | 5223 | 19270 | 1754140 | 2020-03-02 18:03 | 2020-03-03 11:56 | 1073 | 11kV | 192003 | 197 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Recloser CP45013 Gunderman has tripped and reclosed on Relays: OC trip, L/O Cause: HV OH down near pole BF73 at PT47195 Low Volts brown out. See OMS 1763938 1763939 1763941 1763942 1754230 1754140 1754070 | March | 2020 | 2020Q3 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-03-02 | N | 974.6345 | N | 10 | N | N | 1.1101 | 39.4971 | 140310.1293
[7 empty] | 3520 | 2195 | 1754234 | 2020-03-03 05:49 | 2020-03-03 12:35 | 406 | 11kV | 109205 | 772 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 208209 2 fault operations a phase Overcurrent, Earth Fault X arm fire KU-10928 Excluded OMS 1754302 | March | 2020 | 2020Q3 | 2020 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2020-03-03 | N | 141.4573 | N | 6 | N | N | 1.1101 | 39.4971 | 79803.793
[7 empty] | 4791 | 14954 | 1754134 | 2020-03-02 19:12 | 2020-03-03 13:15 | 1083 | 11kV | 32499 | 157 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP45071 Central mangrove Tripped, reclosed tripped and locked out on Relays: OC trip, Lockout Cause: 11kV Feeder from Lk41190 to AB43582 tee PT12308 and PT11248 Isolated See OMS 1763943 1763944 1763945 1763946 1763948 1754225 1754223 | March | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2020-03-02 | N | 207 | N | 10 | N | N | 1.1101 | 39.4971 | 23749.3106
[7 empty] | 3518 | 2184 | 1754620 | 2020-03-03 16:48 | 2020-03-03 17:01 | 13 | 11kV | 11869 | 913 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.1 tripped on: A phase OC Abnormal: S9413 Sw/D closed with S9411 Sw/A Open (DMA) Tripped on energising when returning DMA UG cable fault to service between Caringbah Zn Pnl.8 and S9411 via S9017 | March | 2020 | 2020Q3 | 2020 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2020-03-03 | N | 13 | N | 6 | N | N | 1.1101 | 39.4971 | 8673.5151
[7 empty] | 4947 | 16577 | 1754593 | 2020-03-03 12:01 | 2020-03-03 19:35 | 454 | 11kV | 2724 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 208218 Cracked Insulator at P. FD-30148 also refer to Trip and Reclose OMS 1762087 @ 03/03/2020 12:00:00 | March | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2020-03-03 | N | 454 | N | 6 | N | N | 1.1101 | 39.4971 | 1990.6189
[7 empty] | 4009 | 7097 | 1754762 | 2020-03-03 23:50 | 2020-03-04 00:45 | 55 | 11kV | 3740 | 68 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 208222 Sub interrupted to replace LA Excluded OMS 1754762 1754791 | March | 2020 | 2020Q3 | 2020 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2020-03-03 | N | 55 | N | 6 | N | N | 1.1101 | 39.4971 | 2733.0817
[7 empty] | 3322 | 321 | 1754319 | 2020-03-03 08:52 | 2020-03-04 01:30 | 998 | 11kV | 103767 | 229 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 208213 Broken x arm sub 10819 section isolated for repairs. Excluded OMS 1754319 | March | 2020 | 2020Q3 | 2020 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2020-03-03 | N | 453.131 | N | 6 | N | N | 1.1101 | 39.4971 | 75829.863
[7 empty] | 4742 | 14449 | 1754815 | 2020-03-04 02:08 | 2020-03-04 03:33 | 85 | 11kV | 73695 | 867 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14143 Somersby Falls has tripped on Signals: 11kV trip Relays: B and C phase IOC Field EFI's Cause: fallen Tree has clashed 11kV Mains | March | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-03-04 | N | 85 | N | 9 | N | N | 1.1101 | 39.4971 | 53854.1324
[7 empty] | 4657 | 13671 | 1754843 | 2020-03-04 06:14 | 2020-03-04 07:30 | 76 | 11kV | 9956 | 131 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | @ ZN15013 Terrey Hills - ex Panel 4 "S16440 Aumuna Mona" 11kV Recloser 21350 Booralie Kalgoa tripped, re-closed and tripped Relays: OC Trip Signals: OC trip, CP.21350 open, lockout, Voltage dead EFIs | March | 2020 | 2020Q3 | 2020 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2020-03-04 | N | 76 | N | 9 | N | N | 1.1101 | 39.4971 | 7275.5511
[7 empty] | 3700 | 3922 | 1754013 | 2020-03-02 17:25 | 2020-03-04 08:51 | 2366 | 11kV | 1636740 | 705 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | 11kV Recloser 3282 Alberta Avenue Ex Berowra Panel 11 'Brooklyn' tripped Tree on 11kV OH between AB2336 LK2337. From Re3282 to AB2336 restored on 1754013 AB2336 to LB 2423 restored on 1754193 ABNORMAL SWITCHING: LB 2423 & AB1034 open, SRA closed | March | 2020 | 2020Q3 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2020-03-02 | N | 2321.617 | N | 10 | N | N | 1.1101 | 39.4971 | 1196081.3163
[7 empty] | 3758 | 4666 | 1754840 | 2020-03-04 06:33 | 2020-03-04 09:40 | 187 | 11kV | 243736 | 2015 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | At Zn 14892 Charmhaven Panel 16 has tripped. Signals: 11kV trip Relays: SEL, EF Field EFI's: nil Surge arrestor at PT11625 Kallaroo Liamena has faield and caught fire. | March | 2020 | 2020Q3 | 2020 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2020-03-04 | N | 120.9608 | N | 9 | N | N | 1.1101 | 39.4971 | 178115.0798
[7 empty] | 3755 | 4605 | 1755013 | 2020-03-04 11:16 | 2020-03-04 13:20 | 124 | 11kV | 117511.4667 | 1462 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN12610 Long Jetty ex Panel 10, Recloser 61729 The Entrance Cresthaven has tripped. Relays: OC trip and LO Original Fault causing low volts HR bond on LB 42922. Tail on LB 42954 has come loose and flashed over to the next phase when Dop was opening LB 42954, causing Rec to trip. See 1755146, 1755089, 1759063 | March | 2020 | 2020Q3 | 2020 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2020-03-04 | N | 80.3772 | N | 9 | N | N | 1.1101 | 39.4971 | 85873.9138
[7 empty] | 5219 | 19229 | 1756839 | 2020-03-04 13:05 | 2020-03-04 13:58 | 53 | 11kV | 106 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 208237 Single phase DOLF : 10 Amp Reported by customer to depot. | March | 2020 | 2020Q3 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-03-04 | N | 53 | N | 9 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 4374 | 10805 | 1757750 | 2020-03-03 20:12 | 2020-03-04 14:45 | 1113 | 11kV | 526666 | 1277 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | ZN1290 Leightonfield - Panel 9 Tripped, reclosed, tripped and locked out Relays: A phase OC + Earth Fault, EFI OH wires down - Campbell Hill Rd and Gurney Rd, Chester Hill See 1757750, 1757752, 1757753, 1757754 | March | 2020 | 2020Q3 | 2020 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-03-03 | N | 412.4244 | N | 6 | N | N | 1.1101 | 39.4971 | 384871.9788
[7 empty] | 5094 | 18186 | 1755306 | 2020-03-04 10:36 | 2020-03-04 18:30 | 474 | 11kV | 999 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 208241 Single phase Faulty 11kV links 6L701 causing fluctuating volts. Operator advised no protection operation. Excluded OMS No. 1755055 + 1755306 | March | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-03-04 | N | 124.875 | N | 9 | N | N | 1.1101 | 39.4971 | 730.0397
[7 empty] | 4710 | 14205 | 1757100 | 2020-03-04 16:50 | 2020-03-04 19:45 | 175 | 11kV | 107495 | 994 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn 3154 St Ives, 11kV Panel 24 has tripped on: Relays- A phase OC and IOC, Reclose and lock out, EFI Signals- 11kV trip, Tx3 group earth Field EFIs- S4300, 4265, 4733 EFIs at 77658, 50052 did not operate EXISTING DMA from S35027 to S8273 Closed at S5389. 11kV Feeder from S4733 Sw/B to LB 2089 tee PT 1391 has an UG Fault. PT 1391 restored via LV// Event ID 8074. See 1757100, 1757101, 1757104, 175106 | March | 2020 | 2020Q3 | 2020 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | UG | Not Veg | 2020-03-04 | N | 108.1439 | N | 9 | N | N | 1.1101 | 39.4971 | 78554.1754
[7 empty] | 5030 | 17565 | 1755058 | 2020-03-04 10:41 | 2020-03-04 20:30 | 589 | 11kV | 70091 | 119 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Light | N | S4571 Waterloo Shipway - 11kV/415V TX - Dist.1 and 2 At S4571 Waterloo Shipway when restoring dist.1 dop discovered low volts and found the associated TX had tripped. LV// Event ID 8075. | March | 2020 | 2020Q3 | 2020 | ZN2635:PA35 | ZN2635:PA35 | ZN02635/000035 | RYDE | UG | Not Veg | 2020-03-04 | N | 589 | N | 9 | N | N | 1.1101 | 39.4971 | 51220.4355
[7 empty] | 4432 | 11320 | 1755385 | 2020-03-04 19:28 | 2020-03-04 22:10 | 162 | 11kV | 108424 | 1717 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 208242 Tree on 11kV OHM at IV10948 Protection details required Excluded OMS 1755385 1755387 | March | 2020 | 2020Q3 | 2020 | 270:83590 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2020-03-04 | N | 63.1474 | N | 9 | N | N | 1.1101 | 39.4971 | 79233.0612
[7 empty] | 3547 | 2447 | 1755421 | 2020-03-05 03:08 | 2020-03-05 06:55 | 227 | 11kV | 204013 | 1774 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn12600 Lisarow Panel 3 tripped on Signals A phase OC+ Earth Fault, SEF and EFI Abnormal Switching: CP50706 Closed, S14262 SW/A Open Cauuse: Feeder Patrolled cause not ascertained See OMS 1763732 1763733 1763734 1755421 | March | 2020 | 2020Q3 | 2020 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2020-03-05 | N | 115.0017 | N | 9 | N | N | 1.1101 | 39.4971 | 149086.683
[7 empty] | 4793 | 14967 | 1755427 | 2020-03-05 05:30 | 2020-03-05 08:00 | 150 | 11kV | 83374 | 809 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North Panel 17 Tripped on Signals 11kv trip Relays: 50T BC, Trip, UF and EFI Abnormal Switching: LB61274 Closed - S65545 SW Open Cause: Possum on LB61274 See OMS 1763728 1763729 1755427 | March | 2020 | 2020Q3 | 2020 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2020-03-05 | N | 103.0581 | N | 9 | N | N | 1.1101 | 39.4971 | 60927.2601
[7 empty] | 5005 | 17266 | 1755418 | 2020-03-05 00:48 | 2020-03-05 09:49 | 541 | 11kV | 2164 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV recloser CP26228 Valley Rd tripped, reclosed tripped and locked out on Relays: OC trip,IOC trip and Lockout Cause: Tree branh on OH mains near PT16351 | March | 2020 | 2020Q3 | 2020 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2020-03-05 | N | 541 | N | 9 | N | N | 1.1101 | 39.4971 | 1581.3874
[7 empty] | 4222 | 9496 | 1755541 | 2020-03-05 11:13 | 2020-03-05 11:55 | 42 | 11kV | 51324 | 1222 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 208250 3 fault operations A Phase Overcurrent FDR TRIPPED & RECLOSED TWICE BEFORE LOCKING OUT ,see Emergency switching. Excluded OMS REPORT NO 1755542. | March | 2020 | 2020Q3 | 2020 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Veg | 2020-03-05 | N | 42 | N | 9 | N | N | 1.1101 | 39.4971 | 37506.0654
[7 empty] | 4928 | 16399 | 1755592 | 2020-03-05 13:12 | 2020-03-05 14:30 | 78 | 11kV | 63685 | 868 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | LID 208256 No protection involved. burnt off tapping at UGOH pole IU-67004. feeder switched around & sub 61214 interconnected. Excluded oms report no 1755592. | March | 2020 | 2020Q3 | 2020 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Not Veg | 2020-03-05 | N | 73.3698 | N | 9 | N | N | 1.1101 | 39.4971 | 46539.1196
[7 empty] | 4117 | 8351 | 1755516 | 2020-03-05 10:26 | 2020-03-05 14:50 | 264 | 11kV | 3712 | 15 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 208254 loose burnt up llc at sub 51816 Excluded oms 1755516 | March | 2020 | 2020Q3 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-03-05 | N | 247.4667 | N | 9 | N | N | 1.1101 | 39.4971 | 2712.6201
[7 empty] | 4784 | 14842 | 1755526 | 2020-03-05 10:48 | 2020-03-05 17:00 | 372 | 11kV | 142776 | 1218 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn12690 Berkeley Vale Panel 19L tripped on SEF Cause: Suspect Bond /connection on section of feeder between S18559 to AB44724 to LB 43329 See OMS 1763245 1763247 1755526 1755582 | March | 2020 | 2020Q3 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2020-03-05 | N | 117.2217 | N | 9 | N | N | 1.1101 | 39.4971 | 104336.4896
[7 empty] | 4179 | 9180 | 1755726 | 2020-03-05 16:34 | 2020-03-05 17:55 | 81 | 11kV | 81 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 208260 A Phase DOLF : 63 Amp Excluded OMS 1755726 | March | 2020 | 2020Q3 | 2020 |  |  |  | UPPER HUNTER | OH | Veg | 2020-03-05 | N | 81 | N | 9 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 5075 | 18063 | 1755669 | 2020-03-05 15:24 | 2020-03-05 20:19 | 295 | 11kV | 214941 | 1889 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 208257 2 fault operations A & C Phase Overcurrent Fault Current: Aph - 1526A, Bph - 101A, Cph - 1461A Excluded OMS No. 1755669 | March | 2020 | 2020Q3 | 2020 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2020-03-05 | N | 113.7856 | N | 9 | N | N | 1.1101 | 39.4971 | 157072.5431
[7 empty] | 4194 | 9281 | 1755826 | 2020-03-06 01:33 | 2020-03-06 02:28 | 55 | 11kV | 1540 | 28 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At ZN2196 Milperra ex Panel 5, 11kV feeder was interrupted due to fire at S6358 Cook Park. Isolated between S8239 Forest Monie to S78176 Maclaurin Broe tee S6358 Cook Park. See 1760315, 16, 17 | March | 2020 | 2020Q3 | 2020 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-03-06 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 1125.3866
[7 empty] | 3741 | 4395 | 1755830 | 2020-03-06 02:38 | 2020-03-06 13:35 | 657 | 11kV | 60715 | 467 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12660 Woy Woy, 11kV Panel 6 has tripped, reclosed and locked out on: Relays: C Phase IOC, C Phase OC, Timing and lockout Signals: 11kV trip Field EFIs: NA Tree has fallen on mains outside 225 Steyne Rd Saratoga and damaged crossarm and broken ties off insulators. Feeder is isolated from LB 42919 to S18564 tee PT 12674. 415v Dist 2 from PT 12297 interrupted at 0700 hrs to make repairs to HV above. 415V Dist 2 from PT 12674 restore via LV//. See 1760380, 1760381, 1760382, 1755854 | March | 2020 | 2020Q3 | 2020 | ZN12660:PA6 | ZN12660:PA6 | ZN12660/000006 | CENTRAL COAST | OH | Veg | 2020-03-06 | N | 130.0107 | N | 5 | N | N | 1.1101 | 39.4971 | 44368.7312
[7 empty] | 3566 | 2614 | 1757064 | 2020-03-06 16:00 | 2020-03-06 18:30 | 150 | 11kV | 750 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208274 Isolated to repair under AP | March | 2020 | 2020Q3 | 2020 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2020-03-06 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 4875 | 15740 | 1756233 | 2020-03-06 20:24 | 2020-03-06 21:25 | 61 | 11kV | 5429 | 89 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 208276 A Phase DOLF : 40 Amp Dead Possum Excluded OMS 1756233 CC1: 22-"Refer to SOp" | March | 2020 | 2020Q3 | 2020 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2020-03-06 | N | 61 | N | 5 | N | N | 1.1101 | 39.4971 | 3967.3531
[7 empty] | 5235 | 19364 | 1756241 | 2020-03-06 22:00 | 2020-03-07 00:55 | 175 | 11kV | 73215 | 498 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 208278 1 fault operation Blown LA at UGOH to sub 24107, Replaced under AP Excluded oms 1756241 | March | 2020 | 2020Q3 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2020-03-06 | N | 147.0181 | N | 5 | N | N | 1.1101 | 39.4971 | 53503.3625
[7 empty] | 3702 | 3982 | 1756259 | 2020-03-07 07:44 | 2020-03-07 09:40 | 116 | 11kV | 464 | 4 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 208287 Single phase DOLF : 5 Amp Dead possum found at sub. Excluded OMS No. 1756259 | March | 2020 | 2020Q3 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-03-07 | N | 116 | N | 3 | N | N | 1.1101 | 39.4971 | 339.0775
[7 empty] | 4977 | 16899 | 1756262 | 2020-03-07 08:32 | 2020-03-07 11:25 | 173 | 11kV | 519 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208288 A Phase DOLF : 31 Amp Excluded OMS 1756262 | March | 2020 | 2020Q3 | 2020 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2020-03-07 | N | 173 | N | 3 | N | N | 1.1101 | 39.4971 | 379.2699
[7 empty] | 3492 | 1935 | 1756328 | 2020-03-07 15:08 | 2020-03-07 16:03 | 55 | 11kV | 990 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12650 West Gosford ex Panel 1 "Dog Trap Rd" Recloser 45010 Palm Cover tripped on: Signals: Lockout Relays: OC trip Tree removed by Dops in Platypus Creek lane. | March | 2020 | 2020Q3 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-03-07 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 723.4628
[7 empty] | 4543 | 12487 | 1756386 | 2020-03-08 01:06 | 2020-03-08 02:45 | 99 | 11kV | 891 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 208291 B & C Phase DOLF : 40 Amp Excluded OMS 1756386 | March | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-03-08 | N | 99 | N | 6 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 4920 | 16254 | 1756388 | 2020-03-08 01:51 | 2020-03-08 04:47 | 176 | 11kV | 3889 | 933 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN129 Hunters Hill ex Panel 51, IR CP50285 Sirius Orion tripped on: Relays: Overcurrent Upon restoration: ZN80 Chatswood 11kV feeder panel 31 tripped on: Relays: Earth Fault, fault check, EFI Signals: 11kV trip Field EFIs: S3819 Note: EFIs at S64397 & S64396 did not operate. 11kV UG cable fault from S64397 Epping Mowbray No.2 SW/B to S7075 Epping Rd 166 SW/A to S750 Mowbray Fitz No.1 SW/D See 1761583, 1761584, 1761585, 1761586, 1756388 | March | 2020 | 2020Q3 | 2020 | ZN129:PA51 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Not Veg | 2020-03-08 | N | 4.1683 | N | 6 | N | N | 1.1101 | 39.4971 | 2841.9665
[7 empty] | 3674 | 3672 | 1756402 | 2020-03-08 07:13 | 2020-03-08 08:35 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208296 Single phase DOLF : 10 Amp Excluded OMS 1756402 | March | 2020 | 2020Q3 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-03-08 | N | 82 | N | 6 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 5321 | 20046 | 1756513 | 2020-03-08 10:46 | 2020-03-08 14:00 | 194 | 11kV | 388 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 208300 Damaged DOLF assemblies Excluded OMS 1756513 | March | 2020 | 2020Q3 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-03-08 | N | 194 | N | 6 | N | N | 1.1101 | 39.4971 | 283.539
[7 empty] | 4065 | 7730 | 1756394 | 2020-03-08 05:24 | 2020-03-08 15:10 | 586 | 11kV | 86726 | 206 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | LID 208302 2 fault operations B & C Phase Overcurrent Car into pole HR-53207. Broken 11kV crossarm replaced. Excluded OMS 1756394 | March | 2020 | 2020Q3 | 2020 | 502:48002 | 502:48002 | ZN00502/048002 | MAITLAND | OH | Not Veg | 2020-03-08 | N | 421 | N | 6 | N | N | 1.1101 | 39.4971 | 63376.8028
[7 empty] | 5137 | 18491 | 1756391 | 2020-03-08 03:38 | 2020-03-09 16:00 | 2182 | 11kV | 158950 | 704 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN2400 Berowra ex Panel 11, IR CP61454 Berowra Tollgates tripped Relays: SEF trip, OC trip Tree/ branch brought down OH mains. 1 bay down nr pole MU00247 difficult inaccessible area. See 1759366, 1759367, 1759369, 1759371 | March | 2020 | 2020Q3 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2020-03-08 | N | 225.7812 | N | 6 | N | N | 1.1101 | 39.4971 | 116155.9718
[7 empty] | 4618 | 13386 | 1757030 | 2020-03-09 20:03 | 2020-03-09 22:50 | 167 | 11kV | 4509 | 27 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LB43748 (Berkeley Vale Panel 10) Opened By and Operator. Cause: Pole at PT14051 Pleasant Valley Manns Has snapped at TX Tank level. Supply restored via LV PT14051 - Event ID See OMS 1757030 1757028 | March | 2020 | 2020Q3 | 2020 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2020-03-09 | N | 167 | N | 1 | N | N | 1.1101 | 39.4971 | 3295.0442
[7 empty] | 4509 | 12142 | 1757043 | 2020-03-10 01:54 | 2020-03-10 02:49 | 55 | 11kV | 74745 | 1359 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP40118 Murrawal Kilpa 0.2 tripped on OC and Locked out Cause: Dead possum found at the base of PT13099 | March | 2020 | 2020Q3 | 2020 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2020-03-10 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 54621.4414
[7 empty] | 5145 | 18532 | 1757070 | 2020-03-10 08:16 | 2020-03-10 10:45 | 149 | 11kV | 894 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208330 Broken Live Line Clamp Dropper lead Excluded OMS 1757070 | March | 2020 | 2020Q3 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-03-10 | N | 149 | N | 4 | N | N | 1.1101 | 39.4971 | 653.3088
[7 empty] | 4361 | 10699 | 1757227 | 2020-03-10 14:10 | 2020-03-10 17:00 | 170 | 11kV | 1190 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208505 2 DOLFs down at 71410. Power restored 1700. LID entered late | March | 2020 | 2020Q3 | 2020 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-03-10 | N | 170 | N | 4 | N | N | 1.1101 | 39.4971 | 869.6169
[7 empty] | 5277 | 19641 | 1757333 | 2020-03-10 21:30 | 2020-03-10 22:38 | 68 | 11kV | 120632 | 1774 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 57 Tripped on B and C phase Overcurrent, A and B phase Protection Cause: Bat on mains 75 Carranya See OMS 1757333 1757337 | March | 2020 | 2020Q3 | 2020 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2020-03-10 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 88154.3076
[7 empty] | 5113 | 18326 | 1757447 | 2020-03-11 16:20 | 2020-03-11 18:25 | 125 | 11kV | 1125 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 208338 Tx Faulty leaking. N protection operated. Excluded OMS 1757447. | March | 2020 | 2020Q3 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2020-03-11 | N | 125 | N | 1 | N | N | 1.1101 | 39.4971 | 822.1168
[7 empty] | 3784 | 4889 | 1757634 | 2020-03-12 00:23 | 2020-03-12 01:26 | 63 | 11kV | 2709 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208342 3 fault operations Overcurrent B & C O/C Excluded OMS 1757634 | March | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-03-12 | N | 63 | N | 7 | N | N | 1.1101 | 39.4971 | 1979.6573
[7 empty] | 3865 | 5632 | 1757784 | 2020-03-12 14:19 | 2020-03-12 16:35 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208360 C Phase DOLF : 10 Amp Excluded OMS 1757784 | March | 2020 | 2020Q3 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-03-12 | N | 136 | N | 7 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 4079 | 7951 | 1757811 | 2020-03-12 16:04 | 2020-03-12 17:07 | 63.1 | 11kV | 7698.2 | 122 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 208359 No protection operated, isolation to allow repairs done safely. | March | 2020 | 2020Q3 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-03-12 | N | 63.1 | N | 7 | N | N | 1.1101 | 39.4971 | 5625.6175
[7 empty] | 3855 | 5573 | 1757839 | 2020-03-12 18:01 | 2020-03-12 18:19 | 18 | 11kV | 21914 | 1218 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S12690 Berkeley Vale the 11kV Panel 19 tripped on Relays: Panel 19 SEL Cause: Section of feeder has previously tripped on SEL and was taken out of service. Fault not found. After energising feeder held until SEL was made auto. Tripped aftter 1 minute see OMS 1760139 1757839 | March | 2020 | 2020Q3 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | Unknown | Unknown | 2020-03-12 | N | 17.9918 | N | 7 | N | N | 1.1101 | 39.4971 | 16014.1048
[7 empty] | 5220 | 19257 | 1757832 | 2020-03-12 18:30 | 2020-03-12 19:15 | 45 | 11kV | 315 | 7 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv Feeder from Link44046 to Link41190 Isolated for safety Exiting Panel 3 Peats ridge Cause: Interrupted due to rope on 11kV (Rope came from nearby glider club) See OMS 1763949 1757832 | March | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2020-03-12 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 3687 | 3768 | 1757861 | 2020-03-12 23:10 | 2020-03-13 08:30 | 560 | 11kV | 97440 | 174 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208363 car hit pole JU-41711 interrupt to replace pole Excluded oms 1757862 | March | 2020 | 2020Q3 | 2020 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Not Veg | 2020-03-12 | N | 560 | N | 7 | N | N | 1.1101 | 39.4971 | 71206.278
[7 empty] | 4183 | 9220 | 1757915 | 2020-03-13 09:31 | 2020-03-13 14:47 | 316 | 11kV | 10856 | 73 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208370 A Phase DOLF : 40 Amp Blown HV fuse at sub 24107 Hilldale Dr No 3. De-energised oil switch to safely try back fault. Excluded OMS 1757915 & 1758002. | March | 2020 | 2020Q3 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-03-13 | N | 148.7123 | N | 4 | N | N | 1.1101 | 39.4971 | 7933.2446
[7 empty] | 3692 | 3810 | 1757922 | 2020-03-13 09:40 | 2020-03-13 15:45 | 365 | 11kV | 31284 | 131 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208371 1 fault operation Sensitive earth fault Excluded OMS 1757922 | March | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2020-03-13 | N | 238.8092 | N | 4 | N | N | 1.1101 | 39.4971 | 22861.4245
[7 empty] | 5308 | 19940 | 1757924 | 2020-03-13 09:57 | 2020-03-13 16:45 | 408 | 11kV | 6106.7 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT1308 Silverwater Estate - Roadside phase HDO operated Fuse fatigue | March | 2020 | 2020Q3 | 2020 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2020-03-13 | N | 407.1133 | N | 4 | N | N | 1.1101 | 39.4971 | 4462.5962
[7 empty] | 4758 | 14541 | 1758067 | 2020-03-13 18:33 | 2020-03-14 00:50 | 377 | 11kV | 26767 | 71 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP49206 Mangrove Mountain tripped Cause: Vehicle Hit pole adjacent PT11292 | March | 2020 | 2020Q3 | 2020 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2020-03-13 | N | 377 | N | 4 | N | N | 1.1101 | 39.4971 | 19560.5341
[7 empty] | 3414 | 1135 | 1758114 | 2020-03-14 07:04 | 2020-03-14 10:13 | 189 | 11kV | 49826 | 1134 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.10 tripped & reclosed on: B & C phase OC Field EFIs: S10123 & S10949 Tree branch clashed mains causing bond to burn off See 1759009 1759010 | March | 2020 | 2020Q3 | 2020 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2020-03-14 | N | 43.9383 | N | 2 | N | N | 1.1101 | 39.4971 | 36411.3712
[7 empty] | 4181 | 9210 | 1758303 | 2020-03-14 20:02 | 2020-03-14 21:30 | 88 | 11kV | 9130 | 1494 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.55 tripped when attempting to re-energise defective UG section of cable on Pnl.31 between S65872, S4627 and s77441 PT64863 Delaware Cliff - Dist #2 - A, B & C phase fuses blown - LV parallel failure during feeder trip In // for phasing of UG cable fault. See 1760884 1760886 | March | 2020 | 2020Q3 | 2020 | ZN2635:PA55 | ZN2635:PA55 | ZN02635/000055 | PARRAMATTA | UG | Not Veg | 2020-03-14 | N | 6.1111 | N | 2 | N | N | 1.1101 | 39.4971 | 6671.9347
[7 empty] | 4188 | 9250 | 1758336 | 2020-03-15 08:01 | 2020-03-15 09:10 | 69.3667 | 11kV | 277.4667 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208381 B & C Phase DOLF : 20 Amp Excluded OMS 1758344 1758343 | March | 2020 | 2020Q3 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-03-15 | N | 69.3667 | N | 2 | N | N | 1.1101 | 39.4971 | 202.7645
[7 empty] | 5149 | 18591 | 1758337 | 2020-03-15 08:14 | 2020-03-15 09:24 | 70 | 11kV | 40320 | 576 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn901 Surry Hills - Pnl.9 tripped on: A phase O/C Field EFIs; All to S6260. UG cable fault between S6260, S7898, S1113 and S5514 | March | 2020 | 2020Q3 | 2020 | ZN901:PA9 | ZN901:PA9 | ZN00901/000009 | SYDNEY | UG | Not Veg | 2020-03-15 | N | 70 | N | 2 | N | N | 1.1101 | 39.4971 | 29464.6668
[7 empty] | 5066 | 17945 | 1757850 | 2020-03-12 18:12 | 2020-03-15 16:05 | 4193 | 11kV | 3126303 | 963 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.31 tripped on: O/C Abnormal: Existing UG cable fault between S77441 Sw/B , S4627 Sw/A and S65872 Sw/A (from 6/1/20) UG cable fault between S4845 Sw/B, S7061 Sw/A and S77626 Sw/B. 9 DCs unable to be restored between the 2 defectives. See 1760869 1760870 1760872 | March | 2020 | 2020Q3 | 2020 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2020-03-12 | N | 3246.4206 | N | 7 | N | N | 1.1101 | 39.4971 | 2284610.0221
[7 empty] | 4259 | 9888 | 1758680 | 2020-03-16 15:03 | 2020-03-16 15:55 | 52 | 11kV | 15704 | 302 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S12659 Australian Heritage At S12975 Fleet Northumberland and PT18686 Bapaume Birdwood The above the DC's interrupted to allow safe repair of 66kV 840 Feeder See OMS 1758680 1758681 1758682 | March | 2020 | 2020Q3 | 2020 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | Unknown | Unknown | 2020-03-16 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 11476.02
[7 empty] | 3456 | 1580 | 1758461 | 2020-03-16 03:13 | 2020-03-16 16:45 | 812 | 11kV | 254349 | 1051 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1290 Leightonfield Panel 12 tripped and reclosed on Signals: 11kV trip, Relays: Earth fault, EFI, Lockout and Timer Cause: HV into LV at PT63837 Hynes St Vehicle hit pole See OMS 1763724 1763725 1763726 1758501 1758468 1758461 | March | 2020 | 2020Q3 | 2020 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-03-16 | N | 242.0067 | N | 5 | N | N | 1.1101 | 39.4971 | 185870.7472
[7 empty] | 5311 | 19959 | 1758624 | 2020-03-16 12:49 | 2020-03-16 17:00 | 251 | 11kV | 251 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 208397 C Phase DOLF : 10 Amp Excluded OMS 1758624 | March | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-03-16 | N | 251 | N | 5 | N | N | 1.1101 | 39.4971 | 183.4234
[7 empty] | 4486 | 11879 | 1758466 | 2020-03-16 04:34 | 2020-03-16 18:30 | 836 | 11kV | 510624 | 620 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S15005 Belrose Panel 12 feeder to USL 21843 tee N/O AB21063 interrupted for safety Cause: See OMS 1762958 1762961 1758466 1758477 | March | 2020 | 2020Q3 | 2020 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Veg | 2020-03-16 | N | 823.5871 | N | 5 | N | N | 1.1101 | 39.4971 | 373148.9583
[7 empty] | 3334 | 437 | 1758751 | 2020-03-16 18:40 | 2020-03-16 21:10 | 150 | 11kV | 75000 | 500 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 208398 3 phase section of fdr interupted to repair x arm and arrestor Excluded oms 1758534 | March | 2020 | 2020Q3 | 2020 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2020-03-16 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 54807.7879
[7 empty] | 3648 | 3324 | 1758846 | 2020-03-17 10:55 | 2020-03-17 12:30 | 95.4167 | 11kV | 37498.75 | 393 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S571 Myler St 11kV/415V TX 2A & 2B failed Relays: K3 fuse Transformer failure. | March | 2020 | 2020Q3 | 2020 | ZN35555:PA3 | ZN35555:PA3 | ZN35555/000003 | CANADA BAY | UG | Not Veg | 2020-03-17 | N | 95.4167 | N | 4 | N | N | 1.1101 | 39.4971 | 27402.9805
[7 empty] | 4689 | 14000 | 1758895 | 2020-03-17 14:30 | 2020-03-17 14:50 | 20 | 11kV | 200 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208410 11kV Insulator broke down just under 50V measure low on pole 9J 30127. | March | 2020 | 2020Q3 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-03-17 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 3533 | 2327 | 1758814 | 2020-03-17 09:04 | 2020-03-17 15:45 | 401 | 11kV | 401 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 208412 LL Clamp came dislodged. No protection operated. Excluded OMS 1758814 | March | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2020-03-17 | N | 401 | N | 4 | N | N | 1.1101 | 39.4971 | 293.039
[7 empty] | 3317 | 242 | 1758906 | 2020-03-17 14:55 | 2020-03-17 17:30 | 155 | 11kV | 26195 | 169 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208411 Tree near OHM between ABS 40362 and pole GS-91960 | March | 2020 | 2020Q3 | 2020 | 507:80931 | 507:80931 | ZN00507/080931 | CESSNOCK | OH | Veg | 2020-03-17 | N | 155 | N | 4 | N | N | 1.1101 | 39.4971 | 19142.5334
[7 empty] | 5209 | 19081 | 1759210 | 2020-03-18 17:53 | 2020-03-18 18:47 | 54 | 11kV | 61824 | 1164 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.9 tripped on: C phase O/C UG cable fault between S1888 Sw/B and S6403 Sw/A. Pit explosion outside 55 Fotheringham St See 1759455 1759456 | March | 2020 | 2020Q3 | 2020 | ZN2568:PA9 | ZN2568:PA9 | ZN02568/000009 | INNER WEST | UG | Not Veg | 2020-03-18 | N | 53.1134 | N | 3 | N | N | 1.1101 | 39.4971 | 45179.1557
[7 empty] | 3782 | 4883 | 1759217 | 2020-03-18 18:29 | 2020-03-18 21:45 | 196 | 11kV | 93841 | 904 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 3154 St Ives - 11kV No.12 CB "Killeaton Warrimoo" tripped, reclosed & locked out on: Relays: Earth Fault, EFI, Lockout, Timing Signals: 11kV Trip EFIs: S4112, S35697, S78206 Abnormal Switching: Closed at LB 63181 and Open at CP63174 11kV UG cable fault from LB60 to S6253 Du Faur Kirkpatrick SW/A See 1761660, 1761661, 1761662, 1761663, 1761664 | March | 2020 | 2020Q3 | 2020 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Not Veg | 2020-03-18 | N | 103.8064 | N | 3 | N | N | 1.1101 | 39.4971 | 68576.235
[7 empty] | 4121 | 8388 | 1759230 | 2020-03-18 20:08 | 2020-03-18 22:40 | 152 | 11kV | 223554 | 1933 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.31 tripped, reclosed and locked out on: Earth Fault Abnormal: S10166 Sw/A Closed with S63035 Sw/A Open UG cable fault in front line section of feeder from Pnl.31 to LB31155 tee S10492 See 1759458 1759459 | March | 2020 | 2020Q3 | 2020 | ZN10998:PA31 | ZN10998:PA31 | ZN10998/000031 | BAYSIDE | UG | Not Veg | 2020-03-18 | N | 115.6513 | N | 3 | N | N | 1.1101 | 39.4971 | 163366.6695
[7 empty] | 4063 | 7698 | 1759242 | 2020-03-19 02:38 | 2020-03-19 03:40 | 62 | 11kV | 59582 | 961 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pn.35 tripped on A & C phase IOC Possum found at base of PT612 | March | 2020 | 2020Q3 | 2020 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Not Veg | 2020-03-19 | N | 62 | N | 6 | N | N | 1.1101 | 39.4971 | 43540.7682
[7 empty] | 3314 | 217 | 1759244 | 2020-03-19 05:28 | 2020-03-19 06:01 | 33 | 11kV | 14553 | 441 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn1673 Turrumurra - Pnl.9 tripped on: C phase IOC Possum on PT30 | March | 2020 | 2020Q3 | 2020 | ZN1673:PA9 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | OH | Not Veg | 2020-03-19 | N | 33 | N | 6 | N | N | 1.1101 | 39.4971 | 10634.9032
[7 empty] | 4572 | 12814 | 1759269 | 2020-03-19 09:17 | 2020-03-19 13:25 | 248 | 11kV | 496 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208446 B & C Phase DOLF : 16 Amp Isolated sub to repair HV droppers Excluded OMS 1759269 | March | 2020 | 2020Q3 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-03-19 | N | 248 | N | 6 | N | N | 1.1101 | 39.4971 | 362.4622
[7 empty] | 4991 | 17068 | 1760148 | 2020-03-19 11:05 | 2020-03-19 13:46 | 161 | 11kV | 483 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208447 volts detected pole 8M-30662. subs isolated for repairs. | March | 2020 | 2020Q3 | 2020 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2020-03-19 | N | 161 | N | 6 | N | N | 1.1101 | 39.4971 | 352.9622
[7 empty] | 4975 | 16847 | 1761674 | 2020-03-19 13:27 | 2020-03-19 14:17 | 50 | 11kV | 20014 | 2128 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN10999 Kogarah Panel 22 - feeder has tripped on: Signals: 11kV trip Relays: 22L Protection Panel: Earth Fault, EF check relay Field EFIs: S50796 Argyle Willison, S10451 Regent Forest Feeder failed after attempting to restore defective feeder after repairs NAR53389. Feeder isolated from LB 46554 to AB 30019 to PT10764 Westbourne Waratah to S10397 Locksley Haig. Cause not ascertained. See 1761674, 1761678 | March | 2020 | 2020Q3 | 2020 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Not Veg | 2020-03-19 | N | 9.4051 | N | 6 | N | N | 1.1101 | 39.4971 | 14625.6409
[7 empty] | 4897 | 15947 | 1759297 | 2020-03-19 10:25 | 2020-03-20 06:30 | 1205 | 11kV | 37367 | 70 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208448 3 phase Overcurrent; Earth Fault sw 35200 EF, C ph OC, INST EF, 3ph OC 3720 amps Truck hit OH mains causing excessive damage to mains and pole. section isolated for repairs. Excluded oms 1759297 | March | 2020 | 2020Q3 | 2020 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2020-03-19 | N | 533.8143 | N | 6 | N | N | 1.1101 | 39.4971 | 27306.7015
[7 empty] | 3863 | 5622 | 1759543 | 2020-03-20 13:18 | 2020-03-20 14:25 | 67 | 11kV | 56883 | 849 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12570 Avoca 11kV feeder Panel 34 "Terrigal" feeder tripped and locked out on: Relays: B and C phase IOC, EFI, auto reclose, lockout Field EFIs: Nil Tree branch removed by Dop adj PT 12363, supply restored. | March | 2020 | 2020Q3 | 2020 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2020-03-20 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 41568.4186
[7 empty] | 5237 | 19380 | 1759542 | 2020-03-20 13:18 | 2020-03-20 15:30 | 132 | 11kV | 264 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208466 Single phase DOLF : 10 Amp Excluded OMS 1759542 | March | 2020 | 2020Q3 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-03-20 | N | 132 | N | 4 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 4189 | 9262 | 1759609 | 2020-03-20 16:53 | 2020-03-20 17:55 | 62 | 11kV | 4588 | 74 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208467 Tree growing into mains Excluded OMS 1759609 | March | 2020 | 2020Q3 | 2020 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2020-03-20 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 3352.7751
[7 empty] | 4274 | 9990 | 1759643 | 2020-03-20 18:29 | 2020-03-20 19:30 | 61.6333 | 11kV | 9429.9 | 153 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 208468 A Phase DOLF : 31 Amp suspect fuse failure at crimp. dq Excluded OMS 1759643 CC1: 22-"Refer to SOp" | March | 2020 | 2020Q3 | 2020 | 257:82000 | 257:82000 | ZN00257/082000 | NEWCASTLE | OH | Not Veg | 2020-03-20 | N | 61.6333 | N | 4 | N | N | 1.1101 | 39.4971 | 6891.0928
[7 empty] | 5119 | 18360 | 1759709 | 2020-03-21 07:27 | 2020-03-21 08:28 | 61 | 11kV | 57596 | 976 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 340 Botany Panel 30 "S5896 William Morgan" has tripped : Relays: IOC, A+B+C OC, EFI Field EFI: S5896, S2267 UG Fault between S2267 Dransfield Av, S3693 Maloney Sparks and S4451 Tunbridge St See 1761779, 1761778 | March | 2020 | 2020Q3 | 2020 | ZN340:PA40 | ZN340:PA40 | ZN00340/000040 | BAYSIDE | UG | Not Veg | 2020-03-21 | N | 59.0123 | N | 5 | N | N | 1.1101 | 39.4971 | 42089.458
[7 empty] | 4246 | 9721 | 1759713 | 2020-03-21 09:50 | 2020-03-21 12:11 | 141 | 11kV | 5707 | 47 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 208472 Broken HV X arm pole GU-72629 Excluded OMS 1759713 | March | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-03-21 | N | 121.4255 | N | 5 | N | N | 1.1101 | 39.4971 | 4170.5073
[7 empty] | 4159 | 8937 | 1759828 | 2020-03-21 22:58 | 2020-03-21 23:55 | 57 | 11kV | 5358 | 94 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208476 A Phase DOLF : 40 Amp Possum Excluded OMS 1759828 | March | 2020 | 2020Q3 | 2020 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2020-03-21 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 3915.4684
[7 empty] | 4330 | 10444 | 1759823 | 2020-03-21 23:00 | 2020-03-22 01:45 | 165 | 11kV | 6930 | 51 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV mains down OS 45 Excelsior 11kV feeder isolated for safety at 2300hrs 21/3 from S14833 to extent of feeder. 11kV feeder isolated for repairs from S14833 to LB9996 to LK43716 tee PT14705 to PT13962 permit issued to LW to make repairs. also refer to related T&R OMS 1760894 @ 21/03/2020 22:24:00 See 1760894, 1760895, 1760896, 1760897, 1760899, 1760900 | March | 2020 | 2020Q3 | 2020 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2020-03-21 | N | 135.8824 | N | 5 | N | N | 1.1101 | 39.4971 | 5064.2396
[7 empty] | 4451 | 11522 | 1759934 | 2020-03-22 20:25 | 2020-03-22 21:56 | 91 | 11kV | 25956 | 290 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN35370 Galston ex Panel 8 Recloser 427 Arcadia Fagans Park reclosed and tripped on: Signals: A & B phase OC Abnormal Switching: LB 490 was defective (Hornsby Panel 45), CP62108 was closed. Branch/tree on 11kV near PT 61737 Fishburn Bevans. See 1759934, 1760530, 1760528, 1760525, 1759936 | March | 2020 | 2020Q3 | 2020 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2020-03-22 | N | 89.5034 | N | 2 | N | N | 1.1101 | 39.4971 | 18967.8792
[7 empty] | 4585 | 13035 | 1759940 | 2020-03-22 21:06 | 2020-03-22 23:19 | 133 | 11kV | 227395.4 | 1711 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn 9550 Gwawley Bay - 11kV Panel 3 Tripped on: Relays: Bassler - TRIP 50 TBC Abnormal Switching: Sw B closed @ S9669 Princes Clare Sw A open @ S9875 Belgrave Lachlan Dop patrolled feeder nothing found - cause not ascertained See 1759940, 1760519, 1760518 | March | 2020 | 2020Q3 | 2020 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | OH | Veg | 2020-03-22 | N | 132.902 | N | 2 | N | N | 1.1101 | 39.4971 | 166173.8513
[7 empty] | 4052 | 7565 | 1759955 | 2020-03-23 00:14 | 2020-03-23 01:19 | 65 | 11kV | 63505 | 977 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN3472 Sefton 11kv VCB Panel 22 "S1279 Virgil Ave" Feeder tripped on: Relays: A phase OC Field EFI's: nil Signals: 11kV trip Dop removed bat from 11kV OH mains. No damage to mains. PT65044 was in LV// with S1279 (pnl 22) at time of trip. See 1761191. See 1761191, 1759955 | March | 2020 | 2020Q3 | 2020 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-03-23 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 46407.5809
[7 empty] | 5048 | 17795 | 1760151 | 2020-03-23 16:19 | 2020-03-23 17:10 | 51.4667 | 11kV | 1080.8 | 21 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208489 Pole cap fell of between both phases. Excluded OMS 1760154 | March | 2020 | 2020Q3 | 2020 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2020-03-23 | N | 51.4667 | N | 5 | N | N | 1.1101 | 39.4971 | 789.8168
[7 empty] | 3393 | 901 | 1760182 | 2020-03-23 22:16 | 2020-03-23 22:36 | 19.6833 | 11kV | 925.1167 | 47 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT1803 Waninga Aldous - Interrupted to remove Bat from sealing end on Q type PT | March | 2020 | 2020Q3 | 2020 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2020-03-23 | N | 19.6833 | N | 5 | N | N | 1.1101 | 39.4971 | 676.048
[7 empty] | 4466 | 11620 | 1760212 | 2020-03-23 23:43 | 2020-03-24 01:51 | 128 | 11kV | 205783 | 1621 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn180 Mosman - Pnl.7 tripped on: B Phase O/C & E/F Field EFIs: S47018, S2131 S35066 UG cable fault between S47018 and S2131. EFIs found down from previous fault Pnl.20 tripped on: Earth Fault upon restoration attempt See 1760600 1760601 1760602 | March | 2020 | 2020Q3 | 2020 | ZN180:PA7 | ZN180:PA7 | ZN00180/000007 | MOSMAN | UG | Not Veg | 2020-03-23 | N | 126.9482 | N | 5 | N | N | 1.1101 | 39.4971 | 150380.1468
[7 empty] | 5105 | 18254 | 1760234 | 2020-03-24 07:58 | 2020-03-24 12:45 | 287 | 11kV | 1435 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208496 A & B Phase DOLF : 20 Amp Excluded OMS 1760234 | March | 2020 | 2020Q3 | 2020 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2020-03-24 | N | 287 | N | 6 | N | N | 1.1101 | 39.4971 | 1048.6557
[7 empty] | 3469 | 1676 | 1760327 | 2020-03-24 12:06 | 2020-03-24 13:10 | 64 | 11kV | 256 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208504 Single phase DOLF : 10 Amp Excluded OMS 1760327 | March | 2020 | 2020Q3 | 2020 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-03-24 | N | 64 | N | 6 | N | N | 1.1101 | 39.4971 | 187.0772
[7 empty] | 3917 | 6093 | 1760273 | 2020-03-24 09:45 | 2020-03-24 16:16 | 390.5833 | 11kV | 600238.1333 | 2784 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 10999 Kogarah 11kV Feeder Panel 24 "High Carlton" feeder tripped and locked out on: Relays: E/F, EFI, E/F check Field EFIs: S10666, S10182, S47882, S62443 Proven EFIs: S10666, S10182 Suspected UG cable fault in section of feeder SW/B@S10182 Station Lily to AB31299 to LB47480 to AB31050. See 1761688, 1761690, 1761691, 1761693, 1761694, 1761696, 1760275, 1760277 | March | 2020 | 2020Q3 | 2020 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | OH | Not Veg | 2020-03-24 | N | 215.6028 | N | 6 | N | N | 1.1101 | 39.4971 | 438636.3238
[7 empty] | 4934 | 16440 | 1760409 | 2020-03-24 16:13 | 2020-03-24 17:05 | 52 | 11kV | 52 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208510 A Phase DOLF : 10 Amp Excluded OMS 1760409 | March | 2020 | 2020Q3 | 2020 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-03-24 | N | 52 | N | 6 | N | N | 1.1101 | 39.4971 | 38.0001
[7 empty] | 5169 | 18731 | 1760418 | 2020-03-24 16:55 | 2020-03-24 18:20 | 85 | 11kV | 10540 | 124 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208507 live pole reported 8M-30093, section isolated for repairs Excludedoms 1760250 | March | 2020 | 2020Q3 | 2020 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2020-03-24 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 7702.3211
[7 empty] | 4396 | 11013 | 1760438 | 2020-03-24 21:48 | 2020-03-24 23:09 | 81 | 11kV | 72495 | 895 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN14892 Charmhaven 11kV Panel 14 "Tavern Pacific" feeder tripped on: Relays: OC+EF, 51N, FC, Prohibition 11kV UG feeder fault between Charmhaven Zn Pnl 14 and S18599 Tavern Pacific. See 1760440 possible GIS error. | March | 2020 | 2020Q3 | 2020 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2020-03-24 | N | 81 | N | 6 | N | N | 1.1101 | 39.4971 | 52977.2078
[7 empty] | 3738 | 4351 | 1759832 | 2020-03-21 23:53 | 2020-03-25 01:12 | 4399 | 11kV | 85500.7 | 837 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn965 Pennant Hills Panel 33- feeder has tripped Signals: 11kV trip, AR lockout Zone Earth, group earth Relays: Earth Fault, EFI timing relay, lockout Field EFIs: nil UG cable fault ZN965 Pennant Hills Panel 33 to SW/A S4493 Bellamt to AB1022 tee S4613 MWS & DB Victoria Leo No.1. Isolated for UG feeder switching tag left at ZN. Region to organise test/repair. See 1761601 for outage to S4613, 1759832, 1759833 | March | 2020 | 2020Q3 | 2020 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2020-03-21 | N | 102.1514 | N | 5 | N | N | 1.1101 | 39.4971 | 62481.3897
[7 empty] | 4954 | 16638 | 1760202 | 2020-03-23 22:28 | 2020-03-25 05:26 | 1857.9 | 11kV | 1857.9 | 1 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | And now as of 23/03/20 2300hrs The standby supply to HVC has failed from CP 4749 MWS & DB Victoria Leo No 2. SOC (Glen) has been advised to get a generator on site. Sydney water SOC contacted and advised both HVC defective from CP 4613 MWS & DB Victoria Leo No 1 CC1: 22-"Refer to SOp" | March | 2020 | 2020Q3 | 2020 |  |  |  | HORNSBY | Unknown | Not Veg | 2020-03-23 | N | 1857.9 | N | 5 | N | N | 1.1101 | 39.4971 | 1357.6985
[7 empty] | 4821 | 15241 | 1760459 | 2020-03-25 07:35 | 2020-03-25 11:55 | 260.25 | 11kV | 1301.25 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208518 patrolled feeder and found nothing | March | 2020 | 2020Q3 | 2020 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2020-03-25 | N | 260.25 | N | 8 | N | N | 1.1101 | 39.4971 | 950.9151
[7 empty] | 3442 | 1401 | 1760586 | 2020-03-25 13:26 | 2020-03-25 14:35 | 69.1833 | 11kV | 345.9167 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208524 A Phase DOLF : 20 Amp | March | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-03-25 | N | 69.1833 | N | 8 | N | N | 1.1101 | 39.4971 | 252.7857
[7 empty] | 4511 | 12177 | 1760570 | 2020-03-25 12:53 | 2020-03-25 14:45 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208525 A Phase DOLF : 10 Amp Excluded OMS 1760570 | March | 2020 | 2020Q3 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-03-25 | N | 112 | N | 8 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 3343 | 490 | 1760581 | 2020-03-25 13:09 | 2020-03-25 14:50 | 101 | 11kV | 404 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208526 replaced 2 x dolfs Excluded oms 1760581 | March | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2020-03-25 | N | 101 | N | 8 | N | N | 1.1101 | 39.4971 | 295.2313
[7 empty] | 3697 | 3892 | 1760690 | 2020-03-25 16:21 | 2020-03-25 18:05 | 104 | 11kV | 208 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 208529 Single phase faulty tx replaced Excluded oms 1760690 | March | 2020 | 2020Q3 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-03-25 | N | 104 | N | 8 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 4566 | 12785 | 1760672 | 2020-03-25 15:45 | 2020-03-25 18:30 | 165 | 11kV | 165 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208534 Car has hit pole, supply lost. Driver has apparently called 000. Minimal info available, third party reporting. Excluded OMS 1760672 | March | 2020 | 2020Q3 | 2020 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2020-03-25 | N | 165 | N | 8 | N | N | 1.1101 | 39.4971 | 120.5771
[7 empty] | 4602 | 13211 | 1760684 | 2020-03-25 16:13 | 2020-03-25 18:30 | 137 | 11kV | 274 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208530 B & C Phase DOLF : 10 Amp Excluded OMS 1760684 | March | 2020 | 2020Q3 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-03-25 | N | 137 | N | 8 | N | N | 1.1101 | 39.4971 | 200.2311
[7 empty] | 5052 | 17836 | 1760630 | 2020-03-25 15:25 | 2020-03-25 18:50 | 205 | 11kV | 144037 | 2383 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn14892 Charmhaven - Pnl.3 tripped on: B & C phase O/C Abnormal: AB44110 Closed with AB40127 Open 11kV down between AB42481, LB61136 & USL43624 tee PT11856 See 1760965 1760966 | March | 2020 | 2020Q3 | 2020 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2020-03-25 | N | 60.4436 | N | 8 | N | N | 1.1101 | 39.4971 | 105257.9912
[7 empty] | 3773 | 4798 | 1760777 | 2020-03-26 07:04 | 2020-03-26 07:44 | 40 | 11kV | 71280 | 1782 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca tripped on: B & C phase IOC Tree on mains adj USL44519 | March | 2020 | 2020Q3 | 2020 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2020-03-26 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 52089.3216
[7 empty] | 3504 | 2056 | 1760793 | 2020-03-26 08:06 | 2020-03-26 09:20 | 74 | 11kV | 51245 | 695 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Rain Light | N | Zn630 Mascot - Pnl.31 tripped on: B phase O/C External contractor damaged UG cable between S6458 Sw/B, S8070 Sw/A and S5937 Sw/A See 1761554 1761556 | March | 2020 | 2020Q3 | 2020 | ZN630:PA31 | ZN630:PA31 | ZN00630/000031 | BAYSIDE | UG | Not Veg | 2020-03-26 | N | 73.7338 | N | 4 | N | N | 1.1101 | 39.4971 | 37448.3345
[7 empty] | 3783 | 4888 | 1760992 | 2020-03-26 16:42 | 2020-03-26 20:45 | 242.6833 | 11kV | 242.6833 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 208545 Single phase LL lead broken Excluded OMS 1761005 | March | 2020 | 2020Q3 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-03-26 | N | 242.6833 | N | 4 | N | N | 1.1101 | 39.4971 | 177.3458
[7 empty] | 3681 | 3733 | 1761001 | 2020-03-26 17:38 | 2020-03-26 20:45 | 187.45 | 11kV | 18745 | 100 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex West Gosford Pnl.3 - 11kV interrupted from S18117 Sw/B & S12869 Sw/B to allow HV UGOH crossarm to be repaired | March | 2020 | 2020Q3 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2020-03-26 | N | 187.45 | N | 4 | N | N | 1.1101 | 39.4971 | 13698.2931
[7 empty] | 3760 | 4675 | 1761044 | 2020-03-27 00:18 | 2020-03-27 01:53 | 95.0167 | 11kV | 2375.4167 | 25 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | PT564 Sewell Ave - A & B Phase HDOs operated 11kV bushings damaged Restored via LV // | March | 2020 | 2020Q3 | 2020 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-03-27 | N | 95.0167 | N | 3 | N | N | 1.1101 | 39.4971 | 1735.8844
[7 empty] | 3468 | 1664 | 1761049 | 2020-03-27 03:50 | 2020-03-27 05:25 | 95 | 11kV | 99940 | 1052 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Lake Munmorah Pnl. - Bond burnt off USL43270 Abnormal: REC45139 Closed with S18069 Sw/B Open | March | 2020 | 2020Q3 | 2020 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2020-03-27 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 73033.2043
[7 empty] | 3483 | 1843 | 1761064 | 2020-03-27 07:37 | 2020-03-27 14:50 | 433.0667 | 11kV | 1299.2 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Autolinks 44952 Morgans Rd interrupted to remove large tree from CCT mains. | March | 2020 | 2020Q3 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-03-27 | N | 433.0667 | N | 3 | N | N | 1.1101 | 39.4971 | 949.417
[7 empty] | 3818 | 5247 | 1761279 | 2020-03-28 06:59 | 2020-03-28 09:32 | 153 | 11kV | 31220 | 372 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn187 Crows Nest Panel 23 Tripped on Relays: C phase IOC, Earth Fault, Fault Check, EFI, C phase Trip Signals: 11kV trip, Group Earth, No11 Group Earth Abnormal Switcing SW/A @ S6594 to SW/B @ S5623 OOS due to previous fault. See OMS 1763713 1763714 1761279 | March | 2020 | 2020Q3 | 2020 | ZN187:PA23 | ZN187:PA23 | ZN00187/000023 | LANE COVE | UG | Not Veg | 2020-03-28 | N | 83.9247 | N | 2 | N | N | 1.1101 | 39.4971 | 22814.6552
[7 empty] | 3815 | 5214 | 1761291 | 2020-03-28 09:02 | 2020-03-28 10:23 | 81 | 11kV | 71036 | 882 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn 10998 Rockdale Panel 2 tripped on SEL Cause: Bond failed in section of OH between UGOH and SW/B @ S10109 (pole K00974) See OMS 1763711 1763712 OMS 1761291 | March | 2020 | 2020Q3 | 2020 | ZN10998:PA2 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2020-03-28 | N | 80.5397 | N | 2 | N | N | 1.1101 | 39.4971 | 51911.0136
[7 empty] | 4166 | 9058 | 1762194 | 2020-03-30 06:59 | 2020-03-30 07:11 | 12 | 11kV | 5044 | 937 | HV | Staff Operation | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 10991 Blakehurst - Panel 1 tripped on: Relays: IOC A + C phase, Timed OC C Phase EFIs: S10137 Abnormal switching: AB 31302 Open, SW/A at S10860 Water Princess Open and LV 31021 closed for NAR 53408. S10620 Beach Torrens in LV//. During restoration of network Dop closed onto earth. See 1762194, 1762196 | March | 2020 | 2020Q3 | 2020 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2020-03-30 | N | 5.3831 | N | 2 | N | N | 1.1101 | 39.4971 | 3686.0064
[7 empty] | 3513 | 2167 | 1761770 | 2020-03-30 11:28 | 2020-03-30 14:15 | 167 | 11kV | 167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 208577 Single phase DOLF : 10 Amp Excluded OMS 1762605 | March | 2020 | 2020Q3 | 2020 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-03-30 | N | 167 | N | 2 | N | N | 1.1101 | 39.4971 | 122.0387
[7 empty] | 4971 | 16818 | 1761893 | 2020-03-31 13:40 | 2020-03-31 17:40 | 240 | 11kV | 480 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208590 B ph HV dropper lead broken off to dolf. sub isolated for repair Excluded OMS 1761893 | March | 2020 | 2020Q3 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2020-03-31 | N | 240 | N | 2 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 3367 | 673 | 1761986 | 2020-03-31 22:16 | 2020-03-31 23:33 | 77 | 11kV | 55517 | 721 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn9900 Menai - Pnl.6 tripped on: O/C & E/F Possum found on UGOH at PT9544 David Underwood | March | 2020 | 2020Q3 | 2020 | ZN9900:PA6 | ZN9900:PA6 | ZN09900/000006 | SUTHERLAND | OH | Not Veg | 2020-03-31 | N | 77 | N | 2 | N | N | 1.1101 | 39.4971 | 40570.1861
[7 empty] | 4109 | 8274 | 1762030 | 2020-04-01 08:34 | 2020-04-01 09:35 | 61 | 11kV | 915 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 208592 B Phase DOLF : 50 Amp Fuse fatigue | April | 2020 | 2020Q4 | 2020 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-04-01 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 668.655
[7 empty] | 5013 | 17327 | 1762167 | 2020-04-01 14:36 | 2020-04-01 17:05 | 149 | 11kV | 24734 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP 45012 Bar Point (Ex Somersby Panel 17) tripped on: Relays: OC (Scan Fail) Signals: PA 17 EFI at Somersby Zn Tree/branch on OH mains. CC1: 22-"Refer to SOp" | April | 2020 | 2020Q4 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-04-01 | N | 149 | N | 3 | N | N | 1.1101 | 39.4971 | 18074.8777
[7 empty] | 4951 | 16621 | 1762258 | 2020-04-01 20:46 | 2020-04-01 21:28 | 42 | 11kV | 24192 | 576 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN1193 Lindfield ex Panel 12, Recloser 49996 Churchill Fairbairn tripped on: Signals: OC trip, Lockout EFIs: nil Network switched abnormally due to DMAs: AB 576 open, LB 46265 open, LB 79087 open, LB 62192 closed Bat found across HV near PT 1773 Springdale roper | April | 2020 | 2020Q4 | 2020 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2020-04-01 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 17678.8001
[7 empty] | 3320 | 308 | 1762282 | 2020-04-02 07:00 | 2020-04-02 08:00 | 60 | 11kV | 120 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208604 C Phase DOLF : 10 Amp Possom on HV Excluded OMS 1762282 | April | 2020 | 2020Q4 | 2020 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2020-04-02 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 4631 | 13517 | 1762339 | 2020-04-02 10:06 | 2020-04-02 12:08 | 122 | 11kV | 16470 | 135 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | PT2392 Lindsay Bransgrove 11kV C phase HDO blown (50A) Report of incident with bird | April | 2020 | 2020Q4 | 2020 | ZN2196:PA9 | ZN2196:PA9 | ZN02196/000009 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-04-02 | N | 122 | N | 4 | N | N | 1.1101 | 39.4971 | 12035.7902
[7 empty] | 4482 | 11863 | 1762417 | 2020-04-02 13:57 | 2020-04-02 16:58 | 181 | 11kV | 350737 | 1941 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 35800 Bankstown Panel 16 "Canterbury Fair" Feeder tripped on B/C phase OC (50 tn, 50 tbc) Vehicle hit OH mains. See 1765109, 1765110, 1765113, 1765114, 1762408 Subs S5773 and S5762 normally fed from panel 14 were in LV// at time of fault. | April | 2020 | 2020Q4 | 2020 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-04-02 | N | 180.6991 | N | 4 | N | N | 1.1101 | 39.4971 | 256308.2546
[7 empty] | 5317 | 20008 | 1762483 | 2020-04-02 19:17 | 2020-04-02 20:40 | 83 | 11kV | 249 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT 11071 Boundary Hillside Tree/branch has hit PT and the HDOs have operated. | April | 2020 | 2020Q4 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2020-04-02 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 181.9619
[7 empty] | 4341 | 10522 | 1762711 | 2020-04-03 20:30 | 2020-04-03 21:45 | 75 | 11kV | 10350 | 138 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Light | N | LID 208626 FAULTY PG CLAMP AT POLE KT-40685 Fullerton Cove. Section isolated to repair. Excluded OMS REPORT NO 1762711,1762722-23-24. | April | 2020 | 2020Q4 | 2020 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2020-04-03 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 7563.4747
[7 empty] | 3379 | 800 | 1762727 | 2020-04-03 20:49 | 2020-04-04 00:15 | 206 | 11kV | 252151 | 2099 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn10993 Hurstville North - Pnl.22 tripped, relcosed & locked out on: Earth Fault Possible UG cable fault or UGOH flashover between AB31213 to LB30072 to S48119 Sw/B See 1764939 1764937 1764938 1764939 1764940 | April | 2020 | 2020Q4 | 2020 | ZN10993:PA22 | ZN10993:PA22 | ZN10993/000022 | BAYSIDE | UG | Not Veg | 2020-04-03 | N | 120.1291 | N | 2 | N | N | 1.1101 | 39.4971 | 184264.5136
[7 empty] | 3958 | 6519 | 1762829 | 2020-04-04 12:57 | 2020-04-04 14:35 | 98 | 11kV | 113496 | 1524 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208633 Tree on OHM pole GS-84062 51BN Lock out relay Excluded OMS 1762855 | April | 2020 | 2020Q4 | 2020 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2020-04-04 | N | 74.4724 | N | 8 | N | N | 1.1101 | 39.4971 | 82939.5292
[7 empty] | 3587 | 2710 | 1762746 | 2020-04-04 11:08 | 2020-04-04 17:15 | 367 | 11kV | 15414 | 42 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 208640 Car hit pole ES-62987 Excluded OMS 1762800 | April | 2020 | 2020Q4 | 2020 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2020-04-04 | N | 367 | N | 8 | N | N | 1.1101 | 39.4971 | 11264.0966
[7 empty] | 3603 | 2796 | 1762762 | 2020-04-04 09:22 | 2020-04-04 17:55 | 513 | 11kV | 7695 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Peats Ridge Pnl.10 interrupted from AB44293 to LB41564. Large tree brought down 4 bays of LVand knocked 11kV CCT off pole | April | 2020 | 2020Q4 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-04-04 | N | 513 | N | 8 | N | N | 1.1101 | 39.4971 | 5623.279
[7 empty] | 5271 | 19602 | 1763013 | 2020-04-04 15:13 | 2020-04-04 19:15 | 242 | 11kV | 25803 | 185 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC61341 George Bloodtree 0.1 tripped Abnormal: REC61341 closed with LB41564 Open Tree on mains 252 Wisemans Ferry Rd See 1765010 1765009 | April | 2020 | 2020Q4 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-04-04 | N | 139.4757 | N | 8 | N | N | 1.1101 | 39.4971 | 18856.0713
[7 empty] | 5257 | 19503 | 1762877 | 2020-04-04 14:09 | 2020-04-04 20:50 | 401 | 11kV | 37012 | 184 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208645 1 fault operation 3 phase Earth Fault Excluded oms1762877, 1762960, 1762913 | April | 2020 | 2020Q4 | 2020 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2020-04-04 | N | 201.1522 | N | 8 | N | N | 1.1101 | 39.4971 | 27047.2779
[7 empty] | 3787 | 4911 | 1762857 | 2020-04-04 13:52 | 2020-04-04 23:25 | 573.4667 | 11kV | 5191.4667 | 16 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 208644 A Phase LLC lead broken LVL closed at 1843. All on Excluded oms 1763015 | April | 2020 | 2020Q4 | 2020 | 528:83013 | 528:83013 | ZN00528/083013 | MAITLAND | OH | Not Veg | 2020-04-04 | N | 324.4667 | N | 8 | N | N | 1.1101 | 39.4971 | 3793.7707
[7 empty] | 4677 | 13908 | 1763003 | 2020-04-04 18:00 | 2020-04-05 16:20 | 1340 | 11kV | 60374.6 | 607 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn35370 Galston - Pnl.8 tripped on: A & C phase OC Abnormal: AB2907 Open DMA with AB2063 Closed Tree brought down OH mains near PT2109 See 1765057 1765058 | April | 2020 | 2020Q4 | 2020 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2020-04-04 | N | 99.4639 | N | 8 | N | N | 1.1101 | 39.4971 | 44119.9769
[7 empty] | 3425 | 1236 | 1763157 | 2020-04-05 18:45 | 2020-04-05 20:15 | 90 | 11kV | 8820 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | REC44607 Matcham North interrupted for safety due to tree on 11kV CCT outside 220 Matcham Rd | April | 2020 | 2020Q4 | 2020 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-04-05 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 6445.3959
[7 empty] | 4017 | 7180 | 1763178 | 2020-04-05 21:15 | 2020-04-05 21:45 | 30 | 11kV | 10020 | 594 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208651 Possum found at sw 2418 with damaged arrestors cut away, & blown tapping found at sw 17519. also refer to previous Trip and Reclose event OMS 1763292 @ 05/04/2020 18:54:00 Excluded oms report no 1733180,1763178,1763200,1763179,1763186,1763204. | April | 2020 | 2020Q4 | 2020 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2020-04-05 | N | 16.8687 | N | 3 | N | N | 1.1101 | 39.4971 | 7322.3205
[7 empty] | 4112 | 8297 | 1762809 | 2020-04-04 11:45 | 2020-04-06 08:00 | 2655 | 33kV Distribution | 40193 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208635 Sw 90700 - Dir E/F Sw 80500 A prot - A phase E trip, Mutti trip. B prot - 50N, Multitrip, L/O 33kV main on ground at pole KT-70524, 33kV into neutral sub 3916, EMSO to check, unable to access customer premises, LVF 3916 & LVL 19970 left open until access provided. Excluded OMS 1762809 | April | 2020 | 2020Q4 | 2020 | 417:80500 | 417:80500 | ZN00417/080500 | NEWCASTLE | OH | Not Veg | 2020-04-04 | N | 1826.9545 | N | 8 | N | N | 1.1101 | 39.4971 | 29371.8589
[7 empty] | 3646 | 3322 | 1763274 | 2020-04-06 09:21 | 2020-04-06 14:25 | 304 | 11kV | 384 | 17 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 208657 B Phase DOLF : 5 Amp Blown L/A's at PT59022 Excluded OMS 1763274 | April | 2020 | 2020Q4 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-04-06 | N | 22.5882 | N | 2 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 5194 | 18895 | 1763181 | 2020-04-05 19:05 | 2020-04-06 16:10 | 1265 | 11kV | 1077376 | 2067 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.3 tripped on: Earth Fault Abnormal: S62412 Sw/B closed with S310 Sw/D oepn. S2740 Sw/A closed with CP1555 Sw/A Open (DMA) UG cabel fault between S3151 Sw/A, S2366 Sw/B and S2145 Sw/B Delayed restoration due to existing DMA See 1763565 1763566 1763567 | April | 2020 | 2020Q4 | 2020 | ZN690:PA11 | ZN690:PA11 | ZN00690/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-04-05 | N | 521.2269 | N | 3 | N | N | 1.1101 | 39.4971 | 787314.6036
[7 empty] | 3840 | 5435 | 1763424 | 2020-04-06 17:12 | 2020-04-06 23:48 | 396 | 11kV | 3960 | 10 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 208660 Truck trailer hit pole IT-21164. See also LID T&R report #208658. Excluded OMS No. 1763424, 1763425, 1763428, 1763442 | April | 2020 | 2020Q4 | 2020 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2020-04-06 | N | 396 | N | 2 | N | N | 1.1101 | 39.4971 | 2893.8512
[7 empty] | 3471 | 1702 | 1763467 | 2020-04-07 01:15 | 2020-04-07 03:00 | 105 | 11kV | 3255 | 31 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 208666 NO PROTECTION OPERATED. SECTION ISOLATED TO REPAIR FAULTY 11KV TAPPING AT POLE MD-90675. Excluded OMS REPORT NO 1763447 | April | 2020 | 2020Q4 | 2020 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2020-04-07 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 2378.658
[7 empty] | 5281 | 19698 | 1763465 | 2020-04-07 00:24 | 2020-04-07 10:20 | 596 | 11kV | 9070 | 146 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208665 3 fault operations Overcurrent, Earth Fault 11kV mains down between pole JP-85042 & JP-85043 Faulty tie at pole JP-85044 Excluded OMS 1763465 | April | 2020 | 2020Q4 | 2020 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2020-04-07 | N | 62.1233 | N | 3 | N | N | 1.1101 | 39.4971 | 6628.0885
[7 empty] | 3391 | 874 | 1763564 | 2020-04-07 11:03 | 2020-04-07 12:07 | 64 | 11kV | 34894 | 562 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.34 tripped on: IOC B phase UG cable fault between S4311 Sw/B and S48886 Sw/A See 1765515 1765516 | April | 2020 | 2020Q4 | 2020 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | UG | Not Veg | 2020-04-07 | N | 62.089 | N | 3 | N | N | 1.1101 | 39.4971 | 25499.506
[7 empty] | 4133 | 8519 | 1763927 | 2020-04-08 18:08 | 2020-04-08 19:36 | 88 | 11kV | 52028 | 626 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC48036 Rawson Woy Woy tripped on: OC Bat on mains, burnt off bond See 1765097 1765098 | April | 2020 | 2020Q4 | 2020 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2020-04-08 | N | 83.1118 | N | 1 | N | N | 1.1101 | 39.4971 | 38020.5278
[7 empty] | 3371 | 685 | 1764169 | 2020-04-09 19:42 | 2020-04-09 22:45 | 183 | 11kV | 1464 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208712 A Phase DOLF : 16 Amp Excluded OMS 1764169 | April | 2020 | 2020Q4 | 2020 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2020-04-09 | N | 183 | N | 2 | N | N | 1.1101 | 39.4971 | 1069.848
[7 empty] | 3633 | 3183 | 1764178 | 2020-04-09 22:56 | 2020-04-10 00:10 | 74 | 11kV | 136988 | 2790 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.42 tripped on A Phase O/C & E/F UG cable fault between S2477, S2916 tee S529 See 1765521 1765522 | April | 2020 | 2020Q4 | 2020 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2020-04-09 | N | 49.0996 | N | 2 | N | N | 1.1101 | 39.4971 | 100106.7899
[7 empty] | 4293 | 10123 | 1764141 | 2020-04-10 08:35 | 2020-04-10 09:18 | 43 | 11kV | 5934 | 138 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208714 Wire off a pin at pole FO-20056 Job referred to Mark Baxter. After MArk inspected the site he informed me of the following. Access is not safe in the Dark. The conductor is not on the X-arm & is intrinsically safe. Conductor can not blow of crossarm. No Volts are present at Ground level. ERC has given the OK to return in daylight to find a safer access and repair the damaged insulator. Excluded OMS 1764141 | April | 2020 | 2020Q4 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-04-10 | N | 43 | N | 4 | N | N | 1.1101 | 39.4971 | 4336.3922
[7 empty] | 5155 | 18629 | 1764209 | 2020-04-10 09:54 | 2020-04-10 11:21 | 87 | 11kV | 26564 | 464 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.14 tripped on: B phase OC UG cable fault between S9206, S9050 & S61005 See 1765076 1765077 | April | 2020 | 2020Q4 | 2020 | ZN9037:PA14 | ZN9037:PA14 | ZN09037/000014 | SUTHERLAND | UG | Not Veg | 2020-04-10 | N | 57.25 | N | 4 | N | N | 1.1101 | 39.4971 | 19412.1877
[7 empty] | 4105 | 8220 | 1764218 | 2020-04-10 10:49 | 2020-04-10 12:30 | 101 | 11kV | 202 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 208715 A Phase DOLF : 10 Amp Excluded OMS 1764218 | April | 2020 | 2020Q4 | 2020 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2020-04-10 | N | 101 | N | 4 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 3656 | 3460 | 1764245 | 2020-04-10 13:36 | 2020-04-10 15:00 | 84 | 11kV | 336 | 4 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Rain Light | N | LID 208716 B Phase DOLF : 10 Amp Broken stay wire at sub pole. Excluded OMS 1764245. | April | 2020 | 2020Q4 | 2020 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-04-10 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 3952 | 6462 | 1764361 | 2020-04-11 13:12 | 2020-04-11 13:53 | 41 | 11kV | 30709 | 749 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S12580 Erina, the 11kV Panel 12 feeder tripped, reclosed, tripped and locked out A & B phase O/C. Abnormal switching LB44838 Closed, Sw A @ S14953 Open Tree / branch on mains outside 279 The Entrance road. See also 1764361, 62, 67, and 1765533 | April | 2020 | 2020Q4 | 2020 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2020-04-11 | N | 41 | N | 6 | N | N | 1.1101 | 39.4971 | 22441.2314
[7 empty] | 4614 | 13337 | 1764386 | 2020-04-11 13:55 | 2020-04-11 15:21 | 86 | 11kV | 31648 | 368 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S14891 Wyong Pa 5, CP 45101 Jilliby Dunks reclosed and then tripped on Overcurrent. Tree on 11kV OH mains at Jilliby Road. OMS 1764386, 1764408 | April | 2020 | 2020Q4 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2020-04-11 | N | 86 | N | 6 | N | N | 1.1101 | 39.4971 | 23127.4249
[7 empty] | 4363 | 10721 | 1764399 | 2020-04-11 14:42 | 2020-04-11 15:21 | 39 | 11kV | 59046 | 1514 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208720 2 fault operations A Phase Overcurrent 1409hrs Fdr 14394 Trip & Reclose Reports of material on Fdr Auto Reclose Switched Off 1442hrs Fdr 14394 Trip and lockout Surf Kite removed from Fdr near sub 5693 1521hrs Fdr 14394 Closed back on Excluded OMS 1764399 1764414 1764420 | April | 2020 | 2020Q4 | 2020 | 223:14394 | 223:14394 | ZN00223/014394 | LAKE MACQUARIE | OH | Veg | 2020-04-11 | N | 39 | N | 6 | N | N | 1.1101 | 39.4971 | 43149.0752
[7 empty] | 4171 | 9092 | 1764510 | 2020-04-11 17:43 | 2020-04-11 19:27 | 104 | 11kV | 4576 | 44 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | CP35910 interrupted by DOp Cause: 11kV resting on x-arm Abnnormal switching: Sw A open @ S.9535 Captain Sir Joseph, CP 35910 Closed. See oms 1764510, 1765523 | April | 2020 | 2020Q4 | 2020 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2020-04-11 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 3344.0058
[7 empty] | 4228 | 9550 | 1764514 | 2020-04-11 17:44 | 2020-04-11 19:35 | 111 | 11kV | 3330 | 30 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Air Break Switch | Unplanned | Wind Strong | N | LID 208723 Main contacts open circuit & flicker blades burnt on 11kV links 79632. Excluded OMS No. 1764512 | April | 2020 | 2020Q4 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-04-11 | N | 111 | N | 6 | N | N | 1.1101 | 39.4971 | 2433.4658
[7 empty] | 4286 | 10054 | 1764569 | 2020-04-11 22:27 | 2020-04-11 22:35 | 8 | 11kV | 1632 | 204 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | LID 208725 De energised Fdr 19072 to open faulty ABS 74247 Excluded OMS 1764569 | April | 2020 | 2020Q4 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2020-04-11 | N | 8 | N | 6 | N | N | 1.1101 | 39.4971 | 1192.6175
[7 empty] | 4868 | 15685 | 1764584 | 2020-04-12 03:04 | 2020-04-12 04:35 | 91 | 11kV | 59587 | 657 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 208728 2 fault operations B & C Phase Overcurrent SW-89061 L/O - 50T BC & 2nd trip 51OC LA's at Sw 74495 replaced Sw 74495 low gas had to be bypassed. | April | 2020 | 2020Q4 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-04-12 | N | 90.6956 | N | 6 | N | N | 1.1101 | 39.4971 | 43544.4221
[7 empty] | 5080 | 18127 | 1764600 | 2020-04-12 08:16 | 2020-04-12 11:25 | 189.1667 | 11kV | 10215 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208729 2 fault operation B & C Phase Overcurrent No cause found, feeder was patrolled. | April | 2020 | 2020Q4 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-04-12 | N | 189.1667 | N | 6 | N | N | 1.1101 | 39.4971 | 7464.8207
[7 empty] | 3955 | 6477 | 1764656 | 2020-04-12 12:38 | 2020-04-12 14:30 | 112 | 11kV | 672 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 208730 C Phase tapping at ABS 74247 ABS Replaced Excluded OMS 1764656 | April | 2020 | 2020Q4 | 2020 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2020-04-12 | N | 112 | N | 6 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 5278 | 19679 | 1764704 | 2020-04-12 16:22 | 2020-04-12 17:35 | 73 | 11kV | 58838 | 806 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 12650 West Gosford Panel 12R 'North Gosford' tripped on: A & B phase OC, EFI, Timing Relay, Lockout Relay Field EFIs: S48206 Abnormal switching: AB 43277 Closed, AB 40372 Open Tree branch on 11kV OH near PT 12352 Dolly Alison, Erina 1 B9 See 1764703, 1764704 | April | 2020 | 2020Q4 | 2020 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2020-04-12 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 42997.075
[7 empty] | 4062 | 7696 | 1764703 | 2020-04-12 16:23 | 2020-04-12 17:35 | 72.1667 | 11kV | 149168.5 | 2067 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 12650 West Gosford Panel 12R 'North Gosford' tripped on: A & B phase OC, EFI, Timing Relay, Lockout Relay Field EFIs: S48206 Abnormal switching: AB 43277 Closed, AB 40372 Open Tree branch on 11kV OH near PT 12352 Dolly Alison, Erina 1 B9 See 1764703, 1764704 | April | 2020 | 2020Q4 | 2020 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2020-04-12 | N | 72.1667 | N | 6 | N | N | 1.1101 | 39.4971 | 109007.9401
[7 empty] | 3653 | 3398 | 1764763 | 2020-04-13 09:01 | 2020-04-13 10:07 | 66 | 11kV | 156552 | 2372 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2310 Punchbowl PAnel 15 tripped on A phase earth fault and efi Cause: UG cable fault | April | 2020 | 2020Q4 | 2020 | ZN2310:PA15 | ZN2310:PA15 | ZN02310/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-04-13 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 114403.5841
[7 empty] | 5222 | 19264 | 1764839 | 2020-04-13 20:14 | 2020-04-13 21:30 | 76 | 11kV | 199228 | 2715 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.26 tripped on" O/C & E/F UG cable fault in front line section of feeder between Pnl.26, S8252 Sw/A,S6899 Sw/A & S778 Sw/B | April | 2020 | 2020Q4 | 2020 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2020-04-13 | N | 73.3805 | N | 2 | N | N | 1.1101 | 39.4971 | 145589.9462
[7 empty] | 4297 | 10196 | 1764853 | 2020-04-14 04:13 | 2020-04-14 09:07 | 294 | 11kV | 6437 | 171 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208734 2 fault operations C Phase Earth Fault; Sensitive Earth Fault Fault detector B - Sw 83495. Fault detector - ELB 64855. Sw 47926 - C phase E/F first trip, SEF second trip. 11kV OHM on ground pole SF-50052. Excluded OMS 1764853, 1764854 | April | 2020 | 2020Q4 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-04-14 | N | 37.6433 | N | 2 | N | N | 1.1101 | 39.4971 | 4703.9697
[7 empty] | 3599 | 2785 | 1764931 | 2020-04-14 10:06 | 2020-04-14 11:28 | 82 | 11kV | 78179 | 1011 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.15 tripped on: C phase OC, IOC UG cable damaged by excavator outside 10 Amy St, Campsie. (front line section of feeder) | April | 2020 | 2020Q4 | 2020 | ZN690:PA15 | ZN690:PA15 | ZN00690/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-04-14 | N | 77.3284 | N | 2 | N | N | 1.1101 | 39.4971 | 57130.9073
[7 empty] | 5055 | 17861 | 1764581 | 2020-04-12 01:43 | 2020-04-14 12:50 | 3547 | 11kV | 53202 | 141 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208727 3 fault operations Earth Fault Fault 11kV mains on the ground between pole AT-40042 and sub 59009. 2nd paragraph for sub 59009 to be completed when final repairs completed. Excluded OMS 1764581 | April | 2020 | 2020Q4 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-04-12 | N | 377.3191 | N | 6 | N | N | 1.1101 | 39.4971 | 38878.4524
[7 empty] | 3457 | 1589 | 1765164 | 2020-04-15 05:27 | 2020-04-15 07:30 | 122.95 | 11kV | 17458.9 | 142 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208746 A Phase DOLF : 40 Amp Possible Possum | April | 2020 | 2020Q4 | 2020 | 223:14393 | 223:14393 | ZN00223/014393 | LAKE MACQUARIE | OH | Not Veg | 2020-04-15 | N | 122.95 | N | 2 | N | N | 1.1101 | 39.4971 | 12758.4492
[7 empty] | 5154 | 18621 | 1765377 | 2020-04-15 23:58 | 2020-04-16 01:52 | 114 | 11kV | 137628 | 1286 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 12570 Avoca 11kV feeder Panel 26 "S49886 Avoca Aux No.11" tripped and locked out on: Relays: IOC B phase, EFI Field EFIs: S49886, S14846, S49472, S12855, S14126, S18394, S18293 At Recloser 40425 Kurrawyba Cadell Opened at same time as Zone CB, suspect grading issues - T/Pe to investigate. Relays: E/F trip UG cable fault identified between S18293 Henley Wilson (SW/B) to S14908 Maroomba Ash (SW/A). See 1765431, 1765432, 1765434 | April | 2020 | 2020Q4 | 2020 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2020-04-15 | N | 107.0202 | N | 2 | N | N | 1.1101 | 39.4971 | 100574.4831
[7 empty] | 4088 | 8053 | 1765470 | 2020-04-16 11:57 | 2020-04-16 13:55 | 118 | 11kV | 4956 | 42 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 208762 B & C Phase DOLF : 20 Amp Removed tree branch from OHM Excluded OMS 1765470, 1765544 | April | 2020 | 2020Q4 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-04-16 | N | 118 | N | 2 | N | N | 1.1101 | 39.4971 | 3621.6986
[7 empty] | 4809 | 15112 | 1765525 | 2020-04-16 17:10 | 2020-04-16 19:55 | 165 | 11kV | 1320 | 8 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208770 Vollts reported on pole 8M60078 by pole inspector. Excluded OMS 1765525 1765547 | April | 2020 | 2020Q4 | 2020 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2020-04-16 | N | 165 | N | 2 | N | N | 1.1101 | 39.4971 | 964.6171
[7 empty] | 3304 | 176 | 1765647 | 2020-04-17 11:14 | 2020-04-17 12:09 | 55 | 11kV | 59211 | 1179 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35400 North Sydney - Pnl.73 tripped on: Earth Fault UG cable fault between S79178 and S4375 See 1766457 1766458 | April | 2020 | 2020Q4 | 2020 | ZN35400:PA73 | ZN35400:PA73 | ZN35400/000073 | NORTH SYDNEY | UG | Not Veg | 2020-04-17 | N | 50.2214 | N | 2 | N | N | 1.1101 | 39.4971 | 43269.6524
[7 empty] | 3295 | 81 | 1765780 | 2020-04-17 22:36 | 2020-04-18 00:30 | 114 | 11kV | 228 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208783 Single phase DOLF : 10 Amp excluded OMS 1765780 | April | 2020 | 2020Q4 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | MUSWELLBROOK | OH | Veg | 2020-04-17 | N | 114 | N | 2 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 4430 | 11308 | 1765793 | 2020-04-18 07:56 | 2020-04-18 09:41 | 105 | 11kV | 125950 | 1230 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | At S 36000 Olympic Park Zone, Panel 24 Parramatta Alban tripped on: Feeder A: B phase IOC to N/E Feeder B: IOC B phase, EFI No abnormal switching. Jointer contacted Control Room advising duct ws being cut into at the time of trip. No injury Restoration switching from S36115 to 3685 @ 09:33 , from S78145 to S3685 @ 09:41 See OMS 1765793, 1765993, 1765998 | April | 2020 | 2020Q4 | 2020 | ZN36000:PA24 | ZN36000:PA24 | ZN36000/000024 | CUMBERLAND | UG | Not Veg | 2020-04-18 | N | 102.3984 | N | 4 | N | N | 1.1101 | 39.4971 | 92040.5451
[7 empty] | 4110 | 8295 | 1765854 | 2020-04-18 16:43 | 2020-04-18 17:48 | 65 | 33kV Distribution | 1040 | 16 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | No LID Report ABS 2740 burning up Normally open point moved to defective ABS Excluded OMS 1765854 | April | 2020 | 2020Q4 | 2020 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Not Veg | 2020-04-18 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 3299 | 135 | 1765847 | 2020-04-18 15:32 | 2020-04-18 20:12 | 280.1 | 11kV | 35292.6 | 126 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S5597 Newline Edward - A phase HV fuse blown Tree branch on mains. Fuse grading issue | April | 2020 | 2020Q4 | 2020 | ZN965:PA29 | ZN965:PA29 | ZN00965/000029 | HORNSBY | OH | Veg | 2020-04-18 | N | 280.1 | N | 4 | N | N | 1.1101 | 39.4971 | 25790.7911
[7 empty] | 3785 | 4895 | 1765859 | 2020-04-18 17:36 | 2020-04-19 00:35 | 419 | 11kV | 35265 | 120 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC61097 Wise Ferry Lavender 10.2 tripped on: OC Tree brought down OH mains are damaged cross arms near PT13629 See 1766462 1766463 | April | 2020 | 2020Q4 | 2020 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-04-18 | N | 293.875 | N | 4 | N | N | 1.1101 | 39.4971 | 25770.6219
[7 empty] | 3907 | 6004 | 1765940 | 2020-04-19 16:53 | 2020-04-19 19:24 | 151 | 11kV | 7748 | 54 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 208789 3 fault operations A Phase Instantaneous Overcurrent, Earth Fault Sw 42031 Aph EF 628amps Tapping burnt away from LA at Regulator. Needs fixing. Excluded oms 1765940 | April | 2020 | 2020Q4 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-04-19 | N | 143.4815 | N | 1 | N | N | 1.1101 | 39.4971 | 5662.0099
[7 empty] | 3463 | 1631 | 1766021 | 2020-04-20 10:30 | 2020-04-20 13:50 | 200 | 11kV | 135021 | 708 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208794 No cause found......But a guy was cutting trees up, no proof thou. Excluded oms 1766021. | April | 2020 | 2020Q4 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-04-20 | N | 190.7076 | N | 5 | N | N | 1.1101 | 39.4971 | 98669.3644
[7 empty] | 4752 | 14517 | 1765931 | 2020-04-20 11:14 | 2020-04-20 14:28 | 194 | 11kV | 4462 | 23 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 208795 pole 4m-90099 broken below ground level. Excluded OMS 1765931. | April | 2020 | 2020Q4 | 2020 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Not Veg | 2020-04-20 | N | 194 | N | 5 | N | N | 1.1101 | 39.4971 | 3260.698
[7 empty] | 3327 | 342 | 1766152 | 2020-04-20 18:20 | 2020-04-20 19:05 | 45 | 11kV | 38205 | 849 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca - Pnl.34 tripped, reclosed & tripped on: A & B phase IOC & OC Large tree across all 3 phases near LB44119 | April | 2020 | 2020Q4 | 2020 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2020-04-20 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 27919.0871
[7 empty] | 4663 | 13752 | 1766169 | 2020-04-20 19:10 | 2020-04-20 20:04 | 54 | 11kV | 4212 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC45117 Glenning Valley tripped, reclosed & tripped on: OC Tree on mains between LB44745 and PT13811 | April | 2020 | 2020Q4 | 2020 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2020-04-20 | N | 54 | N | 5 | N | N | 1.1101 | 39.4971 | 3078.0054
[7 empty] | 4357 | 10685 | 1766166 | 2020-04-20 19:02 | 2020-04-20 21:40 | 158 | 11kV | 119963 | 789 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12600 Lisarow - Pnl.2 tripped, reclosed & tripped on: A & C phase O/C UG cable fault between LB77072, S14337 Sw/A and S18040 Sw/A See 1766469 1766470 1766471 | April | 2020 | 2020Q4 | 2020 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | UG | Not Veg | 2020-04-20 | N | 152.0444 | N | 5 | N | N | 1.1101 | 39.4971 | 87665.4221
[7 empty] | 4002 | 7054 | 1766189 | 2020-04-21 06:20 | 2020-04-21 07:31 | 71 | 11kV | 175438 | 3002 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Lingsford - Pnl.9 tripped on Earth Fault (9L) UG cable fault between S8560 Sw/B, S3006 and S5472 Sw/A See 1766477 1766478 1766479 | April | 2020 | 2020Q4 | 2020 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2020-04-21 | N | 58.4404 | N | 6 | N | N | 1.1101 | 39.4971 | 128204.9159
[7 empty] | 5231 | 19337 | 1766187 | 2020-04-21 00:28 | 2020-04-21 09:00 | 512 | 11kV | 24172 | 67 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge - Pnl.8 tripped on SEF Cause not ascertained See 1766482 1766483 1766484 | April | 2020 | 2020Q4 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2020-04-21 | N | 360.7761 | N | 6 | N | N | 1.1101 | 39.4971 | 17664.1846
[7 empty] | 3639 | 3241 | 1766226 | 2020-04-21 09:04 | 2020-04-21 10:50 | 106 | 11kV | 424 | 4 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208804 C Phase DOLF : 10 Amp Excluded OMS 1766226 | April | 2020 | 2020Q4 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-04-21 | N | 106 | N | 6 | N | N | 1.1101 | 39.4971 | 309.8467
[7 empty] | 4122 | 8389 | 1766193 | 2020-04-21 07:04 | 2020-04-21 11:00 | 236 | 11kV | 236 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208810 C Phase NO PROTECTION OPERATED Three phase PT - 17047 has C phase live line lead was found broken away from top of DOLF. Excluded OMS 1766193. | April | 2020 | 2020Q4 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-04-21 | N | 236 | N | 6 | N | N | 1.1101 | 39.4971 | 172.4618
[7 empty] | 3939 | 6293 | 1766210 | 2020-04-21 08:00 | 2020-04-21 11:25 | 205 | 11kV | 205 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 208811 Fatigued fuse elelment Excluded OMS 1766210 | April | 2020 | 2020Q4 | 2020 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Not Veg | 2020-04-21 | N | 205 | N | 6 | N | N | 1.1101 | 39.4971 | 149.808
[7 empty] | 3454 | 1540 | 1766368 | 2020-04-21 18:05 | 2020-04-21 19:11 | 66 | 11kV | 103554 | 1569 | HV | Animal Flying Fox | Animal | UGOH | Unplanned | No Weather Impact | N | Zn1193 Lindfield -Pnl.26 tripped on: IOC A & B phase Bat on UGOH @ PT31475 | April | 2020 | 2020Q4 | 2020 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Not Veg | 2020-04-21 | N | 66 | N | 6 | N | N | 1.1101 | 39.4971 | 75674.2089
[7 empty] | 3341 | 477 | 1766487 | 2020-04-22 11:55 | 2020-04-22 12:55 | 60 | 11kV | 360 | 6 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 208824 Stay broken at sub 51649 | April | 2020 | 2020Q4 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-04-22 | N | 60 | N | 1 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 3936 | 6241 | 1766584 | 2020-04-23 06:35 | 2020-04-23 08:29 | 114 | 11kV | 98130 | 881 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.26 tripped on: B phase O/C UG cable fault in front line section between P26, S36265 and S35140 | April | 2020 | 2020Q4 | 2020 | ZN1788:PA26 | ZN1788:PA42 | ZN01788/000042 | RANDWICK | UG | Not Veg | 2020-04-23 | N | 111.3848 | N | 1 | N | N | 1.1101 | 39.4971 | 71710.5097
[7 empty] | 4829 | 15313 | 1766773 | 2020-04-24 10:15 | 2020-04-24 12:55 | 159.8167 | 11kV | 2716.8833 | 17 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | Insulator | Unplanned | No Weather Impact | N | LID 208853 oms contractor dropped tree on OHM. 1 phase came off pin. at 8V-20028 Excluded OMS 1766773 | April | 2020 | 2020Q4 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-04-24 | N | 159.8167 | N | 4 | N | N | 1.1101 | 39.4971 | 1985.4182
[7 empty] | 4797 | 14995 | 1766821 | 2020-04-24 13:04 | 2020-04-24 13:48 | 44 | 11kV | 1980 | 45 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208851 Broken insulator pole KR-30639 Excluded OMS 1766821, 1766849 | April | 2020 | 2020Q4 | 2020 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2020-04-24 | N | 44 | N | 4 | N | N | 1.1101 | 39.4971 | 1446.9256
[7 empty] | 3900 | 5969 | 1766854 | 2020-04-24 13:20 | 2020-04-24 17:46 | 266.2333 | 11kV | 286.2333 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208863 Increase transformer tap to 251V as pump load and voltage drop affecting pump protection EC attend reporting LV and causing pumps to shut down on soft start. Other day smart meter struck by lightning, AG bridged out and was reporting high voltage. AG turned down Taps on TX 50088. Check network, 'Chad' attended previously. no iso/quarantine. Excluded OMS 1766854 | April | 2020 | 2020Q4 | 2020 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2020-04-24 | N | 95.4111 | N | 4 | N | N | 1.1101 | 39.4971 | 209.1709
[7 empty] | 3949 | 6429 | 1766914 | 2020-04-24 20:11 | 2020-04-24 20:48 | 37 | 11kV | 48951 | 1323 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208864 possum pole NR60248 - no damage Sw 48705 Lemon Tree Passage Rd IR failed to operate Nil EFI's Excluded OMS 1766916 | April | 2020 | 2020Q4 | 2020 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2020-04-24 | N | 37 | N | 4 | N | N | 1.1101 | 39.4971 | 35771.947
[7 empty] | 4822 | 15255 | 1766980 | 2020-04-25 14:54 | 2020-04-25 21:35 | 401 | 11kV | 802 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 208866 No fuses blew, just internal fault inside TX, one phase 53V to ground. OMS job managed by depot not in control queue. Excluded OMS 1766980 | April | 2020 | 2020Q4 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2020-04-25 | N | 401 | N | 1 | N | N | 1.1101 | 39.4971 | 586.0779
[7 empty] | 5216 | 19186 | 1767093 | 2020-04-26 18:07 | 2020-04-26 20:17 | 130 | 11kV | 136814 | 1235 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1673 Turramurra Zone, 11kV CB Panel 18 Turramurra Aux No.2 tripped. Relays: C phase IOC, L/O, EFI, F/C. Partial restoration from S4698 to S36233 failed. UG 11 kV feeder cable fault between S46717 and S36233 and LB 1840. Abnormal Switching: LB 2209 Closed, AB 3019 Open. See also OMS 1767096, 1767102, 1767093, 1767706 | April | 2020 | 2020Q4 | 2020 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | UG | Not Veg | 2020-04-26 | N | 110.7806 | N | 3 | N | N | 1.1101 | 39.4971 | 99979.6359
[7 empty] | 3930 | 6169 | 1767079 | 2020-04-26 15:26 | 2020-04-26 23:29 | 483 | 11kV | 15574 | 118 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208871 2 fault operations Overcurrent; Earth Fault Tree fallen on mains pole GV-97007. Broken crossarm replaced under AP Excluded OMS 1767079 | April | 2020 | 2020Q4 | 2020 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2020-04-26 | N | 131.9831 | N | 3 | N | N | 1.1101 | 39.4971 | 11381.0198
[7 empty] | 3771 | 4790 | 1767063 | 2020-04-26 14:19 | 2020-04-27 01:15 | 655.5333 | 11kV | 7866.4 | 12 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 208872 Tree fell on 11kV OHM near pole FR-35171 towards FR-30002. | April | 2020 | 2020Q4 | 2020 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2020-04-26 | N | 655.5333 | N | 3 | N | N | 1.1101 | 39.4971 | 5748.5331
[7 empty] | 3774 | 4800 | 1767122 | 2020-04-27 06:20 | 2020-04-27 08:51 | 151 | 11kV | 204679 | 1525 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S 12570 Avoca Zone, 11 kV Panel 37 "S 18439 Picketts Scenic 0.7" CB tripped on SEL. At AB 43386, Centre phase bond burnt off. See 1767122 | April | 2020 | 2020Q4 | 2020 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2020-04-27 | N | 134.2157 | N | 3 | N | N | 1.1101 | 39.4971 | 149573.3762
[7 empty] | 4008 | 7091 | 1767173 | 2020-04-27 09:34 | 2020-04-27 11:10 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208877 C Phase DOLF : 16 Amp Excluded OMS 1767173 | April | 2020 | 2020Q4 | 2020 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-04-27 | N | 96 | N | 3 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 4331 | 10446 | 1767287 | 2020-04-27 15:25 | 2020-04-27 16:19 | 54 | 11kV | 97254 | 1801 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35900 Potts Hill Zone, 11 kV CB Panel 17 Tripped, reclosed, tripped and locked out Relays: Earth fault left, EFI, Inst Earth Fault left, Reclose, Lockout 11 kV UG cable fault between CB 17 at zone and S1265 Hill Rd See also 1767287 | April | 2020 | 2020Q4 | 2020 | ZN35900:PA17 | ZN35900:PA17 | ZN35900/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-04-27 | N | 54 | N | 3 | N | N | 1.1101 | 39.4971 | 71070.3547
[7 empty] | 4780 | 14824 | 1767450 | 2020-04-28 13:05 | 2020-04-28 14:43 | 98 | 11kV | 240215 | 2715 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.26 tripped on: C phase OC UG cable fault in front line section of feeder between Pnl.26, S8252, S6899 & S778 | April | 2020 | 2020Q4 | 2020 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2020-04-28 | N | 88.477 | N | 4 | N | N | 1.1101 | 39.4971 | 175542.0369
[7 empty] | 4571 | 12807 | 1767435 | 2020-04-28 12:07 | 2020-04-28 16:25 | 258 | 11kV | 516 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208899 C Phase DOLF : 16 Amp excluded OMS 1767435 | April | 2020 | 2020Q4 | 2020 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2020-04-28 | N | 258 | N | 4 | N | N | 1.1101 | 39.4971 | 377.0776
[7 empty] | 3973 | 6653 | 1767491 | 2020-04-28 15:32 | 2020-04-28 16:59 | 87 | 11kV | 848 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.4 tripped on B & C phase O/C UG cable fault between S18446, S14776 and S18323 See 17676586 1767588 | April | 2020 | 2020Q4 | 2020 | ZN12690:PA4 | ZN12690:PA4 | ZN12690/000004 | CENTRAL COAST | UG | Not Veg | 2020-04-28 | N | 84.8 | N | 4 | N | N | 1.1101 | 39.4971 | 619.6934
[7 empty] | 3801 | 5025 | 1767518 | 2020-04-28 18:42 | 2020-04-28 19:33 | 51 | 11kV | 62067 | 1217 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.19 tripped on SEL Abnormal: S18559 Sw/B open DMA with S15400 Sw/F Closed SEL relay defective | April | 2020 | 2020Q4 | 2020 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | Exclude | Not Veg | 2020-04-28 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 45356.7329
[7 empty] | 4268 | 9952 | 1767716 | 2020-04-29 16:45 | 2020-04-29 19:15 | 150 | 11kV | 7650 | 51 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 208911 Replace defective crossarm Section isolated for emerg repairs pole HR-33301 Scobies Lane. Excluded OMS 1767716 | April | 2020 | 2020Q4 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2020-04-29 | N | 150 | N | 1 | N | N | 1.1101 | 39.4971 | 5590.3944
[7 empty] | 4041 | 7451 | 1767765 | 2020-04-30 07:38 | 2020-04-30 09:55 | 137 | 11kV | 16736 | 133 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 208918 3 Phase Sensitive Earth Fault Fdr patrolled, isolated subs 72252, 70060 & 72249 isolated, for repair and power restored. Sub 72249 defective transformer Excluded OMS 1767765 | April | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-04-30 | N | 125.8346 | N | 8 | N | N | 1.1101 | 39.4971 | 12230.1752
[7 empty] | 4990 | 17065 | 1767749 | 2020-04-30 01:54 | 2020-04-30 11:53 | 599 | 11kV | 66542 | 666 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 208912 Blown HV Bond at pole JU-67140 Excluded OMS 1767819 | April | 2020 | 2020Q4 | 2020 | 202:34232 | 202:34232 | ZN00202/034232 | NEWCASTLE | OH | Not Veg | 2020-04-30 | N | 99.9129 | N | 8 | N | N | 1.1101 | 39.4971 | 48626.9309
[7 empty] | 3465 | 1645 | 1767823 | 2020-04-30 10:46 | 2020-04-30 11:53 | 67 | 11kV | 67 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 208921 3 phase DOLF : 10 Amp Excluded OMS 1767823 | April | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-04-30 | N | 67 | N | 8 | N | N | 1.1101 | 39.4971 | 48.9616
[7 empty] | 4175 | 9130 | 1767848 | 2020-04-30 07:38 | 2020-04-30 12:10 | 272 | 11kV | 544 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 208922 Single phase Defective Lightning arrestor | April | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-04-30 | N | 272 | N | 8 | N | N | 1.1101 | 39.4971 | 397.5392
[7 empty] | 3497 | 2003 | 1767868 | 2020-04-30 12:37 | 2020-04-30 13:08 | 31 | 11kV | 26319 | 849 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn12570 Avoca - Pnl.34 tripped on: B & C phase IOC Tree hit LV mains and caught fire. | April | 2020 | 2020Q4 | 2020 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2020-04-30 | N | 31 | N | 8 | N | N | 1.1101 | 39.4971 | 19233.1489
[7 empty] | 3421 | 1200 | 1767849 | 2020-04-30 07:38 | 2020-04-30 15:30 | 472 | 11kV | 944 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 208924 Single phase replaced faulty tx after storm. Excluded oms 1767765 | April | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-04-30 | N | 472 | N | 8 | N | N | 1.1101 | 39.4971 | 689.8474
[7 empty] | 4081 | 7980 | 1767958 | 2020-04-30 17:33 | 2020-04-30 18:20 | 47 | 11kV | 60873 | 2139 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 187 Crows Nest, 11kV Panel 20 "Emmett Pacific etc" tripped on Earth Fault. UG cable fault from S6584 to S48018. See also 1767958, 1768128 | April | 2020 | 2020Q4 | 2020 | ZN187:PA20 | ZN187:PA20 | ZN00187/000020 | NORTH SYDNEY | UG | Not Veg | 2020-04-30 | N | 28.4586 | N | 8 | N | N | 1.1101 | 39.4971 | 44484.193
[7 empty] | 4149 | 8688 | 1767988 | 2020-04-30 22:26 | 2020-05-01 01:35 | 189 | 11kV | 275235 | 1771 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9245 Engadine Zone, 11kV CB Panel 10 "S9089 Railway Mianga" tripped, reclosed, tripped and locked out. Relays: Earth Fault, EFI, Lockout. Abnormal Switching at time of interruption: SW/A Open @ S 9434 Rawson Business Centre, SW/B Closed @ S9818 Wheatley Glenora. UG cable fault between LB 35188 and LB35504 and S9345 Carnarvon Yanchep. | April | 2020 | 2020Q4 | 2020 | ZN9245:PA10 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | UG | Not Veg | 2020-04-30 | N | 155.4122 | N | 8 | N | N | 1.1101 | 39.4971 | 201133.6199
[7 empty] | 4943 | 16527 | 1768066 | 2020-05-01 10:30 | 2020-05-01 11:54 | 84 | 11kV | 66720 | 942 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208939 2 fault operation C Phase Overcurrent Fdr 74181 abnormally feeding majority of Fdr 74184. ABS 74679 OPEN/ABS 74417 CLOSED. Sw 74181 Denman sub T/R/T/Lo @ 1030hrs. Sw 74434 Riverview Rd RAGCB T/R/T/Lo @ 1031hrs. Cph 11kV wire down between poles 8M-80109 & 8M-80108. Excluded OMS No. 1768064, 1768069, 1768066, 1768166. See also LID #208940. | May | 2020 | 2020Q4 | 2020 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2020-05-01 | N | 70.828 | N | 8 | N | N | 1.1101 | 39.4971 | 48757.0081
[7 empty] | 4747 | 14481 | 1768041 | 2020-05-01 09:39 | 2020-05-01 13:17 | 218 | 11kV | 9972 | 187 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208933 1 fault operation Sensitive Earth Fault Tree brough down 11kV OHM between poles EO-80755 & EO-80007. Excluded OMS No. 1768041 | May | 2020 | 2020Q4 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-05-01 | N | 53.3262 | N | 8 | N | N | 1.1101 | 39.4971 | 7287.2435
[7 empty] | 5234 | 19358 | 1768064 | 2020-05-01 10:30 | 2020-05-01 14:53 | 263 | 11kV | 43319 | 193 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208940 2 fault operations C phase Fdr 74181 abnormally feeding majority of Fdr 74184. ABS 74679 OPEN/ABS 74417 CLOSED. Sw 74181 Denman sub T/R/T/Lo @ 1030hrs. Sw 74434 Riverview Rd RAGCB T/R/T/Lo @ 1031hrs. Cph 11kV wire down between poles 8M-80109 & 8M-80108. Excluded OMS No. 1768064, 1768069, 1768066, 1768166. See also LID #208939. | May | 2020 | 2020Q4 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-05-01 | N | 224.4508 | N | 8 | N | N | 1.1101 | 39.4971 | 31656.2475
[7 empty] | 3589 | 2734 | 1768226 | 2020-05-01 16:06 | 2020-05-01 17:00 | 54 | 11kV | 54 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | HV bond off near UGOH to S14177 Bateau Bay STW | May | 2020 | 2020Q4 | 2020 | ZN12610:PA5 | ZN12610:PA5 | ZN12610/000005 | CENTRAL COAST | OH | Not Veg | 2020-05-01 | N | 54 | N | 8 | N | N | 1.1101 | 39.4971 | 39.4616
[7 empty] | 5301 | 19843 | 1769560 | 2020-05-01 15:15 | 2020-05-01 17:15 | 120 | 11kV | 8160 | 68 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | PT11441Cromarty Hill North Scenic -HV Interrupted PT12881 North Scenic Forresters - dist #2 - Interrupted Pole replacement near PT11441 See 1769561 1769560 | May | 2020 | 2020Q4 | 2020 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2020-05-01 | N | 120 | N | 8 | N | N | 1.1101 | 39.4971 | 5963.0873
[7 empty] | 3531 | 2309 | 1768107 | 2020-05-01 11:24 | 2020-05-01 18:40 | 436 | 11kV | 19184 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC44853 Ourimbah Bumble tripped on OC Large tree on mains between poles OU684 and OU685 | May | 2020 | 2020Q4 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-05-01 | N | 436 | N | 8 | N | N | 1.1101 | 39.4971 | 14019.1014
[7 empty] | 4906 | 16008 | 1768264 | 2020-05-01 20:12 | 2020-05-01 22:12 | 120 | 11kV | 90509 | 942 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208941 2 fault operations B Phase Earth Fault mains broken between poles 8M80108 & 8M80109 Fault beyond Sw 74434 Riverview RAGCB which operated also. Possible malgrade in this network configuration. Excluded OMS 1768265 & 1768264 Also see LID # 208943. | May | 2020 | 2020Q4 | 2020 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2020-05-01 | N | 96.0817 | N | 8 | N | N | 1.1101 | 39.4971 | 66141.3076
[7 empty] | 3861 | 5604 | 1768265 | 2020-05-01 20:12 | 2020-05-02 01:42 | 330 | 11kV | 45552 | 193 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208943 2 fault operations overcurrent mains broken between poles 8M80108 & 8M80109 Fault beyond Sw 74434 Riverview RAGCB which operated also. Possible malgrade in this network configuration. Excluded OMS 1768265 & 1768264 Also see LID # 208941. | May | 2020 | 2020Q4 | 2020 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-05-01 | N | 236.0207 | N | 8 | N | N | 1.1101 | 39.4971 | 33288.058
[7 empty] | 3561 | 2580 | 1768288 | 2020-05-02 08:14 | 2020-05-02 11:25 | 191 | 11kV | 764 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208946 blown spur fuse DOLF : 20 Amp | May | 2020 | 2020Q4 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-05-02 | N | 191 | N | 15 | N | N | 1.1101 | 39.4971 | 558.3087
[7 empty] | 3651 | 3382 | 1768417 | 2020-05-02 12:57 | 2020-05-02 15:08 | 131 | 11kV | 50566 | 386 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn 14891 Wyong, Ex 11kV Panel 20, CP 50560 Hue Hue Sandra has tripped and locked out on OC. Tree / branch on OH mains near CP 40665 | May | 2020 | 2020Q4 | 2020 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2020-05-02 | N | 131 | N | 15 | N | N | 1.1101 | 39.4971 | 36952.1414
[7 empty] | 3433 | 1355 | 1768365 | 2020-05-02 11:21 | 2020-05-02 15:45 | 263.9333 | 11kV | 28768.7333 | 109 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208956 Broken LL lead. LV interconnected while waiting for crew. Excluded OMS 1768388 | May | 2020 | 2020Q4 | 2020 | 532:83301 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Not Veg | 2020-05-02 | N | 263.9333 | N | 15 | N | N | 1.1101 | 39.4971 | 21023.3418
[7 empty] | 4936 | 16447 | 1768360 | 2020-05-02 11:13 | 2020-05-02 15:55 | 282 | 11kV | 282 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208953 Broken Live Line Lead Excluded OMS 1768360 | May | 2020 | 2020Q4 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-05-02 | N | 282 | N | 15 | N | N | 1.1101 | 39.4971 | 206.0773
[7 empty] | 4485 | 11873 | 1768470 | 2020-05-02 11:30 | 2020-05-02 16:30 | 300 | 11kV | 9000 | 134 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208954 Broken LL lead at sub 50785 was seen by DOp. Had to open off Fdr at Sw 42382 to get lead off OHM. As OMS job 1768288 was still open it rolled up to Sw 42382. Excluded OMS 1768288 | May | 2020 | 2020Q4 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2020-05-02 | N | 67.1642 | N | 15 | N | N | 1.1101 | 39.4971 | 6576.9345
[7 empty] | 4705 | 14152 | 1768306 | 2020-05-02 09:05 | 2020-05-02 16:50 | 465 | 11kV | 303875 | 1635 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208945 2 fault operations A phase Overcurrent; Earth Fault Tree broke HV conductor between poles TB-50096 & TB-50098.Due to location, 4 substations could not be restored until repairs were completed. 1300kVA of connected capacity in this location. Potentially HV into LV which required EMSOs to check some installations (thus increasing duration). Note: 2 May 2020 was a very windy/stormy day. There were multiple interruptions and OMS jobs throughout the day which would have further slowed this response down (finish prior job before getting to site). Excluded OMS 1768304. | May | 2020 | 2020Q4 | 2020 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2020-05-02 | N | 185.8563 | N | 15 | N | N | 1.1101 | 39.4971 | 222062.8872
[7 empty] | 4262 | 9921 | 1768367 | 2020-05-02 11:13 | 2020-05-02 17:25 | 372 | 11kV | 9471 | 63 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN 12630 Peats Ridge, Ex Panel 3 "Mangrove Mountain Feeder", CP 46895 Wise Ferry Ironbark tripped on SEL. 4 bays of 11kV OH down between CP 46895 and CP 44845. | May | 2020 | 2020Q4 | 2020 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2020-05-02 | N | 150.3333 | N | 15 | N | N | 1.1101 | 39.4971 | 6921.1275
[7 empty] | 4700 | 14107 | 1768511 | 2020-05-02 15:15 | 2020-05-02 17:48 | 153 | 11kV | 119036 | 866 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | At ZN 14143 Somersby, 11kV Panel 17 CB "Somersby Falls" tripped. Relays: A and B phase OC, IOC, EFI. Tree / branch on OH mains between PT18807 and PT 13021. Blown clear. | May | 2020 | 2020Q4 | 2020 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-05-02 | N | 137.455 | N | 15 | N | N | 1.1101 | 39.4971 | 86987.9978
[7 empty] | 4704 | 14145 | 1768453 | 2020-05-02 13:44 | 2020-05-02 18:52 | 308 | 11kV | 114154 | 388 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Wind Strong | N | At ZN 14891 Wyong, Ex Panel 12 "Yarramalong", Recloser 50630 Yarramalong Chandler 0.1 has tripped and locked out. Relays: OC Trip, LO. Tree / branch brought down 3 bays of overhead HV mains at CP 44771. | May | 2020 | 2020Q4 | 2020 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2020-05-02 | N | 294.2113 | N | 15 | N | N | 1.1101 | 39.4971 | 83420.3762
[7 empty] | 3922 | 6137 | 1768425 | 2020-05-02 13:09 | 2020-05-02 20:40 | 451 | 11kV | 129651 | 2037 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208955 OHM down from pole HR-92039 Excluded OMS 1768425 | May | 2020 | 2020Q4 | 2020 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2020-05-02 | N | 63.648 | N | 15 | N | N | 1.1101 | 39.4971 | 94745.1267
[7 empty] | 4292 | 10109 | 1768585 | 2020-05-02 18:58 | 2020-05-02 20:46 | 108 | 11kV | 16524 | 153 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN 15014 Mona Vale, Ex 11kV Panel 14 "Walnut Mona etc" loss of supply beyond CP20433 due to burnt bond. OMS 1768591, 1768585 | May | 2020 | 2020Q4 | 2020 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Not Veg | 2020-05-02 | N | 108 | N | 15 | N | N | 1.1101 | 39.4971 | 12075.2518
[7 empty] | 4118 | 8356 | 1768431 | 2020-05-02 13:20 | 2020-05-02 21:30 | 490 | 11kV | 940 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 208958 A Phase DOLF : 16 Amp A Phase Dist : 200 Amp Private LV pole and mains down, sub isolated to cut away lv mains and restore lvf. 16 amp hvf also replaced. Excluded OMS 1768431 | May | 2020 | 2020Q4 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-05-02 | N | 235 | N | 15 | N | N | 1.1101 | 39.4971 | 686.9243
[7 empty] | 5253 | 19470 | 1768392 | 2020-05-02 12:04 | 2020-05-02 22:45 | 641 | 11kV | 15880 | 120 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC46803 tripped on: SEL OH mains down beyong USL44005 See 1769725 1769726 | May | 2020 | 2020Q4 | 2020 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2020-05-02 | N | 132.3333 | N | 15 | N | N | 1.1101 | 39.4971 | 11604.6356
[7 empty] | 4850 | 15547 | 1768605 | 2020-05-03 06:17 | 2020-05-03 08:05 | 108 | 11kV | 19872 | 184 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S6846 Belmore Waratah - No.1, 2 & #3 HV CBs tripped on low gas Low gas in CB No.3 | May | 2020 | 2020Q4 | 2020 | ZN2602:PA30 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | Unknown | Not Veg | 2020-05-03 | N | 108 | N | 4 | N | N | 1.1101 | 39.4971 | 14521.8715
[7 empty] | 3481 | 1837 | 1768535 | 2020-05-02 15:54 | 2020-05-03 15:10 | 1396 | 11kV | 6754 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208960 Tree leaning on 22kV OHM between pole 8w-20011 & 8w-20012. Excluded OMS 1768535,1768601 | May | 2020 | 2020Q4 | 2020 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-05-02 | N | 750.4444 | N | 15 | N | N | 1.1101 | 39.4971 | 4935.624
[7 empty] | 4760 | 14567 | 1768629 | 2020-05-03 09:53 | 2020-05-03 15:15 | 322 | 11kV | 6097 | 23 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 208967 3 fault operations 3 phase Overcurrent; Earth Fault tree on mains pole 7F40003 Excluded oms 1768629 | May | 2020 | 2020Q4 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-05-03 | N | 265.087 | N | 4 | N | N | 1.1101 | 39.4971 | 4455.5078
[7 empty] | 4678 | 13912 | 1768668 | 2020-05-03 16:45 | 2020-05-03 17:20 | 35 | 11kV | 735 | 21 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT12035 Interrupted from LK42282 to remove large tree from mains | May | 2020 | 2020Q4 | 2020 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2020-05-03 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 537.1163
[7 empty] | 4744 | 14456 | 1768738 | 2020-05-04 07:59 | 2020-05-04 09:15 | 76 | 11kV | 608 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 208976 B & C Phase DOLF : 16 Amp Excluded OMS 1768738 | May | 2020 | 2020Q4 | 2020 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-05-04 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 444.3085
[7 empty] | 3705 | 4025 | 1768699 | 2020-05-03 17:08 | 2020-05-04 09:30 | 982 | 11kV | 982 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 208979 LV Insulator failed in service Excluded OMS 1768699 | May | 2020 | 2020Q4 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-05-03 | N | 982 | N | 4 | N | N | 1.1101 | 39.4971 | 717.6166
[7 empty] | 4828 | 15302 | 1768916 | 2020-05-04 14:45 | 2020-05-04 16:40 | 115 | 11kV | 2300 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 208983 A Phase Wire stranded near PT 27225 Cant. | May | 2020 | 2020Q4 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2020-05-04 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 1680.7722
[7 empty] | 4846 | 15519 | 1768745 | 2020-05-04 15:53 | 2020-05-04 17:45 | 112 | 11kV | 4928 | 44 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | At ZN 12650 West Gosford, Ex 11kV Panel 1 Ourimbah Bumble, Rec 44853 tripped and locked out. 11kV OH feeder found to be touching pole step outside 528 Ourimbah Creek Rd, Palm Grove. See also 1768943, 1768745 | May | 2020 | 2020Q4 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2020-05-04 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 3601.237
[7 empty] | 4963 | 16763 | 1768986 | 2020-05-05 05:40 | 2020-05-05 07:10 | 90 | 11kV | 129060 | 1434 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 342 Paddington, 11kV Panel 23 "Renny Lane" tripped on: Relays: OC, Earth Fault FNG 1A N. Suspected UG cable fault between start of feeder and S7839 Remy Lane. | May | 2020 | 2020Q4 | 2020 | ZN342:PA23 | ZN342:PA23 | ZN00342/000023 | SYDNEY | UG | Not Veg | 2020-05-05 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 94313.2414
[7 empty] | 4814 | 15173 | 1769053 | 2020-05-05 09:26 | 2020-05-05 12:20 | 174 | 11kV | 29826 | 689 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 208993 A Phase note HV mains low within reach, NOT on ground due to insulator dead end breaking. Excluded oms 1769053/9025 | May | 2020 | 2020Q4 | 2020 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2020-05-05 | N | 43.2888 | N | 5 | N | N | 1.1101 | 39.4971 | 21795.9611
[7 empty] | 3921 | 6124 | 1769122 | 2020-05-05 12:05 | 2020-05-05 12:25 | 20 | 11kV | 760 | 38 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 208992 Following item 35 SI 56327, VT failed at Coolmoore Stud Sectionaliser Sw 4716. Excluded OMS 1769122 | May | 2020 | 2020Q4 | 2020 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | Unknown | Not Veg | 2020-05-05 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 555.3856
[7 empty] | 3875 | 5717 | 1769172 | 2020-05-05 13:30 | 2020-05-05 13:50 | 20 | 11kV | 660 | 33 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | at Zn 12570 Avoca, ex 11kV panel 33 Macmasters Beach, AB 44320 interrupted for safety to allow removal of tree branch. | May | 2020 | 2020Q4 | 2020 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2020-05-05 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 482.3085
[7 empty] | 4669 | 13817 | 1769267 | 2020-05-05 23:47 | 2020-05-06 00:18 | 31 | 11kV | 3596 | 116 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 208998 B Phase DOLF : 40 Amp Fuse carrier burnt up - replaced | May | 2020 | 2020Q4 | 2020 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2020-05-05 | N | 31 | N | 5 | N | N | 1.1101 | 39.4971 | 2627.8507
[7 empty] | 3620 | 3000 | 1769280 | 2020-05-06 07:41 | 2020-05-06 08:35 | 54 | 11kV | 27540 | 510 | HV | Burnt Contacts | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | At Zn 1287 Revesby, Ex 11kV Panel 3, bond burnt off B phase at 11kV ABS, CP 2371. See also 1769280 | May | 2020 | 2020Q4 | 2020 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-05-06 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 20125.4197
[7 empty] | 3950 | 6441 | 1769586 | 2020-05-06 12:25 | 2020-05-06 13:25 | 60 | 11kV | 78660 | 1311 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN690 Campsie, 11kV CB Panel 36 "Mooney Woolcott" tripped. Relays: Earth leakage, EFI, fault check. HV UG cable fault from origin of feeder to S4925 Mooney Woolcott Sw/A. See also 1769366 | May | 2020 | 2020Q4 | 2020 | ZN690:PA36 | ZN690:PA36 | ZN00690/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-05-06 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 57482.4079
[7 empty] | 4654 | 13654 | 1769343 | 2020-05-06 10:53 | 2020-05-06 14:00 | 187 | 11kV | 3179 | 17 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209011 NAR 57067 done as emergency work. | May | 2020 | 2020Q4 | 2020 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2020-05-06 | N | 187 | N | 4 | N | N | 1.1101 | 39.4971 | 2323.1194
[7 empty] | 4860 | 15620 | 1769331 | 2020-05-06 10:02 | 2020-05-06 19:40 | 578 | 11kV | 11925 | 36 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209016 11kV OHM broke between poles GP-43085 & GP-40010. See also LID 208997 the Sandhills recloser tripped and reclosed at 2246 the day before, it is possible this is the fault the caused the trip and reclose. Excluded OMS No. 1769331 | May | 2020 | 2020Q4 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-05-06 | N | 331.25 | N | 4 | N | N | 1.1101 | 39.4971 | 8714.4383
[7 empty] | 4163 | 9003 | 1769472 | 2020-05-07 02:07 | 2020-05-07 04:10 | 123 | 11kV | 85320 | 1131 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.14 tripped on: B phase O/C UG cable fault between S48392, S35133 tee S35273 See 1769732 1769733 1769734 | May | 2020 | 2020Q4 | 2020 | ZN1788:PA14 | ZN1788:PA14 | ZN01788/000014 | RANDWICK | UG | Not Veg | 2020-05-07 | N | 75.4377 | N | 2 | N | N | 1.1101 | 39.4971 | 62349.3395
[7 empty] | 5096 | 18212 | 1769623 | 2020-05-07 18:50 | 2020-05-07 20:18 | 88 | 11kV | 13904 | 158 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 209025 Isolated section to replace broken xarm pole GW-60082. Excluded OMS 1769623, 17696 | May | 2020 | 2020Q4 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2020-05-07 | N | 88 | N | 2 | N | N | 1.1101 | 39.4971 | 10160.6331
[7 empty] | 3690 | 3782 | 1769839 | 2020-05-09 15:26 | 2020-05-10 01:00 | 574 | 11kV | 64506.3667 | 113 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S3528 Quigg Cant, All LV Distributors interrupted for safety. Car hit pole on Canterbury Rd, requiring pole replacement. CC1: 22-"Refer to SOp" | May | 2020 | 2020Q4 | 2020 | ZN2310:PA14 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-05-09 | N | 570.8528 | N | 1 | N | N | 1.1101 | 39.4971 | 47139.3501
[7 empty] | 3575 | 2651 | 1769965 | 2020-05-10 13:12 | 2020-05-10 16:50 | 218 | 11kV | 102600 | 904 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.12 tripped on SEF Abnormal: LB63181 Closed with iR63174 Open DMA UGOH downstream of S35697 open circuit See 1770945 1770946 | May | 2020 | 2020Q4 | 2020 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | Unknown | Unknown | 2020-05-10 | N | 113.4956 | N | 2 | N | N | 1.1101 | 39.4971 | 74977.0538
[7 empty] | 4673 | 13841 | 1770000 | 2020-05-10 19:21 | 2020-05-10 20:53 | 92 | 11kV | 102028 | 1109 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.43 tripped on Earth Fault UG cable fault between S48722 and S9073 See 1770940 1770941 | May | 2020 | 2020Q4 | 2020 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | UG | Not Veg | 2020-05-10 | N | 92 | N | 2 | N | N | 1.1101 | 39.4971 | 74559.0531
[7 empty] | 5205 | 19005 | 1770015 | 2020-05-11 00:58 | 2020-05-11 18:50 | 1072 | 11kV | 171716 | 1400 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | Zn12610 Long Jetty Pnl.9 tripped on OC S.18426 Ozone Ocean engulfed in fire, 11kv UGOH bonds blown off above LB41784 S18426 Dist #1 - Direct Distributor restored by MG See 1770926 1770927 1770929 1770930 | May | 2020 | 2020Q4 | 2020 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | UG | Not Veg | 2020-05-11 | N | 122.6543 | N | 1 | N | N | 1.1101 | 39.4971 | 125484.988
[7 empty] | 5276 | 19638 | 1770226 | 2020-05-12 06:00 | 2020-05-12 08:25 | 145 | 11kV | 112399 | 1360 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S10998 Rockdale Zone, 11kV CB Panel 18 "Wollongong Allen" tripped on Earth Fault. Suspected cable fault in section of 11kV UG feeder from S78518 SW/B to S10888 SW/A, Tee S10558 to S62761 SW/B. See also 1770539 1770533 | May | 2020 | 2020Q4 | 2020 | ZN10998:PA18 | ZN10998:PA18 | ZN10998/000018 | BAYSIDE | UG | Not Veg | 2020-05-12 | N | 82.6463 | N | 2 | N | N | 1.1101 | 39.4971 | 82137.874
[7 empty] | 4612 | 13326 | 1769376 | 2020-05-02 17:49 | 2020-05-12 14:30 | 14201 | 11kV | 15353 | 2 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind Strong | N | LID 208959 Pole FM-10091 fell over in high winds. Excluded OMS No. 1768575 + 1769376 | May | 2020 | 2020Q4 | 2020 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2020-05-02 | N | 7676.5 | N | 15 | N | N | 1.1101 | 39.4971 | 11219.5196
[7 empty] | 3590 | 2753 | 1770365 | 2020-05-12 15:30 | 2020-05-12 18:30 | 180 | 11kV | 33660 | 187 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 209065 Termination insulator failed on ABS 5656. Excluded OMS No. 1770365 | May | 2020 | 2020Q4 | 2020 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2020-05-12 | N | 180 | N | 2 | N | N | 1.1101 | 39.4971 | 24597.7352
[7 empty] | 4280 | 10018 | 1770411 | 2020-05-13 07:10 | 2020-05-13 09:50 | 160 | 11kV | 1440 | 9 | HV | Animal Possum | Animal | DC Transformer | Unplanned | No Weather Impact | N | At PT13500 Barnes George Downes 0.6, Ex Peats Rigde Zn Panel 8, Centre phase High Voltage dropout fuse operated. Dead possum found at pole base. | May | 2020 | 2020Q4 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-05-13 | N | 160 | N | 4 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 3476 | 1801 | 1770430 | 2020-05-13 08:59 | 2020-05-13 10:14 | 75.3333 | 11kV | 56048 | 744 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn15001 Brookevale Pnl.18 - Bond burnt off near USL21622 | May | 2020 | 2020Q4 | 2020 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Not Veg | 2020-05-13 | N | 75.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 40958.2253
[7 empty] | 4271 | 9985 | 1770574 | 2020-05-13 17:40 | 2020-05-13 19:00 | 80 | 11kV | 320 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209083 A & B Phase DOLF : 20 Amp fdr patrolled no faults found, replaced A & B ph hvfs power restored 1900. mdv Excluded oms 1770574 | May | 2020 | 2020Q4 | 2020 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-05-13 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 4389 | 10937 | 1770610 | 2020-05-13 23:40 | 2020-05-14 02:33 | 173 | 11kV | 251871 | 1689 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.36 tripped, reclosed & tripped on: A & B phase IOC Cause not ascertained. Supply restored. Pnl.36 recently transferred from Pnl.28R and found Pnl.36 has reclosing but not shown on diagram or SAO. See 1770951 1770952 1770953 | May | 2020 | 2020Q4 | 2020 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Veg | 2020-05-13 | N | 149.1243 | N | 4 | N | N | 1.1101 | 39.4971 | 184059.8979
[7 empty] | 3369 | 681 | 1770944 | 2020-05-15 13:20 | 2020-05-15 14:30 | 70 | 11kV | 700 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 209114 Leakage current reported at pole AF-60143. Excluded OMS 1770831 | May | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-05-15 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 4269 | 9967 | 1771012 | 2020-05-15 17:40 | 2020-05-15 18:46 | 66 | 11kV | 21186 | 321 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12360 Peats Ridge ZN, 11kV Panel 10 tripped and locked out. Relays: A and B Phase OC, RC and LO Tree on OH mains adjacent PT14624 Housten Wiseferry | May | 2020 | 2020Q4 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-05-15 | N | 66 | N | 5 | N | N | 1.1101 | 39.4971 | 15482.1039
[7 empty] | 4901 | 15977 | 1771036 | 2020-05-15 19:19 | 2020-05-15 21:25 | 126 | 11kV | 73362 | 620 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 2400 Berowra, Ex 11kV Panel 11, CP 1239 Brooklyn tripped and locked out Relays: IOC trip, OC trip. | May | 2020 | 2020Q4 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2020-05-15 | N | 118.3258 | N | 5 | N | N | 1.1101 | 39.4971 | 53610.7858
[7 empty] | 5014 | 17345 | 1771045 | 2020-05-15 20:16 | 2020-05-15 23:45 | 209 | 11kV | 19461 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At ZN 15013 Terrey Hills Ex 11kV Panel 10, CP 1126 Mona Vale Rd tripped and locked out relays: IOC trip, OC trip and LO. Abnormal Switching: CP20129 Open, CP20234 Closed. Cause not ascertained. | May | 2020 | 2020Q4 | 2020 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2020-05-15 | N | 180.1944 | N | 5 | N | N | 1.1101 | 39.4971 | 14221.5248
[7 empty] | 5103 | 18247 | 1771054 | 2020-05-15 22:47 | 2020-05-16 00:13 | 86 | 11kV | 111816 | 1302 | HV | 3rd Party Vehicle | 3rd Party Impact | UGOH | Unplanned | No Weather Impact | N | At S 36200 Empire Bay Zone, 11kV CB Panel 11 "Empire Bay Aux" tripped and locked out on: Earth leakage Motor Vehicle accident at 107 Empire Bay Drive, causing damage to 11kV UGOH from CP42818 to S50259, tee PT 12229. See also 1771602, 1771054, 1771604 | May | 2020 | 2020Q4 | 2020 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | UG | Not Veg | 2020-05-15 | N | 85.8802 | N | 5 | N | N | 1.1101 | 39.4971 | 81711.8348
[7 empty] | 4070 | 7769 | 1771058 | 2020-05-16 04:09 | 2020-05-16 05:15 | 66 | 11kV | 8382 | 127 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209119 A Phase DOLF : 31 Amp Possum on transformer Excluded OMS 1771058 | May | 2020 | 2020Q4 | 2020 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2020-05-16 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 6125.3184
[7 empty] | 4764 | 14668 | 1771064 | 2020-05-16 06:50 | 2020-05-16 15:30 | 520 | 11kV | 36358 | 108 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At S 15013 Terry Hills Zone, Ex Panel 10 Mona Vale Aumuna, Recloser CP1126 "Mona Vale Rd" has tripped and locked out on OC trip, EF, lockout. Abnormal Switching: CP 20129 Open, CP 20234 Closed. Faulty surge arrestor between CP 20184 to CP 78527 tee PT 15672. See also OMS 177120, 1771623, 1771619 | May | 2020 | 2020Q4 | 2020 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2020-05-16 | N | 336.6481 | N | 2 | N | N | 1.1101 | 39.4971 | 26569.354
[7 empty] | 4129 | 8468 | 1771207 | 2020-05-17 18:33 | 2020-05-17 20:59 | 145.7333 | 11kV | 12487.7667 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | PT1527 Glencoe Avenue - Roadside HDO blown Abnormal: PT2257 Mactier Ave- Dist #1 - Defective section of UG and in LV // with PT1527 Cause not ascertained See 1771207 1771210 | May | 2020 | 2020Q4 | 2020 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-05-17 | N | 130.0809 | N | 1 | N | N | 1.1101 | 39.4971 | 9125.6916
[7 empty] | 3537 | 2355 | 1771226 | 2020-05-18 06:53 | 2020-05-18 08:22 | 89 | 11kV | 101485 | 1199 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209127 Bird between phases at pole AK-61670. Excluded OMS 1771226 | May | 2020 | 2020Q4 | 2020 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2020-05-18 | N | 84.6414 | N | 4 | N | N | 1.1101 | 39.4971 | 74162.2447
[7 empty] | 3926 | 6156 | 1771301 | 2020-05-18 10:22 | 2020-05-18 16:45 | 383 | 11kV | 25496 | 102 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC44995 Kulnura tripped on: OC Tree on mains adjacent PT13323 See 1772003 1772004 | May | 2020 | 2020Q4 | 2020 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2020-05-18 | N | 249.9608 | N | 4 | N | N | 1.1101 | 39.4971 | 18631.7248
[7 empty] | 3416 | 1141 | 1771278 | 2020-05-18 09:44 | 2020-05-18 17:30 | 466 | 11kV | 91336 | 196 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At PT 243 High St, HV fuse blown on Centre Phase. Customers reporting abnormal voltages. PT 1739 Dist 1 also affected as in LV // at time of failure. see 1771864, 5 | May | 2020 | 2020Q4 | 2020 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-05-18 | N | 466 | N | 4 | N | N | 1.1101 | 39.4971 | 66745.6548
[7 empty] | 4753 | 14518 | 1771412 | 2020-05-18 16:15 | 2020-05-18 17:55 | 100 | 11kV | 14200 | 142 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209136 B Phase DOLF : 40 Amp DOP reports all dolf assemblies need replacing. Excluded OMS 1771412, 1771416, 1771429. | May | 2020 | 2020Q4 | 2020 | 223:14393 | 223:14393 | ZN00223/014393 | LAKE MACQUARIE | OH | Veg | 2020-05-18 | N | 100 | N | 4 | N | N | 1.1101 | 39.4971 | 10376.9412
[7 empty] | 4167 | 9062 | 1771785 | 2020-05-19 05:36 | 2020-05-19 14:55 | 559 | 11kV | 6542 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 12650 West Gosford, Ex Panel 1, CP45010 Palm Grove has tripped. Relays: OC and EF. See also 1771785 , 86 | May | 2020 | 2020Q4 | 2020 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-05-19 | N | 363.4444 | N | 3 | N | N | 1.1101 | 39.4971 | 4780.7006
[7 empty] | 5342 | 20325 | 1771648 | 2020-05-19 16:54 | 2020-05-19 17:21 | 27 | 11kV | 11205 | 415 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | iR44444 Geoffrey Royle tripped on: OC Bird near PT13087 Note: Refer to OMS 1772012 customers then impacted by further events | May | 2020 | 2020Q4 | 2020 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2020-05-19 | N | 27 | N | 3 | N | N | 1.1101 | 39.4971 | 8188.2835
[7 empty] | 3426 | 1278 | 1771651 | 2020-05-19 17:21 | 2020-05-19 19:29 | 128 | 11kV | 76336 | 670 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Berkeley Vale Pnl.6 - Bond burnt off between LB41187 & tee PT13076 See 1772012 1772013 | May | 2020 | 2020Q4 | 2020 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2020-05-19 | N | 113.9343 | N | 3 | N | N | 1.1101 | 39.4971 | 55784.0973
[7 empty] | 3946 | 6400 | 1771684 | 2020-05-20 04:28 | 2020-05-20 05:56 | 88 | 11kV | 176 | 2 | HV | Vandalism | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | LId 209150 1 fault operation 3 phase Overcurrent Vandalism Kiosk fire 39389 | May | 2020 | 2020Q4 | 2020 | 525:34580 | 525:34580 | ZN00525/034580 | CESSNOCK | Unknown | Not Veg | 2020-05-20 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 128.6156
[7 empty] | 4722 | 14296 | 1771685 | 2020-05-20 04:35 | 2020-05-20 06:03 | 88 | 11kV | 35528 | 427 | HV | Vandalism | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | LID 209151 1 fault operation 3 phase Kiosk fire 39389 Excluded OMS 1771684 | May | 2020 | 2020Q4 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | Unknown | Not Veg | 2020-05-20 | N | 83.2037 | N | 4 | N | N | 1.1101 | 39.4971 | 25962.8145
[7 empty] | 3979 | 6685 | 1771701 | 2020-05-20 08:22 | 2020-05-20 09:28 | 66 | 11kV | 4120 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209152 1 fault operation Overcurrent Reclose function at Sw 74927 was non auto due to planned switching 55937, so could not auto reclose. Feeder was patrolled and no cause found. Excluded OMS 1771701 | May | 2020 | 2020Q4 | 2020 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2020-05-20 | N | 41.2 | N | 4 | N | N | 1.1101 | 39.4971 | 3010.7745
[7 empty] | 5243 | 19416 | 1771704 | 2020-05-20 08:40 | 2020-05-20 12:47 | 247 | 11kV | 2964 | 12 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 209156 Emergency replacement of condemend pole AG 20013. Apparently pole inspection contractors knew of this yesterday but did not pass on until 615 this morning. Excluded OMS 1771704 | May | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-05-20 | N | 247 | N | 4 | N | N | 1.1101 | 39.4971 | 2166.0038
[7 empty] | 4381 | 10851 | 1772015 | 2020-05-21 15:25 | 2020-05-21 16:29 | 64 | 11kV | 2560 | 40 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 209178 broken bridging pin at pole AH-42113, section isolated for repairs Excluded oms 1772020 | May | 2020 | 2020Q4 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-05-21 | N | 64 | N | 1 | N | N | 1.1101 | 39.4971 | 1870.7725
[7 empty] | 4781 | 14833 | 1772096 | 2020-05-22 05:27 | 2020-05-22 08:40 | 193 | 11kV | 195436 | 1555 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Panel 7 @ ZN10999 Kogarah tripped and reclosed to Locked Out Relays Overcurrent E/F (51C) EFI Reclose Relay, lockout relay,fault check Signals - 11 kV Trip Fiels EFI's - Nil 11 kV UGOH Fault on Pole to tee off S10582 See 1773621,1773623 1772096 1772133 | May | 2020 | 2020Q4 | 2020 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | UG | Not Veg | 2020-05-22 | N | 125.6823 | N | 4 | N | N | 1.1101 | 39.4971 | 142818.8644
[7 empty] | 3527 | 2262 | 1772120 | 2020-05-22 07:38 | 2020-05-22 11:55 | 257 | 11kV | 5789 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | REC47742 Euloo Peats Ridge - tripped on: Earth Fault Tree brought down OH mains at pole PR280 See 1773371 1773372 | May | 2020 | 2020Q4 | 2020 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-05-22 | N | 199.6207 | N | 4 | N | N | 1.1101 | 39.4971 | 4230.4305
[7 empty] | 5323 | 20075 | 1772106 | 2020-05-22 08:32 | 2020-05-22 12:00 | 208.2 | 11kV | 11867.4 | 57 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | PT10466 Victor Palmerston - 11kV Interrupted from S10644 to S10076 due to defective pole. | May | 2020 | 2020Q4 | 2020 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | GEORGES RIVER | OH | Not Veg | 2020-05-22 | N | 208.2 | N | 4 | N | N | 1.1101 | 39.4971 | 8672.3459
[7 empty] | 5136 | 18474 | 1772268 | 2020-05-22 15:51 | 2020-05-22 18:55 | 183.5667 | 11kV | 1835.6667 | 10 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 209192 No protection operation, LLC burnt up at sub 71067. | May | 2020 | 2020Q4 | 2020 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2020-05-22 | N | 183.5667 | N | 4 | N | N | 1.1101 | 39.4971 | 1341.4511
[7 empty] | 3346 | 509 | 1772547 | 2020-05-24 13:47 | 2020-05-24 16:01 | 134 | 11kV | 116982 | 873 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | REC35756 Bundeena tripped on: O/C DOp patrolled, suspect trees contacted mains on CNR Bundeena and Liverpool Rd | May | 2020 | 2020Q4 | 2020 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2020-05-24 | N | 134 | N | 1 | N | N | 1.1101 | 39.4971 | 85486.9952
[7 empty] | 5060 | 17923 | 1772623 | 2020-05-25 03:31 | 2020-05-25 15:40 | 729 | 11kV | 65778 | 152 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 209205 B & C Phase DOLF : 31 Amp Replace sub 23186 Excluded OMS 1772623 | May | 2020 | 2020Q4 | 2020 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2020-05-25 | N | 432.75 | N | 3 | N | N | 1.1101 | 39.4971 | 48068.6223
[7 empty] | 5264 | 19560 | 1772847 | 2020-05-25 13:59 | 2020-05-25 15:57 | 118 | 11kV | 44542 | 426 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn8000 Macquarie Park Panel 10 Tripped on relays Earth Fault with fault check on Pa10 Left Signals: 11kV trip TX1 Group Earth With EFI Cause: UG cable fault - form S64450 North Ryde Station S02 to S7979 Richardson See OMS 1773166 1773167 1772847 | May | 2020 | 2020Q4 | 2020 | ZN8000:PA10 | ZN8000:PA10 | ZN08000/000010 | RYDE | UG | Not Veg | 2020-05-25 | N | 104.5587 | N | 3 | N | N | 1.1101 | 39.4971 | 32549.9798
[7 empty] | 4526 | 12278 | 1772944 | 2020-05-25 18:30 | 2020-05-25 20:00 | 90 | 11kV | 270 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 209214 Single phase DOLF : 10 Amp Dead Cockatoo found on site. Excluded OMS 1772944 | May | 2020 | 2020Q4 | 2020 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-05-25 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 4123 | 8403 | 1773010 | 2020-05-26 05:14 | 2020-05-26 10:45 | 331 | 11kV | 172781 | 1008 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn3153 St Ives - Pnl.11 tripped on C Phase IOC 2nd Attempt: tripped on: C phase IOC (CB shooting through) UG cable fault between S7763 and S4911 tee S4919 PE called in to fix CB shooting through See 1773507 1773508 | May | 2020 | 2020Q4 | 2020 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | UG | Not Veg | 2020-05-26 | N | 171.4097 | N | 3 | N | N | 1.1101 | 39.4971 | 126263.2586
[7 empty] | 4600 | 13189 | 1773003 | 2020-05-26 01:36 | 2020-05-26 13:10 | 694 | 11kV | 39714 | 115 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209217 2 fault operations Glen McIntosh found a possum at CCT L/A pole FQ-95213. This may have been the initial fault causing single phasing to the Intellirupter. Could this increase voltages at the intellirupter due to capacitive charging causing the L/A at the Intellirupter to blow. B Ph L/A was reaplaced at Intellirupter 64037. Excluded OMS 1772995, 1773003, 1773040 | May | 2020 | 2020Q4 | 2020 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Not Veg | 2020-05-26 | N | 345.3391 | N | 3 | N | N | 1.1101 | 39.4971 | 29021.8198
[7 empty] | 5221 | 19258 | 1772993 | 2020-05-26 01:32 | 2020-05-26 18:10 | 998 | 11kV | 408250 | 695 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | REC62731 Narara Creek Mans tripped on: O/C On restoration attempt REC62730 tripped 2 x UG faults in sections between (S18117 Sw/B, S12869 Sw/B and LB41157) + ( S14568 Sw/A and S18118 Sw/A tee PT12869, S12643, PT49023) See 1773496 1773497 1773498 | May | 2020 | 2020Q4 | 2020 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | UG | Not Veg | 2020-05-26 | N | 587.4101 | N | 3 | N | N | 1.1101 | 39.4971 | 298337.0587
[7 empty] | 5304 | 19901 | 1773465 | 2020-05-27 11:45 | 2020-05-27 17:45 | 360 | 11kV | 4640 | 13 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 209236 Field staff sighted ABS 74223 with 2 phases only making contact with flicker blades, tried to adjust but failed, Isolation required to mskr repairs. Excluded OMS 1773406, 1773466 | May | 2020 | 2020Q4 | 2020 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2020-05-27 | N | 356.9231 | N | 4 | N | N | 1.1101 | 39.4971 | 3390.7751
[7 empty] | 3860 | 5594 | 1773528 | 2020-05-27 21:06 | 2020-05-27 21:45 | 39 | 11kV | 663 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT12500 Beaufort Serpentine - Interrupted 11kV from AB44638 to AB43307 to remove tree from OH mains | May | 2020 | 2020Q4 | 2020 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2020-05-27 | N | 39 | N | 4 | N | N | 1.1101 | 39.4971 | 484.5008
[7 empty] | 3871 | 5685 | 1773490 | 2020-05-27 21:46 | 2020-05-27 21:52 | 6 | 11kV | 24 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC26228 Valley Rd - Interrupted 3 PTs beyond to remove tree from 11kV mains | May | 2020 | 2020Q4 | 2020 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2020-05-27 | N | 6 | N | 4 | N | N | 1.1101 | 39.4971 | 17.5385
[7 empty] | 4672 | 13832 | 1773536 | 2020-05-27 23:20 | 2020-05-28 07:16 | 476 | 11kV | 229864 | 1231 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209239 1 fault operation 3 phase Sensitive Earth Fault 11kV wire down cnr telarah st and ivor st. high into low. dq Excluded oms 1773536 | May | 2020 | 2020Q4 | 2020 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Not Veg | 2020-05-27 | N | 186.7295 | N | 4 | N | N | 1.1101 | 39.4971 | 167977.8314
[7 empty] | 3438 | 1371 | 1773709 | 2020-05-28 15:46 | 2020-05-28 15:56 | 10 | 11kV | 270 | 27 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse | Unplanned | No Weather Impact | N | At PT 15361 Kulgoa Cr 240 LHS and Centre phase fuses blown Cause not ascertained See 1773709 | May | 2020 | 2020Q4 | 2020 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2020-05-28 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 4296 | 10185 | 1773747 | 2020-05-28 17:54 | 2020-05-28 18:44 | 50 | 11kV | 27250 | 545 | HV | Animal Flying Fox | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | At Zone 965 Pennant Hills Panel 2 "Bishop Boyd etc' Circuit Breker feeder tripped on: Relays: EF, EFI Signals : 11kV Trip, TX #1 Group Earth, Zone Earth Field EFIs: S4968 Bat failed explosively at PT1385 | May | 2020 | 2020Q4 | 2020 | ZN965:PA2 | ZN965:PA2 | ZN00965/000002 | HORNSBY | OH | Not Veg | 2020-05-28 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 19913.4963
[7 empty] | 4142 | 8635 | 1773714 | 2020-05-28 15:57 | 2020-05-28 19:45 | 228 | 11kV | 684 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209251 Bph broken LV Tx lead & Cph Tx LV lead repaired. Supply restored at 1945hrs. | May | 2020 | 2020Q4 | 2020 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2020-05-28 | N | 228 | N | 3 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 3427 | 1284 | 1773954 | 2020-05-30 01:54 | 2020-05-30 05:22 | 207.3333 | 11kV | 2280.6667 | 11 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Section off 11kV feeder interrupted between REC45055 to LB62481 tee PT14459 to allow repairs following car hit pole | May | 2020 | 2020Q4 | 2020 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2020-05-30 | N | 207.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 1666.6439
[7 empty] | 4864 | 15640 | 1773963 | 2020-05-30 05:28 | 2020-05-30 14:20 | 532 | 11kV | 8367 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC24722 Forest Crazier tripped, reclosed & locked out Cause not ascertained See 1774737 1774739 | May | 2020 | 2020Q4 | 2020 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2020-05-30 | N | 209.175 | N | 4 | N | N | 1.1101 | 39.4971 | 6114.3568
[7 empty] | 5260 | 19523 | 1774038 | 2020-05-30 13:29 | 2020-05-30 20:20 | 411 | 11kV | 822 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209262 Single Phase Tree on service wire. Sub isolated for live work pause. Service from sub pole to customers 'A' pole has come away. Crew required to retension. Service is being held up by Isolated service at LV sub fuse slack creek bridge is landmark - bottle brush tree has fallen and DW are down low - power on at gahams place but cannot contact neighbour to confirm - graham advised he has cut tree off wire and propped it up - adv to stay 8m back for safety 30/05/20 18:00: Graham called - advised that we are coming back to retension | May | 2020 | 2020Q4 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-05-30 | N | 411 | N | 4 | N | N | 1.1101 | 39.4971 | 600.6934
[7 empty] | 4611 | 13310 | 1774027 | 2020-05-30 14:11 | 2020-05-31 15:00 | 1489 | 11kV | 63660 | 60 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC1238 Milsons Passage - tripped & locked out Tree brought down OH mains. Customer Leong Lim was cutting down branches may have brought down 11kV See 1774689 1774685 1774684 | May | 2020 | 2020Q4 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2020-05-30 | N | 1061 | N | 4 | N | N | 1.1101 | 39.4971 | 46520.8503
[7 empty] | 5185 | 18840 | 1774232 | 2020-06-01 11:44 | 2020-06-01 14:08 | 143.7667 | 11kV | 4600.5333 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209277 No cause found, not storm conditions Single Phase 16Amp fuse | June | 2020 | 2020Q4 | 2020 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Veg | 2020-06-01 | N | 143.7667 | N | 5 | N | N | 1.1101 | 39.4971 | 3361.9341
[7 empty] | 4325 | 10412 | 1774254 | 2020-06-01 12:18 | 2020-06-01 14:15 | 117 | 11kV | 819 | 7 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 209278 Single Phase Broken LLC sub 71102, sub isolated for repairs | June | 2020 | 2020Q4 | 2020 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2020-06-01 | N | 117 | N | 5 | N | N | 1.1101 | 39.4971 | 598.501
[7 empty] | 4229 | 9554 | 1774278 | 2020-06-01 13:45 | 2020-06-01 14:47 | 62 | 11kV | 28706 | 463 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.44 tripped on B & C phase OC Cause not ascertained | June | 2020 | 2020Q4 | 2020 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Veg | 2020-06-01 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 20977.4981
[7 empty] | 4336 | 10487 | 1774317 | 2020-06-01 17:55 | 2020-06-01 18:30 | 35 | 11kV | 140 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 209281 Branch has come down onto wires, pole # PP90670 running north from service pole wires are sagging about 10ft off ground. No arcing or sparking, concerned for safety as it is very windy. | June | 2020 | 2020Q4 | 2020 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-06-01 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 3805 | 5066 | 1774312 | 2020-06-01 16:22 | 2020-06-01 21:30 | 308 | 11kV | 308 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 209282 HV lead has come off on sub 52146. Reported by Stephen Oliver. | June | 2020 | 2020Q4 | 2020 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2020-06-01 | N | 308 | N | 5 | N | N | 1.1101 | 39.4971 | 225.0773
[7 empty] | 4803 | 15068 | 1774518 | 2020-06-02 16:14 | 2020-06-02 19:00 | 166 | 11kV | 3153.4 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Ex Peats Ridge Pnl.3 - Auto Link 46938 was found open and defective on 1 phase. Auto link previously worked on that day NAR57271. By pass LB46938Z closed and warning tag left. See 1774518 | June | 2020 | 2020Q4 | 2020 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2020-06-02 | N | 165.9684 | N | 2 | N | N | 1.1101 | 39.4971 | 2304.4117
[7 empty] | 3891 | 5861 | 1774514 | 2020-06-02 16:01 | 2020-06-02 22:11 | 370 | 11kV | 262729 | 2053 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12640 Unima - Pnl.13 tripped, reclosed & locked out on: B Phase O/C Pelican had flown into 11 KV overhead open wire conductor near pole BR240 & tangled itself & the wire together.This burnt the wire to the ground & also burnt off bonds in two other locations.At BR240 one bay of .64.cu conductor was repaired. At BR348 and BR358 locations the 11 KV bonds were replaced. These last locations were very difficult to access and took longer than may have been expected to achieve. PT13954-D1 (HV into LV) outside No58 Patonga St - No damage found or protection operated at cust. MSB's in vicinity & at LV open points | June | 2020 | 2020Q4 | 2020 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2020-06-02 | N | 127.9732 | N | 2 | N | N | 1.1101 | 39.4971 | 191994.604
[7 empty] | 4834 | 15388 | 1774831 | 2020-06-03 20:20 | 2020-06-03 21:05 | 45 | 11kV | 3690 | 82 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | At S14891 Wyong Zone, Ex Panel 5, CP 45017 Whiteman was opened by DOp to allow emergency repairs to 11kV OH pin insulator. Also 1774831 | June | 2020 | 2020Q4 | 2020 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2020-06-03 | N | 45 | N | 1 | N | N | 1.1101 | 39.4971 | 2696.5432
[7 empty] | 3778 | 4821 | 1774850 | 2020-06-04 03:23 | 2020-06-04 04:28 | 65 | 11kV | 87828 | 1361 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn12640 Umina - Pnl.4 tripped on IOC Possum found burnt at base of UGOH outside 47 Melbourne St (Near S14989) see 1774943 1774944 | June | 2020 | 2020Q4 | 2020 | ZN12640:PA4 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2020-06-04 | N | 64.532 | N | 2 | N | N | 1.1101 | 39.4971 | 64182.1119
[7 empty] | 3424 | 1231 | 1774942 | 2020-06-04 12:19 | 2020-06-04 16:14 | 235 | 11kV | 4700 | 20 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209325 Tree dangerously close to mains. KR-30366. | June | 2020 | 2020Q4 | 2020 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2020-06-04 | N | 235 | N | 2 | N | N | 1.1101 | 39.4971 | 3434.6214
[7 empty] | 4441 | 11417 | 1775059 | 2020-06-05 02:12 | 2020-06-05 07:55 | 343 | 11kV | 35672 | 104 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209329 Replaced B Phase 40Amp substation DOLF Possum at base of pole also refer to OMS 1775065 & 1775059 | June | 2020 | 2020Q4 | 2020 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2020-06-05 | N | 343 | N | 4 | N | N | 1.1101 | 39.4971 | 26068.0455
[7 empty] | 3838 | 5418 | 1775238 | 2020-06-05 18:23 | 2020-06-05 20:45 | 142 | 11kV | 155547 | 1516 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 1285 Greenacre Park Zn, 11kV Panel 17 "S64560" Feeder CB tripped. Relays: EFI Earth fault. Abnormal Switching: S4398 Dist 2 in LV //. UG cable fault in section of 11kV feeder from S77608 to S7247 to S1708. | June | 2020 | 2020Q4 | 2020 | ZN1285:PA17 | ZN37100:PA6 | ZN37100/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-06-05 | N | 102.6036 | N | 4 | N | N | 1.1101 | 39.4971 | 113669.1597
[7 empty] | 3333 | 413 | 1775205 | 2020-06-05 18:04 | 2020-06-05 21:26 | 202 | 11kV | 120496 | 1180 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209339 Tension joint broke, dead side/back feed through delta winding fell on the ground. CB 83126 did not trip High impedance fault. CB sw83126 open by SOp. Note: 'See 209338 for Trip reclose and targets. | June | 2020 | 2020Q4 | 2020 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2020-06-05 | N | 102.1153 | N | 4 | N | N | 1.1101 | 39.4971 | 88054.9228
[7 empty] | 5268 | 19587 | 1775294 | 2020-06-06 08:17 | 2020-06-06 10:45 | 148 | 11kV | 1332 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 209342 replace insulators pole AG-50354 | June | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-06-06 | N | 148 | N | 1 | N | N | 1.1101 | 39.4971 | 973.3863
[7 empty] | 4416 | 11215 | 1775218 | 2020-06-05 18:06 | 2020-06-06 12:10 | 1084 | 11kV | 226700 | 213 | HV | Overload Operational | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Pnl.11 Berowra - Temp 11kV generator supplying Dangar Island tripped on suspected O/L See NAR57210 See 1776226 1776228 1776229 | June | 2020 | 2020Q4 | 2020 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | Unknown | Not Veg | 2020-06-05 | N | 1064.3192 | N | 4 | N | N | 1.1101 | 39.4971 | 165665.6735
[7 empty] | 3539 | 2378 | 1775506 | 2020-06-08 01:11 | 2020-06-08 08:35 | 443.55 | 11kV | 24395.25 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Rain Light | N | LID 209346 C phase 63 Amp fuse Dolf carrier burning up. Customers reporting fluctuating supply aslo see 'OMS 1775506 | June | 2020 | 2020Q4 | 2020 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-06-08 | N | 443.55 | N | 2 | N | N | 1.1101 | 39.4971 | 17827.3292
[7 empty] | 3411 | 1088 | 1775527 | 2020-06-08 08:16 | 2020-06-08 09:14 | 58 | 11kV | 123830 | 2135 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.22 tripped on B & C phase IOC Bird on mains outside 84 Willson | June | 2020 | 2020Q4 | 2020 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Not Veg | 2020-06-08 | N | 58 | N | 2 | N | N | 1.1101 | 39.4971 | 90491.3116
[7 empty] | 4659 | 13700 | 1775850 | 2020-06-10 04:53 | 2020-06-10 07:45 | 172 | 11kV | 135795 | 926 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.26 tripped, reclosed and locked out on Earth fault Field EFIs: S6153 S4988 S79820 S7942 UG cable fault between S7942, S4494 tee PT1988 See 1775931 1775934 1775935 | June | 2020 | 2020Q4 | 2020 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2020-06-10 | N | 146.6469 | N | 3 | N | N | 1.1101 | 39.4971 | 99234.9807
[7 empty] | 3571 | 2623 | 1775857 | 2020-06-10 06:35 | 2020-06-10 08:20 | 105 | 11kV | 2100 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 209357 Found blown A phase 10 Amp spur fuse at 17006. DO required Fuse Fatigued | June | 2020 | 2020Q4 | 2020 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2020-06-10 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 1534.6181
[7 empty] | 4427 | 11288 | 1776071 | 2020-06-10 19:10 | 2020-06-10 21:15 | 125 | 11kV | 2500 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 209368 A Phase 10 Amp Line Dolf fuse fatigue. OMS Report no 1776071. | June | 2020 | 2020Q4 | 2020 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2020-06-10 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 1826.9263
[7 empty] | 4773 | 14768 | 1776198 | 2020-06-11 11:48 | 2020-06-11 13:10 | 82 | 11kV | 42460 | 1388 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209373 Dumont Cl sw cubicle on fire section isolated for repairs. Gillette Cl sub interconnected all customers restored. Prot. 51C Excluded oms 1776198 | June | 2020 | 2020Q4 | 2020 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2020-06-11 | N | 30.5908 | N | 4 | N | N | 1.1101 | 39.4971 | 31028.5156
[7 empty] | 5297 | 19818 | 1776152 | 2020-06-11 10:34 | 2020-06-11 13:50 | 196 | 11kV | 135572 | 1456 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S15002 Narrabeen Zone, 11kV Panel 8 "Nareen Taitara" CB has tripped on: Relays: Earth fault with fault check Abnormal Switching: Sw/B closed @ S16686, CP 24376 Open. Suspect UG cable fault in section of UG feeder to S16646. See also 1776151/2 | June | 2020 | 2020Q4 | 2020 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | UG | Not Veg | 2020-06-11 | N | 93.1126 | N | 4 | N | N | 1.1101 | 39.4971 | 99072.0189
[7 empty] | 3914 | 6050 | 1776267 | 2020-06-11 15:58 | 2020-06-11 17:10 | 72 | 11kV | 1008 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209377 11kV mains too low adjacent Craig sub 315. | June | 2020 | 2020Q4 | 2020 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-06-11 | N | 72 | N | 4 | N | N | 1.1101 | 39.4971 | 736.6167
[7 empty] | 4191 | 9273 | 1776163 | 2020-06-11 11:07 | 2020-06-11 20:45 | 578.25 | 11kV | 71703 | 124 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | AT S9577 Fowler Bignell TX and associated LV distributors isolated. Car hit pole at 22 Fowler Rd Illawong. 1776163, 1776165 | June | 2020 | 2020Q4 | 2020 | ZN9900:PA12 | ZN9900:PA12 | ZN09900/000012 | SUTHERLAND | OH | Not Veg | 2020-06-11 | N | 578.25 | N | 4 | N | N | 1.1101 | 39.4971 | 52398.4375
[7 empty] | 4988 | 17021 | 1776342 | 2020-06-12 09:24 | 2020-06-12 10:52 | 88 | 11kV | 174504 | 2014 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn10999 Kogarah panel 19L tripped on Relays: Earth Fault, EFI and Fault Check Cause: UG cable fault from S10511 Baxter Cross SW/B to S10202 SW/A See OMS 177510 1777511 1776342 | June | 2020 | 2020Q4 | 2020 | ZN10999:PA19 | ZN10999:PA19 | ZN10999/000019 | BAYSIDE | UG | Not Veg | 2020-06-12 | N | 86.6455 | N | 2 | N | N | 1.1101 | 39.4971 | 127522.3762
[7 empty] | 4077 | 7930 | 1776396 | 2020-06-12 12:10 | 2020-06-12 13:21 | 71 | 11kV | 34933 | 495 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S 35700 Port Botany Zone, 11kV Panel 10 "Botany Point" tripped. relays : 51 B, 51 N, EFI. UG cable fault in section of 11kV feeder from S.8708 to S.6789 to S.6192. Contractor underboring outside #1901 Botany Rd Matraville. Likely cause. | June | 2020 | 2020Q4 | 2020 | ZN35700:PA10 | ZN35700:PA10 | ZN35700/000010 | RANDWICK | UG | Not Veg | 2020-06-12 | N | 70.5717 | N | 2 | N | N | 1.1101 | 39.4971 | 25528.0061
[7 empty] | 4718 | 14270 | 1776503 | 2020-06-13 05:27 | 2020-06-13 10:30 | 303 | 11kV | 87390 | 2163 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 209392 sw 34254 open by S.O 11kV wire off pin at pole JU-61576 LINEWORKERS CONFIRMED NO ARCING WHERE 11KV LINE WAS SITTING ON 3 SERVICES. VISUAL INSPECTION PERFORMED ON DISTRIBUTOR HP00218/218L, NO FAILURES FOUND or damage to surrounding installations Also interrupt LH LVF 218. Excluded oms 1776503 | June | 2020 | 2020Q4 | 2020 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Not Veg | 2020-06-13 | N | 40.4022 | N | 4 | N | N | 1.1101 | 39.4971 | 63862.0344
[7 empty] | 3779 | 4823 | 1776540 | 2020-06-13 09:18 | 2020-06-13 11:50 | 152 | 11kV | 304 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 209395 DOP found LLC cable dangling. customer advised this has happend before, should sub get maintenance to check LLC No protection operation. also see OMS 1776450 AND 1776543. | June | 2020 | 2020Q4 | 2020 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-06-13 | N | 152 | N | 4 | N | N | 1.1101 | 39.4971 | 222.1542
[7 empty] | 4912 | 16139 | 1776544 | 2020-06-13 09:58 | 2020-06-13 13:15 | 197 | 11kV | 2364 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209396 A and B phase 20A line fuses replaced at 1315hours . No Cause Found, Not Storm Conditions | June | 2020 | 2020Q4 | 2020 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2020-06-13 | N | 197 | N | 4 | N | N | 1.1101 | 39.4971 | 1727.5415
[7 empty] | 3769 | 4769 | 1776609 | 2020-06-13 19:42 | 2020-06-14 02:30 | 408 | 11kV | 2040 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209397 B and C Phase Line DOLF No Cause Found Not Storm Conditions | June | 2020 | 2020Q4 | 2020 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2020-06-13 | N | 408 | N | 4 | N | N | 1.1101 | 39.4971 | 1490.7718
[7 empty] | 5174 | 18768 | 1776899 | 2020-06-15 17:48 | 2020-06-15 19:15 | 86.7167 | 11kV | 5463.15 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209405 Sub 8016 A phase 31.5A DOLF Suspected cause fatigue Excluded OMS 1776897 | June | 2020 | 2020Q4 | 2020 | 216:10728 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Veg | 2020-06-15 | N | 86.7167 | N | 1 | N | N | 1.1101 | 39.4971 | 3992.3089
[7 empty] | 5164 | 18699 | 1776973 | 2020-06-16 10:11 | 2020-06-16 11:30 | 79 | 11kV | 2765 | 35 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 209412 C Phase DOLF No protection operations. C phase DOLF contacts burnt. Sub interconnected. Excluded OMS 1776973. | June | 2020 | 2020Q4 | 2020 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2020-06-16 | N | 79 | N | 4 | N | N | 1.1101 | 39.4971 | 2020.5804
[7 empty] | 4356 | 10684 | 1776936 | 2020-06-16 10:57 | 2020-06-16 12:23 | 86 | 11kV | 946 | 11 | HV | 3rd Party Vehicle | 3rd Party Impact | Insulator | Unplanned | No Weather Impact | N | LID 209414 truck hit pole JP-97010 dislodge wire from pin xcluded OMS 1776936 | June | 2020 | 2020Q4 | 2020 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2020-06-16 | N | 86 | N | 4 | N | N | 1.1101 | 39.4971 | 691.3089
[7 empty] | 4483 | 11867 | 1777065 | 2020-06-16 15:45 | 2020-06-16 16:50 | 65 | 11kV | 1300 | 20 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 209416 Broken 11kV xarm pole AI-70029 | June | 2020 | 2020Q4 | 2020 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-06-16 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 950.0017
[7 empty] | 4583 | 12969 | 1777039 | 2020-06-16 14:35 | 2020-06-16 16:53 | 138 | 11kV | 127333 | 995 | HV | Excavation 3rd Party | 3rd Party Impact | Circuit Breaker | Unplanned | No Weather Impact | N | At Zone 1648 Panel 16 tripped on A & C phase IOC, earth leakage, EFI Field EFI's down to S35005 Underground cable damaged by contractor #9 Weldon St Burwood - section from S35005 SW/B to S2374 SW/A See 1777418,1777039,1777420 | June | 2020 | 2020Q4 | 2020 | ZN1648:PA16 | ZN4853:PA16 | ZN04853/000016 | BURWOOD | UG | Not Veg | 2020-06-16 | N | 127.9729 | N | 4 | N | N | 1.1101 | 39.4971 | 93051.2007
[7 empty] | 3627 | 3078 | 1777106 | 2020-06-17 01:24 | 2020-06-17 02:34 | 70 | 11kV | 135110 | 1979 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At Zn10999 Kogarah Panel 38 tripped on Relays: A and B phase IPOC Signals: 11kV trip with reclose lockout Cause: Vehicle hit pole. Feeder isolated from S62735 to S10726 See OMS 1777485 17777486 1777106 | June | 2020 | 2020Q4 | 2020 | ZN10999:PA38 | ZN10999:PA38 | ZN10999/000038 | BAYSIDE | OH | Not Veg | 2020-06-17 | N | 68.2719 | N | 5 | N | N | 1.1101 | 39.4971 | 98734.4029
[7 empty] | 4969 | 16812 | 1777203 | 2020-06-17 13:37 | 2020-06-17 15:40 | 123 | 11kV | 175644 | 1428 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Zn1193 Lindfield - Pnl.27 tripped, reclosed and locked out on Earth Fault Abnormal S899 Sw/B closed with LB2834 Open, LB244 Closed with LB46265 Open (DMA) Car hit pole cr Archibold and Tryon Rd (Pole PY53869) | June | 2020 | 2020Q4 | 2020 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2020-06-17 | N | 123 | N | 5 | N | N | 1.1101 | 39.4971 | 128355.4546
[7 empty] | 5116 | 18338 | 1777310 | 2020-06-17 20:37 | 2020-06-17 22:45 | 128 | 11kV | 203776 | 1592 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn15005 Belrose 11kV Panel 8 tripped and reclosed on Overcurrent Cause: Roadside bond burnt off @ LK24445 Abnormal Switching: CP26243 Closed with LK 21843 and SW A open @ S16736 1777505 1777312 1777310 | June | 2020 | 2020Q4 | 2020 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2020-06-17 | N | 128 | N | 5 | N | N | 1.1101 | 39.4971 | 148913.4904
[7 empty] | 4006 | 7075 | 1777328 | 2020-06-18 05:54 | 2020-06-18 07:08 | 74 | 11kV | 1554 | 21 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill - Pnl.11 tripped on B & C phase OC UG cable fault in front line section of feeder See 1777328 | June | 2020 | 2020Q4 | 2020 | ZN35900:PA11 | ZN35900:PA11 | ZN35900/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-06-18 | N | 74 | N | 8 | N | N | 1.1101 | 39.4971 | 1135.6174
[7 empty] | 3356 | 620 | 1777326 | 2020-06-18 05:46 | 2020-06-18 07:38 | 112 | 11kV | 4480 | 40 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | REC24722 Forrest Crozier - Bond burnt off top side of links | June | 2020 | 2020Q4 | 2020 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2020-06-18 | N | 112 | N | 8 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 4950 | 16586 | 1777455 | 2020-06-18 12:52 | 2020-06-18 14:04 | 72 | 11kV | 216 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 209437 Wire found off a pin at Pole FO-40017 excluded OMS 1777455 | June | 2020 | 2020Q4 | 2020 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-06-18 | N | 72 | N | 8 | N | N | 1.1101 | 39.4971 | 157.8464
[7 empty] | 4550 | 12547 | 1777292 | 2020-06-17 19:30 | 2020-06-18 15:15 | 1185 | 11kV | 77025 | 65 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At PT 15487 Rounce Ave, Both LV distributors interrupted for safety. Vehicle hit pole at 27 Altona Ave. See also 1777317, 303 | June | 2020 | 2020Q4 | 2020 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Not Veg | 2020-06-17 | N | 1185 | N | 5 | N | N | 1.1101 | 39.4971 | 56287.5981
[7 empty] | 4679 | 13919 | 1777250 | 2020-06-17 16:14 | 2020-06-18 15:45 | 1411.25 | 11kV | 95965 | 68 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT 15244 "Wellman Rd", substation HV and associated LV Dist interrupted for safety. Car hit pole at 27 Altona Ave. See also 1777303 CC1: 22-"Refer to SOp" | June | 2020 | 2020Q4 | 2020 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Not Veg | 2020-06-17 | N | 1411.25 | N | 5 | N | N | 1.1101 | 39.4971 | 70128.3915
[7 empty] | 3943 | 6373 | 1777517 | 2020-06-18 15:35 | 2020-06-18 16:25 | 50 | 11kV | 29616 | 664 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN188 Zetland, 11 kV Panel 9 "S35134" feeder tripped. Relays: Earth Fault, EFI UG cable fault from Sw/B S5987 to Sw/A S5505. See 17778546,7 | June | 2020 | 2020Q4 | 2020 | ZN188:PA9 | ZN188:PA9 | ZN00188/000009 | SYDNEY | UG | Not Veg | 2020-06-18 | N | 44.6024 | N | 8 | N | N | 1.1101 | 39.4971 | 21642.4993
[7 empty] | 4150 | 8702 | 1777472 | 2020-06-18 13:03 | 2020-06-18 18:54 | 350.7667 | 11kV | 7015.3333 | 20 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | SOP arrange NAR59240 (could not find this NAR on the Planned outage list for the 18th June on SRR, hence have left as Unplanned Event) Notif 1201752047 HV x-arm replaced | June | 2020 | 2020Q4 | 2020 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2020-06-18 | N | 350.7667 | N | 8 | N | N | 1.1101 | 39.4971 | 5126.5987
[7 empty] | 5023 | 17484 | 1777559 | 2020-06-18 19:00 | 2020-06-18 19:42 | 42 | 11kV | 56245 | 1394 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209449 Protection please look at grading on SEF at Sw 80932 and Sw 3978. See darts. On return of nar 56467. Becase a kiosk is gone and a STJ is added the under ground cable is now 3.6km ...you can not use single phase switching on 11kv links 43125. Replacement of 11kv link to a ABS would help but not urgent. Excluded oms 1777559 | June | 2020 | 2020Q4 | 2020 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2020-06-18 | N | 40.3479 | N | 8 | N | N | 1.1101 | 39.4971 | 41102.1871
[7 empty] | 4563 | 12706 | 1777324 | 2020-06-18 03:37 | 2020-06-19 00:52 | 1275 | 11kV | 193927 | 320 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID209438 3 fault operations Tree on 11kv ohm at pole GW-50068 possible malgrade with sw 13015 avondale sub see report # 209439 Excluded oms 1777324 & 1777412 | June | 2020 | 2020Q4 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-06-18 | N | 606.0219 | N | 8 | N | N | 1.1101 | 39.4971 | 141716.1317
[7 empty] | 3889 | 5837 | 1778077 | 2020-06-18 05:19 | 2020-06-19 00:52 | 1173 | 11kV | 20295 | 1429 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209439 Trip & Reclose Senitive Earth Fault see report # 209438 possible malgrade during fault beyond sw 13793 Excluded oms 1777324 | June | 2020 | 2020Q4 | 2020 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-06-18 | N | 14.2022 | N | 8 | N | N | 1.1101 | 39.4971 | 14830.9874
[7 empty] | 3809 | 5114 | 1777603 | 2020-06-19 09:50 | 2020-06-19 13:02 | 192 | 11kV | 3840 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209452 Single phase Remove hazardous tree between poles GS-24528 & GS-24529. | June | 2020 | 2020Q4 | 2020 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2020-06-19 | N | 192 | N | 2 | N | N | 1.1101 | 39.4971 | 2806.1587
[7 empty] | 4073 | 7849 | 1777659 | 2020-06-19 12:01 | 2020-06-19 13:30 | 89 | 11kV | 178243 | 2237 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1994 Mortdale - Pnl.4 tripped, reclosed and locked out on: A phase IOC UG cable fault between S10284 Sw/B and S10564 Sw/A See 1778985 1778986 | June | 2020 | 2020Q4 | 2020 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | UG | Not Veg | 2020-06-19 | N | 79.6795 | N | 2 | N | N | 1.1101 | 39.4971 | 130254.7271
[7 empty] | 3689 | 3774 | 1777847 | 2020-06-20 17:55 | 2020-06-21 00:30 | 395 | 11kV | 58984.4667 | 178 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | No Weather Impact | N | S3954 Marceau Ward - 11kV fuse blown LV Pillar fault. In lV // with S61576 Dist #3 See 1777848 1777847 | June | 2020 | 2020Q4 | 2020 | ZN2835:PA19 | ZN2835:PA19 | ZN02835/000019 | CANADA BAY | UG | Not Veg | 2020-06-20 | N | 331.3734 | N | 1 | N | N | 1.1101 | 39.4971 | 43104.1085
[7 empty] | 3634 | 3201 | 1778037 | 2020-06-21 18:25 | 2020-06-21 19:27 | 62 | 11kV | 83514 | 1347 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.8 tripped on OC Bird on PT 9391 | June | 2020 | 2020Q4 | 2020 | ZN9118:PA8 | ZN9118:PA8 | ZN09118/000008 | SUTHERLAND | OH | Not Veg | 2020-06-21 | N | 62 | N | 1 | N | N | 1.1101 | 39.4971 | 61029.568
[7 empty] | 5040 | 17674 | 1778061 | 2020-06-22 04:00 | 2020-06-22 05:15 | 75 | 11kV | 8775 | 117 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209473 A & B Phase DOLF ; 40 Amp Possum found at sub pole Excluded OMS 1778061 | June | 2020 | 2020Q4 | 2020 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2020-06-22 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 6412.5112
[7 empty] | 4548 | 12525 | 1778107 | 2020-06-22 10:17 | 2020-06-22 11:48 | 91 | 11kV | 173082 | 1902 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 1285 Greenacre Park Panel 23 'beresford hume' tripped on earth leakge, EFI 11 kV feeder fault in section of feeder from S1285 to S35577 Sw/A See 1778107,1778126,1778117,1778607 | June | 2020 | 2020Q4 | 2020 | ZN1285:PA23 | ZN37100:PA33 | ZN37100/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-06-22 | N | 91 | N | 3 | N | N | 1.1101 | 39.4971 | 126483.2205
[7 empty] | 4512 | 12183 | 1778260 | 2020-06-22 22:35 | 2020-06-23 00:47 | 131.8833 | 11kV | 57935.7667 | 494 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 7841 Darling Harbour 11kV Pnl1 19 "Union Ln Harwood' tripped on Earth Fault Relay Relays - Earth Fault Signals 11 kv Trip an TX 12 group Earth Field EFI's Pnl 19 to S3092 Cable fault from Sub 3092 Darling Harbour Markets #2 to Sub 6532 Monorail Wesrtern Bvd See 1778677,1778674,1778260,1778261,1778265 | June | 2020 | 2020Q4 | 2020 | ZN7481:PA19 | ZN7481:PA19 | ZN07481/000019 | SYDNEY | UG | Not Veg | 2020-06-22 | N | 117.2789 | N | 3 | N | N | 1.1101 | 39.4971 | 42337.7495
[7 empty] | 4102 | 8204 | 1778292 | 2020-06-23 06:57 | 2020-06-23 08:10 | 73 | 11kV | 4964 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209486 A Phase DOLF : 40 Amp excluded OMS 1778293 | June | 2020 | 2020Q4 | 2020 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2020-06-23 | N | 73 | N | 5 | N | N | 1.1101 | 39.4971 | 3627.5448
[7 empty] | 3319 | 286 | 1778300 | 2020-06-23 08:05 | 2020-06-23 12:00 | 235 | 11kV | 18330 | 78 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT1512 malton Clarke - Centre phase HDO operated Fuse Fatigue (Batch 1009) | June | 2020 | 2020Q4 | 2020 | ZN965:PA17 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Not Veg | 2020-06-23 | N | 235 | N | 5 | N | N | 1.1101 | 39.4971 | 13395.0234
[7 empty] | 3582 | 2690 | 1778360 | 2020-06-23 11:35 | 2020-06-23 12:40 | 65 | 11kV | 3605 | 67 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill - Pnl.6 tripped on: A C phase IOC UGOH bond failed on first UGOH out of zone on 6R leg | June | 2020 | 2020Q4 | 2020 | ZN15011:PA6 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | Unknown | Unknown | 2020-06-23 | N | 53.806 | N | 5 | N | N | 1.1101 | 39.4971 | 2634.4277
[7 empty] | 4452 | 11533 | 1778382 | 2020-06-23 12:48 | 2020-06-23 14:18 | 90 | 11kV | 25304 | 340 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn12690 berkely vale - Pnl.16 tripped SPAJ relay 140 defective. - Protection malfunction | June | 2020 | 2020Q4 | 2020 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | Exclude | Not Veg | 2020-06-23 | N | 74.4235 | N | 5 | N | N | 1.1101 | 39.4971 | 18491.4169
[7 empty] | 3885 | 5790 | 1778507 | 2020-06-23 21:37 | 2020-06-23 22:31 | 54 | 11kV | 12240 | 244 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S 5868 Gore Hill Zn, 11kV Panel 17 "S 3266 reserve campbell" tripped. Relays: EF, EFI. 11kV UG cable fault from S 7543 Lanceley Waste Shredder to S 7771 Lanceley Place ABC | June | 2020 | 2020Q4 | 2020 | ZN5868:PA17 | ZN5868:PA17 | ZN05868/000017 | LANE COVE | UG | Not Veg | 2020-06-23 | N | 50.1639 | N | 5 | N | N | 1.1101 | 39.4971 | 8944.631
[7 empty] | 4638 | 13544 | 1778517 | 2020-06-24 00:42 | 2020-06-24 01:23 | 41 | 11kV | 2347 | 67 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At ZN 15011 Beacon Hill, 11 kV Panel 6 tripped. Relays: NIL Defective relay on Pnl 6 @ ZN 15011. See also 1778517 | June | 2020 | 2020Q4 | 2020 | ZN15011:PA6 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | Unknown | Not Veg | 2020-06-24 | N | 35.0299 | N | 3 | N | N | 1.1101 | 39.4971 | 1715.1184
[7 empty] | 4892 | 15868 | 1778689 | 2020-06-24 15:37 | 2020-06-24 17:05 | 88 | 11kV | 1056 | 12 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 209498 Faulty crossarm at pole: AE-90108 excluded OMS 1778689 | June | 2020 | 2020Q4 | 2020 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-06-24 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 771.6937
[7 empty] | 3408 | 1074 | 1778700 | 2020-06-24 16:12 | 2020-06-24 17:16 | 64 | 11kV | 8426 | 143 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8000 Macquarie Park - Pnl.4 tripped & reclosed on: O/C UG cable fault between Pnl.4, S2004Sw/A and LB2672 | June | 2020 | 2020Q4 | 2020 | ZN8000:PA4 | ZN8000:PA4 | ZN08000/000004 | RYDE | UG | Not Veg | 2020-06-24 | N | 58.9231 | N | 3 | N | N | 1.1101 | 39.4971 | 6157.4723
[7 empty] | 4317 | 10351 | 1779067 | 2020-06-25 21:06 | 2020-06-25 21:54 | 48 | 11kV | 39899 | 918 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 3472 Sefton, 11kV Panel 22 "S.1279 Virgil Ave" tripped on Relays: EF, EFI, Fault check 11kV UG cable fault between S47490 to S7342 to LB2105 to LB3272 See also 1780002,3 | June | 2020 | 2020Q4 | 2020 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-06-25 | N | 43.463 | N | 1 | N | N | 1.1101 | 39.4971 | 29157.0124
[7 empty] | 3947 | 6427 | 1779229 | 2020-06-26 22:33 | 2020-06-27 00:28 | 115 | 11kV | 87329 | 953 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 209525 2 fault operations B & C Phase Instantaneous Overcurrent; Earth Fault OC EF Relay, Instant OC B-C, EF 11kV UG cable/joint fault between S-67743/S-58714/S-17074 excluded OMS 1779229 | June | 2020 | 2020Q4 | 2020 | 202:34256 | 202:34256 | ZN00202/034256 | NEWCASTLE | UG | Not Veg | 2020-06-26 | N | 91.6359 | N | 1 | N | N | 1.1101 | 39.4971 | 63817.4574
[7 empty] | 5274 | 19635 | 1779254 | 2020-06-27 08:50 | 2020-06-27 10:20 | 90 | 11kV | 123154 | 1594 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S.195 Pymble Zone, 11kV Panel 28 "S.6056 Bridge Pacific Etc" tripped. Relays: EF, OC, EFI, Fault check Abnormal Switching at time of fault: AB 1718 Open (DMA), Sw/B @ S.6931 Closed, AB 3017 Closed, Sw/A @ S 8776 Open. 11kV UG fault from S 4934 to S 4941, Tee PT 1800. See also 1779659, 60 | June | 2020 | 2020Q4 | 2020 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | UG | Not Veg | 2020-06-27 | N | 77.261 | N | 1 | N | N | 1.1101 | 39.4971 | 89997.3108
[7 empty] | 4160 | 8941 | 1779381 | 2020-06-28 09:30 | 2020-06-28 10:30 | 60 | 11kV | 5460 | 91 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | No Weather Impact | N | At S.10610 Beach Torrens, HV Tx switch opened, all distributors interrupted for safety. A phase fuse open cct and HR on Dist 3 beach st south. DMA created for T con to check LV Dist 3 is radial non Lv //. | June | 2020 | 2020Q4 | 2020 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | UG | Not Veg | 2020-06-28 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 3990.007
[7 empty] | 5006 | 17268 | 1779375 | 2020-06-28 09:20 | 2020-06-28 11:55 | 155 | 11kV | 17495.1667 | 113 | HV | Overload LV Parallel | Utility Process Issue | DC-PT Transformer | Unplanned | No Weather Impact | N | At PT1916 Treatts Nelson, All phases lost due to LV parallel failure from S 928 Nelson Rd. PT 1916 DMA. See also 1779635 | June | 2020 | 2020Q4 | 2020 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | Unknown | Not Veg | 2020-06-28 | N | 154.8245 | N | 3 | N | N | 1.1101 | 39.4971 | 12784.9518
[7 empty] | 3736 | 4339 | 1779418 | 2020-06-28 15:30 | 2020-06-28 17:35 | 125 | 11kV | 6875 | 55 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 12690 Berkeley Vale, Ex 11kV Panel 12 "Craftsman Ave", feeder isolated between LB 49055 and USL 44932 Tee PT 13657. Vehicle hit pole, 11kV resting on X-arm. See also 1779370, 1779418 | June | 2020 | 2020Q4 | 2020 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2020-06-28 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 5024.0472
[7 empty] | 3388 | 863 | 1779527 | 2020-06-29 09:27 | 2020-06-29 13:40 | 253 | 11kV | 3036 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209536 A & B Phase DOLF : 20 Amp Excluded OMS 1779527 | June | 2020 | 2020Q4 | 2020 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2020-06-29 | N | 253 | N | 3 | N | N | 1.1101 | 39.4971 | 2218.6193
[7 empty] | 4940 | 16478 | 1779632 | 2020-06-29 15:52 | 2020-06-29 16:48 | 56 | 11kV | 6216 | 112 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn262 Marrickville - Pnl.13 tripped on: A phase O/C UG cable fault between S7116 and S4685 DMA created @ S6273 - unable to determine oil level See 1780088 1780089 | June | 2020 | 2020Q4 | 2020 | ZN262:PA13 | ZN262:PA13 | ZN00262/000013 | INNER WEST | UG | Not Veg | 2020-06-29 | N | 55.5 | N | 3 | N | N | 1.1101 | 39.4971 | 4542.4695
[7 empty] | 3347 | 522 | 1779476 | 2020-06-29 01:07 | 2020-06-30 19:00 | 2513 | 11kV | 138525 | 752 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | Zn3425 Castle Cove - Pnl.16 tripped on: Earth Fault Flooding at S7313 and S6541 (1 meter of water) See 1780081 1780082 1780084 1780083 | June | 2020 | 2020Q4 | 2020 | ZN3425:PA16 | ZN3425:PA16 | ZN03425/000016 | WILLOUGHBY | UG | Not Veg | 2020-06-29 | N | 184.2088 | N | 3 | N | N | 1.1101 | 39.4971 | 101229.9842
[7 empty] | 2751 | 13157 | 1780049 | 2020-07-01 17:38 | 2020-07-01 18:42 | 64 | 11kV | 43793 | 885 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.7 tripped on: O/C Ug cable fault in frontline section of cable between Pnl.7, S1358 and S133 | July | 2020 | 2021Q1 | 2021 | ZN7900:PA7 | ZN7900:PA7 | ZN07900/000007 | SYDNEY | UG | Not Veg | 2020-07-01 | N | 49.4836 | N | 3 | N | N | 1.1101 | 39.4971 | 32002.6327
[7 empty] | 1865 | 2402 | 1780096 | 2020-07-01 21:57 | 2020-07-01 23:20 | 83 | 11kV | 664 | 8 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT13245 Yarramalong Boyds 0.5 - Roadside and Middle phase fuses operated Possum on PT | July | 2020 | 2021Q1 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2020-07-01 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 485.2316
[7 empty] | 2831 | 14181 | 1780059 | 2020-07-01 18:28 | 2020-07-01 23:50 | 322 | 11kV | 38265.3167 | 119 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | PT10332 Weeney Burgess - Dist #1 - 11kV bond burnt off Section of Dist #2 S10268 - multiple NS calls - suspect GIS error See 1780059 1780135 | July | 2020 | 2021Q1 | 2021 | ZN10999:PA16 | ZN10999:PA16 | ZN10999/000016 | GEORGES RIVER | OH | Not Veg | 2020-07-01 | N | 321.5573 | N | 3 | N | N | 1.1101 | 39.4971 | 27963.1648
[7 empty] | 2145 | 5651 | 1780126 | 2020-07-02 12:50 | 2020-07-02 13:15 | 25 | 11kV | 25 | 1 | HV | Staff Other | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209570 Asset Inspector damaged sub earth conductor when brushcutting around pole. Excluded OMS No. 1780126 | July | 2020 | 2021Q1 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-07-02 | N | 25 | N | 4 | N | N | 1.1101 | 39.4971 | 18.2693
[7 empty] | 3107 | 18268 | 1780176 | 2020-07-02 11:25 | 2020-07-02 13:45 | 140 | 11kV | 4480 | 32 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | At PT48041 Karuah Algona: Road side 31.5 Fuse operated Cause: Fuse carrier HR Blown HV fuse at PT48041, has not dropped down, welded in. All LV 3 phase still on. Suspect LV parallel in. At pole9231 Cnr Algona & Seabreeze Ave LV links closed not shown on my LV maps. See OMS 1781239 1780176 | July | 2020 | 2021Q1 | 2021 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Not Veg | 2020-07-02 | N | 140 | N | 4 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 3096 | 18102 | 1780127 | 2020-07-02 08:04 | 2020-07-02 14:30 | 386 | 11kV | 14736 | 96 | HV | Staff Other | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | LID 209563 Following SI 27983 ITEM 11. 11kV Links 74093 & 75073 Ironbark Ave sub 72234 were incorrectly labelled in field. | July | 2020 | 2021Q1 | 2021 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2020-07-02 | N | 153.5 | N | 4 | N | N | 1.1101 | 39.4971 | 10768.6342
[7 empty] | 3208 | 19462 | 1780268 | 2020-07-02 19:46 | 2020-07-02 23:50 | 244 | 11kV | 27925 | 232 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Flemington ZN 2466, 11kV Panel 27 tripped Relays: EF, EFI, Fault check S.8775 Hill M4 SwB to S.7616 Parramatta day No.1 tee to S.791 Grace John see 1780319, 20 , 21 | July | 2020 | 2021Q1 | 2021 | ZN2466:PA27 | ZN2466:PA1 | ZN02466/000001 | PARRAMATTA | UG | Not Veg | 2020-07-02 | N | 120.3664 | N | 4 | N | N | 1.1101 | 39.4971 | 20406.7664
[7 empty] | 2001 | 3821 | 1780371 | 2020-07-03 13:25 | 2020-07-03 14:16 | 51 | 11kV | 16983 | 333 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP63182 Riverview Cottage has tripped on Relays: OC trip and Lockout Cause: tree branch at pole GL88324 | July | 2020 | 2021Q1 | 2021 | ZN129:PA41 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2020-07-03 | N | 51 | N | 2 | N | N | 1.1101 | 39.4971 | 12410.6755
[7 empty] | 1910 | 2900 | 1780423 | 2020-07-03 21:01 | 2020-07-04 01:40 | 279.0667 | 11kV | 25674.1333 | 92 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209590 Customer cut tree, hitting mains & breaking x arm pole DV-51713 Excluded OMS 1780423. | July | 2020 | 2021Q1 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-07-03 | N | 279.0667 | N | 2 | N | N | 1.1101 | 39.4971 | 18761.8994
[7 empty] | 2796 | 13816 | 1780511 | 2020-07-04 15:35 | 2020-07-04 17:00 | 85 | 11kV | 680 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 209593 B Phase DOLF : 10 Amp Fuse Fatigued, Fuse carier perished. JMH Excluded OMS 1780511 | July | 2020 | 2021Q1 | 2021 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2020-07-04 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 496.9239
[7 empty] | 2517 | 10279 | 1780531 | 2020-07-04 17:52 | 2020-07-04 18:35 | 43 | 11kV | 2451 | 57 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 209594 Buring DOLF carrier replaced Excluded OMS 1780531. | July | 2020 | 2021Q1 | 2021 | 257:81999 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2020-07-04 | N | 43 | N | 2 | N | N | 1.1101 | 39.4971 | 1791.1185
[7 empty] | 1850 | 2255 | 1780618 | 2020-07-05 18:07 | 2020-07-05 20:13 | 125.7167 | 11kV | 93156.05 | 741 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209599 C ph DOLF 61862 found blown. | July | 2020 | 2021Q1 | 2021 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Veg | 2020-07-05 | N | 125.7167 | N | 1 | N | N | 1.1101 | 39.4971 | 68075.6937
[7 empty] | 2580 | 10967 | 1780654 | 2020-07-06 12:58 | 2020-07-06 15:00 | 122.4333 | 11kV | 12120.9 | 99 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S16635 Karloo Barrenjoey the 11kV tee off TX was interrupted for emergency repairs. Interrupted to repair damage from car hitting pole. Inspect pole MV4205- please check 11kV tie wires. Pole MV4204- LV crossarm twisted and phase in contact with streeght light bracket. | July | 2020 | 2021Q1 | 2021 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | OH | Not Veg | 2020-07-06 | N | 122.4333 | N | 3 | N | N | 1.1101 | 39.4971 | 8857.5962
[7 empty] | 2323 | 7785 | 1780829 | 2020-07-06 16:35 | 2020-07-06 17:50 | 75 | 11kV | 5700 | 76 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT11856 Suncrest Gleddon 63A HV DOF operated Cause: Galah made contact with 11kV @ PT11856 See OMS 1781236 1780836 1780835 1780832 1780830 1780829 | July | 2020 | 2021Q1 | 2021 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2020-07-06 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 4165.3919
[7 empty] | 3258 | 19937 | 1780841 | 2020-07-06 17:29 | 2020-07-06 19:40 | 131 | 11kV | 262 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209609 Single phase DOLF : 10 Amp Excluded OMS 1780841 | July | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-07-06 | N | 131 | N | 3 | N | N | 1.1101 | 39.4971 | 191.4619
[7 empty] | 2331 | 7978 | 1780950 | 2020-07-07 11:44 | 2020-07-07 15:05 | 201 | 11kV | 25409 | 313 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209614 Self propelled spray rig drove boom into 11kV OHM. 11kV OHM main down between poles AH-11764 & AH-10131. Excluded OMS No. 1780950 | July | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-07-07 | N | 81.1789 | N | 4 | N | N | 1.1101 | 39.4971 | 18568.1478
[7 empty] | 3250 | 19796 | 1781020 | 2020-07-07 18:15 | 2020-07-07 19:20 | 65 | 11kV | 6695 | 103 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209616 HV droper burnt off stirrup clamp. Lead is in SAFE position. Sub in LV parallel. Excluded OMS 1781020 | July | 2020 | 2021Q1 | 2021 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2020-07-07 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 4892.5085
[7 empty] | 2687 | 12236 | 1781035 | 2020-07-07 21:04 | 2020-07-07 23:01 | 117 | 11kV | 209759 | 1851 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 1610 Homebush Bay Panel 19 "Evans Asia' tripped on Relays - A and N phase overcurrent, Fault Check (TX2) 11 kV Trip Signals - 11kV Trip Field EFI's S36068 S6305, S4805, S4790 Cause of Interruption - UG Fault (S4790 America's Europe to S3019 Silverwater EG) See 1781183,1781185,1781035 | July | 2020 | 2021Q1 | 2021 | ZN1610:PA19 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2020-07-07 | N | 113.322 | N | 4 | N | N | 1.1101 | 39.4971 | 153285.6904
[7 empty] | 2683 | 12185 | 1781045 | 2020-07-07 22:57 | 2020-07-07 23:34 | 37 | 11kV | 43401 | 1173 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 15012 Killarney 11kV Panel 8 tripped on: Relays A and C phase IOC Reclose and lockout Signals 11 kV Trip Field EFI's N/A Tree Branch on O/H Mains, CNR Starkey and Warringah Rd, Forrestville See 1781047 | July | 2020 | 2021Q1 | 2021 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2020-07-07 | N | 37 | N | 4 | N | N | 1.1101 | 39.4971 | 31716.1707
[7 empty] | 2969 | 16237 | 1781446 | 2020-07-10 06:13 | 2020-07-10 08:05 | 112 | 11kV | 2016 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT14093 Ruterford Roxburgh - Footpath phase HDO found blown Fuse fatigue | July | 2020 | 2021Q1 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2020-07-10 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 1473.2333
[7 empty] | 2172 | 5892 | 1781448 | 2020-07-10 06:19 | 2020-07-10 09:00 | 161 | 11kV | 322 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209643 'No Cause Found (Not Storm Condition) Phase B, 16 Amp Substation DOLF also see OMS No. 1781448 | July | 2020 | 2021Q1 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-07-10 | N | 161 | N | 3 | N | N | 1.1101 | 39.4971 | 235.3081
[7 empty] | 2631 | 11442 | 1781557 | 2020-07-10 19:14 | 2020-07-10 22:31 | 196.7667 | 11kV | 11412.4667 | 58 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At PT 12207 Tambelin Yaldemee HV Drop Out Fuse pulled to allow removal of B Double wedged at pole. Interrupted for Safety Reasons B-Double wedged against AG pole WY-2761. Pole erector/boarer required ASAP to stay pole for tow vehicle to retrieve front-half of truck. See 1781557,1781573 | July | 2020 | 2021Q1 | 2021 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2020-07-10 | N | 196.7667 | N | 3 | N | N | 1.1101 | 39.4971 | 8339.894
[7 empty] | 2578 | 10916 | 1781608 | 2020-07-11 09:05 | 2020-07-11 14:25 | 320 | 11kV | 320 | 1 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Rain Light | N | LID 209651 'Broken stay wire at sub pole Customer advises the stays that connect the wires to the pole from the ground have come away.The pole is leaning and the wires to the house are now sagging. No pets no self isolating or other. | July | 2020 | 2021Q1 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-07-11 | N | 320 | N | 3 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 1878 | 2536 | 1781684 | 2020-07-11 19:00 | 2020-07-11 20:05 | 65 | 11kV | 21385 | 329 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC63734 George Downes Blood 2.45 tripped on: OC Possum on mains at pole KA422 | July | 2020 | 2021Q1 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-07-11 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 15627.5272
[7 empty] | 3112 | 18358 | 1781663 | 2020-07-11 18:35 | 2020-07-11 20:25 | 110 | 11kV | 220 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209653 Broken OHM dead end pole Adj ABS 3612 | July | 2020 | 2021Q1 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2020-07-11 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 2050 | 4656 | 1781711 | 2020-07-12 09:30 | 2020-07-12 10:50 | 80 | 11kV | 960 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209655 Phases A & B. 20 Amp Line DOLF No Cause Found (Not Storm Condition) | July | 2020 | 2021Q1 | 2021 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2020-07-12 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 1751 | 921 | 1781739 | 2020-07-12 18:11 | 2020-07-12 23:49 | 337.8167 | 11kV | 21282.45 | 63 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | PT599 Attunga Sherwood - 11kV interrupted to repair broken cross arm outside 109 Attunga Rd. | July | 2020 | 2021Q1 | 2021 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2020-07-12 | N | 337.8167 | N | 5 | N | N | 1.1101 | 39.4971 | 15552.5867
[7 empty] | 1980 | 3663 | 1781827 | 2020-07-12 21:17 | 2020-07-13 00:55 | 218 | 11kV | 207746 | 1162 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 209669 B and C Phase Overcurrent Refer to OMS 1781827## tapping burnt off pole JU-13406 DQ Note: PS and NS calls started coming in at 12/07/20 21:27, as per switching sheet all customers restored at 13/07/20 00:55 | July | 2020 | 2021Q1 | 2021 | 258:80779 | 258:80779 | ZN00258/080779 | NEWCASTLE | OH | Not Veg | 2020-07-12 | N | 178.7831 | N | 5 | N | N | 1.1101 | 39.4971 | 151814.6493
[7 empty] | 2897 | 14939 | 1781764 | 2020-07-12 18:28 | 2020-07-13 02:30 | 482 | 11kV | 400695 | 3528 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn10995 Riverwood - Pnl.1 tripped on: SEL Abnormal: LB31090 Closed with AB30040 Open 11kV Mains down into LV between S10947 Meadowland Baumans and LB31327 See 1782018 1782019 LV:1782021 1781813 1781791 GIS: 1781800 | July | 2020 | 2021Q1 | 2021 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2020-07-12 | N | 113.5757 | N | 5 | N | N | 1.1101 | 39.4971 | 292816.0875
[7 empty] | 2775 | 13574 | 1781820 | 2020-07-12 21:17 | 2020-07-13 05:10 | 473 | 11kV | 176892 | 898 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 209668 Phase C Earth Fault Blown surge arrestor at pole ju-10206. Also C ph 31A Dolf found blown sub 19824 Hill St West sub during patrol. - see OMS 1782985 Withdrawn oms 1781820## | July | 2020 | 2021Q1 | 2021 | 210:83474 | 210:83474 | ZN00210/083474 | NEWCASTLE | OH | Not Veg | 2020-07-12 | N | 196.9844 | N | 5 | N | N | 1.1101 | 39.4971 | 129267.4562
[7 empty] | 2791 | 13774 | 1781849 | 2020-07-13 15:00 | 2020-07-13 16:00 | 60 | 11kV | 4080 | 68 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 209673 Damaged earth cable and earth guard on sub pole FS82771. 11kV B ph tie appears broken on one side but is still holding main to insulator. Please have crew attend to repair sub earth, replace earth guard and inspect 11kV tie for integrity. POLICE RADIO MVA - CAR HIT POLE - LINES DOWN POLE TO POLE - POLE# 42626 (FS 82771) - CAD# 823849 Ties Broken at pole FS-82771. | July | 2020 | 2021Q1 | 2021 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Not Veg | 2020-07-13 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 2981.5437
[7 empty] | 2212 | 6412 | 1781938 | 2020-07-13 15:15 | 2020-07-13 16:50 | 95 | 11kV | 1900 | 20 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 209672 car hit pole. replaced broken 11kv insulator & retensioned service 11KV insulator snapped off pole JR72445 causing 11KV main to rest on Crossarm. No Voltage on pole. LV service has also come out of chock. Sop 2 notified. Please send crew. DR1 form filed. | July | 2020 | 2021Q1 | 2021 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2020-07-13 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 1388.464
[7 empty] | 2446 | 9476 | 1782046 | 2020-07-13 16:55 | 2020-07-13 19:42 | 166.5667 | 11kV | 3331.3333 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 209675 Phase A LF 17006 Fuse carrier burnt out suspect failure of fibreglass tube. Replaced by dop O CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | July | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2020-07-13 | N | 166.5667 | N | 4 | N | N | 1.1101 | 39.4971 | 2434.4401
[7 empty] | 2417 | 9233 | 1781987 | 2020-07-13 13:13 | 2020-07-13 21:35 | 502 | 11kV | 5010 | 10 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 209676 40 Amp, B phase Line DOLF Blown Arrestor at UGOH P.ER-53066 | July | 2020 | 2021Q1 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2020-07-13 | N | 501 | N | 4 | N | N | 1.1101 | 39.4971 | 3661.1602
[7 empty] | 2741 | 13048 | 1782097 | 2020-07-14 06:43 | 2020-07-14 08:08 | 85 | 11kV | 102428 | 1330 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn15008 Harbord - Pnl.5 tripped on; B & C phase IOC Abnormal: LB23499 Closed with S16917 Sw/B Open OH down outside 29 Moore Rd Freshwater See 1782641 1782642 | July | 2020 | 2021Q1 | 2021 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2020-07-14 | N | 77.0135 | N | 10 | N | N | 1.1101 | 39.4971 | 74851.3613
[7 empty] | 2672 | 12003 | 1782174 | 2020-07-14 08:45 | 2020-07-14 10:00 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 209678 Phase A 10 Amp Substation DOLF Also refer to OMS 1782174 | July | 2020 | 2021Q1 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-07-14 | N | 75 | N | 10 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 2303 | 7563 | 1782245 | 2020-07-14 10:02 | 2020-07-14 11:30 | 88 | 11kV | 86700 | 1048 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Zn14144 Wamberal - Pnl.7 tripped, reclosed, tripped & locked out on: B&C phase IOC Bond off at pole WL3656 See 1782657 1782658 | July | 2020 | 2021Q1 | 2021 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2020-07-14 | N | 82.729 | N | 10 | N | N | 1.1101 | 39.4971 | 63357.8028
[7 empty] | 2565 | 10758 | 1782312 | 2020-07-14 13:35 | 2020-07-14 14:10 | 35 | 11kV | 105 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Previous Storm | N | LID 209681 Replace LL lead" also refer to "OMS 1782312 | July | 2020 | 2021Q1 | 2021 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2020-07-14 | N | 35 | N | 10 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 1864 | 2398 | 1782326 | 2020-07-14 11:05 | 2020-07-14 14:20 | 195 | 11kV | 13650 | 70 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | iR63686 Bundaleer Empire Bay 0.2 tripped on: OC Tree on mains near iR63686 | July | 2020 | 2021Q1 | 2021 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2020-07-14 | N | 195 | N | 10 | N | N | 1.1101 | 39.4971 | 9975.0174
[7 empty] | 1991 | 3742 | 1782247 | 2020-07-14 10:03 | 2020-07-14 16:10 | 367 | 11kV | 61656 | 168 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | iR61952 Ballarock Avoca - tripped on: OC tree on mains adj iR61952 | July | 2020 | 2021Q1 | 2021 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2020-07-14 | N | 367 | N | 10 | N | N | 1.1101 | 39.4971 | 45056.3863
[7 empty] | 2991 | 16555 | 1782318 | 2020-07-14 13:35 | 2020-07-14 16:10 | 155 | 11kV | 1395 | 9 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 209686 Phase C 11kv OHM sagged between KS60226 & KS60225 allowing ohm to swing and hip steel street light standard section isolated for repairs" also see "#1782318 | July | 2020 | 2021Q1 | 2021 | 229:34992 | 229:34992 | ZN00229/034992 | PORT STEPHENS | OH | Not Veg | 2020-07-14 | N | 155 | N | 10 | N | N | 1.1101 | 39.4971 | 1019.4249
[7 empty] | 2137 | 5503 | 1782472 | 2020-07-14 15:26 | 2020-07-14 16:31 | 65 | 11kV | 4355 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn15013 Terrey Hills - Pnl.2 tripped on: C phase OCand IOC Tree on mains outside 314 Mona Vale Rd. | July | 2020 | 2021Q1 | 2021 | ZN15013:PA2 | ZN15013:PA2 | ZN15013/000002 | NORTHERN BEACHES | OH | Veg | 2020-07-14 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 3182.5055
[7 empty] | 2781 | 13607 | 1782310 | 2020-07-14 10:51 | 2020-07-14 16:50 | 359 | 11kV | 3231 | 9 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | PT13804 Mona Arizona - Footpath and middle phase HDOs operated Surge arrestors blown clear | July | 2020 | 2021Q1 | 2021 | ZN14892:PA5 | ZN14892:PA5 | ZN14892/000005 | CENTRAL COAST | OH | Not Veg | 2020-07-14 | N | 359 | N | 10 | N | N | 1.1101 | 39.4971 | 2361.1195
[7 empty] | 2240 | 6737 | 1782681 | 2020-07-15 10:50 | 2020-07-15 14:15 | 205 | 11kV | 615 | 3 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S1959 Bankstown Airport No.2 - 11kV A phase fuse blown Suspect cable fault on customer's HVC. Supply restored, referred customer to organise repairs. | July | 2020 | 2021Q1 | 2021 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2020-07-15 | N | 205 | N | 4 | N | N | 1.1101 | 39.4971 | 449.4239
[7 empty] | 2056 | 4762 | 1782890 | 2020-07-15 16:45 | 2020-07-15 17:30 | 45 | 11kV | 225 | 5 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209702 Trees growing into mains, section isolated to retension mains to sub 72522. | July | 2020 | 2021Q1 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-07-15 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 1735 | 705 | 1782791 | 2020-07-15 18:58 | 2020-07-15 20:20 | 82 | 11kV | 82 | 1 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 209703 A Hagan assigned, magppie across B & C arrestors, 10 HV fuses replaced power restored 2020. MdV | July | 2020 | 2021Q1 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-07-15 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 59.9232
[7 empty] | 2716 | 12508 | 1782780 | 2020-07-15 20:52 | 2020-07-15 21:52 | 60 | 11kV | 360 | 6 | HV | Arcing | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 209704 J Frazer assigned, hot joint on A phase outgoing link. link replaced section isolated to repair outgoing link sw 42048 Bridgeman Rd RAGCB" also refer to "oms 1782780, 1782801 Customer reported - Pole no SI30698 arcing and sparking eastern connection of centre arm. | July | 2020 | 2021Q1 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2020-07-15 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 3008 | 16756 | 1782908 | 2020-07-16 11:38 | 2020-07-16 13:25 | 107 | 11kV | 107 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 209710 Single Phase 10 Amp Substation DOLF | July | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-07-16 | N | 107 | N | 2 | N | N | 1.1101 | 39.4971 | 78.1924
[7 empty] | 3217 | 19588 | 1782389 | 2020-07-14 13:01 | 2020-07-16 18:05 | 3184 | 11kV | 223277.1667 | 87 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | REC47746 Ptonga Meroo tripped on: OC Tree removed off HV mains OPEN on Rec47746 , PM L/Men Sup advises parts of feeder extensive walks to patrol , advised request a complete patrol and advise Control room and give clearance to energize. Extended outage. See 1782389 1782765 | July | 2020 | 2021Q1 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2020-07-14 | N | 2566.4042 | N | 10 | N | N | 1.1101 | 39.4971 | 163164.3678
[7 empty] | 3062 | 17500 | 1783004 | 2020-07-16 18:40 | 2020-07-17 02:25 | 465 | 11kV | 61168 | 1066 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 209718 Phase C Earth Fault Sw 33413 C phase to Earth, Sw 69392 E/F indicator, ELB 50354 C phase O/C & E/F. 11kV xarm burnt in half & mains on ground pole OS-20185 Fire brigade reported pole on fire also refer to OMS 1783004 | July | 2020 | 2021Q1 | 2021 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2020-07-16 | N | 57.3809 | N | 2 | N | N | 1.1101 | 39.4971 | 44699.7702
[7 empty] | 1898 | 2797 | 1783189 | 2020-07-17 21:25 | 2020-07-17 22:50 | 85 | 11kV | 970 | 12 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 209732 Broken 11kV ties pole HV-50072 Excluded OMS 1783189 | July | 2020 | 2021Q1 | 2021 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2020-07-17 | N | 80.8333 | N | 1 | N | N | 1.1101 | 39.4971 | 708.8474
[7 empty] | 3251 | 19797 | 1783262 | 2020-07-18 16:00 | 2020-07-18 16:20 | 20 | 11kV | 4660 | 233 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209734 Magpie & piece of wire on 11kV mains at Pole HR-22736. De-enegised HV & LV to remove with Operating stick. Excluded OMS 1783281 & 1783262 | July | 2020 | 2021Q1 | 2021 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | OH | Not Veg | 2020-07-18 | N | 20 | N | 2 | N | N | 1.1101 | 39.4971 | 3405.3906
[7 empty] | 2525 | 10346 | 1783290 | 2020-07-18 17:46 | 2020-07-19 00:45 | 419 | 11kV | 249735 | 1612 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209736 3 fault operations wires down at pole OS-30315 causing HV into LV The roadside span of 11kV copper mains failed between poles OR-30278 and OR-30315 and came to rest of the c phase LV conductor Excluded oms 1783290 | July | 2020 | 2021Q1 | 2021 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2020-07-18 | N | 154.9225 | N | 2 | N | N | 1.1101 | 39.4971 | 182498.9721
[7 empty] | 2083 | 5028 | 1783824 | 2020-07-21 19:29 | 2020-07-22 00:30 | 301 | 11kV | 165741 | 1201 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209752 2 fault operations 3 phase Overcurrent All part of one outage 1929hrs Fdr 81882 T & R & LO BCph OC (50TBC) possum burnt off tapping pole JU-72374 2250hrs Fdr 81864 Tripped E/F (51N) (reclose OFF for Fdr 81882) possum found on UGOH JU-72509 2329hrs Fdr 81864 Tripped OC ABC (50TABC) (relclose OFF for Fdr 81882) possum found on UGOH JU-72509. These outages are on one emergency swithcing sheet as fdr load switched on to 81864. Excluded OMS 1783823 & OMS 1783839 #### DQ | July | 2020 | 2021Q1 | 2021 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2020-07-21 | N | 138.0025 | N | 1 | N | N | 1.1101 | 39.4971 | 121118.6343
[7 empty] | 2017 | 4122 | 1783854 | 2020-07-22 01:46 | 2020-07-22 02:15 | 29 | 11kV | 37497 | 1293 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | At S12570 Avoca Panel 26 tripped on Relays: B phase IOC and EFI Cause: Flashover ciaused by possum between Panels 25 and Panel 26 @ Recloser CP45442 | July | 2020 | 2021Q1 | 2021 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2020-07-22 | N | 29 | N | 4 | N | N | 1.1101 | 39.4971 | 27401.7016
[7 empty] | 1803 | 1606 | 1784014 | 2020-07-22 16:18 | 2020-07-22 17:17 | 59 | 11kV | 49307 | 889 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 19 tripped on Relays: B phase E/F, Fault Check and EFI Signals: TX2 GE, ZE Cause: 11kV Feeder Fault from S78041 t0 S5301 See OMS 1784259 1784260 1784014 | July | 2020 | 2021Q1 | 2021 | ZN4545:PA19 | ZN4545:PA19 | ZN04545/000019 | RYDE | UG | Not Veg | 2020-07-22 | N | 55.4634 | N | 4 | N | N | 1.1101 | 39.4971 | 36032.1013
[7 empty] | 1903 | 2842 | 1784038 | 2020-07-22 18:06 | 2020-07-22 19:34 | 88 | 11kV | 186368 | 2243 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Cold <10C | N | At S15012 killarney Panel 4 Opened on SEL Cause: UGOH fault eblow USL 22875 Abnormal Switching: USL 23766 Open/LB22077 Closed (DMA Panel 8 UGOH) See OMS 1784255 1784256 1784063 1784052 1784039 1784038 | July | 2020 | 2021Q1 | 2021 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | Unknown | Unknown | 2020-07-22 | N | 83.0887 | N | 4 | N | N | 1.1101 | 39.4971 | 136192.2375
[7 empty] | 2305 | 7567 | 1784069 | 2020-07-22 21:05 | 2020-07-22 22:24 | 79 | 11kV | 179093 | 2267 | HV | Animal Possum | Animal | UGOH | Unplanned | Cold <10C | N | At S10999 Kogarah Panel 11 tripped on Signals: 11kV trip Relays: B and C phase OC, EFI, Minor Alarm A Cause: Possum found at the base of UGOH to S10292 The Strand Hayburn See OMS 1784069 1784251 1784250 1784072 1784075 1784074 1784071 1784070 | July | 2020 | 2021Q1 | 2021 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Not Veg | 2020-07-22 | N | 79 | N | 4 | N | N | 1.1101 | 39.4971 | 130875.8821
[7 empty] | 3059 | 17463 | 1784283 | 2020-07-24 00:35 | 2020-07-24 02:54 | 139 | 11kV | 222261 | 2034 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 398 Panel 4 tripped on timed O/C B phase and timed Earth Fault EFI Signals - 11kV trip, Zone and TX 1 group earths Field EFI's S3523, S57 A and B S5382 11kV cable fault from Sub 5832 Ness Tennyson to Sub 1943 Riverview Rd. See 1785462,1785458,1785456,1784543,1784286,1784283,1784285 | July | 2020 | 2021Q1 | 2021 | ZN398:PA4 | ZN398:PA4 | ZN00398/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-07-24 | N | 109.2729 | N | 2 | N | N | 1.1101 | 39.4971 | 162421.7832
[7 empty] | 1926 | 3070 | 1784274 | 2020-07-24 01:35 | 2020-07-24 19:40 | 1085 | 11kV | 1085 | 1 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | S5911 Shaddock Metal Polisher - Interrupted due to Jetski which was chained to 11kV UGOH pole was set on fire. | July | 2020 | 2021Q1 | 2021 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-07-24 | N | 1085 | N | 2 | N | N | 1.1101 | 39.4971 | 792.886
[7 empty] | 2493 | 10045 | 1784622 | 2020-07-26 07:20 | 2020-07-26 13:58 | 397.6167 | 11kV | 17892.75 | 45 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209796 2 fault operations Birds nest adjacent L/A. Bare conductor exposed. Not built to standard. | July | 2020 | 2021Q1 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-07-26 | N | 397.6167 | N | 5 | N | N | 1.1101 | 39.4971 | 13075.494
[7 empty] | 3117 | 18372 | 1784702 | 2020-07-26 16:01 | 2020-07-26 18:05 | 124.4167 | 11kV | 2488.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209799 C Phase DOLF : 10 Amp Please patrol as customer complained of numerous outages reciently | July | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-07-26 | N | 124.4167 | N | 5 | N | N | 1.1101 | 39.4971 | 1818.4006
[7 empty] | 2673 | 12015 | 1784747 | 2020-07-26 19:21 | 2020-07-26 20:37 | 76.0167 | 11kV | 10338.2667 | 136 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Rain Heavy | N | LID 209801 C Phase DOLF : 31 Amp HV Fuse carrier burnt in half. Excluded OMS 1784747 | July | 2020 | 2021Q1 | 2021 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2020-07-26 | N | 76.0167 | N | 5 | N | N | 1.1101 | 39.4971 | 7554.9004
[7 empty] | 2774 | 13572 | 1784830 | 2020-07-26 21:47 | 2020-07-26 23:50 | 123 | 11kV | 11808 | 96 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | Ex Panel 2 Rockdale Zone PT10001 Occupation Bestie Crentre Pase HDO 63Amp Cause: Centre phase HDO blown | July | 2020 | 2021Q1 | 2021 | ZN10998:PA2 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2020-07-26 | N | 123 | N | 5 | N | N | 1.1101 | 39.4971 | 8628.9381
[7 empty] | 1737 | 757 | 1784787 | 2020-07-26 20:41 | 2020-07-27 01:15 | 274 | 11kV | 94979 | 1635 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | CP49612 Barinya Wells Tripped and locked out on OC Cause: Large tree fallen onto 11kV OH mains. See OMS 1786035 1786036 See OMS 1784787 | July | 2020 | 2021Q1 | 2021 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2020-07-26 | N | 58.0911 | N | 5 | N | N | 1.1101 | 39.4971 | 69407.8518
[7 empty] | 2354 | 8272 | 1784955 | 2020-07-27 08:56 | 2020-07-27 10:05 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 209810 A Phase DOLF : 10 Amp Fuse Replace No Cause Found Excluded OMS 1784955 | July | 2020 | 2021Q1 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-07-27 | N | 69 | N | 7 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 1962 | 3411 | 1785060 | 2020-07-27 12:00 | 2020-07-27 13:15 | 75 | 11kV | 150 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 209819 Single phase DOLF : 10 Amp Transformer Requires Replacement Excluded OMS 1785060 | July | 2020 | 2021Q1 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2020-07-27 | N | 75 | N | 7 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 2596 | 11188 | 1785807 | 2020-07-27 14:00 | 2020-07-27 17:20 | 200 | 11kV | 1000 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Feeder from AB 3343 to LB 493 tee to PT1890, PT1941 and PT 1969 were interrupted to allow emergency tree removal at Blacks Road Arcadia. Interrrupted for Safety Reasons. | July | 2020 | 2021Q1 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2020-07-27 | N | 200 | N | 7 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 2792 | 13787 | 1785204 | 2020-07-27 17:57 | 2020-07-27 19:46 | 109 | 11kV | 139870 | 1284 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN1290 Leightonfield 11kV Panel 11 'Biloela Gurr No.2 feeder tripped out on Signals 11kV Trip Relays C phase O/C Field EFI's NIL Cause not ascertained DOp patrolled feeder but was unable to find anyting See1785204,1785960,1785962,1785210 | July | 2020 | 2021Q1 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-07-27 | N | 108.933 | N | 7 | N | N | 1.1101 | 39.4971 | 102212.8705
[7 empty] | 2028 | 4310 | 1785191 | 2020-07-27 20:30 | 2020-07-27 20:50 | 20 | 11kV | 1880 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Section of 11kV feeder from AB2362 to AB318 to AB290 tee S5809 Interrupted to allow tree brach removal Cause: Tree on OH mains | July | 2020 | 2021Q1 | 2021 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-07-27 | N | 20 | N | 7 | N | N | 1.1101 | 39.4971 | 1373.8485
[7 empty] | 2947 | 15810 | 1785237 | 2020-07-27 21:03 | 2020-07-28 00:45 | 222.4167 | 11kV | 19350.25 | 87 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN 14144 Wamberal Zone ex 11kV Panel 10L S18824 Wamberal Aux No.2 Isolated from 11kV Recloser 44582 Erina to extent of Feeder. Tree/branch on OH Mains at pole WL04998 Interrupted to remove tree and repair HV Mains. See 1785252,1785257 | July | 2020 | 2021Q1 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-07-27 | N | 222.4167 | N | 7 | N | N | 1.1101 | 39.4971 | 14140.592
[7 empty] | 2127 | 5417 | 1785266 | 2020-07-28 10:20 | 2020-07-28 18:00 | 459.8167 | 11kV | 104838.2 | 228 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2057 Shadforth St the 11kV TX tee off was interrupted for safety Interrupted to repair LV fault adjacent to LV board. Cable fault within kiosk on Distributor #2. See 1785412,1785266 | July | 2020 | 2021Q1 | 2021 | ZN180:PA7 | ZN180:PA7 | ZN00180/000007 | MOSMAN | UG | Not Veg | 2020-07-28 | N | 459.8167 | N | 1 | N | N | 1.1101 | 39.4971 | 76612.6644
[7 empty] | 2605 | 11219 | 1785646 | 2020-07-29 06:13 | 2020-07-29 08:45 | 152 | 11kV | 456 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | S62215 Muir Dasea No.2 - RMCB tripped inadvertently without any relay flags Cause unknown | July | 2020 | 2021Q1 | 2021 | ZN35900:PA22 | ZN35900:PA10 | ZN35900/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-07-29 | N | 152 | N | 4 | N | N | 1.1101 | 39.4971 | 333.2314
[7 empty] | 2909 | 15154 | 1785690 | 2020-07-29 09:45 | 2020-07-29 11:30 | 105 | 11kV | 4620 | 44 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 209842 Isolated to repair PT 50608, but Borer was bogged before reaching pole. Repair to continue with LLC as isolation. See also LID#209817 Excluded OMS 1785690 | July | 2020 | 2021Q1 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-07-29 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 3376.1597
[7 empty] | 3129 | 18458 | 1785174 | 2020-07-27 16:03 | 2020-07-29 18:15 | 3012 | 11kV | 27456 | 45 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 209817 Faulty Tx @ sub 50608. Note: N.Smith advised no access till flodd waters receeds. JMH Repairs have been delayed to no access due to flood waters. Also Borer got bogged - refer to OMS 1785888 Excluded OMS No. 1785174 | July | 2020 | 2021Q1 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-07-27 | N | 610.1333 | N | 7 | N | N | 1.1101 | 39.4971 | 20064.035
[7 empty] | 1833 | 2024 | 1785872 | 2020-07-29 23:30 | 2020-07-30 02:30 | 180 | 11kV | 77586 | 753 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | iR77908 Copacabana Koorabel tripped on: OC OH mains down between LB42041 and AB40456 to LB43148 tee PT11851 See 1785973 1785974 1785975 | July | 2020 | 2021Q1 | 2021 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2020-07-29 | N | 103.0359 | N | 4 | N | N | 1.1101 | 39.4971 | 56697.5604
[7 empty] | 1933 | 3178 | 1785873 | 2020-07-29 23:56 | 2020-07-30 08:30 | 514 | 11kV | 30840 | 60 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Bond off to PT10513 also See 1785970 Zn10994 Mortdale - Pnl.21 tripped & reclosed on: Earth Fault | July | 2020 | 2021Q1 | 2021 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Not Veg | 2020-07-29 | N | 514 | N | 4 | N | N | 1.1101 | 39.4971 | 22536.9624
[7 empty] | 2749 | 13148 | 1786065 | 2020-07-30 17:01 | 2020-07-30 18:50 | 109 | 11kV | 218 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 209853 no cause found. From Previous Storm Single Phase 10 Amp DOLF OMS 1786065" | July | 2020 | 2021Q1 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-07-30 | N | 109 | N | 2 | N | N | 1.1101 | 39.4971 | 159.308
[7 empty] | 1786 | 1465 | 1786066 | 2020-07-30 20:30 | 2020-07-30 20:52 | 22 | 11kV | 5324 | 242 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | S4075 Mowbray Avian - Interrupted to cut away tree growing into 11kV mains. | July | 2020 | 2021Q1 | 2021 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2020-07-30 | N | 22 | N | 2 | N | N | 1.1101 | 39.4971 | 3890.6222
[7 empty] | 2496 | 10072 | 1786320 | 2020-07-31 08:14 | 2020-07-31 10:05 | 111 | 11kV | 111327 | 1161 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35900 Potts Hill - Pnl.23 tripped on A Phase OC UG cable fault between CP3292 Sw/A, S8221 Sw/B and S47504 Sw/B See 1787123 1787124 1787125 | July | 2020 | 2021Q1 | 2021 | ZN35900:PA23 | ZN3472:PA19 | ZN03472/000019 | CUMBERLAND | UG | Not Veg | 2020-07-31 | N | 95.8889 | N | 3 | N | N | 1.1101 | 39.4971 | 81354.488
[7 empty] | 1890 | 2725 | 1786478 | 2020-07-31 16:55 | 2020-07-31 18:26 | 91 | 11kV | 12922 | 142 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID Job 209871 OMS 1786478, 1786480, 1786483, 1787156 DOLF down but not blown, cleaned contacts and re fitted | July | 2020 | 2021Q1 | 2021 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Not Veg | 2020-07-31 | N | 91 | N | 3 | N | N | 1.1101 | 39.4971 | 9443.0165
[7 empty] | 3069 | 17636 | 1786512 | 2020-08-01 01:01 | 2020-08-01 03:11 | 130 | 11kV | 33072 | 474 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman - Pnl.15 tripped on: C phase OC Field EFIs: S36230 & S48321 UG cable fault between S48321 Sw/B and S35178 Sw/A tee S4856. See 1787455 1787456 | August | 2020 | 2021Q1 | 2021 | ZN180:PA15 | ZN180:PA15 | ZN00180/000015 | MOSMAN | UG | Not Veg | 2020-08-01 | N | 69.7722 | N | 2 | N | N | 1.1101 | 39.4971 | 24168.0421
[7 empty] | 2588 | 11126 | 1786613 | 2020-08-01 17:56 | 2020-08-01 20:04 | 128 | 11kV | 6936 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209880 No Cause Found (Not Storm Condition) Phase B Pole Mounted RAGCB Overcurrent Refer to OMS 1786613 B Ph OC 163Amps" | August | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-08-01 | N | 126.1091 | N | 2 | N | N | 1.1101 | 39.4971 | 5068.6242
[7 empty] | 2147 | 5663 | 1786501 | 2020-07-31 20:35 | 2020-08-02 05:03 | 1948 | 11kV | 231251 | 1376 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.4 tripped on Earth Fault UG cable fault between S2147 Sw/B, S49418 Sw/A, 5300 Sw/A tee S1251 See 1787120 1787121 1787122 | July | 2020 | 2021Q1 | 2021 | ZN4545:PA4 | ZN4545:PA4 | ZN04545/000004 | RYDE | UG | Not Veg | 2020-07-31 | N | 168.0603 | N | 3 | N | N | 1.1101 | 39.4971 | 168991.4101
[7 empty] | 2169 | 5857 | 1786889 | 2020-08-03 15:11 | 2020-08-03 16:29 | 78 | 11kV | 5924 | 76 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.21 tripped on: A & C phase OC UG cable fault between S65311 and S35094 See 1789043 1789044 | August | 2020 | 2021Q1 | 2021 | ZN1788:PA21 | ZN1788:PA67 | ZN01788/000067 | BAYSIDE | UG | Not Veg | 2020-08-03 | N | 77.9474 | N | 2 | N | N | 1.1101 | 39.4971 | 4329.0845
[7 empty] | 2651 | 11719 | 1786955 | 2020-08-03 22:22 | 2020-08-03 23:46 | 84 | 11kV | 116384 | 1405 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Cold <10C | N | Zn10999 Kogarah - Pnl.36 tripped on SEF Cause not ascertained. Possible fault in old cast iron 11kvUGOH near USL30584. Restored OK See 1789037 1789038 | August | 2020 | 2021Q1 | 2021 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | OH | Veg | 2020-08-03 | N | 82.8356 | N | 2 | N | N | 1.1101 | 39.4971 | 85049.9945
[7 empty] | 3111 | 18347 | 1787146 | 2020-08-04 18:46 | 2020-08-04 20:33 | 107 | 11kV | 243092 | 2293 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.36 tripped on: SEF Suspect developing cable fault. Second fault in 2 days. Suspected section of cable taken out of service See 1789071 1789073 | August | 2020 | 2021Q1 | 2021 | ZN10999:PA36 | ZN10999:PA36 | ZN10999/000036 | GEORGES RIVER | UG | Not Veg | 2020-08-04 | N | 106.0148 | N | 1 | N | N | 1.1101 | 39.4971 | 177644.4636
[7 empty] | 1703 | 351 | 1787291 | 2020-08-05 13:50 | 2020-08-05 14:37 | 47 | 11kV | 47 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 209919 Animals or Birds Single Phase 10 Amp Substation DOLF See OMS 1787291 | August | 2020 | 2021Q1 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2020-08-05 | N | 47 | N | 2 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 2177 | 6013 | 1787323 | 2020-08-05 16:35 | 2020-08-05 17:23 | 47.6833 | 11kV | 4904.1333 | 104 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 209921 Phase A Substation DOLF "DOLF Replaced CC1: 22-"Refer to SOp" | August | 2020 | 2021Q1 | 2021 | 512:83741 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2020-08-05 | N | 47.1551 | N | 2 | N | N | 1.1101 | 39.4971 | 3583.796
[7 empty] | 2465 | 9574 | 1787371 | 2020-08-06 03:14 | 2020-08-06 06:10 | 176 | 11kV | 274570 | 2020 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.10 trippedon: A phase IOC, B pahse SEF Roadside bond burnt off AB30032 See 1789025 1789026 | August | 2020 | 2021Q1 | 2021 | ZN10998:PA10 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | OH | Not Veg | 2020-08-06 | N | 135.9257 | N | 1 | N | N | 1.1101 | 39.4971 | 200647.6576
[7 empty] | 2736 | 12906 | 1787656 | 2020-08-07 13:30 | 2020-08-07 15:38 | 127.7167 | 11kV | 20562.3833 | 161 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Heavy | N | At S9118 Cronulla Panel 3 - CP35260 Pacific Cres East was opened by AOP at the request of lineworker Cause: 11kv pole adjacent to CP35260 is about to fall over | August | 2020 | 2021Q1 | 2021 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Not Veg | 2020-08-07 | N | 127.7167 | N | 2 | N | N | 1.1101 | 39.4971 | 15026.3833
[7 empty] | 3215 | 19546 | 1787751 | 2020-08-07 22:19 | 2020-08-08 03:55 | 336 | 11kV | 118644 | 1499 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 209948 No Cause Found (Not Storm Condition) tapping blown off at pole JT-71023 during fault causing HV into LV, fault location not found. UG was connected to OH with AL PG clamps. All 3 PG clamps were burnt/melted. There was broken strands of wire on the 2 phases that were still up. PGs on all phases were replaced and a splice over damaged piece of wire on each phase. Low voltage mains were inspected and there was no visible damage see OMS 1787751 | August | 2020 | 2021Q1 | 2021 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2020-08-07 | N | 79.1488 | N | 2 | N | N | 1.1101 | 39.4971 | 86701.5358
[7 empty] | 3116 | 18371 | 1787795 | 2020-08-08 10:07 | 2020-08-08 11:07 | 60 | 11kV | 56220 | 937 | HV | Animal Bird | Animal | Circuit Breaker | Unplanned | Rain Light | N | 209952 Phases A & B. Overcurrent "oms 1787795 1787796 1787799 birds at pole SW-30141" Cust reported - Name Comment loud explosion at the pole near caravan park across road, round ball of fire and bird feathers everywhere - white cockatoos where on wires on pole | August | 2020 | 2021Q1 | 2021 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2020-08-08 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 41083.9178
[7 empty] | 2710 | 12413 | 1787763 | 2020-08-08 10:30 | 2020-08-08 15:35 | 305 | 11kV | 2135 | 7 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 209947 section isolated to repair pole KS-90108 also seeLID report # 209946 Trip and Reclose Semi Trailor has hit and broken off 11KV pole - KS9 0108. 11kv still alive and mains measure 4.8m above ground. Only approx 2m from 11kv to back of trailor. Please have DOPs attend and organise crew for pole replacement. EMSO standing by until crew arrives. SO1 has been notified. | August | 2020 | 2021Q1 | 2021 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2020-08-08 | N | 305 | N | 4 | N | N | 1.1101 | 39.4971 | 1560.195
[7 empty] | 3242 | 19742 | 1787859 | 2020-08-08 20:40 | 2020-08-08 23:45 | 185 | 11kV | 740 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 209999 Open circuit Live Line Lead Excluded OMS 1787859 | August | 2020 | 2021Q1 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-08-08 | N | 185 | N | 4 | N | N | 1.1101 | 39.4971 | 540.7702
[7 empty] | 2247 | 6810 | 1787867 | 2020-08-08 20:34 | 2020-08-09 00:15 | 221 | 11kV | 343243 | 3018 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S35900 Potts Hill Panel 1 tripped on Relays: IOC, Timed Signals: 11KV Trip Abnormal Switching: CP586 Closed, CP2360 Open, S36196 Closed SW/D open at S7247 Cause: UG cable fault from S32073 - Woodbine to S6513 Cairds Avon SW/A See OMS 1789080 1789081 1787857 | August | 2020 | 2021Q1 | 2021 | ZN35900:PA1 | ZN35900:PA1 | ZN35900/000001 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-08-08 | N | 113.7319 | N | 4 | N | N | 1.1101 | 39.4971 | 250831.8604
[7 empty] | 3036 | 17197 | 1788090 | 2020-08-09 20:47 | 2020-08-09 23:00 | 133 | 11kV | 9766 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ex Zn35370 Galston panel 8 Recloser CP559 Cobah Rd Tripped on Relays: IOC Trip OC Trip and Lockout Cause: Feeder Patrolled and restored except for section from LB3342 to NOAB2063. Which could not be patrolled as it crosses a gullt and involves fire trails. Will need to be patrolled by lineworker on Monday See OMS 1788929 1788924 1788931 1788090 | August | 2020 | 2021Q1 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2020-08-09 | N | 97.66 | N | 2 | N | N | 1.1101 | 39.4971 | 7136.7048
[7 empty] | 2029 | 4321 | 1788002 | 2020-08-09 19:26 | 2020-08-10 03:25 | 479 | 11kV | 432894 | 2294 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At ZN2196 Milperra Panel 25 Tripped and Locked out on Relays: A and B phase OC. Cause: 11kV Bond burnt off on footpath phase Doyle Ave Padstow (11kV feeder from LV3061 tee S1226 to S5371 Padstow Tech College NOTE: Distributor 1 @ S1226 broken up, Distributor 1 alive in and in LV Parallel. Distributor 2 and 3 interrupted longer due to inadequate LV parallels available See oMS 1788911 1788 912 1788913 1788914 1788915 1788002 1788124 1788125 CC1: 22-"Refer to SOp" | August | 2020 | 2021Q1 | 2021 | ZN2196:PA25 | ZN2196:PA25 | ZN02196/000025 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-08-09 | N | 188.7071 | N | 2 | N | N | 1.1101 | 39.4971 | 316346.167
[7 empty] | 2988 | 16494 | 1788354 | 2020-08-10 09:46 | 2020-08-10 10:21 | 35 | 11kV | 2590 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | REC48425 Kangy Angy tripped on: O/C Tree branch on 11kV OH mains near LK42499, removed by DOp | August | 2020 | 2021Q1 | 2021 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2020-08-10 | N | 35 | N | 11 | N | N | 1.1101 | 39.4971 | 1892.6956
[7 empty] | 2693 | 12284 | 1788248 | 2020-08-10 07:57 | 2020-08-10 10:38 | 161 | 11kV | 11087 | 91 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | REC559 Cobah - tripped 11kV OH off pin insulator between AB451 and LB2903 See previous interruption at 2047 9/8 See 1788918 1788919 | August | 2020 | 2021Q1 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2020-08-10 | N | 121.8352 | N | 11 | N | N | 1.1101 | 39.4971 | 8102.0526
[7 empty] | 1814 | 1741 | 1788477 | 2020-08-10 12:11 | 2020-08-10 13:03 | 52 | 11kV | 68744 | 1322 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn847 Hornsby - Pnl.7 tripped on A & C phase IOC Tree on mains adj LB1079, no apparent damage | August | 2020 | 2021Q1 | 2021 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | OH | Veg | 2020-08-10 | N | 52 | N | 11 | N | N | 1.1101 | 39.4971 | 50236.0876
[7 empty] | 2816 | 14003 | 1788174 | 2020-08-10 06:04 | 2020-08-10 13:30 | 446 | 11kV | 129493 | 574 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP50249 Kipling Shakespear tripped on Relays: OC and Lockout Section of Panel 18 down beyond LB42200 HV into LV inpection of premises in vicinity of incident.No damage found.Advised Dop onsite. See OMS 1788174 1788264 | August | 2020 | 2021Q1 | 2021 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2020-08-10 | N | 225.5976 | N | 11 | N | N | 1.1101 | 39.4971 | 94629.665
[7 empty] | 3209 | 19478 | 1788444 | 2020-08-10 11:08 | 2020-08-10 13:53 | 165 | 11kV | 2640 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 209967 10 Amp, Phase A Line DOLF Tree On 11kV Mains GS-31346 Note: start time amended from 10/08/20 11:07 due to Trip and Reclose prior to this event see OMS 1788925 CC1: 22-"Refer to SOp" | August | 2020 | 2021Q1 | 2021 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2020-08-10 | N | 165 | N | 11 | N | N | 1.1101 | 39.4971 | 1929.2341
[7 empty] | 1810 | 1701 | 1788202 | 2020-08-10 07:12 | 2020-08-10 14:48 | 455.6667 | 11kV | 9113.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 209961 Phase C 10 Amp Line DOLF | August | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-08-10 | N | 455.6667 | N | 11 | N | N | 1.1101 | 39.4971 | 6659.7552
[7 empty] | 3101 | 18171 | 1788397 | 2020-08-10 14:20 | 2020-08-10 15:20 | 60 | 11kV | 876 | 69 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 209970 Sub isolated to clear dislodged service wire. refer to OMS No. 1788397 | August | 2020 | 2021Q1 | 2021 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2020-08-10 | N | 12.6957 | N | 11 | N | N | 1.1101 | 39.4971 | 640.155
[7 empty] | 1702 | 338 | 1788386 | 2020-08-10 10:34 | 2020-08-10 20:05 | 571 | 11kV | 128683 | 1337 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Zn14891 Wyong - Pnl.9 tripped on A phase IOC Tree brought down 11kV mains outside 4 Hasluck DR. See 1788898 1788899 178901 | August | 2020 | 2021Q1 | 2021 | ZN14891:PA9 | ZN14891:PA9 | ZN14891/000009 | CENTRAL COAST | OH | Veg | 2020-08-10 | N | 96.2476 | N | 11 | N | N | 1.1101 | 39.4971 | 94037.7409
[7 empty] | 2740 | 13037 | 1788575 | 2020-08-10 13:42 | 2020-08-10 20:15 | 393 | 11kV | 34326 | 164 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 209974 Phases A,B & C (Three Phase) Instantaneous Overcurrent Sensitive Earth Fault 11kv Mains Broken away from ABS 40269 Burnt Tapping at pole FS93221 OMS 1788575##" Burnt Tapping at pole FS93221 also refer to OMS 1788575 | August | 2020 | 2021Q1 | 2021 | 522:83121 | 522:83121 | ZN00522/083121 | CESSNOCK | OH | Not Veg | 2020-08-10 | N | 209.3049 | N | 11 | N | N | 1.1101 | 39.4971 | 25084.4284
[7 empty] | 1874 | 2496 | 1788237 | 2020-08-10 07:45 | 2020-08-10 21:45 | 840 | 11kV | 4200 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S15067 Rodborough Rd 28 - 11kV/415V Tx tripped with low oil Transformer failure | August | 2020 | 2021Q1 | 2021 | ZN15011:PA6 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | UG | Not Veg | 2020-08-10 | N | 840 | N | 11 | N | N | 1.1101 | 39.4971 | 3069.2361
[7 empty] | 1994 | 3769 | 1788632 | 2020-08-10 14:51 | 2020-08-10 22:00 | 429 | 11kV | 19305 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | LID 209972 Pole Mounted RAGCB Sensitive Earth Fault | August | 2020 | 2021Q1 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-08-10 | N | 429 | N | 11 | N | N | 1.1101 | 39.4971 | 14107.5246
[7 empty] | 1802 | 1604 | 1789028 | 2020-08-11 14:49 | 2020-08-11 20:30 | 341 | 11kV | 369627 | 1551 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 209989 Burning 11kV Xarm pole JV50250 Excluded oms 1789028,1789050, | August | 2020 | 2021Q1 | 2021 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2020-08-11 | N | 238.3153 | N | 1 | N | N | 1.1101 | 39.4971 | 270112.5094
[7 empty] | 2135 | 5481 | 1789158 | 2020-08-12 02:07 | 2020-08-12 03:19 | 72 | 11kV | 41518 | 634 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.6 tripped on: A, B & C phase IOC 11kV End box failed at S5723 Gibson Drevet See 1789542 1789543 | August | 2020 | 2021Q1 | 2021 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-08-12 | N | 65.4858 | N | 6 | N | N | 1.1101 | 39.4971 | 30340.1298
[7 empty] | 2708 | 12389 | 1789184 | 2020-08-12 08:31 | 2020-08-12 09:35 | 64 | 11kV | 67072 | 1165 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 209994, 209995, 209996 and 209997 Sw 74582 tripped while switching NAR 61197. Scone Fdr's 89065 89061 & Aberdeen Fdr 82283 abnormal. 106A recorded at Sw 74582 (PU 100A) also refer to OMS 1789184, 1789185,1789190 | August | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-08-12 | N | 57.5725 | N | 6 | N | N | 1.1101 | 39.4971 | 49014.2393
[7 empty] | 2581 | 10973 | 1789260 | 2020-08-12 11:35 | 2020-08-12 13:24 | 109 | 11kV | 171674 | 2168 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.11 tripped on: BU IOC REC35756 Bundeena tripped & reclosed at the same time Abnormal: REC35260 Open DMA with REC62657 Closed Cockatoo found below 11kV mains in Baker St Bundeena Appears to be a protection malgrade between REC35756 and Pnl.11 See 1789532 1789533 | August | 2020 | 2021Q1 | 2021 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2020-08-12 | N | 79.1854 | N | 6 | N | N | 1.1101 | 39.4971 | 125454.2957
[7 empty] | 3168 | 19075 | 1789268 | 2020-08-12 12:28 | 2020-08-12 16:25 | 237 | 11kV | 4503 | 19 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200037 Broken crossarm pole IR-42273 Pitacree Rd. | August | 2020 | 2021Q1 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2020-08-12 | N | 237 | N | 6 | N | N | 1.1101 | 39.4971 | 3290.6596
[7 empty] | 2270 | 7130 | 1789422 | 2020-08-12 19:21 | 2020-08-12 22:45 | 204 | 11kV | 11628 | 57 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Lightning | N | Zn36200 Empire Bay - Pnl.8 tripped & reclosed on: A phase O/C - refer to OMS 1789536 @PT12216 Manly View Macdonalds - Roadside 20A HDO went HR and failed to operate during suspected lightning strike See 1789536 1789537 | August | 2020 | 2021Q1 | 2021 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2020-08-12 | N | 204 | N | 6 | N | N | 1.1101 | 39.4971 | 8497.3994
[7 empty] | 1828 | 1902 | 1789413 | 2020-08-13 01:19 | 2020-08-13 05:02 | 223 | 11kV | 8474 | 38 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 200009 Top of Line Fuse 64199 Burnt off Lightning hit crossarm on pole IR-13605 Excluded OMS 1789413 | August | 2020 | 2021Q1 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2020-08-13 | N | 223 | N | 8 | N | N | 1.1101 | 39.4971 | 6192.5493
[7 empty] | 2618 | 11289 | 1789564 | 2020-08-13 13:19 | 2020-08-13 15:15 | 116 | 11kV | 34220 | 295 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.6 tripped on A, B & C Phase IOC Abnormal: S5723 to S7865 out of service defective End box at S5723 Sw/A failed explosively. Restored via LV // See 1790297 1790298 | August | 2020 | 2021Q1 | 2021 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-08-13 | N | 116 | N | 8 | N | N | 1.1101 | 39.4971 | 25006.9667
[7 empty] | 2836 | 14255 | 1789575 | 2020-08-13 13:58 | 2020-08-13 15:50 | 112 | 11kV | 247151 | 2214 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn116 Leichhardt - Pnl.31 tripped on: 50TN Suspected UG cable fault between S1435, S8311 & S4615 See 1790289 1790290 | August | 2020 | 2021Q1 | 2021 | ZN116:PA31 | ZN116:PA31 | ZN00116/000031 | INNER WEST | UG | Not Veg | 2020-08-13 | N | 111.631 | N | 8 | N | N | 1.1101 | 39.4971 | 180610.6611
[7 empty] | 2808 | 13906 | 1789490 | 2020-08-13 16:05 | 2020-08-13 18:15 | 130 | 11kV | 1560 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV from iR44289 Berkeley Enterprise to LB44129 tee PT64101 & PT64873 interrupted to remove tree from OH mains ex Berkeley Vale Pnl.24L See 1790310 1793011 | August | 2020 | 2021Q1 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2020-08-13 | N | 130 | N | 8 | N | N | 1.1101 | 39.4971 | 1140.002
[7 empty] | 3225 | 19623 | 1789423 | 2020-08-12 21:57 | 2020-08-13 19:20 | 1283 | 11kV | 326513 | 1363 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | iR40118 Murrawal Kilpa 0.2 tripped on: OC Outside 28 Stanley St Wyongah, vehcile hit pole. Pole caught fire and brought down mains. Section of 11kV between LB40962, AB43654 to LK41536 tee PT11042 See 1790315 1790318 | August | 2020 | 2021Q1 | 2021 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2020-08-12 | N | 239.5547 | N | 6 | N | N | 1.1101 | 39.4971 | 238606.0699
[7 empty] | 1960 | 3399 | 1789638 | 2020-08-13 20:36 | 2020-08-13 22:16 | 100 | 11kV | 36575 | 487 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.13 tripped on Earth Fault UG cable fault between S1210 Sw/B and S4357 Sw/B See 1790307 1790308 | August | 2020 | 2021Q1 | 2021 | ZN35800:PA13 | ZN35800:PA13 | ZN35800/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-08-13 | N | 75.1027 | N | 8 | N | N | 1.1101 | 39.4971 | 26727.9312
[7 empty] | 2242 | 6755 | 1789609 | 2020-08-13 17:13 | 2020-08-14 01:23 | 490 | 11kV | 54880 | 112 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200010 11kV lead burnt off bottom of DOLF Excluded OMS 1789609 | August | 2020 | 2021Q1 | 2021 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Not Veg | 2020-08-13 | N | 490 | N | 8 | N | N | 1.1101 | 39.4971 | 40104.6853
[7 empty] | 2694 | 12295 | 1789623 | 2020-08-13 18:30 | 2020-08-14 14:30 | 1200 | 11kV | 23413.3 | 50 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | S2004 Magdala Pittwater - Dw/B Opened to make isolation point for DMA section of OH feeder with snapped head on 11kV pole. PT1822 Pittwater Magdala - Dist #1 - Interrupted for safety Abnormal: Macquarie Park Pnl.4 open, LB2672 Open, S2004 Sw/A Open, LB347 Closed, S8258 Sw/B Closed due to existing DMA See 1789624 1789623 1789625 | August | 2020 | 2021Q1 | 2021 | ZN8000:PA4 | ZN8000:PA4 | ZN08000/000004 | RYDE | OH | Not Veg | 2020-08-13 | N | 468.266 | N | 8 | N | N | 1.1101 | 39.4971 | 17109.7491
[7 empty] | 2384 | 8694 | 1789777 | 2020-08-14 16:47 | 2020-08-14 17:35 | 47.7167 | 11kV | 858.9 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT13944 Peach Orchard Beery 0.7 - Interrupted for safety OH crew please attend urgently. Customer's service neutral connection has burnt off at PT13944 which has caused distributor neutral connection to go open circuit as well for 1 bunch of LV ABC mains. Safe to leave dist on as pair of ABC mains parallelled 2 poles up. SB tied shut and tagged with SF and service neutral pulled. Please contact despatch after repairs made for Emso to reattend and test. Life support customer on tank water & sceptic, please attend ASAP. Thanks. | August | 2020 | 2021Q1 | 2021 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2020-08-14 | N | 47.7167 | N | 1 | N | N | 1.1101 | 39.4971 | 627.6588
[7 empty] | 2865 | 14500 | 1789614 | 2020-08-13 21:00 | 2020-08-15 14:40 | 2500 | 11kV | 2500 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | Section of 11kV OH between AB45004 & USL43581 tee PT12582 & PT13478 interrupted to reattach CCT to pin insulator Peats Ridge Zn - Pnl.1 See 1790584 1790585 | August | 2020 | 2021Q1 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-08-13 | N | 2500 | N | 8 | N | N | 1.1101 | 39.4971 | 1826.9263
[7 empty] | 2214 | 6464 | 1789884 | 2020-08-15 12:02 | 2020-08-15 16:27 | 265 | 11kV | 171330 | 826 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.8 tripped on: C phase timed OC DOP reports possible stick in contact with 11kV near PT48048 + Burnt bond off AB45143 See 1790581 1790582 | August | 2020 | 2021Q1 | 2021 | ZN12580:PA8 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2020-08-15 | N | 207.4213 | N | 5 | N | N | 1.1101 | 39.4971 | 125202.9106
[7 empty] | 3033 | 17171 | 1789897 | 2020-08-15 17:00 | 2020-08-15 18:30 | 90 | 11kV | 1530 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | PT1851 Knights Bevan - Interrupted for safety to remove tree from 1kV CCT RYAN TREE SERVE Tree Serve Large branch over all three phases of cct on pole AR26255. Is pulling alot weight on lines and will need ewp truck to remove. no arcing or sparking. lines are covered. | August | 2020 | 2021Q1 | 2021 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2020-08-15 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 1118.0789
[7 empty] | 1947 | 3270 | 1789882 | 2020-08-15 11:54 | 2020-08-15 19:00 | 426 | 11kV | 6816 | 16 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200029 Truck Hit pole IR-21123 damaged LV OH mains Excluded OMS 1789882 + 1789908 | August | 2020 | 2021Q1 | 2021 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2020-08-15 | N | 426 | N | 5 | N | N | 1.1101 | 39.4971 | 4980.9318
[7 empty] | 1806 | 1658 | 1789934 | 2020-08-15 20:35 | 2020-08-15 21:19 | 44 | 11kV | 12697 | 319 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.23 tripped on Earth Fault UG cable fault between S8181 to S8719 to S66064 See 1790509 1790510 1790511 | August | 2020 | 2021Q1 | 2021 | ZN8100:PA22 | ZN8100:PA22 | ZN08100/000022 | SYDNEY | UG | Not Veg | 2020-08-15 | N | 39.8025 | N | 5 | N | N | 1.1101 | 39.4971 | 9278.5931
[7 empty] | 1937 | 3202 | 1789930 | 2020-08-15 20:07 | 2020-08-15 21:21 | 74 | 11kV | 52234 | 758 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.29 tripped on: Earth Fault UG Cable fault between S5553 Sw/B, S5552 Sw/A and S35078 Sw/A See 1790516 1790515 | August | 2020 | 2021Q1 | 2021 | ZN965:PA29 | ZN965:PA29 | ZN00965/000029 | HORNSBY | UG | Not Veg | 2020-08-15 | N | 68.9103 | N | 5 | N | N | 1.1101 | 39.4971 | 38171.0666
[7 empty] | 2373 | 8590 | 1789951 | 2020-08-16 10:14 | 2020-08-16 16:50 | 396 | 11kV | 396 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 200036 Single phase LLC broken Wrong sub in OMS Excluded OMS 1789951 | August | 2020 | 2021Q1 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-08-16 | N | 396 | N | 1 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 2213 | 6440 | 1790032 | 2020-08-17 08:26 | 2020-08-17 10:30 | 124 | 11kV | 63203 | 838 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | LID 200040 2 fault operation B & C Phases Overcurrent, Earth Fault Cable termination onto Hazemeyer switchgear 29081 failed. Excluded OMS 1790032. | August | 2020 | 2021Q1 | 2021 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | UG | Not Veg | 2020-08-17 | N | 75.4212 | N | 3 | N | N | 1.1101 | 39.4971 | 46186.8882
[7 empty] | 2317 | 7700 | 1790067 | 2020-08-17 09:42 | 2020-08-17 11:20 | 98 | 11kV | 19229 | 203 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.30 tripped on: Earth Fault Fencing contractor damaged UG cable in Tracey St. Section between Pnl.30, AB31050, S10188 Sw/A & S10089 Sw/A | August | 2020 | 2021Q1 | 2021 | ZN10999:PA30 | ZN10999:PA30 | ZN10999/000030 | GEORGES RIVER | UG | Not Veg | 2020-08-17 | N | 94.7241 | N | 3 | N | N | 1.1101 | 39.4971 | 14051.986
[7 empty] | 1748 | 860 | 1790211 | 2020-08-17 21:50 | 2020-08-18 16:50 | 1140 | 11kV | 85189 | 615 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.2 tripped on: B Phase to N & Earth Fault UG cable fault between S7057 Sw/B & S63790 Sw/A tee S3281 See 1791576 1791577 1791578 | August | 2020 | 2021Q1 | 2021 | ZN1610:PA2 | ZN1610:PA2 | ZN01610/000002 | PARRAMATTA | UG | Not Veg | 2020-08-17 | N | 138.5187 | N | 3 | N | N | 1.1101 | 39.4971 | 62253.6085
[7 empty] | 2975 | 16319 | 1790423 | 2020-08-19 00:49 | 2020-08-19 13:20 | 751 | 11kV | 27571 | 97 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 200071 C Phase LLC fallen/burnt off mains Excluded OMS 1790423 1790485 | August | 2020 | 2021Q1 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2020-08-19 | N | 284.2371 | N | 9 | N | N | 1.1101 | 39.4971 | 20148.0736
[7 empty] | 1846 | 2121 | 1790527 | 2020-08-19 13:40 | 2020-08-19 15:09 | 89 | 11kV | 173105 | 1945 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.44 tripped on: A & C phase OC & C Phase IOC Tree on mains near LB62952 See 1792023 1790534 | August | 2020 | 2021Q1 | 2021 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Veg | 2020-08-19 | N | 89 | N | 9 | N | N | 1.1101 | 39.4971 | 126500.0283
[7 empty] | 1830 | 1927 | 1790566 | 2020-08-19 15:26 | 2020-08-19 16:03 | 37 | 11kV | 37 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.4 tripped onL Earth Fault UG cable fault between Pnl.41 and S1321 | August | 2020 | 2021Q1 | 2021 |  |  |  | SYDNEY | UG | Not Veg | 2020-08-19 | N | 37 | N | 9 | N | N | 1.1101 | 39.4971 | 27.0385
[7 empty] | 2555 | 10640 | 1790612 | 2020-08-19 17:58 | 2020-08-19 18:06 | 8 | 11kV | 9616 | 1202 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | LID 200080 Feeder isolated to re-arrange network ABS 6A062 burning up Excluded OMS 1790612. | August | 2020 | 2021Q1 | 2021 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2020-08-19 | N | 8 | N | 9 | N | N | 1.1101 | 39.4971 | 7027.0892
[7 empty] | 2847 | 14346 | 1790587 | 2020-08-19 16:03 | 2020-08-19 19:45 | 222 | 11kV | 1110 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200077 DOLF : 10 Amp HV mains down section isolated for repairs @ FP-40111. LF 61331 Bph replaced Excluded oms 1790587 | August | 2020 | 2021Q1 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-08-19 | N | 222 | N | 9 | N | N | 1.1101 | 39.4971 | 811.1553
[7 empty] | 2820 | 14062 | 1790607 | 2020-08-19 16:57 | 2020-08-19 21:40 | 283 | 11kV | 283 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200079 DOLF lead broken excluded OMS 1790607 | August | 2020 | 2021Q1 | 2021 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2020-08-19 | N | 283 | N | 9 | N | N | 1.1101 | 39.4971 | 206.8081
[7 empty] | 2562 | 10744 | 1790650 | 2020-08-19 17:52 | 2020-08-19 22:50 | 298 | 11kV | 27183 | 269 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200085 section isolated (935023/4755/61450) to remove tree on mains at pole NB-40689 Excluded oms 1790679 | August | 2020 | 2021Q1 | 2021 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2020-08-19 | N | 101.052 | N | 9 | N | N | 1.1101 | 39.4971 | 19864.5346
[7 empty] | 3207 | 19458 | 1790543 | 2020-08-19 18:35 | 2020-08-19 23:50 | 315 | 11kV | 28980 | 92 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Wind Strong | N | LID 200081 Replace leaking transformer at sub 3853 Excluded oms 1790543, 571,672,673,671 | August | 2020 | 2021Q1 | 2021 | 508:82576 | 508:82576 | ZN00508/082576 | PORT STEPHENS | OH | Not Veg | 2020-08-19 | N | 315 | N | 9 | N | N | 1.1101 | 39.4971 | 21177.7292
[7 empty] | 1982 | 3702 | 1790701 | 2020-08-20 01:45 | 2020-08-20 02:44 | 59 | 11kV | 76169 | 1291 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.16 tripped on: Earth Fault UG cable fault beyond S9133 Sw.B | August | 2020 | 2021Q1 | 2021 | ZN9037:PA16 | ZN9037:PA16 | ZN09037/000016 | SUTHERLAND | UG | Not Veg | 2020-08-20 | N | 59 | N | 9 | N | N | 1.1101 | 39.4971 | 55662.0586
[7 empty] | 3234 | 19669 | 1790735 | 2020-08-20 00:06 | 2020-08-20 08:05 | 479 | 11kV | 7185 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 200086 C Phase DOLF : 10 Amp Excluded OMS 1790697 | August | 2020 | 2021Q1 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-08-20 | N | 479 | N | 9 | N | N | 1.1101 | 39.4971 | 5250.5861
[7 empty] | 1783 | 1433 | 1790646 | 2020-08-19 17:42 | 2020-08-20 08:33 | 891 | 11kV | 891 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200082 HV droppers burnt off OHM Excluded oms 1790646 | August | 2020 | 2021Q1 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-08-19 | N | 891 | N | 9 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 2053 | 4745 | 1790752 | 2020-08-20 08:33 | 2020-08-20 09:50 | 77 | 11kV | 770 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200082 part 2 HV droppers burnt off OHM also refer to previous event 1791006 | August | 2020 | 2021Q1 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-08-20 | N | 77 | N | 9 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 2495 | 10068 | 1790709 | 2020-08-20 04:20 | 2020-08-20 10:50 | 390 | 11kV | 482508 | 1304 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12610 Long Jetty - Pnl.2 tripped & reclosed on B & C phase OC Bond burnt off above iR62165 Point Lakin Bond burnt off below LB40834 2 separate HV bonds failed. See 1791943 1791944 1791945 | August | 2020 | 2021Q1 | 2021 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2020-08-20 | N | 370.0215 | N | 9 | N | N | 1.1101 | 39.4971 | 352602.6148
[7 empty] | 2217 | 6550 | 1790789 | 2020-08-20 10:21 | 2020-08-20 15:00 | 279.15 | 11kV | 7257.9 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP44781 Dunks lane - 11kV Roadside & middle phase fuses blown Cause not ascertained | August | 2020 | 2021Q1 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2020-08-20 | N | 279.15 | N | 9 | N | N | 1.1101 | 39.4971 | 5303.8592
[7 empty] | 2685 | 12209 | 1790827 | 2020-08-20 11:44 | 2020-08-20 16:40 | 296 | 11kV | 185473 | 854 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Kogarah Zn Pnl.7 - S10925 Forest Water Board - Sw.B & Sw/A Tripped on: Earth Fault Abnormal: S10725 Sw/B closed with AB30253 Open OH mains down into LV outside 2 Croydon Rd Hurstville between S10920, LB46434 tee S10635 sEE 1791926 1791927 1791929 1791930 1791931 | August | 2020 | 2021Q1 | 2021 | ZN10999:PA24 | ZN10993:PA43 | ZN10993/000043 | GEORGES RIVER | OH | Not Veg | 2020-08-20 | N | 217.1815 | N | 9 | N | N | 1.1101 | 39.4971 | 135538.1979
[7 empty] | 2950 | 15888 | 1790700 | 2020-08-20 01:21 | 2020-08-20 16:55 | 934 | 11kV | 63277 | 673 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC49433 Pacific Minnesota 0.5 tripped on OC Tree brought down OH mains between S18541 Sw/B & AB44571 tee PT14521 See 1792029 1792030 | August | 2020 | 2021Q1 | 2021 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | OH | Veg | 2020-08-20 | N | 94.0223 | N | 9 | N | N | 1.1101 | 39.4971 | 46240.9652
[7 empty] | 2866 | 14514 | 1790699 | 2020-08-20 01:09 | 2020-08-20 18:00 | 1011 | 11kV | 19393 | 112 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200084 1 Fault operation Single phase Earth Fault 11kV OHM down between GW-80344 & GW-80345. Excluded OMS 1790699 | August | 2020 | 2021Q1 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2020-08-20 | N | 173.1518 | N | 9 | N | N | 1.1101 | 39.4971 | 14171.8324
[7 empty] | 1730 | 637 | 1791540 | 2020-08-21 11:28 | 2020-08-21 13:50 | 142 | 11kV | 142 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 200116 Faulty 11kV tapping pole JT-82752 | August | 2020 | 2021Q1 | 2021 |  |  |  | NEWCASTLE | OH | Not Veg | 2020-08-21 | N | 142 | N | 3 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 2541 | 10559 | 1790975 | 2020-08-20 19:12 | 2020-08-21 15:20 | 1208 | 11kV | 298809 | 1378 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200104 2 Fault operations B phase Sw 2123 Tripped and locked out due to Suspected Trans 17030 fault blew A phase DOLF + blew dropper to top of A phase DOLF + blew B phase DOLF + B phase bail clamp burnt through OHM causing it to fall into LV OHM Excluded OMS 1790975 | August | 2020 | 2021Q1 | 2021 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2020-08-20 | N | 216.8425 | N | 9 | N | N | 1.1101 | 39.4971 | 218360.8038
[7 empty] | 1870 | 2457 | 1791549 | 2020-08-21 17:21 | 2020-08-21 17:26 | 5 | 11kV | 4810 | 962 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200122 Interrupt to remove hazardous 11kv main broken from DOLF 52121 Excluded OMS 1791131 See also LID 200123/OMS 1791548 for Sub 52121 interruption | August | 2020 | 2021Q1 | 2021 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2020-08-21 | N | 5 | N | 3 | N | N | 1.1101 | 39.4971 | 3515.0061
[7 empty] | 3032 | 17120 | 1791131 | 2020-08-21 14:07 | 2020-08-21 17:50 | 223 | 11kV | 16056 | 72 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200123 Broken 11kv MAin of to of DOLF 52121 Excluded OMS 1791131 See also LID 200122/OMS 1791549 | August | 2020 | 2021Q1 | 2021 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2020-08-21 | N | 223 | N | 3 | N | N | 1.1101 | 39.4971 | 11733.2512
[7 empty] | 1839 | 2073 | 1791254 | 2020-08-22 04:17 | 2020-08-22 13:22 | 545 | 11kV | 47415 | 87 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC47746 Patonga Meroo tripped on: IOC Wires down at water crossing in caravan park | August | 2020 | 2021Q1 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2020-08-22 | N | 545 | N | 6 | N | N | 1.1101 | 39.4971 | 34649.4835
[7 empty] | 2610 | 11231 | 1791318 | 2020-08-22 14:23 | 2020-08-22 14:31 | 8 | 11kV | 3632 | 454 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200127 section of fdr de-energised to remove branch from 11kv mains. Excluded OMS 1791321 | August | 2020 | 2021Q1 | 2021 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Veg | 2020-08-22 | N | 8 | N | 6 | N | N | 1.1101 | 39.4971 | 2654.1585
[7 empty] | 1944 | 3257 | 1791326 | 2020-08-22 14:46 | 2020-08-22 15:45 | 59 | 11kV | 92158 | 1562 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn15009 Manly - Pnl.7 tripped, relcosed & locked out on: A & B phase OC Weather related, DOp patrolled no cause found. | August | 2020 | 2021Q1 | 2021 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Veg | 2020-08-22 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 67346.3482
[7 empty] | 1868 | 2435 | 1791329 | 2020-08-22 15:06 | 2020-08-22 16:44 | 98 | 11kV | 31140 | 375 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn187 Crows Nest - Pnl.23L tripped on: A & C phase IOC UG cable fault between S6594 and S5623 See 1791918 1791921 | August | 2020 | 2021Q1 | 2021 | ZN187:PA23 | ZN187:PA23 | ZN00187/000023 | LANE COVE | UG | Not Veg | 2020-08-22 | N | 83.04 | N | 6 | N | N | 1.1101 | 39.4971 | 22756.1935
[7 empty] | 1717 | 473 | 1791280 | 2020-08-22 10:10 | 2020-08-22 20:00 | 590 | 11kV | 16103 | 169 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200125 3 fault operations 3 phase Intellirupter; Overcurrent tree brought down 11kV mains between poles MG-90022 & MG-90021. Excluded OMS 1791280 | August | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-08-22 | N | 95.284 | N | 6 | N | N | 1.1101 | 39.4971 | 11767.5974
[7 empty] | 3054 | 17390 | 1791381 | 2020-08-22 23:20 | 2020-08-22 23:50 | 30 | 11kV | 30 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200129 Cph LLC burnt up. Excluded OMS 1791381 | August | 2020 | 2021Q1 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-08-22 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 3127 | 18435 | 1791460 | 2020-08-23 15:25 | 2020-08-23 16:50 | 85 | 11kV | 4335 | 51 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 200136 3 phase D Apps assigned, section isolated BEYOND abs 63919 for repairs to Xarm pole 8F-60139 Sparkes Rd . MdV | August | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-08-23 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 3167.8901
[7 empty] | 2861 | 14458 | 1791423 | 2020-08-23 11:16 | 2020-08-23 23:30 | 734 | 11kV | 101133 | 661 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At S3155 Double Bay panel 22 tripped on Relays: A and B phase OC, A phase IOC, EFI, Fault Check 2nd Attempt Panel 22 Tripped on relays: A and B phase IOC, EFI, Fault Check At S3155 Double Bay - Panel 17 tripped on A and B phase OC, Earth fault, EFI, fault check Cause: 2 UG faults S3705 - S364 defective S364 - S2164 -S318 defective See OMS 1791614 1791617 1791618 1791423/1447/1446 | August | 2020 | 2021Q1 | 2021 | ZN3155:PA22 | ZN3155:PA22 | ZN03155/000022 | WOOLLAHRA | UG | Not Veg | 2020-08-23 | N | 153 | N | 2 | N | N | 1.1101 | 39.4971 | 73905.0135
[7 empty] | 3164 | 19000 | 1791742 | 2020-08-24 17:05 | 2020-08-24 19:23 | 138 | 11kV | 22218 | 161 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | 11kV feeder from REC40178 Elizabeth Bay to AB44591 to AB41323 tee PT11394 & S12438 to repair AB43175 See 1791748 1791742 | August | 2020 | 2021Q1 | 2021 | ZN13000:PA10 | ZN13000:PA10 | ZN13000/000010 | CENTRAL COAST | OH | Not Veg | 2020-08-24 | N | 138 | N | 1 | N | N | 1.1101 | 39.4971 | 16236.2591
[7 empty] | 2435 | 9362 | 1791798 | 2020-08-25 09:03 | 2020-08-25 10:45 | 102 | 11kV | 9486 | 93 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200147 2 fault operations Wire off pin AI-50501 | August | 2020 | 2021Q1 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-08-25 | N | 102 | N | 4 | N | N | 1.1101 | 39.4971 | 6932.089
[7 empty] | 1799 | 1561 | 1791827 | 2020-08-25 11:04 | 2020-08-25 11:56 | 52 | 11kV | 64836 | 1344 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.28 tripped on: O/C & Earth Fault UG cable fault between S6254 Sw/B to S7283 Sw/A & S7384 Sw/A See 1792051 1792052 | August | 2020 | 2021Q1 | 2021 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-08-25 | N | 48.2411 | N | 4 | N | N | 1.1101 | 39.4971 | 47380.2365
[7 empty] | 1701 | 336 | 1791850 | 2020-08-25 12:14 | 2020-08-25 13:00 | 45.9833 | 11kV | 47822.6667 | 1040 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP62391 Wells Brougham tripped on: OC Tree branch on OH mains outside 30 Allison Rd Springfield | August | 2020 | 2021Q1 | 2021 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2020-08-25 | N | 45.9833 | N | 4 | N | N | 1.1101 | 39.4971 | 34947.3943
[7 empty] | 1798 | 1554 | 1791888 | 2020-08-25 13:45 | 2020-08-25 14:25 | 40 | 11kV | 440 | 11 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200157 Crossarm coach bolt out of pole HY-60171 | August | 2020 | 2021Q1 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-08-25 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 2447 | 9479 | 1791996 | 2020-08-26 02:16 | 2020-08-26 03:34 | 78 | 11kV | 101244 | 1298 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn12640 Umina - Pnl.12 tripped on: A & B phase IOC Possum on 11kV UGOH adj PT14097. | August | 2020 | 2021Q1 | 2021 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Not Veg | 2020-08-26 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 73986.129
[7 empty] | 1742 | 786 | 1791998 | 2020-08-26 03:46 | 2020-08-26 12:15 | 509 | 11kV | 25433 | 55 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP45015 Brush Creek tripped, reclosed and locked out on Earth Fault and IOC Cause: 11kV wires down adjacent to pole KA163 See OMS 1793444 1793446 1793447 1791998 | August | 2020 | 2021Q1 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2020-08-26 | N | 462.4182 | N | 3 | N | N | 1.1101 | 39.4971 | 18585.6863
[7 empty] | 2920 | 15318 | 1792059 | 2020-08-26 10:31 | 2020-08-26 16:45 | 374 | 11kV | 141862 | 1061 | HV | Wind Blown Debris | Adverse Weather/Environment | Bond | Unplanned | No Weather Impact | N | At S1290 Leightonfiled Panel 12 Tripped onC phase IOC and timed O/C Cause: Bond burnt off 41 Bileola Rd Note: Reports of Balloons on OG mains @ 77 Farrell Rd 11kV UGOH from S7430 to FA1123 defective 11kV OH mid span break done by L/W between poles See OMS 1792301 1792299 1792059 1792068 1792088 1792106 1792109 1792118 | August | 2020 | 2021Q1 | 2021 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-08-26 | N | 133.7059 | N | 3 | N | N | 1.1101 | 39.4971 | 103668.5654
[7 empty] | 2183 | 6074 | 1792219 | 2020-08-27 05:31 | 2020-08-27 07:35 | 124 | 11kV | 36580 | 295 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | DOp found possum at base of UGOH before AB1388 and road side phase at UGOH bond burnt off. also see OMS 1793243 for T&R Zn3154 St Ives - Pnl.17 tripped & reclosed on: Times Earth Fault Abnormal: LB64433 closed with AB2082 Open | August | 2020 | 2021Q1 | 2021 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Not Veg | 2020-08-27 | N | 124 | N | 3 | N | N | 1.1101 | 39.4971 | 26731.5851
[7 empty] | 3011 | 16781 | 1792214 | 2020-08-27 01:23 | 2020-08-27 12:00 | 637 | 11kV | 6086 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 200181 1 fault operation C Phase Overcurrent; Earth Fault 11kv link 40871 to UGOH broken. EF, Cph OC, ABC Time O/C Counter 53. Lockout relay Excluded oms 1792214. | August | 2020 | 2021Q1 | 2021 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2020-08-27 | N | 86.9429 | N | 3 | N | N | 1.1101 | 39.4971 | 4447.4693
[7 empty] | 2797 | 13836 | 1792282 | 2020-08-27 10:32 | 2020-08-27 12:05 | 93 | 11kV | 98652 | 1634 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15001 Brookvale - Pnl.18 tripped on: A phase IOC Abnormal: S50262 Sw/B Closed with S46891 Sw/A Open (DMA) UG cable fault between S16837 & S46889 to USL21622 (Common Point of isolation with existing DMA) See 1793235 1793236 1793237 1793239 1793240 | August | 2020 | 2021Q1 | 2021 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | UG | Not Veg | 2020-08-27 | N | 60.3745 | N | 3 | N | N | 1.1101 | 39.4971 | 72091.9719
[7 empty] | 2368 | 8506 | 1792522 | 2020-08-28 14:20 | 2020-08-28 15:36 | 76 | 11kV | 32334 | 461 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.44 tripped on: C phase OC Field EFi @ S49499 Cause not ascertained See 1793218 1793219 | August | 2020 | 2021Q1 | 2021 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Veg | 2020-08-28 | N | 70.1388 | N | 2 | N | N | 1.1101 | 39.4971 | 23628.7335
[7 empty] | 2234 | 6709 | 1792503 | 2020-08-28 13:25 | 2020-08-28 19:35 | 370 | 11kV | 219842 | 2327 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca -Pnl.21 tripped on A & C phase IOC & Inst Earth Fault Tree on 11kV mains causing them to twist together See 1793226 1793227 | August | 2020 | 2021Q1 | 2021 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Veg | 2020-08-28 | N | 94.4744 | N | 2 | N | N | 1.1101 | 39.4971 | 160654.0494
[7 empty] | 3181 | 19245 | 1792587 | 2020-08-29 02:43 | 2020-08-29 04:55 | 132 | 11kV | 79615 | 954 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9252 Jannali - Pnl.21 tripped, relcosed & locked out on: C phase O/C Field EFIs: S9014, S9973 S9878 S78420 S9129 UG Cable fault between S9129 Sw/B, AB35196, LB35290 tee PT9995 Note: EFI @ S9402 failed to operate on initial fault See 1793248 1793249 1793251 1793250 | August | 2020 | 2021Q1 | 2021 | ZN9252:PA21 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | UG | Not Veg | 2020-08-29 | N | 83.4539 | N | 2 | N | N | 1.1101 | 39.4971 | 58180.2938
[7 empty] | 2478 | 9840 | 1792593 | 2020-08-29 07:27 | 2020-08-29 09:17 | 110 | 11kV | 8690 | 79 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Somersby Zn Pnl.17 - Bond burnt off on footpath phase at LK44302 (Pole CA538) | August | 2020 | 2021Q1 | 2021 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2020-08-29 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 6350.3957
[7 empty] | 2158 | 5787 | 1792735 | 2020-08-30 10:48 | 2020-08-30 11:53 | 65 | 11kV | 101800 | 1570 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.24 tripped on Earth Fault Abnormal: S62726 Sw/B Closed with S49065 Sw/B Open due to DMA on Pnl.38 UG cable fault in frontline section of feeder between Pnl.24, S5568 & S5347 See 1793214 | August | 2020 | 2021Q1 | 2021 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | UG | Not Veg | 2020-08-30 | N | 64.8408 | N | 5 | N | N | 1.1101 | 39.4971 | 74392.4374
[7 empty] | 2413 | 9193 | 1792760 | 2020-08-30 13:59 | 2020-08-30 15:25 | 86 | 11kV | 344 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200212 B Phase DOLF : 32 Amp Excluded OMS 1792760 | August | 2020 | 2021Q1 | 2021 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2020-08-30 | N | 86 | N | 5 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 2646 | 11625 | 1792702 | 2020-08-30 05:20 | 2020-08-30 18:10 | 770 | 11kV | 378996 | 1437 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 200207 (Part 2) Car into pole JV-44002. also see OMS 1792850 Sw 8689 T/R @ 0424hrs and unplanned 200206. Excluded OMS 1792702. | August | 2020 | 2021Q1 | 2021 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2020-08-30 | N | 263.7411 | N | 5 | N | N | 1.1101 | 39.4971 | 276959.0983
[7 empty] | 1813 | 1716 | 1792790 | 2020-08-30 19:21 | 2020-08-30 20:35 | 74 | 11kV | 136381 | 1919 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.14 tripped on: Earth Fault UG cable fault between S48955 Sw/B & S2979 Sw/A See 1793196 1793197 | August | 2020 | 2021Q1 | 2021 | ZN35600:PA14 | ZN35600:PA14 | ZN35600/000014 | RANDWICK | UG | Not Veg | 2020-08-30 | N | 71.0688 | N | 5 | N | N | 1.1101 | 39.4971 | 99663.2122
[7 empty] | 3080 | 17796 | 1792807 | 2020-08-30 22:28 | 2020-08-30 23:40 | 72 | 11kV | 34010 | 571 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.24 tripped on: C phase OC 2 phases of 11kV OH mains twisted together with burning span before PT1533. See 1793191 1793192 1793193 | August | 2020 | 2021Q1 | 2021 | ZN1287:PA24 | ZN1287:PA24 | ZN01287/000024 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-08-30 | N | 59.5622 | N | 5 | N | N | 1.1101 | 39.4971 | 24853.5049
[7 empty] | 1778 | 1386 | 1792815 | 2020-08-31 06:26 | 2020-08-31 08:00 | 94 | 11kV | 146728 | 2019 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.11 tripped on: Earth Leakage UG cable fault between S9836 and S9357 tee S9709 See 1793203 1793206 1793207 | August | 2020 | 2021Q1 | 2021 | ZN9035:PA11 | ZN9035:PA11 | ZN09035/000011 | SUTHERLAND | UG | Not Veg | 2020-08-31 | N | 72.6736 | N | 5 | N | N | 1.1101 | 39.4971 | 107224.4947
[7 empty] | 2883 | 14742 | 1792937 | 2020-08-31 11:40 | 2020-08-31 14:26 | 166 | 11kV | 155 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200225 Broken dead ends at P. AH-90012 Excluded OMS 1792937 | August | 2020 | 2021Q1 | 2021 | 813:89058 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2020-08-31 | N | 155 | N | 5 | N | N | 1.1101 | 39.4971 | 113.2694
[7 empty] | 1915 | 2964 | 1793009 | 2020-08-31 15:27 | 2020-08-31 18:01 | 154 | 11kV | 314687 | 3283 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.16 tripped on: B Phase OC UG cable fault between S64006 Sw/B, S36060 Sw/B and S35036 Sw/D See 1793468 1793469 1793471 | August | 2020 | 2021Q1 | 2021 | ZN35600:PA16 | ZN35600:PA16 | ZN35600/000016 | SYDNEY | UG | Not Veg | 2020-08-31 | N | 95.8535 | N | 5 | N | N | 1.1101 | 39.4971 | 229963.9779
[7 empty] | 2392 | 8791 | 1792998 | 2020-08-31 15:09 | 2020-08-31 20:00 | 291 | 11kV | 163781 | 1351 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S36300 Balgowlah North Panel 13 Tripped on Signals: 11kV Trip, No1 TX group earth Relays: E/F, O/C, EFI Lockout Cause: UGOH defective to S15619 Lovett St See OMS 1793470 1793455 1793454 1793453 1793451 1793033/015/010/008/005/004/003/002/000/999/998 | August | 2020 | 2021Q1 | 2021 | ZN36300:PA13 | ZN36300:PA13 | ZN36300/000013 | NORTHERN BEACHES | Unknown | Unknown | 2020-08-31 | N | 121.2295 | N | 5 | N | N | 1.1101 | 39.4971 | 119686.3241
[7 empty] | 2954 | 15973 | 1792944 | 2020-08-31 12:20 | 2020-08-31 23:10 | 650 | 11kV | 5988 | 12 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | REC3333 Davidson Park tripped on: OC Section of UG cable to S4575 St Ives Showground hit by contractors See 1792944 1792965 | August | 2020 | 2021Q1 | 2021 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | UG | Not Veg | 2020-08-31 | N | 499 | N | 5 | N | N | 1.1101 | 39.4971 | 4375.8538
[7 empty] | 1987 | 3720 | 1793092 | 2020-09-01 04:59 | 2020-09-01 06:20 | 81 | 11kV | 36662 | 500 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.37 tripped on Earth Fault UG cable fault between S6152, S3213 & S6914 See 1793480 1793481 1793482 | September | 2020 | 2021Q1 | 2021 | ZN965:PA37 | ZN965:PA37 | ZN00965/000037 | HORNSBY | UG | Not Veg | 2020-09-01 | N | 73.324 | N | 3 | N | N | 1.1101 | 39.4971 | 26791.5083
[7 empty] | 3042 | 17241 | 1793289 | 2020-09-01 16:15 | 2020-09-01 17:35 | 80 | 11kV | 12951 | 171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn167 Auburn - Pnl.1 tripped on IOC & Earth Fault UG cable fault between S8124 Sw/B and S5441 Sw/A See 1793641 1793642 | September | 2020 | 2021Q1 | 2021 | ZN167:PA1 | ZN167:PA1 | ZN00167/000001 | CUMBERLAND | UG | Not Veg | 2020-09-01 | N | 75.7368 | N | 3 | N | N | 1.1101 | 39.4971 | 9464.2088
[7 empty] | 3266 | 20029 | 1793313 | 2020-09-01 18:45 | 2020-09-01 21:03 | 138 | 11kV | 4083 | 38 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200241 pole IR-12218 conductor off insulator and resting on x-arm. isolated to repair under AP. Excluded OMS 1793282 | September | 2020 | 2021Q1 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2020-09-01 | N | 107.4474 | N | 3 | N | N | 1.1101 | 39.4971 | 2983.736
[7 empty] | 2664 | 11893 | 1793427 | 2020-09-02 11:57 | 2020-09-02 13:38 | 101 | 11kV | 117897 | 2079 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200254 Phases A & B. Overcurrent Leg 1 C phase O/C Leg 2 A & B O/C, Fault indication on Leg 2 & E/F indicator operated Sw 78759B. No fault found. Detailed patrol required" No Cause Found (Not Storm Condition) refer to OMS 1793427 | September | 2020 | 2021Q1 | 2021 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Veg | 2020-09-02 | N | 56.7085 | N | 2 | N | N | 1.1101 | 39.4971 | 86155.6502
[7 empty] | 3066 | 17607 | 1793539 | 2020-09-02 20:39 | 2020-09-02 22:07 | 88 | 11kV | 29304 | 333 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 200256 1 fault operation B Phase Earth Fault 11kV UGOH arrestor blown & UGOH termination damaged at pole IU-59102. Excluded OMS No. 1793539 | September | 2020 | 2021Q1 | 2021 | 224:80331 | 224:80331 | ZN00224/080331 | LAKE MACQUARIE | OH | Not Veg | 2020-09-02 | N | 88 | N | 2 | N | N | 1.1101 | 39.4971 | 21414.4989
[7 empty] | 2122 | 5377 | 1793662 | 2020-09-03 17:22 | 2020-09-03 19:00 | 98 | 11kV | 1078 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200268 C phase Damaged HV main between Poles DT20081 and DT20082. Broken HV insulator at Pole DT20082. Excluded OMS 1793662 | September | 2020 | 2021Q1 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-09-03 | N | 98 | N | 1 | N | N | 1.1101 | 39.4971 | 787.7706
[7 empty] | 2037 | 4496 | 1793869 | 2020-09-04 19:32 | 2020-09-04 21:35 | 123 | 11kV | 615 | 5 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | PT18738 Paroo Wattle Tree 0.3 - Footpath phase HDO blown Lightning | September | 2020 | 2021Q1 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2020-09-04 | N | 123 | N | 2 | N | N | 1.1101 | 39.4971 | 449.4239
[7 empty] | 2863 | 14470 | 1793859 | 2020-09-04 18:47 | 2020-09-04 22:50 | 243 | 11kV | 172840 | 1259 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12660 Woy Woy - pnl.14 tripped on C phase OC Lightning in the area at the time See 1795526 1795527 1795528 | September | 2020 | 2021Q1 | 2021 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2020-09-04 | N | 137.2836 | N | 2 | N | N | 1.1101 | 39.4971 | 126306.3741
[7 empty] | 2098 | 5177 | 1793916 | 2020-09-05 07:54 | 2020-09-05 10:35 | 161 | 11kV | 1449 | 9 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Previous Storm | N | PT13500 Barnes George Downe 0.6 - HDO operated Possible storm damage from night before | September | 2020 | 2021Q1 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-09-05 | N | 161 | N | 6 | N | N | 1.1101 | 39.4971 | 1058.8865
[7 empty] | 1711 | 411 | 1793944 | 2020-09-05 10:30 | 2020-09-05 13:00 | 150 | 11kV | 600 | 4 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Previous Storm | N | PT13277 George Downes Kamb 0.8 - Footpath phase HDO operated Possible storm damage from the night before | September | 2020 | 2021Q1 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-09-05 | N | 150 | N | 6 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 1988 | 3721 | 1795521 | 2020-09-05 17:54 | 2020-09-05 19:05 | 71 | 11kV | 49913 | 703 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9900 Menai - Pnl.19 tripped, reclosed & locked out on: B Phase timed O/C UG cable fault between S9322 Sw/A and S9175 Sw/B | September | 2020 | 2021Q1 | 2021 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | UG | Not Veg | 2020-09-05 | N | 71 | N | 6 | N | N | 1.1101 | 39.4971 | 36474.9482
[7 empty] | 3222 | 19614 | 1794004 | 2020-09-05 17:41 | 2020-09-05 23:28 | 347 | 11kV | 17350 | 50 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200291 section isolated to repair faulty xarm at pole KQ-50022 | September | 2020 | 2021Q1 | 2021 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2020-09-05 | N | 347 | N | 6 | N | N | 1.1101 | 39.4971 | 12678.8683
[7 empty] | 1871 | 2458 | 1794018 | 2020-09-05 22:18 | 2020-09-05 23:55 | 97 | 11kV | 194 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 200293 3 phase tapping burnt off at 43905 Greta Sports Ground No 1 Excluded oms 1794018 | September | 2020 | 2021Q1 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2020-09-05 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 141.7695
[7 empty] | 1959 | 3394 | 1794023 | 2020-09-06 00:10 | 2020-09-06 02:30 | 139.7333 | 11kV | 2654.9333 | 19 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 200295 suspect fuse fatigue dq | September | 2020 | 2021Q1 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-09-06 | N | 139.7333 | N | 2 | N | N | 1.1101 | 39.4971 | 1940.147
[7 empty] | 2785 | 13710 | 1794021 | 2020-09-06 00:07 | 2020-09-06 07:20 | 433 | 11kV | 8660 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200296 B Phase DOLF : 31 Amp BLOWN B PHASE (31.5A) 11KV DOLF AT TX 4972 - WARNERS BAY RD, NO FAULTS/FAILURES FOUND AT TX, LINE PATROLLED LV DISTRIBUTOR 4972, NO FAULTS FOUND. REPLACED DOLF AT 7:20, VOLTAGES A1 TO N=245 VOLTS, A2 TO N = 247 VOLTS, A3 TO N = 246 VOLTS Excluded OMS 1704022 | September | 2020 | 2021Q1 | 2021 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2020-09-06 | N | 433 | N | 2 | N | N | 1.1101 | 39.4971 | 6328.4726
[7 empty] | 2534 | 10466 | 1794031 | 2020-09-05 22:48 | 2020-09-06 10:05 | 677 | 11kV | 3385 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At PT 15550 McCowen Rd centre phase HDO was blown Cuase not ascertained, see recloser trip at same time, Terrey Hills PA10 | September | 2020 | 2021Q1 | 2021 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2020-09-05 | N | 677 | N | 6 | N | N | 1.1101 | 39.4971 | 2473.6582
[7 empty] | 3077 | 17737 | 1794210 | 2020-09-07 13:12 | 2020-09-07 21:30 | 498 | 11kV | 94592 | 974 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwhich Hill - Pnl.4 tripped on: Earth Fault Abnormal: Feeder between S57 Sw/B, S3246 Sw/A, S1943 via S5832 out of service under AP LV // related to planned work failed at S238 Excavating contractors exposed 11kV UG cable and appeared to have caused damage. See 1795485 1795486 1795487 | September | 2020 | 2021Q1 | 2021 | ZN398:PA4 | ZN398:PA4 | ZN00398/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-09-07 | N | 97.117 | N | 1 | N | N | 1.1101 | 39.4971 | 69125.0436
[7 empty] | 2893 | 14845 | 1794303 | 2020-09-08 08:11 | 2020-09-08 09:15 | 64 | 11kV | 128 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200311 Replaced DOLF screw cap Excluded OMS 1794303 | September | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-09-08 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 2113 | 5286 | 1794461 | 2020-09-08 23:53 | 2020-09-09 01:13 | 80 | 11kV | 51618 | 732 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn1850Bass Hill - Pnl.32 tripped on: A & B phase OC Cause not ascertained See 1795518 1795519 | September | 2020 | 2021Q1 | 2021 | ZN1850:PA32 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-09-08 | N | 70.5164 | N | 2 | N | N | 1.1101 | 39.4971 | 37720.9119
[7 empty] | 2035 | 4467 | 1794571 | 2020-09-09 14:30 | 2020-09-09 16:42 | 132 | 11kV | 33354 | 262 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | Ex Revesby Pnl.4 - 11k interrupted between LB3261 & S8587 Sw/B (N/O) tee PT64897 & PT390 Leakage to earth down pole (Pole EH1974 outside 871 Henry Lawson Dr). HV Insulator cracked & voltage measured at base of pole S.8587 Dist #2 - Interrupted for safety See 1794571 1794592 | September | 2020 | 2021Q1 | 2021 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-09-09 | N | 127.3053 | N | 3 | N | N | 1.1101 | 39.4971 | 24374.1194
[7 empty] | 2690 | 12263 | 1794624 | 2020-09-09 17:01 | 2020-09-09 17:36 | 35 | 11kV | 27820 | 935 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn80 Chatswood - Pnl.31 tripped on: B & C phase IOC Tree on OH mains outside 30 Sharland | September | 2020 | 2021Q1 | 2021 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2020-09-09 | N | 29.754 | N | 3 | N | N | 1.1101 | 39.4971 | 20330.0354
[7 empty] | 2237 | 6722 | 1794659 | 2020-09-09 23:50 | 2020-09-10 00:58 | 68 | 11kV | 103428 | 1528 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca - Pnl.37 tripped, relcosed & locked out on: A & B phase IOC Tree branch on mains near AB40431. See 1795512 1795513 | September | 2020 | 2021Q1 | 2021 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2020-09-09 | N | 67.6885 | N | 3 | N | N | 1.1101 | 39.4971 | 75582.1318
[7 empty] | 2156 | 5769 | 1794783 | 2020-09-10 15:25 | 2020-09-10 16:50 | 85.1833 | 11kV | 340.7333 | 4 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200334 A Phase DOLF : 10 Amp Galah | September | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-09-10 | N | 85.1833 | N | 1 | N | N | 1.1101 | 39.4971 | 248.9979
[7 empty] | 1739 | 766 | 1794821 | 2020-09-11 05:18 | 2020-09-11 09:20 | 242 | 11kV | 242 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 200341 Single phase LLC reapplied Kerr sub10903 | September | 2020 | 2021Q1 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2020-09-11 | N | 242 | N | 2 | N | N | 1.1101 | 39.4971 | 176.8465
[7 empty] | 3227 | 19630 | 1794955 | 2020-09-11 19:35 | 2020-09-11 19:56 | 20.75 | 11kV | 83 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200346 section isolated to repair xarm straps at pole BU-10228 Excluded OMS 1794955 | September | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2020-09-11 | N | 20.75 | N | 2 | N | N | 1.1101 | 39.4971 | 60.654
[7 empty] | 3136 | 18590 | 1795066 | 2020-09-12 15:24 | 2020-09-12 23:11 | 467 | 33kV Distribution | 1430 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200351 3 fault operations 2 previous T/Recloses.L/O on this operation. faulty xarm replaced at pole JT-61860 A prot = B phase Earth fault B prot = 50TB & 50TN | September | 2020 | 2021Q1 | 2021 | 417:80491 | 417:80491 | ZN00417/080491 | NEWCASTLE | OH | Not Veg | 2020-09-12 | N | 238.3333 | N | 1 | N | N | 1.1101 | 39.4971 | 1045.0018
[7 empty] | 3277 | 20179 | 1795498 | 2020-09-13 03:52 | 2020-09-13 11:46 | 474 | 11kV | 474 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S.1485 Arnott - B phase 11kV Fuse tripped (110Amp) Customer's installation fault - suspect grading issue | September | 2020 | 2021Q1 | 2021 |  |  |  | CANADA BAY | Unknown | Not Veg | 2020-09-13 | N | 474 | N | 1 | N | N | 1.1101 | 39.4971 | 346.3852
[7 empty] | 2711 | 12414 | 1795159 | 2020-09-14 01:13 | 2020-09-14 02:55 | 102.1167 | 11kV | 178720.1167 | 1845 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.29 tripped on: IOC A & C phases Abnormal: LB1477 closed with LB336 Open (DMA) Field EFIs: S46659 Cause not ascertained. See 1795490 1795491 1795492 | September | 2020 | 2021Q1 | 2021 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Veg | 2020-09-14 | N | 96.8673 | N | 1 | N | N | 1.1101 | 39.4971 | 130603.3899
[7 empty] | 2326 | 7916 | 1795358 | 2020-09-15 02:30 | 2020-09-15 08:20 | 350 | 11kV | 2020 | 14 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 200367 Broken Live Line Clamp at sub 49558 excluded OMS 1795358 | September | 2020 | 2021Q1 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-09-15 | N | 144.2857 | N | 3 | N | N | 1.1101 | 39.4971 | 1476.1564
[7 empty] | 2254 | 6918 | 1795462 | 2020-09-15 15:54 | 2020-09-15 16:35 | 41 | 11kV | 779 | 19 | HV | Staff Other | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | Section of 11kV feeder from AB2063 to AB451 interrupted due to incorrect open point opened on reconnect of NAR62515 Abnormal: AB2063 Closed with LB451 Open & Defective | September | 2020 | 2021Q1 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2020-09-15 | N | 41 | N | 3 | N | N | 1.1101 | 39.4971 | 569.2702
[7 empty] | 2426 | 9286 | 1795500 | 2020-09-15 18:54 | 2020-09-15 20:38 | 104 | 11kV | 141128 | 1357 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200379 1 fault operation 3 phase Overcurrent Over Head Mains wrapped together at ABS 40350 Excluded OMS 1795500 | September | 2020 | 2021Q1 | 2021 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2020-09-15 | N | 104 | N | 3 | N | N | 1.1101 | 39.4971 | 103132.1798
[7 empty] | 1927 | 3076 | 1795558 | 2020-09-16 07:32 | 2020-09-16 09:20 | 108 | 11kV | 130100 | 1355 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.8 tripped on: Earth Fault UG cable fault between S9294 & S9872 EFIs incorrectly operated at S9855, 9866, 9872 See 1795791 1795792 | September | 2020 | 2021Q1 | 2021 | ZN9118:PA8 | ZN9118:PA8 | ZN09118/000008 | SUTHERLAND | UG | Not Veg | 2020-09-16 | N | 96.0148 | N | 5 | N | N | 1.1101 | 39.4971 | 95073.2427
[7 empty] | 1954 | 3372 | 1795560 | 2020-09-16 07:42 | 2020-09-16 10:07 | 145 | 11kV | 318093 | 2318 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.31 tripped on: IOC UG cable fault between S.291 Sw/A, S35473 Sw/A, S300 Sw/A & S3924 Sw/B See 1795788 1795789 | September | 2020 | 2021Q1 | 2021 | ZN2602:PA31 | ZN2602:PA31 | ZN02602/000031 | RANDWICK | UG | Not Veg | 2020-09-16 | N | 137.2274 | N | 5 | N | N | 1.1101 | 39.4971 | 232452.9822
[7 empty] | 2222 | 6628 | 1795608 | 2020-09-16 12:05 | 2020-09-16 14:50 | 164.65 | 11kV | 23215.65 | 141 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | S4866 Nobel Boronia - 11kV Fuse switch was tripped by DOP for safety after car hit Kiosk Kiosk will require replacement. Restored via LV // | September | 2020 | 2021Q1 | 2021 | ZN1285:PA20 | ZN1285:PA20 | ZN01285/000020 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2020-09-16 | N | 164.65 | N | 5 | N | N | 1.1101 | 39.4971 | 16965.3123
[7 empty] | 2589 | 11129 | 1795715 | 2020-09-16 14:30 | 2020-09-16 15:15 | 45 | 11kV | 405 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200384 B Phase DOLF : 20 Amp | September | 2020 | 2021Q1 | 2021 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2020-09-16 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 2762 | 13308 | 1795667 | 2020-09-16 16:07 | 2020-09-16 17:31 | 84 | 11kV | 115527 | 1457 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15012 Killarney - Pnl.6 tripped. UG cable fault between S15605 Sw/B and S15337 Sw/A See 1795758 17957591795760 | September | 2020 | 2021Q1 | 2021 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | UG | Not Veg | 2020-09-16 | N | 79.291 | N | 5 | N | N | 1.1101 | 39.4971 | 84423.7241
[7 empty] | 2130 | 5462 | 1795708 | 2020-09-17 03:25 | 2020-09-17 04:41 | 76 | 11kV | 93632 | 1232 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn1673 Turramurra - Pnl.7 tripped on: A phase IOC & Earth Fault Abnormal: Closed LB203 with REC63174 Closed Possum made contact with PT1561. No Damage | September | 2020 | 2021Q1 | 2021 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2020-09-17 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 68423.5039
[7 empty] | 3124 | 18420 | 1795786 | 2020-09-17 11:22 | 2020-09-17 13:25 | 123 | 11kV | 253248 | 2146 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3155 Double Bay Pa44 tripped on Relays: EF, EFI, Fault Check, IT receive Signals: Zone Earth, Group Earth 11kV trip Cause: Section of 11kV feeder from S4522 New Beach Loftus SW/ B to S2803 See OMS 1797241 1797242 1795786 | September | 2020 | 2021Q1 | 2021 | ZN3155:PA44 | ZN3155:PA44 | ZN03155/000044 | WOOLLAHRA | UG | Not Veg | 2020-09-17 | N | 118.0093 | N | 6 | N | N | 1.1101 | 39.4971 | 185066.1688
[7 empty] | 2528 | 10373 | 1795906 | 2020-09-17 17:22 | 2020-09-17 18:59 | 97 | 11kV | 133569 | 1377 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S12610 Long Jetty - Bond burnt off adjacent to PT11299 @ pole BV3734 See OMS 1797247 1795906 | September | 2020 | 2021Q1 | 2021 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2020-09-17 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 97608.2856
[7 empty] | 2827 | 14105 | 1795951 | 2020-09-17 19:02 | 2020-09-17 20:52 | 110 | 11kV | 6270 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At CP44604 Dog Trap Rd feeder tripped on relays - Overcurrent Cause: Tree/Branch on 11kV mains at Pole OU-756 | September | 2020 | 2021Q1 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-09-17 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 4581.9311
[7 empty] | 2960 | 16048 | 1795930 | 2020-09-17 17:51 | 2020-09-17 22:30 | 279 | 11kV | 30171 | 189 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn3154 St Ives Panel 23 Tripped on Signals: 11kV Trip Abnormal Switcing: CP527 and Bypass Open, CP2082 opened for NAR63806 Cause: Tree branch on OH mains OS27 Catherine St St Ives See OMS 1797252 1797254 1797255 1795980 1795979 1795930 NOTE: PT2397 PT1333 PT1335 were in LV parallel due ton Planned work. All would have experienced supply issues | September | 2020 | 2021Q1 | 2021 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2020-09-17 | N | 159.6349 | N | 6 | N | N | 1.1101 | 39.4971 | 22048.0769
[7 empty] | 2475 | 9742 | 1796000 | 2020-09-18 07:32 | 2020-09-18 13:30 | 358 | 11kV | 73592 | 988 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Light | N | LID 200405 2 fault operations, A & C phase, Overcurrent UGOH fault IU-63080. A ph 11kV down towards pole IU-63023. Note C ph LH LVF 9491 also blown. 11kv "C" phase conductor failed at UGHOH pole IU63080 towards pole IU63023 clashing with "C' phase LV conductor before landing on ground. This incident was caused by a magpie and its nest that was built behind the UGOH pole top bracket Excluded OMS 1796000 | September | 2020 | 2021Q1 | 2021 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | OH | Not Veg | 2020-09-18 | N | 74.4858 | N | 3 | N | N | 1.1101 | 39.4971 | 53778.863
[7 empty] | 2927 | 15404 | 1796085 | 2020-09-18 15:20 | 2020-09-18 16:50 | 90 | 11kV | 3150 | 35 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | At Zn15000 Narrabeen - LB25608 Opened for safety Cause: C phase HDO fell apart at PT16266 | September | 2020 | 2021Q1 | 2021 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2020-09-18 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 2301.9271
[7 empty] | 3273 | 20098 | 1796182 | 2020-09-18 17:30 | 2020-09-18 21:00 | 210 | 11kV | 10080 | 48 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | SW/B Opened @ S4916 Yarrabung Lawson Cause: Interrupted to repair AB2959 After treet has come down | September | 2020 | 2021Q1 | 2021 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2020-09-18 | N | 210 | N | 3 | N | N | 1.1101 | 39.4971 | 7366.1667
[7 empty] | 2194 | 6207 | 1795932 | 2020-09-17 17:51 | 2020-09-18 22:15 | 1704 | 11kV | 289680 | 170 | HV | Overload LV Parallel | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | PT2397 PT1333 PT1335 were in LV parallel due ton Planned work. All would have experienced supply issues Also HV into LV dist 2 PT2397 At Zn3154 St Ives Panel 23 Tripped on Signals: 11kV Trip Abnormal Switcing: CP527 and Bypass Open, CP2082 opened for NAR63806 Cause: Tree branch on OH mains OS27 Catherine St St Ives See OMS 1797252 1797254 1797255 1795980 1795979 1795930 | September | 2020 | 2021Q1 | 2021 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Not Veg | 2020-09-17 | N | 1704 | N | 6 | N | N | 1.1101 | 39.4971 | 211689.5999
[7 empty] | 2191 | 6164 | 1796308 | 2020-09-19 19:35 | 2020-09-19 20:40 | 65 | 11kV | 5395 | 83 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200425 repairs to faulty insulator at pole OS-20762 Excluded oms 1796308 | September | 2020 | 2021Q1 | 2021 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2020-09-19 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 3942.5069
[7 empty] | 1905 | 2847 | 1796313 | 2020-09-19 20:39 | 2020-09-19 21:25 | 46 | 11kV | 1104 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200426 B Phase DOLF : 20 Amp Excluded OMS 1796313 | September | 2020 | 2021Q1 | 2021 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2020-09-19 | N | 46 | N | 5 | N | N | 1.1101 | 39.4971 | 806.7706
[7 empty] | 2277 | 7185 | 1796265 | 2020-09-19 11:42 | 2020-09-19 22:00 | 618 | 11kV | 128157 | 1067 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 200423 3 fault operation A Phase Overcurrent, Earth Fault Suspect faulty UG cable Fishermans Bay MG connected to sub 4968 at 2200hrs Excluded OMS 1796265 | September | 2020 | 2021Q1 | 2021 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | UG | Not Veg | 2020-09-19 | N | 120.1097 | N | 5 | N | N | 1.1101 | 39.4971 | 93653.3556
[7 empty] | 2649 | 11708 | 1796323 | 2020-09-19 23:30 | 2020-09-20 00:34 | 64 | 11kV | 149376 | 2334 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.29 tripped on: B & C phase OC Matelized balloons went across mains causing flashover. Removed by DOp | September | 2020 | 2021Q1 | 2021 | ZN10999:PA29 | ZN10999:PA29 | ZN10999/000029 | BAYSIDE | OH | Veg | 2020-09-19 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 109159.575
[7 empty] | 1784 | 1436 | 1796697 | 2020-09-19 23:40 | 2020-09-20 00:45 | 65 | 11kV | 130 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200427 isolated to repair insulator at pole KR-90025 | September | 2020 | 2021Q1 | 2021 | 233:82818 | 233:82813 | ZN00233/082813 | PORT STEPHENS | OH | Not Veg | 2020-09-19 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 2472 | 9692 | 1796446 | 2020-09-20 20:51 | 2020-09-21 09:57 | 786 | 11kV | 1816 | 6 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35900 Potts Hill Pa7 tripped on A B and C phase OC and EFI Cause: 11kV UG feeder fault from S76809 - S3770 - S3746 See OMS 1797237 1797238 1796446 1796450 | September | 2020 | 2021Q1 | 2021 | ZN35900:PA7 | ZN35900:PA7 | ZN35900/000007 | CUMBERLAND | UG | Not Veg | 2020-09-20 | N | 302.6667 | N | 1 | N | N | 1.1101 | 39.4971 | 1327.0792
[7 empty] | 2997 | 16626 | 1796568 | 2020-09-21 12:31 | 2020-09-21 14:00 | 89 | 11kV | 91429 | 1484 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 200449 2 fault operations B Phase Earth Fault Protection Details Required Faulty UGOH IU80725 Excluded OMS 1796576 1796607 | September | 2020 | 2021Q1 | 2021 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | Unknown | Unknown | 2020-09-21 | N | 61.6098 | N | 6 | N | N | 1.1101 | 39.4971 | 66813.6165
[7 empty] | 2318 | 7742 | 1796560 | 2020-09-21 12:06 | 2020-09-21 14:30 | 144 | 11kV | 288 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 200443 DOLF : 10 Amp Excluded OMS 1796560 | September | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-09-21 | N | 144 | N | 6 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 2924 | 15356 | 1796551 | 2020-09-21 13:30 | 2020-09-21 16:00 | 150 | 11kV | 450 | 3 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200445 Excavator contacted OHM at sub 51047 also see previous event LID 200444, OMS 1796744 Excluded OMS 1796551 | September | 2020 | 2021Q1 | 2021 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2020-09-21 | N | 150 | N | 6 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 2351 | 8228 | 1796648 | 2020-09-21 16:41 | 2020-09-21 19:25 | 164 | 11kV | 222699 | 1431 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kV Recloser CP45061 Chain Valley Bay Mulloway Tripped and locked out on SEL Cause: AB43823 roadsite pgase on load side burnt off See OMS 1797230 1797231 1797232 | September | 2020 | 2021Q1 | 2021 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2020-09-21 | N | 155.6247 | N | 6 | N | N | 1.1101 | 39.4971 | 162741.8607
[7 empty] | 3097 | 18103 | 1796683 | 2020-09-21 22:36 | 2020-09-22 00:30 | 114 | 11kV | 342 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 200453 Single phase DOLF Excluded OMS 1796683 | September | 2020 | 2021Q1 | 2021 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-09-21 | N | 114 | N | 6 | N | N | 1.1101 | 39.4971 | 249.9235
[7 empty] | 2709 | 12395 | 1796666 | 2020-09-21 18:49 | 2020-09-22 00:55 | 366 | 11kV | 303780 | 1503 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 200452 2 fault operations A Phase Overcurrent, Sensitive Earth Fault Feeder fault causing blown HV tapping at ABS 1381 left DMA, & pole JT-70375 repaired. Excluded OMS 1796666 | September | 2020 | 2021Q1 | 2021 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2020-09-21 | N | 202.1158 | N | 6 | N | N | 1.1101 | 39.4971 | 221993.464
[7 empty] | 2204 | 6321 | 1796816 | 2020-09-22 15:28 | 2020-09-22 20:05 | 277 | 11kV | 66536 | 686 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S14144 Panel 10 tripped, reclosed, tripped and locked out on Relays: A phase OC, EFI, lockout Signals: 11kV trip, TX2 GE Tree beanch brought down OH in Birrerick place Wamberal also see LV event 1796839 (Distributor interrupted to allow 11 kV Repairs) See OMS 1797219 1797222 1797223 1797221 1796819 1796837 | September | 2020 | 2021Q1 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-09-22 | N | 96.9913 | N | 1 | N | N | 1.1101 | 39.4971 | 48622.5463
[7 empty] | 2087 | 5065 | 1796864 | 2020-09-23 07:43 | 2020-09-23 09:00 | 77 | 11kV | 42658 | 554 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200467 Phases A and B Pole Mounted RAGCB Overcurrent FDR patrolled no fault found fdr restored. | September | 2020 | 2021Q1 | 2021 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-09-23 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 31173.2082
[7 empty] | 2826 | 14095 | 1796886 | 2020-09-23 09:25 | 2020-09-23 11:46 | 141 | 11kV | 160326 | 1142 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S10998 Rockdale Panel 17 tripped on A protection A and B phase IOC B protection A and B phase IOC lockout reclose time delay Cause not ascertained for outage - Dop patrolled entire feeder no issues identified See OMS 1797199 1797200 1796886 | September | 2020 | 2021Q1 | 2021 | ZN10998:PA17 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Veg | 2020-09-23 | N | 140.3905 | N | 3 | N | N | 1.1101 | 39.4971 | 117161.512
[7 empty] | 2721 | 12604 | 1797012 | 2020-09-23 19:58 | 2020-09-23 22:22 | 144 | 11kV | 191374 | 1329 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S14143 Somersby Panel 12 tripped on Signals: 11kV Trip Relays: A and B phase earth fault, neutral OC, IOC EFI: Panel 12 and 17 UG fault between S14143 Somersby Panel 12 to CP44633 Phillips Gindurra SW/A See OMS 1797188 1797189 1797012 | September | 2020 | 2021Q1 | 2021 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2020-09-23 | N | 143.9985 | N | 3 | N | N | 1.1101 | 39.4971 | 139850.4746
[7 empty] | 2531 | 10393 | 1797026 | 2020-09-24 04:36 | 2020-09-24 05:33 | 57 | 11kV | 42123 | 739 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT S1673 Turramurra Panel 2 Forbes Higgs feeder Relays: A phase IOC with fault check Signals: 11kV trip, TX2 Group Earth and EFI Field EFI's Panel 2 to S4699 (SW/C Open at CP373 to PT1917 (PT in LV parallel) See OMS 1797169 1797026 | September | 2020 | 2021Q1 | 2021 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Not Veg | 2020-09-24 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 30782.246
[7 empty] | 3086 | 17946 | 1797033 | 2020-09-24 07:45 | 2020-09-24 10:30 | 165 | 11kV | 1155 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | At PT61530 Hawksbury Inn Ex Somersby Pnl 17 "Somersby Falls" the center phase HDO blew HDO blew instantly when replaced - Transformer Failure Middle HV fuse blown on PT61530. Fuse hasn't dropped down, blown tail hanging out of base. | September | 2020 | 2021Q1 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-09-24 | N | 165 | N | 5 | N | N | 1.1101 | 39.4971 | 844.0399
[7 empty] | 2719 | 12569 | 1797059 | 2020-09-24 09:10 | 2020-09-24 11:05 | 115 | 11kV | 345 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200491 Single Phase 10 Amp, substation DOLF also see oms 1797059 | September | 2020 | 2021Q1 | 2021 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-09-24 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 2013 | 4089 | 1797090 | 2020-09-24 10:15 | 2020-09-24 11:05 | 50 | 11kV | 6050 | 142 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200492 No protection operations. Burning HV x arm JT-81218. Excluded OMS 1797090. | September | 2020 | 2021Q1 | 2021 | 240:34849 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Not Veg | 2020-09-24 | N | 42.6056 | N | 5 | N | N | 1.1101 | 39.4971 | 4421.1616
[7 empty] | 2310 | 7638 | 1797094 | 2020-09-24 10:39 | 2020-09-24 14:25 | 226 | 11kV | 1130 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT 18533 Wise Ferry Bimbil 16 amp Footpath HDO operated Section of 11 KV feeder Panel No. 21 ex Sub 14143 Somersby Fuse Fatighe Dop required, footpath side HV fuse blown at PT18533. Fuse hasn't dropped, tail hanging from base of fuse. | September | 2020 | 2021Q1 | 2021 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2020-09-24 | N | 226 | N | 5 | N | N | 1.1101 | 39.4971 | 825.7707
[7 empty] | 2497 | 10093 | 1797262 | 2020-09-25 00:32 | 2020-09-25 02:06 | 94 | 11kV | 125906 | 1431 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S340 Paddington Panel 23 Tripped on OC and Earth Fault FN G1 B phase, N, Trip Cause: Suspected UG cable fault in 11kV feeder from S3377SW/B to S6430 SW/A See OMS1798923 1797262 1798294 | September | 2020 | 2021Q1 | 2021 | ZN342:PA23 | ZN342:PA23 | ZN00342/000023 | SYDNEY | OH | Veg | 2020-09-25 | N | 87.9846 | N | 18 | N | N | 1.1101 | 39.4971 | 92008.3912
[7 empty] | 1821 | 1850 | 1798343 | 2020-09-25 12:30 | 2020-09-25 13:20 | 50 | 11kV | 1200 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200508 A & B Phase DOLF : 16 Amp | September | 2020 | 2021Q1 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-09-25 | N | 50 | N | 18 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 2548 | 10608 | 1797335 | 2020-09-25 13:24 | 2020-09-25 15:04 | 100 | 11kV | 7861 | 424 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200517 Earth Fault Mains down at pole MT90026 section isolated for repairs all customers restred at 1504. mdv Excluded OMS 1797335 | September | 2020 | 2021Q1 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-09-25 | N | 18.5401 | N | 18 | N | N | 1.1101 | 39.4971 | 5744.5869
[7 empty] | 3131 | 18528 | 1797449 | 2020-09-25 10:40 | 2020-09-25 15:50 | 310 | 11kV | 30690 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200504 Overcurrent; Earth Fault Excluded OMS 1797449 | September | 2020 | 2021Q1 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-09-25 | N | 310 | N | 18 | N | N | 1.1101 | 39.4971 | 22427.3468
[7 empty] | 1989 | 3734 | 1797402 | 2020-09-25 15:40 | 2020-09-25 17:40 | 120 | 11kV | 193116 | 1738 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S36800 Waverley Panel 33 tripped on Signals: 11kV Trip Cause: UG cable fault between S977 - S48741 - S339 See OMS 1798910 1798911 | September | 2020 | 2021Q1 | 2021 | ZN36800:PA33 | ZN36800:PA33 | ZN36800/000033 | WAVERLEY | UG | Not Veg | 2020-09-25 | N | 111.1139 | N | 18 | N | N | 1.1101 | 39.4971 | 141123.4768
[7 empty] | 2114 | 5290 | 1797474 | 2020-09-25 16:19 | 2020-09-25 17:57 | 98.15 | 11kV | 98.15 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | At PT 16698 Kimbriki Tip No. 2 Section of Panel No. 10 ex Sub15013 Terrey Hills Customers installation fault, Ausgrid equipment ok | September | 2020 | 2021Q1 | 2021 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | Unknown | Not Veg | 2020-09-25 | N | 98.15 | N | 18 | N | N | 1.1101 | 39.4971 | 71.7251
[7 empty] | 2968 | 16236 | 1797494 | 2020-09-25 16:43 | 2020-09-25 18:15 | 92 | 11kV | 44860 | 717 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Recloser CP46116 Lancaster Andrew Tripped, reclosed, tripped and locked out on OC Section of Panel 25 ex S4545 Meadowbank Cause: Insulator on Xarm on OH section of feeder between S4666 Bell Windbourne and S4667 John Windbourne to LB61774 See OMS 1798916 1798918 1798917 | September | 2020 | 2021Q1 | 2021 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Not Veg | 2020-09-25 | N | 62.5662 | N | 18 | N | N | 1.1101 | 39.4971 | 32782.3649
[7 empty] | 2919 | 15283 | 1797351 | 2020-09-25 11:38 | 2020-09-25 18:35 | 417 | 11kV | 16409 | 113 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200521 Earth Fault; Sensitive Eath Fault Trees down at sub 6479 Excluded 1797351 | September | 2020 | 2021Q1 | 2021 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2020-09-25 | N | 145.2124 | N | 18 | N | N | 1.1101 | 39.4971 | 11991.2132
[7 empty] | 2171 | 5868 | 1797566 | 2020-09-25 17:10 | 2020-09-25 18:39 | 89.0333 | 11kV | 29737.1333 | 334 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S2400 Berowra Panel 23 Tripped on B and C phase IOC and reclose lockout Cause: Tree branch on OH between S4402 and S35269 Talbot Preston | September | 2020 | 2021Q1 | 2021 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | OH | Veg | 2020-09-25 | N | 89.0333 | N | 18 | N | N | 1.1101 | 39.4971 | 21731.0199
[7 empty] | 1781 | 1403 | 1797477 | 2020-09-25 16:29 | 2020-09-25 18:50 | 141 | 11kV | 564 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200525 A & B Phase DOLF : 20 Amp Excluded OMS 1797477 | September | 2020 | 2021Q1 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-09-25 | N | 141 | N | 18 | N | N | 1.1101 | 39.4971 | 412.1546
[7 empty] | 2805 | 13891 | 1797711 | 2020-09-25 19:10 | 2020-09-25 20:07 | 57 | 11kV | 6384 | 112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200529 DOLF : 3 Amp Removed tree branch from pole GX-50032 | September | 2020 | 2021Q1 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2020-09-25 | N | 57 | N | 18 | N | N | 1.1101 | 39.4971 | 4665.2389
[7 empty] | 2653 | 11755 | 1797613 | 2020-09-25 18:30 | 2020-09-25 20:45 | 135 | 11kV | 15660 | 116 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200530 Tree on Mains adjacent to pole 8M-60234 Excluded OMS 1797613 | September | 2020 | 2021Q1 | 2021 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2020-09-25 | N | 135 | N | 18 | N | N | 1.1101 | 39.4971 | 11443.8661
[7 empty] | 2085 | 5044 | 1798441 | 2020-09-25 16:00 | 2020-09-25 21:00 | 300 | 11kV | 21160 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200531 2 Fault operations A & C Phase Overcurrent | September | 2020 | 2021Q1 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-09-25 | N | 213.7374 | N | 18 | N | N | 1.1101 | 39.4971 | 15463.1039
[7 empty] | 1838 | 2065 | 1797701 | 2020-09-25 18:50 | 2020-09-25 22:10 | 200 | 11kV | 15232 | 218 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 200528 2 fault operation Single phase Earth Fault | September | 2020 | 2021Q1 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-09-25 | N | 69.8716 | N | 18 | N | N | 1.1101 | 39.4971 | 11131.0963
[7 empty] | 2460 | 9546 | 1797713 | 2020-09-25 19:14 | 2020-09-25 23:59 | 285 | 11kV | 3705 | 13 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200535 A Phase DOLF : 20 Amp Tree on mains near sub 50947. Open curcuit lv neutral at sub 50947. | September | 2020 | 2021Q1 | 2021 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2020-09-25 | N | 285 | N | 18 | N | N | 1.1101 | 39.4971 | 2707.5047
[7 empty] | 2306 | 7587 | 1797706 | 2020-09-25 20:46 | 2020-09-26 00:12 | 206 | 11kV | 13610 | 280 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200532 3 phase NO prot operations. Fdr 74123 OPENED for safety, section Isolated at ABS 74920 then remainder of Feeder supply restored. Excluded oms 1797757 & 1797706 | September | 2020 | 2021Q1 | 2021 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-09-25 | N | 48.6071 | N | 18 | N | N | 1.1101 | 39.4971 | 9945.7866
[7 empty] | 1867 | 2429 | 1797649 | 2020-09-25 17:49 | 2020-09-26 00:50 | 421 | 11kV | 421 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200537 Single phase Broken LLC Dropper lead. repairs complete Excluded oms 1797649 | September | 2020 | 2021Q1 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-09-25 | N | 421 | N | 18 | N | N | 1.1101 | 39.4971 | 307.6544
[7 empty] | 2215 | 6515 | 1797788 | 2020-09-26 01:41 | 2020-09-26 02:47 | 66 | 11kV | 17560 | 276 | HV | Animal Possum | Animal | Bond | Unplanned | No Weather Impact | N | Section of Panel 1 Noraville - Zn 12610 Noraville - Reclose CP47817 Cause: Possum at LB41240 and Burnt bond See OMS 1798320 1798317 1797788 | September | 2020 | 2021Q1 | 2021 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2020-09-26 | N | 63.6232 | N | 10 | N | N | 1.1101 | 39.4971 | 12832.3301
[7 empty] | 2337 | 8095 | 1797712 | 2020-09-26 01:10 | 2020-09-26 03:46 | 156 | 11kV | 148588 | 953 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200538 2 fault operations A & B Phase Overcurrent; Earth fault Removed tree branch span before sub 15109 Morisset country club. Tree in mains. Restring mains between MG9002 and MG90215. Excluded OMS 1797779 | September | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-09-26 | N | 155.9161 | N | 10 | N | N | 1.1101 | 39.4971 | 108583.7278
[7 empty] | 2698 | 12329 | 1797790 | 2020-09-26 02:25 | 2020-09-26 04:03 | 98 | 11kV | 74008 | 776 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12690 - Berkeley Vale - Panel 26 Tripped on Relays: 26R, IOC ABC Signals: 11kV trip with EFI Cause: CP40053 i s closed to Open Bonds on PA24R (Near CP77831) See OMS 1798969 1498971 1797790 | September | 2020 | 2021Q1 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2020-09-26 | N | 95.3711 | N | 10 | N | N | 1.1101 | 39.4971 | 54082.8635
[7 empty] | 1854 | 2266 | 1797821 | 2020-09-26 06:06 | 2020-09-26 08:30 | 143.5833 | 11kV | 15363.4167 | 107 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 200540 B Phase DOLF : 40 Amp B phase 40A DOLF no cause found | September | 2020 | 2021Q1 | 2021 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Veg | 2020-09-26 | N | 143.5833 | N | 10 | N | N | 1.1101 | 39.4971 | 11227.1318
[7 empty] | 1992 | 3747 | 1797797 | 2020-09-26 05:21 | 2020-09-26 09:14 | 233 | 11kV | 932 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200547 sub lead broken Excluded oms 1797797 | September | 2020 | 2021Q1 | 2021 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2020-09-26 | N | 233 | N | 10 | N | N | 1.1101 | 39.4971 | 681.0781
[7 empty] | 1686 | 53 | 1797905 | 2020-09-26 11:20 | 2020-09-26 12:57 | 97 | 11kV | 4947 | 51 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200548 Tree on OHM repaired Pole 8M-60234 required strengthening | September | 2020 | 2021Q1 | 2021 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2020-09-26 | N | 97 | N | 10 | N | N | 1.1101 | 39.4971 | 3615.1217
[7 empty] | 2888 | 14808 | 1797869 | 2020-09-26 09:52 | 2020-09-26 13:55 | 243 | 11kV | 131504 | 953 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200541 2 fault operations Tree cut onto Fdr 80755 at MG37028 Excluded OMS 1797869 | September | 2020 | 2021Q1 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-09-26 | N | 137.9895 | N | 10 | N | N | 1.1101 | 39.4971 | 96099.2445
[7 empty] | 2939 | 15627 | 1797663 | 2020-09-25 18:01 | 2020-09-26 14:55 | 1254 | 11kV | 3762 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200549 Broken Live Line Lead excluded OMS 1797663 | September | 2020 | 2021Q1 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-09-25 | N | 1254 | N | 18 | N | N | 1.1101 | 39.4971 | 2749.1586
[7 empty] | 2884 | 14744 | 1797971 | 2020-09-26 14:45 | 2020-09-26 15:25 | 40 | 11kV | 840 | 21 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200545 Sub 9523 interrupted in section to repair Bphase DOLF dropper at sub 12821 Excluded OMS 1797971 | September | 2020 | 2021Q1 | 2021 | 220:8688 | 220:8688 | ZN00220/008688 | LAKE MACQUARIE | OH | Not Veg | 2020-09-26 | N | 40 | N | 10 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 2945 | 15795 | 1797806 | 2020-09-26 06:31 | 2020-09-26 18:30 | 719.45 | 11kV | 9352.85 | 13 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Wind Strong | N | LID 200550 B Phase DOLF : 20 Amp Stay wire broke & contacted Bph OHM Stay wire made safe, supply restored, Maitland depot advised of repairs needed. | September | 2020 | 2021Q1 | 2021 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2020-09-26 | N | 719.45 | N | 10 | N | N | 1.1101 | 39.4971 | 6834.7869
[7 empty] | 2267 | 7111 | 1798013 | 2020-09-26 18:37 | 2020-09-26 19:11 | 34 | 11kV | 3502 | 103 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Link | Unplanned | No Weather Impact | N | ZN5868 Gore Hill Panel 17 tripped on Relays: SPAJ relay function code 6 Earth Fault, Fault Check and EFI Signals: 11kV Trip Cause: SW/B Open at S7543, SW/A CLosed at S2626 Cause: NBN contractor damaged the 11kV UG cable - UG canle damaged by contractor See OMS 1798051 1798013 | September | 2020 | 2021Q1 | 2021 | ZN5868:PA17 | ZN5868:PA17 | ZN05868/000017 | WILLOUGHBY | UG | Not Veg | 2020-09-26 | N | 34 | N | 10 | N | N | 1.1101 | 39.4971 | 2559.1583
[7 empty] | 2298 | 7513 | 1798037 | 2020-09-27 01:20 | 2020-09-27 07:55 | 395 | 11kV | 51350 | 130 | HV | Animal Flying Fox | Animal | Bond | Unplanned | No Weather Impact | N | Cause: Bat on 11kV after LB48414 - Burnt off 11kV bond Also see OMS At ZN12640 Umina Panel 7 tripped and reclosed on Relays: A and B phase IOC, Timing, Lockout , Trip and alarm Signals: 11kV trip | September | 2020 | 2021Q1 | 2021 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Not Veg | 2020-09-27 | N | 395 | N | 3 | N | N | 1.1101 | 39.4971 | 37525.0654
[7 empty] | 1819 | 1830 | 1798034 | 2020-09-27 00:44 | 2020-09-27 08:06 | 442 | 11kV | 188330 | 427 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP45189 Cooks Peats Ridge Tripped on No Indication Cause not ascertained for outage See OMS 1799013 1799014 1799015 1798034 | September | 2020 | 2021Q1 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-09-27 | N | 441.0539 | N | 3 | N | N | 1.1101 | 39.4971 | 137626.0092
[7 empty] | 3190 | 19319 | 1798051 | 2020-09-27 08:24 | 2020-09-27 09:45 | 81 | 11kV | 20692 | 301 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35400 North Sydney the 110kV panel 83 tripped on Relays: A prot C phase, N phase, EFI Fignals: Trip Cause: UG cable fault - 11kV UG fault between S2899 -S35547 S6307 See OMS 1799007 1799008 1798051 | September | 2020 | 2021Q1 | 2021 | ZN35400:PA83 | ZN35400:PA83 | ZN35400/000083 | NORTH SYDNEY | UG | Not Veg | 2020-09-27 | N | 68.7442 | N | 3 | N | N | 1.1101 | 39.4971 | 15121.1033
[7 empty] | 2324 | 7877 | 1798408 | 2020-09-29 06:04 | 2020-09-29 07:44 | 100 | 11kV | 122320 | 1224 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1290 Leightonfield Panel 11 Tripped on Earth leakage with EFI Cause: Suspect front line cable fault from Pa11 to S7614 to S5013 See OMS 1798998 1798999 1798408 | September | 2020 | 2021Q1 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-09-29 | N | 99.9346 | N | 2 | N | N | 1.1101 | 39.4971 | 89387.8482
[7 empty] | 2487 | 9911 | 1798621 | 2020-09-29 18:48 | 2020-09-29 19:20 | 32 | 11kV | 64 | 2 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 200581 A Phase DOLF : 10 Amp Bird caused A phase dolf to blow. Excluded OMS 1798621 | September | 2020 | 2021Q1 | 2021 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-09-29 | N | 32 | N | 2 | N | N | 1.1101 | 39.4971 | 46.7693
[7 empty] | 2859 | 14430 | 1798653 | 2020-09-30 08:20 | 2020-09-30 08:47 | 27 | 11kV | 1107 | 41 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200583 wire on xarm pole GN-80001, SECTION ISOLATED FOR REPAIR. | September | 2020 | 2021Q1 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-09-30 | N | 27 | N | 2 | N | N | 1.1101 | 39.4971 | 808.9629
[7 empty] | 2335 | 8090 | 1798808 | 2020-09-30 18:48 | 2020-10-01 00:50 | 362 | 11kV | 101290.25 | 280 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | At S2767 Poate St, B phase LV TX braid burnt off. Transformer tail defective | September | 2020 | 2021Q1 | 2021 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2020-09-30 | N | 361.7509 | N | 2 | N | N | 1.1101 | 39.4971 | 74019.9271
[7 empty] | 2524 | 10330 | 1798837 | 2020-10-01 08:06 | 2020-10-01 09:15 | 69 | 11kV | 138 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200595 REPLACED BLOWN B PHASE DOF AT TX 26214. A PHASE 241 VOLTS 105 AMPS, B PHASE 230 VOLTS 66 AMPS, C PHASE 230 VOLTS 67 AMPS. 421 VOLTS BETWEEN PHASES. SUPPLY RESTORED AT 0915. 20 AMP FUSE. CAUSE UNKNOWN. | October | 2020 | 2021Q2 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-10-01 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 2747 | 13134 | 1798946 | 2020-10-01 15:11 | 2020-10-01 17:41 | 150 | 11kV | 56600 | 647 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 Botany - pnl.8 tripped on: Earth Fault UG Cable fault between S2496 Sw/B, S6803 Sw/B, S36156 Sw/A & S63754 Sw/A See 1799594 1799596 | October | 2020 | 2021Q2 | 2021 | ZN340:PA8 | ZN340:PA8 | ZN00340/000008 | BAYSIDE | UG | Not Veg | 2020-10-01 | N | 87.4807 | N | 3 | N | N | 1.1101 | 39.4971 | 41361.6106
[7 empty] | 2763 | 13312 | 1799458 | 2020-10-01 16:30 | 2020-10-01 18:42 | 132 | 11kV | 792 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 200601 TX leaking oil replaced and repaired damaged neutral. No protection operation. Excluded oms 1798887 | October | 2020 | 2021Q2 | 2021 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Not Veg | 2020-10-01 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 578.7702
[7 empty] | 2879 | 14682 | 1799068 | 2020-10-02 09:41 | 2020-10-02 12:30 | 169 | 11kV | 202427 | 1499 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12600 Lisarow - Pnl.9 tripped on: C phase IOC & OC UG cable fault between S14911, S14921 tee PT14333 See 1799613 1799614 1799615 | October | 2020 | 2021Q2 | 2021 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | UG | Not Veg | 2020-10-02 | N | 135.0414 | N | 2 | N | N | 1.1101 | 39.4971 | 147927.681
[7 empty] | 2912 | 15175 | 1799080 | 2020-10-02 10:10 | 2020-10-02 14:15 | 245 | 11kV | 1225 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200609 Low mains at pt 72214 due to broken X arm. still alive on arrival. Excluded OMS 1799033 | October | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-10-02 | N | 245 | N | 2 | N | N | 1.1101 | 39.4971 | 895.1939
[7 empty] | 2586 | 11057 | 1799255 | 2020-10-03 15:58 | 2020-10-03 16:58 | 60 | 11kV | 54896 | 1121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC46118 Dalton Blazland - tripped, reclosed & locked out on IOC & OC Tree on OH mains outside 37 Richmond St. See 1799606 1799607 | October | 2020 | 2021Q2 | 2021 | ZN4545:PA36 | ZN4545:PA36 | ZN04545/000036 | RYDE | OH | Veg | 2020-10-03 | N | 48.9706 | N | 2 | N | N | 1.1101 | 39.4971 | 40116.3776
[7 empty] | 2401 | 8944 | 1799246 | 2020-10-03 13:48 | 2020-10-03 19:10 | 322 | 11kV | 5474 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | PT13153 Pacific Ashbrooke - 2 x HDOs blown Tx failed (50KVA) due to being in LV // with PT61530 (200kVA) See 1799246 1799603 | October | 2020 | 2021Q2 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-10-03 | N | 322 | N | 2 | N | N | 1.1101 | 39.4971 | 4000.2377
[7 empty] | 2033 | 4409 | 1799331 | 2020-10-04 16:42 | 2020-10-04 17:55 | 73 | 11kV | 132249 | 2106 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.4 tripped. Abnormal: LV35376 Open with S9203 Sw/B Closed UG cable fault between S9552 Sw/B and S9283 Sw/A See 1799703 1799704 | October | 2020 | 2021Q2 | 2021 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | UG | Not Veg | 2020-10-04 | N | 62.7963 | N | 1 | N | N | 1.1101 | 39.4971 | 96643.6685
[7 empty] | 2951 | 15910 | 1799348 | 2020-10-05 00:46 | 2020-10-05 01:57 | 71 | 11kV | 3621 | 51 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC705 Knights Chad tripped on: O/C Cause not ascertained. Live possum seen on pole near LB62109 | October | 2020 | 2021Q2 | 2021 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2020-10-05 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 2646.12
[7 empty] | 1931 | 3160 | 1799351 | 2020-10-05 07:05 | 2020-10-05 07:58 | 53 | 11kV | 58035 | 1095 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.13 tripped, reclosed, tripped & locked out on: A & C phase IOC Bird on 11kV OH mains outside 59 Rosa St Oatley | October | 2020 | 2021Q2 | 2021 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2020-10-05 | N | 53 | N | 7 | N | N | 1.1101 | 39.4971 | 42410.2663
[7 empty] | 3183 | 19254 | 1799349 | 2020-10-05 06:13 | 2020-10-05 10:45 | 272 | 11kV | 972 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 200619 tapping broken at 11kv links 51639, section isolated for repairs. Excluded OMS 1799349 | October | 2020 | 2021Q2 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-10-05 | N | 121.5 | N | 7 | N | N | 1.1101 | 39.4971 | 710.3089
[7 empty] | 1755 | 958 | 1799403 | 2020-10-05 15:38 | 2020-10-05 16:25 | 47 | 11kV | 3666 | 78 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200622 Broken pin insulator | October | 2020 | 2021Q2 | 2021 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2020-10-05 | N | 47 | N | 7 | N | N | 1.1101 | 39.4971 | 2679.0047
[7 empty] | 2179 | 6051 | 1799404 | 2020-10-05 15:59 | 2020-10-05 23:10 | 431 | 11kV | 431 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 200625 Tree brought down mains at sub 5469 | October | 2020 | 2021Q2 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-10-05 | N | 431 | N | 7 | N | N | 1.1101 | 39.4971 | 314.9621
[7 empty] | 2188 | 6143 | 1799444 | 2020-10-05 23:39 | 2020-10-06 01:08 | 89 | 11kV | 185654 | 2086 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn10999 Kogarah - Pnl.24 tripped on: B & C phase IOC & Earth Fault Abnormal: AB30253 Open with S10725 Sw/B Closed. S10188 Sw/A Open with Sw/B Closed Possum on 11kV mains near UGOH below S47882 | October | 2020 | 2021Q2 | 2021 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | OH | Not Veg | 2020-10-05 | N | 89 | N | 7 | N | N | 1.1101 | 39.4971 | 135670.4673
[7 empty] | 2265 | 7045 | 1799433 | 2020-10-05 20:05 | 2020-10-06 04:30 | 505 | 11kV | 13447 | 91 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200626 OHM down @ JQ20220 bird strike | October | 2020 | 2021Q2 | 2021 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2020-10-05 | N | 147.7692 | N | 7 | N | N | 1.1101 | 39.4971 | 9826.671
[7 empty] | 2347 | 8187 | 1799591 | 2020-10-06 14:10 | 2020-10-06 15:51 | 100.8833 | 11kV | 1916.7833 | 19 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200630 A & B Phase DOLF : 20 Amp Bird | October | 2020 | 2021Q2 | 2021 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2020-10-06 | N | 100.8833 | N | 3 | N | N | 1.1101 | 39.4971 | 1400.7287
[7 empty] | 3173 | 19122 | 1799679 | 2020-10-06 19:53 | 2020-10-06 20:03 | 9.55 | 11kV | 19.1 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200634 ll CLMAP DROPPER LEAD BURTN OFF Excluded OMS 1799679 | October | 2020 | 2021Q2 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2020-10-06 | N | 9.55 | N | 3 | N | N | 1.1101 | 39.4971 | 13.9577
[7 empty] | 1790 | 1487 | 1799661 | 2020-10-06 16:55 | 2020-10-06 20:15 | 200 | 11kV | 400 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200632 C Phase DOLF : 10 Amp SUSPECT FUSE FATIGUE. OMS 1799661 | October | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-10-06 | N | 200 | N | 3 | N | N | 1.1101 | 39.4971 | 292.3082
[7 empty] | 2427 | 9288 | 1799909 | 2020-10-08 06:16 | 2020-10-08 09:40 | 204 | 11kV | 12648 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT18598 Shelly Beach Kendall - Roadside HDO operated HDO fuse carrier defective, requires new carrier | October | 2020 | 2021Q2 | 2021 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2020-10-08 | N | 204 | N | 6 | N | N | 1.1101 | 39.4971 | 9242.7853
[7 empty] | 2510 | 10218 | 1799954 | 2020-10-08 09:22 | 2020-10-08 10:20 | 58 | 11kV | 58 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200650 Replaced 10 amp Single Phase HV DOLF on Sub 26385 at 10.20 am. No Cause found, not storm conditions | October | 2020 | 2021Q2 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2020-10-08 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 42.3847
[7 empty] | 2689 | 12259 | 1800045 | 2020-10-08 14:54 | 2020-10-08 16:01 | 67 | 11kV | 1608 | 24 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2568 St Peters Panel 6 tripped on Relays: Overcurrent, Earth Fault, EFI Signals: TX4 Group Earth, Zone Earth, 11kV Trip Cause: UG fault from S2568 St Peters Panel 6 to S8168 Elizabeth Richard No1 to S47663 Salisbury Missended SW/A See OMS 1800770 1800045 | October | 2020 | 2021Q2 | 2021 | ZN2568:PA6 | ZN2568:PA6 | ZN02568/000006 | SYDNEY | UG | Not Veg | 2020-10-08 | N | 67 | N | 6 | N | N | 1.1101 | 39.4971 | 1175.079
[7 empty] | 2366 | 8410 | 1800086 | 2020-10-08 17:45 | 2020-10-08 20:43 | 178 | 11kV | 12888 | 218 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 200662 11kV A and B Phase auto open, 3 device operations Overcurrent OHM at pole AK-52836 off pins & tangled | October | 2020 | 2021Q2 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-10-08 | N | 59.1193 | N | 6 | N | N | 1.1101 | 39.4971 | 9418.1703
[7 empty] | 2136 | 5499 | 1800112 | 2020-10-08 21:19 | 2020-10-08 22:55 | 96 | 11kV | 200352 | 2087 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kV Panel 24 High Carlton from Zn10999 Kogarah tripped on Signals: 11kV Trip, Relays: B and C phase IOC and OC Abnormal Switching: Ab30253 Open and Defective with SW B at S10725 Closed S10188 SW/A closed SW/A Open See OMS 1800662 1800112 1800120 | October | 2020 | 2021Q2 | 2021 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | OH | Not Veg | 2020-10-08 | N | 96 | N | 6 | N | N | 1.1101 | 39.4971 | 146411.3322
[7 empty] | 2858 | 14423 | 1800126 | 2020-10-08 23:22 | 2020-10-09 03:29 | 247 | 11kV | 104839 | 427 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12630 Peats Ridge 11kV Recloser CP45189 Cooks Peatds Ridge 0.5 Tripped, reclosed and Tripped Relay: OC Trip Cause: Tree branch contact Tree ttrimming required adjacent to PT49032 Glenowrth Cooks 1.0 See OMS 1800638 1800640 180061 1800126 | October | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-10-08 | N | 245.5246 | N | 6 | N | N | 1.1101 | 39.4971 | 76613.249
[7 empty] | 2869 | 14543 | 1800653 | 2020-10-09 03:30 | 2020-10-09 04:02 | 32 | 11kV | 12073 | 486 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby 11kV Recloser CP44961 Morgan Pacific 0.4 Tripped Relays: OC Tripped Abnormal Switching: CP44077 Closed, Recloser CP44945 Open CP61925 CLosed, CP45004 Open Cause: Feeder restoration after CP45189 Cooks Peats Ridge tripped | October | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-10-09 | N | 24.8416 | N | 4 | N | N | 1.1101 | 39.4971 | 8822.5923
[7 empty] | 2756 | 13226 | 1800131 | 2020-10-09 05:56 | 2020-10-09 07:30 | 94 | 11kV | 282 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200663 A Phase DOLF : 16 Amp Excluded OMS 1800131 | October | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-10-09 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 206.0773
[7 empty] | 2490 | 9920 | 1800189 | 2020-10-09 11:30 | 2020-10-09 13:30 | 120 | 11kV | 360 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | 11kV Feeder Isolated from Recloser CP45189 to AB45004 tee to PT64974 Tee PT49032 tee PT12386 Cause: Urgent Bushfire tree trimming near PT49032 See OMS 1800628 1800189 1800191 1800190 | October | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | Unknown | Unknown | 2020-10-09 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 2383 | 8657 | 1800185 | 2020-10-09 10:55 | 2020-10-09 14:35 | 220 | 11kV | 220 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 200679 A Phase Broken Live Line Clamp Excluded OMS 1800185 | October | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-10-09 | N | 220 | N | 4 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 2238 | 6734 | 1800324 | 2020-10-10 10:40 | 2020-10-10 11:25 | 45 | 11kV | 45 | 1 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 200682 Replaced broken stay wire at sub 72880 excluded OMS 1800324 .jmh | October | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-10-10 | N | 45 | N | 1 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 3184 | 19260 | 1800403 | 2020-10-11 02:46 | 2020-10-11 02:54 | 8 | 11kV | 15076 | 2087 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 200686 ABS 22083 b ph burnt up dumped fdr to open ABS probably related to T&R on LID #200687/OMS 1800484 Excluded oms 1800403 | October | 2020 | 2021Q2 | 2021 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2020-10-11 | N | 7.2238 | N | 4 | N | N | 1.1101 | 39.4971 | 11017.0961
[7 empty] | 1880 | 2558 | 1800417 | 2020-10-11 10:29 | 2020-10-11 12:40 | 131 | 11kV | 393 | 3 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 200690 DOLF : 10 Amp DOLF & LVF found blown. Customers pump faulty Excluded OMS 1800417 | October | 2020 | 2021Q2 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | Unknown | Not Veg | 2020-10-11 | N | 131 | N | 4 | N | N | 1.1101 | 39.4971 | 287.1928
[7 empty] | 2084 | 5030 | 1800445 | 2020-10-11 17:43 | 2020-10-11 22:41 | 298 | 11kV | 16986 | 57 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 200692 Car hit pole 8N-50245. Excluded OMS 1800446 | October | 2020 | 2021Q2 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-10-11 | N | 298 | N | 4 | N | N | 1.1101 | 39.4971 | 12412.8678
[7 empty] | 3070 | 17644 | 1800456 | 2020-10-11 21:59 | 2020-10-12 00:20 | 141 | 11kV | 139716 | 1032 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN10994 Mortdale Panel 19 tripped on Signals : A phase IOC, Eartf ault with EFI Note: Panel 19 Mortdale was de energised to allow SW/A to be closed at S10207 Cause not ascertained for outages See OMS 1800552/553/554/558/559 1800240 1800456 | October | 2020 | 2021Q2 | 2021 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2020-10-11 | N | 135.3837 | N | 4 | N | N | 1.1101 | 39.4971 | 102100.3319
[7 empty] | 2925 | 15362 | 1800472 | 2020-10-12 05:52 | 2020-10-12 11:50 | 358 | 11kV | 146256 | 959 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200700 1 fault operation B Phase Earth Fault Pelican Damaged HV mains and wires on ground. POLE MQ70038 - MQ70037 Excluded OMS 1800472, 1800475 & 1800492 | October | 2020 | 2021Q2 | 2021 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2020-10-12 | N | 152.5089 | N | 5 | N | N | 1.1101 | 39.4971 | 106879.571
[7 empty] | 3241 | 19739 | 1800465 | 2020-10-12 02:25 | 2020-10-12 14:00 | 695 | 11kV | 4170 | 6 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Switching tag at Pillar SU7893. SU7892 customers Yungana Pl interrupted from pillar jointer required in morning to make repairs Neutral bond wiped on. M.Thompson | October | 2020 | 2021Q2 | 2021 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | UG | Not Veg | 2020-10-12 | N | 695 | N | 5 | N | N | 1.1101 | 39.4971 | 3047.313
[7 empty] | 2421 | 9259 | 1800526 | 2020-10-12 09:48 | 2020-10-12 14:00 | 252 | 11kV | 69734 | 870 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9252 Jannali - Pnl.25 opened by AOp after advice from Lineworker 11kV OH mains on the ground. Panel 25 tripped & reclosed at 0430 that morning. Lineworkers patrolled and found OH mains down. Isolated between LB35248, LB35341 & N/O LB35012 tee PT9315 Grand Delta Wires down beyond tee off to N/O LB35012 See 1801235 1801236 | October | 2020 | 2021Q2 | 2021 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Not Veg | 2020-10-12 | N | 80.154 | N | 5 | N | N | 1.1101 | 39.4971 | 50959.5504
[7 empty] | 3178 | 19181 | 1800508 | 2020-10-12 09:14 | 2020-10-12 15:00 | 346 | 11kV | 19731 | 133 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 200704 1 Fault operation Sinlge phase DOLF : 10 Amp Sensitive Earth Fault Faulty PT tx at 73016 T Collett sub. 10 Line dolf also blown at 75013. Excluded OMS 1800508 | October | 2020 | 2021Q2 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2020-10-12 | N | 148.3534 | N | 5 | N | N | 1.1101 | 39.4971 | 14418.8328
[7 empty] | 2162 | 5820 | 1800679 | 2020-10-12 16:34 | 2020-10-12 17:30 | 56 | 11kV | 56 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200708 Single phase DOLF : 10 Amp Excluded OMS 1800679 | October | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-10-12 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 2330 | 7957 | 1800712 | 2020-10-13 00:51 | 2020-10-13 02:55 | 124 | 11kV | 13144 | 106 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200714 C Phase DOLF : 40 Amp Possum | October | 2020 | 2021Q2 | 2021 | 206:34438 | 206:34438 | ZN00206/034438 | LAKE MACQUARIE | OH | Not Veg | 2020-10-13 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 9605.2475
[7 empty] | 3126 | 18434 | 1800716 | 2020-10-13 05:38 | 2020-10-13 06:41 | 63 | 11kV | 30744 | 488 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.13 tripped on: B & C phase IOC & Earth Fault UG cable fault between S48388 Sw/B and S1210 Sw/A | October | 2020 | 2021Q2 | 2021 | ZN35800:PA13 | ZN35800:PA13 | ZN35800/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-10-13 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 22466.8084
[7 empty] | 1771 | 1293 | 1800899 | 2020-10-13 16:54 | 2020-10-13 19:10 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200726 Single phase DOLF : 20 Amp Excluded OMS 1800899 | October | 2020 | 2021Q2 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-10-13 | N | 136 | N | 5 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 3091 | 18020 | 1800888 | 2020-10-13 16:20 | 2020-10-13 20:00 | 220 | 11kV | 17503 | 141 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.17 tripped on: IOC & Earth Fault UG cable fault between S14827 Sw/B to S14003 Sw/A tee PT14130 See 1801245 1801246 1801247 | October | 2020 | 2021Q2 | 2021 | ZN12690:PA17 | ZN12690:PA17 | ZN12690/000017 | CENTRAL COAST | UG | Not Veg | 2020-10-13 | N | 124.1348 | N | 5 | N | N | 1.1101 | 39.4971 | 12790.6761
[7 empty] | 1773 | 1351 | 1800931 | 2020-10-13 19:49 | 2020-10-13 21:25 | 96 | 11kV | 80352 | 837 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford - LB61991 Bond HR on 1 phase | October | 2020 | 2021Q2 | 2021 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2020-10-13 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 58718.8716
[7 empty] | 2467 | 9626 | 1800998 | 2020-10-14 09:26 | 2020-10-14 10:29 | 63 | 11kV | 98784 | 1568 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn1285 Greenacre park - Pnl.24L tripped, reclosed & locked out on: O/C & Earth Fault Large party baloon removed from 11kV mains adj PT1811 by DOp | October | 2020 | 2021Q2 | 2021 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-10-14 | N | 63 | N | 3 | N | N | 1.1101 | 39.4971 | 72188.4336
[7 empty] | 2089 | 5080 | 1800987 | 2020-10-14 09:10 | 2020-10-14 10:39 | 89 | 11kV | 95222 | 1448 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200729 1 fault operation Single phase Earth Fault excluded OMS 1800987 | October | 2020 | 2021Q2 | 2021 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2020-10-14 | N | 65.761 | N | 3 | N | N | 1.1101 | 39.4971 | 69585.429
[7 empty] | 2985 | 16403 | 1801124 | 2020-10-14 21:48 | 2020-10-14 23:15 | 87 | 11kV | 21690 | 276 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 200737 Faulty UGOH AH-20558 Excluded OMS 1801124 | October | 2020 | 2021Q2 | 2021 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | Unknown | Unknown | 2020-10-14 | N | 78.587 | N | 3 | N | N | 1.1101 | 39.4971 | 15850.4123
[7 empty] | 2209 | 6381 | 1801243 | 2020-10-15 12:30 | 2020-10-15 16:10 | 220 | 11kV | 46946 | 218 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200748 section isolated to replace HV crossarm Excluded OMS 1801209 | October | 2020 | 2021Q2 | 2021 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | OH | Not Veg | 2020-10-15 | N | 215.3486 | N | 1 | N | N | 1.1101 | 39.4971 | 34306.7521
[7 empty] | 2803 | 13884 | 1801344 | 2020-10-16 08:42 | 2020-10-16 09:52 | 70 | 11kV | 34840 | 788 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 200755 B & C Phase Earth Fault, Overcurrent Trip and reclose 0842. Burning uo ABS 19646. Targets. OC, EF 51BC Excluded 1801344 | October | 2020 | 2021Q2 | 2021 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2020-10-16 | N | 44.2132 | N | 1 | N | N | 1.1101 | 39.4971 | 25460.0444
[7 empty] | 2786 | 13723 | 1801502 | 2020-10-17 03:52 | 2020-10-17 04:52 | 60 | 11kV | 9840 | 164 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC41873 Woolana Woodlawn tripped & reclosed REC47817 Buff Point Elouera tripped and locked out shortly after Abnormal: LB64574 Open with LB63990 Closed, LB41240 Open, LB42404 Closed & LB63990 Closed Cause not ascertained See 1802390 1802389 | October | 2020 | 2021Q2 | 2021 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Veg | 2020-10-17 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 7190.7818
[7 empty] | 2656 | 11817 | 1801550 | 2020-10-17 11:15 | 2020-10-17 13:52 | 157 | 11kV | 7571 | 56 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200766 2 fault operations A & B Phase Overcurrent Magpie contacted mains at pole 9L-50408. Excluded OMS 1801550 & 1801569 | October | 2020 | 2021Q2 | 2021 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2020-10-17 | N | 135.1964 | N | 3 | N | N | 1.1101 | 39.4971 | 5532.6635
[7 empty] | 2451 | 9513 | 1801576 | 2020-10-17 13:11 | 2020-10-17 21:40 | 509 | 11kV | 16674 | 102 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200767 3 fault operations 3 phase Overcurrent, Earth Fault Tree brought mains down between poles KR-40065 & KR-40066. Excluded OMS 1801562 | October | 2020 | 2021Q2 | 2021 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2020-10-17 | N | 163.4706 | N | 3 | N | N | 1.1101 | 39.4971 | 12184.8674
[7 empty] | 2340 | 8123 | 1801634 | 2020-10-18 05:25 | 2020-10-18 07:08 | 102.8833 | 11kV | 55042.5833 | 535 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15008 Harbord - Pnl.4 tripped, reclosed & locked out on: A & B phase IOC Abnormal: Pnl.4 Harbord closed with AB25219 Open & Defective Possum found at 33 Gordon St | October | 2020 | 2021Q2 | 2021 | ZN36300:PA13 | ZN15008:PA4 | ZN15008/000004 | NORTHERN BEACHES | OH | Not Veg | 2020-10-18 | N | 102.8833 | N | 3 | N | N | 1.1101 | 39.4971 | 40223.4964
[7 empty] | 1768 | 1204 | 1801677 | 2020-10-18 17:02 | 2020-10-18 23:21 | 378.65 | 11kV | 111128.95 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | One phase of 11kV Feeder brought down between poles SP94 and SP95 Cause: Tree/Branch brought down one 11kV phase See 1801677 1801686 1801691 1801697 1801699 1801700 | October | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-10-18 | N | 341.9352 | N | 3 | N | N | 1.1101 | 39.4971 | 81209.7589
[7 empty] | 2410 | 9175 | 1801704 | 2020-10-18 22:00 | 2020-10-19 02:30 | 270 | 11kV | 49950 | 185 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Pnl.3 Lisarow - 11kV isolated from S18521 Sw/B to AB40317 for repairs to HV & LV mains after car hit pole outside 684 Pacific Hwy See 1801710 1801712 | October | 2020 | 2021Q2 | 2021 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2020-10-18 | N | 270 | N | 3 | N | N | 1.1101 | 39.4971 | 36501.9867
[7 empty] | 1961 | 3402 | 1801717 | 2020-10-19 04:04 | 2020-10-19 05:12 | 68 | 11kV | 75530 | 2317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.17 tripped on: Earth Fault UG cable fault between S20 Sw/D, S5883 Sw/A & S77856 Sw/B See 1802392 1802393 | October | 2020 | 2021Q2 | 2021 | ZN188:PA17 | ZN188:PA17 | ZN00188/000017 | SYDNEY | UG | Not Veg | 2020-10-19 | N | 32.5982 | N | 5 | N | N | 1.1101 | 39.4971 | 55195.0962
[7 empty] | 1736 | 747 | 1801722 | 2020-10-19 04:55 | 2020-10-19 07:50 | 175 | 11kV | 1435 | 9 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200772 DOLF : 20 Amp Excluded OMS 1801722 | October | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Not Veg | 2020-10-19 | N | 159.4444 | N | 5 | N | N | 1.1101 | 39.4971 | 1048.6557
[7 empty] | 2111 | 5284 | 1801802 | 2020-10-19 10:24 | 2020-10-19 11:57 | 93 | 11kV | 21018 | 226 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200773 Sensitive Earth Fault Tipper truck came into contact with 11kV adj sub 46386. No damage found to OHM or nearby poles. Truck details from OMS registration BB56QX, Woodberry Civil. Reported by GRANT, DARREN - Truck has hit wires on property in which it caused arcing and now cust without power. No wires down. Truck details Woodberry Civil Rego no BB56QX. No isolation/quarantine advised. | October | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2020-10-19 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 15359.3345
[7 empty] | 2872 | 14611 | 1801764 | 2020-10-19 09:19 | 2020-10-19 13:26 | 247 | 11kV | 247 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 200774 A & B phase :10 Amp Blown L/A. Replaced by Ken Garland Excluded OMS 1801764 | October | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-10-19 | N | 247 | N | 5 | N | N | 1.1101 | 39.4971 | 180.5003
[7 empty] | 2412 | 9177 | 1801887 | 2020-10-19 15:17 | 2020-10-19 16:10 | 53 | 11kV | 133242 | 2514 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn1285 Greenacre park - Pnl.31 tripped on: A phase O/C Abnormal: AB207 Open & Defective Metal balloon floated into 11kV mains outside 151 Acacia Ave, Greenacre | October | 2020 | 2021Q2 | 2021 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-10-19 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 97369.3236
[7 empty] | 2521 | 10318 | 1802073 | 2020-10-20 14:03 | 2020-10-20 18:00 | 237 | 11kV | 12747 | 160 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP45071 Central Mangrove Open and Locked out on IOC Section of Panel 3 Tree branch brought down OH @ 211 Blood Tree Rd 1802369 1802367 1802099 1802073 | October | 2020 | 2021Q2 | 2021 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2020-10-20 | N | 79.6688 | N | 1 | N | N | 1.1101 | 39.4971 | 9315.1316
[7 empty] | 1997 | 3795 | 1802270 | 2020-10-21 15:06 | 2020-10-21 16:21 | 75 | 11kV | 10050 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | iR49506 Spring Road - tripped & reclosed on OC Cause not ascertained | October | 2020 | 2021Q2 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2020-10-21 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 7344.2436
[7 empty] | 1945 | 3260 | 1802318 | 2020-10-21 19:07 | 2020-10-21 21:15 | 128 | 11kV | 128 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200810 Single phase Polly dropper broken off TX tank end. Excluded OMS 1802318. | October | 2020 | 2021Q2 | 2021 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2020-10-21 | N | 128 | N | 2 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 2557 | 10673 | 1802478 | 2020-10-22 17:05 | 2020-10-22 18:10 | 65 | 11kV | 3380 | 52 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | LID 200821 Road roller backed into pole GS-62053. X-arm needed replacement Excluded oms 1802478 | October | 2020 | 2021Q2 | 2021 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2020-10-22 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 2470.0043
[7 empty] | 2599 | 11204 | 1802453 | 2020-10-22 18:05 | 2020-10-22 18:40 | 35 | 11kV | 5460 | 156 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200822 Isolated 11kV OHM to repair frayed conductor between poles GW-10158 & GW-10157 Excluded OMS 1802453 | October | 2020 | 2021Q2 | 2021 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2020-10-22 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 3990.007
[7 empty] | 3243 | 19745 | 1802487 | 2020-10-22 18:15 | 2020-10-22 19:10 | 55 | 11kV | 5300 | 102 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | Ex Pnl.13L Umina - 11kV intuerrupted between AB45427 to AB42590 to CP4774 to replace broken stand off insulator at AB45428 (N/O) See 1802490 1802487 | October | 2020 | 2021Q2 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2020-10-22 | N | 51.9608 | N | 5 | N | N | 1.1101 | 39.4971 | 3873.0837
[7 empty] | 2666 | 11907 | 1802429 | 2020-10-22 14:15 | 2020-10-22 19:30 | 315 | 11kV | 2205 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Lisarow Pnl.2 - 11kV interrupted from AB44323 to CO44605 to remove tree from 11kV mains Large tree across covered 11kV, LV distributors and hanging across rd (one lane closed). | October | 2020 | 2021Q2 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-10-22 | N | 315 | N | 5 | N | N | 1.1101 | 39.4971 | 1611.349
[7 empty] | 2724 | 12663 | 1802615 | 2020-10-23 15:14 | 2020-10-23 18:20 | 186 | 11kV | 2790 | 15 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | PT46693 The Ridgeway Timber - Centre phase bond burnt off dropper to HDO | October | 2020 | 2021Q2 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2020-10-23 | N | 186 | N | 2 | N | N | 1.1101 | 39.4971 | 2038.8497
[7 empty] | 1741 | 780 | 1802685 | 2020-10-23 23:20 | 2020-10-24 01:10 | 110 | 11kV | 92451 | 1021 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn10994 Mortdale - Pnl.1 tripped, reclosed & locked out on: A & B phase IOC Cause not ascertained See 1803360 1803361 1803362 | October | 2020 | 2021Q2 | 2021 | ZN10994:PA1 | ZN10994:PA1 | ZN10994/000001 | GEORGES RIVER | OH | Veg | 2020-10-23 | N | 90.5495 | N | 2 | N | N | 1.1101 | 39.4971 | 67560.464
[7 empty] | 2745 | 13107 | 1802689 | 2020-10-24 02:15 | 2020-10-24 03:35 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 200835 Single phase DOLF : 10 Amp Both DOLFs & 100A LVF found blown Excluded OMS 1802689. | October | 2020 | 2021Q2 | 2021 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2020-10-24 | N | 80 | N | 10 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 3088 | 17964 | 1802703 | 2020-10-24 06:24 | 2020-10-24 07:48 | 84 | 11kV | 7308 | 87 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 200839 B Phase DOLF : 40 Amp Sub 5540 B phase 40a DOLF supply off 0624hrs on 0748hrs | October | 2020 | 2021Q2 | 2021 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Veg | 2020-10-24 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 5340.4709
[7 empty] | 2019 | 4139 | 1802486 | 2020-10-22 19:02 | 2020-10-24 12:30 | 2488 | 11kV | 2488 | 1 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S8710 Hume Shellcote No.4 - RMCB (Merlin Gerrin) failed. RMCB replaced Friday and restored Saturday | October | 2020 | 2021Q2 | 2021 | ZN35900:PA14 | ZN35900:PA14 | ZN35900/000014 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2020-10-22 | N | 2488 | N | 5 | N | N | 1.1101 | 39.4971 | 1818.157
[7 empty] | 1848 | 2246 | 1802791 | 2020-10-24 13:46 | 2020-10-24 16:06 | 140 | 11kV | 10030 | 87 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | CP44582 Erina - tripped, reclosed & locked out on OC Stick found across OH beyond Link43162 See 1803185 1803186 | October | 2020 | 2021Q2 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2020-10-24 | N | 115.2874 | N | 10 | N | N | 1.1101 | 39.4971 | 7329.6282
[7 empty] | 2379 | 8641 | 1802813 | 2020-10-24 16:50 | 2020-10-24 17:35 | 45 | 11kV | 180 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 200845 A & B Phase DOLF : 31 Amp replaced A & B phase line fuses 61537. Excluded oms 1802813 | October | 2020 | 2021Q2 | 2021 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2020-10-24 | N | 45 | N | 10 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 2094 | 5151 | 1802762 | 2020-10-24 10:49 | 2020-10-24 18:40 | 471 | 11kV | 29431 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP44995 Kulnura Opened, Reclosed, Opened and locked out on IOC Section of Panel 8 Kulnura ex S12630 Peats Ridge Cause: OH resting on cross arm 11kV mains stranded and off pin insulator near PT13646 See OMS 1803337 1803338 1803340 1802762 | October | 2020 | 2021Q2 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-10-24 | N | 291.396 | N | 10 | N | N | 1.1101 | 39.4971 | 21507.3067
[7 empty] | 2313 | 7658 | 1802823 | 2020-10-24 18:57 | 2020-10-24 20:46 | 109 | 11kV | 47473 | 502 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 200847 A & B Phase Tarpaulin & branches on OHM adj sub 51678 Excluded OMS 1802823 ## | October | 2020 | 2021Q2 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2020-10-24 | N | 94.5677 | N | 10 | N | N | 1.1101 | 39.4971 | 34691.8682
[7 empty] | 2165 | 5834 | 1802848 | 2020-10-24 20:46 | 2020-10-24 22:12 | 86 | 11kV | 84256 | 1378 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Rain Heavy | N | LID 200846 2 Fault Operations 3 phase Earth Fault UGOH IS-51565 Damaged by Lightning Excluded OMS 1802848 | October | 2020 | 2021Q2 | 2021 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2020-10-24 | N | 61.1437 | N | 10 | N | N | 1.1101 | 39.4971 | 61571.7997
[7 empty] | 2572 | 10880 | 1802854 | 2020-10-24 21:50 | 2020-10-24 22:50 | 59.7167 | 11kV | 3403.85 | 57 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | PT12528 Highes Kingston - Roadside and Centre phase HDOs blew Possum | October | 2020 | 2021Q2 | 2021 | ZN14891:PA1 | ZN14891:PA1 | ZN14891/000001 | CENTRAL COAST | OH | Not Veg | 2020-10-24 | N | 59.7167 | N | 10 | N | N | 1.1101 | 39.4971 | 2487.4332
[7 empty] | 2361 | 8360 | 1802837 | 2020-10-24 23:50 | 2020-10-25 00:48 | 58 | 11kV | 580 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 200850 A Phase Blown tapping pole FP-40168 replaced under AP. Excluded 1802837. | October | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-10-24 | N | 58 | N | 10 | N | N | 1.1101 | 39.4971 | 423.8469
[7 empty] | 2344 | 8170 | 1802869 | 2020-10-25 01:10 | 2020-10-25 12:35 | 685 | 11kV | 5480 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT12822 The Scenic Doyle - Interrupted to restore fallen LV mains. PT interrupted at 8:42 - First no supply call at 1:10 and EMSO report of a HV fuse blown | October | 2020 | 2021Q2 | 2021 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2020-10-25 | N | 685 | N | 7 | N | N | 1.1101 | 39.4971 | 4004.6224
[7 empty] | 2339 | 8107 | 1804352 | 2020-10-25 12:51 | 2020-10-25 13:05 | 14 | 11kV | 658 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Recloswer CP42086 Opened, reclosed, opened and reclosed on CO and EF Cause: Section of no 2 ex S12600 Lisarow | October | 2020 | 2021Q2 | 2021 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2020-10-25 | N | 14 | N | 7 | N | N | 1.1101 | 39.4971 | 480.847
[7 empty] | 2628 | 11399 | 1802888 | 2020-10-25 10:11 | 2020-10-25 13:10 | 179.0167 | 11kV | 1432.1333 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Lisarow Pnl.2 - 11kV interrupted between AB45186 to AB44336 tee PT644778 Patterson Wattle tree to cut away tree from 11kV mains. | October | 2020 | 2021Q2 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-10-25 | N | 179.0167 | N | 7 | N | N | 1.1101 | 39.4971 | 1046.5608
[7 empty] | 3083 | 17846 | 1802753 | 2020-10-24 10:25 | 2020-10-25 16:10 | 1785 | 11kV | 220630 | 2027 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.19 tripped on: Earth Fault UG cable fault between S10148 Sw/A, S10884 Sw/A and S10645 (non // sub) See 1803156 1803158 1803159 | October | 2020 | 2021Q2 | 2021 | ZN10999:PA19 | ZN10999:PA19 | ZN10999/000019 | BAYSIDE | UG | Not Veg | 2020-10-24 | N | 108.8456 | N | 10 | N | N | 1.1101 | 39.4971 | 161229.8965
[7 empty] | 2585 | 11052 | 1802956 | 2020-10-25 15:22 | 2020-10-25 19:05 | 222.6833 | 11kV | 10466.1167 | 47 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of Panel 13 feeder ZN12600 Lisarow Recloser CP42086 North Lisarow Isolated by DOp Cause: Tree branch on OH 22Bangalow Cres | October | 2020 | 2021Q2 | 2021 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2020-10-25 | N | 222.6833 | N | 7 | N | N | 1.1101 | 39.4971 | 7648.3294
[7 empty] | 2520 | 10305 | 1802995 | 2020-10-25 20:36 | 2020-10-25 21:27 | 51 | 11kV | 67320 | 1320 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Ex Blakehurst Pnl.1 - Roadside phase 11kV bond burnt off AB31134 | October | 2020 | 2021Q2 | 2021 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2020-10-25 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 49195.4704
[7 empty] | 2652 | 11735 | 1803018 | 2020-10-26 00:06 | 2020-10-26 00:18 | 12 | 11kV | 29688 | 2474 | HV | Arcing | Equipment Failure | Bond | Unplanned | Wind Strong | N | At Zn10991 Blakehurst Panel 13 tripped and locked out on Relays: SEL and EFI Signals: 11kV trip Abnormal Switching: LB31023 Closed and AB31134 Open and Defective Cause: DOp patrolled See OMS 1803363 1803018 | October | 2020 | 2021Q2 | 2021 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2020-10-26 | N | 12 | N | 14 | N | N | 1.1101 | 39.4971 | 21695.1148
[7 empty] | 2746 | 13131 | 1803356 | 2020-10-25 22:22 | 2020-10-26 00:20 | 118 | 11kV | 21712 | 184 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | AT Zn10991 Blakehurst panel 1 tripped and locked out on RelaysL SEL and EFI Cause: DOp Patrolled feeder aat defective AB31134. Bond was arcing across the middle of phase of the AB Abnormal Switching: LB31023 Closed and AB31134 Open and defective See OMS 1803356 1803019 | October | 2020 | 2021Q2 | 2021 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2020-10-25 | N | 118 | N | 7 | N | N | 1.1101 | 39.4971 | 15866.4892
[7 empty] | 2420 | 9252 | 1803017 | 2020-10-25 22:06 | 2020-10-26 00:44 | 158 | 11kV | 284172 | 1842 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S15014 Mona Vale Panel 10 Tripped and locked out on Relays: A Protn: IOC B and C phase B Protn: IOC and EFI B and C phase Cause: Suspect UG cable fault from CP21620 Lentara Nangana SW/B to S16467 Lentara Kara SW/A See OMS 1803433 1803435 1803017 | October | 2020 | 2021Q2 | 2021 | ZN15014:PA10 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2020-10-25 | N | 154.2736 | N | 7 | N | N | 1.1101 | 39.4971 | 207664.5159
[7 empty] | 2009 | 4008 | 1803038 | 2020-10-26 00:50 | 2020-10-26 02:00 | 70 | 11kV | 7176 | 114 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser 41020 Wattle Tree Rd North Trippeed and Locked out on Relays: Overcurrent Section fo Panel 2 Holgate Feeder at S12600 Lisarow Cause: Tree has come down and Broke 11kV ties on section of OH. From AB44336 to LV45186 tee PT64478 See OMS 1803445 1803448 1803451 1803038 | October | 2020 | 2021Q2 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2020-10-26 | N | 62.9474 | N | 14 | N | N | 1.1101 | 39.4971 | 5244.0091
[7 empty] | 2959 | 16035 | 1803029 | 2020-10-26 00:06 | 2020-10-26 02:50 | 164.2167 | 11kV | 6897.1 | 42 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 200855 B & C Phase DOLF : 20 Amp Branch on mains adjacent to sub pole. Excluded OMS 1803037 CC1: 22-"Refer to SOp" | October | 2020 | 2021Q2 | 2021 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-10-26 | N | 164.2167 | N | 14 | N | N | 1.1101 | 39.4971 | 5040.1972
[7 empty] | 2184 | 6087 | 1803054 | 2020-10-26 04:49 | 2020-10-26 06:51 | 122 | 11kV | 9760 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S353470 Galston Panel 2 Recloser CP3280 Hunt Ave Tripped and Locked out on Relays: OC trip Cause: A tree branch was found on the 11kV mains near LB1548 | October | 2020 | 2021Q2 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-10-26 | N | 122 | N | 14 | N | N | 1.1101 | 39.4971 | 7132.3201
[7 empty] | 1899 | 2801 | 1803079 | 2020-10-26 06:45 | 2020-10-26 07:42 | 57 | 11kV | 48336 | 848 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca - Pnl.34 tripped on: OC Tree on 11kV OH mains | October | 2020 | 2021Q2 | 2021 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2020-10-26 | N | 57 | N | 14 | N | N | 1.1101 | 39.4971 | 35322.5231
[7 empty] | 2761 | 13289 | 1803049 | 2020-10-26 03:43 | 2020-10-26 07:52 | 249 | 11kV | 150324 | 1608 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca - Pnl.22 tripped on: SEL 11kV OH mains on the ground between USL45430 and PT18027 See 1804356 1804357 | October | 2020 | 2021Q2 | 2021 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2020-10-26 | N | 93.4851 | N | 14 | N | N | 1.1101 | 39.4971 | 109852.3454
[7 empty] | 3005 | 16723 | 1803050 | 2020-10-26 05:58 | 2020-10-26 09:20 | 202 | 11kV | 186006 | 1092 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn1673 Turramurra tripped, reclosed & locked out on: B & C phase OC Dop found OH mains twisted together See 1804361 1804362 | October | 2020 | 2021Q2 | 2021 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Not Veg | 2020-10-26 | N | 170.3352 | N | 14 | N | N | 1.1101 | 39.4971 | 135927.6986
[7 empty] | 2783 | 13691 | 1803153 | 2020-10-26 08:16 | 2020-10-26 09:53 | 97 | 11kV | 55872 | 576 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S15005 Belrose - 11kV feeder 8R LB24368 has a bond burnt off Abnormal: CP25623 Closed, CP244445 Open and defective See OMS 1804375 1803153 | October | 2020 | 2021Q2 | 2021 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2020-10-26 | N | 97 | N | 14 | N | N | 1.1101 | 39.4971 | 40829.6097
[7 empty] | 2116 | 5305 | 1803275 | 2020-10-26 09:45 | 2020-10-26 10:59 | 74 | 11kV | 43364 | 586 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 200858 2 fault operations Tree on mains - self clearing | October | 2020 | 2021Q2 | 2021 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2020-10-26 | N | 74 | N | 14 | N | N | 1.1101 | 39.4971 | 31689.1322
[7 empty] | 1793 | 1516 | 1803225 | 2020-10-26 09:29 | 2020-10-26 11:45 | 135.7 | 11kV | 29854 | 220 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Recloser CP62705 Jilliby Durren Open and Locked out Cause not ascertained for outage CC1: 22-"Refer to SOp" | October | 2020 | 2021Q2 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2020-10-26 | N | 135.7 | N | 14 | N | N | 1.1101 | 39.4971 | 21816.4227
[7 empty] | 2448 | 9480 | 1803129 | 2020-10-26 11:35 | 2020-10-26 12:40 | 65 | 11kV | 390 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 200860 HV arrestor at DP-70112 buring up and tracking. feeder did not trip Excluded oms 1803367, 1803129 | October | 2020 | 2021Q2 | 2021 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2020-10-26 | N | 65 | N | 14 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 2633 | 11474 | 1803478 | 2020-10-26 12:58 | 2020-10-26 15:50 | 172 | 11kV | 113458 | 1028 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | 11kV Panel 43 CP @ Zn965 Pennant Hills Tripped on Signals: 11kV Trip, TX2 Group Earth, Zone Earth Relays: EFI SEF Cause: Surge arrestor blown @ UGOH ex S4492 See OMS 1804406 1804407 1804408 1804408 1804409 1803478 | October | 2020 | 2021Q2 | 2021 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2020-10-26 | N | 110.3677 | N | 14 | N | N | 1.1101 | 39.4971 | 82911.76
[7 empty] | 2381 | 8650 | 1803530 | 2020-10-26 14:57 | 2020-10-26 17:42 | 165 | 11kV | 3300 | 20 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 200862 2 fault operations Tree across 11kV mains at pole KR-30020. Excluded OMS 1803536 | October | 2020 | 2021Q2 | 2021 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2020-10-26 | N | 165 | N | 14 | N | N | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 2295 | 7432 | 1803685 | 2020-10-27 00:04 | 2020-10-27 00:45 | 41 | 11kV | 2173 | 53 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200867 B Phase DOLF : 10 Amp Excluded OMS 1803685 | October | 2020 | 2021Q2 | 2021 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2020-10-27 | N | 41 | N | 4 | N | N | 1.1101 | 39.4971 | 1587.9643
[7 empty] | 2271 | 7139 | 1803696 | 2020-10-27 05:58 | 2020-10-27 08:30 | 152 | 11kV | 149653 | 2605 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn690 Campsie - Pnl.33 tripped on: Earth Fault UG cable fault between S4328 Sw/B, S1880 Sw/A tee S6420 Note; S2297, S4328 , S1880 & S3438 EFIs failed to flag resulting in Pnl.18 tripping on restoration attempt. Canturbury Hospital supplied by Pnl.18. See 1804394 1804395 1804400 1804396 1804399 | October | 2020 | 2021Q2 | 2021 | ZN690:PA33 | ZN690:PA33 | ZN00690/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-10-27 | N | 57.4484 | N | 4 | N | N | 1.1101 | 39.4971 | 109361.9984
[7 empty] | 2946 | 15804 | 1803602 | 2020-10-26 17:26 | 2020-10-27 08:40 | 914 | 11kV | 1828 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 200868 A Phase DOLF : 16 Amp Excluded OMS 1803602 | October | 2020 | 2021Q2 | 2021 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2020-10-26 | N | 914 | N | 14 | N | N | 1.1101 | 39.4971 | 1335.8485
[7 empty] | 1743 | 817 | 1803919 | 2020-10-27 16:58 | 2020-10-27 18:30 | 92 | 11kV | 120568 | 1364 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.36 tripped on: Earth Fault UG cable fault between S5921, REC46118 tee S1163 See 1804390 1804391 | October | 2020 | 2021Q2 | 2021 | ZN4545:PA36 | ZN4545:PA36 | ZN04545/000036 | RYDE | UG | Not Veg | 2020-10-27 | N | 88.393 | N | 4 | N | N | 1.1101 | 39.4971 | 88107.5382
[7 empty] | 2128 | 5439 | 1803885 | 2020-10-27 15:01 | 2020-10-27 20:40 | 339 | 11kV | 74669 | 609 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 200878 2 fault operation Overcurrent broken 33kv x-arm pole HR-80463, Section isolated for repairs. see report 200877 Excluded OMS 1803885 | October | 2020 | 2021Q2 | 2021 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2020-10-27 | N | 122.6092 | N | 4 | N | N | 1.1101 | 39.4971 | 54565.9028
[7 empty] | 3265 | 20016 | 1803984 | 2020-10-28 03:24 | 2020-10-28 07:55 | 271 | 11kV | 542 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 200883 A & B Phase DOLF : 10 Amp Excluded OMS 1803984 | October | 2020 | 2021Q2 | 2021 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2020-10-28 | N | 271 | N | 4 | N | N | 1.1101 | 39.4971 | 396.0776
[7 empty] | 2046 | 4601 | 1804117 | 2020-10-28 14:27 | 2020-10-28 15:45 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 200887 C Phase DOLF : 20 Amp Excluded OMS 1804117 | October | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-10-28 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 1687 | 110 | 1804154 | 2020-10-28 16:31 | 2020-10-28 17:40 | 69 | 11kV | 138 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200889 A Phase DOLF : 10 Amp Bird dead beneath transformer. Excluded OMS 1804154 | October | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-10-28 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 2881 | 14698 | 1804177 | 2020-10-28 19:34 | 2020-10-28 20:45 | 71 | 11kV | 1136 | 16 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 200891 A & C Phase DOLF : 20 Amp Lightning strike LF 74388 replaced ##OMS1804177,78,79 Please patrol in daylight | October | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-10-28 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 830.1553
[7 empty] | 2365 | 8394 | 1804196 | 2020-10-29 04:30 | 2020-10-29 07:15 | 165 | 11kV | 113565 | 1176 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn129 Hunters Hill - pnl.52 tripped on: C phase O/C UG cable fault in frontline section of feeder between Pnl.52, S6209, S62084 tee S5267 See 1804338 1804339 | October | 2020 | 2021Q2 | 2021 | ZN129:PA52 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2020-10-29 | N | 96.5689 | N | 6 | N | N | 1.1101 | 39.4971 | 82989.9524
[7 empty] | 3130 | 18459 | 1804286 | 2020-10-29 11:21 | 2020-10-29 12:40 | 79 | 11kV | 316 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | @ S 14143 Somersby ex Panel 6 " S 18379 Pinnacle Trinnium" PT 18018 Quarry Girrakool HV drop out operated Roadside phase 16amp Lightning / Surge Arrestor - defective HV arrestors cutaway by Dop | October | 2020 | 2021Q2 | 2021 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2020-10-29 | N | 79 | N | 6 | N | N | 1.1101 | 39.4971 | 230.9235
[7 empty] | 2976 | 16322 | 1804397 | 2020-10-29 16:37 | 2020-10-29 18:15 | 98 | 11kV | 2156 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 200907 B & C Phase DOLF : 63 Amp Blown LF 6905 Feeder patrolled no fault found. excluded OMS1804397 | October | 2020 | 2021Q2 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2020-10-29 | N | 98 | N | 6 | N | N | 1.1101 | 39.4971 | 1575.5412
[7 empty] | 2637 | 11534 | 1804437 | 2020-10-29 21:03 | 2020-10-29 21:50 | 47 | 11kV | 40439 | 1017 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.7 tripped on: A phase IOC Abnormal: S78202 Sw/B Closed with LB44013 Open. LB44708 closed with AB43308 Open 11kV UGOH between S65075 and REC45055 failed explosively. See 1804515 1804516 | October | 2020 | 2021Q2 | 2021 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | Unknown | Unknown | 2020-10-29 | N | 39.763 | N | 6 | N | N | 1.1101 | 39.4971 | 29551.6285
[7 empty] | 2503 | 10131 | 1804422 | 2020-10-29 17:58 | 2020-10-29 23:00 | 302 | 11kV | 604 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 200911 Single phase DOLF : 10 Amp Tx Volts: 242V Tx load: 12A Excluded OMS No. 1804422 | October | 2020 | 2021Q2 | 2021 | 507:80914 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2020-10-29 | N | 302 | N | 6 | N | N | 1.1101 | 39.4971 | 441.3854
[7 empty] | 2515 | 10258 | 1804445 | 2020-10-29 23:15 | 2020-10-30 01:50 | 155 | 11kV | 554519 | 4713 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.12 tripped on: Pnl.12R Earth Fault Zn15006 Dee Why West - Pnl.13 tripped on: O/C & Earth Fault (at the same time as Pnl.12) Abnormal: Pnl.12: S16549 Sw/A Closed with S17009 Sw/A Open (Load relief switching from Pnl.8 due to DMA) Abnormal: Pnl.13: S16618 Sw/A Closed with LK24947 Open (DMA) UG cable fault in common line sections of both feeders. Pnl.12 between S.16803 Sw/B, S15783 Sw/A & S15149 Sw/A Pnl.13 between Pnl.13 & S79533 Sw/A See 1804487 1804488 1804492 | October | 2020 | 2021Q2 | 2021 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | UG | Not Veg | 2020-10-29 | N | 117.6573 | N | 6 | N | N | 1.1101 | 39.4971 | 405226.1297
[7 empty] | 2134 | 5476 | 1804708 | 2020-10-31 11:45 | 2020-10-31 16:05 | 260 | 11kV | 16986 | 215 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200922 1 fault operation Tree on mains between poles FS-61762 and FS-61763. Excluded OMS 1804708 | October | 2020 | 2021Q2 | 2021 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2020-10-31 | N | 79.0047 | N | 1 | N | N | 1.1101 | 39.4971 | 12412.8678
[7 empty] | 2940 | 15631 | 1804830 | 2020-11-01 08:19 | 2020-11-01 11:22 | 183 | 11kV | 366 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 200927 A Phase Live Line Clamp broken, sub isolated for repairs Excluded OMS 1804830 | November | 2020 | 2021Q2 | 2021 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2020-11-01 | N | 183 | N | 7 | N | N | 1.1101 | 39.4971 | 267.462
[7 empty] | 2069 | 4858 | 1804881 | 2020-11-01 14:36 | 2020-11-01 16:35 | 119 | 11kV | 714 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 200931 B Phase DOLF : 16 Amp Excluded OMS 1804881 | November | 2020 | 2021Q2 | 2021 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2020-11-01 | N | 119 | N | 7 | N | N | 1.1101 | 39.4971 | 521.7701
[7 empty] | 2180 | 6052 | 1804957 | 2020-11-01 20:16 | 2020-11-01 21:36 | 80 | 11kV | 141360 | 1767 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 200933 damaged 11kV UGOH pole OR-67112. Excluded OMS No. 1804957 | November | 2020 | 2021Q2 | 2021 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | Unknown | Unknown | 2020-11-01 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 103301.7186
[7 empty] | 3027 | 17037 | 1804973 | 2020-11-01 22:20 | 2020-11-01 23:47 | 87 | 11kV | 76580 | 1130 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | LID 200936 3 fault operations A & B Phases Overcurrent Damaged Bph 11kV UGOH & Blown arrestor at pole MW-40625. Excluded OMS No. 1804973 | November | 2020 | 2021Q2 | 2021 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | Unknown | Unknown | 2020-11-01 | N | 67.7699 | N | 7 | N | N | 1.1101 | 39.4971 | 55962.4053
[7 empty] | 1692 | 204 | 1804949 | 2020-11-01 19:50 | 2020-11-02 00:25 | 275 | 11kV | 1535 | 15 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Light | N | LID 200935 Required clearance for earthing to repair broken LLC lead at sub 47248. Excluded OMS No. 1804949 | November | 2020 | 2021Q2 | 2021 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2020-11-01 | N | 102.3333 | N | 7 | N | N | 1.1101 | 39.4971 | 1121.7327
[7 empty] | 2433 | 9326 | 1804972 | 2020-11-01 22:16 | 2020-11-02 09:45 | 689 | 11kV | 2067 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200937 Repaired burnt off Live Line Lead from DOLF Excluded OMS 1804972 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-11-01 | N | 689 | N | 7 | N | N | 1.1101 | 39.4971 | 1510.5026
[7 empty] | 2612 | 11250 | 1804995 | 2020-11-02 07:12 | 2020-11-02 10:40 | 208 | 11kV | 42662 | 694 | HV | Staff Other | Utility Process Issue | Circuit Breaker | Unplanned | No Weather Impact | N | Recloser Cp64071 Wattle First tripped during switching Cause: During switching or NAR64043 Dop has made recloser CP64071 manual using telescopic operating stick (followingh advice5/2103) This was due to the recloser being out of scan. It is believed that the SEF has in advertainly been left auto. Operator tripped on SEF See OMS 1805798 1805858 180580 1805803 1804995 Abniormal switching SW/A open @ S9151 for NAR64043 | November | 2020 | 2021Q2 | 2021 | ZN9252:PA28 | ZN9252:PA28 | ZN09252/000028 | SUTHERLAND | Unknown | Not Veg | 2020-11-02 | N | 61.4726 | N | 3 | N | N | 1.1101 | 39.4971 | 31176.1313
[7 empty] | 3133 | 18543 | 1804978 | 2020-11-01 23:30 | 2020-11-02 12:30 | 780 | 11kV | 49140 | 63 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Section of 11kV from S18033 to AB42968 to AB44425 interrupted to allow LW to replace broken cross arm and safely tension OH See OMS1805955 1804980 1805954 1805979 | November | 2020 | 2021Q2 | 2021 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Not Veg | 2020-11-01 | N | 780 | N | 7 | N | N | 1.1101 | 39.4971 | 35910.0626
[7 empty] | 2388 | 8732 | 1805008 | 2020-11-02 07:55 | 2020-11-02 16:40 | 525 | 11kV | 87110 | 1087 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Recloser CP41115 Lakedge Audie Tripped Abnormal Switching: Recloser 43262 Closed, CP42072 Open Cause: Car hit pole O/S 37 Kwerry Cres Berkeley Vale See OMS 1805037 1805971 1805970 1805083 1805009 1805008 1805969 | November | 2020 | 2021Q2 | 2021 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2020-11-02 | N | 80.138 | N | 3 | N | N | 1.1101 | 39.4971 | 63657.4187
[7 empty] | 1886 | 2657 | 1805159 | 2020-11-02 17:22 | 2020-11-02 19:00 | 98 | 11kV | 1470 | 15 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 200943 Faulty Insulator at pole JS-12430 Excluded OMS 1805159 | November | 2020 | 2021Q2 | 2021 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2020-11-02 | N | 98 | N | 3 | N | N | 1.1101 | 39.4971 | 1074.2326
[7 empty] | 2269 | 7123 | 1805232 | 2020-11-03 00:13 | 2020-11-03 02:19 | 126 | 11kV | 203364 | 1614 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200945 1 fault operation Sensitive Earth Fault Suspect dead kookaburra found adj. pole OR-30116. | November | 2020 | 2021Q2 | 2021 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2020-11-03 | N | 126 | N | 6 | N | N | 1.1101 | 39.4971 | 148612.413
[7 empty] | 2992 | 16568 | 1805422 | 2020-11-03 18:10 | 2020-11-03 19:40 | 90 | 11kV | 165871 | 2176 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35800 Bankstwon Panel 4 -Feeder has tripped Siganls: 11kV Trip Relays: Earth Fault Check, Earth Fault Cause: ZN35800 Bankstwon Panel 14 Cable fault from SW/B at S66038 ti LV 315 to S5895. Delwood Marshall. See OMS 1805904 1805906 1805907 1805422 | November | 2020 | 2021Q2 | 2021 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-03 | N | 76.2275 | N | 6 | N | N | 1.1101 | 39.4971 | 121213.6344
[7 empty] | 2378 | 8631 | 1805346 | 2020-11-03 13:40 | 2020-11-03 20:00 | 380 | 11kV | 86716 | 700 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 200954 1 fault operation Earth Fault Broken x-arm pole KR-60492. HV into LV. Excluded OMS 1805346 | November | 2020 | 2021Q2 | 2021 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2020-11-03 | N | 123.88 | N | 6 | N | N | 1.1101 | 39.4971 | 63369.4951
[7 empty] | 2196 | 6251 | 1805415 | 2020-11-03 19:03 | 2020-11-03 21:12 | 129 | 11kV | 2193 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12650 West Gosford Recloser CP45010 Palmgrove was opened to allow emergency repairs to 11kV CCT between pole OU2373 and Pole OU2374 Cause: OH down | November | 2020 | 2021Q2 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2020-11-03 | N | 129 | N | 6 | N | N | 1.1101 | 39.4971 | 1602.5797
[7 empty] | 2874 | 14642 | 1805447 | 2020-11-03 21:59 | 2020-11-03 23:20 | 81 | 11kV | 162 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 200955 Single Phase DOLF : 10 Amp Possum Excluded OMS 1805447 | November | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-11-03 | N | 81 | N | 6 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 1812 | 1712 | 1805451 | 2020-11-04 04:04 | 2020-11-04 05:30 | 86 | 11kV | 172 | 2 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200956 B & C Phase DOLF : 10 Amp Swans Excluded OMS 1805451 | November | 2020 | 2021Q2 | 2021 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2020-11-04 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 2273 | 7152 | 1805594 | 2020-11-04 14:51 | 2020-11-04 20:45 | 354 | 11kV | 175561 | 1228 | HV | Animal Possum | Animal | Cross arm | Unplanned | No Weather Impact | N | LID 200964 Possum led to crossarm failure pole JT-81923. Excluded OMS 1805594 | November | 2020 | 2021Q2 | 2021 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Not Veg | 2020-11-04 | N | 142.965 | N | 3 | N | N | 1.1101 | 39.4971 | 128294.8006
[7 empty] | 3201 | 19394 | 1805305 | 2020-11-03 11:43 | 2020-11-04 20:48 | 1985 | 11kV | 121385 | 169 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At CP25760 Woobak Narilla amp HV fuse operated on tee off to S15682 Currawong Park Section of Panel 28 ex S15010 Careel Bay Cause: UG fault from S15682 Crrawong Park SW/C to S47300 Coasters Retreat See OMS 1805690 1805692 1805691 1805465 1805305 1805377 | November | 2020 | 2021Q2 | 2021 | ZN15010:PA28 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | UG | Not Veg | 2020-11-03 | N | 718.2544 | N | 6 | N | N | 1.1101 | 39.4971 | 88704.5777
[7 empty] | 3206 | 19451 | 1805664 | 2020-11-04 23:45 | 2020-11-05 00:53 | 68 | 11kV | 23364 | 428 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park tripped on Relays: (Panel 10 Left, Earth Fault, EFI, Fault Check) Signals: 11kV trip, TZ1 Group Earth Cause: 11kV UG fault from S64450 to S7979 to S7889 See OMS 1805974 1805975 1805664 | November | 2020 | 2021Q2 | 2021 | ZN8000:PA10 | ZN8000:PA10 | ZN08000/000010 | RYDE | UG | Not Veg | 2020-11-04 | N | 54.5888 | N | 3 | N | N | 1.1101 | 39.4971 | 17073.7221
[7 empty] | 2977 | 16323 | 1805671 | 2020-11-05 04:10 | 2020-11-05 08:43 | 273 | 11kV | 1911 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200968 A & B Phase DOLF : 10 Amp excluded OMS 1805671 | November | 2020 | 2021Q2 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-11-05 | N | 273 | N | 5 | N | N | 1.1101 | 39.4971 | 1396.5024
[7 empty] | 1725 | 583 | 1805711 | 2020-11-05 09:00 | 2020-11-05 10:39 | 99 | 11kV | 19701 | 199 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV Reclosr CP45013 Gunderman Tripped on O/C Cause: Tree branch removed of 11kV OH adjaent to AB43179 | November | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-11-05 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 14396.9097
[7 empty] | 2549 | 10621 | 1805853 | 2020-11-05 15:08 | 2020-11-05 16:44 | 96.2333 | 11kV | 2502.0667 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 200975 A phase, 10 Amp Line DOLF No further information supplied CC1: 22-"Refer to SOp" | November | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-11-05 | N | 96.2333 | N | 5 | N | N | 1.1101 | 39.4971 | 1828.4365
[7 empty] | 3074 | 17709 | 1805786 | 2020-11-05 11:32 | 2020-11-05 17:50 | 378 | 11kV | 171099 | 1225 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kV Panel 1 Engadine tripped, relocsed and locked out on Signals: 11kV Trip Relays: Recloser Lockout, OC and EF -51N = EF and EFI Cause: 11kV and LV down outside 23 Lantana Rd Engadine See OMS 1805959 1805960 1805961 1805962 1805828 1805778 | November | 2020 | 2021Q2 | 2021 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2020-11-05 | N | 139.6727 | N | 5 | N | N | 1.1101 | 39.4971 | 125034.1026
[7 empty] | 2744 | 13065 | 1805908 | 2020-11-05 17:15 | 2020-11-05 18:40 | 85 | 11kV | 255 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 200978 Single Phase 10Amp Substation DOLF No cause found, not storm conditions | November | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-11-05 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 1856 | 2293 | 1806047 | 2020-11-06 11:23 | 2020-11-06 14:00 | 157 | 11kV | 314 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 200988 A Phase Substation DOLF cause attributed to storm the night before. PD | November | 2020 | 2021Q2 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-11-06 | N | 157 | N | 1 | N | N | 1.1101 | 39.4971 | 229.4619
[7 empty] | 3163 | 18975 | 1806247 | 2020-11-07 12:12 | 2020-11-07 13:25 | 73 | 11kV | 75899 | 1670 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn2196 Milperra - Pnl.5 tripped on: C phase IOC Tree on OH mains adj PT1527. PT1527 restored via LV // See 1807146 1807148 1807149 | November | 2020 | 2021Q2 | 2021 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2020-11-07 | N | 45.4485 | N | 8 | N | N | 1.1101 | 39.4971 | 55464.7506
[7 empty] | 3212 | 19513 | 1806240 | 2020-11-07 15:50 | 2020-11-07 17:10 | 80 | 11kV | 320 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200993 SECTION ISOLATED TO REPAIR STRANDED 11KV MAINS NEAR POLE HV-93600. Found a damaged copper main on centre phase mid span between UGOH pole HV9 3600 and H construction poles ( HV9 3599 - 3598 ).Two strands have unwound about a meter. S01 notified over phone. Please have crew attend for repairs. | November | 2020 | 2021Q2 | 2021 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2020-11-07 | N | 80 | N | 8 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 2758 | 13263 | 1806299 | 2020-11-07 16:29 | 2020-11-07 17:35 | 66 | 11kV | 15499 | 364 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn10994 Mortdale - Pnl.8 opened by AOp Manoukian for safety due to 11kV pole on fire and baloons on the 11kV OH mains. See previous trip and reclose. | November | 2020 | 2021Q2 | 2021 | ZN10994:PA8 | ZN10994:PA8 | ZN10994/000008 | GEORGES RIVER | OH | Veg | 2020-11-07 | N | 42.5797 | N | 8 | N | N | 1.1101 | 39.4971 | 11326.2121
[7 empty] | 2041 | 4564 | 1806301 | 2020-11-07 17:06 | 2020-11-07 18:15 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 200994 10 Amp substation DOLF, single phase fuse replaced power restored 18.15. mdv | November | 2020 | 2021Q2 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2020-11-07 | N | 69 | N | 8 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 2994 | 16587 | 1806323 | 2020-11-07 18:40 | 2020-11-07 19:42 | 62 | 11kV | 11470 | 185 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 200995 Tree branch has fallen on DW going through propertty 100m from highway and has brought wires down to ground andthere is arcing and sparkign causing small grass fire, have advised to call fire department. Clear access, no pets, no iso | November | 2020 | 2021Q2 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-11-07 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 8381.9377
[7 empty] | 2052 | 4737 | 1806359 | 2020-11-07 20:16 | 2020-11-07 20:36 | 20 | 11kV | 80 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 200997 A phase 63Amp, substation DOLF No Cause found, not storm conditions | November | 2020 | 2021Q2 | 2021 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Veg | 2020-11-07 | N | 20 | N | 8 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 2978 | 16325 | 1806321 | 2020-11-07 18:04 | 2020-11-07 20:50 | 166 | 11kV | 166 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Light | N | LID 200996 broken off live line lead sub isolated for repars. Hayden Collier assigned sub 52932 isolated to repair broken live line lead. power restored 2050 | November | 2020 | 2021Q2 | 2021 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2020-11-07 | N | 166 | N | 8 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 1936 | 3200 | 1806371 | 2020-11-07 22:33 | 2020-11-08 00:54 | 141 | 11kV | 259008 | 2267 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S10999 Kogarah Panel 11 has tripped Signals: 11kV Trip Relays: NIL Cause Not ascertained, reason for trip unknown | November | 2020 | 2021Q2 | 2021 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Veg | 2020-11-07 | N | 114.2514 | N | 8 | N | N | 1.1101 | 39.4971 | 189275.407
[7 empty] | 3287 | 20389 | 1806445 | 2020-11-09 02:41 | 2020-11-09 04:24 | 103 | 11kV | 106196 | 1106 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12610 Long Jetty 11 kV panel 18 has tripped on Relays: A phase IOC, Earth fault, Fault Check and EFI Signals: 11kV trip Cause: UG cable fault from S11788 Waratah Marlowe to S12134 Waratah Rickard See OMS 1806828 1806445 1806444 | November | 2020 | 2021Q2 | 2021 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | UG | Not Veg | 2020-11-09 | N | 96.0181 | N | 1 | N | N | 1.1101 | 39.4971 | 77604.9045
[7 empty] | 2576 | 10903 | 1806674 | 2020-11-10 05:56 | 2020-11-10 07:43 | 107 | 11kV | 133114 | 1400 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn10997 Sans Souci - Pnl.12 tripped on IOC Cause not ascertained See 1807177 1807178 | November | 2020 | 2021Q2 | 2021 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Veg | 2020-11-10 | N | 95.0814 | N | 2 | N | N | 1.1101 | 39.4971 | 97275.785
[7 empty] | 1881 | 2566 | 1806713 | 2020-11-10 16:30 | 2020-11-10 17:10 | 40 | 11kV | 160 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 201018 broken earth wire from arrestor | November | 2020 | 2021Q2 | 2021 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2020-11-10 | N | 40 | N | 2 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 2584 | 11011 | 1806951 | 2020-11-11 09:38 | 2020-11-11 12:08 | 150 | 11kV | 217908 | 1520 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.10 tripped on: A Phase IOC Field EFIs 1st trip: S9795 & S65052 2nd trip: S9795 UG cable fault between S9795, S65052 and S9657 Suspect EFI @ S65052 was not reset See 1807169 1807170 | November | 2020 | 2021Q2 | 2021 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | UG | Not Veg | 2020-11-11 | N | 143.3605 | N | 2 | N | N | 1.1101 | 39.4971 | 159240.7392
[7 empty] | 3047 | 17261 | 1807096 | 2020-11-11 21:24 | 2020-11-12 00:18 | 174 | 11kV | 112254 | 1229 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1290 Leightonfield - Pnl.11 tripped on C phase IOC Abnormal: S8601 Sw/B closed with S8600 Sw/A Open UG cable fault between S3399 Sw/B and S79491 Sw/A Helium balloon found on LB 145 - section of feeder had to be isolated to remove balloon so LB 145 could be closed to restore supply. See 1807159 1807160 | November | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-11 | N | 91.3377 | N | 2 | N | N | 1.1101 | 39.4971 | 82031.9123
[7 empty] | 1809 | 1681 | 1807300 | 2020-11-13 01:13 | 2020-11-13 03:35 | 142 | 11kV | 2840 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201052 DOLF : 20 Amp Excluded OMS 1807300 | November | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-11-13 | N | 142 | N | 12 | N | N | 1.1101 | 39.4971 | 2075.3882
[7 empty] | 2304 | 7566 | 1807305 | 2020-11-13 02:41 | 2020-11-13 04:37 | 116 | 11kV | 84457 | 737 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1290 Leightonfield 11kV panel 8 tripped on Realys: E/F and EFI Front Line feeder fault See OMS 1807936 1807305 | November | 2020 | 2021Q2 | 2021 | ZN1290:PA8 | ZN1290:PA8 | ZN01290/000008 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-13 | N | 114.5957 | N | 12 | N | N | 1.1101 | 39.4971 | 61718.6845
[7 empty] | 3236 | 19687 | 1807320 | 2020-11-13 07:12 | 2020-11-13 08:20 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201053 A & B Phase DOLF : 10 Amp Excluded OMS 1807320 | November | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-11-13 | N | 68 | N | 12 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 2942 | 15670 | 1807337 | 2020-11-13 08:21 | 2020-11-13 08:35 | 14 | 11kV | 14 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201054 A Phase DOLF : 10 Amp Excluded OMS 1807337 | November | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-11-13 | N | 14 | N | 12 | N | N | 1.1101 | 39.4971 | 10.2308
[7 empty] | 2684 | 12187 | 1807345 | 2020-11-13 09:05 | 2020-11-13 12:20 | 195 | 11kV | 195 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201060 B Phase DOLF : 10 Amp Excluded OMS 1807345 | November | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2020-11-13 | N | 195 | N | 12 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 1770 | 1265 | 1807414 | 2020-11-13 13:10 | 2020-11-13 14:05 | 55 | 11kV | 935 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201062 Conductor strands required repairs | November | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2020-11-13 | N | 55 | N | 12 | N | N | 1.1101 | 39.4971 | 683.2704
[7 empty] | 1951 | 3361 | 1807516 | 2020-11-13 18:48 | 2020-11-13 21:10 | 142 | 11kV | 284 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201080 DOLF : 10 Amp Excluded OMS 1807516 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-11-13 | N | 142 | N | 12 | N | N | 1.1101 | 39.4971 | 207.5388
[7 empty] | 1796 | 1541 | 1807501 | 2020-11-13 16:17 | 2020-11-13 21:55 | 338 | 11kV | 12530 | 73 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT S12570 Avoca - Panel 33 tripped on A phase Cause: OH down adjacent to USL41825 See OMS 1707883 1707884 1807457 | November | 2020 | 2021Q2 | 2021 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2020-11-13 | N | 171.6438 | N | 12 | N | N | 1.1101 | 39.4971 | 9156.5544
[7 empty] | 2617 | 11284 | 1807531 | 2020-11-13 20:58 | 2020-11-13 22:35 | 97 | 11kV | 582 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201081 DOLF : 20 Amp Excluded OMS 1807531 | November | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-11-13 | N | 97 | N | 12 | N | N | 1.1101 | 39.4971 | 425.3084
[7 empty] | 2015 | 4106 | 1807535 | 2020-11-13 23:02 | 2020-11-14 00:19 | 77 | 11kV | 138584 | 1832 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7481 Darling Harbour 14L Tripped on OC and Earth Cause: Suspect UG cable fault - 1kV feeder from S7946 SW/B to S8061 SW/A Cause: UG cable Fault 1807846 1807847 1807535 | November | 2020 | 2021Q2 | 2021 | ZN3672:PA13 | ZN3672:PA13 | ZN03672/000013 | RANDWICK | UG | Not Veg | 2020-11-13 | N | 75.6463 | N | 12 | N | N | 1.1101 | 39.4971 | 101273.0997
[7 empty] | 1689 | 190 | 1807515 | 2020-11-13 18:45 | 2020-11-14 01:08 | 383 | 11kV | 9919 | 92 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 201084 Broken 11kV tapping to sub 63513 Excluded OMS 1807515 | November | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-11-13 | N | 107.8152 | N | 12 | N | N | 1.1101 | 39.4971 | 7248.5126
[7 empty] | 1808 | 1667 | 1807556 | 2020-11-14 08:47 | 2020-11-14 10:09 | 82 | 11kV | 90736 | 1168 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 40tripped on Relays: A protection: earth fault, IOC, B phase B protection: IOC EFI Cause: 11kV UG feeder fault from S5262 to S49184 see OMS 1809399 1809402 1807556 | November | 2020 | 2021Q2 | 2021 | ZN129:PA40 | ZN129:PA40 | ZN00129/000040 | RYDE | UG | Not Veg | 2020-11-14 | N | 77.6849 | N | 1 | N | N | 1.1101 | 39.4971 | 66307.1925
[7 empty] | 2658 | 11842 | 1807397 | 2020-11-13 12:09 | 2020-11-14 12:30 | 1461 | 11kV | 13791 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12650 West Gosford Recloser CP44602 Orimbah Creek has tripped Relays:L EF Trip, OC trip and Lockout Cause: Tree branch brought down near PT12952 See OMS 1809391 1809393 1807397 1807420 | November | 2020 | 2021Q2 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-11-13 | N | 130.1038 | N | 12 | N | N | 1.1101 | 39.4971 | 10078.056
[7 empty] | 2157 | 5784 | 1807651 | 2020-11-15 02:18 | 2020-11-15 03:45 | 87 | 11kV | 15312 | 176 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kV Bond burnt off to PT10857 Beaconsfield Queen also caused At 15/11/20 02:18 Zn10999 Kogarah Panel 12 tripped and reclosed on Relays: A and B phase IOC Abnormal Switching: LB30004 Closed and AB31045 Open DMA Refer to OMS 1807827 | November | 2020 | 2021Q2 | 2021 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Not Veg | 2020-11-15 | N | 87 | N | 5 | N | N | 1.1101 | 39.4971 | 11189.558
[7 empty] | 3114 | 18361 | 1807657 | 2020-11-15 06:49 | 2020-11-15 08:10 | 81 | 11kV | 162 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201091 DOLF : 10 Amp Excluded OMS 1807657 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-11-15 | N | 81 | N | 5 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 3249 | 19789 | 1807669 | 2020-11-15 10:10 | 2020-11-15 10:30 | 20 | 11kV | 100 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 201097 B phase DOLF carrier faulty, 16A DOLF fuse and carrier replaced Excluded OMS 1807669 | November | 2020 | 2021Q2 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2020-11-15 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 3106 | 18265 | 1807665 | 2020-11-15 08:59 | 2020-11-15 11:30 | 151 | 11kV | 302 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201099 Single phase DOLF : 10 Amp Excluded OMS 1807665 | November | 2020 | 2021Q2 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2020-11-15 | N | 151 | N | 5 | N | N | 1.1101 | 39.4971 | 220.6927
[7 empty] | 3237 | 19704 | 1807711 | 2020-11-15 16:06 | 2020-11-15 17:17 | 71 | 11kV | 94764 | 1394 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7481 Darling Harbour Panel 14L triped on OC and Earth Fault Cause: Suspect UG cable fault in 11kjV feeder from S7946 to S8061 See OMS 1809380 1809382 1807711 | November | 2020 | 2021Q2 | 2021 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2020-11-15 | N | 67.9799 | N | 5 | N | N | 1.1101 | 39.4971 | 69250.7361
[7 empty] | 1993 | 3754 | 1807858 | 2020-11-16 11:24 | 2020-11-16 12:51 | 87 | 11kV | 52374 | 602 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | LID 201110 Overcurrent, Sensitive Earth Fault no fault found. Chad said this happened on monday 2nd nov.? No clause found then either. | November | 2020 | 2021Q2 | 2021 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2020-11-16 | N | 87 | N | 10 | N | N | 1.1101 | 39.4971 | 38273.3744
[7 empty] | 2949 | 15841 | 1807950 | 2020-11-16 15:00 | 2020-11-16 16:25 | 85 | 11kV | 6800 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | REC3280 Hunt Ave - tripped on OC Tree on 11kV OH mains near LB1548 | November | 2020 | 2021Q2 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-11-16 | N | 85 | N | 10 | N | N | 1.1101 | 39.4971 | 4969.2394
[7 empty] | 2571 | 10871 | 1808006 | 2020-11-16 16:34 | 2020-11-16 17:35 | 61 | 11kV | 19620 | 348 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | Y | Zn14892 Charmhaven - Pnl.9 tripped, reclosed & locked out on: Earth Fault End box fault at S14678 (Sw/A) See 1809414 1809416 | November | 2020 | 2021Q2 | 2021 | ZN14892:PA9 | ZN14892:PA9 | ZN14892/000009 | CENTRAL COAST | UG | Not Veg | 2020-11-16 | N | 56.3793 | N | 10 | N | N | 1.1101 | 39.4971 | 14337.7173
[7 empty] | 2516 | 10261 | 1807976 | 2020-11-16 15:39 | 2020-11-16 18:09 | 150 | 11kV | 168750 | 1125 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn874 Concord - Pnl.17 tripped on: A Phase O/C Suspected UG cable fault in frontline section of feeder. Supply restored via Pnl.22 - AOp interrupted Pnl.22 @1824 due to extreme high load and performed load relief switching. See 1809383 1809385 | November | 2020 | 2021Q2 | 2021 | ZN874:PA17 | ZN874:PA17 | ZN00874/000017 | CANADA BAY | UG | Not Veg | 2020-11-16 | Y | 150 | N | 10 | N | Y | 1.1101 | 39.4971 | 123317.5227
[7 empty] | 2627 | 11398 | 1808020 | 2020-11-16 16:54 | 2020-11-16 18:36 | 102 | 11kV | 41106 | 403 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At ZN.35400 North Sydney Pnl 64 CB tripped. A prot B phase & N fault; B prot B phase & Earth fault. Cause: UG cable fault between Zn.35400 North Sydney,S.3336 Miller Mount,S.3915 Miller Northpoint & CP77880 Victoria Cross Station. | November | 2020 | 2021Q2 | 2021 | ZN35400:PA64 | ZN35400:PA64 | ZN35400/000064 | NORTH SYDNEY | UG | Not Veg | 2020-11-16 | N | 102 | N | 10 | N | N | 1.1101 | 39.4971 | 30039.0524
[7 empty] | 2634 | 11485 | 1808061 | 2020-11-16 18:24 | 2020-11-16 18:38 | 14 | 11kV | 34412 | 2458 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor U/G | Unplanned | No Weather Impact | Y | AOp interrupted Pnl.22 @1824 due to extreme high load and performed load relief switching. because Supply restored via Pnl.22 when Zn874 Concord - Pnl.17 tripped on: A Phase O/C Suspected UG cable fault in frontline section of feeder. See 1809383 1809385 | November | 2020 | 2021Q2 | 2021 | ZN874:PA22 | ZN874:PA22 | ZN00874/000022 | CANADA BAY | UG | Not Veg | 2020-11-16 | Y | 14 | N | 10 | N | Y | 1.1101 | 39.4971 | 25147.2746
[7 empty] | 1986 | 3710 | 1808197 | 2020-11-16 20:13 | 2020-11-16 21:43 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201112 C Phase 10 Amp substation DOLF Electrical Storrm | November | 2020 | 2021Q2 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2020-11-16 | Y | 90 | N | 10 | N | Y | 1.1101 | 39.4971 | 131.5387
[7 empty] | 3154 | 18844 | 1807939 | 2020-11-16 14:44 | 2020-11-16 22:25 | 461 | 11kV | 461 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | LID 201109 10Amp, substation DOLF | November | 2020 | 2021Q2 | 2021 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2020-11-16 | N | 461 | N | 10 | N | N | 1.1101 | 39.4971 | 336.8852
[7 empty] | 1942 | 3239 | 1808205 | 2020-11-16 20:54 | 2020-11-16 23:00 | 126 | 11kV | 2394 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201117 Single phase DOLF 2 x 20 Amp 2 x 20 amp HVF replaced power restored 2300. Excluded oms 1808331 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-11-16 | N | 126 | N | 10 | N | N | 1.1101 | 39.4971 | 1749.4646
[7 empty] | 2742 | 13057 | 1808084 | 2020-11-16 22:20 | 2020-11-16 23:00 | 40 | 11kV | 3440 | 86 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201116 Sub 52012 isolated for tree removal from lv mains | November | 2020 | 2021Q2 | 2021 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2020-11-16 | N | 40 | N | 10 | N | N | 1.1101 | 39.4971 | 2513.8505
[7 empty] | 1918 | 3016 | 1808289 | 2020-11-16 20:38 | 2020-11-17 00:37 | 239 | 11kV | 956 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201118 C phase 10 amp HVF replaced power restored 0037. mdv | November | 2020 | 2021Q2 | 2021 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2020-11-16 | N | 239 | N | 10 | N | N | 1.1101 | 39.4971 | 698.6166
[7 empty] | 2248 | 6824 | 1808144 | 2020-11-16 20:04 | 2020-11-17 01:10 | 306 | 11kV | 400248 | 1308 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201119 Overcurrent, Earth Fault targets required sw 81241 R Mancini assigned tree branch removed from pole kr-70567 and power restored .mdv Excluded oms 1808325 | November | 2020 | 2021Q2 | 2021 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Veg | 2020-11-16 | N | 306 | N | 10 | N | N | 1.1101 | 39.4971 | 292489.4331
[7 empty] | 2059 | 4778 | 1808101 | 2020-11-16 19:52 | 2020-11-17 01:30 | 338.2667 | 11kV | 9471.4667 | 28 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201121 Neil Curtis assigned, tree branch removed from mains, 2 x 16 amp A & B phase LF replaced power restored Excluded oms 1808104 CC1: 22-"Refer to SOp" | November | 2020 | 2021Q2 | 2021 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2020-11-16 | N | 338.2667 | N | 10 | N | N | 1.1101 | 39.4971 | 6921.4685
[7 empty] | 2887 | 14797 | 1808211 | 2020-11-16 20:06 | 2020-11-17 02:28 | 382 | 11kV | 255940 | 670 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201127 Tree branch on OHM adj. sub 62772. Targets required. | November | 2020 | 2021Q2 | 2021 | 202:34232 | 202:34232 | ZN00202/034232 | NEWCASTLE | OH | Veg | 2020-11-16 | Y | 382 | N | 10 | N | Y | 1.1101 | 39.4971 | 187033.403
[7 empty] | 2176 | 5963 | 1808163 | 2020-11-16 20:04 | 2020-11-17 02:36 | 392 | 11kV | 182682 | 858 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201142 2 fault operations A & B Phases Instantaneous Overcurrent Tree branch on 11hV OHM between poles JU-55786 & JU-50151. Excluded OMS No. 1808212 | November | 2020 | 2021Q2 | 2021 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Veg | 2020-11-16 | Y | 212.9161 | N | 10 | N | Y | 1.1101 | 39.4971 | 133498.6174
[7 empty] | 1792 | 1499 | 1808115 | 2020-11-16 20:08 | 2020-11-17 03:51 | 463 | 11kV | 1852 | 4 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201157 A & B Phases Overcurrent 11kV mains down JT-80270 Excluded OMS 1808115. | November | 2020 | 2021Q2 | 2021 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | OH | Not Veg | 2020-11-16 | Y | 463 | N | 10 | N | Y | 1.1101 | 39.4971 | 1353.387
[7 empty] | 2910 | 15157 | 1808257 | 2020-11-17 03:40 | 2020-11-17 04:30 | 50 | 11kV | 1300 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201123 Neil Curtis assigned section isolated to remove large branch off 11kv mains adj ABS 40176. Excluded OMS 1808257 | November | 2020 | 2021Q2 | 2021 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2020-11-17 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 950.0017
[7 empty] | 1831 | 1966 | 1808110 | 2020-11-16 19:54 | 2020-11-17 05:32 | 578 | 11kV | 789548 | 1366 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 201140 2 fault operations A & B Phase Overcurrent 11kV main off pin & tree on OHM adj sub 19964. | November | 2020 | 2021Q2 | 2021 | 213:33774 | 213:33774 | ZN00213/033774 | NEWCASTLE | OH | Not Veg | 2020-11-16 | Y | 578 | N | 10 | N | Y | 1.1101 | 39.4971 | 576978.3907
[7 empty] | 2086 | 5047 | 1808295 | 2020-11-16 20:00 | 2020-11-17 07:43 | 703 | 33kV Distribution | 14060 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201156 3 fault operations A Phase Earth Fault | November | 2020 | 2021Q2 | 2021 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Veg | 2020-11-16 | Y | 703 | N | 10 | N | Y | 1.1101 | 39.4971 | 10274.6333
[7 empty] | 2430 | 9322 | 1808127 | 2020-11-16 20:00 | 2020-11-17 08:43 | 763 | 11kV | 1339187 | 1783 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201130 2 fault operatiojns A & B phase Overcurrent Targest: 51AB Excluded OMS No. 1808127 + 1808516 | November | 2020 | 2021Q2 | 2021 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Veg | 2020-11-16 | Y | 751.0864 | N | 10 | N | Y | 1.1101 | 39.4971 | 978638.3603
[7 empty] | 1934 | 3182 | 1808175 | 2020-11-16 20:07 | 2020-11-17 09:05 | 778 | 11kV | 1179975 | 1575 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201155 A Phase Earth Fault Excluded OMS 1808330 & 1808444 | November | 2020 | 2021Q2 | 2021 | 256:80635 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Veg | 2020-11-16 | Y | 749.1905 | N | 10 | N | Y | 1.1101 | 39.4971 | 862290.9266
[7 empty] | 2047 | 4623 | 1808286 | 2020-11-16 20:37 | 2020-11-17 09:15 | 758 | 11kV | 758 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201128 Sub 1111 isolated to repair service Wires on ground between Transformer on pole IT20050 and customer private pole on property. | November | 2020 | 2021Q2 | 2021 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2020-11-16 | Y | 758 | N | 10 | N | Y | 1.1101 | 39.4971 | 553.924
[7 empty] | 2778 | 13589 | 1808598 | 2020-11-16 20:00 | 2020-11-17 09:49 | 829 | 11kV | 3316 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201133 10Amp fuse substation DOLF Replaced blown 10A A ph DOLF on Sub 65141. Supply restored 0949hrs. Note: as per customers call, customers had been without supply since 16/11/20 20:00 | November | 2020 | 2021Q2 | 2021 | 264:81232 | 264:81232 | ZN00264/081232 | MAITLAND | OH | Veg | 2020-11-16 | Y | 829 | N | 10 | N | Y | 1.1101 | 39.4971 | 2423.235
[7 empty] | 2789 | 13739 | 1808611 | 2020-11-17 10:30 | 2020-11-17 10:55 | 25 | 11kV | 250 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201134 Tree Branch on Mains 4.5 KM FROM HWY ON LHS ON ANAMBAH RD BROKEN TREE BRANCH ON DW - CAUSING DW TO BE LOW ON EDGE ROAD - POWER ON Excluded OMS 1808611 | November | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-11-17 | N | 25 | N | 7 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 2533 | 10440 | 1808690 | 2020-11-17 12:18 | 2020-11-17 13:45 | 87 | 11kV | 15747 | 181 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | Previous Storm | N | LID 201154 Leakage on pole JT-71662 Excluded OMS 1808690. | November | 2020 | 2021Q2 | 2021 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Not Veg | 2020-11-17 | N | 87 | N | 7 | N | N | 1.1101 | 39.4971 | 11507.4431
[7 empty] | 3179 | 19237 | 1809128 | 2020-11-17 15:30 | 2020-11-17 15:45 | 15 | 11kV | 15 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201163 Single phase C Pengelly assigned. sub isolated to install loggers. . Excluded oms 1808656 | November | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-11-17 | N | 15 | N | 7 | N | N | 1.1101 | 39.4971 | 10.9616
[7 empty] | 2474 | 9723 | 1808812 | 2020-11-17 15:20 | 2020-11-17 16:35 | 75 | 11kV | 225 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 201165 Sub 51041 isolated to repair neutral connection | November | 2020 | 2021Q2 | 2021 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2020-11-17 | N | 75 | N | 7 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 3231 | 19656 | 1807980 | 2020-11-16 16:45 | 2020-11-17 17:45 | 1500 | 11kV | 1500 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | Y | Ex Pnl.4 Concord - 11kV interrupted from S64913 Sw/B due to S65412 Hilly Edwin No.2 catching on fire. | November | 2020 | 2021Q2 | 2021 | ZN874:PA4 | ZN874:PA4 | ZN00874/000004 | CANADA BAY | UG | Not Veg | 2020-11-16 | Y | 1500 | N | 10 | N | Y | 1.1101 | 39.4971 | 1096.1558
[7 empty] | 2044 | 4594 | 1808862 | 2020-11-17 15:32 | 2020-11-17 18:35 | 183 | 11kV | 183 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 201171 Single Phase 10 Amp fuse, substation DOLF Fuse on pole struck by lightning pump not working. Please attend. | November | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-11-17 | N | 183 | N | 7 | N | N | 1.1101 | 39.4971 | 133.731
[7 empty] | 2218 | 6571 | 1808108 | 2020-11-16 20:02 | 2020-11-17 19:18 | 1396 | 11kV | 1418029 | 1568 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201138 2 fault operations A & B Phase Instantaneous Overcurrent Tree into 11kV adj. ABS 13987. 11kV into LV between poles JU-71448 & JU-71449. EMSO inspected LV MSBs OK. Burnt off tapping on road side of load connection on ABS 23079. Excluded OMS No. 1808108 + 1808746 + 1808764 + 1808847 | November | 2020 | 2021Q2 | 2021 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Veg | 2020-11-16 | Y | 904.3552 | N | 10 | N | Y | 1.1101 | 39.4971 | 1036253.7684
[7 empty] | 1829 | 1908 | 1808920 | 2020-11-17 18:52 | 2020-11-17 21:40 | 168 | 11kV | 209496 | 2241 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | Zn1285 Greenacre Park - Pnl.31 tripped on A phase OC Abnormal: LB2481 Closed with AB2582 Open (PT612219, S1200 & S5692 in LV // DMA) S5605 Sw/B Closed with AB2496 open (DMA) Bird on UGOH to S5692 (Pole RP17542) See 1809361 1809363 1809365 | November | 2020 | 2021Q2 | 2021 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-11-17 | N | 93.4833 | N | 7 | N | N | 1.1101 | 39.4971 | 153093.4977
[7 empty] | 2767 | 13372 | 1808112 | 2020-11-16 19:56 | 2020-11-18 01:20 | 1764 | 11kV | 1463257 | 1872 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201170 2 fault operations OHM down High-into-low at 3 possible locations. pole JT-40311, pole JT-40308,and Pole JT-40282. EMSOs checking for damage Excluded oms 1808113, 1808713, 18088609, 1808735 | November | 2020 | 2021Q2 | 2021 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2020-11-16 | Y | 781.6544 | N | 10 | N | Y | 1.1101 | 39.4971 | 1069305.0568
[7 empty] | 2616 | 11281 | 1808116 | 2020-11-16 19:56 | 2020-11-18 06:40 | 2084 | 11kV | 400463 | 427 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201180 2 fault operations 3 phase Overcurrent Mains down JT-12458 Excluded OMS 1808217 | November | 2020 | 2021Q2 | 2021 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Veg | 2020-11-16 | Y | 937.8525 | N | 10 | N | Y | 1.1101 | 39.4971 | 292646.5487
[7 empty] | 1695 | 237 | 1808801 | 2020-11-16 19:56 | 2020-11-18 08:45 | 2209 | 11kV | 68479 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201179 ## OMS 1808801, 1808116, 1808334. 11kV mains down JT-12458 Vegetation brought down 11kV | November | 2020 | 2021Q2 | 2021 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Veg | 2020-11-16 | Y | 2209 | N | 10 | N | Y | 1.1101 | 39.4971 | 50042.4334
[7 empty] | 2307 | 7593 | 1808239 | 2020-11-16 20:22 | 2020-11-18 12:30 | 2408 | 11kV | 12040 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | Y | LID 201143 B ph Live Line Lead broken off top of DOLF on Sub 10837. Open LVF's 10837. Open Dolfs 10837. Warning tag applied. Please have crew attend to carry out repairs. Narrow road. Traffic control required. Note: restore time confirmed by AOP | November | 2020 | 2021Q2 | 2021 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2020-11-16 | Y | 2408 | N | 10 | N | Y | 1.1101 | 39.4971 | 8798.4769
[7 empty] | 2882 | 14737 | 1809123 | 2020-11-18 16:55 | 2020-11-18 19:30 | 155 | 11kV | 6355 | 41 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 201191 Refer to OMS 1809123 AND 1809232 11kV on cross arms at poles FU-42610 and FU-42573.. No protection operated. | November | 2020 | 2021Q2 | 2021 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2020-11-18 | N | 155 | N | 2 | N | N | 1.1101 | 39.4971 | 4644.0466
[7 empty] | 1723 | 530 | 1809275 | 2020-11-18 20:25 | 2020-11-18 21:30 | 65 | 11kV | 35750 | 550 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 201192 1 CB operation, B Phase Earth Fault faulty section of UGM (36944/38927/11604) isolated & AP left | November | 2020 | 2021Q2 | 2021 | 202:34261 | 202:34261 | ZN00202/034261 | NEWCASTLE | UG | Not Veg | 2020-11-18 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 26125.0456
[7 empty] | 2948 | 15839 | 1809454 | 2020-11-19 14:59 | 2020-11-19 16:30 | 91 | 11kV | 91 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201198 Single phase DOLF : 10 Amp Excluded OMS 1809454 | November | 2020 | 2021Q2 | 2021 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-11-19 | N | 91 | N | 1 | N | N | 1.1101 | 39.4971 | 66.5001
[7 empty] | 2635 | 11501 | 1809580 | 2020-11-20 10:01 | 2020-11-20 12:00 | 119 | 11kV | 5133 | 57 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 201205 2 Fault operations B Phase Earth Fault Defective UGOH pole IU-57135 DQ Excluded oms 1809580## | November | 2020 | 2021Q2 | 2021 | 224:80328 | 214:8672 | ZN00214/008672 | LAKE MACQUARIE | Unknown | Unknown | 2020-11-20 | N | 90.0526 | N | 6 | N | N | 1.1101 | 39.4971 | 3751.045
[7 empty] | 2107 | 5241 | 1809689 | 2020-11-20 16:47 | 2020-11-20 18:15 | 88 | 11kV | 4576 | 52 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | No Weather Impact | N | At PT1959 Kookaburra Galston - A B and C phase HDO operated following a lightning strike AB63753 DMS, Open LB2919 Closed See OMS 1810362 1809691 | November | 2020 | 2021Q2 | 2021 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Not Veg | 2020-11-20 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 3344.0058
[7 empty] | 2943 | 15705 | 1809692 | 2020-11-20 16:47 | 2020-11-20 18:54 | 127 | 11kV | 20320 | 160 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Recloser CP555 Arcadia Park Opened and Locked out on Section of Panel 4 Ex35370 Galston Abnormal Switching: CP451 Open and DMA, CP2063 Closed Cause: tree branch on OH mains OS 58 Bay Rd Removed by DOp | November | 2020 | 2021Q2 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2020-11-20 | N | 127 | N | 6 | N | N | 1.1101 | 39.4971 | 14849.2567
[7 empty] | 1757 | 964 | 1810233 | 2020-11-20 22:51 | 2020-11-21 05:05 | 374 | 11kV | 1870 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 201235 blown 11kV tapping pole FS-94486 also see report 201224/ OMS 1810232 | November | 2020 | 2021Q2 | 2021 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2020-11-20 | N | 374 | N | 6 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 2139 | 5512 | 1809751 | 2020-11-20 22:51 | 2020-11-21 05:19 | 388 | 11kV | 7372 | 19 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201224 1 fault operation 3 phase Overcurrent Fault Current: Aph - 831A, Bph - 740A, Cph - 708A Intellirupter did not reclose due to blown tapping upstream. see report 201235 Excluded OMS No. 1809751, 1809758 | November | 2020 | 2021Q2 | 2021 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2020-11-20 | N | 388 | N | 6 | N | N | 1.1101 | 39.4971 | 5387.2402
[7 empty] | 2648 | 11661 | 1809756 | 2020-11-21 00:24 | 2020-11-21 08:55 | 511 | 11kV | 772 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201234 A & B Phase DOLF : 20 Amp Blown LF 48165, Blown ODLF sub 113228, blown DOLF19983 and suspect faulty TX, Repleaced blown L/A 21/11/20 Excluded OMS 1809756, 1809760 1809769 | November | 2020 | 2021Q2 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2020-11-21 | N | 386 | N | 16 | N | N | 1.1101 | 39.4971 | 564.1548
[7 empty] | 2737 | 12919 | 1809754 | 2020-11-20 23:49 | 2020-11-21 09:32 | 583 | 11kV | 12735 | 22 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201233 DOLF : 63 Amp 3 x blown line fuses 3 x 10A DOLF S.50308. + 1 Cph 100A LVF Excluded OMS 1809754. | November | 2020 | 2021Q2 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2020-11-20 | N | 578.8636 | N | 6 | N | N | 1.1101 | 39.4971 | 9306.3624
[7 empty] | 2355 | 8290 | 1809759 | 2020-11-21 03:46 | 2020-11-21 10:05 | 379 | 11kV | 1516 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201238 Single phase DOLF : 10 Amp Blown sub fuses not LF 79031. Excluded OMS 1809759 | November | 2020 | 2021Q2 | 2021 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2020-11-21 | N | 379 | N | 16 | N | N | 1.1101 | 39.4971 | 1107.8481
[7 empty] | 2604 | 11217 | 1809782 | 2020-11-21 07:44 | 2020-11-21 10:46 | 182 | 11kV | 546 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201237 A & B Phase DOLF : 20 Amp Also replaced 1 x 10 Bph Dolf sub 63884 | November | 2020 | 2021Q2 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2020-11-21 | N | 182 | N | 16 | N | N | 1.1101 | 39.4971 | 399.0007
[7 empty] | 2900 | 14992 | 1809761 | 2020-11-21 05:24 | 2020-11-21 11:10 | 346 | 11kV | 3460 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201241 Single phase DOLF : 20 Amp PAtrolled Fdr OK. Blown LF Excluded OMS 1809768 & 1809761 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-11-21 | N | 346 | N | 16 | N | N | 1.1101 | 39.4971 | 2528.4659
[7 empty] | 2961 | 16053 | 1809772 | 2020-11-21 06:44 | 2020-11-21 12:18 | 334 | 11kV | 8016 | 24 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 201242 Faulty Transformer Excluded OMS 1809772 | November | 2020 | 2021Q2 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-11-21 | N | 334 | N | 16 | N | N | 1.1101 | 39.4971 | 5857.8564
[7 empty] | 2624 | 11368 | 1809795 | 2020-11-21 08:55 | 2020-11-21 13:00 | 245 | 11kV | 490 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201243 Single Phase DOLF : 10 Amp Replaced Lightning Arrestor Excluded OMS 1809795 | November | 2020 | 2021Q2 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2020-11-21 | N | 245 | N | 16 | N | N | 1.1101 | 39.4971 | 358.0775
[7 empty] | 3090 | 18008 | 1809832 | 2020-11-21 12:09 | 2020-11-21 13:45 | 96 | 11kV | 480 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201246 Single phase DOLF : 10 Amp Excluded OMS 1809832 | November | 2020 | 2021Q2 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-11-21 | N | 96 | N | 16 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 1724 | 545 | 1809852 | 2020-11-21 14:18 | 2020-11-21 15:19 | 61 | 11kV | 40472 | 699 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT Zn630 Mascot Panel 31 Tripped on Relays: EF, EFI Field EFI's 35284 S6458 S8070 Cause: UG cable fault from S8070 to S49071 to S65256 See OMS 1810279 1810280 1809852 | November | 2020 | 2021Q2 | 2021 | ZN630:PA31 | ZN630:PA31 | ZN00630/000031 | BAYSIDE | UG | Not Veg | 2020-11-21 | N | 57.8999 | N | 16 | N | N | 1.1101 | 39.4971 | 29575.7439
[7 empty] | 2825 | 14089 | 1809878 | 2020-11-21 14:45 | 2020-11-21 18:35 | 230 | 11kV | 460 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201249 HV lead broken at transformer bushing Excluded OMS 1809859 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-11-21 | N | 230 | N | 16 | N | N | 1.1101 | 39.4971 | 336.1544
[7 empty] | 3186 | 19301 | 1809774 | 2020-11-21 06:52 | 2020-11-21 19:30 | 758 | 11kV | 2274 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 201247 Single phase DOLF : 10 Amp excluded OMS 1809774 | November | 2020 | 2021Q2 | 2021 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2020-11-21 | N | 758 | N | 16 | N | N | 1.1101 | 39.4971 | 1661.7721
[7 empty] | 2937 | 15583 | 1809863 | 2020-11-21 15:50 | 2020-11-21 19:40 | 230 | 11kV | 173062 | 1671 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ex Zn15015 North Head Panel 25 At S16194 Manly Hospital No1. SW/B tripped on A phase timed OC Cause: Bird flew into LV mains in Osbourne Rd that were in LV parallel causing mains to burn down and protection pick up on Feeder @ Manly (S16194) | November | 2020 | 2021Q2 | 2021 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | OH | Not Veg | 2020-11-21 | N | 103.5679 | N | 16 | N | N | 1.1101 | 39.4971 | 126468.6051
[7 empty] | 2294 | 7431 | 1809915 | 2020-11-21 20:44 | 2020-11-21 22:55 | 131 | 11kV | 23515 | 199 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201256 2 fault operations 3 phase Overcurrent Excluded OMS 1809915 | November | 2020 | 2021Q2 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2020-11-21 | N | 118.1658 | N | 16 | N | N | 1.1101 | 39.4971 | 17184.0684
[7 empty] | 2470 | 9684 | 1809899 | 2020-11-21 23:15 | 2020-11-22 | 45 | 11kV | 270 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 201258 Isolated PT 52659 for clearance to erect service wire Excluded OMS 1809899 | November | 2020 | 2021Q2 | 2021 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2020-11-21 | N | 45 | N | 16 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 1851 | 2257 | 1809920 | 2020-11-21 22:39 | 2020-11-22 01:00 | 141 | 11kV | 19612 | 240 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.1 tripped on: O/C and E/F UG cable fault between S8775 Sw/B, S7616 Sw/B tee S791 Note: No access to CP1006 and S35475. No EFi @ S7616 See 1811095 1811096 | November | 2020 | 2021Q2 | 2021 | ZN2466:PA1 | ZN2466:PA1 | ZN02466/000001 | PARRAMATTA | UG | Not Veg | 2020-11-21 | N | 81.7167 | N | 16 | N | N | 1.1101 | 39.4971 | 14331.8711
[7 empty] | 1928 | 3099 | 1809926 | 2020-11-22 01:15 | 2020-11-22 02:44 | 89 | 11kV | 85953 | 1024 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At Zn10994 Mortdale Panel 19 Tripped on' Relays: O/C B and C phase, Reclose Timing, EFI Cause: Vehicle hit pole on CBR Lorraine and Roberts St Mortdale damaging UGOH pole dection from S10954 to CP31043 to S10289 See OMS 1810240 1810241 1810242 1809926 | November | 2020 | 2021Q2 | 2021 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2020-11-22 | N | 83.9385 | N | 10 | N | N | 1.1101 | 39.4971 | 62811.9172
[7 empty] | 3040 | 17218 | 1809916 | 2020-11-21 20:51 | 2020-11-22 03:39 | 408 | 11kV | 43221 | 138 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201254 3 fault operations 3 phase Sensitive Earth Fault 2 x 11kV wires down at pole 5I-40056, repairs complete. Excluded oms ## 1809916 | November | 2020 | 2021Q2 | 2021 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2020-11-21 | N | 313.1957 | N | 16 | N | N | 1.1101 | 39.4971 | 31584.632
[7 empty] | 2065 | 4809 | 1809913 | 2020-11-21 20:37 | 2020-11-22 06:51 | 614 | 11kV | 110565 | 181 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201255 5 fault operations 3 phase Earth Fault Excluded OMS 1809913 | November | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-11-21 | N | 610.8564 | N | 16 | N | N | 1.1101 | 39.4971 | 80797.6409
[7 empty] | 1811 | 1706 | 1809951 | 2020-11-22 08:52 | 2020-11-22 15:00 | 368 | 11kV | 440 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 201266 L/F 40742 blowing for Tank failure at sub 51961. LF is loaded with a5 A fuse. S 51961 DOLF is loaded with a 10A fuse. Excluded OMS 1809951 | November | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-11-22 | N | 88 | N | 10 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 2118 | 5318 | 1809932 | 2020-11-22 05:27 | 2020-11-22 15:55 | 628 | 11kV | 232165 | 1357 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.19 tripped on: A & B phase IOC, SEF 11kV OH down adj LB35051. Section between LB35675, LB35668 to S9969 Sw/B tee S9880 See 1810626 1810627 1810628 | November | 2020 | 2021Q2 | 2021 | ZN9245:PA19 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2020-11-22 | N | 171.087 | N | 10 | N | N | 1.1101 | 39.4971 | 169659.3343
[7 empty] | 1713 | 432 | 1809954 | 2020-11-22 05:35 | 2020-11-22 16:31 | 656 | 11kV | 10496 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201274 all subs restored when L/F replaced. Excluded OMS 1809991, 1809971, 1809972 ,1809973 | November | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-11-22 | N | 656 | N | 10 | N | N | 1.1101 | 39.4971 | 7670.1672
[7 empty] | 2346 | 8185 | 1810003 | 2020-11-22 14:47 | 2020-11-22 16:55 | 128 | 11kV | 128 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201275 DOLF : 10 Amp Excluded OMS 1810003 | November | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-11-22 | N | 128 | N | 10 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 2632 | 11458 | 1810015 | 2020-11-22 15:52 | 2020-11-22 17:45 | 113 | 11kV | 23102 | 220 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | iR62705 Jiliby Durren 0.1 tripped Abnormal: R45016 CB open with by-pass AB closed Branch on mains Adj PT14839 See 1810615 1810618 1810619 | November | 2020 | 2021Q2 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2020-11-22 | N | 105.0091 | N | 10 | N | N | 1.1101 | 39.4971 | 16882.2602
[7 empty] | 3034 | 17181 | 1810072 | 2020-11-22 18:33 | 2020-11-22 19:27 | 54 | 11kV | 10982 | 207 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.2 tripped on: A & C OC & Earth Fault UG cable fault between S5690 and S3721 See 1810632 1810633 | November | 2020 | 2021Q2 | 2021 | ZN8100:PA2 | ZN8100:PA2 | ZN08100/000002 | SYDNEY | UG | Not Veg | 2020-11-22 | N | 53.0531 | N | 10 | N | N | 1.1101 | 39.4971 | 8025.3217
[7 empty] | 2850 | 14376 | 1810035 | 2020-11-22 16:28 | 2020-11-22 19:33 | 185 | 11kV | 555 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201281 A & C Phase DOLF : 16 Amp 2 x blown DOLF & 1 x LA Excluded OMS 1810035 | November | 2020 | 2021Q2 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | CENTRAL COAST | OH | Veg | 2020-11-22 | N | 185 | N | 10 | N | N | 1.1101 | 39.4971 | 405.5776
[7 empty] | 2715 | 12497 | 1810059 | 2020-11-22 17:49 | 2020-11-22 19:50 | 121 | 11kV | 363 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 201283 A Phase DOLF : 16 Amp Excluded OMS 1810059 | November | 2020 | 2021Q2 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-11-22 | N | 121 | N | 10 | N | N | 1.1101 | 39.4971 | 265.2697
[7 empty] | 1845 | 2111 | 1810044 | 2020-11-22 16:48 | 2020-11-22 23:32 | 404 | 11kV | 2020 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | HV fuse operated PT13324 Note: no control room report raised, job re-entered based on EMSO site visit and notes on related job | November | 2020 | 2021Q2 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2020-11-22 | N | 404 | N | 10 | N | N | 1.1101 | 39.4971 | 1476.1564
[7 empty] | 1683 | 25 | 1810097 | 2020-11-23 01:57 | 2020-11-23 03:30 | 93 | 11kV | 77934 | 838 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zb10994 Mortdale roadside bond burnt off AB31321 also refer to OMS 1810609 for Pnl.13 tripped and reclosed due to posum on UGOH to S49678 at 23/11/20 01:57 See 1810609 1810610 | November | 2020 | 2021Q2 | 2021 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2020-11-23 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 56951.8685
[7 empty] | 1785 | 1459 | 1810130 | 2020-11-23 07:31 | 2020-11-23 08:10 | 39.4667 | 11kV | 39.4667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201291 DOLF : 10 Amp | November | 2020 | 2021Q2 | 2021 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2020-11-23 | N | 39.4667 | N | 5 | N | N | 1.1101 | 39.4971 | 28.8411
[7 empty] | 2348 | 8191 | 1810136 | 2020-11-23 07:55 | 2020-11-23 10:10 | 135 | 11kV | 307106 | 3043 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn4545 Meadowbank - Pnl.31 tripped on: OC Abnormal: REC46117 DMA out of service with by pass LB closed Tree branch on OH mains near LB794 (Corner Blaxland Rd and Albuera Rd See 181102 181103 181104 | November | 2020 | 2021Q2 | 2021 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Veg | 2020-11-23 | N | 100.9221 | N | 5 | N | N | 1.1101 | 39.4971 | 224424.0067
[7 empty] | 2615 | 11273 | 1810207 | 2020-11-23 10:31 | 2020-11-23 11:36 | 65 | 11kV | 2844 | 44 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36000 Olympic Park - Pnl.1 tripped on A phase IOC UG cable fault in front line section of feeder between Pnl.1, S3447 Sw/A and S6695 Sw/A | November | 2020 | 2021Q2 | 2021 | ZN36000:PA1 | ZN36000:PA1 | ZN36000/000001 | PARRAMATTA | UG | Not Veg | 2020-11-23 | N | 64.6364 | N | 5 | N | N | 1.1101 | 39.4971 | 2078.3113
[7 empty] | 2322 | 7779 | 1810276 | 2020-11-23 12:16 | 2020-11-23 15:40 | 204 | 11kV | 408 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 201300 Broken Live Line Clamp Excluded OMS 1810276 | November | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-11-23 | N | 204 | N | 5 | N | N | 1.1101 | 39.4971 | 298.1544
[7 empty] | 2097 | 5161 | 1810974 | 2020-11-25 22:30 | 2020-11-25 23:20 | 50 | 11kV | 650 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 201334 section isolated to repair HV tapping at pole AJ-90031. Excluded OMS 1810974. | November | 2020 | 2021Q2 | 2021 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2020-11-25 | N | 50 | N | 2 | N | N | 1.1101 | 39.4971 | 475.0008
[7 empty] | 2830 | 14165 | 1810981 | 2020-11-25 21:10 | 2020-11-26 02:00 | 290 | 11kV | 200526 | 1236 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.1 tripped on: Earth Fault Contractor drove steel pole into 11kV feeder to S5442. Adjacent pole 16002 S5442 Darford Milson isolated for possible damage. See 181111 1811112 1811113 | November | 2020 | 2021Q2 | 2021 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | UG | Not Veg | 2020-11-25 | N | 162.2379 | N | 2 | N | N | 1.1101 | 39.4971 | 146538.4863
[7 empty] | 2818 | 14033 | 1811139 | 2020-11-26 15:42 | 2020-11-26 16:51 | 69 | 11kV | 9729 | 141 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 201349 Broken insulator found on Pole FR24774; Excluded OMS job 1811139 | November | 2020 | 2021Q2 | 2021 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Not Veg | 2020-11-26 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 7109.6662
[7 empty] | 2984 | 16387 | 1811221 | 2020-11-27 01:04 | 2020-11-27 08:11 | 427 | 11kV | 42700 | 100 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S6879 Miller Metroplaza No.1 - All Tee off Tx CBs tripped Tx 1 No.1 RMCB tripped on low gasand tripped remaining Tx's via // tripping | November | 2020 | 2021Q2 | 2021 | ZN35400:PA56 | ZN35400:PA56 | ZN35400/000056 | NORTH SYDNEY | Unknown | Not Veg | 2020-11-27 | N | 427 | N | 6 | N | N | 1.1101 | 39.4971 | 31203.9006
[7 empty] | 2970 | 16263 | 1811326 | 2020-11-27 13:20 | 2020-11-27 14:28 | 68 | 11kV | 1156 | 17 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Hot >35C | N | LID 201358 Pole 8L-90250 replaced under emergency. No trip. Excluded OMS 1811326 | November | 2020 | 2021Q2 | 2021 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2020-11-27 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 844.7707
[7 empty] | 2195 | 6245 | 1811205 | 2020-11-26 21:48 | 2020-11-27 15:20 | 1052 | 11kV | 1052 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201359 C Phase DOLF : 3 Amp Blown dolf found by EMSO on 26/11/20, left for day work and replaced by CAW on 27/11/20. Excluded OMS no. 1811205 | November | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2020-11-26 | N | 1052 | N | 2 | N | N | 1.1101 | 39.4971 | 768.7706
[7 empty] | 2560 | 10724 | 1811356 | 2020-11-27 15:19 | 2020-11-27 16:47 | 88 | 11kV | 70808 | 844 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.14 tripped on: Earth Fault Abnormal: S3551 Sw/B Closed with S8061 Sw/A open (DMA) UG cable fault between S8203 Sw/N and S7567 Sw/D See 1813592 1813594 | November | 2020 | 2021Q2 | 2021 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2020-11-27 | N | 83.8957 | N | 6 | N | N | 1.1101 | 39.4971 | 51744.3979
[7 empty] | 3000 | 16660 | 1811155 | 2020-11-27 16:08 | 2020-11-27 19:45 | 217 | 11kV | 434 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | AT PT2059 Bloodwood Potter Prop - TX failed Test MG supplyinmg customers See OMS 1813638 1811264 1811155 | November | 2020 | 2021Q2 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2020-11-27 | N | 217 | N | 6 | N | N | 1.1101 | 39.4971 | 317.1544
[7 empty] | 2034 | 4457 | 1811399 | 2020-11-27 18:17 | 2020-11-27 20:15 | 118 | 11kV | 118 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201362 C Phase DOLF : 10 Amp Excluded OMS 1811399 | November | 2020 | 2021Q2 | 2021 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2020-11-27 | N | 118 | N | 6 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 2464 | 9570 | 1811413 | 2020-11-27 21:35 | 2020-11-27 22:37 | 62 | 11kV | 434 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201363 A Phase DOLF : 10 AMP Line Fuse 40679 A phase 10A no fault found suspect previous storm Excluded OMS 1811413 | November | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-11-27 | N | 62 | N | 6 | N | N | 1.1101 | 39.4971 | 317.1544
[7 empty] | 2205 | 6323 | 1811418 | 2020-11-28 00:05 | 2020-11-28 03:19 | 194 | 11kV | 238484 | 1230 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1290 Leightonfield - Pnl.11 tripped on: Earth Fault Abnormal: S8601 Sw/B Closed with S8600 Sw/A Open UG cable fault between Pnl.11, S7614 & S5013. | November | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-28 | N | 193.8894 | N | 19 | N | N | 1.1101 | 39.4971 | 174277.0731
[7 empty] | 2174 | 5925 | 1811472 | 2020-11-28 11:33 | 2020-11-28 12:45 | 72 | 11kV | 62496 | 1178 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At S15006 dee Why West Panel 8 Recloser CP20285 tripped pm Signals: OC trip, EF trip and Lockout Cause: UGOH fault short circuit - adjacent to S16166 Abnormal Switching: SW/A Closed @ S16549, SW/A Opened at S17099 SW/B Closed @ S50262, SW/A Opened @ S46891 See OMS1813880 1813882 1811472 1811478 | November | 2020 | 2021Q2 | 2021 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | Unknown | Unknown | 2020-11-28 | N | 53.0526 | N | 19 | N | N | 1.1101 | 39.4971 | 45670.2335
[7 empty] | 2006 | 3959 | 1811508 | 2020-11-28 13:03 | 2020-11-28 14:08 | 65 | 11kV | 5819 | 91 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | REC21799 Oxford Booker tripped Cause not ascertained See 1813795 1813794 | November | 2020 | 2021Q2 | 2021 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Veg | 2020-11-28 | N | 63.9451 | N | 19 | N | N | 1.1101 | 39.4971 | 4252.3536
[7 empty] | 2311 | 7650 | 1811515 | 2020-11-28 13:17 | 2020-11-28 14:47 | 90 | 11kV | 24289 | 408 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | At S630 Panel 35 tripped on Relays: Earth Fault, Timed OC, IOC and EFI At S59347 Oriordan King RMI SW/B Endbox Failure See OMS 1813490 1813492 Cause: End Box fault | November | 2020 | 2021Q2 | 2021 | ZN630:PA35 | ZN630:PA35 | ZN00630/000035 | BAYSIDE | UG | Not Veg | 2020-11-28 | N | 59.5319 | N | 19 | N | N | 1.1101 | 39.4971 | 17749.6848
[7 empty] | 2350 | 8213 | 1811518 | 2020-11-28 13:17 | 2020-11-28 15:40 | 143 | 11kV | 106759 | 1113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | REC21801 Sorlie merrie tripped, reclosed and locked out on: OC Abnormal: LB25623 closed with USL24445 Open (DMA) Tree on 11kV OH mains See 1813824 1813825 | November | 2020 | 2021Q2 | 2021 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Veg | 2020-11-28 | N | 95.92 | N | 19 | N | N | 1.1101 | 39.4971 | 78016.3283
[7 empty] | 3119 | 18409 | 1811536 | 2020-11-28 14:17 | 2020-11-28 15:45 | 88 | 11kV | 76472 | 869 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 201365 1 fault operation B & C Phase Overcurrent, Earth Fault Please check Auto Reclose function on 19066. Didnt seem to reclose. | November | 2020 | 2021Q2 | 2021 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2020-11-28 | N | 88 | N | 19 | N | N | 1.1101 | 39.4971 | 55883.4821
[7 empty] | 1722 | 519 | 1811590 | 2020-11-28 16:26 | 2020-11-28 17:38 | 72 | 11kV | 61020 | 877 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At S10997 Sans Souci Pa5 tripped on Cause: UGOH fault Short curcuit S78668 to S10940 to S10009 See OMS 1813595 1813596 1811590 | November | 2020 | 2021Q2 | 2021 | ZN10997:PA5 | ZN10997:PA5 | ZN10997/000005 | BAYSIDE | Unknown | Unknown | 2020-11-28 | N | 69.5781 | N | 19 | N | N | 1.1101 | 39.4971 | 44591.6162
[7 empty] | 2141 | 5579 | 1811682 | 2020-11-28 17:44 | 2020-11-28 17:53 | 9 | 11kV | 9657 | 1073 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | N | @ Zn 9037 Miranda - 11kV Panel No.2 "LB 35854" feeder interrupted by Sop Panel No.2 interrupted to remove load of Tx No.2 which had a thermal and was close to it's emergency rating. The short duration was due to Panel No.8 being O/L which was abetter option. See separate interruption report for Panel No.8 | November | 2020 | 2021Q2 | 2021 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2020-11-28 | N | 9 | N | 19 | N | N | 1.1101 | 39.4971 | 7057.0508
[7 empty] | 1690 | 193 | 1811570 | 2020-11-28 16:16 | 2020-11-28 19:00 | 164.3167 | 11kV | 142133.9167 | 865 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | iR62226 Connels Terry tripped and locked out Cause not ascertained | November | 2020 | 2021Q2 | 2021 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2020-11-28 | N | 164.3167 | N | 19 | N | N | 1.1101 | 39.4971 | 103867.2741
[7 empty] | 1740 | 770 | 1811628 | 2020-11-28 16:53 | 2020-11-28 19:00 | 127 | 11kV | 1524 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | At PT13233 Yarramalong Maitland HVDO operated on fuse fatigue | November | 2020 | 2021Q2 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2020-11-28 | N | 127 | N | 19 | N | N | 1.1101 | 39.4971 | 1113.6942
[7 empty] | 2120 | 5334 | 1811634 | 2020-11-28 16:59 | 2020-11-28 19:00 | 121 | 11kV | 248013 | 2670 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At Zn1193 Lindfield Panel 28 tripped on Relays: 28L EF, 51N, 1501TN, Lockout and EFI Signa;sL 11kV Trip Cause: UGOH fault short circuit See OMS 1813784, 1813786,1813788 1811634 | November | 2020 | 2021Q2 | 2021 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | KU-RING-GAI | Unknown | Unknown | 2020-11-28 | N | 92.8888 | N | 19 | N | N | 1.1101 | 39.4971 | 181240.5853
[7 empty] | 3205 | 19446 | 1811677 | 2020-11-28 17:45 | 2020-11-28 19:54 | 129 | 11kV | 110526 | 917 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn1285 Greenacre Park Panel 20 tripped and locked out on Relays: A phase OC, EFI, EF, Lockout and Timing Cause:UG cable fault between S7859 and S1730 See OMS 1813614 1813615 1811677 | November | 2020 | 2021Q2 | 2021 | ZN1285:PA20 | ZN1285:PA20 | ZN01285/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-28 | N | 120.53 | N | 19 | N | N | 1.1101 | 39.4971 | 80769.1408
[7 empty] | 2787 | 13725 | 1811716 | 2020-11-28 18:18 | 2020-11-28 20:05 | 107 | 11kV | 60241 | 563 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Hot >35C | N | LID 201372 2 fault operations C Phase Earth Fault Main off adj ABS 9159 - feed towards sub 52304 Excluded oms 1811781 | November | 2020 | 2021Q2 | 2021 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2020-11-28 | N | 107 | N | 19 | N | N | 1.1101 | 39.4971 | 44022.346
[7 empty] | 1872 | 2471 | 1811637 | 2020-11-28 17:01 | 2020-11-28 21:00 | 239 | 11kV | 236167 | 1259 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn3154 St Ives - Pnl.18 tripped on: OC and IOC Field EFI: NIL (did not work) UG cable fault between S64714 Sw/B, S4915 Sw/A, S4903 Sw/B tee PT426 See 1813843 1813844 | November | 2020 | 2021Q2 | 2021 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | UG | Not Veg | 2020-11-28 | N | 187.583 | N | 19 | N | N | 1.1101 | 39.4971 | 172583.8779
[7 empty] | 2477 | 9791 | 1811756 | 2020-11-28 18:59 | 2020-11-28 21:10 | 131 | 11kV | 195647 | 1918 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At Zn12650 West Gosford Panel 13 Tripped Relays: A B and C phase IOC EF and Lockout Signals: 11kV Trip Cause: UGOH blown on pole GO6305 OS Old gosford pole depot See OMS 1813565 1813569 1813570 1813571 1813572 1811478 1811756 | November | 2020 | 2021Q2 | 2021 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Unknown | Unknown | 2020-11-28 | N | 102.0057 | N | 19 | N | N | 1.1101 | 39.4971 | 142973.057
[7 empty] | 2679 | 12129 | 1811645 | 2020-11-28 17:17 | 2020-11-28 22:20 | 303 | 11kV | 206244 | 1904 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | Panel 22 @ Concord interrupted due to Overload situation Cause: Overload die to Hot weather and Pa17 DMA Abnromal Switching: S36239 Closed, S48393 Open S7961 Closed, S7960 Open S3196 Closed, S7817 Open Cause: Overload see OMS 1813528 1813529 1811646 1811645 1813093 | November | 2020 | 2021Q2 | 2021 | ZN874:PA17 | ZN874:PA17 | ZN00874/000017 | CANADA BAY | Unknown | Not Veg | 2020-11-28 | N | 108.3214 | N | 19 | N | N | 1.1101 | 39.4971 | 150717.032
[7 empty] | 2720 | 12582 | 1811686 | 2020-11-28 17:52 | 2020-11-29 00:45 | 413 | 11kV | 1044413 | 2734 | HV | Overload | Utility Process Issue | ZS STS Primary Equip | Unplanned | Hot >35C | N | AT S9037 Miranda Panel 8 Interrupted by SOp due to OL on TX2 after failure of TX1 Abnormal Switcing: TX1 OOS and Defective 11kV DMA 975 to S9657 to S65062 OOS with S6494 Closed Cause: Panel 8 interrupted to remove load of TX2, Panel 8 also has an OL | November | 2020 | 2021Q2 | 2021 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | Exclude | Not Veg | 2020-11-28 | N | 382.0091 | N | 19 | N | N | 1.1101 | 39.4971 | 763226.2154
[7 empty] | 1776 | 1365 | 1811905 | 2020-11-29 06:29 | 2020-11-29 09:30 | 181 | 11kV | 112212 | 737 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn2196 Milperra - Pnl.26 tripped on: B & C phase IOC OH mains down corner Eldridge & Edgar See 1813352 1813354 | November | 2020 | 2021Q2 | 2021 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-11-29 | N | 152.2551 | N | 38 | Y | Y | 1.1101 | 39.4971 | 82001.2199
[7 empty] | 2272 | 7151 | 1811922 | 2020-11-29 09:57 | 2020-11-29 11:07 | 70 | 11kV | 5600 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | ZN35370 Galston Pa2 - Recloser CP3280 Tripped on OC Cause; Tree branch on OH mains near PT2061 | November | 2020 | 2021Q2 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2020-11-29 | N | 70 | N | 38 | Y | Y | 1.1101 | 39.4971 | 4092.3148
[7 empty] | 1779 | 1397 | 1811971 | 2020-11-29 09:45 | 2020-11-29 12:05 | 140 | 11kV | 140 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Hot >35C | N | LID 201377 B & C Phases Overcurrent Private network getting patrolled. | November | 2020 | 2021Q2 | 2021 |  |  |  | SINGLETON | Unknown | Not Veg | 2020-11-29 | N | 140 | N | 38 | Y | Y | 1.1101 | 39.4971 | 102.3079
[7 empty] | 2650 | 11711 | 1812066 | 2020-11-29 11:42 | 2020-11-29 12:31 | 49 | 11kV | 62648.7833 | 1302 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex Panel 2 Long Jetty CP40834 Bond burnt off CC1: 22-"Refer to SOp" | November | 2020 | 2021Q2 | 2021 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2020-11-29 | N | 48.1173 | N | 38 | Y | Y | 1.1101 | 39.4971 | 45781.883
[7 empty] | 2765 | 13322 | 1812042 | 2020-11-29 11:11 | 2020-11-29 12:35 | 84 | 11kV | 5124 | 61 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 201378 Live Line lead broken excluded OMS 1812042 | November | 2020 | 2021Q2 | 2021 | 523:33509 | 523:33509 | ZN00523/033509 | SINGLETON | OH | Not Veg | 2020-11-29 | N | 84 | N | 38 | Y | Y | 1.1101 | 39.4971 | 3744.4681
[7 empty] | 3123 | 18419 | 1811891 | 2020-11-29 09:38 | 2020-11-29 12:39 | 181 | 11kV | 186135 | 1230 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn1290 Leightonfield - pnl.11 tripped on: Earth Fault Abnormal: S8601 Sw/B Closed with S8600 Sw/A Open Suspected UG cable fault in front line section of feeder. Section was restored after previous faults but failed again. | November | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-29 | N | 151.3293 | N | 38 | Y | Y | 1.1101 | 39.4971 | 136021.9679
[7 empty] | 1911 | 2926 | 1812076 | 2020-11-29 11:50 | 2020-11-29 12:53 | 63 | 11kV | 92736 | 1472 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | At S9245 Engadine- Panel 10 Tripped on SEF Cause: 11kV Bond Failed @ AB35746 | November | 2020 | 2021Q2 | 2021 | ZN9245:PA10 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | OH | Not Veg | 2020-11-29 | N | 63 | N | 38 | Y | Y | 1.1101 | 39.4971 | 67768.7336
[7 empty] | 3175 | 19128 | 1811987 | 2020-11-29 10:35 | 2020-11-29 13:07 | 152 | 11kV | 228304 | 1502 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | At S10999 Blakehurst Panel 1 Tripped and locked out on Relays: No flag or primary fault cause. Signal: 11kV Trip Cause: Patrolled by DOp - Not related to Streetlight wire down | November | 2020 | 2021Q2 | 2021 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Veg | 2020-11-29 | N | 152 | N | 38 | Y | Y | 1.1101 | 39.4971 | 166837.8294
[7 empty] | 2278 | 7193 | 1812192 | 2020-11-29 13:01 | 2020-11-29 13:57 | 56 | 11kV | 112056 | 2001 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn10994 Mortdale - pnl.10 tripped & reclosed on: B & C phase O/C Abnormal: S10093 Elm St Sw/B Closed with AB30063 (DMA) Tree on OH mains adj LB31211 | November | 2020 | 2021Q2 | 2021 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2020-11-29 | N | 56 | N | 38 | Y | Y | 1.1101 | 39.4971 | 81887.2197
[7 empty] | 1698 | 307 | 1812199 | 2020-11-29 13:05 | 2020-11-29 15:45 | 160 | 11kV | 640 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 201386 A & B Phase DOLF : 20 Amp Excluded OMS 1812199 | November | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-11-29 | N | 160 | N | 38 | Y | Y | 1.1101 | 39.4971 | 467.6931
[7 empty] | 2993 | 16575 | 1812120 | 2020-11-29 12:19 | 2020-11-29 16:17 | 238 | 11kV | 10006 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 201385 1 fault operation A & B Phase Overcurrent Recloser set to 1 shot due o Toban. Fully patrol required. No cause found. Excluded oms 1812120. | November | 2020 | 2021Q2 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-11-29 | N | 175.5439 | N | 38 | Y | Y | 1.1101 | 39.4971 | 7312.0897
[7 empty] | 2933 | 15503 | 1812239 | 2020-11-29 13:15 | 2020-11-29 16:28 | 193 | 11kV | 6358 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 201387 1 fault operation 3 phase Overcurrent Small stick on OHM. Full patrol done ddue to Bush fire. Excluded oms 1812239. | November | 2020 | 2021Q2 | 2021 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2020-11-29 | N | 163.0256 | N | 38 | Y | Y | 1.1101 | 39.4971 | 4646.2389
[7 empty] | 2026 | 4226 | 1812399 | 2020-11-29 14:55 | 2020-11-29 17:10 | 135 | 11kV | 269001 | 2001 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Zn10994 Mortdale - Pnl.10 tripped & locked out on: Earth Fault Abnormal: S10093 Sw/B Closed with AB30063 (DMA) Cause not ascertained See 1813331 1813333 | November | 2020 | 2021Q2 | 2021 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2020-11-29 | N | 134.4333 | N | 38 | Y | Y | 1.1101 | 39.4971 | 196577.9966
[7 empty] | 2422 | 9264 | 1812606 | 2020-11-29 15:57 | 2020-11-29 17:10 | 73 | 11kV | 73 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Hot >35C | N | LID 201389 Broken Live Line Clamp Excluded OMS 1812606 | November | 2020 | 2021Q2 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-11-29 | N | 73 | N | 38 | Y | Y | 1.1101 | 39.4971 | 53.3462
[7 empty] | 3139 | 18633 | 1812797 | 2020-11-29 17:21 | 2020-11-29 17:30 | 9 | 11kV | 11205 | 1245 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | At Zn12620 Noraville Panel 7 CP41085 Fravent Main has tripped on OC and Lockout | November | 2020 | 2021Q2 | 2021 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | Unknown | Not Veg | 2020-11-29 | N | 9 | N | 38 | Y | Y | 1.1101 | 39.4971 | 8188.2835
[7 empty] | 2187 | 6139 | 1812336 | 2020-11-29 14:21 | 2020-11-29 17:50 | 209 | 11kV | 154149 | 1201 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Hot >35C | N | Zn9245 Engadine - Pnl.3 interrupted by AOp for safety 11kV mains fallen down into a tree Note: start time amended as per initial NS calls, multiple made from 14:21 See 1813532 1813533 1813534 | November | 2020 | 2021Q2 | 2021 | ZN9245:PA3 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2020-11-29 | N | 128.3505 | N | 38 | Y | Y | 1.1101 | 39.4971 | 112647.5426
[7 empty] | 1943 | 3255 | 1812454 | 2020-11-29 15:14 | 2020-11-29 18:30 | 196 | 11kV | 336959 | 1823 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 201410 Tripped locked out Mains down at pole JU-63806 feeding UGOH | November | 2020 | 2021Q2 | 2021 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2020-11-29 | N | 184.8376 | N | 38 | Y | Y | 1.1101 | 39.4971 | 246239.6986
[7 empty] | 2849 | 14370 | 1812917 | 2020-11-29 18:36 | 2020-11-29 19:49 | 73 | 33kV Distribution | 1460 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 201404 2 failt operations A Phase Earth Fault Earth wire at pole JT70898 detached from pole swinging into Fdr | November | 2020 | 2021Q2 | 2021 | 417:80504 | 417:80504 | ZN00417/080504 | NEWCASTLE | OH | Not Veg | 2020-11-29 | N | 73 | N | 38 | Y | Y | 1.1101 | 39.4971 | 1066.9249
[7 empty] | 2072 | 4881 | 1811975 | 2020-11-29 10:12 | 2020-11-29 20:20 | 608 | 11kV | 60302 | 150 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | REC46935 Ironbark Kirks 0.8 tripped on: OC Tree brought mains down near LK40954 Note: DOP reports High into low. All houses on both dist's from PT13564 checked and found in order. 2777, 2790, 2769, 2734 and NBN tower on Wisemans ferry Rd checked, no damage found. All houses on dist from PT14982 checked and found in order. 2924, 2909 and 2967 Wisemans ferry road checked, no damage found. All accessible houses checked on both distributors off PT13138. #2 Ironbark, and 2820 Wisemans Ferry checked and found in order. No access to meter boards at 2858 and 2829 Wisemans Ferry Rd (Childcare Center). | November | 2020 | 2021Q2 | 2021 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2020-11-29 | N | 402.0133 | N | 38 | Y | Y | 1.1101 | 39.4971 | 44066.923
[7 empty] | 1876 | 2527 | 1811996 | 2020-11-29 10:41 | 2020-11-29 20:20 | 578.7667 | 11kV | 9842.3 | 63 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | REC45035 Mangrove Mountain tripped on : OC OH mains down Note: Recloser in scan fail and did not indicate a trip See 1811996 1812211 CC1: 22-"Refer to SOp" | November | 2020 | 2021Q2 | 2021 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2020-11-29 | N | 156.227 | N | 38 | Y | Y | 1.1101 | 39.4971 | 7192.4625
[7 empty] | 2319 | 7750 | 1812235 | 2020-11-29 13:19 | 2020-11-29 20:47 | 448 | 11kV | 429434 | 962 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201394 A & B Phases Overcurrent Tree down near sub 12313 | November | 2020 | 2021Q2 | 2021 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2020-11-29 | N | 446.3971 | N | 38 | Y | Y | 1.1101 | 39.4971 | 313817.701
[7 empty] | 2100 | 5196 | 1812391 | 2020-11-29 20:17 | 2020-11-29 20:58 | 41 | 11kV | 738 | 18 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201399 Tree on mains Excluded OMS 1812391 | November | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-11-29 | N | 41 | N | 38 | Y | Y | 1.1101 | 39.4971 | 539.3086
[7 empty] | 2060 | 4784 | 1812948 | 2020-11-29 19:04 | 2020-11-29 21:20 | 136 | 11kV | 29784 | 219 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 201396 & 201398 C Phase Overcurrent Sw 90525 Dir OC c Phase Sw 2728 OC c Phase Please trim trees between poles IS-62830 and IS-62829. strands broken between poles IS-62829 and IS-62828. please see separate LID report for associated SUb 10620 Note: start time amended as per first NS call received Excluded OMS 1812948, 1812957, 1812953 | November | 2020 | 2021Q2 | 2021 | 235:2728 | 235:2728 | ZN00235/002728 | NEWCASTLE | OH | Veg | 2020-11-29 | N | 136 | N | 38 | Y | Y | 1.1101 | 39.4971 | 21765.2687
[7 empty] | 2288 | 7304 | 1813048 | 2020-11-29 20:36 | 2020-11-29 21:45 | 69 | 11kV | 129576 | 1904 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn874 Concord - Pnl.18 tripped on: B Phase O/C Field EFIs: S8361 S48827 S8358 S35966 S8292 S35719 S36240 S3846 S3196 Abnormal: S8451 Sw/B Closed with S35955 Sw/B Open - S7880 Sw/A closed with S7880 Sw/B Open - S7961 Sw/B Closed with S7960 Sw/A Open - S3196 Sw/B Closed with S7817 Sw/A Open (DMA) UG cable fault between S3196 Sw/A and S7817 Sw/B See 1813510 1813511 | November | 2020 | 2021Q2 | 2021 | ZN874:PA18 | ZN874:PA18 | ZN00874/000018 | CANADA BAY | UG | Not Veg | 2020-11-29 | N | 68.0546 | N | 38 | Y | Y | 1.1101 | 39.4971 | 94690.319
[7 empty] | 3140 | 18639 | 1812971 | 2020-11-29 20:03 | 2020-11-29 22:06 | 123 | 11kV | 29134 | 275 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201392 2 fault operations A & B Phases Overcurrent Excluded OMS 1812971 | November | 2020 | 2021Q2 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-11-29 | N | 105.9418 | N | 38 | Y | Y | 1.1101 | 39.4971 | 21290.2679
[7 empty] | 2385 | 8721 | 1812470 | 2020-11-29 15:14 | 2020-11-29 23:20 | 486 | 11kV | 33048 | 68 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Bluey provided makes no sense Based on load trends, pnl lost supply at 1514 and restored 2320 unknown cause Request by Ausgrid AOp. Investigate HV into LV S16405 distributor 2. DOp Andrew Creswell mkb:0408498303 on site. Only services on distributor are Sydney Water Service adjacent to next pole up from point of HV into LV also At S16405 Warringah Allambie 400A fuse blown on A B and C phase of distributor 1 Cause: Tree branch brougbht down OH - Mains down | November | 2020 | 2021Q2 | 2021 | ZN15011:PA6 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | OH | Veg | 2020-11-29 | N | 486 | N | 38 | Y | Y | 1.1101 | 39.4971 | 24150.5036
[7 empty] | 2907 | 15088 | 1812270 | 2020-11-29 13:35 | 2020-11-29 23:30 | 595 | 11kV | 199375 | 1715 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn14891 Wyong - Pnl.10 tripped on B Phase OL Field EFIs; S14857 Tree branch brought 11kV mains down in LV mains outside 165 Pollock Ave Wyong See 1813314 1813315 1813316 | November | 2020 | 2021Q2 | 2021 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2020-11-29 | N | 116.2536 | N | 38 | Y | Y | 1.1101 | 39.4971 | 145697.3694
[7 empty] | 2902 | 15018 | 1812760 | 2020-11-29 17:09 | 2020-11-29 23:40 | 391 | 11kV | 445396 | 2129 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 201409 HV wires down 11kv HV mains burnt thru where the HV UGOH lead joins onto the overhead HV mains @ 21 Lachlan Rd Cardiff. HV mains contacted LV mains below. Excluded job OMS 1812760 | November | 2020 | 2021Q2 | 2021 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2020-11-29 | N | 209.2043 | N | 38 | Y | Y | 1.1101 | 39.4971 | 325482.2598
[7 empty] | 2620 | 11297 | 1812967 | 2020-11-29 19:11 | 2020-11-30 00:03 | 292 | 11kV | 16936 | 58 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 201400 Branch removed from Fdr | November | 2020 | 2021Q2 | 2021 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-11-29 | N | 292 | N | 38 | Y | Y | 1.1101 | 39.4971 | 12376.3293
[7 empty] | 2854 | 14401 | 1812899 | 2020-11-29 18:29 | 2020-11-30 01:03 | 394 | 11kV | 64132 | 163 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201405 2 fault operations A Phase Earth Fault Falling tree struck Fdr near sub 9243 Fdr checked ok no damage found Excluded OMS 1812899 | November | 2020 | 2021Q2 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-11-29 | N | 393.4479 | N | 38 | Y | Y | 1.1101 | 39.4971 | 46865.774
[7 empty] | 3288 | 20394 | 1811876 | 2020-11-29 01:19 | 2020-11-30 02:05 | 1486 | 11kV | 89542 | 909 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn195 Pymble - Pnl.9 tripped on B phase O/C Abnormal: S4297 Sw/A Open with S2542 Sw/B Closed. LB224 closed with LB3341 Open UG cable fault between S47348, S1102 tee S5593. Note: No access to S5593 See 1813539 1813540 1813542 | November | 2020 | 2021Q2 | 2021 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2020-11-29 | N | 98.5061 | N | 38 | Y | Y | 1.1101 | 39.4971 | 65434.6526
[7 empty] | 2619 | 11290 | 1813129 | 2020-11-30 02:30 | 2020-11-30 04:01 | 91 | 11kV | 118601 | 1332 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201411 2 fault operations Possible cause car fire under Fdr Excluded OMS 1813129 | November | 2020 | 2021Q2 | 2021 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Not Veg | 2020-11-30 | N | 89.0398 | N | 7 | N | N | 1.1101 | 39.4971 | 86670.1127
[7 empty] | 2810 | 13951 | 1812699 | 2020-11-29 16:37 | 2020-11-30 05:00 | 743.3667 | 11kV | 80283.6 | 108 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 201412 & 201413 Sub 16116 B phase40A DOLF carrier burnt up And tree pull LV Distributor out of fuse assembly Excluded OMS 1812730 | November | 2020 | 2021Q2 | 2021 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2020-11-29 | N | 743.3667 | N | 38 | Y | Y | 1.1101 | 39.4971 | 58668.8869
[7 empty] | 2206 | 6324 | 1811579 | 2020-11-28 16:25 | 2020-11-30 10:00 | 2495 | 11kV | 933290 | 2321 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn1290 leightonfield - Pnl9 tripped on: A & C phase OC Abnormal: S7235 Closed with CP311 Sw/A Open - LB407 Close with S55013 Open - 11kV UGOH broken away near S7430 with LB189 closed - S5950 Closed with S7472 Open. UG cable fault between S664 and S5764 tee S1309 (N//) During restoration Pnl.16 overloaded and needed to be interrupted See 1813617 1813619 1813620 1813622 | November | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-11-28 | N | 402.1069 | N | 19 | N | N | 1.1101 | 39.4971 | 682020.8046
[7 empty] | 1769 | 1247 | 1813012 | 2020-11-29 20:27 | 2020-11-30 11:14 | 887 | 11kV | 236851 | 1073 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn9037 Miranda - Pnl.2 tripped on B Phase OC 11kV OH mains down in LV mains in Robvic Ave See 1813397 1813398 1813400 1813406 1813407 | November | 2020 | 2021Q2 | 2021 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2020-11-29 | N | 220.7372 | N | 38 | Y | Y | 1.1101 | 39.4971 | 173083.7249
[7 empty] | 1963 | 3432 | 1813392 | 2020-11-30 11:31 | 2020-11-30 12:20 | 49 | 11kV | 2646 | 54 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | PT14431 Shannon Kilkenny - Footpath phase HDO blown Lightning arrestor failed | November | 2020 | 2021Q2 | 2021 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Not Veg | 2020-11-30 | N | 49 | N | 7 | N | N | 1.1101 | 39.4971 | 1933.6188
[7 empty] | 2681 | 12164 | 1813413 | 2020-11-30 11:43 | 2020-11-30 12:35 | 52.1667 | 11kV | 1356.3333 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex Berkeley vale Pnl.24R - AB42102 opened to remove tree from 11kV CCT | November | 2020 | 2021Q2 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2020-11-30 | N | 52.1667 | N | 7 | N | N | 1.1101 | 39.4971 | 991.1684
[7 empty] | 3064 | 17586 | 1812926 | 2020-11-29 18:48 | 2020-11-30 13:46 | 1138 | 11kV | 4552 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Hot >35C | N | LID 201416 Single Phase DOLF assembly faulty requires feeder outage to repair. Excluded OMS 1812102 See report 201415 | November | 2020 | 2021Q2 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2020-11-29 | N | 1138 | N | 38 | Y | Y | 1.1101 | 39.4971 | 3326.4673
[7 empty] | 2485 | 9899 | 1813460 | 2020-11-30 13:10 | 2020-11-30 13:46 | 36 | 11kV | 1728 | 48 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201415 FAULTY DOLF AT SUB 20539 WHICH REQUIRES FEEDER OUTAGE TO REPLACE See report 201416. | November | 2020 | 2021Q2 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2020-11-30 | N | 36 | N | 7 | N | N | 1.1101 | 39.4971 | 1262.7714
[7 empty] | 3149 | 18798 | 1812210 | 2020-11-29 13:04 | 2020-11-30 14:00 | 1496 | 11kV | 42302 | 508 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Hot >35C | N | LID 201383 3 phase Overcurrent Fault 1 High set oc trip, AC oc, protection trip, A and B fault flag. (Xarm broken at sub 51575). Fault 2. Work mode set to ON. ABC O/C work mode trip. AB Fault detector Excluded oms 1812210 | November | 2020 | 2021Q2 | 2021 | 513:83504 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Not Veg | 2020-11-29 | N | 83.2717 | N | 38 | Y | Y | 1.1101 | 39.4971 | 30913.0539
[7 empty] | 2603 | 11216 | 1812749 | 2020-11-29 13:04 | 2020-11-30 14:00 | 1496 | 11kV | 4488 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 201420 DOLF : 20 Amp Burnt HV Cross Arm that caused LID outage 201383, see also oms 1812210 and 1812749. Excluded OMS 1812749 | November | 2020 | 2021Q2 | 2021 | 513:83504 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Not Veg | 2020-11-29 | N | 1496 | N | 38 | Y | Y | 1.1101 | 39.4971 | 3279.698
[7 empty] | 3180 | 19240 | 1813640 | 2020-11-30 16:32 | 2020-11-30 17:40 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201422 Single phase DOLF : 10 Amp Excluded OMS 1813640 | November | 2020 | 2021Q2 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2020-11-30 | N | 68 | N | 7 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 1888 | 2715 | 1813662 | 2020-11-30 17:44 | 2020-11-30 19:24 | 100 | 11kV | 5924 | 69 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.22 tripped on Earth Fault UG cable fault between S35664 and S5152 See 1813783 1813785 | November | 2020 | 2021Q2 | 2021 | ZN188:PA22 | ZN188:PA22 | ZN00188/000022 | SYDNEY | UG | Not Veg | 2020-11-30 | N | 85.8551 | N | 7 | N | N | 1.1101 | 39.4971 | 4329.0845
[7 empty] | 2040 | 4561 | 1813151 | 2020-11-29 22:00 | 2020-11-30 21:19 | 1398.7 | 11kV | 26571.4 | 19 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | 2 HV drop out fuses hanging from hv at PT 812 pole DU42127 Defective PT region to arrange new PT to be installed. Note: multiple calls, drop corrected based on customer calls advising part supply overnight CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | November | 2020 | 2021Q2 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2020-11-29 | N | 1398.4947 | N | 38 | Y | Y | 1.1101 | 39.4971 | 19417.5954
[7 empty] | 3046 | 17258 | 1813710 | 2020-11-30 22:12 | 2020-11-30 23:03 | 51 | 11kV | 13821 | 271 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | U/G Cable | Unplanned | No Weather Impact | N | At ZN.3425 Castle Cove,Pnl 8 CB tripped.Relays EFI,FC,No.6 trip (SPAJ 140) Cause: UG cable fault between Zn.3425 & S.4391 SW/B | November | 2020 | 2021Q2 | 2021 | ZN3425:PA8 | ZN3425:PA8 | ZN03425/000008 | WILLOUGHBY | UG | Not Veg | 2020-11-30 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 10099.9791
[7 empty] | 1972 | 3618 | 1814599 | 2020-12-01 06:58 | 2020-12-01 08:45 | 107 | 11kV | 642 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 201537 C Phase DOLF : 16 Amp Excluded OMS 1814599 | December | 2020 | 2021Q2 | 2021 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2020-12-01 | Y | 107 | N | 6 | N | Y | 1.1101 | 39.4971 | 469.1547
[7 empty] | 2595 | 11185 | 1811672 | 2020-11-28 17:42 | 2020-12-01 14:19 | 4117.3167 | 11kV | 12351.95 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | At PT2089 Bayfield Knight - 16A HDO blown on roadside phase Cause: Cause not ascertained suspect weather PT.2089 defective Customers on generators until further notice Note: as per phone calls and notepad comments on related jobs, customers did not have supply returned and were put on generators on the 1 Dec | November | 2020 | 2021Q2 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2020-11-28 | N | 4117.3167 | N | 19 | N | N | 1.1101 | 39.4971 | 9026.4407
[7 empty] | 1897 | 2781 | 1813955 | 2020-12-01 14:04 | 2020-12-01 15:26 | 82 | 11kV | 92997 | 1231 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | Zn1290 Leigthonfield - Pnl.11 tripped on: C phase IOC & OC Abnormal: S8601 Sw/B closed with S8600 Sw/A Open - LB145 closed with LB24 Open (DMA) UG cable fault in front line section of feeder betwee Pnl.11, S7614 Sw/A and S5013 Sw/A | December | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-12-01 | N | 75.5459 | N | 6 | N | N | 1.1101 | 39.4971 | 67959.4647
[7 empty] | 3187 | 19304 | 1813934 | 2020-12-01 13:22 | 2020-12-01 16:04 | 162 | 11kV | 112266 | 693 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | Y | Section of Pnl.30 Pymble Zn - Bond burnt off between S6931 and PT1522 Abnormal: S6931 Sw/B closed with AB1718 open DMA | December | 2020 | 2021Q2 | 2021 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2020-12-01 | N | 162 | N | 6 | N | N | 1.1101 | 39.4971 | 82040.6815
[7 empty] | 2404 | 9075 | 1813996 | 2020-12-01 15:30 | 2020-12-01 17:46 | 136 | 11kV | 287328 | 3495 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | Y | Zn1290 Leightonfield - Pnl.9 tripped on: C phase OC Abnormal: LB189 closed with UGOH below S7430 disconnection (DMA) - S35033 Sw/B Open with LB407 Closed - S47349 Sw/B Open with S5013 Sw/A Open (DMA) Overload - After switching Pnl.11 and 12 onto Pnl 9 due to frontline feeder fault. Apeared to be tripping at 390A instead of expected 450A, upon inspection transducer reading incorrectly and load was actually approx 70A higher than the analogue. See 1814893 1814894 1814898 1814900 1814901 1814902 1814906 | December | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2020-12-01 | N | 82.2112 | N | 6 | N | N | 1.1101 | 39.4971 | 209970.8277
[7 empty] | 1925 | 3067 | 1814021 | 2020-12-01 16:15 | 2020-12-01 18:39 | 144 | 11kV | 238690 | 2001 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | Zn10994 Mortdale - Pnl.10 tripped, reclosed & locked out on OC Abnormal: S10093 Sw/B closed with AB30063 OPen (DMA) Lightning arrestor failed at UGOH to S10675 See 1814927 1814929 1814931 | December | 2020 | 2021Q2 | 2021 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Not Veg | 2020-12-01 | N | 119.2854 | N | 6 | N | N | 1.1101 | 39.4971 | 174427.6118
[7 empty] | 1932 | 3167 | 1812409 | 2020-11-29 14:56 | 2020-12-01 19:00 | 3124 | 11kV | 153854 | 1947 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | At Zn5868 Gore Hill - Panel 14 tripped on Relays: Earth Leakage Fault check, EFI Signals: 11kV trip Cause: End Box Fault at S8002 George Place 10 See OMS 1813742 1813743 1812409 | November | 2020 | 2021Q2 | 2021 | ZN5868:PA14 | ZN5868:PA14 | ZN05868/000014 | WILLOUGHBY | UG | Not Veg | 2020-11-29 | N | 79.0211 | N | 38 | Y | Y | 1.1101 | 39.4971 | 112431.9653
[7 empty] | 2469 | 9653 | 1814080 | 2020-12-01 18:03 | 2020-12-01 19:59 | 116 | 11kV | 152349 | 1557 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn2568 St Peters - Pnl.14 tripped on: 14L Earth Fault UG cable fault between Pnl.14, S4794, S8121 & S2409 Note: Access to St Peters Zone restricted due to electronic key access | December | 2020 | 2021Q2 | 2021 | ZN2568:PA14 | ZN2568:PA14 | ZN02568/000014 | SYDNEY | UG | Not Veg | 2020-12-01 | N | 97.8478 | N | 6 | N | N | 1.1101 | 39.4971 | 111332.1557
[7 empty] | 2638 | 11547 | 1814086 | 2020-12-01 18:36 | 2020-12-01 20:07 | 91 | 11kV | 109779 | 1217 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | No Weather Impact | Y | At S965 Pennant Hills Panel 3 tripped on Relays: A phase IOC, EFI Signals: 11kV Tri[p, TX1 Group earth Cause: Tree bark has made contact with UGOH adjacent PT1069 Gunbalanya St Beecroft See OMS 1815203 1815205 1814086 | December | 2020 | 2021Q2 | 2021 | ZN965:PA3 | ZN965:PA3 | ZN00965/000003 | HORNSBY | OH | Veg | 2020-12-01 | Y | 90.2046 | N | 6 | N | Y | 1.1101 | 39.4971 | 80223.2553
[7 empty] | 2284 | 7245 | 1814440 | 2020-12-01 22:04 | 2020-12-01 22:12 | 8.25 | 11kV | 13546.5 | 1642 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | No Outage form provided for interruption Suspect PA11 @ Lake Mumorah Tripped - Confirmed by load trends | December | 2020 | 2021Q2 | 2021 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2020-12-01 | Y | 8.25 | N | 6 | N | Y | 1.1101 | 39.4971 | 9899.3826
[7 empty] | 2512 | 10231 | 1814100 | 2020-12-01 18:57 | 2020-12-01 22:30 | 213 | 11kV | 48990 | 230 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | REC555 Arcadia Park tripped Abnormal: LB62158 Closed with LB65122 Open (NAR61017) - AB2063 Closed with AB451 Open (DMA) Tree on OH mains | December | 2020 | 2021Q2 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2020-12-01 | Y | 213 | N | 6 | N | Y | 1.1101 | 39.4971 | 35800.447
[7 empty] | 3143 | 18676 | 1814387 | 2020-12-01 21:42 | 2020-12-01 22:51 | 69 | 11kV | 182538 | 2742 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201428 nothing found please arrange patrol in daylight. dq Excluded OMS 1814389 | December | 2020 | 2021Q2 | 2021 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Veg | 2020-12-01 | N | 66.5711 | N | 6 | N | N | 1.1101 | 39.4971 | 133393.3864
[7 empty] | 3284 | 20314 | 1814187 | 2020-12-01 19:04 | 2020-12-01 23:45 | 281 | 11kV | 16017 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | T11421 Bay View Carrol 0.5 centra and footpath HDO Operated 31amp Tree rbanch cause flashover at PT11421 Cleared by DOp* See OMS 1814187 1814190 | December | 2020 | 2021Q2 | 2021 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 281 | N | 6 | N | Y | 1.1101 | 39.4971 | 11704.7512
[7 empty] | 2543 | 10583 | 1814344 | 2020-12-01 21:06 | 2020-12-01 23:59 | 173 | 11kV | 256863 | 1922 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | ZS STS Primary Equip | Unplanned | Electrical Storm | Y | LID 201431 3 phase Possible protection malgrade or failure refered to L Archer via Email. dq Transfer trip from Fdtr 83732. Excluded OMS 1814386 | December | 2020 | 2021Q2 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | Exclude | Not Veg | 2020-12-01 | Y | 133.6436 | N | 6 | N | Y | 1.1101 | 39.4971 | 187707.9042
[7 empty] | 2688 | 12237 | 1814477 | 2020-12-01 22:46 | 2020-12-02 00:11 | 85 | 11kV | 3825 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201532 2 fault operations CB tripped and L/O .FDR patrolled, no fault found. Power restored 0011 2/12/20 Prot flags 51BC on leg1 | December | 2020 | 2021Q2 | 2021 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Veg | 2020-12-01 | Y | 85 | N | 6 | N | Y | 1.1101 | 39.4971 | 2795.1972
[7 empty] | 2682 | 12184 | 1814493 | 2020-12-01 23:19 | 2020-12-02 01:58 | 159 | 11kV | 33231 | 209 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201496 3 phase CB 48002 trip and LO , tree on mains P HS-53213 power restored at 0158 Prot flags B ph O/C OMS 1814493## | December | 2020 | 2021Q2 | 2021 | 502:48002 | 502:48002 | ZN00502/048002 | MAITLAND | OH | Veg | 2020-12-01 | Y | 159 | N | 6 | N | Y | 1.1101 | 39.4971 | 24284.2347
[7 empty] | 1935 | 3194 | 1814197 | 2020-12-01 19:47 | 2020-12-02 02:25 | 398 | 11kV | 333325 | 877 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Lightning | Y | Zn12690 Berkeley Vale - Pnl.7 tripped, reclosed and locked out on: B & C phase OC 1st UGOH out from zone failed explosively. | December | 2020 | 2021Q2 | 2021 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | Unknown | Unknown | 2020-12-01 | Y | 380.0741 | N | 6 | N | Y | 1.1101 | 39.4971 | 243584.0786
[7 empty] | 2573 | 10884 | 1814207 | 2020-12-01 19:51 | 2020-12-02 03:45 | 474 | 11kV | 4266 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | Y | At ZN.12610 Long Jetty, Pnl 22 CB tripped. Relays EFI,IOC,B ph OC,FC,LO Cause: cause not ascertained. Suspect fault in UGOH See OMS 1815242, 1814207,1814230 | December | 2020 | 2021Q2 | 2021 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 474 | N | 6 | N | Y | 1.1101 | 39.4971 | 3117.467
[7 empty] | 3132 | 18529 | 1814191 | 2020-12-01 19:46 | 2020-12-02 04:00 | 493.7667 | 11kV | 38020.0333 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | No LID report raised. Multiple events in the area due to widespread storm. Multiple calls from customers | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-12-01 | Y | 493.7667 | N | 6 | N | Y | 1.1101 | 39.4971 | 27783.919
[7 empty] | 2529 | 10376 | 1814329 | 2020-12-01 21:04 | 2020-12-02 07:00 | 596 | 11kV | 7152 | 12 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Date/Time User Note 02/12/20 10:10 t46306 Dop reports HDO replace and customers restored @ 0700 02/12/2020 | December | 2020 | 2021Q2 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2020-12-01 | Y | 596 | N | 6 | N | Y | 1.1101 | 39.4971 | 5226.4707
[7 empty] | 2877 | 14667 | 1814090 | 2020-12-01 20:03 | 2020-12-02 07:20 | 677 | 11kV | 28434 | 42 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At PT1069 Gnabalanya St B phase HDO operated Cause: Weather related Note: customers also impacted prior to this by feeder event at 01/12/2020 18:36, refer to OMS 1815203 See OMS 1814793 1814466 1814346 1814090 | December | 2020 | 2021Q2 | 2021 | ZN965:PA3 | ZN965:PA3 | ZN00965/000003 | HORNSBY | OH | Not Veg | 2020-12-01 | Y | 677 | N | 6 | N | Y | 1.1101 | 39.4971 | 20778.7285
[7 empty] | 2202 | 6311 | 1814499 | 2020-12-01 23:49 | 2020-12-02 07:45 | 476 | 11kV | 7616 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 201534 A Phase DOLF : 10 Amp Excluded OMS 1814499 | December | 2020 | 2021Q2 | 2021 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2020-12-01 | Y | 476 | N | 6 | N | Y | 1.1101 | 39.4971 | 5565.5482
[7 empty] | 2022 | 4193 | 1814441 | 2020-12-01 22:04 | 2020-12-02 08:23 | 619 | 11kV | 25998 | 42 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | Y | LID 201535 A Phase DOLF : 31 Amp Excluded OMS 1814441 Note: start date amended to first call in advising power issues | December | 2020 | 2021Q2 | 2021 | 508:82576 | 508:82576 | ZN00508/082576 | PORT STEPHENS | OH | Not Veg | 2020-12-01 | Y | 619 | N | 6 | N | Y | 1.1101 | 39.4971 | 18998.5716
[7 empty] | 1956 | 3380 | 1814458 | 2020-12-01 22:17 | 2020-12-02 09:30 | 673 | 11kV | 2019 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 201538 A Phase DOLF : 10 Amp Excluded OMS 1814458 | December | 2020 | 2021Q2 | 2021 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2020-12-01 | Y | 673 | N | 6 | N | Y | 1.1101 | 39.4971 | 1475.4256
[7 empty] | 2064 | 4794 | 1814541 | 2020-12-02 03:46 | 2020-12-02 09:40 | 354 | 11kV | 215208 | 1590 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn129 Hunters Hill Panel 57 Tripped on Relays: B phase IOC, Earth Fault, EFI Cauise: UG cable fault from S48279 Eltham Gerrish to S4670 Penrose Burns to S5585 Best Bridge - Tee PT1638 See OMS 1814834 1814835 1814541 1814570 18145731814546 | December | 2020 | 2021Q2 | 2021 | ZN129:PA57 | ZN129:PA57 | ZN00129/000057 | LANE COVE | UG | Not Veg | 2020-12-02 | N | 135.3509 | N | 15 | N | N | 1.1101 | 39.4971 | 157267.6588
[7 empty] | 2703 | 12352 | 1814528 | 2020-12-02 02:11 | 2020-12-02 10:00 | 469 | 11kV | 10318 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201434 A & C Phase DOLF : 16 Amp replaced A & C phace line dolfs 747869( 16amp) & 74431(10 amp) Excluded oms 1814528 | December | 2020 | 2021Q2 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-12-02 | N | 469 | N | 15 | N | N | 1.1101 | 39.4971 | 7540.0901
[7 empty] | 3167 | 19045 | 1814682 | 2020-12-02 09:06 | 2020-12-02 10:10 | 64 | 11kV | 192 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Replace C phase DOLF - 10A at PT - 48090. Supply restored 10.10 Am. Job complete. Note: unable to locate LID report | December | 2020 | 2021Q2 | 2021 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2020-12-02 | N | 64 | N | 15 | N | N | 1.1101 | 39.4971 | 140.3079
[7 empty] | 1733 | 687 | 1814510 | 2020-12-02 00:34 | 2020-12-02 10:35 | 600.8833 | 11kV | 4206.1833 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201435 B & C Phase DOLF : 10 Amp Replaced blown HV fuses at LF40679. Supply restored. | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-12-02 | N | 600.8833 | N | 15 | N | N | 1.1101 | 39.4971 | 3073.7547
[7 empty] | 3196 | 19354 | 1814425 | 2020-12-01 22:02 | 2020-12-02 11:05 | 783 | 11kV | 3132 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 201439 C Phase DOLF : 10 Amp Excluded OMS 1814425 | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-12-01 | Y | 783 | N | 6 | N | Y | 1.1101 | 39.4971 | 2288.7732
[7 empty] | 3071 | 17668 | 1814253 | 2020-12-01 20:19 | 2020-12-02 11:30 | 911 | 11kV | 166562 | 187 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201559 Tree on mains PoleGT-43308,GT-43309,GT-43342 Prot O/C Excluded OMS 1814609## | December | 2020 | 2021Q2 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2020-12-01 | Y | 890.7059 | N | 6 | N | Y | 1.1101 | 39.4971 | 121718.5969
[7 empty] | 2055 | 4759 | 1814482 | 2020-12-01 23:05 | 2020-12-02 11:45 | 760.2833 | 11kV | 13685.1 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201542 B Phase DOLF Blown DOLF | December | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-12-01 | Y | 760.2833 | N | 6 | N | Y | 1.1101 | 39.4971 | 10000.6674
[7 empty] | 2193 | 6203 | 1814309 | 2020-12-01 20:55 | 2020-12-02 11:48 | 893 | 11kV | 5358 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 201485 Burnt off tapping at Pole LK 6009 caused by storm on the 01/12/20, with first call of outage received at 2055. ABS was interupted at 0935 on 2/12/2020 to allow repairs with the power being restored at 1148 excluded OMS 1814309## | December | 2020 | 2021Q2 | 2021 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2020-12-01 | Y | 893 | N | 6 | N | Y | 1.1101 | 39.4971 | 3915.4684
[7 empty] | 2623 | 11307 | 1814200 | 2020-12-01 19:51 | 2020-12-02 12:15 | 984 | 11kV | 20664 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 201441 section isolated for repairs to broken x-arms & , mains down sub 59059 | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-12-01 | Y | 984 | N | 6 | N | Y | 1.1101 | 39.4971 | 15100.6417
[7 empty] | 1758 | 968 | 1814436 | 2020-12-01 22:00 | 2020-12-02 12:20 | 860 | 11kV | 49880 | 58 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 201480 C Phase no protection devices operated -blown tapping found at 11kV Recloser 61054. Recloser bypassed at 1220. excluded OMS 1814602## | December | 2020 | 2021Q2 | 2021 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2020-12-01 | Y | 860 | N | 6 | N | Y | 1.1101 | 39.4971 | 36450.8328
[7 empty] | 2382 | 8654 | 1814087 | 2020-12-01 18:36 | 2020-12-02 12:22 | 1066 | 11kV | 403714 | 2225 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At Zn9245 Engadine Panel 13 tripped, reclosed, and locked out on OC/EF Relay 50 TBC, Reclose Lockout,EFI Cause: Lightning strike LB35744 to S9814 tee S9240 Engadine Pump HVC UGOH in Fairview Ave Near Cutler Rd See OMS 1815236 1815240 1815244 1815254 1814087 Note: PA9 tripped during fault restoration | December | 2020 | 2021Q2 | 2021 | ZN9245:PA13 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Not Veg | 2020-12-01 | Y | 181.4445 | N | 6 | N | Y | 1.1101 | 39.4971 | 295022.2837
[7 empty] | 3195 | 19345 | 1814523 | 2020-12-01 23:59 | 2020-12-02 13:13 | 794 | 11kV | 2382 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | Replaced blown HV fuses at sub 52979. 11KV feeder already restored. | December | 2020 | 2021Q2 | 2021 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2020-12-01 | Y | 794 | N | 6 | N | Y | 1.1101 | 39.4971 | 1740.6953
[7 empty] | 2987 | 16444 | 1814485 | 2020-12-01 23:09 | 2020-12-02 13:15 | 846 | 11kV | 11844 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201446 B & C Phase DOLF : 20 Amp replaced 3 x HV Fuses. Excluded oms 1814485 | December | 2020 | 2021Q2 | 2021 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2020-12-01 | Y | 846 | N | 6 | N | Y | 1.1101 | 39.4971 | 8655.2459
[7 empty] | 2376 | 8628 | 1814412 | 2020-12-01 21:47 | 2020-12-02 13:28 | 940.9 | 11kV | 24463.4 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201550 A Phase DOLF : 10 Amp Blown DOLF | December | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-12-01 | Y | 940.9 | N | 6 | N | Y | 1.1101 | 39.4971 | 17877.1312
[7 empty] | 1774 | 1353 | 1814410 | 2020-12-01 21:42 | 2020-12-02 13:41 | 959 | 11kV | 360917 | 1327 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201568 2 fault operations 33kv mains came down into the 11kv mains at pole IR-72843 Prot flags Z2 trip AB O/C Excluded OMS 1814544## | December | 2020 | 2021Q2 | 2021 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2020-12-01 | Y | 271.9797 | N | 6 | N | Y | 1.1101 | 39.4971 | 263747.4984
[7 empty] | 2457 | 9532 | 1814307 | 2020-12-01 20:52 | 2020-12-02 14:50 | 1078 | 11kV | 4312 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201555 B Phase DOLF : 20 Amp Blown DOLF Excluded OMS 1814307 | December | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-12-01 | Y | 1078 | N | 6 | N | Y | 1.1101 | 39.4971 | 3151.0824
[7 empty] | 2230 | 6669 | 1814747 | 2020-12-02 10:25 | 2020-12-02 14:50 | 265 | 11kV | 265 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | Replaced blown HV fuse on PT sub. Note: no lid report raised from control room, job re-entered based on notepad comments on related record | December | 2020 | 2021Q2 | 2021 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2020-12-02 | N | 265 | N | 15 | N | N | 1.1101 | 39.4971 | 193.6542
[7 empty] | 2834 | 14241 | 1814567 | 2020-12-02 05:51 | 2020-12-02 14:59 | 548 | 11kV | 334985 | 2120 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Previous Storm | N | At Zn.12610 Long Jetty, AOp opened Pnl.13 CB for safety reasons. Cause: Interrupted for safety reasons. Crossarm burnt through & on 45deg angle,11kV close to coming down onto LV mains. See OMS 1816922,1816948,1816935 | December | 2020 | 2021Q2 | 2021 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2020-12-02 | N | 158.0118 | N | 15 | N | N | 1.1101 | 39.4971 | 244797.1576
[7 empty] | 2926 | 15379 | 1814603 | 2020-12-02 07:05 | 2020-12-02 15:00 | 475 | 11kV | 1425 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201551 A Phase DOLF : 10 Amp Replaced blown DOLF at PT - 2549 c phase 10A. Found blown B phase line fuse 79849, which could not be replaced from ground. Also found centre phase insulator broken on head bracket on main line at line fuse pole - 79849. Crew required for repairs. DOLF carrier left hanging on fence. S02 has been notified. Note: unable to locate a LID report and customers advised NS since the storm on the 1st | December | 2020 | 2021Q2 | 2021 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-12-02 | N | 475 | N | 15 | N | N | 1.1101 | 39.4971 | 1041.348
[7 empty] | 3135 | 18589 | 1814752 | 2020-12-02 10:32 | 2020-12-02 15:10 | 278 | 11kV | 278 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201557 Replace blown DOLF B phase 10A at PT - 78321. Supply restored at 15.10. Job complete Note: No LID identified, record based on customer calls, and notepad comments | December | 2020 | 2021Q2 | 2021 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2020-12-02 | N | 278 | N | 15 | N | N | 1.1101 | 39.4971 | 203.1542
[7 empty] | 2556 | 10651 | 1814786 | 2020-12-02 11:07 | 2020-12-02 15:10 | 243 | 11kV | 1701 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201556 A Phase DOLF : 10 Amp Blown HV fuse. Attended by Adam Pople. EDWINA - WOODBURY PTY LTD EC attended this morning, fuses down and 1 phase tripped. Pumps running water to livestock and sheds not working. Clear access. 02/12/20 13:13: Please ring before as its rutral and they wont see you arrive Edwina 0418494292 Note: no LID report located | December | 2020 | 2021Q2 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2020-12-02 | N | 243 | N | 15 | N | N | 1.1101 | 39.4971 | 1243.0406
[7 empty] | 2891 | 14830 | 1814266 | 2020-12-01 20:28 | 2020-12-02 15:20 | 1132.5 | 11kV | 113250 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201573 supply was restored by DO | December | 2020 | 2021Q2 | 2021 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2020-12-01 | Y | 1132.5 | N | 6 | N | Y | 1.1101 | 39.4971 | 82759.7597
[7 empty] | 1971 | 3611 | 1814165 | 2020-12-01 19:27 | 2020-12-02 15:49 | 1222 | 11kV | 160176 | 134 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | iR49506 Springs Rd tripped on OC Weather related. Patrolled OK See 1817670 1817671 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-12-01 | Y | 1195.3433 | N | 6 | N | Y | 1.1101 | 39.4971 | 117051.8964
[7 empty] | 2626 | 11377 | 1814774 | 2020-12-02 10:52 | 2020-12-02 15:51 | 299 | 11kV | 598 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201475 B Phase DOLF B phase dolf carrier opened, no fuse blown. Susppect not fully closed and dropped out in wind dq Excluded OMS 1814774 | December | 2020 | 2021Q2 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-12-02 | N | 299 | N | 15 | N | N | 1.1101 | 39.4971 | 437.0008
[7 empty] | 2468 | 9639 | 1814153 | 2020-12-01 19:21 | 2020-12-02 16:30 | 1269 | 11kV | 133146 | 267 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN14143 Somersby the Panel 17 has tripped on Relays: B and C phase OC, EF Signals: 11kV Trip @1907 01/12/2020 Ex Somersby Pa17 Recloser CP45202 Pacific Ashbrook 2.0 Tripped on Cause: OH wind related SW/A Closed at S76820, SW/A Open at S14458 Tree on Mains near AB43180 1817693/692/694/695/696/697/699/705/706/708/710 1814136 1814153 1814506 1814992 1815030 | December | 2020 | 2021Q2 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 498.6742 | N | 6 | N | Y | 1.1101 | 39.4971 | 97299.1697
[7 empty] | 3283 | 20250 | 1814832 | 2020-12-02 12:19 | 2020-12-02 16:30 | 251 | 11kV | 251 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201479 Single phase DOLF : 10 Amp Excluded OMS 1814832 | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-02 | N | 251 | N | 15 | N | N | 1.1101 | 39.4971 | 183.4234
[7 empty] | 1938 | 3221 | 1814322 | 2020-12-01 20:43 | 2020-12-02 16:35 | 1192 | 11kV | 460942 | 1265 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | Zn12620 Noraville - Pnl.8 tripped & reclosed on: ABC phase OC Bonds burnt off at USL43866 and AB40933 See 1815237 1815238 1815239 | December | 2020 | 2021Q2 | 2021 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2020-12-01 | Y | 364.381 | N | 6 | N | Y | 1.1101 | 39.4971 | 336842.8181
[7 empty] | 2824 | 14086 | 1814957 | 2020-12-02 15:29 | 2020-12-02 17:30 | 121 | 11kV | 847 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201482 A Phase DOLF : 10 Amp Excluded OMS 1814957 | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-12-02 | N | 121 | N | 15 | N | N | 1.1101 | 39.4971 | 618.9626
[7 empty] | 2574 | 10889 | 1814974 | 2020-12-01 23:59 | 2020-12-02 17:50 | 1071 | 11kV | 2142 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 201489 A Phase DOLF : 10 Amp Excluded OMS 1814974 Customers never regained supply after the feeder was restored refer to call on OMS 1814523 | December | 2020 | 2021Q2 | 2021 | 512:83732 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2020-12-01 | Y | 1071 | N | 6 | N | Y | 1.1101 | 39.4971 | 1565.3104
[7 empty] | 1816 | 1804 | 1814685 | 2020-12-02 09:09 | 2020-12-02 18:55 | 586 | 11kV | 1172 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 201490 DOLF Excluded OMS 1814685 | December | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-12-02 | N | 586 | N | 15 | N | N | 1.1101 | 39.4971 | 856.463
[7 empty] | 2815 | 13998 | 1814988 | 2020-12-02 17:00 | 2020-12-02 19:00 | 120 | 11kV | 1080 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201484 3 phase section of 11kV fdr from ABS 63017 interupted for emergency tree removal dq | December | 2020 | 2021Q2 | 2021 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2020-12-02 | N | 120 | N | 15 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 3026 | 17029 | 1814179 | 2020-12-01 19:36 | 2020-12-02 19:40 | 1444 | 11kV | 610383 | 1392 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn13000 Lake Munmorah - Pnl.2 tripped, reclosed and locked out Tree on OH mains adj PT64430 See 1817676 1817677 | December | 2020 | 2021Q2 | 2021 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 438.4935 | N | 6 | N | Y | 1.1101 | 39.4971 | 446049.8931
[7 empty] | 3219 | 19604 | 1814137 | 2020-12-01 19:22 | 2020-12-02 20:30 | 1508 | 11kV | 133446 | 343 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | Y | At ZN.12630 Peats Ridge,Pnl.10 CB Fdr tripped, EF,EFI. Cause: Tree/branch on OH mains. Tree on OH just past LB 48995 See OMS 1817951,1817593,1817597,1817601,1817602,1817604,1817606,,1817608, 1814137,1814141 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 389.0554 | N | 6 | N | Y | 1.1101 | 39.4971 | 97518.4008
[7 empty] | 2966 | 16163 | 1814108 | 2020-12-01 19:07 | 2020-12-02 22:15 | 1628 | 11kV | 873396 | 618 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Ex Somersby Pa17 Recloser CP45202 Pacific Ashbrook 2.0 Tripped on Cause: OH wind related - SW/A Closed at S76820, SW/A Open at S14458 Tree on Mains near AB43180 and also 1 phase of HV in 1 bay had come down into LV near#2 Point Rd (Mooney Mooney on PT12458 resulting in delayed restoration to PT12458. Removed tree and Restrung hv. EMSO Inspected 8 premises around #2 Point Rd (1,3,5,7,9,14,19,22,24-25,26-27,28,29,31,33) and found all in order.. At eastern end of Point Rd pole #BR 50 service insulators pulled away are pulled away. | December | 2020 | 2021Q2 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 1413.2621 | N | 6 | N | Y | 1.1101 | 39.4971 | 638252.036
[7 empty] | 1824 | 1863 | 1815002 | 2020-12-01 22:07 | 2020-12-02 22:45 | 1478 | 11kV | 5912 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 201494 DOLF : 10 Amp Excluded OMS 1814446 | December | 2020 | 2021Q2 | 2021 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2020-12-01 | Y | 1478 | N | 6 | N | Y | 1.1101 | 39.4971 | 4320.3152
[7 empty] | 2979 | 16326 | 1814633 | 2020-12-01 20:00 | 2020-12-03 04:05 | 1925 | 11kV | 459253 | 276 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 201498 3 fault operations Earth Fault Note: multiple customers advising supply lost since approx 8pm on the 1st | December | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-12-01 | Y | 1663.9601 | N | 6 | N | Y | 1.1101 | 39.4971 | 335608.5467
[7 empty] | 2676 | 12070 | 1815071 | 2020-12-03 03:34 | 2020-12-03 05:04 | 90 | 11kV | 67492 | 1044 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | LID 201499 Possum at base of UGOH pole JU-61251, tapping blown to OHM, suspect UG cable requires test, report water main leaking in footpath since fault. refer to OMS 1815071 Note: also see later job OMS 1815397, customers off sub 22802 interrupted again as part of switching | December | 2020 | 2021Q2 | 2021 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | OH | Not Veg | 2020-12-03 | N | 64.6475 | N | 3 | N | N | 1.1101 | 39.4971 | 49321.1629
[7 empty] | 1759 | 973 | 1814119 | 2020-12-01 19:13 | 2020-12-03 09:10 | 2277 | 11kV | 179428 | 125 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC61375 Wise Ferry Biara 1.27 tripped on OC Tree brought mains down beteen PT49014 and PT12179 See 1817666 1817667 1817668 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 1435.424 | N | 6 | N | Y | 1.1101 | 39.4971 | 131120.6902
[7 empty] | 3100 | 18141 | 1814483 | 2020-12-01 22:57 | 2020-12-03 09:34 | 2077 | 11kV | 85443 | 138 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201430 3 phase Earth Fault; Overcurrent earth wire down @ pole MT-30220 Section isolated for repairs. See LID 201440. Excluded oms 1814483 | December | 2020 | 2021Q2 | 2021 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2020-12-01 | Y | 619.1522 | N | 6 | N | Y | 1.1101 | 39.4971 | 62439.2243
[7 empty] | 1834 | 2033 | 1815081 | 2020-12-02 02:44 | 2020-12-03 12:00 | 1996 | 11kV | 7984 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 201539 sub isolated for tx replacement. | December | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-12-02 | N | 1996 | N | 15 | N | N | 1.1101 | 39.4971 | 5834.4717
[7 empty] | 3240 | 19736 | 1814106 | 2020-12-01 19:03 | 2020-12-03 13:39 | 2556 | 11kV | 498774 | 199 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC45013 Gunderman tripped on OC Tree brought down mains in 2 locations. 1. Between AB42632 and AB43179. 2. Between USL42686 and USL42515 See 1817661 1817662 1817663 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-12-01 | Y | 2506.402 | N | 6 | N | Y | 1.1101 | 39.4971 | 364489.3279
[7 empty] | 2821 | 14066 | 1815273 | 2020-12-03 11:58 | 2020-12-03 15:10 | 192 | 11kV | 9216 | 48 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 201561 SW 42090 tripped while trying to restore dolfs @ sub 52778 Found faulty lightning arrestor at sub 52777 replaced arrestor and restored supply | December | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2020-12-03 | N | 192 | N | 3 | N | N | 1.1101 | 39.4971 | 6734.781
[7 empty] | 2374 | 8591 | 1814221 | 2020-12-01 19:23 | 2020-12-03 15:37 | 2654 | 11kV | 438494 | 397 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 201493 and LID 201497 Sensitive Earth Fault 2 fault operations HV Mains down pole WB91956 | December | 2020 | 2021Q2 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2020-12-01 | Y | 1104.5189 | N | 6 | N | Y | 1.1101 | 39.4971 | 320438.4818
[7 empty] | 2491 | 9968 | 1814127 | 2020-12-01 19:15 | 2020-12-03 17:45 | 2790 | 11kV | 147000 | 54 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Recloser CP44945 Lower Mangrove tripped OC & LO Cause: Weather related.-,storm see OMS 1817022,1817022,1817023 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2020-12-01 | Y | 2722.2222 | N | 6 | N | Y | 1.1101 | 39.4971 | 107423.2642
[7 empty] | 2699 | 12333 | 1815413 | 2020-12-03 20:00 | 2020-12-03 20:10 | 10 | 11kV | 330 | 33 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Between CP3847 & CP40343 interrupted for safety to remove tree branch. Cause: Interrupted for Safety reasons See OMS 1815521, 1815413 | December | 2020 | 2021Q2 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2020-12-03 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 2255 | 6919 | 1815015 | 2020-12-01 19:21 | 2020-12-03 20:23 | 2942 | 11kV | 5884 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | Y | PT18366 Jones Peats 0.7 - Paddock side HDO blew Lightning arrestor failed Note: customers had LV since storm on the 1st refer to related jobs also 1817699 | December | 2020 | 2021Q2 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-12-01 | Y | 2942 | N | 6 | N | Y | 1.1101 | 39.4971 | 4299.8537
[7 empty] | 2297 | 7447 | 1815427 | 2020-12-04 06:08 | 2020-12-04 09:15 | 187 | 11kV | 187 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201580 Single phase DOLF : 10 Amp Excluded OMS 1815427 | December | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-12-04 | N | 187 | N | 8 | N | N | 1.1101 | 39.4971 | 136.6541
[7 empty] | 2568 | 10807 | 1814616 | 2020-12-04 08:28 | 2020-12-04 10:30 | 122 | 11kV | 122 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Previous Storm | N | LID 201579 33kV fdr issue, 11kV fdr out for safety clearance Lighting strike on pole on 2nd Dec causing damage on 33kV insulator on section of 33kV from Williamtown to stockton under access with NAR 64957. PD | December | 2020 | 2021Q2 | 2021 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2020-12-04 | N | 122 | N | 8 | N | N | 1.1101 | 39.4971 | 89.154
[7 empty] | 3029 | 17063 | 1815442 | 2020-12-04 08:18 | 2020-12-04 11:00 | 162 | 11kV | 13446 | 83 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | No Weather Impact | N | Between S.10676 & AB 31321 interrupted by DOp. Cause: Interrupted for safety reasons to repair burnt off bond at AB 31321. | December | 2020 | 2021Q2 | 2021 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2020-12-04 | N | 162 | N | 8 | N | N | 1.1101 | 39.4971 | 9825.9402
[7 empty] | 3254 | 19849 | 1815429 | 2020-12-04 06:46 | 2020-12-04 13:30 | 404 | 11kV | 462812 | 1601 | HV | Animal Bird | Animal | UGOH | Unplanned | Snow / Hail Storm | N | 11kV CB Zn10994 Mortdale Tripped on Signals: 11kV trip, TX3 Group Earth Relays: 50TN- Earth fault, OC A and B phase EFI Cause: The 11kV UGOH abovee S49678 Charles Rosa has been blown up by a crow Cause 2: Burnt off Bond at CP31321 Abnromal Switching: AB31103 Is closed, CP31321 Open and Defective See OMS 1817774 1817775 1817779 1815429 1815430 1815514 1817682 | December | 2020 | 2021Q2 | 2021 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2020-12-04 | N | 289.0768 | N | 8 | N | N | 1.1101 | 39.4971 | 338209.359
[7 empty] | 2370 | 8539 | 1816694 | 2020-12-04 05:00 | 2020-12-04 17:15 | 735 | 11kV | 1470 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201584 Single phase DOLF : 10 Amp No OMS. reported directly to depot. | December | 2020 | 2021Q2 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2020-12-04 | N | 735 | N | 8 | N | N | 1.1101 | 39.4971 | 1074.2326
[7 empty] | 3280 | 20208 | 1815665 | 2020-12-04 17:49 | 2020-12-04 18:41 | 52 | 11kV | 1612 | 31 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 201586 interrupt to replace cracked insulator pole JR55043 Excluded OMS 1815665 | December | 2020 | 2021Q2 | 2021 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2020-12-04 | N | 52 | N | 8 | N | N | 1.1101 | 39.4971 | 1178.0021
[7 empty] | 3079 | 17772 | 1815695 | 2020-12-04 22:31 | 2020-12-05 01:15 | 164 | 11kV | 191925 | 1814 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.18 tripped on C phase O/C Abnormal: S65993 Sw/A Closed with S4328 Sw/B Open (DMA) UG cable fault between S1688 and S8056 S4328 Anderson Leyland - Dist #2 - LV parallel failure during feeder trip. Restored via LV // - fuses replaced at 1315. See 1816364 1816365 1816366 | December | 2020 | 2021Q2 | 2021 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-12-04 | N | 105.8021 | N | 8 | N | N | 1.1101 | 39.4971 | 140253.1292
[7 empty] | 1852 | 2258 | 1815687 | 2020-12-04 23:45 | 2020-12-05 01:50 | 125 | 11kV | 7125 | 57 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 201588 interrupt to repair broken 33kV crossarm pole HR80481 fdr KU4 Excluded oms 1815687 | December | 2020 | 2021Q2 | 2021 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2020-12-04 | N | 125 | N | 8 | N | N | 1.1101 | 39.4971 | 5206.7398
[7 empty] | 3169 | 19087 | 1815714 | 2020-12-05 03:05 | 2020-12-05 05:17 | 132 | 11kV | 307998 | 2586 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.3 tripped on: Earth Fault UG cable fault in front line section of feeder between Pnl.3, S77728, S8811 & S49242 See 1816323 | December | 2020 | 2021Q2 | 2021 | ZN35600:PA3 | ZN35600:PA11 | ZN35600/000011 | RANDWICK | UG | Not Veg | 2020-12-05 | N | 119.1021 | N | 10 | N | N | 1.1101 | 39.4971 | 225075.854
[7 empty] | 2246 | 6807 | 1815875 | 2020-12-05 20:38 | 2020-12-05 21:25 | 47 | 11kV | 39903 | 849 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Zn12570 Avoca - Pnl.34 tripped on B & C phase IOC Tree on OH mains near PT12363 Francis Duncan. | December | 2020 | 2021Q2 | 2021 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2020-12-05 | N | 47 | N | 10 | N | N | 1.1101 | 39.4971 | 29159.9355
[7 empty] | 3052 | 17353 | 1815869 | 2020-12-05 19:29 | 2020-12-05 22:30 | 181 | 11kV | 181 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201601 Singlwe phase DOLF : 10 Amp Excluded OMS 1815869 | December | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-12-05 | N | 181 | N | 10 | N | N | 1.1101 | 39.4971 | 132.2695
[7 empty] | 3269 | 20050 | 1815912 | 2020-12-05 22:06 | 2020-12-05 23:06 | 60 | 11kV | 108540 | 1809 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | At ZN.129 Hunters Hill, Pnl 64 CB tripped,reclosed,tripped & locked out. Cause: Tree/branch on OH mains o/s 302 Pittwater Rd. See OMS 1815912, 1815944, 1815924, 1815923 | December | 2020 | 2021Q2 | 2021 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2020-12-05 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 79317.8306
[7 empty] | 1721 | 516 | 1815898 | 2020-12-05 21:41 | 2020-12-05 23:48 | 127 | 11kV | 33822 | 276 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 201602 Patrol requested | December | 2020 | 2021Q2 | 2021 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | OH | Veg | 2020-12-05 | N | 122.5435 | N | 10 | N | N | 1.1101 | 39.4971 | 24716.12
[7 empty] | 3037 | 17208 | 1815903 | 2020-12-05 22:01 | 2020-12-05 23:54 | 113 | 11kV | 85089 | 753 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | At ZN.9037 Miranda, Pnl.8 CB tripped & reclosed. Cause: Tree/branch on OH mains adjacent to AB 35181 Abnormal Switching: SW.B open at S.9292 See OMS 1815903, 1815907 | December | 2020 | 2021Q2 | 2021 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Veg | 2020-12-05 | N | 113 | N | 10 | N | N | 1.1101 | 39.4971 | 62180.5315
[7 empty] | 2081 | 4971 | 1815933 | 2020-12-05 22:27 | 2020-12-06 01:26 | 179 | 11kV | 101066 | 702 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201603 1 fault operation A & B Phase Overcurrent tree removed from OHM pole AH-20052 also 11kV link 74658 hot joint - DMA'd Excluded OMS 1815933 | December | 2020 | 2021Q2 | 2021 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Veg | 2020-12-05 | N | 143.9687 | N | 10 | N | N | 1.1101 | 39.4971 | 73856.0519
[7 empty] | 1981 | 3698 | 1815899 | 2020-12-05 21:43 | 2020-12-06 02:05 | 262 | 11kV | 53342 | 293 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201604 Patrol found nothing 1 Fault operation Pole Mounted RAGCB, Overcurrent | December | 2020 | 2021Q2 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-12-05 | N | 182.0546 | N | 10 | N | N | 1.1101 | 39.4971 | 38980.7603
[7 empty] | 1889 | 2721 | 1815901 | 2020-12-05 21:45 | 2020-12-06 03:17 | 332 | 11kV | 28636 | 115 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201606 2 fault operations 3 phase Overcurrent tree brought down 11kV OHM at pole SM70027/26 Excluded OMS 1815901 | December | 2020 | 2021Q2 | 2021 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2020-12-05 | N | 249.0087 | N | 10 | N | N | 1.1101 | 39.4971 | 20926.3442
[7 empty] | 2338 | 8105 | 1815972 | 2020-12-06 02:14 | 2020-12-06 09:15 | 421 | 11kV | 2526 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | PT1585 South Pacific Cowan - footpath pahse HDO blown Lightning / surge arrestor blown clear | December | 2020 | 2021Q2 | 2021 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2020-12-06 | N | 421 | N | 4 | N | N | 1.1101 | 39.4971 | 1845.9263
[7 empty] | 2930 | 15489 | 1815996 | 2020-12-06 08:21 | 2020-12-06 10:25 | 124 | 11kV | 372 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At PT12263 Wise Ferry Hensons 1.5 Middle PHase HDO Blown Cause not ascertained for outage See OMS 1816877 1816000 1815996 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2020-12-06 | N | 124 | N | 4 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 2262 | 7027 | 1815994 | 2020-12-06 08:15 | 2020-12-06 15:25 | 430.15 | 11kV | 9463.3 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201620 Wires down between poles AH-82524 and AH-82521 Customer reports of low volts beyond | December | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-12-06 | N | 430.15 | N | 4 | N | N | 1.1101 | 39.4971 | 6915.5005
[7 empty] | 3118 | 18386 | 1815942 | 2020-12-05 22:35 | 2020-12-06 15:30 | 1015 | 11kV | 18630 | 63 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REC46895 Wise Ferry Ironbark - tripped on SEL Abnormal: Rec out of scan SCADA DMA 11kV OH mains down between outside 2931 Wise Ferry Rd | December | 2020 | 2021Q2 | 2021 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2020-12-05 | N | 295.7143 | N | 10 | N | N | 1.1101 | 39.4971 | 13614.2545
[7 empty] | 3189 | 19316 | 1816136 | 2020-12-06 21:12 | 2020-12-07 02:15 | 303 | 11kV | 70217 | 933 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201622 2 fault operations Line Impedence pole fire pole IS35133 - 33kV Fdr 83241 Sw 81204 - A prot L1, L2, L3 line diff, B prot L/O relay Sw 83241 - A prot L2 -L3 line diff 7.5km; B prot B-C diff 9.05km S.O de-enegised 11kV Sw 2124 Excluded oms 1816136 | December | 2020 | 2021Q2 | 2021 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Veg | 2020-12-06 | N | 75.2594 | N | 4 | N | N | 1.1101 | 39.4971 | 51312.5125
[7 empty] | 1862 | 2384 | 1816164 | 2020-12-07 06:57 | 2020-12-07 09:18 | 141 | 11kV | 118722 | 842 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Long Jetty Pnl.7 - Bond burnt off LB44652 | December | 2020 | 2021Q2 | 2021 | ZN12610:PA7 | ZN12610:PA7 | ZN12610/000007 | CENTRAL COAST | OH | Not Veg | 2020-12-07 | N | 141 | N | 2 | N | N | 1.1101 | 39.4971 | 86758.5359
[7 empty] | 3098 | 18105 | 1816204 | 2020-12-07 09:08 | 2020-12-07 11:47 | 159 | 11kV | 186782 | 3928 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35555 Croydon - Pnl.20 tripped on A Phase OC Note: EFIs @ S49765 & S46285 did not work hence - Pnl.5 tripped on A & B Phase OC during restoration switching UG cable fault between S49765 Sw/A, S6318 Sw/B tee S1907 See 1817616 1817617 1817618 1817620 1817621 | December | 2020 | 2021Q2 | 2021 | ZN35555:PA20 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | UG | Not Veg | 2020-12-07 | N | 47.5514 | N | 2 | N | N | 1.1101 | 39.4971 | 136494.7765
[7 empty] | 2903 | 15021 | 1816524 | 2020-12-08 01:05 | 2020-12-08 03:10 | 125 | 11kV | 23643 | 198 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn14891 Wyong - Pnl.19 tripped, reclosed & locked out on: A & B phase OC Possum at base of UGOH above S46804 See 1817260 1817261 1817263 | December | 2020 | 2021Q2 | 2021 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | OH | Not Veg | 2020-12-08 | N | 119.4091 | N | 7 | N | N | 1.1101 | 39.4971 | 17277.607
[7 empty] | 1827 | 1884 | 1816532 | 2020-12-08 02:03 | 2020-12-08 03:44 | 101 | 11kV | 131755 | 1389 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn15001 Brookvale - Pnl.6 tripped on: A & B phase IOC Cause not ascertained See 1817178 1817179 | December | 2020 | 2021Q2 | 2021 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Veg | 2020-12-08 | N | 94.856 | N | 7 | N | N | 1.1101 | 39.4971 | 96282.6679
[7 empty] | 2359 | 8357 | 1816538 | 2020-12-08 06:22 | 2020-12-08 09:40 | 198 | 11kV | 198 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 201632 A Phase Broken Live Line Clamp | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-12-08 | N | 198 | N | 7 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 1732 | 644 | 1816591 | 2020-12-08 09:30 | 2020-12-08 12:05 | 155 | 11kV | 775 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 201633 Burnt off tapping line side of L/F 74993. Excluded OMS 1816591, 1816541 | December | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-12-08 | N | 155 | N | 7 | N | N | 1.1101 | 39.4971 | 566.3471
[7 empty] | 2701 | 12342 | 1816728 | 2020-12-08 14:12 | 2020-12-08 14:59 | 47 | 11kV | 5781 | 123 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 201634 Broken xarm pole FO-30073. Excluded OMS 1816659 | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-12-08 | N | 47 | N | 7 | N | N | 1.1101 | 39.4971 | 4224.5843
[7 empty] | 2341 | 8132 | 1816748 | 2020-12-08 16:30 | 2020-12-08 17:20 | 50 | 11kV | 2550 | 51 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex Berkeley Vale Onl.24 - AB40033 interrutped to remove tree from HV CCT and LV mains | December | 2020 | 2021Q2 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2020-12-08 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 1863.4648
[7 empty] | 2360 | 8359 | 1816821 | 2020-12-08 20:29 | 2020-12-08 21:25 | 56 | 11kV | 672 | 12 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 201636 B Phase insulator/ CT assembley faield at Device 42131 Standen Drive Pole Caps, these caps have been ooos for a seperte fault not attended to since July 2018. It appears there is no plan to repair this pole cap, so it will continue to fall apart and cause future problems. If it is not needed and will never be repaired please consider removing it. Excluded OMS 1816821 | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-12-08 | N | 56 | N | 7 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 2544 | 10596 | 1816829 | 2020-12-09 01:13 | 2020-12-09 05:50 | 277 | 11kV | 39645 | 187 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201678 2 Fault Operation B & C Phase Overcurrent Excluded OMS 1816829 | December | 2020 | 2021Q2 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2020-12-09 | N | 212.0053 | N | 5 | N | N | 1.1101 | 39.4971 | 28971.3967
[7 empty] | 2010 | 4012 | 1816981 | 2020-12-09 13:09 | 2020-12-09 19:28 | 379 | 11kV | 400956 | 1472 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15011 Beacon Hill - Panel 2 Tripped on Signals: Panel 2 A phase Trip, A phase OC, Neutral, OC, EF B phase OC, IOC, EF, Reclose EF, Reclose Lockout, EFI Cause: Outside 35 Roosevelt Ave Alambie Heights - HV into LV Secondary Fault: Burnt off Bond @ AB20521 See OMS 1817577 1817578 1817057 1816981 1817053 | December | 2020 | 2021Q2 | 2021 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2020-12-09 | N | 272.3886 | N | 5 | N | N | 1.1101 | 39.4971 | 293006.8186
[7 empty] | 2189 | 6151 | 1816954 | 2020-12-09 14:50 | 2020-12-09 19:30 | 280 | 11kV | 27720 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 201646 SW was opened by DOP due to unstable tree being ID'D C Collard | December | 2020 | 2021Q2 | 2021 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2020-12-09 | N | 280 | N | 5 | N | N | 1.1101 | 39.4971 | 20256.9584
[7 empty] | 2892 | 14832 | 1817089 | 2020-12-09 11:30 | 2020-12-09 20:45 | 555 | 11kV | 555 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201648 B & C Phase DOLF : 10 Amp Excluded OMS 1817089 | December | 2020 | 2021Q2 | 2021 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2020-12-09 | N | 555 | N | 5 | N | N | 1.1101 | 39.4971 | 405.5776
[7 empty] | 1761 | 1024 | 1817123 | 2020-12-09 22:42 | 2020-12-10 00:17 | 95 | 11kV | 163210 | 1718 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201652 2 fault operations B & C Phase Overcurrent | December | 2020 | 2021Q2 | 2021 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Veg | 2020-12-09 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 119269.0541
[7 empty] | 2453 | 9520 | 1817196 | 2020-12-10 09:48 | 2020-12-10 10:50 | 62 | 11kV | 124 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 201653 Blown L/A on sub 59074 Excluded OMS 1817196 | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-12-10 | N | 62 | N | 9 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 2358 | 8334 | 1817239 | 2020-12-10 11:26 | 2020-12-10 11:37 | 11 | 11kV | 14795 | 1345 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn10995 Riverwood - Pnl.12 tripped on C phase IOC Balloons tangled in 11kV above AB31240 | December | 2020 | 2021Q2 | 2021 | ZN10995:PA12 | ZN10995:PA12 | ZN10995/000012 | GEORGES RIVER | OH | Veg | 2020-12-10 | N | 11 | N | 9 | N | N | 1.1101 | 39.4971 | 10811.7496
[7 empty] | 2440 | 9435 | 1817184 | 2020-12-10 09:30 | 2020-12-10 16:30 | 420 | 11kV | 16696 | 59 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | REC44945 Lower Mangrove - tripped on OC Cause not ascertained See 1817743 1817744 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-12-10 | N | 282.9831 | N | 9 | N | N | 1.1101 | 39.4971 | 12200.9444
[7 empty] | 3158 | 18911 | 1817391 | 2020-12-10 15:47 | 2020-12-10 17:20 | 93 | 11kV | 71424 | 768 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8100 Green Square - Pnl.20 tripped on: Earth Fault UG cable fault in front line section of feeder | December | 2020 | 2021Q2 | 2021 | ZN8100:PA20 | ZN384:PA68 | ZN00384/000068 | SYDNEY | UG | Not Veg | 2020-12-10 | N | 93 | N | 9 | N | N | 1.1101 | 39.4971 | 52194.5525
[7 empty] | 2530 | 10392 | 1817422 | 2020-12-10 16:25 | 2020-12-10 18:10 | 105 | 11kV | 65337 | 733 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Lightning | N | REC40425 Kurrawyba Cadell tripped on OC PT18550 Tx appears to have been struck by lightning See 1817731 1817732 | December | 2020 | 2021Q2 | 2021 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2020-12-10 | N | 89.1364 | N | 9 | N | N | 1.1101 | 39.4971 | 47746.3525
[7 empty] | 2377 | 8630 | 1817445 | 2020-12-10 17:13 | 2020-12-10 19:05 | 112 | 11kV | 336 | 3 | HV | Animal Goanna | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201659 B Phase DOLF : 10 Amp Goanna | December | 2020 | 2021Q2 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2020-12-10 | N | 112 | N | 9 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 2706 | 12383 | 1817463 | 2020-12-10 18:29 | 2020-12-10 19:06 | 37 | 11kV | 24272 | 656 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC46673 Terrigal Penrose tripped, reclosed and locked out on: OC Tree on OH mains near USL42501 | December | 2020 | 2021Q2 | 2021 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2020-12-10 | N | 37 | N | 9 | N | N | 1.1101 | 39.4971 | 17737.2617
[7 empty] | 1849 | 2251 | 1817399 | 2020-12-10 15:57 | 2020-12-10 19:10 | 193 | 11kV | 25695 | 141 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201657 2 fault operation A Phase FI | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-12-10 | N | 182.234 | N | 9 | N | N | 1.1101 | 39.4971 | 18777.1481
[7 empty] | 3272 | 20080 | 1817401 | 2020-12-10 16:00 | 2020-12-10 19:48 | 228 | 11kV | 136642 | 1823 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 201660 Blown 11kV tapping JU66537 Excluded OMS 1817401 | December | 2020 | 2021Q2 | 2021 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2020-12-10 | N | 74.9545 | N | 9 | N | N | 1.1101 | 39.4971 | 99853.9433
[7 empty] | 3103 | 18207 | 1817509 | 2020-12-11 02:59 | 2020-12-11 08:30 | 331 | 11kV | 26618 | 174 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 201661 2 Fault Operations 3 phase Overcurrent; Earth Fault 11kV mains down pole AI-90367. Excluded OMS 1817514. | December | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-12-11 | N | 152.977 | N | 4 | N | N | 1.1101 | 39.4971 | 19451.6493
[7 empty] | 1775 | 1360 | 1817607 | 2020-12-11 09:42 | 2020-12-11 11:45 | 123 | 11kV | 1845 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT50019 Warnervale Virginia - Footpath phase HDO blown Fuse fatigue | December | 2020 | 2021Q2 | 2021 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2020-12-11 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 1348.2716
[7 empty] | 1940 | 3225 | 1817698 | 2020-12-11 12:32 | 2020-12-11 13:48 | 76 | 11kV | 199535 | 2702 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.26 tripped on: Earth Fault UG cable fault between S5857 and S5719 See 1817735 1817766 | December | 2020 | 2021Q2 | 2021 | ZN2568:PA26 | ZN2568:PA26 | ZN02568/000026 | INNER WEST | UG | Not Veg | 2020-12-11 | N | 73.8472 | N | 4 | N | N | 1.1101 | 39.4971 | 145814.2927
[7 empty] | 2471 | 9686 | 1817711 | 2020-12-11 12:52 | 2020-12-11 15:05 | 133 | 11kV | 21679 | 163 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | At S.1595 Morrice River West,C phase 40A HV fuse operated. Cause: Vehicle hit pole. Truck clipped DW accross St at cnr of Morrice & River Rd. See OMS 1818402, 1817711 | December | 2020 | 2021Q2 | 2021 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | OH | Not Veg | 2020-12-11 | N | 133 | N | 4 | N | N | 1.1101 | 39.4971 | 15842.3738
[7 empty] | 2329 | 7932 | 1817953 | 2020-12-13 05:55 | 2020-12-13 07:20 | 85 | 11kV | 163968 | 2164 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2835 Burwood Panel 15 Tripped on Relays: Earth leakage Cause: 11kV Feeder fault from S5717 to S6630 to S2256 See OMS 1818171 1818173 1817953 | December | 2020 | 2021Q2 | 2021 | ZN2835:PA15 | ZN2835:PA15 | ZN02835/000015 | STRATHFIELD | UG | Not Veg | 2020-12-13 | N | 75.7708 | N | 3 | N | N | 1.1101 | 39.4971 | 119822.9782
[7 empty] | 2692 | 12282 | 1817990 | 2020-12-13 13:11 | 2020-12-13 13:57 | 46 | 11kV | 13984 | 304 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN630 Mascot Panel 10 tripped on Relays: Timed O/C, E/F and EFI Signals: 11kV Trip Cause: 11kV UG feeder fault from ZN630 Mascot Panel 10 to S49987 to S6547 to S6258 | December | 2020 | 2021Q2 | 2021 | ZN630:PA10 | ZN630:PA10 | ZN00630/000010 | SYDNEY | UG | Not Veg | 2020-12-13 | N | 46 | N | 3 | N | N | 1.1101 | 39.4971 | 10219.0947
[7 empty] | 3282 | 20228 | 1817982 | 2020-12-13 13:45 | 2020-12-13 16:40 | 175 | 11kV | 700 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201677 retension mains between poles ES-34924 & ES 34925 Excluded OMS 1817986 | December | 2020 | 2021Q2 | 2021 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2020-12-13 | N | 175 | N | 3 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 2210 | 6385 | 1818047 | 2020-12-14 02:02 | 2020-12-14 03:48 | 106 | 11kV | 424 | 4 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Berkeley Vale ZN12690:PA1 suspected underground cable fault in feeder from panel 1 to S14732 swB to S 14500 sw F | December | 2020 | 2021Q2 | 2021 | ZN12690:PA1 | ZN12690:PA1 | ZN12690/000001 | CENTRAL COAST | UG | Not Veg | 2020-12-14 | N | 106 | N | 5 | N | N | 1.1101 | 39.4971 | 309.8467
[7 empty] | 2941 | 15650 | 1818057 | 2020-12-14 06:38 | 2020-12-14 07:15 | 37 | 11kV | 148 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201675 B Phase DOLF : 31 Amp fuse breakdown dq Excluded oms 1818057 | December | 2020 | 2021Q2 | 2021 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Veg | 2020-12-14 | N | 37 | N | 5 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 1904 | 2845 | 1818063 | 2020-12-14 06:53 | 2020-12-14 08:05 | 72 | 11kV | 68284 | 2083 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn847 Hornsby Panel 36 Tripped on Relays: Earth Fault with fault check. Cause: Cable fault between S4383 Patterson Romsey to S8109 to S5157 See OMS 1818219 1818220 1818221 1818063 | December | 2020 | 2021Q2 | 2021 | ZN847:PA36 | ZN847:PA36 | ZN00847/000036 | HORNSBY | UG | Not Veg | 2020-12-14 | N | 32.7816 | N | 5 | N | N | 1.1101 | 39.4971 | 49899.9332
[7 empty] | 2117 | 5309 | 1818246 | 2020-12-14 19:35 | 2020-12-14 20:44 | 69 | 11kV | 1035 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | Recloser CP48045 Myoora Chilkes GCC operated. Cause: 11kV OH cable left with 1 strand between Rec CP48045 & CP40509 CC1: 22-"Refer to SOp" CC2: 23-"Mains Required" FRC1: 300-"Specify details by voice" FRC2: 300-"Specify details by voice" | December | 2020 | 2021Q2 | 2021 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2020-12-14 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 756.3475
[7 empty] | 2428 | 9314 | 1818299 | 2020-12-14 23:46 | 2020-12-15 01:26 | 100 | 11kV | 148140 | 3643 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At ZN.15001 Brookvale,Pnl 2 R CB tripped Relays: O/C & EF 50T A&C Field EFI: nil At CP62936 A&B phase OC inidcations Cause: Tree branch contact Tree on mains Ryan Pl,11kV bond of LB 62936 & pole FF44186 see OMS 1819106,1818299,1819108 | December | 2020 | 2021Q2 | 2021 | ZN15001:PA2 | ZN15001:PA2 | ZN15001/000002 | NORTHERN BEACHES | OH | Veg | 2020-12-14 | N | 40.6643 | N | 5 | N | N | 1.1101 | 39.4971 | 108256.3426
[7 empty] | 2700 | 12339 | 1818328 | 2020-12-15 06:57 | 2020-12-15 08:50 | 113 | 11kV | 226 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT14113 Tall Timbers STW Centra Phase 50A HDOs operated Cause: Fuse Fatigue - Replaced By DOp See OMS 1819232 1818328 | December | 2020 | 2021Q2 | 2021 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Not Veg | 2020-12-15 | N | 113 | N | 5 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 3050 | 17339 | 1818321 | 2020-12-15 05:57 | 2020-12-15 11:40 | 343 | 11kV | 1715 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 201692 B Phase DOLF : 10 Amp Excluded OMS 1818321 | December | 2020 | 2021Q2 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-12-15 | N | 343 | N | 5 | N | N | 1.1101 | 39.4971 | 1253.2714
[7 empty] | 2289 | 7375 | 1818419 | 2020-12-15 10:40 | 2020-12-15 16:00 | 320 | 11kV | 33203 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S35370 Galston - Panel 4 Recloser CP428 Bayfield Rd has tripped on overcurrent CP450 Is Open and Defective, CP2063 Closed Cause: Tree brought down OH @ 5 Geelans Rd Acacia See OMS 1819221 1819220 1818480 1818479 1818421 1818419 | December | 2020 | 2021Q2 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2020-12-15 | N | 101.2287 | N | 5 | N | N | 1.1101 | 39.4971 | 24263.7731
[7 empty] | 2986 | 16414 | 1818484 | 2020-12-15 14:58 | 2020-12-15 17:15 | 137 | 11kV | 10275 | 75 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 201699 3 Phase FDR isolated for repairs of broken 33kv pin at pole KT20180. please see related Reports 33kv LID 201697/ OMS 1818684 11kv T+R LID 201698/ OMS 1818685 Excluded OMS 1818483 | December | 2020 | 2021Q2 | 2021 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2020-12-15 | N | 137 | N | 5 | N | N | 1.1101 | 39.4971 | 7508.6669
[7 empty] | 2021 | 4148 | 1818554 | 2020-12-15 18:03 | 2020-12-16 00:16 | 373 | 11kV | 15126 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 201700 A Phase Sensitive Earth fault 11kv mains down from sw 5839 to pole FS11703, section isolated for repairs. Excluded OMS 1818554 | December | 2020 | 2021Q2 | 2021 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2020-12-15 | N | 360.1429 | N | 5 | N | N | 1.1101 | 39.4971 | 11053.6347
[7 empty] | 1983 | 3703 | 1818626 | 2020-12-16 03:46 | 2020-12-16 09:00 | 314 | 11kV | 9734 | 31 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT18023 Neera Lace Roadside 50K HDO has operated but failed to Drop Cause: Animal/Birds | December | 2020 | 2021Q2 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2020-12-16 | N | 314 | N | 14 | N | N | 1.1101 | 39.4971 | 7113.3201
[7 empty] | 2717 | 12557 | 1818641 | 2020-12-16 03:44 | 2020-12-16 12:30 | 526 | 11kV | 301256 | 2449 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12570 Avoca Panel 12 Tripped and reclosed on IOC - A and B phase, Lockout Cause: Tree brach on OH See OMS 1819272 1819274 1819275 1819276 1819277 1819278 1819268 1818743 1818742 | December | 2020 | 2021Q2 | 2021 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2020-12-16 | N | 123.0118 | N | 14 | N | N | 1.1101 | 39.4971 | 220148.9993
[7 empty] | 3015 | 16845 | 1818622 | 2020-12-16 05:30 | 2020-12-16 12:50 | 440.3167 | 11kV | 24217.4167 | 55 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 201709 Isolation to repair Pole 4G-40016 broken X-arm . | December | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-12-16 | N | 440.3167 | N | 14 | N | N | 1.1101 | 39.4971 | 17697.3738
[7 empty] | 1885 | 2642 | 1818734 | 2020-12-16 10:31 | 2020-12-16 13:10 | 159 | 11kV | 159 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At S14143 Somersby PT47788 Old Sydney Town No2 Footpath HDO 16K Operated Cause Fuse Fatigue | December | 2020 | 2021Q2 | 2021 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2020-12-16 | N | 159 | N | 14 | N | N | 1.1101 | 39.4971 | 116.1925
[7 empty] | 1760 | 1012 | 1818788 | 2020-12-16 12:37 | 2020-12-16 14:10 | 93 | 11kV | 93 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 201716 A Phase DOLF : 10 Amp Excluded OMS 1818788 | December | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-12-16 | N | 93 | N | 14 | N | N | 1.1101 | 39.4971 | 67.9617
[7 empty] | 2764 | 13321 | 1818904 | 2020-12-16 17:25 | 2020-12-16 19:55 | 150 | 11kV | 1050 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201722 C Phase DOLF : 20 Amp Thunderstorm Excluded OMS 1818904 | December | 2020 | 2021Q2 | 2021 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2020-12-16 | N | 150 | N | 14 | N | N | 1.1101 | 39.4971 | 767.309
[7 empty] | 2286 | 7279 | 1818681 | 2020-12-16 12:39 | 2020-12-16 20:02 | 443 | 11kV | 50813 | 138 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 201720 interrupt to repair UGOH KT 40097 to sub 15491 Excluded OMS 1818681 | December | 2020 | 2021Q2 | 2021 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | Unknown | Unknown | 2020-12-16 | N | 368.2101 | N | 14 | N | N | 1.1101 | 39.4971 | 37132.6417
[7 empty] | 3153 | 18841 | 1818919 | 2020-12-16 18:40 | 2020-12-16 21:40 | 180 | 11kV | 720 | 4 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | PT13531 Kyola Mangrove Dam 2.6 - Roadside phase HDO blown Suspect lightning | December | 2020 | 2021Q2 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-12-16 | N | 180 | N | 14 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 2439 | 9384 | 1818931 | 2020-12-16 20:06 | 2020-12-16 22:50 | 164 | 11kV | 1968 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201725 Single phase DOLF : 20 Amp Excluded OMS 1818931 | December | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-12-16 | N | 164 | N | 14 | N | N | 1.1101 | 39.4971 | 1438.1564
[7 empty] | 1941 | 3232 | 1818948 | 2020-12-16 21:31 | 2020-12-16 23:14 | 103 | 11kV | 618 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201733 interrupt to repair LLC lead Excluded oms 1818948 | December | 2020 | 2021Q2 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2020-12-16 | N | 103 | N | 14 | N | N | 1.1101 | 39.4971 | 451.6162
[7 empty] | 2263 | 7035 | 1818942 | 2020-12-16 20:27 | 2020-12-16 23:42 | 195 | 11kV | 27105 | 139 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201730 Overcurrent on Device HC74436 and also LID 201734 A & C Phase DOLF : 10 Amp sub 73235 from 16/12/20 20:27 to 16/12/20 23:13 Note: customer also affected by Trip and Reclose on Feeder on device HC74436 see OMS 1818942 @ p16/12/2020 20:27 | December | 2020 | 2021Q2 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2020-12-16 | N | 195 | N | 14 | N | N | 1.1101 | 39.4971 | 19807.5345
[7 empty] | 1822 | 1857 | 1818943 | 2020-12-16 20:44 | 2020-12-17 01:00 | 256 | 11kV | 1024 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201735 DOLF : 10 Amp Excluded OMS 1818943 | December | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2020-12-16 | N | 256 | N | 14 | N | N | 1.1101 | 39.4971 | 748.309
[7 empty] | 2228 | 6666 | 1818963 | 2020-12-16 23:46 | 2020-12-17 02:55 | 189 | 11kV | 17299 | 139 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 201736 2 Fault Operation Earth Fault broken isulator at pole 7L-50516 Excluded oms 1818963 | December | 2020 | 2021Q2 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2020-12-16 | N | 124.4532 | N | 14 | N | N | 1.1101 | 39.4971 | 12641.599
[7 empty] | 1780 | 1400 | 1818910 | 2020-12-16 17:40 | 2020-12-17 04:02 | 621.7 | 11kV | 40410.5 | 65 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201718 Lightning has struck pole AK32067 and split pole. | December | 2020 | 2021Q2 | 2021 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2020-12-16 | N | 621.7 | N | 14 | N | N | 1.1101 | 39.4971 | 29530.8015
[7 empty] | 2178 | 6028 | 1818966 | 2020-12-17 00:49 | 2020-12-17 11:25 | 636 | 11kV | 77809 | 171 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201737 2 Operations Earth Fault 11kV on Cross Arm at Sub 51983 | December | 2020 | 2021Q2 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2020-12-17 | N | 455.0234 | N | 14 | N | N | 1.1101 | 39.4971 | 56860.5222
[7 empty] | 2002 | 3848 | 1819018 | 2020-12-17 08:48 | 2020-12-17 11:25 | 157 | 11kV | 157 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201740 10 Amp Single Phase Substation DOLF Faulty LA replaced | December | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2020-12-17 | N | 157 | N | 14 | N | N | 1.1101 | 39.4971 | 114.731
[7 empty] | 2845 | 14335 | 1819026 | 2020-12-17 09:04 | 2020-12-17 12:50 | 226 | 11kV | 452 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201743 A phase 10 Amp Substation DOLF | December | 2020 | 2021Q2 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-12-17 | N | 226 | N | 14 | N | N | 1.1101 | 39.4971 | 330.3083
[7 empty] | 1859 | 2322 | 1819083 | 2020-12-17 10:56 | 2020-12-17 13:10 | 134 | 11kV | 268 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201744 C phase 10 Amp Substation DOLF | December | 2020 | 2021Q2 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2020-12-17 | N | 134 | N | 14 | N | N | 1.1101 | 39.4971 | 195.8465
[7 empty] | 2224 | 6639 | 1819039 | 2020-12-17 09:32 | 2020-12-17 13:35 | 243 | 11kV | 243 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201746 3 Amp single Phase substation DOLF | December | 2020 | 2021Q2 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2020-12-17 | N | 243 | N | 14 | N | N | 1.1101 | 39.4971 | 177.5772
[7 empty] | 3177 | 19171 | 1819195 | 2020-12-17 16:29 | 2020-12-17 16:57 | 28 | 11kV | 55384 | 1978 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn10991 Blakehurst - Pnl.7 tripped on C phase IOC Balloon into 11kV at 87 Woniora Rd | December | 2020 | 2021Q2 | 2021 | ZN10991:PA7 | ZN10991:PA7 | ZN10991/000007 | GEORGES RIVER | OH | Veg | 2020-12-17 | N | 28 | N | 14 | N | N | 1.1101 | 39.4971 | 40472.9936
[7 empty] | 1738 | 762 | 1818986 | 2020-12-17 07:15 | 2020-12-17 18:00 | 645 | 11kV | 10166 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 201739 16 Amp A and B Phase Line DOLF Tree on mains and broken pole at Pole 6O-70045 | December | 2020 | 2021Q2 | 2021 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2020-12-17 | N | 221 | N | 14 | N | N | 1.1101 | 39.4971 | 7429.013
[7 empty] | 3246 | 19762 | 1819165 | 2020-12-17 15:39 | 2020-12-17 18:06 | 147 | 11kV | 305822 | 2739 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201752 No Cause found Earth Fault Note: customer called advising lightning strike on pole near Oakdale Rd and Dudley Rd intersection note: Network in abnormal state, SW 2062 Closed, and SW43092 Open | December | 2020 | 2021Q2 | 2021 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2020-12-17 | N | 111.6546 | N | 14 | N | N | 1.1101 | 39.4971 | 223485.6974
[7 empty] | 2492 | 9979 | 1819210 | 2020-12-17 16:57 | 2020-12-17 18:43 | 106 | 11kV | 154193 | 1560 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN2568 ST PETERS 11kV CB Panel 14 tripped on left leg timed OC, SPAJ 140c relay 6 trip, EFI Cause: UG Fault between Zn2568 St Peters to S4794 to S8121 to S2409 See 1820722,3,4 Ex 1819210 | December | 2020 | 2021Q2 | 2021 | ZN2568:PA14 | ZN2568:PA14 | ZN02568/000014 | SYDNEY | UG | Not Veg | 2020-12-17 | N | 98.8417 | N | 14 | N | N | 1.1101 | 39.4971 | 112679.6965
[7 empty] | 2024 | 4210 | 1819230 | 2020-12-17 17:45 | 2020-12-17 20:00 | 135 | 11kV | 141489 | 1577 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN15004 NEWPORT 11kV CB Panel 9 'S16880 Bishop Bardo ETC' fdr tripped on Signals: 11kv trip, Zone Earth Relays: 50TA, Fault CHeck, EFI Cause: UGOH fault short ciricuit Suspect UGOH between AB21783 to S16868 SwA to S16681 SwB tee PT15467 Hillside Rd 22 See 1820706,7,8 Ex 1819230,3,6 | December | 2020 | 2021Q2 | 2021 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | Unknown | Unknown | 2020-12-17 | N | 89.7204 | N | 14 | N | N | 1.1101 | 39.4971 | 103395.988
[7 empty] | 2657 | 11835 | 1819196 | 2020-12-17 16:33 | 2020-12-17 22:20 | 346.7333 | 11kV | 22537.6667 | 65 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | refer to: LID 201754 and LID 201755 11kV 80 Amp B Fuse replace HV blown Bph 80 sub fuse at sub 21191. Interrupt 11kV section to replace HV sub fuse and for 33kV pin replacement | December | 2020 | 2021Q2 | 2021 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Veg | 2020-12-17 | N | 346.7333 | N | 14 | N | N | 1.1101 | 39.4971 | 16469.8621
[7 empty] | 2828 | 14111 | 1819226 | 2020-12-17 19:24 | 2020-12-17 22:54 | 210 | 11kV | 66500 | 380 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 201754 and LID 201755 11kV 80 Amp B Fuse Sw 3635 Line Diff A,B-N Sw 3431 Line Diff A, B-N repair broken pin insulator JV-41246 and replace HV blown Bph 80 A sub fuse at sub 21191. Interrupt 11kV section to replace HV sub fuse and for 33kV pin replacement | December | 2020 | 2021Q2 | 2021 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2020-12-17 | N | 175 | N | 14 | N | N | 1.1101 | 39.4971 | 48596.2386
[7 empty] | 2261 | 6984 | 1819300 | 2020-12-17 22:16 | 2020-12-17 23:10 | 54 | 11kV | 594 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | PT1752 QUARRY ELOUERA RESERVE Road Side HDO operated 31A Fuse replaced Cause: not ascertained See 1820730 ex 1819300 | December | 2020 | 2021Q2 | 2021 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2020-12-17 | N | 54 | N | 14 | N | N | 1.1101 | 39.4971 | 434.0777
[7 empty] | 2325 | 7878 | 1819308 | 2020-12-18 03:05 | 2020-12-18 08:43 | 338 | 11kV | 135612 | 1226 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1290 Leightonfield - Pnl.11 tripped on Earth Fault UG cable fault in front line section of feeder | December | 2020 | 2021Q2 | 2021 | ZN1290:PA11 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-12-18 | N | 110.6134 | N | 14 | N | N | 1.1101 | 39.4971 | 99101.2497
[7 empty] | 2851 | 14385 | 1819364 | 2020-12-18 09:28 | 2020-12-18 10:49 | 81 | 11kV | 32319 | 399 | HV | Overload Operational | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Section of St Peters Pnl.14 interrupted due to overloading of Pnl.43 Zetland Abnormal: Pnl.14 front line UG cable fault - S62254 Closed with S2409 Open | December | 2020 | 2021Q2 | 2021 | ZN2568:PA14 | ZN2568:PA14 | ZN02568/000014 | SYDNEY | Unknown | Not Veg | 2020-12-18 | N | 81 | N | 14 | N | N | 1.1101 | 39.4971 | 23617.772
[7 empty] | 1716 | 446 | 1819423 | 2020-12-18 11:47 | 2020-12-18 13:55 | 128 | 11kV | 128 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201766 10 Amp, single phase, substation DOLF | December | 2020 | 2021Q2 | 2021 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2020-12-18 | N | 128 | N | 14 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 1873 | 2473 | 1819247 | 2020-12-17 18:26 | 2020-12-18 15:45 | 1279 | 11kV | 162483 | 1275 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Zn15005 Belrose - Pnl.6 tripped on B Phase OC 11kV Pole FF88974 snapped half way down See 1820753 1820754 | December | 2020 | 2021Q2 | 2021 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2020-12-17 | N | 127.4376 | N | 14 | N | N | 1.1101 | 39.4971 | 118737.784
[7 empty] | 1766 | 1164 | 1819476 | 2020-12-18 14:47 | 2020-12-18 16:24 | 97 | 11kV | 211261 | 2293 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35555 Croydon - Pnl.13 tripped on: C Phase IOC UG cable fault in frontline section of feeder See 1821378 | December | 2020 | 2021Q2 | 2021 | ZN35555:PA13 | ZN35555:PA13 | ZN35555/000013 | INNER WEST | UG | Not Veg | 2020-12-18 | N | 92.133 | N | 14 | N | N | 1.1101 | 39.4971 | 154383.3077
[7 empty] | 2144 | 5627 | 1819464 | 2020-12-18 13:44 | 2020-12-18 17:20 | 216 | 11kV | 432 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201774 10Amp, single phase, substation DOLF | December | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-12-18 | N | 216 | N | 14 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 2754 | 13222 | 1819471 | 2020-12-18 14:24 | 2020-12-18 17:20 | 176 | 11kV | 528 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201773 10Amp, single phase, substation DOLF | December | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-12-18 | N | 176 | N | 14 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 2630 | 11436 | 1819482 | 2020-12-18 15:25 | 2020-12-18 17:35 | 130.1167 | 11kV | 2732.45 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201771 20Amp A Phase Line DOLF | December | 2020 | 2021Q2 | 2021 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2020-12-18 | N | 130.1167 | N | 14 | N | N | 1.1101 | 39.4971 | 1996.7939
[7 empty] | 2308 | 7605 | 1819534 | 2020-12-18 18:44 | 2020-12-18 20:30 | 106 | 11kV | 212 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201777 C phase, 10Amp, substation DOLF | December | 2020 | 2021Q2 | 2021 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2020-12-18 | N | 106 | N | 14 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 1706 | 392 | 1819490 | 2020-12-18 15:53 | 2020-12-18 21:40 | 347 | 11kV | 694 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201772 10Amp, Single Phase, substation DOLF | December | 2020 | 2021Q2 | 2021 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2020-12-18 | N | 347 | N | 14 | N | N | 1.1101 | 39.4971 | 507.1547
[7 empty] | 2408 | 9126 | 1819562 | 2020-12-18 20:36 | 2020-12-18 21:55 | 79 | 11kV | 158 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201778 C phase 10Amp, substation DOLF | December | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-12-18 | N | 79 | N | 14 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 2848 | 14365 | 1819487 | 2020-12-18 15:50 | 2020-12-18 22:10 | 379.75 | 11kV | 21266 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201779 Phase B & C, Intellirupter, Overcurrent Note: Reclose for for BF defect Cursory Patrol, no fault found | December | 2020 | 2021Q2 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2020-12-18 | N | 379.75 | N | 14 | N | N | 1.1101 | 39.4971 | 15540.5656
[7 empty] | 2414 | 9198 | 1819496 | 2020-12-18 16:30 | 2020-12-18 22:15 | 345 | 11kV | 3417 | 33 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201776 Single Phase 10Amp Substation DOLF Blown Tx at sub 72070. Tripped off Sw 11874 when trying back Dolfs after replacing L/As @ 1824. Sw 11874 closed back up at 2000hrs" | December | 2020 | 2021Q2 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2020-12-18 | N | 103.5455 | N | 14 | N | N | 1.1101 | 39.4971 | 2497.0428
[7 empty] | 2005 | 3955 | 1819571 | 2020-12-18 22:25 | 2020-12-19 00:14 | 109 | 11kV | 545 | 5 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT12925 Wattagan Dunks 0.6 - Footpath phase HDO blown after tree fell onto PT | December | 2020 | 2021Q2 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2020-12-18 | N | 109 | N | 14 | N | N | 1.1101 | 39.4971 | 398.2699
[7 empty] | 1764 | 1151 | 1819586 | 2020-12-19 01:26 | 2020-12-19 03:20 | 114 | 11kV | 9462 | 83 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | REC45017 Whiteman tripped on Earth Fault HDO found blown at PT14965 | December | 2020 | 2021Q2 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2020-12-19 | N | 114 | N | 7 | N | N | 1.1101 | 39.4971 | 6914.5505
[7 empty] | 2857 | 14415 | 1819588 | 2020-12-19 05:17 | 2020-12-19 06:15 | 58 | 11kV | 174 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201783 A phase, substation DOLF | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-12-19 | N | 58 | N | 7 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 3068 | 17619 | 1819442 | 2020-12-18 12:37 | 2020-12-19 10:00 | 1283 | 11kV | 33358 | 26 | HV | Overload LV Parallel | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | PT1868 Wallhs Wylds - 11kV HDOs are open and defective. PT in LV // but customers experiencing low volts. HDOs repaired under NAR68210 | December | 2020 | 2021Q2 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | Unknown | Not Veg | 2020-12-18 | N | 1283 | N | 14 | N | N | 1.1101 | 39.4971 | 24377.0425
[7 empty] | 3259 | 19948 | 1819604 | 2020-12-19 08:42 | 2020-12-19 10:45 | 123.1833 | 11kV | 246.3667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201784 10Amp, single Phase substation DOLF | December | 2020 | 2021Q2 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2020-12-19 | N | 123.1833 | N | 7 | N | N | 1.1101 | 39.4971 | 180.0375
[7 empty] | 2678 | 12104 | 1819645 | 2020-12-19 11:59 | 2020-12-19 13:45 | 106 | 11kV | 90312 | 852 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | iR41778 Amy Kimcumber 0.1 tripped and locked out on OC Cause not ascertained | December | 2020 | 2021Q2 | 2021 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2020-12-19 | N | 106 | N | 7 | N | N | 1.1101 | 39.4971 | 65997.3458
[7 empty] | 2444 | 9466 | 1819628 | 2020-12-19 14:05 | 2020-12-19 17:06 | 181 | 11kV | 2896 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 201787 Large branch resting on 11KV main near Pole GU84550. Crew with EWP and isolation required. Closest Sub 54428. | December | 2020 | 2021Q2 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2020-12-19 | N | 181 | N | 7 | N | N | 1.1101 | 39.4971 | 2116.3114
[7 empty] | 2837 | 14266 | 1819693 | 2020-12-19 16:15 | 2020-12-19 17:38 | 83 | 11kV | 36601 | 627 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201788 3 Phase Overcurrent Suspect 50 plus birds on sections of mains caused 11kv to clash as reported by the public. PD | December | 2020 | 2021Q2 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2020-12-19 | N | 58.3748 | N | 7 | N | N | 1.1101 | 39.4971 | 26746.9313
[7 empty] | 2166 | 5841 | 1819680 | 2020-12-19 15:06 | 2020-12-19 19:15 | 249 | 11kV | 2739 | 11 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 201789 A phase Open taps at pole AI-80063. No protection operation." | December | 2020 | 2021Q2 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2020-12-19 | N | 249 | N | 7 | N | N | 1.1101 | 39.4971 | 2001.5804
[7 empty] | 3102 | 18201 | 1819757 | 2020-12-20 03:37 | 2020-12-20 04:37 | 60 | 11kV | 1620 | 27 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | PT11912 Hansens Immaculata - Roadside and Middle phase HDOs blown Tree fell onto PT | December | 2020 | 2021Q2 | 2021 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Veg | 2020-12-20 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 2316 | 7685 | 1819784 | 2020-12-20 09:29 | 2020-12-20 10:15 | 46 | 11kV | 76672 | 2317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.17 tripped on Earth Fault UG cable fault between S5883 and S8309 See 1821380 1821381 1821383 | December | 2020 | 2021Q2 | 2021 | ZN188:PA17 | ZN188:PA17 | ZN00188/000017 | SYDNEY | UG | Not Veg | 2020-12-20 | N | 33.0911 | N | 6 | N | N | 1.1101 | 39.4971 | 56029.6362
[7 empty] | 2239 | 6735 | 1819783 | 2020-12-20 09:29 | 2020-12-20 14:55 | 326 | 11kV | 978 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201793 10Amp, substation DOLF No Cause Found (Not Storm Condition) | December | 2020 | 2021Q2 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2020-12-20 | N | 326 | N | 6 | N | N | 1.1101 | 39.4971 | 714.6936
[7 empty] | 2723 | 12643 | 1819826 | 2020-12-20 12:51 | 2020-12-20 15:30 | 159 | 11kV | 318 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201794 10Amp, single phase, substation DOLF | December | 2020 | 2021Q2 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2020-12-20 | N | 159 | N | 6 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 1844 | 2109 | 1819817 | 2020-12-20 12:08 | 2020-12-20 18:51 | 403 | 11kV | 69546 | 199 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | REC45013 Gunderman tripped and locked out on OC iR44316 Wisemans Ferry tripped on OC Tree brought down OH mains near PT14580 See 1820740 1820741 1820742 1820743 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2020-12-20 | N | 349.4774 | N | 6 | N | N | 1.1101 | 39.4971 | 50822.1655
[7 empty] | 3075 | 17710 | 1819838 | 2020-12-20 13:33 | 2020-12-20 23:50 | 617 | 11kV | 15646 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | REC46803 Wise Ferry Dog Trap .1 tripped on OC Abnormal: USL42860 Open (DMA) with LB62765 Closed Tree brought down OH mains near PT18875 See 1820738 1820739 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2020-12-20 | N | 159.6531 | N | 6 | N | N | 1.1101 | 39.4971 | 11433.6353
[7 empty] | 2982 | 16365 | 1819931 | 2020-12-21 08:35 | 2020-12-21 10:40 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 201799 10Amp, A Phase, substation DOLF No Cause found, not storm conditions OMS 1819931 | December | 2020 | 2021Q2 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2020-12-21 | N | 125 | N | 4 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 1948 | 3328 | 1820085 | 2020-12-21 15:47 | 2020-12-21 16:47 | 60 | 11kV | 19920 | 332 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | LID 201802 Open tapping at pole IU-90250 no protection operation" | December | 2020 | 2021Q2 | 2021 | 206:34441 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2020-12-21 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 14556.9485
[7 empty] | 1763 | 1129 | 1819938 | 2020-12-21 09:10 | 2020-12-21 19:10 | 600 | 11kV | 1120 | 14 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 201803 and LID 201804 Sub 59068 isolated to replace faulty tx. | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-12-21 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 1978 | 3659 | 1820167 | 2020-12-22 02:26 | 2020-12-22 04:53 | 147 | 11kV | 117415 | 1224 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn12690 Berkeley Vale - Pnl.19 tripped on: Earth Fault RHS Cause not ascertained See 1820695 1820696 1820697 1820698 1820699 | December | 2020 | 2021Q2 | 2021 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2020-12-22 | N | 95.9273 | N | 5 | N | N | 1.1101 | 39.4971 | 85803.4188
[7 empty] | 2645 | 11618 | 1820189 | 2020-12-22 07:34 | 2020-12-22 08:10 | 36 | 11kV | 15392 | 662 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn711 Blackwattle Bay - Tx No.13 5kV CB tripped (Nil relay operations) Pnl.15 tripped on Earth Fault UG cable fault in front line section of feeder between Pnl15 and S7527 See 1820690 1820691 | December | 2020 | 2021Q2 | 2021 | ZN711:PA21 | ZN711:PA18 | ZN00711/000018 | SYDNEY | UG | Not Veg | 2020-12-22 | N | 23.2508 | N | 5 | N | N | 1.1101 | 39.4971 | 11248.0196
[7 empty] | 3003 | 16701 | 1820170 | 2020-12-22 03:06 | 2020-12-22 10:55 | 469 | 11kV | 74032 | 746 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | REC63104 Wards Hill Stewart 0.4 tripped on: OC Tree on OH mains See 1820687 1820688 | December | 2020 | 2021Q2 | 2021 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2020-12-22 | N | 99.2386 | N | 5 | N | N | 1.1101 | 39.4971 | 54100.402
[7 empty] | 3093 | 18040 | 1820343 | 2020-12-22 13:19 | 2020-12-22 15:04 | 105 | 11kV | 184125 | 1872 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn12580 Erina- Pnl.14 tripped on B Phase IOC EFIs (First patrol - all down to S49902, S3845 EFI unable to be located) 2nd Patrol NIL UG cable fault in front line section of feeder | December | 2020 | 2021Q2 | 2021 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | UG | Not Veg | 2020-12-22 | N | 98.3574 | N | 5 | N | N | 1.1101 | 39.4971 | 134553.1192
[7 empty] | 2835 | 14253 | 1820418 | 2020-12-22 19:06 | 2020-12-23 02:10 | 424 | 11kV | 2544 | 6 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 201813 LLC lead burnt off." | December | 2020 | 2021Q2 | 2021 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2020-12-22 | N | 424 | N | 5 | N | N | 1.1101 | 39.4971 | 1859.0802
[7 empty] | 1841 | 2083 | 1820431 | 2020-12-23 00:56 | 2020-12-23 03:36 | 160 | 11kV | 134816 | 962 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn2400 Berowra - Pnl.26 tripped on: SEL Bond burnt off pole BE-77908 See 1820675 1820676 1820677 | December | 2020 | 2021Q2 | 2021 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Not Veg | 2020-12-23 | N | 140.1414 | N | 3 | N | N | 1.1101 | 39.4971 | 98519.5564
[7 empty] | 2729 | 12732 | 1820528 | 2020-12-23 11:22 | 2020-12-23 13:35 | 133 | 11kV | 931 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201817 A Phase DOLF : 10 Amp Excluded OMS 1820528 | December | 2020 | 2021Q2 | 2021 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2020-12-23 | N | 133 | N | 3 | N | N | 1.1101 | 39.4971 | 680.3473
[7 empty] | 2045 | 4595 | 1820559 | 2020-12-23 14:39 | 2020-12-23 17:30 | 171 | 11kV | 171 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201820 Single phase DOLF : 10 Amp Excluded OMS 1820559 | December | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-12-23 | N | 171 | N | 3 | N | N | 1.1101 | 39.4971 | 124.9618
[7 empty] | 2208 | 6349 | 1820063 | 2020-12-21 15:01 | 2020-12-24 11:30 | 4109 | 11kV | 154157 | 2293 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3922 Drummoyne - Pnl.2 tripped on Earth Fault UG cable fault between S48988 Sw/A, S65484 Sw/A tee S1513 Spectacle Island See 1821364 1821365 | December | 2020 | 2021Q2 | 2021 | ZN3922:PA2 | ZN3922:PA2 | ZN03922/000002 | INNER WEST | UG | Not Veg | 2020-12-21 | N | 67.2294 | N | 4 | N | N | 1.1101 | 39.4971 | 112653.3887
[7 empty] | 2660 | 11862 | 1820720 | 2020-12-24 13:27 | 2020-12-24 14:45 | 78 | 11kV | 234 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201824 A Phase DOLF : 10 Amp Excluded OMS 1820720 | December | 2020 | 2021Q2 | 2021 | 526:34635 | 526:34635 | ZN00526/034635 | SINGLETON | OH | Veg | 2020-12-24 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 2416 | 9228 | 1820755 | 2020-12-24 14:39 | 2020-12-24 16:10 | 91 | 11kV | 273 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 201825 Single phase DOLF : 10 Amp Excluded OMS 1820755 | December | 2020 | 2021Q2 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2020-12-24 | N | 91 | N | 4 | N | N | 1.1101 | 39.4971 | 199.5003
[7 empty] | 2167 | 5843 | 1820746 | 2020-12-24 14:17 | 2020-12-24 18:45 | 268 | 11kV | 57508 | 244 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC61922 pacific Bar Point - tripped 11kV in LV between USL43257, LB62503 and LB40586 tee PT12458 EMSO checked All premises inspected between #25 thru to #36 with no faults found. No circuits found tripped . Earths intact and no sign of burning or arcing. See 1821362 1821363 | December | 2020 | 2021Q2 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2020-12-24 | N | 235.6885 | N | 4 | N | N | 1.1101 | 39.4971 | 42025.1502
[7 empty] | 2445 | 9472 | 1820770 | 2020-12-24 16:02 | 2020-12-24 20:30 | 268.0667 | 11kV | 2144.5333 | 8 | HV | Animal Other | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201826 A & B Phase DOLF : 16 Amp possible koala, seen alive at base of sub pole by customer but not sighted at time of visit by EMSO. dq CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | December | 2020 | 2021Q2 | 2021 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2020-12-24 | N | 268.0667 | N | 4 | N | N | 1.1101 | 39.4971 | 1567.1617
[7 empty] | 2647 | 11652 | 1820815 | 2020-12-25 02:39 | 2020-12-25 03:53 | 74 | 11kV | 94350 | 1275 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn15005 Belrose - Pnl.6 tripped, relcosed and locked out on B & C phase IOC Possum on UGOH pole FF91447 | December | 2020 | 2021Q2 | 2021 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2020-12-25 | N | 74 | N | 5 | N | N | 1.1101 | 39.4971 | 68948.1971
[7 empty] | 2606 | 11224 | 1824003 | 2020-12-25 14:15 | 2020-12-25 15:25 | 70 | 11kV | 2660 | 38 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 201861 A Phase Isolation to repair Faulty 11kV tapping adj ABS 6641 | December | 2020 | 2021Q2 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-12-25 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 1943.8495
[7 empty] | 2513 | 10243 | 1820828 | 2020-12-25 07:05 | 2020-12-25 16:30 | 565 | 11kV | 30987 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201827 SEF 15A Tree on mains at Pole 8V-70066 Excluded OMS 1820828 | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-12-25 | N | 316.1939 | N | 5 | N | N | 1.1101 | 39.4971 | 22644.3856
[7 empty] | 3156 | 18863 | 1820891 | 2020-12-25 17:13 | 2020-12-25 17:59 | 46 | 11kV | 76820 | 1670 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.10 tripped on OC tree contacted 11kV mains and brought down Service near PT14132 | December | 2020 | 2021Q2 | 2021 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2020-12-25 | N | 46 | N | 5 | N | N | 1.1101 | 39.4971 | 56137.7902
[7 empty] | 1749 | 881 | 1820915 | 2020-12-25 23:45 | 2020-12-26 00:30 | 45 | 11kV | 405 | 9 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.11 tripped on Earth Fault UG cable fault in frontline section of feeder | December | 2020 | 2021Q2 | 2021 | ZN12690:PA11 | ZN12690:PA11 | ZN12690/000011 | CENTRAL COAST | UG | Not Veg | 2020-12-25 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 2566 | 10769 | 1820945 | 2020-12-26 11:27 | 2020-12-26 15:30 | 243 | 11kV | 243 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S7475 Willfox Ilma No.2 - C phase 11kV HV Fuse blown - Tx No.2 RMI Tx No.2 failure. Customer load restricted | December | 2020 | 2021Q2 | 2021 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2020-12-26 | N | 243 | N | 6 | N | N | 1.1101 | 39.4971 | 177.5772
[7 empty] | 3073 | 17697 | 1820984 | 2020-12-26 16:37 | 2020-12-26 20:35 | 238 | 11kV | 13090 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201839 DOLFS down at 3 subs, Fdr openned to repair damage OHM at poles 4K-60118 & 6K-60125 Excluded OMS 1820984, 1820985 ## | December | 2020 | 2021Q2 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2020-12-26 | N | 238 | N | 6 | N | N | 1.1101 | 39.4971 | 9565.7859
[7 empty] | 2484 | 9898 | 1821023 | 2020-12-26 21:18 | 2020-12-27 09:35 | 737 | 11kV | 2211 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201855 Single phase DOLF : 10 Amp Excluded OMS 1821023 | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-26 | N | 737 | N | 6 | N | N | 1.1101 | 39.4971 | 1615.7336
[7 empty] | 2552 | 10630 | 1821048 | 2020-12-27 08:03 | 2020-12-27 11:30 | 207 | 11kV | 207 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201853 Single phase DOLF : 10 Amp Excluded OMS 1821048 | December | 2020 | 2021Q2 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2020-12-27 | N | 207 | N | 5 | N | N | 1.1101 | 39.4971 | 151.2695
[7 empty] | 2593 | 11166 | 1821008 | 2020-12-26 20:02 | 2020-12-27 12:00 | 958 | 11kV | 2874 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201854 Single phase DOLF : 6 Amp Excluded OMS 1821008 | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2020-12-26 | N | 958 | N | 6 | N | N | 1.1101 | 39.4971 | 2100.2344
[7 empty] | 2967 | 16202 | 1821073 | 2020-12-27 11:01 | 2020-12-27 13:30 | 149 | 11kV | 5513 | 37 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Burnt off 11kv tapping, supply restored 1330. Note: recreated record as best as could with information available | December | 2020 | 2021Q2 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2020-12-27 | N | 149 | N | 5 | N | N | 1.1101 | 39.4971 | 4028.7378
[7 empty] | 2461 | 9556 | 1821013 | 2020-12-26 20:45 | 2020-12-27 14:20 | 1055 | 11kV | 68575 | 65 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201845 3 phase Sensitive Earth Fault Excluded OMS 1821013 | December | 2020 | 2021Q2 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2020-12-26 | N | 1055 | N | 6 | N | N | 1.1101 | 39.4971 | 50112.5874
[7 empty] | 1718 | 474 | 1821088 | 2020-12-27 12:13 | 2020-12-27 17:20 | 307 | 11kV | 307 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201857 A & C Phase DOLF : 10 Amp Excluded OMS 1821088 | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-12-27 | N | 307 | N | 5 | N | N | 1.1101 | 39.4971 | 224.3465
[7 empty] | 2398 | 8889 | 1821020 | 2020-12-26 21:13 | 2020-12-27 17:45 | 1232 | 11kV | 36910 | 54 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 201846 3 fault operations 3 phase Earth fault Blown Transformer at sub 70301 | December | 2020 | 2021Q2 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2020-12-26 | N | 683.5185 | N | 6 | N | N | 1.1101 | 39.4971 | 26972.7393
[7 empty] | 3055 | 17398 | 1821107 | 2020-12-27 14:51 | 2020-12-27 17:50 | 179 | 11kV | 358 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 201858 Single phase DOLF : 10 Amp Excluded OMS 1821107 | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-27 | N | 179 | N | 5 | N | N | 1.1101 | 39.4971 | 261.6158
[7 empty] | 1965 | 3471 | 1821068 | 2020-12-27 10:24 | 2020-12-27 18:15 | 471 | 11kV | 3297 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 201859 C Phase DOLF : 10 Amp | December | 2020 | 2021Q2 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-12-27 | N | 471 | N | 5 | N | N | 1.1101 | 39.4971 | 2409.3504
[7 empty] | 2607 | 11227 | 1821149 | 2020-12-28 09:33 | 2020-12-28 10:51 | 78 | 11kV | 41574 | 533 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 201860 3 fault operations C Phase Overcurrent full line patrol done to all open points no fault found. Excluded OMS 1821149 | December | 2020 | 2021Q2 | 2021 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2020-12-28 | N | 78 | N | 13 | N | N | 1.1101 | 39.4971 | 30381.053
[7 empty] | 3191 | 19322 | 1821147 | 2020-12-28 08:19 | 2020-12-28 16:55 | 516 | 11kV | 14463 | 257 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC46992 Goolara Holy Cross tripped on IOC Tree brought down 11kV OH mains between USL42797 and LK42156 teee PT12154 and PT13665 See 1821422 1821430 1821433 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2020-12-28 | N | 56.2763 | N | 13 | N | N | 1.1101 | 39.4971 | 10569.1338
[7 empty] | 2226 | 6655 | 1821266 | 2020-12-28 19:18 | 2020-12-28 21:59 | 161 | 11kV | 44758 | 278 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201868 Weather or Electrical Storm Phases A & C Overcurrent all possible sections of fdr patrolled suspect two lighning striles within reclaim time dq | December | 2020 | 2021Q2 | 2021 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2020-12-28 | N | 161 | N | 13 | N | N | 1.1101 | 39.4971 | 32707.8263
[7 empty] | 3002 | 16664 | 1821272 | 2020-12-28 20:19 | 2020-12-28 22:25 | 126.1 | 11kV | 2017.6 | 16 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201872 Weather or Electrical Storm 10Amp, B and C Phase, substation DOLF suspect lightning dq | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-12-28 | N | 126.1 | N | 13 | N | N | 1.1101 | 39.4971 | 1474.4026
[7 empty] | 1691 | 203 | 1821274 | 2020-12-28 20:27 | 2020-12-28 23:45 | 197.75 | 11kV | 1779.75 | 9 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201873 Weather or Electrical Storm 16 Amp, B and C Phase, Line DOLF suspect lightning CC1: 22-"Refer to SOp" | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-12-28 | N | 197.75 | N | 13 | N | N | 1.1101 | 39.4971 | 1300.5888
[7 empty] | 2463 | 9566 | 1821278 | 2020-12-28 20:40 | 2020-12-28 23:50 | 189.5 | 11kV | 3600.5 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201876 Weather or Electrical Storm A phase Fuse Fuse saver 79382 found operated also found blown dolf at downstream sub 53281 Hooper sub 10A 1phase restored at same time. No switching .DQ CC1: 22-"Refer to SOp" | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2020-12-28 | N | 189.5 | N | 13 | N | N | 1.1101 | 39.4971 | 2631.1392
[7 empty] | 1920 | 3024 | 1821301 | 2020-12-28 23:17 | 2020-12-29 00:13 | 56 | 11kV | 1400 | 25 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 201877 interupted to make emergency repairs to xarm pole JU80921 SI U103 DQ Excluded OMS 1821305 | December | 2020 | 2021Q2 | 2021 | 261:81865 | 261:81865 | ZN00261/081865 | LAKE MACQUARIE | OH | Not Veg | 2020-12-28 | N | 56 | N | 13 | N | N | 1.1101 | 39.4971 | 1023.0787
[7 empty] | 3013 | 16792 | 1821273 | 2020-12-28 20:27 | 2020-12-29 00:35 | 248.1667 | 11kV | 3226.1667 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201870 Weather or Electrical Storm Phases A,B & C (Three Phase) Fdr patrolled in dark nothing found dq | December | 2020 | 2021Q2 | 2021 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2020-12-28 | N | 248.1667 | N | 13 | N | N | 1.1101 | 39.4971 | 2357.5874
[7 empty] | 1953 | 3370 | 1821269 | 2020-12-28 19:44 | 2020-12-29 01:35 | 351 | 11kV | 1053 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201879 Weather or Electrical Storm Blows Surge Arrestor | December | 2020 | 2021Q2 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2020-12-28 | N | 351 | N | 13 | N | N | 1.1101 | 39.4971 | 769.5013
[7 empty] | 2537 | 10552 | 1821316 | 2020-12-29 05:36 | 2020-12-29 07:30 | 114 | 11kV | 411 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201882 LAs cut away 10Amp, single phase, Substation DOLF SUB 14241 R Stanford ALSO had 10A DOLF replaced, Supply ON 0730hrs. | December | 2020 | 2021Q2 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2020-12-29 | N | 102.75 | N | 10 | N | N | 1.1101 | 39.4971 | 300.3467
[7 empty] | 2592 | 11153 | 1821312 | 2020-12-29 03:57 | 2020-12-29 08:40 | 283 | 11kV | 1385 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201884 10Amp, Single Phase, substation DOLFS ## oms 1821312 & 1821313 Note: . No supply to Broken Back Comms towers. Replaced HV fuse on PT sub 350 restored at 0825 10amp element. Replaced HV fuse on PT sub 52738 restored at 0840 10amp element cause storm event | December | 2020 | 2021Q2 | 2021 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2020-12-29 | N | 277 | N | 10 | N | N | 1.1101 | 39.4971 | 1012.1171
[7 empty] | 3172 | 19121 | 1821271 | 2020-12-28 20:18 | 2020-12-29 09:35 | 797 | 11kV | 5579 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201885 No access to spur fuses due to water levels luke watters DQ 10Amp, C Phase Line DOLF Weather or Electrical Storm | December | 2020 | 2021Q2 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2020-12-28 | N | 797 | N | 13 | N | N | 1.1101 | 39.4971 | 4076.9686
[7 empty] | 2885 | 14758 | 1821310 | 2020-12-29 02:21 | 2020-12-29 09:55 | 454 | 11kV | 75901 | 417 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 201880 2 fault operations C Phase Earth Fault defective arrestor on pole JU-31044 and burnt off tapping pole ju35513 dq Excluded OMS 1821307 | December | 2020 | 2021Q2 | 2021 | 204:82701 | 204:82701 | ZN00204/082701 | NEWCASTLE | OH | Not Veg | 2020-12-29 | N | 182.0168 | N | 10 | N | N | 1.1101 | 39.4971 | 55466.2121
[7 empty] | 2965 | 16125 | 1821297 | 2020-12-28 22:41 | 2020-12-29 10:40 | 719 | 11kV | 1438 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201886 10Amp, B phase, substation DOLF Weather or Electrical Storm Delay due to Job not despatched as other Miranee job will not be done till daylight due to safety dq | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-28 | N | 719 | N | 13 | N | N | 1.1101 | 39.4971 | 1050.848
[7 empty] | 2908 | 15126 | 1821283 | 2020-12-28 21:08 | 2020-12-29 10:50 | 822 | 11kV | 14796 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201894 Device 40569 10Amp, B phase Line DOLF LID 201887 Device 53412:11kV 10Amp. A and C phase, Substation DOLF CC1: 22-"Refer to SOp" | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-28 | N | 822 | N | 13 | N | N | 1.1101 | 39.4971 | 10812.4804
[7 empty] | 2579 | 10955 | 1821394 | 2020-12-29 10:21 | 2020-12-29 11:06 | 45 | 11kV | 43785 | 973 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Ex Zn12570 Avoca - Pnl.22 - Footpath phase bond burnt off AB40388 Abnormal: S65223 Sw/B Closed with AB40382 Open (DMA) | December | 2020 | 2021Q2 | 2021 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2020-12-29 | N | 45 | N | 10 | N | N | 1.1101 | 39.4971 | 31996.7866
[7 empty] | 2293 | 7422 | 1821385 | 2020-12-29 10:06 | 2020-12-29 11:40 | 94 | 11kV | 3008 | 32 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 201900 B & C Phase DOLF : 16 Amp Excluded OMS 1821390 | December | 2020 | 2021Q2 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2020-12-29 | N | 94 | N | 10 | N | N | 1.1101 | 39.4971 | 2198.1577
[7 empty] | 3166 | 19035 | 1821270 | 2020-12-28 19:57 | 2020-12-29 13:50 | 1073 | 11kV | 2146 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201878 Weather or Electrical Storm 10Amp, 3 phases, substation DOLF 3x blown arrestors to be replaced in daylight | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2020-12-28 | N | 1073 | N | 13 | N | N | 1.1101 | 39.4971 | 1568.2335
[7 empty] | 2878 | 14670 | 1821461 | 2020-12-29 12:04 | 2020-12-29 13:52 | 108 | 11kV | 66250 | 869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn901 Surry Hills - Pnl.20 tripped on Earth Fault Abnormal: S5653 Sw/B Open with Sw/A Closed UG cable fault between S8232 Sw/B and S5653 Sw/A | December | 2020 | 2021Q2 | 2021 | ZN901:PA20 | ZN901:PA29 | ZN00901/000029 | SYDNEY | UG | Not Veg | 2020-12-29 | N | 76.2371 | N | 10 | N | N | 1.1101 | 39.4971 | 48413.546
[7 empty] | 2066 | 4813 | 1821314 | 2020-12-29 04:51 | 2020-12-29 14:30 | 579 | 11kV | 1158 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 201909 Electrical Storm 10Amp, A phase, Substation DOLF | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-29 | N | 579 | N | 10 | N | N | 1.1101 | 39.4971 | 846.2322
[7 empty] | 2432 | 9325 | 1821353 | 2020-12-29 09:00 | 2020-12-29 15:35 | 395 | 11kV | 1580 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 201911 Weather or Electrical Storm A phase substation DOLF 10 Amp Blown LA, 3 replaced | December | 2020 | 2021Q2 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2020-12-29 | N | 395 | N | 10 | N | N | 1.1101 | 39.4971 | 1154.6174
[7 empty] | 2769 | 13429 | 1821561 | 2020-12-29 23:55 | 2020-12-30 01:40 | 104.55 | 11kV | 1672.8 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 201913 No Cause Found (Not Storm Condition) A phase, 10 Amp Line DOLF | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-29 | N | 104.55 | N | 10 | N | N | 1.1101 | 39.4971 | 1222.4329
[7 empty] | 2713 | 12427 | 1821638 | 2020-12-30 09:56 | 2020-12-30 11:20 | 84 | 11kV | 36426 | 664 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Light | N | Zn9550 Gwawley Bay - Pnl.9 tripped on ABC phase OC and Earth Fault Bird made contact with UGOH and appears to have caused damage near PT9745. See 1821707 1821708 7821709 | December | 2020 | 2021Q2 | 2021 | ZN9550:PA9 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | OH | Not Veg | 2020-12-30 | N | 54.8584 | N | 3 | N | N | 1.1101 | 39.4971 | 26619.0464
[7 empty] | 2489 | 9919 | 1821325 | 2020-12-29 08:50 | 2020-12-30 12:10 | 1640 | 11kV | 8050 | 13 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 201908 Pole substation 71992 fell over Excluded OMS 1821325 | December | 2020 | 2021Q2 | 2021 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2020-12-29 | N | 619.2308 | N | 10 | N | N | 1.1101 | 39.4971 | 5882.7026
[7 empty] | 2349 | 8197 | 1821572 | 2020-12-30 03:49 | 2020-12-30 14:30 | 641 | 11kV | 49806 | 364 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC61340 George Bloodtree 0.2 tripped, reclosed and locked out on OC OH mains down between LB40546 and REC63734 (PT11567 & 13277) See 1822118 1822119 | December | 2020 | 2021Q2 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2020-12-30 | N | 136.8297 | N | 3 | N | N | 1.1101 | 39.4971 | 36396.7558
[7 empty] | 1729 | 636 | 1821732 | 2020-12-30 15:06 | 2020-12-30 16:15 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 201914 No Cause Found (Not Storm Condition) A Phase, 10 Amp Substation DOLF | December | 2020 | 2021Q2 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2020-12-30 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 1694 | 226 | 1821769 | 2020-12-31 03:41 | 2020-12-31 09:45 | 364 | 11kV | 165070 | 915 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn4545 Meadowbank - pnl21 tripped on EFI 11kV OH down on corner of Douglas and Phillips Rd Putney See 1822122 1822123 | December | 2020 | 2021Q2 | 2021 | ZN4545:PA21 | ZN4545:PA21 | ZN04545/000021 | RYDE | OH | Not Veg | 2020-12-31 | N | 180.4044 | N | 2 | N | N | 1.1101 | 39.4971 | 120628.2873
[7 empty] | 3150 | 18806 | 1821803 | 2020-12-31 09:23 | 2020-12-31 10:20 | 57 | 11kV | 2109 | 37 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 201917 Fdr did not trip Broken xarm, ohm on timber cross arm at 8M-60100 | December | 2020 | 2021Q2 | 2021 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2020-12-31 | N | 57 | N | 2 | N | N | 1.1101 | 39.4971 | 1541.195
[7 empty] | 2591 | 11151 | 1821880 | 2021-01-01 03:04 | 2021-01-01 05:02 | 118 | 11kV | 163548 | 1386 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn4545 Meadowbank Panel 42 fdr has tripped SIgnals: 11kv trip Relays: A & B Phase time OC, Lock out EFI: nil Cause: not ascertained Zn4545 Meadowbank Panel 42 CB failed to spring charge and unable to close CB DMA created | January | 2021 | 2021Q3 | 2021 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Veg | 2021-01-01 | N | 118 | N | 3 | N | N | 1.1101 | 39.4971 | 119516.0546
[7 empty] | 3224 | 19619 | 1821890 | 2021-01-01 11:10 | 2021-01-01 15:47 | 277 | 11kV | 1939 | 7 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 211920 MVA at stay pole HW-70723. Excluded OMS No. 1821890 | January | 2021 | 2021Q3 | 2021 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2021-01-01 | N | 277 | N | 3 | N | N | 1.1101 | 39.4971 | 1416.964
[7 empty] | 2838 | 14294 | 1821932 | 2021-01-01 15:47 | 2021-01-01 23:21 | 454 | 11kV | 46252 | 273 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 210001 2 fault operations tree removed from OHM near sub 51289 please investigate protection fault past Sw 42045 but tripping Sw 64036. Excluded oms 1821932 and 1821944 | January | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-01-01 | N | 169.4212 | N | 3 | N | N | 1.1101 | 39.4971 | 33799.5974
[7 empty] | 2454 | 9521 | 1822044 | 2021-01-02 19:05 | 2021-01-03 00:10 | 305 | 11kV | 3355 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 210004 11kV mains of pin insulators poles HQ 40003 HQ 40004 HQ 40005 HW 47436 HW 47437 | January | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-01-02 | N | 305 | N | 1 | N | N | 1.1101 | 39.4971 | 2451.735
[7 empty] | 1710 | 408 | 1822050 | 2021-01-03 01:36 | 2021-01-03 02:10 | 34 | 11kV | 4318 | 127 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 210005 Possum on Tx B phase 40 Amp substation DOLF | January | 2021 | 2021Q3 | 2021 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Not Veg | 2021-01-03 | N | 34 | N | 6 | N | N | 1.1101 | 39.4971 | 3155.467
[7 empty] | 1728 | 629 | 1822060 | 2021-01-03 07:43 | 2021-01-03 08:52 | 69 | 11kV | 345 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 210007 A phase 16Amp fuse, substation DOLF, No cause found not storm conditions | January | 2021 | 2021Q3 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2021-01-03 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 3128 | 18440 | 1822057 | 2021-01-03 06:29 | 2021-01-03 10:40 | 251 | 11kV | 92727 | 932 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 210006 2 fault operations A & B Phases Overcurrent CAR HIT POLE JU-21918. targets A-B O/C B PROT. Excluded oms report no 1822057,1822061,1822066 | January | 2021 | 2021Q3 | 2021 | 257:81988 | 257:81988 | ZN00257/081988 | NEWCASTLE | OH | Not Veg | 2021-01-03 | N | 99.4925 | N | 6 | N | N | 1.1101 | 39.4971 | 67762.1566
[7 empty] | 2203 | 6314 | 1822136 | 2021-01-03 14:29 | 2021-01-03 16:30 | 121 | 11kV | 230479 | 2313 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At Sub 9700 kirrawee Panel No.17 opened on A phase timed & IOC, timing, lockout, fault check, SEL & EFI field EFI's @ subs 9048, 9587, 9838, 9807, 9881 Remarks: lightning/surge arrestor. At PT9730 Marina Cr South | January | 2021 | 2021Q3 | 2021 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2021-01-03 | N | 99.645 | N | 6 | N | N | 1.1101 | 39.4971 | 168427.2552
[7 empty] | 1767 | 1189 | 1822092 | 2021-01-03 11:15 | 2021-01-03 17:30 | 375.35 | 11kV | 1876.75 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Rain Light | N | LID 210008 A Phase Broken live line clamp at pole NV-80013 | January | 2021 | 2021Q3 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-01-03 | N | 375.35 | N | 6 | N | N | 1.1101 | 39.4971 | 1371.4735
[7 empty] | 3065 | 17604 | 1822075 | 2021-01-03 09:06 | 2021-01-03 18:10 | 544 | 11kV | 165990 | 680 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn2400 Berowra Pa11 'IR61454 Berowra Tollgates' RE1772 Seymours Creek tripped and reclosed Singals: OC Trip, IOC Trip RE1239 Brooklyn tripped on Signals: OC Trip, Lockout Cause: Tree/Branch on OH Mains Tree on PT318 2nd Event @1101 S1586 Brooklyn Causeway 66kV HDO operated centre phase due to Fuse Fatigue See 1824671,2,3,4,5,6 2nd 1824677,8,9,80 Ex 1822075,89,90,3897,8,9,900,1,2 | January | 2021 | 2021Q3 | 2021 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2021-01-03 | N | 244.1029 | N | 6 | N | N | 1.1101 | 39.4971 | 121300.5961
[7 empty] | 2251 | 6854 | 1822192 | 2021-01-04 05:56 | 2021-01-04 08:29 | 153 | 11kV | 1377 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210012 B Phase DOLF : 31 Amp Excluded OMS 1822192 | January | 2021 | 2021Q3 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2021-01-04 | N | 153 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1006.271
[7 empty] | 2397 | 8886 | 1822240 | 2021-01-04 10:45 | 2021-01-04 14:30 | 225 | 11kV | 900 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 210015 SEGREGATED EARTHING SYSTEM. 22 LOZ V FOUND ON MSB SURROUND, METALLIC PLUMBING AND METAL STRUCTURES. 78V FOUND ON LV SUB EARTH TO AN IND EARTH WITH PT LVF OPENED OFF. 40V FOUND ON HV SUB EARTH TO AND EARTH WITH PT LVF OPENED OFF. SUB EARTH VOLTAGE READINGS RETURNED TO ZERO WHEN DOLFS WERE OPENED OFF. OH MAINS ATTENDED AND REPLACED 2 X HV ARRESTERS, 1 X LV ARRESTER AND 1 X SECTION OF CABLING BETWEEN LV TX BUSHING AND LVF AS THERE WAS A BURNING HSC435 ACTIVE CONNECTION MAKING INTERMITTENT CONTACT WITH THE TX TANK. NETWORK THEN TESTED AS NORMAL. SITES WHERE SHOCKS WERE RECEIVED TESTED & RETURNED 0V | January | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-01-04 | N | 225 | N | 27 | Y | Y | 1.1101 | 39.4971 | 657.6935
[7 empty] | 2641 | 11598 | 1822384 | 2021-01-04 16:43 | 2021-01-04 17:30 | 47 | 11kV | 69063 | 1521 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | N | ZN15009 MANLY 11kV CB Panel 5 tripped on Relays: Earth Fault, EFI, Fault check Signals: 11kv trip EFI: S77296 S16408 S16427 Lightning hit UGOH between S16427SwB to S15095SwA. UGOH requires inspection. Switching tag at S15095SwA See 1824535,6 ex 1822384,403 | January | 2021 | 2021Q3 | 2021 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Not Veg | 2021-01-04 | N | 45.4063 | N | 27 | Y | Y | 1.1101 | 39.4971 | 50469.2034
[7 empty] | 3193 | 19333 | 1822385 | 2021-01-04 16:44 | 2021-01-04 17:59 | 75.0333 | 11kV | 69480.8667 | 926 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Lightning | N | At 10998 Rockdale Zn P26 tripped and locked out on efi, B phase and N OC and ef relay EFI's at S65434, S65433 Remarks: tree/branch on OH mains. 16 eden st arncliffe removed by dop | January | 2021 | 2021Q3 | 2021 | ZN10998:PA26 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | OH | Veg | 2021-01-04 | N | 75.0333 | N | 27 | Y | Y | 1.1101 | 39.4971 | 50774.568
[7 empty] | 2675 | 12052 | 1822420 | 2021-01-04 16:51 | 2021-01-04 18:17 | 86 | 11kV | 5332 | 62 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Ex ZN12600 LISAROW section of 11kV Panel 2 CP41020 Wattle Tree Rd North tripped, reclosed and locked out on: OC trip Cause: Tree/Branch on OH Mains near pole WL1057 See 1824713 ex 1822420 | January | 2021 | 2021Q3 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-01-04 | N | 86 | N | 27 | Y | Y | 1.1101 | 39.4971 | 3896.4683
[7 empty] | 2759 | 13271 | 1822333 | 2021-01-04 16:21 | 2021-01-04 18:21 | 120 | 11kV | 84600 | 705 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN2400 BEROWRA section of 11kV Panel 11 RE3282 Alberta Ave tripped Cause: tree/branch on oh mains adjacent AB204 | January | 2021 | 2021Q3 | 2021 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2021-01-04 | N | 120 | N | 27 | Y | Y | 1.1101 | 39.4971 | 61823.1847
[7 empty] | 2714 | 12489 | 1822322 | 2021-01-04 15:38 | 2021-01-04 18:30 | 172 | 11kV | 15824 | 160 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 210036 3 phase Tree on mains adj pole 9k-40054. Excluded OMS 1822322 | January | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-01-04 | N | 98.9 | N | 27 | Y | Y | 1.1101 | 39.4971 | 11563.7125
[7 empty] | 1946 | 3269 | 1822377 | 2021-01-04 16:39 | 2021-01-04 18:30 | 110.65 | 11kV | 2434.3 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 210039 A Phase DOLF : 10 Amp Excluded OMS 1822488 | January | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-01-04 | N | 110.65 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1778.9146
[7 empty] | 1772 | 1335 | 1822539 | 2021-01-04 17:59 | 2021-01-04 19:25 | 86 | 11kV | 15050 | 175 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 210034 A Phase 63 Amp substation DOLF faulty LAs cut away A phase please arrange repairs | January | 2021 | 2021Q3 | 2021 | 256:80641 | 256:80641 | ZN00256/080641 | NEWCASTLE | OH | Not Veg | 2021-01-04 | N | 86 | N | 27 | Y | Y | 1.1101 | 39.4971 | 10998.0961
[7 empty] | 2934 | 15518 | 1822506 | 2021-01-04 17:31 | 2021-01-04 20:10 | 159 | 11kV | 318 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210042 B Phase DOLF : 10 Amp Excluded OMS 1822506 | January | 2021 | 2021Q3 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-01-04 | N | 159 | N | 27 | Y | Y | 1.1101 | 39.4971 | 232.385
[7 empty] | 3051 | 17348 | 1822535 | 2021-01-04 17:57 | 2021-01-04 20:30 | 153.4667 | 11kV | 153.4667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 210041 A Phase DOLF : 10 Amp Excluded OMS 1822617 | January | 2021 | 2021Q3 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2021-01-04 | N | 153.4667 | N | 27 | Y | Y | 1.1101 | 39.4971 | 112.1489
[7 empty] | 2916 | 15218 | 1822567 | 2021-01-04 18:30 | 2021-01-04 20:40 | 130 | 11kV | 260 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 210040 A Phase DOLF : 10 Amp Excluded OMS 1822567 | January | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-01-04 | N | 130 | N | 27 | Y | Y | 1.1101 | 39.4971 | 190.0003
[7 empty] | 2301 | 7541 | 1822594 | 2021-01-04 19:05 | 2021-01-04 20:47 | 102 | 11kV | 204 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | No LID report raised Wide area electrical storm Assumed LID report not raised MARK DONNELLY FRIEND/NEIGHBOUR Fuse has popped at pole. NS. has 3 children in house. floody/boggy in area. MT70087. no iso/quarantine | January | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-01-04 | N | 102 | N | 27 | Y | Y | 1.1101 | 39.4971 | 149.0772
[7 empty] | 2216 | 6523 | 1822591 | 2021-01-04 20:05 | 2021-01-04 21:28 | 83.4833 | 11kV | 4007.2 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210037 B Phase 31Amp, substation DOLF | January | 2021 | 2021Q3 | 2021 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2021-01-04 | N | 83.4833 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2928.3436
[7 empty] | 2788 | 13727 | 1822505 | 2021-01-04 18:40 | 2021-01-04 21:38 | 178 | 11kV | 25098 | 141 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | Ex ZN13000 LAKE MUNMORAH section of 11kV Panel 10 11kV Bond Burnt off Between PT14567 and LB44808 on Pole WH208 See 1824709 ex 1822505,71 | January | 2021 | 2021Q3 | 2021 | ZN13000:PA10 | ZN13000:PA10 | ZN13000/000010 | CENTRAL COAST | OH | Not Veg | 2021-01-04 | N | 178 | N | 27 | Y | Y | 1.1101 | 39.4971 | 18340.8781
[7 empty] | 2768 | 13380 | 1822338 | 2021-01-04 16:23 | 2021-01-04 21:40 | 317 | 11kV | 560373 | 3044 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN4545 MEADOWBANK 11kV CB Panel 31 'Rydale Sixth' tripped on: Relays: B Phase OC Signals: Tx3 Group Earth, ZOne Earth, 11kv trip Abnormal: RE46117 CB open with Bypass AB Closed Cause: Tree Branch brought down OH. Near LB1052 See 1824514,6,7,8 Ex 1822338,62,430,86,552,619 | January | 2021 | 2021Q3 | 2021 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Veg | 2021-01-04 | N | 184.091 | N | 27 | Y | Y | 1.1101 | 39.4971 | 409504.0602
[7 empty] | 3239 | 19724 | 1822335 | 2021-01-04 16:16 | 2021-01-04 22:19 | 363 | 11kV | 54450 | 150 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Electrical Storm | N | The 11kv Rec46935 Iron kirks 0.8 (Ex Zn12630 Peats Ridge Panel 3) tripped, reclosed and locked out on: SEF trip Remarks: tree/branch brought down OH. An 11kv wire found down near Autolink 46938 | January | 2021 | 2021Q3 | 2021 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2021-01-04 | N | 363 | N | 27 | Y | Y | 1.1101 | 39.4971 | 39790.454
[7 empty] | 2409 | 9157 | 1822368 | 2021-01-04 16:37 | 2021-01-04 22:50 | 372.8833 | 11kV | 82034.3333 | 220 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Ex ZN14891 WYONG section of 11kV Panel 5 RE62705 Jilliby Durren tripped, reclosed and locked out on: OC Cause: tree branch on oh mains. Large Piece of bark was found across the 11kv mains near PT14839 Mandalong dooralong 1 See 1822368 ex 1822382,6,98,443 | January | 2021 | 2021Q3 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2021-01-04 | N | 372.8833 | N | 27 | Y | Y | 1.1101 | 39.4971 | 59948.2712
[7 empty] | 2390 | 8757 | 1822454 | 2021-01-04 17:04 | 2021-01-04 22:50 | 346 | 11kV | 11764 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex ZN35500 TOP RYDE section of 11kV Panel 28 PT1824 VALEWOOD DOVER Footpath HDO blew 61Amps Probable cause for previous trip on Panel 28. Previous Storm See 1824708 ex 1822454 1822565 | January | 2021 | 2021Q3 | 2021 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2021-01-04 | N | 346 | N | 27 | Y | Y | 1.1101 | 39.4971 | 8596.7842
[7 empty] | 2007 | 3979 | 1822423 | 2021-01-04 16:53 | 2021-01-05 00:48 | 475 | 11kV | 12825 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210043 3 phase fuses : 20 Amp Excluded OMS 1822423 | January | 2021 | 2021Q3 | 2021 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2021-01-04 | N | 475 | N | 27 | Y | Y | 1.1101 | 39.4971 | 9372.1317
[7 empty] | 2936 | 15549 | 1822489 | 2021-01-04 16:59 | 2021-01-05 00:50 | 471 | 11kV | 7097 | 517 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | The 11kv Panel No.2 from ZN12620 Noraville tripped and reclosed on: Relays: timed overcurrent & efi Field EFI's: Nil At PT12139 mimosa elizabeth bay @ 10K HDOs blown Remarks: cause not ascertained | January | 2021 | 2021Q3 | 2021 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Veg | 2021-01-04 | N | 13.7273 | N | 27 | Y | Y | 1.1101 | 39.4971 | 5186.2783
[7 empty] | 2253 | 6894 | 1822422 | 2021-01-04 17:46 | 2021-01-05 02:08 | 502 | 11kV | 56224 | 112 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210035 tree on OHM adjacent abs 7372 section isolated to make repairs | January | 2021 | 2021Q3 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2021-01-04 | N | 502 | N | 27 | Y | Y | 1.1101 | 39.4971 | 41086.8409
[7 empty] | 1734 | 692 | 1822524 | 2021-01-04 17:44 | 2021-01-05 04:30 | 646 | 11kV | 8398 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210045 A, B and C Phase 20Amp, Line DOLFs | January | 2021 | 2021Q3 | 2021 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2021-01-04 | N | 646 | N | 27 | Y | Y | 1.1101 | 39.4971 | 6137.0107
[7 empty] | 3211 | 19504 | 1822699 | 2021-01-05 07:18 | 2021-01-05 10:13 | 175 | 11kV | 114905 | 1367 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 210048 B & C Phases Overcurrent; Earth Fault 11kv mains down pole FS-80482 section isolated for repairs. Mains down from open taps to break point so no prot operation T/R on fdr 83123 at 1723 4/1/2021 see report 210028 Excluded oms 1822699 | January | 2021 | 2021Q3 | 2021 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2021-01-05 | N | 84.0563 | N | 9 | N | N | 1.1101 | 39.4971 | 83969.1849
[7 empty] | 2126 | 5414 | 1822761 | 2021-01-05 09:55 | 2021-01-05 13:10 | 195 | 11kV | 390 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210054 Single Phase 10Amp Substation DOLF | January | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-01-05 | N | 195 | N | 9 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 1939 | 3224 | 1822728 | 2021-01-05 09:05 | 2021-01-05 13:25 | 260 | 11kV | 1040 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210053 B Phase DOLF : 16 Amp Excluded OMS 1822731 | January | 2021 | 2021Q3 | 2021 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2021-01-05 | N | 260 | N | 9 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 2547 | 10606 | 1822327 | 2021-01-04 16:06 | 2021-01-05 13:40 | 1294 | 11kV | 69466 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN35370 GALSTON section of 11kV Panel 8 RE559 Cobah Rd tripped, reclosed and locked out Cause: tree/branch brought down oh. Tree took down 11kv OH See 1824091,2 ex 1822327 | January | 2021 | 2021Q3 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2021-01-04 | N | 879.3165 | N | 27 | Y | Y | 1.1101 | 39.4971 | 50763.7039
[7 empty] | 2712 | 12426 | 1822592 | 2021-01-04 19:03 | 2021-01-05 14:15 | 1152 | 11kV | 32180 | 167 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex ZN35370 GALSTON section of 11kV Panel 4 RE428 Baygield Rd tripped Cause: tree brought down OH. Previous storm See 1822592,650,1 | January | 2021 | 2021Q3 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2021-01-04 | N | 192.6946 | N | 27 | Y | Y | 1.1101 | 39.4971 | 23516.1949
[7 empty] | 2357 | 8303 | 1822652 | 2021-01-04 21:29 | 2021-01-05 14:20 | 1011 | 11kV | 124084 | 1629 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | ZN13000 LAKE MUNMORAH 11kV CB Panel 4 tripped, reclosed and locked out on: SIgnals: 11kv trip Relays: OC, EF, EFT, Recloser lockout EFI's Nil Abnormal: LB40172 closed, AB43824 is defective and open Cause: Tree/Branch on OH mains Tree found on 11kv mains near PT11713. Isolated from LB41810 to LK42661 tee to PT11713 See 1824069,71,2 ex 1822652,3,82 | January | 2021 | 2021Q3 | 2021 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Veg | 2021-01-04 | N | 76.1719 | N | 27 | Y | Y | 1.1101 | 39.4971 | 90676.9273
[7 empty] | 2071 | 4880 | 1822319 | 2021-01-04 15:34 | 2021-01-05 15:50 | 1456 | 11kV | 23388 | 120 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | REC44316 Wisemans Ferry tripped, reclosed and tripped on OC REC61097 Wise Ferry Lavender 10 interrupted at 18:48 to allow by-pass link at REC44316 to be closed. 11kV UGOH to PT14837 found to be defective. While attempting to prove location of fault by closing by-pass link at REC44316, the by-pass link was then unable to be opened delaying restoration. See 1826015 1826016 1826014 1826018 1826017 | January | 2021 | 2021Q3 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | UG | Not Veg | 2021-01-04 | N | 194.9 | N | 27 | Y | Y | 1.1101 | 39.4971 | 17091.2606
[7 empty] | 2108 | 5246 | 1822794 | 2021-01-05 12:12 | 2021-01-05 16:04 | 232 | 11kV | 2758 | 32 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 210052 Crossarm broken. Head of pole on fire. Wires all in the air. Sw 62930 tripped 1652hrs 4/1//21. See LID #210023 Too wet to replace pole 7M-30158. Cut taps at 7M-30153 & 7M-30160 to restore supply. Excluded OMS 1822814 & 1822794 | January | 2021 | 2021Q3 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2021-01-05 | N | 86.1875 | N | 9 | N | N | 1.1101 | 39.4971 | 2015.4651
[7 empty] | 2168 | 5850 | 1822884 | 2021-01-05 17:04 | 2021-01-05 17:41 | 37 | 11kV | 34558 | 934 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN3472 SEFTON 11kV CB Panel 22 'Virgil Avenue, Meakin Virgil' opened Balloon on 11kv removed by DOp OH See 1822884 ex 1822888 | January | 2021 | 2021Q3 | 2021 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-01-05 | N | 37 | N | 9 | N | N | 1.1101 | 39.4971 | 25253.9671
[7 empty] | 2735 | 12838 | 1822749 | 2021-01-05 09:38 | 2021-01-05 20:00 | 622 | 11kV | 622 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 210051 Replace LV & HV arrestors. Possible leakage to earth. Faulty transformer replaced Excluded OMS 1822755 & 1822749 | January | 2021 | 2021Q3 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-01-05 | N | 622 | N | 9 | N | N | 1.1101 | 39.4971 | 454.5393
[7 empty] | 2793 | 13790 | 1822923 | 2021-01-05 20:26 | 2021-01-05 22:31 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210057 3 phase DOLF : 10 Amp Excluded OMS 1822923 | January | 2021 | 2021Q3 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2021-01-05 | N | 125 | N | 9 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 2109 | 5252 | 1822930 | 2021-01-05 21:33 | 2021-01-06 00:30 | 177 | 11kV | 42825 | 269 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex ZN15002 NARRABEEN section of 11kV Panel 2 RE20112 Kalang Rd tripped on Relays: OC and SEF PT15458 Wilga Powderworks defective. Transformer failure See 1824189,90 ex 1822930 | January | 2021 | 2021Q3 | 2021 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2021-01-05 | N | 159.2007 | N | 9 | N | N | 1.1101 | 39.4971 | 31295.2469
[7 empty] | 2438 | 9376 | 1822917 | 2021-01-05 19:59 | 2021-01-06 00:50 | 291 | 11kV | 2619 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | PT14731 GRETA BUMBLE HILL 0.7 16amp roadside phase HDO blown Cause: not ascertained See 1824158 ex 1822917 | January | 2021 | 2021Q3 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-01-05 | N | 291 | N | 9 | N | N | 1.1101 | 39.4971 | 1913.888
[7 empty] | 2766 | 13344 | 1823095 | 2021-01-06 15:50 | 2021-01-06 16:55 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210062 B phase DOLF : 10 Amp Excluded OMS 1823095 | January | 2021 | 2021Q3 | 2021 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-01-06 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 1891 | 2745 | 1823132 | 2021-01-06 19:23 | 2021-01-06 20:45 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 210063 B Phase HV Fuse : 32 Amp Excluded OMS 1823132 | January | 2021 | 2021Q3 | 2021 | 801:74117 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | UG | Not Veg | 2021-01-06 | N | 82 | N | 2 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 2990 | 16548 | 1823150 | 2021-01-07 04:07 | 2021-01-07 04:43 | 36 | 11kV | 16884 | 469 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN9550 GWAWLEY BAY 11kV CB Panel 4 fdr tripped Singals: 11kv trip Relays: EFI, Earth Fault EFI: S9831 S9456 Cause: explosion out front 68 port hacking rd. Loss of supply and now dead possum at base of pole CR08622 See 1823150 ex 1823151 | January | 2021 | 2021Q3 | 2021 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | OH | Not Veg | 2021-01-07 | N | 36 | N | 2 | N | N | 1.1101 | 39.4971 | 12338.3292
[7 empty] | 3203 | 19423 | 1823162 | 2021-01-07 17:25 | 2021-01-07 18:15 | 50 | 11kV | 1550 | 31 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Lightning Arrestor | Unplanned | No Weather Impact | N | DOp interrupted section of Fdr from CP2902 to extend of Fdr to carry out repairs. Cause: Damaged surge arrestor to PT2281 See OMS 1823293,1823162 | January | 2021 | 2021Q3 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2021-01-07 | N | 50 | N | 2 | N | N | 1.1101 | 39.4971 | 1132.6943
[7 empty] | 2973 | 16306 | 1823334 | 2021-01-08 09:07 | 2021-01-08 10:35 | 88 | 11kV | 264 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210071 C Phase DOLF : 31 Amp Excluded OMS 1823334 | January | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-01-08 | N | 88 | N | 1 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 2159 | 5792 | 1823458 | 2021-01-09 03:27 | 2021-01-09 06:15 | 168 | 11kV | 242646 | 1867 | HV | Animal Possum | Animal | Circuit Breaker | Unplanned | No Weather Impact | N | At ZN.15008 Harbord, Pnl 10 CB tripped. Cause: Possum on 11kV UGOH adjacent to S16576. Relays: A ph OC,EF,IOC,EFI,Timing relay,lockout relay,E/F check relay (Tx.2 panel,O/C pick up,E/F pick up, E/F check) EFI at Sub 17153,other EFI's defective. see OMS 1823458 (Pnl 9 CB) tripped during restoration. see also OMS 1823458,1823994,1823995,1823997 | January | 2021 | 2021Q3 | 2021 | ZN15008:PA10 | ZN15008:PA10 | ZN15008/000010 | NORTHERN BEACHES | OH | Not Veg | 2021-01-09 | N | 129.9657 | N | 6 | N | N | 1.1101 | 39.4971 | 177318.54
[7 empty] | 3279 | 20205 | 1823459 | 2021-01-09 04:10 | 2021-01-09 07:05 | 175 | 11kV | 182954 | 1179 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Rec CP63641 Manchester View tripped. Cause: 11kV UG cable fault between S.9292,S.9809 & LB 35655 Relays: O/C trip,lockout. At ZN.9700 Kirrawee-Signals Tx.3 group E,Zone E See OMS 1824079,1824082,1823459,1823460 | January | 2021 | 2021Q3 | 2021 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2021-01-09 | N | 155.1773 | N | 6 | N | N | 1.1101 | 39.4971 | 133697.387
[7 empty] | 2328 | 7929 | 1823500 | 2021-01-09 12:43 | 2021-01-09 13:44 | 61 | 11kV | 40713 | 687 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 210079 Single phase Overcurrent Faulty UGOH pole KS-90163, Section isolated and customers restored. UGOH requires repairs. Reported to Z Smith Excluded OMS 1823500 | January | 2021 | 2021Q3 | 2021 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | Unknown | Unknown | 2021-01-09 | N | 59.262 | N | 6 | N | N | 1.1101 | 39.4971 | 29751.8596
[7 empty] | 2070 | 4859 | 1823518 | 2021-01-09 14:44 | 2021-01-09 20:55 | 371 | 11kV | 3382 | 50 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 210081 section isolated to replace faulty dolf at sub 26214 Excluded oms 1823518 | January | 2021 | 2021Q3 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2021-01-09 | N | 67.64 | N | 6 | N | N | 1.1101 | 39.4971 | 2471.4658
[7 empty] | 2362 | 8361 | 1823538 | 2021-01-09 21:15 | 2021-01-09 21:28 | 13 | 11kV | 2288 | 176 | HV | Burnt Contacts | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | At PT61317 Ridge Barrenjoey,HV fuse operated by DOp to repair Fuse Equipment. Cause: Footpath phase wedge had gone HR & was cooking up,requiring wedge to be replaced. see OMS 1823538,1823539 CC1: 22-"Refer to SOp" | January | 2021 | 2021Q3 | 2021 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Not Veg | 2021-01-09 | N | 13 | N | 6 | N | N | 1.1101 | 39.4971 | 1672.0029
[7 empty] | 2665 | 11895 | 1823536 | 2021-01-09 20:05 | 2021-01-09 22:00 | 115 | 11kV | 213392 | 2010 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.690 Campsie,Pnl 12 CB tripped. Cause: 11kV UG cable fault from Pnl.12 to S.266 Woolcott St Sw/A Relays-B phase IOC,Earth Fault,EFI,Fault Check Signals-11kV trip Field EFI's-NIL See OMS 1823656,1823536,1823658 | January | 2021 | 2021Q3 | 2021 | ZN690:PA12 | ZN690:PA12 | ZN00690/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-01-09 | N | 106.1652 | N | 6 | N | N | 1.1101 | 39.4971 | 155940.5796
[7 empty] | 3049 | 17326 | 1823549 | 2021-01-10 04:26 | 2021-01-10 07:06 | 160 | 11kV | 113681 | 855 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN.12600 Lisarow,Pnl 13 CB tripped. Cause not ascertained. Relays: Basler relay,50TA (IOC),51 AC(O/C trip),timing & lockout relays. Signals: 11kV trip. See OMS 1824710,1824716,1824717,1823549 | January | 2021 | 2021Q3 | 2021 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2021-01-10 | N | 132.9602 | N | 3 | N | N | 1.1101 | 39.4971 | 83074.7218
[7 empty] | 2243 | 6772 | 1823611 | 2021-01-10 16:40 | 2021-01-10 18:01 | 81 | 11kV | 22594 | 1258 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | UGOH | Unplanned | No Weather Impact | N | At ZN.12650 West Gosford,Pnl.6 CB tripped. Cause: UGOH fault short cct. Burnt marks on UGOH at pole GO7453,located between LB40300,S.14851 SW/A. Sw tag left at S.14851. Signals: 11kV trip Relays: E/F,EFI,Timing,lock out Field EFI''s at S.11974 & S.78883 See OMS 1824622,1824626,1823611 | January | 2021 | 2021Q3 | 2021 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2021-01-10 | N | 17.9603 | N | 3 | N | N | 1.1101 | 39.4971 | 16511.0288
[7 empty] | 2876 | 14658 | 1823612 | 2021-01-10 17:00 | 2021-01-10 19:23 | 143 | 11kV | 166184 | 1996 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | At ZN.9700 Kirrawee,Pnl 17 CB tripped,reclosed & locked out. Cause: OH down, C phase HV wire from OH mains to HV UGOH hanging down. Isolated from LB 35835 to S.9881 tee PT.9552. Relays: C phase OC,Timing,Lockout SEF. Signals: 11kV trip,Tx.3 group Earth, Zone Earth EFI's: NIL See OMS 1824656,1824657,1823612,1823613,1823614 | January | 2021 | 2021Q3 | 2021 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2021-01-10 | N | 83.2585 | N | 3 | N | N | 1.1101 | 39.4971 | 121442.3656
[7 empty] | 3016 | 16865 | 1823642 | 2021-01-11 03:16 | 2021-01-11 04:24 | 68 | 11kV | 72730 | 1106 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | U/G Cable | Unplanned | No Weather Impact | N | At ZN.262 Marrickville,Pnl 27 CB tripped. Cause: UG cable fault from S.35139 Horton Amy SW/B to S.2622 Horton Illawarra SW/A Relays: Earth Fault,EFI,Fault Check. Signals: 11kV trip Field EFI's: S.49749,S.5259,S.35139 See OMS 1824588,1823642,1824589 | January | 2021 | 2021Q3 | 2021 | ZN262:PA27 | ZN262:PA27 | ZN00262/000027 | INNER WEST | UG | Not Veg | 2021-01-11 | N | 65.7595 | N | 12 | N | N | 1.1101 | 39.4971 | 53148.9388
[7 empty] | 2155 | 5758 | 1823780 | 2021-01-11 13:05 | 2021-01-11 14:30 | 85 | 11kV | 850 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210091 B Phase Broken Strands at JR-14717 | January | 2021 | 2021Q3 | 2021 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2021-01-11 | N | 85 | N | 12 | N | N | 1.1101 | 39.4971 | 621.1549
[7 empty] | 2456 | 9525 | 1823873 | 2021-01-11 16:27 | 2021-01-11 17:15 | 48 | 11kV | 12240 | 255 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210095 B phase Broken tie SM-20060 Isolated to repair | January | 2021 | 2021Q3 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-01-11 | N | 48 | N | 12 | N | N | 1.1101 | 39.4971 | 8944.631
[7 empty] | 2315 | 7675 | 1823930 | 2021-01-11 19:29 | 2021-01-11 20:43 | 74 | 11kV | 102490 | 1385 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S36200 Empire Bay Panel 9 Poole Belrose Feeder tripped on B and C phase overcurrent, reclose time delay Field EFIs: Nil 73 Maitland Bay Drive Wires Down - Tree/branch brought down OH mains See 1823945, 1823944 for PTs restored at a later time via LV// , 1823930 | January | 2021 | 2021Q3 | 2021 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2021-01-11 | N | 74 | N | 12 | N | N | 1.1101 | 39.4971 | 74896.6691
[7 empty] | 3120 | 18410 | 1823844 | 2021-01-11 19:00 | 2021-01-11 20:45 | 105 | 11kV | 17010 | 162 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 210093 C Phase Earth Fault Arrestor blown at Pole OR-80561.SECTION ISOLATED. LID 210094 Trip n Reclose at 1430. Excluded OMS 1823844 | January | 2021 | 2021Q3 | 2021 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | Unknown | Unknown | 2021-01-11 | N | 105 | N | 12 | N | N | 1.1101 | 39.4971 | 12430.4063
[7 empty] | 2677 | 12075 | 1823942 | 2021-01-11 20:59 | 2021-01-11 22:20 | 81 | 11kV | 81 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210096 C phase 10Amp, substation DOLF | January | 2021 | 2021Q3 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2021-01-11 | N | 81 | N | 12 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 3060 | 17475 | 1823935 | 2021-01-11 20:44 | 2021-01-11 22:55 | 131 | 11kV | 5240 | 40 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S36200 Empire Bay Panel 9 Poole Belrose Feeder tripped on B and C phase overcurrent, reclose time delay Field EFIs: Nil 73 Maitland Bay Drive Wires Down - Tree/branch brought down OH mains See 1823945, 1823944 for PTs restored at a later time via LV// , 1823930 | January | 2021 | 2021Q3 | 2021 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2021-01-11 | N | 131 | N | 12 | N | N | 1.1101 | 39.4971 | 3829.2374
[7 empty] | 3226 | 19629 | 1823928 | 2021-01-11 21:30 | 2021-01-12 00:25 | 175 | 11kV | 175 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210097 SECTION ISOLATED BROKEN HV CROSSARM AT POLE DD-30276. SEE EMERG SI -U109. Excluded OMS REPORT NO 1823928 | January | 2021 | 2021Q3 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2021-01-11 | N | 175 | N | 12 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 2008 | 4005 | 1823952 | 2021-01-11 22:44 | 2021-01-12 00:58 | 134 | 11kV | 123928 | 1666 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN12620 NORAVILLE section of 11kV Panel 11 CP45054 Norvaille tripped Relays: L/O @0034 12/1/21 ZN12620 NORAVILLE Panel 11 tripped when attempting to restore supply from RE45054 & RE45054 Norvaille tripped Relays: OC trip, IOC trip, L/O Panel 11 Relays: B & C phase timed OC, LO, EFI cause:SCADA/telecontrol defect Surge Arrestor on fire at RE45054 Noraville See 1824747,9,53,6 Ex 1823952,68 | January | 2021 | 2021Q3 | 2021 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2021-01-11 | N | 74.3866 | N | 12 | N | N | 1.1101 | 39.4971 | 90562.9271
[7 empty] | 3145 | 18700 | 1823954 | 2021-01-11 23:04 | 2021-01-12 02:34 | 210 | 11kV | 99244 | 1070 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210101 2 fault operations B & C Phase Overcurrent TREE BRANCH ON MAINS AT POLE OS-27058. Excluded OMS 1823955 & 1823954. | January | 2021 | 2021Q3 | 2021 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2021-01-11 | N | 92.7514 | N | 12 | N | N | 1.1101 | 39.4971 | 72524.588
[7 empty] | 2852 | 14387 | 1824022 | 2021-01-12 09:32 | 2021-01-12 10:14 | 42 | 11kV | 65846 | 1616 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210103 1 Fault operations Sensitive Earth Fault, Please do a detailed patrol No Cause found not storm condition Note: @0847 ELBS43996 went out of scan. This switch could have restored 603 customers via SCADA (No SEF detected on SW 61643) | January | 2021 | 2021Q3 | 2021 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2021-01-12 | N | 40.7463 | N | 4 | N | N | 1.1101 | 39.4971 | 48118.3147
[7 empty] | 2734 | 12826 | 1823947 | 2021-01-11 21:22 | 2021-01-12 11:24 | 842 | 11kV | 5052 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 12 PT12717 HENRY YARRA 16K HDO blown bush side phase. Tree Branch on oh mains. Power Pole broke. DW pulled off the box on the pole See 1825013 ex 1823947 | January | 2021 | 2021Q3 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2021-01-11 | N | 842 | N | 12 | N | N | 1.1101 | 39.4971 | 3691.8526
[7 empty] | 3067 | 17612 | 1824053 | 2021-01-12 10:31 | 2021-01-12 12:19 | 108 | 11kV | 210276 | 1947 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Drummoyne Zn Panel 11 and Panel 17 Tripped due to 11kV UG cable strike by contractor. At Sub 3922 Drummoyne Panel 11 and 17 Relays: Earth Fault, Fault Check, EFI Signals: Zone Earth, No.1 Group , 11kV Trip EFIs: 35633, 7738, 2872, 36034, 2646, 47756, 4533 See 1824053, 1824054, 1824107, 1824055, 1824056, 1824059, 1824066 | January | 2021 | 2021Q3 | 2021 | ZN3922:PA11 | ZN3922:PA11 | ZN03922/000011 | INNER WEST | UG | Not Veg | 2021-01-12 | N | 108 | N | 4 | N | N | 1.1101 | 39.4971 | 153663.4987
[7 empty] | 2739 | 13017 | 1824080 | 2021-01-11 12:39 | 2021-01-12 12:39 | 1440 | 11kV | 118188 | 1586 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Sub 2310 Punchbowl Panel No.23 'LB 893 etc" feeder Opened, Reclosed and Opened on Relays: A Protection Trip C phase to N, IOC, Earth Faukt B Protection Trip, IOC, Earth Fault Reclose, EFI Signals: Nil EFIs: Nil 11kV UGOH to Sub 1257 Noble Ave - Short Circuit Faultl See records: 1824692, 1824689, 1824695 withdrawn: 1824080, 1824088, 1824087, 1824085, 1824101 | January | 2021 | 2021Q3 | 2021 | ZN2310:PA23 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2021-01-11 | N | 74.5195 | N | 12 | N | N | 1.1101 | 39.4971 | 86368.3044
[7 empty] | 2507 | 10165 | 1824054 | 2021-01-12 10:34 | 2021-01-12 22:35 | 721 | 11kV | 455268 | 1278 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Drummoyne Zn Panel 11 and Panel 17 Tripped due to 11kV UG cable strike by contractor. At Sub 3922 Drummoyne Panel 11 and 17 Relays: Earth Fault, Fault Check, EFI Signals: Zone Earth, No.2 Group , 11kV Trip EFIs: 35633, 7738, 2872, 36034, 2646, 47756, 4533 See 1824053, 1824054, 1824107, 1824055, 1824056, 1824059, 1824066 | January | 2021 | 2021Q3 | 2021 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2021-01-12 | N | 356.2347 | N | 4 | N | N | 1.1101 | 39.4971 | 332696.4263
[7 empty] | 2613 | 11262 | 1824217 | 2021-01-12 19:49 | 2021-01-13 00:30 | 281.3667 | 11kV | 31231.7 | 111 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | PT 1968 Jensen Lemon TX LV neutral tail burnt away Withdrawn records: 1824218,19,20,26 CC1: 22-"Refer to SOp" | January | 2021 | 2021Q3 | 2021 | ZN1850:PA41 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-01-12 | N | 281.3667 | N | 4 | N | N | 1.1101 | 39.4971 | 22823.2052
[7 empty] | 1958 | 3391 | 1824389 | 2021-01-13 14:00 | 2021-01-13 14:25 | 25 | 11kV | 50 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210106 Possum between HV Bushings | January | 2021 | 2021Q3 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2021-01-13 | N | 25 | N | 2 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 1985 | 3709 | 1824334 | 2021-01-13 15:05 | 2021-01-13 18:19 | 194 | 11kV | 20897 | 108 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210107 B Phase 11kV main resting on pole SI90617. Excluded OMS 1824334 | January | 2021 | 2021Q3 | 2021 | 513:83503 | 513:83503 | ZN00513/083503 | SINGLETON | OH | Not Veg | 2021-01-13 | N | 193.4907 | N | 2 | N | N | 1.1101 | 39.4971 | 15270.9112
[7 empty] | 1869 | 2454 | 1824789 | 2021-01-14 15:12 | 2021-01-14 17:00 | 108 | 11kV | 3564 | 33 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210119 Broken X-arm pole 6k-60095 | January | 2021 | 2021Q3 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2021-01-14 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 2604.4661
[7 empty] | 1709 | 396 | 1824848 | 2021-01-14 18:27 | 2021-01-14 20:45 | 138 | 11kV | 138 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 210124 refer to oms 1824848 replace burnt out LVF assembly | January | 2021 | 2021Q3 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2021-01-14 | N | 138 | N | 3 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 1700 | 330 | 1824868 | 2021-01-14 20:28 | 2021-01-14 21:11 | 43 | 11kV | 27563 | 641 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn15014 Mona Vale - Pnl.18 tripped on ABC phase OC Tree on 11kV mains near USL24463 | January | 2021 | 2021Q3 | 2021 | ZN15014:PA18 | ZN15014:PA18 | ZN15014/000018 | NORTHERN BEACHES | OH | Veg | 2021-01-14 | N | 43 | N | 3 | N | N | 1.1101 | 39.4971 | 20142.2274
[7 empty] | 3204 | 19438 | 1824902 | 2021-01-15 01:31 | 2021-01-15 03:15 | 104 | 11kV | 118551 | 1265 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12620 Noraville - Pnl.8 tripped on Earth fault UG cabe fault in section to S14824 Sw/A Note: EFI did not operate at S18799 See 1825992 1825994 1825997 1825995 1825999 | January | 2021 | 2021Q3 | 2021 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | UG | Not Veg | 2021-01-15 | N | 93.7162 | N | 8 | N | N | 1.1101 | 39.4971 | 86633.5741
[7 empty] | 1901 | 2814 | 1824903 | 2021-01-15 01:58 | 2021-01-15 04:00 | 122 | 11kV | 26224 | 241 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.1 tripped on Earth Fault UG cable fault between S8775 & S7616 tee S791 See 1825989 1825990 1825991 | January | 2021 | 2021Q3 | 2021 | ZN2466:PA1 | ZN2466:PA1 | ZN02466/000001 | PARRAMATTA | UG | Not Veg | 2021-01-15 | N | 108.8133 | N | 8 | N | N | 1.1101 | 39.4971 | 19163.7257
[7 empty] | 3274 | 20124 | 1824913 | 2021-01-15 05:06 | 2021-01-15 10:05 | 299 | 11kV | 1794 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210125 Single phase DOLF : 20 Amp Excluded OMS 1824913 | January | 2021 | 2021Q3 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-01-15 | N | 299 | N | 8 | N | N | 1.1101 | 39.4971 | 1311.0023
[7 empty] | 2000 | 3805 | 1824941 | 2021-01-15 09:26 | 2021-01-15 11:35 | 129 | 11kV | 387 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210126 Single phase DOLF : 5 Amp Excluded OMS 1824941 | January | 2021 | 2021Q3 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2021-01-15 | N | 129 | N | 8 | N | N | 1.1101 | 39.4971 | 282.8082
[7 empty] | 1715 | 445 | 1825018 | 2021-01-15 12:32 | 2021-01-15 13:01 | 29 | 11kV | 32355 | 1170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210127 1 fault operation A & B Phases Overcurrent Branch on OHM cnr Milford & Annie St Wickham Excluded OMS 1825018 | January | 2021 | 2021Q3 | 2021 | 204:82705 | 204:82705 | ZN00204/082705 | NEWCASTLE | OH | Veg | 2021-01-15 | N | 27.6538 | N | 8 | N | N | 1.1101 | 39.4971 | 23644.0797
[7 empty] | 1977 | 3653 | 1824998 | 2021-01-15 11:48 | 2021-01-15 14:00 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210129 DOLF : 10 Amp Excluded OMS 1824998 | January | 2021 | 2021Q3 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-01-15 | N | 132 | N | 8 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 3228 | 19640 | 1825475 | 2021-01-15 16:12 | 2021-01-15 19:00 | 168 | 11kV | 2016 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210134 Single phase DOLF : 20 Amp 2 x 20A FUSES AT L/F 74748 1 X 10A fuse at PT 70386 Excluded OMS 1825075/1825094 | January | 2021 | 2021Q3 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-01-15 | N | 168 | N | 8 | N | N | 1.1101 | 39.4971 | 1473.2333
[7 empty] | 3022 | 16976 | 1825117 | 2021-01-15 23:31 | 2021-01-16 01:00 | 89 | 11kV | 46992 | 528 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.3 tripped on Earth Fault UG cable fault in frontline section of feeder between Pnl.3 and S64501 Sw/A | January | 2021 | 2021Q3 | 2021 | ZN931:PA3 | ZN931:PA3 | ZN00931/000003 | SYDNEY | UG | Not Veg | 2021-01-15 | N | 89 | N | 8 | N | N | 1.1101 | 39.4971 | 34340.3676
[7 empty] | 2532 | 10417 | 1825119 | 2021-01-16 00:13 | 2021-01-16 02:18 | 125 | 11kV | 105368 | 1006 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At ZN.3154 St Ives,Pnl 16 CB tripped. Cause not ascertained. Feeder patrolled all supply restored checked by DOp. Relays: C phase O/C,E/F,EFI. Field EFI's: S7413,S462,S479,S477,S464,S465 See OMS 1825637,1825638,1825119 | January | 2021 | 2021Q3 | 2021 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | UG | Not Veg | 2021-01-16 | N | 104.7396 | N | 6 | N | N | 1.1101 | 39.4971 | 76999.8266
[7 empty] | 3041 | 17222 | 1825126 | 2021-01-16 02:31 | 2021-01-16 04:49 | 138 | 11kV | 4169 | 56 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.14143 Somersby,Pnl.6 CB tripped. Cause: UG fault,suspected fault in sect of 11kV between S.14278 SW/B to S.18084 SW/A to S.64884 to Open bonds. Relays: E/F,EFI Field EFI's: S65180,S18379,S14634,S18540,S18454,S18253,S18339,S18636,S18256,S14278. See OMS 1825634,1825635,1825636 | January | 2021 | 2021Q3 | 2021 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | UG | Not Veg | 2021-01-16 | N | 74.4464 | N | 6 | N | N | 1.1101 | 39.4971 | 3046.5822
[7 empty] | 1823 | 1862 | 1825163 | 2021-01-16 11:02 | 2021-01-16 13:15 | 133 | 11kV | 399 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210138 B Phase Broken llc dropper lead Excluded oms 1825163 | January | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-01-16 | N | 133 | N | 6 | N | N | 1.1101 | 39.4971 | 291.5774
[7 empty] | 3185 | 19271 | 1825212 | 2021-01-16 16:37 | 2021-01-16 18:19 | 102 | 11kV | 10903 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Rec CP49506 tripped & locked out on O/C & SEF trip. Cause not ascertained. See OMS 1825697,1825699,1825212,1825227 | January | 2021 | 2021Q3 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-01-16 | N | 81.3657 | N | 6 | N | N | 1.1101 | 39.4971 | 7967.5908
[7 empty] | 2403 | 9027 | 1825215 | 2021-01-16 16:52 | 2021-01-17 01:50 | 538 | 11kV | 337552 | 1089 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.3154 St Ives,Pnl.17 CB tripped & locked out. Cause: UG cable fault between S.7416 Yarrabung Grevilea to S.7417 Yarrabung Kelvin tee S.3316 Torokina Wirra. Relays: C phase IOC & earth leakage,timing relay,lockour relay,EFI Signals: 11kV trip,Tx.3 GE,ZE Field EFI's: S.62840,S.35868,S.4914,S.4020,S.7416 Abnormal switching: LB.64168 closed - AB.2082 open & defective. LB.64433 closed - AB.1388 open (UGOH bond burnt) See OMS 1825765,1825766,1825216,1825215,1825228 | January | 2021 | 2021Q3 | 2021 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | UG | Not Veg | 2021-01-16 | N | 309.9651 | N | 6 | N | N | 1.1101 | 39.4971 | 246673.0455
[7 empty] | 2016 | 4112 | 1825276 | 2021-01-17 06:03 | 2021-01-17 06:50 | 47 | 11kV | 3854 | 82 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.2466 Flemington,Pnl.11 Fdr CB tripped. Cause: UG cable fault,section of Fdr from S.8914 Parramatta Telopea No.4 to S.1766 Parramatta Telopea. Relays: EF,EFI,FC Signals:11kV trip Field EFI's: S.5298,S.8916,S.8917,S.8915,S.8764,S.8603,S.8914. | January | 2021 | 2021Q3 | 2021 | ZN2466:PA11 | ZN2466:PA11 | ZN02466/000011 | STRATHFIELD | UG | Not Veg | 2021-01-17 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 2816.3895
[7 empty] | 2252 | 6860 | 1825244 | 2021-01-16 23:36 | 2021-01-17 07:27 | 471 | 11kV | 195492 | 1223 | HV | Animal Bird | Animal | Bond | Unplanned | No Weather Impact | N | At ZN.12580 Erina,Pnl.7 Fdr CB tripped. Cause: Animal/Birds,fault current possible caused burnt off bond on sect of 11kV Fdr tee off betwen S.50037 & AB.43236. Relays: A phase inst.E/F,EFI Field EFI's: S.50037 Signals: 11kV trip. See OMS 1825904,1825905,1825906,1825908,1825910,1825244,1825245,1825258 | January | 2021 | 2021Q3 | 2021 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Not Veg | 2021-01-16 | N | 159.8463 | N | 6 | N | N | 1.1101 | 39.4971 | 142859.7876
[7 empty] | 2236 | 6719 | 1825285 | 2021-01-17 08:18 | 2021-01-17 16:02 | 464.1333 | 11kV | 42700.2667 | 92 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 210143 Single phase Broken live line clamp pole SM21018 | January | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-01-17 | N | 464.1333 | N | 3 | N | N | 1.1101 | 39.4971 | 31204.0954
[7 empty] | 2760 | 13272 | 1825256 | 2021-01-17 23:46 | 2021-01-18 00:23 | 37 | 11kV | 18485 | 1091 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.5868 Gore Hill,Pnl.6 CB tripped. Cause: UG cable fault from S.8112 SW/B to S.3417 SW/A. S.5632 C/S DOp & Asset access required to reset EFI. Relays: O/C & E/F B phase,fault check,EFI Field EFI's: S.3932,S.5632,S.3454,S.63282,S.63283,S.8112 Signals 11kV trip. See OMS 1825745,1825749,1825750,1825256 | January | 2021 | 2021Q3 | 2021 | ZN5868:PA6 | ZN5868:PA6 | ZN05868/000006 | NORTH SYDNEY | UG | Not Veg | 2021-01-17 | N | 16.9432 | N | 3 | N | N | 1.1101 | 39.4971 | 13508.2928
[7 empty] | 2442 | 9461 | 1825364 | 2021-01-18 04:03 | 2021-01-18 05:17 | 74 | 11kV | 6142 | 83 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210152 Isolated section to repair blown tapping ABS 74931. Also see report 210151 Excluded OMS 1825360,1825364 | January | 2021 | 2021Q3 | 2021 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2021-01-18 | N | 74 | N | 7 | N | N | 1.1101 | 39.4971 | 4488.3924
[7 empty] | 2511 | 10226 | 1825365 | 2021-01-18 04:14 | 2021-01-18 10:00 | 346 | 11kV | 27220 | 148 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210150 3 fault operations 3 phase Overcurrent, Earth Fault 11kv on ground at HR-42059. Excluded OMS 1825365. 1825369 | January | 2021 | 2021Q3 | 2021 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2021-01-18 | N | 183.9189 | N | 7 | N | N | 1.1101 | 39.4971 | 19891.5731
[7 empty] | 2733 | 12809 | 1825360 | 2021-01-18 02:01 | 2021-01-18 13:10 | 669 | 11kV | 3518 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210151 3 fault operations Also see report 210152 Replace arrestors @ sub 71629 Excluded OMS 1825362, 1825374,1825380 | January | 2021 | 2021Q3 | 2021 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2021-01-18 | N | 270.6154 | N | 7 | N | N | 1.1101 | 39.4971 | 2570.8506
[7 empty] | 1707 | 393 | 1825404 | 2021-01-18 09:02 | 2021-01-18 16:15 | 433 | 11kV | 866 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210154 Substation DOLF Excluded OMS 1825404 | January | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2021-01-18 | N | 433 | N | 7 | N | N | 1.1101 | 39.4971 | 632.8473
[7 empty] | 2266 | 7076 | 1825568 | 2021-01-18 16:58 | 2021-01-18 19:20 | 142 | 11kV | 86940 | 743 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | No Weather Impact | N | At ZN.2196 Milperra,Pnl.26 Fdr CB tripped. Cause: Flashover/Arching,Baloon has made contact with the 11kV mains o/s 12 Sixth Ave Condell Park. Pnl.26 CB failed to spring charge & electrically closed. DOp Keen had to manually spring charge & close (DMA) created. Relays: E/F,Fault check,EFI Signals:11kV trip Field EFI's-NIL See OMS 1825934,1825937,1825939,568,569,572,575,579 | January | 2021 | 2021Q3 | 2021 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-01-18 | N | 117.0121 | N | 7 | N | N | 1.1101 | 39.4971 | 63533.1877
[7 empty] | 2956 | 16017 | 1825563 | 2021-01-18 16:00 | 2021-01-18 20:44 | 284 | 11kV | 852 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 210157 11KV links burnt up on Reclosers 34992 & 34995 unable to use 34992. backup supply to Airport. see lid 210156 as well | January | 2021 | 2021Q3 | 2021 | 229:34992 | 229:34992 | ZN00229/034992 | PORT STEPHENS | OH | Not Veg | 2021-01-18 | N | 284 | N | 7 | N | N | 1.1101 | 39.4971 | 622.6165
[7 empty] | 3290 | 20436 | 1825565 | 2021-01-18 16:41 | 2021-01-18 21:02 | 261.05 | 11kV | 3387.3 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 210156 11KV links burnt up on Reclosers 34992 & 34995 unable to use 34992. backup supply to Airport. | January | 2021 | 2021Q3 | 2021 | 229:34989 | 229:34989 | ZN00229/034989 | PORT STEPHENS | OH | Not Veg | 2021-01-18 | N | 260.5615 | N | 7 | N | N | 1.1101 | 39.4971 | 2475.3389
[7 empty] | 2405 | 9076 | 1825617 | 2021-01-19 01:33 | 2021-01-19 04:10 | 157 | 11kV | 250260 | 1605 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At S.16194 Manly Hospital No.3 SW/B CB tripped. Cause not ascertained. Relays: OC trip C phase,EFI Signals: 11kV trip Field EFI's at Subs S.16136,S.16721 See OMS 1825924,1825926,1825617,1825619,1825629,1825621,1825624 | January | 2021 | 2021Q3 | 2021 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2021-01-19 | N | 155.9252 | N | 4 | N | N | 1.1101 | 39.4971 | 182882.6266
[7 empty] | 2519 | 10299 | 1825630 | 2021-01-19 02:18 | 2021-01-19 04:55 | 157 | 11kV | 135324 | 1410 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 210159 Isolated fault in UG cable between 41629 & 36529, repairs required. | January | 2021 | 2021Q3 | 2021 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | UG | Not Veg | 2021-01-19 | N | 95.9745 | N | 4 | N | N | 1.1101 | 39.4971 | 98890.7878
[7 empty] | 2149 | 5671 | 1825702 | 2021-01-19 09:49 | 2021-01-19 14:38 | 289 | 11kV | 11182 | 58 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210161 Tree brought down 11kV Mains along Swan Bay Rd 1.5km South of the Pacific Highway near sub 2246, a few ties on upstream poles had snapped. | January | 2021 | 2021Q3 | 2021 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2021-01-19 | N | 192.7931 | N | 4 | N | N | 1.1101 | 39.4971 | 8171.4758
[7 empty] | 1832 | 2021 | 1825829 | 2021-01-19 17:36 | 2021-01-19 18:45 | 69 | 11kV | 69 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210163 A Phase DOLF : 16 Amp Possum | January | 2021 | 2021Q3 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-01-19 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 2853 | 14400 | 1825864 | 2021-01-20 03:17 | 2021-01-20 04:53 | 95.9 | 11kV | 156988.3 | 1637 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Recloser CP.49612 tripped & locked out on O/C. Cause: Tree/branch on OH mains,USL 43367. See OMS 1825864,1825868 | January | 2021 | 2021Q3 | 2021 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2021-01-20 | N | 95.9 | N | 5 | N | N | 1.1101 | 39.4971 | 114722.4193
[7 empty] | 2082 | 4991 | 1825877 | 2021-01-20 07:32 | 2021-01-20 09:55 | 143 | 11kV | 95641 | 2189 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Zn12620 Noraville - Pnl.7 tripped on Earth Fault Abnormal: NAR67107 T2 - AB42740 Closed with AB44459 Open, LB49854 Closed with USL41939 Open During switching for NAR67107 T2, USL41939 fell apart and flashed over. HV into LV. See 1826128 1826129 1826130 1826131 | January | 2021 | 2021Q3 | 2021 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2021-01-20 | N | 43.6916 | N | 5 | N | N | 1.1101 | 39.4971 | 69891.6219
[7 empty] | 2043 | 4570 | 1825898 | 2021-01-20 09:16 | 2021-01-20 11:05 | 109 | 11kV | 109 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210169 C Phase DOLF : 10 Amp Bird on transformer HV, Fuse replaced. Excluded OMS 1825898 | January | 2021 | 2021Q3 | 2021 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2021-01-20 | N | 109 | N | 5 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 2862 | 14461 | 1825971 | 2021-01-20 12:55 | 2021-01-20 14:44 | 109 | 11kV | 33245 | 333 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1068 Lidcombe - Pnl.21 tripped on B Phase OC & Earth Fault UG cable fault between S61577, S65606 tee S2019 See 1826139 1826138 | January | 2021 | 2021Q3 | 2021 | ZN1068:PA21 | ZN1068:PA21 | ZN01068/000021 | CUMBERLAND | UG | Not Veg | 2021-01-20 | N | 99.8348 | N | 5 | N | N | 1.1101 | 39.4971 | 24294.4654
[7 empty] | 2402 | 9020 | 1826020 | 2021-01-20 14:39 | 2021-01-20 15:31 | 52 | 11kV | 8632 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC44916 Kunarra Rd - Tripped on OC Tree on OH mains between AB43318 and USL40234 tee PT13872 DOp removed tree | January | 2021 | 2021Q3 | 2021 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2021-01-20 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 6308.011
[7 empty] | 1836 | 2043 | 1826140 | 2021-01-21 10:48 | 2021-01-21 11:40 | 52 | 11kV | 624 | 12 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210174 Substation DOLF : 10 Amp Bird contacted mains. Excluded OMS 1826140 | January | 2021 | 2021Q3 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2021-01-21 | N | 52 | N | 1 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 3035 | 17182 | 1826354 | 2021-01-22 12:56 | 2021-01-22 13:55 | 59 | 11kV | 16641 | 317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.8100 Green Square,Pnl.22 CB tripped. Cause: UG cable fault between S.8181 Huntley Burrows No.2 to S.8719 Huntley Burrows No.3 & S.66064 Hadfields Nassau. Relays: Faukt check,B ph O/C,Earth Fault. Signals: Tx.2 Group Earth. EFI's: Pa.22,S.8726,S.36242,S.36243,S.1190,S8181 See OMS 1827357,1827359,1827362,1826354 | January | 2021 | 2021Q3 | 2021 | ZN8100:PA22 | ZN8100:PA22 | ZN08100/000022 | SYDNEY | UG | Not Veg | 2021-01-22 | N | 52.4953 | N | 4 | N | N | 1.1101 | 39.4971 | 12160.752
[7 empty] | 2424 | 9269 | 1826349 | 2021-01-22 13:15 | 2021-01-22 14:40 | 85 | 11kV | 510 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210178 No protection operated, isolated due to conductor hanging low so could be repaired safely. Broken stranding between poles 60-70042 and 60-70044. | January | 2021 | 2021Q3 | 2021 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2021-01-22 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 372.693
[7 empty] | 3048 | 17291 | 1826470 | 2021-01-22 21:06 | 2021-01-22 22:28 | 82 | 11kV | 62346 | 983 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.7481 Darling Harbour,Pnl.14 CB tripped. Cause: UG cable fault from ZN.7481 Darling Harbour Pa14 to S.1634 & S.8986. Relays: B ph E/F Signals: Tx.12 group earth,Pnl.14 L,EFI Field EFI's: NIL Abnormal Swtiching: S.35376 SW/A closed,S.7567 SW/D open. See OMS 1827453, 1827465,1826470 | January | 2021 | 2021Q3 | 2021 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2021-01-22 | N | 63.4242 | N | 4 | N | N | 1.1101 | 39.4971 | 45560.6179
[7 empty] | 1957 | 3387 | 1826479 | 2021-01-23 06:11 | 2021-01-23 08:45 | 154 | 11kV | 3388 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210185 B Phase DOLF : 63 Amp Excluded OMS 1826479 | January | 2021 | 2021Q3 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2021-01-23 | N | 154 | N | 4 | N | N | 1.1101 | 39.4971 | 2475.8505
[7 empty] | 3028 | 17053 | 1826447 | 2021-01-22 18:53 | 2021-01-23 11:41 | 1008.5167 | 11kV | 20170.3333 | 20 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Lightning Arrestor | Unplanned | No Weather Impact | N | At PT.63392 Marlows Creek No.2, HDO 16A fuse blown. Cause: Lightning/Surge Arrestor. See OMS 1826447,1826490,1826491 CC1: 11-"Despatch to re-issue" FRC1: 300-"Specify details by voice" | January | 2021 | 2021Q3 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2021-01-22 | N | 1008.5167 | N | 4 | N | N | 1.1101 | 39.4971 | 14739.8847
[7 empty] | 2655 | 11803 | 1826579 | 2021-01-23 18:47 | 2021-01-23 22:03 | 196 | 11kV | 74579 | 1087 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN.1648 Enfield,Pnl.10 CB tripped. Cause: UG cable fault between S.2631 Verona Steet SW/B to S.1081 Toyo Australia SW/A. Relays: A&C phase OC,EFI Signals: 11kV trip,Tx.1 Group Earth,Zone Earth Field EFI's: S.2512,S.5897,S.49250,S.1711,S.35721,S.35532,S.36054,S.79653,S.825,S.1081 See OMS 1827577,1827579,1826579,1826589 | January | 2021 | 2021Q3 | 2021 | ZN1648:PA10 | ZN4853:PA11 | ZN04853/000011 | STRATHFIELD | UG | Not Veg | 2021-01-23 | N | 68.6099 | N | 4 | N | N | 1.1101 | 39.4971 | 54500.1335
[7 empty] | 2546 | 10600 | 1826601 | 2021-01-23 21:50 | 2021-01-23 23:45 | 115 | 11kV | 14814 | 138 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Hot >35C | N | At ZN.14143 Somersby,Pnl.21 CB tripped. Cause not ascertained. Fdr did not reclose,TPE notified,patrolled by DOp,nothing found. Relays: A&B phase IOC,EFI Signals: 11kV trip Field EFI's: S.18108,S.18052,S.18270,S.18849,S.14902,S.49681,S.14956 & UGOH below. See OMS 1827558,1827559,1826601 | January | 2021 | 2021Q3 | 2021 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | UG | Not Veg | 2021-01-23 | N | 107.3478 | N | 4 | N | N | 1.1101 | 39.4971 | 10825.6343
[7 empty] | 2860 | 14452 | 1826606 | 2021-01-23 22:41 | 2021-01-24 00:04 | 83 | 11kV | 10126 | 122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.167 Auburn,Pnl.2 CB tripped. Cause: UG fault from ZN.167 Pnl.14 to S.8437. Relays: C phase IOC,E/F,Fault check,EFI Signals: 11kV trip Field EFI's: S.7794,S.8353,S.7561,S.2377,S.2749,S.8437 | January | 2021 | 2021Q3 | 2021 | ZN167:PA2 | ZN167:PA2 | ZN00167/000002 | CUMBERLAND | UG | Not Veg | 2021-01-23 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 7399.7821
[7 empty] | 2508 | 10209 | 1826642 | 2021-01-24 09:26 | 2021-01-24 11:50 | 144 | 11kV | 576 | 4 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210192 B Phase DOLF : 10 Amp Excluded OMS 1826642 | January | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2021-01-24 | N | 144 | N | 1 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 3082 | 17834 | 1826740 | 2021-01-25 00:50 | 2021-01-25 04:58 | 248 | 11kV | 326351 | 1515 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN.129 Hunters Hill,Pnl.56 CB tripped. Cause: UG cable fault between S.35155 SW/B to S.47769 SW/A to S.8182 SW/B. Relays: A prot; C ph O/C,IOC B prot; C ph O/C,E/F,IOC EFI's: Pa.56,S.3342,S.7577,S.7578,S.7684. At ZN.129 Hunters Hill,Pnl.43 CB tripped when trying back the bottom sect of Pnl.56 from S.8023 SW/B. EFI later found at S.35155 (missed when DOp first attended-difficult spot) See OMS 1827822,823,829,1826740 | January | 2021 | 2021Q3 | 2021 | ZN129:PA56 | ZN129:PA56 | ZN00129/000056 | LANE COVE | UG | Not Veg | 2021-01-25 | N | 215.4132 | N | 8 | N | N | 1.1101 | 39.4971 | 238487.6851
[7 empty] | 1754 | 956 | 1826786 | 2021-01-25 09:42 | 2021-01-25 13:05 | 203 | 11kV | 406 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | LID 210209 Single phase DOLF : 10 Amp Excluded OMS 1826786 | January | 2021 | 2021Q3 | 2021 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2021-01-25 | N | 203 | N | 8 | N | N | 1.1101 | 39.4971 | 296.6928
[7 empty] | 2643 | 11609 | 1826850 | 2021-01-25 13:32 | 2021-01-25 14:47 | 75 | 11kV | 22285 | 332 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2400 Berowra - Pnl.23 tripped, reclosed & locked out on: Earth Fault UG cable fault between S.4402 and S.35269 See 1827954 1827955 | January | 2021 | 2021Q3 | 2021 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | UG | Not Veg | 2021-01-25 | N | 67.1235 | N | 8 | N | N | 1.1101 | 39.4971 | 16285.2207
[7 empty] | 1857 | 2304 | 1826857 | 2021-01-25 13:56 | 2021-01-25 15:17 | 81 | 11kV | 130005 | 1605 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.24 tripped, reclosed & tripped on: A Phase IOC Abnormal: LB3029 Closed with AB1552 Open (DMA) Tree on OH mains removed by DOp. | January | 2021 | 2021Q3 | 2021 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | OH | Veg | 2021-01-25 | N | 81 | N | 8 | N | N | 1.1101 | 39.4971 | 95003.8195
[7 empty] | 2068 | 4857 | 1826732 | 2021-01-25 00:03 | 2021-01-25 16:15 | 972 | 11kV | 144828 | 149 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | S63658 Pacific Government No.2 - 2 x HV fuses operated Transformer failure. Restored via LV // | January | 2021 | 2021Q3 | 2021 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | UG | Not Veg | 2021-01-25 | N | 972 | N | 8 | N | N | 1.1101 | 39.4971 | 105836.0307
[7 empty] | 2691 | 12273 | 1826868 | 2021-01-25 14:03 | 2021-01-25 17:24 | 201 | 11kV | 121872 | 696 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn.3425 Castle Cove - Pnl.7 tripped on ABC phase OC Abnormal: S7313 Sw/D Closed with S4391 Sw/B Open ( DMA) UG cable fault between S3867, S7313 & S3450 See 1827963 1827964 1827965 | January | 2021 | 2021Q3 | 2021 | ZN3425:PA7 | ZN3425:PA7 | ZN03425/000007 | WILLOUGHBY | UG | Not Veg | 2021-01-25 | N | 175.1034 | N | 8 | N | N | 1.1101 | 39.4971 | 89060.463
[7 empty] | 2814 | 13994 | 1826910 | 2021-01-25 16:10 | 2021-01-25 17:47 | 97 | 11kV | 4564 | 52 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | Zn1610 Homebush Bay - Pnl.10 tripped on B phase to Earth End box fault at S7138 Sw/B. Front line section of feeder isolated See 1827971 1827972 | January | 2021 | 2021Q3 | 2021 | ZN1610:PA10 | ZN1610:PA10 | ZN01610/000010 | PARRAMATTA | UG | Not Veg | 2021-01-25 | N | 87.7692 | N | 8 | N | N | 1.1101 | 39.4971 | 3335.2366
[7 empty] | 2832 | 14183 | 1826940 | 2021-01-25 17:22 | 2021-01-25 19:44 | 142 | 11kV | 284 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210198 Single phase DOLF : 10 Amp Bird Excluded OMS 1826940 | January | 2021 | 2021Q3 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2021-01-25 | N | 142 | N | 8 | N | N | 1.1101 | 39.4971 | 207.5388
[7 empty] | 2686 | 12226 | 1827004 | 2021-01-26 05:25 | 2021-01-26 07:07 | 102 | 11kV | 140182 | 1477 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn9118 Cronulla - Pnl.22 tripped on B phase Earth leakage UG cable fault between S.9305 Sw/B and S.9406 Sw/A See 1827731 1827732 | January | 2021 | 2021Q3 | 2021 | ZN9118:PA22 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | UG | Not Veg | 2021-01-26 | N | 94.91 | N | 12 | N | N | 1.1101 | 39.4971 | 102440.8709
[7 empty] | 2014 | 4091 | 1827012 | 2021-01-26 07:18 | 2021-01-26 09:11 | 113 | 11kV | 203435 | 1805 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn5868 Gore Hill - Pnl.30 tripped on Earth Fault UG cable fault between S6916 Sw/D, S6438 Sw/A and S8079 Sw/D See 1827725 1827727 | January | 2021 | 2021Q3 | 2021 | ZN5868:PA30 | ZN5868:PA30 | ZN05868/000030 | LANE COVE | UG | Not Veg | 2021-01-26 | N | 112.7064 | N | 12 | N | N | 1.1101 | 39.4971 | 148664.2977
[7 empty] | 2268 | 7112 | 1827019 | 2021-01-26 08:03 | 2021-01-26 13:45 | 342 | 11kV | 272815 | 1502 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn15009 Manly - Pnl.12 tripped on Earth Fault EFI @ S50491 failed to operate & EFI @ S15820 suspected down from previous fault. Abnormal: USL22305 to USL21129 tee S15255 Out of service with S16909 Sw/B Closed (DMA) UG cable fault between S15820 Sw/B to S50491 Sw/A See 1827717 1827718 | January | 2021 | 2021Q3 | 2021 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2021-01-26 | N | 181.6345 | N | 12 | N | N | 1.1101 | 39.4971 | 199365.1553
[7 empty] | 3081 | 17832 | 1827003 | 2021-01-26 04:50 | 2021-01-26 16:00 | 670 | 11kV | 91470 | 429 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC 45189 Cooks Peats Ridge 0.5 tripped on: O/C Tree brought down OH mains near PT49032 Tree fallen and brushed hv mains on the way down causing clash and hv mains to fall down Earthed hv and made repairs and restrung hv, poles in ok condition slight lean on both poles after shock load of fallen hv | January | 2021 | 2021Q3 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-01-26 | N | 213.2168 | N | 12 | N | N | 1.1101 | 39.4971 | 66843.5781
[7 empty] | 3007 | 16748 | 1827117 | 2021-01-26 15:23 | 2021-01-26 16:31 | 68 | 11kV | 118373 | 1917 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn5868 Gore Hill - Pnl.7 tripped on A & C phase O/C Abnormal: S6438 Sw/A Open with S1960 Sw/B Closed (DMA) UG cable fault between S31391, S829 & S1960 See 1827691 1827693 | January | 2021 | 2021Q3 | 2021 | ZN5868:PA30 | ZN5868:PA30 | ZN05868/000030 | LANE COVE | UG | Not Veg | 2021-01-26 | N | 61.7491 | N | 12 | N | N | 1.1101 | 39.4971 | 86503.497
[7 empty] | 2550 | 10623 | 1827109 | 2021-01-26 14:55 | 2021-01-26 16:37 | 102 | 11kV | 122752 | 1209 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn129 Hunters Hill - Pnl.38 tripped on C phase IOC UG cable fault between S.49203 and S.7579 See 1827696 1827697 | January | 2021 | 2021Q3 | 2021 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | UG | Not Veg | 2021-01-26 | N | 101.5318 | N | 12 | N | N | 1.1101 | 39.4971 | 89703.541
[7 empty] | 3019 | 16930 | 1827130 | 2021-01-26 15:32 | 2021-01-26 16:43 | 71 | 11kV | 163726 | 2306 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | Ex Zn10995 Riverwood Pnl.2 - Centre phase bond burnt off 11kV UGOH below S.10128 Sw/B | January | 2021 | 2021Q3 | 2021 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | Unknown | Unknown | 2021-01-26 | N | 71 | N | 12 | N | N | 1.1101 | 39.4971 | 119646.1317
[7 empty] | 1747 | 854 | 1827206 | 2021-01-26 17:40 | 2021-01-26 18:36 | 56 | 11kV | 9658 | 1471 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2635 St Peters - Pnl.27 tripped on Earth Fault UG cable fault between S6103 , S6362 and S3272 See 1827679 1827680 1827681 | January | 2021 | 2021Q3 | 2021 | ZN2568:PA27 | ZN2568:PA27 | ZN02568/000027 | INNER WEST | UG | Not Veg | 2021-01-26 | N | 6.5656 | N | 12 | N | N | 1.1101 | 39.4971 | 7057.7815
[7 empty] | 2152 | 5730 | 1827189 | 2021-01-26 17:24 | 2021-01-26 18:59 | 95 | 11kV | 49790 | 556 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn1193 Lindfield - Pnl.10 tripped on IOC and Earth Fault UG cable fault between S.7949 and S.5124 See 1827269 1827683 CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | January | 2021 | 2021Q3 | 2021 | ZN1193:PA10 | ZN1193:PA10 | ZN01193/000010 | KU-RING-GAI | UG | Not Veg | 2021-01-26 | N | 89.5504 | N | 12 | N | N | 1.1101 | 39.4971 | 36385.0634
[7 empty] | 2639 | 11562 | 1827165 | 2021-01-26 16:20 | 2021-01-26 19:05 | 165 | 11kV | 126286 | 1717 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Hot >35C | N | LID 210201 2 fault operations Earth Fault; Overcurrent HV hazemyer failure at HS24117 rebecca rd sub SW29873 prot 50T ABC Excluded OMS 1827165 | January | 2021 | 2021Q3 | 2021 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | Unknown | Not Veg | 2021-01-26 | N | 73.5504 | N | 12 | N | N | 1.1101 | 39.4971 | 92286.084
[7 empty] | 3192 | 19330 | 1827239 | 2021-01-26 18:41 | 2021-01-26 20:17 | 96 | 11kV | 131040 | 1365 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | iR40118 Murrawal Kilpa 0.2 - 11kV Bond burnt off on C phase (Pole WY983) | January | 2021 | 2021Q3 | 2021 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2021-01-26 | N | 96 | N | 12 | N | N | 1.1101 | 39.4971 | 95760.167
[7 empty] | 2110 | 5259 | 1827301 | 2021-01-26 21:17 | 2021-01-26 23:05 | 108 | 11kV | 253380 | 2453 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn36000 Olympic Park - Pnl.7 tripped on A phase Earth Fault Abnormal:S3305 Sw/B Closed with S2256 Sw/A Open (11kV DMA) Multiple LV //'s due to LV DMAs along Pnl.6 & 7 Olympic Park Cause: UG cable fault in frontline section of feeder between Pnl.7, S5609, S78053, S7925 & S2543 See 1827661 | January | 2021 | 2021Q3 | 2021 | ZN36000:PA7 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2021-01-26 | N | 103.2939 | N | 12 | N | N | 1.1101 | 39.4971 | 185162.6306
[7 empty] | 2025 | 4213 | 1827323 | 2021-01-27 01:30 | 2021-01-27 04:30 | 180 | 11kV | 363187 | 3158 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn36300 Balgowlah North - Pnl.11 tripped on Earth Fault Note: EFI did not operate at S46415 & S17104 UG cable fault between S15385, S16510 and S16509 See 1827975 1827976 | January | 2021 | 2021Q3 | 2021 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2021-01-27 | N | 115.0054 | N | 10 | N | N | 1.1101 | 39.4971 | 265406.3474
[7 empty] | 1801 | 1603 | 1827380 | 2021-01-27 07:57 | 2021-01-27 09:25 | 88 | 11kV | 72748 | 1044 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 210211 3 fault operations C Phase Instantaneous Overcurrent Suspected U/G Cable fault Excluded OMS 1827380 | January | 2021 | 2021Q3 | 2021 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | UG | Not Veg | 2021-01-27 | N | 69.682 | N | 10 | N | N | 1.1101 | 39.4971 | 53162.0927
[7 empty] | 2819 | 14040 | 1827471 | 2021-01-27 10:39 | 2021-01-27 12:10 | 91 | 11kV | 273 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210208 A Phase DOLF : 10 Amp Excluded OMS 1827471 | January | 2021 | 2021Q3 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2021-01-27 | N | 91 | N | 10 | N | N | 1.1101 | 39.4971 | 199.5003
[7 empty] | 2514 | 10257 | 1827517 | 2021-01-27 11:51 | 2021-01-27 12:53 | 62 | 11kV | 172528 | 3008 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn15005 Belrose - Pnl.2 tripped on A & C phase OC Abnormal: USL23766 Open with LB77808 Closed (DMA - frontline section of Pnl.8 Killarney Out of service) Tree on OH mains in Parni Pl, Frenches Forest See 1827989 1827990 | January | 2021 | 2021Q3 | 2021 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Veg | 2021-01-27 | N | 57.3564 | N | 10 | N | N | 1.1101 | 39.4971 | 126078.3737
[7 empty] | 1969 | 3586 | 1827277 | 2021-01-27 12:10 | 2021-01-27 15:04 | 174 | 11kV | 17874 | 105 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 210213 3 Phase Interupted to replace defective Tx. DQ Excluded OMS 1827277 | January | 2021 | 2021Q3 | 2021 | 213:33769 | 213:33769 | ZN00213/033769 | NEWCASTLE | OH | Not Veg | 2021-01-27 | N | 170.2286 | N | 10 | N | N | 1.1101 | 39.4971 | 13061.792
[7 empty] | 1879 | 2542 | 1827484 | 2021-01-27 11:04 | 2021-01-27 15:38 | 274 | 11kV | 143290 | 830 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn12580 Erina - Pnl.8 tripped on: C phase IOC and OC UG cable fault between S41388 Sw/B, S18045 Sw/A tee S14360 See 1827981 1827983 1827984 | January | 2021 | 2021Q3 | 2021 | ZN12580:PA8 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | UG | Not Veg | 2021-01-27 | N | 172.6386 | N | 10 | N | N | 1.1101 | 39.4971 | 104712.1057
[7 empty] | 2671 | 11999 | 1827668 | 2021-01-27 17:33 | 2021-01-27 18:45 | 72 | 11kV | 2448 | 34 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At PT.13421 Serpentine Terrigal 0.4,Roadside & centre phase HDO fuse 31.5A blown. Cause: Bark on 11kV mains. See OMS 1827970,670,668,675 | January | 2021 | 2021Q3 | 2021 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2021-01-27 | N | 72 | N | 10 | N | N | 1.1101 | 39.4971 | 1788.9262
[7 empty] | 3012 | 16782 | 1827692 | 2021-01-27 18:19 | 2021-01-27 19:27 | 68 | 11kV | 45081.8333 | 672 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN.901 Surry Hills,Pnl.19 CB tripped on E/F with EFI. Cause: UG cable fault from S.6310 to S.7684 Zn Earth,No.3 Group Earth & 11kV trip. EFI's: S.35287,S.1916,S.62722,S.63010 | January | 2021 | 2021Q3 | 2021 | ZN901:PA19 | ZN901:PA31 | ZN00901/000031 | SYDNEY | UG | Not Veg | 2021-01-27 | N | 67.0861 | N | 10 | N | N | 1.1101 | 39.4971 | 32944.4741
[7 empty] | 3084 | 17849 | 1827740 | 2021-01-27 19:47 | 2021-01-27 20:43 | 56 | 11kV | 18256 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Recloser CP22381 tripped (ex ZN.15014 Mona Vale,Pnl.14) Cause: Tree/branch on OH mains,removed by DOp. Relays: O/C trip,IOC trip See OMS 1827740,41 | January | 2021 | 2021Q3 | 2021 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2021-01-27 | N | 56 | N | 10 | N | N | 1.1101 | 39.4971 | 13340.9463
[7 empty] | 3087 | 17961 | 1827799 | 2021-01-27 23:45 | 2021-01-28 01:08 | 83 | 11kV | 57436 | 692 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210217 4 fault operations Overcurrent Removed Palm branch pole NR-60102, remove tree branch pole NR-60508. | January | 2021 | 2021Q3 | 2021 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2021-01-27 | N | 83 | N | 10 | N | N | 1.1101 | 39.4971 | 41972.5347
[7 empty] | 1843 | 2104 | 1827810 | 2021-01-28 03:33 | 2021-01-28 08:37 | 304 | 11kV | 73168 | 259 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | REC 554 Arcadia Rosscommon - tripped, reclosed and locked out on: OC Abnormal: AB2063 Closed with AB451 Open Cause not ascertained See 1827944 1827945 | January | 2021 | 2021Q3 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2021-01-28 | N | 282.5019 | N | 3 | N | N | 1.1101 | 39.4971 | 53469.0163
[7 empty] | 2983 | 16386 | 1827811 | 2021-01-28 08:00 | 2021-01-28 12:25 | 265 | 11kV | 795 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT14049 Berkeley Wyong - Interrupted by DOp Tree brought down OH mains At pole BV1417 falling tree has hit 11KV CCT conductors, broken 2 x pin insulator ties. 2 x 11kv conductors sitting on 11kv cross-arm near roadside phase. Cable on ground near BV1417 is a NBN cable. Found 'C' phase LV distributor down between poles BV1414 & BV1415, cut away. Cause possibily due to shock wave from falling tree. | January | 2021 | 2021Q3 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2021-01-28 | N | 265 | N | 3 | N | N | 1.1101 | 39.4971 | 580.9626
[7 empty] | 2522 | 10323 | 1827830 | 2021-01-28 07:06 | 2021-01-28 20:25 | 799 | 11kV | 117331 | 796 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 210218 Faulty 33kv xarm at pole SW-60024. 33kv into 11kv also faulty tx changed at sub 9408 also refer to subtrans record LID 210219 | January | 2021 | 2021Q3 | 2021 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2021-01-28 | N | 147.4008 | N | 3 | N | N | 1.1101 | 39.4971 | 85742.0341
[7 empty] | 1900 | 2809 | 1828162 | 2021-01-29 08:10 | 2021-01-29 09:12 | 62 | 11kV | 40672 | 656 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Recloser CP46673 tripped,reclosed & locked out on O/C protection. Cause: Tree/branch on OH mains near LB 42542, removed by DOp. | January | 2021 | 2021Q3 | 2021 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2021-01-29 | N | 62 | N | 7 | N | N | 1.1101 | 39.4971 | 29721.898
[7 empty] | 2614 | 11263 | 1828186 | 2021-01-29 09:10 | 2021-01-29 12:15 | 185 | 11kV | 370 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 210230 Phases AB, 10 Amp fuses No Cause Found (Not Storm Condition) Substation DOLF BOTH A and b 11kV surge arrestors cut away | January | 2021 | 2021Q3 | 2021 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2021-01-29 | N | 185 | N | 7 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 3257 | 19877 | 1828246 | 2021-01-29 11:33 | 2021-01-29 14:42 | 189 | 11kV | 65769 | 753 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210231 3 phase 11kV x arm snapped at sub pole 12559 Portland Cement. nil protection interupted for safety dq Excluded OMS 1828246 | January | 2021 | 2021Q3 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2021-01-29 | N | 87.3426 | N | 7 | N | N | 1.1101 | 39.4971 | 48062.0453
[7 empty] | 3256 | 19863 | 1828340 | 2021-01-29 16:40 | 2021-01-30 | 440 | 11kV | 39600 | 90 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Heavy | N | At USL link CP.40165, operated by DOp for safety reasons. Cause: Volt leaking on USL 40165 pole. AP issued to LW to repair - traffic control required to repair delay of restoration expected | January | 2021 | 2021Q3 | 2021 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2021-01-29 | N | 440 | N | 7 | N | N | 1.1101 | 39.4971 | 28938.512
[7 empty] | 2479 | 9843 | 1828430 | 2021-01-29 22:05 | 2021-01-30 02:25 | 260 | 11kV | 94322 | 871 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210237 Pole Fire at OS-20682 Excluded OMS 1828424 | January | 2021 | 2021Q3 | 2021 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2021-01-29 | N | 108.2916 | N | 7 | N | N | 1.1101 | 39.4971 | 68927.7356
[7 empty] | 2780 | 13600 | 1828466 | 2021-01-30 01:27 | 2021-01-30 03:20 | 113 | 11kV | 112570 | 1007 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Rain Heavy | N | At ZN.3154 St Ives,Pnl.16 CB tripped. Cause not ascertained. 11kV fault from S.465 Burraneer Arterial to Rec 1622 Eastern Arterial. Relays: O/C,EFI Field EFI's-NIL Signals,11kV trip At ZN.3154 St Ives,Pnl.16 CB tripped. Cause not ascertained. 11kV fault from S.465 Burraneer Arterial to Rec 1622 Eastern Arterial. Relays: O/C,EFI Field EFI's-NIL Signals,11kV trip See OMS 1829022,026,466 | January | 2021 | 2021Q3 | 2021 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | Unknown | Not Veg | 2021-01-30 | N | 111.7875 | N | 11 | N | N | 1.1101 | 39.4971 | 82262.8357
[7 empty] | 1950 | 3352 | 1828478 | 2021-01-30 05:22 | 2021-01-30 06:25 | 63 | 11kV | 189 | 3 | HV | Animal Frog | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 210239 A Phase DOLF : 10 Amp Frog Excluded OMS 1828478 | January | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-01-30 | N | 63 | N | 11 | N | N | 1.1101 | 39.4971 | 138.1156
[7 empty] | 3018 | 16925 | 1828474 | 2021-01-30 03:51 | 2021-01-30 08:45 | 294 | 11kV | 882 | 3 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 210238 A Phase DOLF : 10 Amp Possum Excluded OMS 1828474 | January | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-01-30 | N | 294 | N | 11 | N | N | 1.1101 | 39.4971 | 644.5396
[7 empty] | 2873 | 14637 | 1828402 | 2021-01-29 19:07 | 2021-01-30 10:25 | 918 | 11kV | 3977 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | REC47302 Hue Hue Sparks 0.1 tripped on Earth Fault Tree on OH mains at pole DD438. Mains smoking on fire. Note: EMSO has been organised to check customers for damaged due to HV falling into LV mains See 1829024 1829025 | January | 2021 | 2021Q3 | 2021 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2021-01-29 | N | 441.8889 | N | 7 | N | N | 1.1101 | 39.4971 | 2906.2743
[7 empty] | 1924 | 3066 | 1828541 | 2021-01-30 09:52 | 2021-01-30 12:10 | 138 | 11kV | 10358 | 80 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | REC3280 Hunt Ave tripped on: OC Cause not ascertained See 1829020 1829021 | January | 2021 | 2021Q3 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2021-01-30 | N | 129.475 | N | 11 | N | N | 1.1101 | 39.4971 | 7569.3209
[7 empty] | 3162 | 18960 | 1828347 | 2021-01-29 16:29 | 2021-01-30 14:00 | 1291 | 11kV | 234049 | 1303 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 210235 UGOH pole iV50155 snapped and wire down UGOH pole IV50731 HV into LV at sub 16792 princess St sub (refer to OMS 1828962) | January | 2021 | 2021Q3 | 2021 | 224:80341 | 224:80341 | ZN00224/080341 | LAKE MACQUARIE | OH | Not Veg | 2021-01-29 | N | 179.6232 | N | 7 | N | N | 1.1101 | 39.4971 | 171036.1059
[7 empty] | 2608 | 11229 | 1828666 | 2021-01-30 15:29 | 2021-01-30 17:15 | 106 | 11kV | 424 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210253 A & B Phase DOLF : 20 Amp Lightning Excluded OMS 1828666 | January | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-01-30 | N | 106 | N | 11 | N | N | 1.1101 | 39.4971 | 309.8467
[7 empty] | 1955 | 3378 | 1828681 | 2021-01-30 15:55 | 2021-01-30 17:38 | 103 | 11kV | 136990 | 1330 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210251 1 fault operation C Phase Earth Fault; Overcurrent | January | 2021 | 2021Q3 | 2021 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2021-01-30 | N | 103 | N | 11 | N | N | 1.1101 | 39.4971 | 100108.2515
[7 empty] | 1714 | 443 | 1828683 | 2021-01-30 16:01 | 2021-01-30 18:30 | 149 | 11kV | 2980 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210256 C Phase DOLF : 16 Amp Excluded OMS 1828683 | January | 2021 | 2021Q3 | 2021 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2021-01-30 | N | 149 | N | 11 | N | N | 1.1101 | 39.4971 | 2177.6961
[7 empty] | 3094 | 18069 | 1828667 | 2021-01-30 15:30 | 2021-01-30 19:00 | 210 | 11kV | 3780 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210258 Single phase DOLF : 16 Amp Excluded OMS 1828667 | January | 2021 | 2021Q3 | 2021 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2021-01-30 | N | 210 | N | 11 | N | N | 1.1101 | 39.4971 | 2762.3125
[7 empty] | 3072 | 17679 | 1828668 | 2021-01-30 15:34 | 2021-01-30 20:30 | 296 | 11kV | 3552 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210260 B & C Phase DOLF : 20 Amp Sub 50521 also had 10A DOLF replaced Excluded OMS 1828668 | January | 2021 | 2021Q3 | 2021 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Veg | 2021-01-30 | N | 296 | N | 11 | N | N | 1.1101 | 39.4971 | 2595.6968
[7 empty] | 2577 | 10905 | 1828760 | 2021-01-30 23:27 | 2021-01-30 23:49 | 22 | 11kV | 3982 | 181 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn187 Crows Nest - Pnl.6 tripped on: I/T Receive @S6643 North Pylon I/T Send Protection scheme unique and incorrectly labelled at S6643. Auto/non-auto toggle switch for auto closing scheme was in auto position and when LV bar was de-energised, 8-10 seconds later, Sw/A opened locally then sent an intertrip to Pnl.6. PE have installed warning label at S6643 | January | 2021 | 2021Q3 | 2021 | ZN187:PA6 | ZN187:PA6 | ZN00187/000006 | NORTH SYDNEY | Unknown | Unknown | 2021-01-30 | N | 22 | N | 11 | N | N | 1.1101 | 39.4971 | 2909.9282
[7 empty] | 2030 | 4340 | 1828714 | 2021-01-30 21:15 | 2021-01-31 00:38 | 203 | 11kV | 1218 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 210263 interrupt to fix wire off pin at pole MG77009 Excluded oms 1828714 | January | 2021 | 2021Q3 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2021-01-30 | N | 203 | N | 11 | N | N | 1.1101 | 39.4971 | 890.0785
[7 empty] | 2996 | 16602 | 1828765 | 2021-01-31 01:05 | 2021-01-31 02:06 | 61 | 11kV | 1403 | 23 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT11933 Nari Coolarn - Centre phase HDO operated Possible fuse fatigue | January | 2021 | 2021Q3 | 2021 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Not Veg | 2021-01-31 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 1025.271
[7 empty] | 2718 | 12564 | 1828822 | 2021-01-31 10:54 | 2021-01-31 14:15 | 201 | 11kV | 201 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210273 DOLF : 3 Amp excluded OMS 1828822 | January | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2021-01-31 | N | 201 | N | 2 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 2079 | 4966 | 1829120 | 2021-02-01 14:57 | 2021-02-01 18:07 | 190 | 11kV | 190 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | No Weather Impact | N | LID 210281 B Phase OQFRN Fuse : 80 Amp Sub 35383 Blown HV B phase fuse no cause found all 3 fuses replaced OQFRN | February | 2021 | 2021Q3 | 2021 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2021-02-01 | N | 190 | N | 2 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 2855 | 14408 | 1829149 | 2021-02-01 16:24 | 2021-02-01 19:00 | 156 | 11kV | 312 | 2 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 210282 Single phase DOLF : 10 Amp Private Pole failure Blown DOLF sub 51338 Excluded OMS 1829149 | February | 2021 | 2021Q3 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | Unknown | Not Veg | 2021-02-01 | N | 156 | N | 2 | N | N | 1.1101 | 39.4971 | 228.0004
[7 empty] | 3010 | 16761 | 1829230 | 2021-02-02 03:45 | 2021-02-02 06:58 | 193 | 11kV | 24378 | 322 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn35800 Bankstown - Pnl.21L tripped on: OC & EF UG cable fault between S3095 Sw/D, CP1108 Sw/A & S2639 Sw/B Note: No access to S3094, S7378 and S3095 (All behind locked gate) Delayed fault location and restoration. See 1829334 1829336 | February | 2021 | 2021Q3 | 2021 | ZN35800:PA21 | ZN35800:PA21 | ZN35800/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-02-02 | N | 75.7081 | N | 6 | N | N | 1.1101 | 39.4971 | 17814.7234
[7 empty] | 3017 | 16895 | 1829242 | 2021-02-02 06:22 | 2021-02-02 08:30 | 128 | 11kV | 128 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210284 Single phase Broken Live Line Lead SUB ISOLATED TO REPAIR LL LEAD Excluded OMS 1829242 | February | 2021 | 2021Q3 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2021-02-02 | N | 128 | N | 6 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 3261 | 19958 | 1829237 | 2021-02-02 05:14 | 2021-02-02 09:40 | 266 | 11kV | 798 | 3 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 210285 Single phase DOLF : 10 Amp Excluded OMS 1829237 | February | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-02-02 | N | 266 | N | 6 | N | N | 1.1101 | 39.4971 | 583.1549
[7 empty] | 2170 | 5860 | 1832833 | 2021-02-02 08:18 | 2021-02-02 11:41 | 203 | 11kV | 18676 | 92 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Customer reports: LOW VOLTS TO LIGHTS AND POWER APPLIANCES 11kv OH conductor down at PT 18706. Pole number BR-00426. CP47746 Patonga Meroo - interrupted at 11:41am for repairs due to OH down. refer to OMS 1829269 | February | 2021 | 2021Q3 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2021-02-02 | N | 203 | N | 6 | N | N | 1.1101 | 39.4971 | 13647.87
[7 empty] | 2962 | 16054 | 1829322 | 2021-02-02 10:58 | 2021-02-02 19:46 | 528 | 11kV | 102407.9333 | 194 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT14535 Bluey Wave Kalakau - Interrutped for safety PT11612 Crystal Noorong - Interrupted for safety PT46144 Henrys Boos - Dist #2 - Interrupted for safety OH Earth wire down near No.2 South Scenic Rd. See 1829322 1829323 1829325 | February | 2021 | 2021Q3 | 2021 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2021-02-02 | N | 527.8759 | N | 6 | N | N | 1.1101 | 39.4971 | 74836.6972
[7 empty] | 2545 | 10599 | 1829486 | 2021-02-03 04:54 | 2021-02-03 08:13 | 199 | 11kV | 8557 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210290 2 fault operations Conductor on ground at FU-24250 Excluded OMS 1829486 | February | 2021 | 2021Q3 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2021-02-03 | N | 199 | N | 3 | N | N | 1.1101 | 39.4971 | 6253.2032
[7 empty] | 2063 | 4789 | 1829581 | 2021-02-03 11:52 | 2021-02-03 13:35 | 103 | 11kV | 618 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210292 C Phase DOLF : 10 Amp Excluded OMS 1829581 | February | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2021-02-03 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 451.6162
[7 empty] | 3085 | 17928 | 1829269 | 2021-02-02 11:41 | 2021-02-03 16:00 | 1699 | 11kV | 156308 | 92 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP47746 Patonga Meroo - interrupted at 11:41am for repairs due to OH down.Prior to that customer reported Part Supply, see OMS 1832833 11kV OH down adjacent to PT18706 Little Patonga No.1 Boat access only CC1: 22-"Refer to SOp" | February | 2021 | 2021Q3 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2021-02-02 | N | 1699 | N | 6 | N | N | 1.1101 | 39.4971 | 114225.2761
[7 empty] | 2276 | 7177 | 1829668 | 2021-02-03 20:03 | 2021-02-03 21:32 | 89 | 11kV | 124131 | 1689 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S342 Paddington Zone - Panel 17 tripped on OC & Earth fault with EFI. Signals: 11kV Trip, No.2 TX group earth. Cause: 11kV UG Cable fault between S160 & S1162 See OMS 1829668, 1829863 & 1829862 | February | 2021 | 2021Q3 | 2021 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2021-02-03 | N | 73.4938 | N | 3 | N | N | 1.1101 | 39.4971 | 90711.2736
[7 empty] | 2345 | 8181 | 1829823 | 2021-02-04 17:40 | 2021-02-04 20:05 | 144.7167 | 11kV | 2894.3333 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210299 A Phase DOLF : 20 Amp | February | 2021 | 2021Q3 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2021-02-04 | N | 144.7167 | N | 1 | N | N | 1.1101 | 39.4971 | 2115.0934
[7 empty] | 2801 | 13862 | 1830405 | 2021-02-05 16:35 | 2021-02-05 18:10 | 95 | 11kV | 475 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210307 Replace crossarm at pole FR-84743 | February | 2021 | 2021Q3 | 2021 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2021-02-05 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 347.116
[7 empty] | 2609 | 11230 | 1830021 | 2021-02-05 17:44 | 2021-02-06 00:44 | 420 | 11kV | 283920 | 676 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Based on customer calls, assumed bond blown in the vicinity of CP40016 causing low vaults to customers. Abnormal: CP44022 open as part of restoration switching for original outage. At ZN14891 Wyong Panel 10 tripped on B & C phase OC Abnormal: LB48817 Closed with LB48613 open (DMA) Large tree branch on 11kV OH, isolated between CP44022, CP40745 and PT64486. See OMS 1830843, 1830844, 1830848 | February | 2021 | 2021Q3 | 2021 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2021-02-05 | N | 420 | N | 4 | N | N | 1.1101 | 39.4971 | 207480.3618
[7 empty] | 2732 | 12801 | 1829998 | 2021-02-05 16:51 | 2021-02-06 02:51 | 600 | 11kV | 826180 | 1502 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | REC44936 Bentley Rd tripped on OC Tree down on PT13115. HV Cross arm and auxiliary equipment need to be rebuilt. PT cut away from network from LB41318 See 1831062 1831063 | February | 2021 | 2021Q3 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-02-05 | N | 550.0533 | N | 4 | N | N | 1.1101 | 39.4971 | 603747.9758
[7 empty] | 2175 | 5941 | 1829971 | 2021-02-05 15:44 | 2021-02-06 04:19 | 755 | 11kV | 172302 | 1908 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN14891 Wyong Panel 10 tripped on B & C phase OC Abnormal: LB48817 Closed with LB48613 open (DMA) Large tree branch on 11kV OH, isolated between CP44022, CP40745 and PT64486. See OMS 1830843, 1830844, 1830848 | February | 2021 | 2021Q3 | 2021 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2021-02-05 | N | 90.305 | N | 4 | N | N | 1.1101 | 39.4971 | 125913.2196
[7 empty] | 2553 | 10638 | 1830105 | 2021-02-06 08:59 | 2021-02-06 09:53 | 54 | 11kV | 54 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210314 A Phase DOLF : 20 Amp Blown A phase dolf no cause found | February | 2021 | 2021Q3 | 2021 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2021-02-06 | N | 54 | N | 3 | N | N | 1.1101 | 39.4971 | 39.4616
[7 empty] | 2407 | 9106 | 1830205 | 2021-02-06 22:21 | 2021-02-07 02:50 | 269 | 11kV | 269 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 210322 Single phase DOLF : 10 Amp Replace HV arrestor. Excluded OMS 1830205 | February | 2021 | 2021Q3 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-02-06 | N | 269 | N | 3 | N | N | 1.1101 | 39.4971 | 196.5773
[7 empty] | 2582 | 10995 | 1830197 | 2021-02-07 00:10 | 2021-02-07 03:25 | 195 | 11kV | 11100 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT77544 Forest River interrupted between S10027 SW/B & CP30141 At S10027 Dist.2 interrupted on A,B & C phases. Tree branch snapped on 11kV cross arm at pole PE99072. See OMS 1830210, 1830208 | February | 2021 | 2021Q3 | 2021 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2021-02-07 | N | 185 | N | 2 | N | N | 1.1101 | 39.4971 | 8111.5526
[7 empty] | 1966 | 3480 | 1830220 | 2021-02-07 08:13 | 2021-02-07 09:20 | 67 | 11kV | 67 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210326 Single phase DOLF : 3.15Amp Replace dolf 3.15 Bird on tank | February | 2021 | 2021Q3 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2021-02-07 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 48.9616
[7 empty] | 2535 | 10468 | 1830193 | 2021-02-06 19:49 | 2021-02-07 18:00 | 1331 | 11kV | 316836 | 918 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 210319 11kV Fdr 81432 isolated to repair pole fire at MW-30024. Excluded OMS No. 1830188 + 1830191 See also LID 210320/ OMS 1830371 | February | 2021 | 2021Q3 | 2021 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2021-02-06 | N | 345.1373 | N | 3 | N | N | 1.1101 | 39.4971 | 231534.4037
[7 empty] | 2452 | 9514 | 1830422 | 2021-02-08 13:26 | 2021-02-08 17:25 | 239 | 11kV | 8208 | 48 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 210330 Protection did not trip. Stay wire broken and hanging over live 11kv. in reach of public. Sop interrupted Sw 42084. Excluded oms 1830422, 1830427 | February | 2021 | 2021Q3 | 2021 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2021-02-08 | N | 171 | N | 2 | N | N | 1.1101 | 39.4971 | 5998.1643
[7 empty] | 2220 | 6582 | 1830512 | 2021-02-08 18:48 | 2021-02-08 22:10 | 202 | 11kV | 81648 | 1052 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | AT ZN1673 Turramurra - Panel 14 tripped on relays C phase IOC, E fault, fault check, under frequency, EFI. 11kV UG cable fault from S6528 SW/B to S4242 SW/A. At S4720 Dist.2 & Dist.3 were interrupted due to LV // being in and incorrect bonding. DMA on Dist.3 is since March 2019. See OMS 1830948 & 1830949 for S4720 interruption and 1830946 & 1830947 for 11kV UG cable fault. | February | 2021 | 2021Q3 | 2021 | ZN1673:PA14 | ZN1673:PA14 | ZN01673/000014 | KU-RING-GAI | UG | Not Veg | 2021-02-08 | N | 77.6122 | N | 2 | N | N | 1.1101 | 39.4971 | 59665.9502
[7 empty] | 2502 | 10124 | 1830543 | 2021-02-09 05:39 | 2021-02-09 10:36 | 297 | 11kV | 790899 | 3684 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S14891 Wyong Panel 16 tripped and locked out on Relays: Timed A B and C phase OC, Fault Check, Recloser Timing, TX2 Earth Fault Abnormal Switching: CP48817 Closed, CP48613 Open S14849 SW/B Closed, SW/A Open S18197 CP40016 Open, CP42386 Closed Cause: UG cable fault between S18169 - S18851 - S14940 See OMS 1831099 1831100 1831101 1831102 1831105 1830543 1830544 1830545 1831035 | February | 2021 | 2021Q3 | 2021 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | UG | Not Veg | 2021-02-09 | N | 214.6849 | N | 5 | N | N | 1.1101 | 39.4971 | 577965.6616
[7 empty] | 2371 | 8548 | 1830830 | 2021-02-09 11:25 | 2021-02-09 12:20 | 55 | 11kV | 495 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210333 no oms reported in to tree services in Ausgrid. fdr did not trip trees on mains. Fdr did not trip | February | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2021-02-09 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 2662 | 11865 | 1830552 | 2021-02-09 06:10 | 2021-02-09 12:45 | 395 | 11kV | 139195 | 1508 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210332 1 fault operation Sensitive Earth Fault HV wire down adjacent ABS 1381 HV into LV all checked OK | February | 2021 | 2021Q3 | 2021 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2021-02-09 | N | 92.3044 | N | 5 | N | N | 1.1101 | 39.4971 | 101719.6004
[7 empty] | 2725 | 12692 | 1830726 | 2021-02-09 17:47 | 2021-02-09 18:48 | 61 | 11kV | 37422 | 1107 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn12610 Long Jetty - Pnl.18 tripped & reclosed on: B & C phase OC iR50249 Kipling Shakespear tripped on: OC Cockatoo fried on DW near PT46144. Burnt off bond at LB47174 caused by fault current See 1831096 1831097 | February | 2021 | 2021Q3 | 2021 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2021-02-09 | N | 33.8049 | N | 5 | N | N | 1.1101 | 39.4971 | 27346.8938
[7 empty] | 2922 | 15334 | 1830757 | 2021-02-09 21:31 | 2021-02-10 00:36 | 185 | 11kV | 4067 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210337 2 fault operations 3 phase Overcurrent TRIP CURRENT A PH 512A B PH 511A C PH 420A Excluded OMS 1830757 | February | 2021 | 2021Q3 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Veg | 2021-02-09 | N | 169.4583 | N | 5 | N | N | 1.1101 | 39.4971 | 2972.0436
[7 empty] | 2602 | 11209 | 1830761 | 2021-02-10 01:06 | 2021-02-10 01:50 | 44 | 11kV | 2596 | 59 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 210339 A Phase DOLF : 31 Amp DOLF blew - tracking down fibreglass carrier caught fire. All 3 DOLF carriers replaced Excluded oms 1830761 | February | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-02-10 | N | 44 | N | 3 | N | N | 1.1101 | 39.4971 | 1897.0802
[7 empty] | 2436 | 9368 | 1830852 | 2021-02-10 11:45 | 2021-02-10 12:50 | 65 | 11kV | 12870 | 198 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | S7286 Wattle William - Tx 2 tripped on C phase Diff - Whole sub interurpted due to parallel tripping. During NAR69225 T5, phasing checks at local Tx (S7286) was used for phasing as other subs were non paralleling. After phasing at zone, DOp close from S2179 Gipps Bank in turn causing in rush current at S7286 tripped Tx 2. | February | 2021 | 2021Q3 | 2021 | ZN711:PA5 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | Unknown | Unknown | 2021-02-10 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 9405.0164
[7 empty] | 3220 | 19606 | 1830910 | 2021-02-10 16:27 | 2021-02-10 17:45 | 78 | 11kV | 2964 | 38 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex Pnl.11 Peats Ridge - 11kV interrupted between USL42943 and AB40754 to repairs to OH mains that came off pin insulators See 1830910 1830911 | February | 2021 | 2021Q3 | 2021 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2021-02-10 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 2166.0038
[7 empty] | 2963 | 16094 | 1830972 | 2021-02-11 02:55 | 2021-02-11 07:30 | 275 | 11kV | 694565 | 9269 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S59550 Gwawley Bay Panel 36 did not open - Backop OC tripped TX 1A and TX1A Tripped off Cause: Supect trunk feeder fault See OMS 1831077 1831068 1830985 1831076 1831075 1831074 1831073 1831072 1831071 1831070 1831069 1831067 18310606 1831065 1830980 1830978 1830972 1830970 | February | 2021 | 2021Q3 | 2021 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | UG | Not Veg | 2021-02-11 | N | 74.9342 | N | 6 | N | N | 1.1101 | 39.4971 | 507567.6158
[7 empty] | 3148 | 18761 | 1830987 | 2021-02-11 06:36 | 2021-02-11 09:25 | 169 | 11kV | 13351 | 79 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT11849 Charlton Rolls - Footpath phase 11kV HDO operated Fuse Fatigue | February | 2021 | 2021Q3 | 2021 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2021-02-11 | N | 169 | N | 6 | N | N | 1.1101 | 39.4971 | 9756.517
[7 empty] | 3155 | 18857 | 1831035 | 2021-02-11 09:42 | 2021-02-11 10:48 | 66 | 11kV | 23826 | 361 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1850 Bass Hill - Pnl.42 tripped on B Phase OC UG cable fault in front line section between Pnl.42 an LB3063 | February | 2021 | 2021Q3 | 2021 | ZN1850:PA42 | ZN1850:PA42 | ZN01850/000042 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-02-11 | N | 66 | N | 6 | N | N | 1.1101 | 39.4971 | 17411.3381
[7 empty] | 3170 | 19096 | 1831083 | 2021-02-11 11:46 | 2021-02-11 13:30 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210344 B Phase DOLF : 10 Amp Replaced B phase DOLF Excluded OMS 1831083 | February | 2021 | 2021Q3 | 2021 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2021-02-11 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 3108 | 18311 | 1830958 | 2021-02-11 00:49 | 2021-02-11 18:50 | 1081 | 11kV | 398671 | 1611 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | ex Zn35800 Bankstown Pnl.1 - iR50006 Marrion Wilkins - tripped, reclosed and locked out on OC Vehicle hit pole (LB101) corner Marion and Williams St. See 1831802 1831803 1831804 1831805 | February | 2021 | 2021Q3 | 2021 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-02-11 | N | 247.468 | N | 6 | N | N | 1.1101 | 39.4971 | 291337.008
[7 empty] | 2292 | 7413 | 1831000 | 2021-02-11 08:24 | 2021-02-11 19:35 | 671 | 11kV | 540343 | 2046 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4545 Meadowbank - Pnl.2 tripped on C phase IOC, Earth Fault UG cable fault between S7830 Sw/A and S2707 Sw/B Abnormal; DMA at S712 in LV // (event ID 11321) failed during feeder trip, mains down. See1831790 1831791 1831792 1831794 | February | 2021 | 2021Q3 | 2021 | ZN4545:PA2 | ZN4545:PA2 | ZN04545/000002 | RYDE | UG | Not Veg | 2021-02-11 | N | 264.0973 | N | 6 | N | N | 1.1101 | 39.4971 | 394866.727
[7 empty] | 2748 | 13139 | 1831236 | 2021-02-12 04:58 | 2021-02-12 06:48 | 110 | 11kV | 194260 | 1766 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn36300 Balgowlah North Panel 3 Hills Griffiths tripped Relays; OC Earth Fault, 51N Group Earth Signals: 11kV Trip TX1 Group Earth Abnormal Switching: LB23296 Open, SW/B Closed at S17132 Cause: Possum on 11kv UGOH above CP22355 See OMS 1831847 1831236 | February | 2021 | 2021Q3 | 2021 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2021-02-12 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 141959.4783
[7 empty] | 1805 | 1639 | 1831306 | 2021-02-12 11:00 | 2021-02-12 12:20 | 80 | 11kV | 6560 | 82 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210346 Broken X arm replaced under emergency. SI-90969 Excluded OMS 1831309 | February | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-02-12 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 4793.8545
[7 empty] | 3267 | 20041 | 1831391 | 2021-02-12 19:45 | 2021-02-12 20:05 | 20 | 11kV | 980 | 49 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | At ZN12600 Lisarow section of feeder from CP44277 to CP42056 tee PT11969 Wyoming Pacific Interrupted Cause: Tree branch on OH CCT | February | 2021 | 2021Q3 | 2021 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2021-02-12 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 716.1551
[7 empty] | 2296 | 7435 | 1831299 | 2021-02-12 11:05 | 2021-02-13 01:35 | 870 | 11kV | 387834 | 539 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15014 Mona Vale - Pnl.19 tripped & reclosed on IOC refer to OMS 1833698 @ 1105 - LB65959 opened due to snapped 11kV pole on Barrenjoey Rd near Karloo Pde after oversized truck hit Optus mains. See 1833698 1833706 1833709 1833710 | February | 2021 | 2021Q3 | 2021 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | OH | Not Veg | 2021-02-12 | N | 719.5436 | N | 4 | N | N | 1.1101 | 39.4971 | 283417.648
[7 empty] | 2952 | 15922 | 1831447 | 2021-02-13 06:41 | 2021-02-13 07:43 | 62 | 11kV | 91388 | 1474 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S9700 kirrawee Panel 24 has tripped and reclosed on C phase IOC and OC, Reclose and Lockout, EFI Signals: 11kV Trip Cause: Tree branch on OH mains - Adjactent S9260 Waratah Arcacia | February | 2021 | 2021Q3 | 2021 | ZN9700:PA24 | ZN9700:PA24 | ZN09700/000024 | SUTHERLAND | OH | Veg | 2021-02-13 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 66783.6549
[7 empty] | 2551 | 10628 | 1831470 | 2021-02-13 08:16 | 2021-02-13 09:00 | 44 | 11kV | 88 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210353 C Phase DOLF : 40 Amp 11kV dolf fuse burnt, replaced DQ Excluded OMS 1831470 | February | 2021 | 2021Q3 | 2021 | 224:80328 | 224:80328 | ZN00224/080328 | LAKE MACQUARIE | OH | Veg | 2021-02-13 | N | 44 | N | 4 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 3039 | 17215 | 1831581 | 2021-02-13 16:10 | 2021-02-13 17:10 | 60 | 11kV | 1080 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At PT13987 Chittaway Fountain 0.4 B and C phase 20A HDO blown Cause: Tree branch contact See OMS 1832310 1831581 | February | 2021 | 2021Q3 | 2021 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2021-02-13 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 3214 | 19537 | 1831574 | 2021-02-13 20:20 | 2021-02-13 21:45 | 85 | 11kV | 49130 | 578 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Section of 11kV Feeder from LK20524 to AB26122 tee PT15073 interrupted for safety reasons Abnormal Switching: AB26122 Closed LK21830 Open Cause: Tree touching 11kV Mains at PT15073 - Interrupted for emergency repairs see OMS 1832176 1831606 183155 1831574 1827070 | February | 2021 | 2021Q3 | 2021 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2021-02-13 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 35902.7549
[7 empty] | 2164 | 5826 | 1831619 | 2021-02-14 04:00 | 2021-02-14 16:30 | 750 | 11kV | 84768 | 690 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14144 Wamberal Panel 10L tripped, reclosed tripped and locked out on Relays: 50TBC, EFI, Lockout, reclose Timing Field EFI's S18824, S18802 S18826 Cause: Tree branch on OH mains S14144 Wamberal section of panel 10 from S18826 to S48880 to LV45192 HV into LV See OMS 1831884 1831888 1831889 1831627 1831622 1831619 | February | 2021 | 2021Q3 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-02-14 | N | 122.8522 | N | 1 | N | N | 1.1101 | 39.4971 | 61945.9542
[7 empty] | 2434 | 9349 | 1831743 | 2021-02-15 03:29 | 2021-02-15 05:17 | 108 | 11kV | 178798 | 1669 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Z12580 Panel 10 tripped on Relays: A phase OC and IOC EFIs all down to S18073 Cause Not ascertained for outage See OMS 1831807 1831808 1831743 | February | 2021 | 2021Q3 | 2021 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2021-02-15 | N | 107.1288 | N | 6 | N | N | 1.1101 | 39.4971 | 130660.3048
[7 empty] | 2697 | 12321 | 1831868 | 2021-02-15 12:56 | 2021-02-15 15:11 | 135 | 11kV | 156602 | 2187 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn15005 Belrose - Pnl.10 tripped on B & C phase OC Abnormal: NAR69682 - USL24307 open to USL21843 to LB23726 with LB22982 Closed at time of failure. Cause not ascertained. Loud explosion heard near PT15900, dop attended nothing found. Pnl.12 @ Belorse interrupted to allow USL21843 to be closed de-energised during restoration switching See 1832656 1832657 1832658 1832659 | February | 2021 | 2021Q3 | 2021 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Veg | 2021-02-15 | N | 71.6059 | N | 6 | N | N | 1.1101 | 39.4971 | 114440.1226
[7 empty] | 1973 | 3625 | 1832012 | 2021-02-15 18:10 | 2021-02-15 19:13 | 63 | 11kV | 59815 | 955 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.31 tripped on Earth Fault UG cable fault between S6229 Sw/B and S48424 Sw/A See 1832654 1832655 | February | 2021 | 2021Q3 | 2021 | ZN398:PA31 | ZN37300:PA6 | ZN37300/000006 | INNER WEST | UG | Not Veg | 2021-02-15 | N | 62.6335 | N | 6 | N | N | 1.1101 | 39.4971 | 43711.0378
[7 empty] | 1863 | 2387 | 1832049 | 2021-02-15 19:32 | 2021-02-15 20:55 | 83 | 11kV | 3237 | 39 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Wind Strong | N | PT1401 Yarrawonga Close - Footpath & Centre phase HDOs blown Tree on PT CC1: 22-"Refer to SOp" | February | 2021 | 2021Q3 | 2021 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2021-02-15 | N | 83 | N | 6 | N | N | 1.1101 | 39.4971 | 2365.5041
[7 empty] | 2488 | 9914 | 1832040 | 2021-02-15 19:20 | 2021-02-15 20:59 | 99.0333 | 11kV | 8318.8 | 84 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Long Jetty Pnl.13 - Bond off 11kV UGOH after USL40896 to S65927. Restored via LV // | February | 2021 | 2021Q3 | 2021 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2021-02-15 | N | 99.0333 | N | 6 | N | N | 1.1101 | 39.4971 | 6079.1337
[7 empty] | 2327 | 7919 | 1832067 | 2021-02-15 21:03 | 2021-02-15 21:43 | 40 | 11kV | 59320 | 1483 | HV | Animal Possum | Animal | UGOH | Unplanned | Rain Heavy | N | LID 210367 2 fault operations 3 phase Overcurrent Possum UGOH pole IU-30522 | February | 2021 | 2021Q3 | 2021 | 258:80793 | 258:80793 | ZN00258/080793 | NEWCASTLE | OH | Not Veg | 2021-02-15 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 43349.3064
[7 empty] | 2668 | 11931 | 1832099 | 2021-02-16 06:24 | 2021-02-16 07:25 | 61.3833 | 11kV | 4787.9 | 78 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT1615 Homes Leeds - Middle phase HDO operated Possum found at base of pole | February | 2021 | 2021Q3 | 2021 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Not Veg | 2021-02-16 | N | 61.3833 | N | 2 | N | N | 1.1101 | 39.4971 | 3498.8561
[7 empty] | 3001 | 16661 | 1832141 | 2021-02-16 08:46 | 2021-02-16 09:22 | 36 | 11kV | 2796 | 116 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210373 Overcurrent NOTE NAR 65887 was switched when Keinbah recloser tripped. Sw 42067 Closed and ABS 47232 open. All customers restored by 0910 with the Hunter Valley Solar farm returned to service 0922hrs. | February | 2021 | 2021Q3 | 2021 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2021-02-16 | N | 24.1034 | N | 2 | N | N | 1.1101 | 39.4971 | 2043.2343
[7 empty] | 1921 | 3036 | 1832678 | 2021-02-18 12:48 | 2021-02-18 14:00 | 72 | 11kV | 72 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210382 B Phase DOLF : 10 Amp Excluded oms 1832678 | February | 2021 | 2021Q3 | 2021 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2021-02-18 | N | 72 | N | 4 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 1974 | 3626 | 1832701 | 2021-02-18 14:10 | 2021-02-18 15:23 | 73 | 11kV | 14381 | 197 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210383 Termite damaged cross arm changed sub 9711. Excluded OMS 1832701. | February | 2021 | 2021Q3 | 2021 | 258:80781 | 258:80781 | ZN00258/080781 | NEWCASTLE | OH | Not Veg | 2021-02-18 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 10509.2106
[7 empty] | 1952 | 3362 | 1832628 | 2021-02-18 10:20 | 2021-02-18 17:50 | 450 | 11kV | 6300 | 14 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210384 A & B phase DOLF : 16 Amp Excluded OMS 1832628 | February | 2021 | 2021Q3 | 2021 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2021-02-18 | N | 450 | N | 4 | N | N | 1.1101 | 39.4971 | 4603.8542
[7 empty] | 2154 | 5747 | 1832770 | 2021-02-18 20:27 | 2021-02-18 22:50 | 143 | 11kV | 9295 | 65 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 210385 Fdr isolated to repair broken insulators at pole SW-20659. Excluded OMS No. 1832770 | February | 2021 | 2021Q3 | 2021 | 270:83587 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Not Veg | 2021-02-18 | N | 143 | N | 4 | N | N | 1.1101 | 39.4971 | 6792.5118
[7 empty] | 2231 | 6670 | 1832844 | 2021-02-19 10:51 | 2021-02-19 12:39 | 108 | 11kV | 108 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 210386 Broken Live Line Clamp Excluded OMS 1832844 | February | 2021 | 2021Q3 | 2021 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2021-02-19 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 2974 | 16310 | 1832858 | 2021-02-19 11:54 | 2021-02-19 12:50 | 56 | 11kV | 112 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210387 Single phase DOLF : 10 Amp Excluded OMS 1832858 | February | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-02-19 | N | 56 | N | 3 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 1964 | 3470 | 1832957 | 2021-02-19 21:49 | 2021-02-19 23:15 | 86 | 11kV | 6536 | 76 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT2394 Cressy Kellaway was found with the 11kV centre phase HDO blown after a fire on the PT Cause: There was a fire at PT2394. The fire was out when the DOp arrived however the 11kV HDO's See OMS 1832958 1832957 | February | 2021 | 2021Q3 | 2021 | ZN35500:PA36 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2021-02-19 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 4776.316
[7 empty] | 1894 | 2754 | 1832971 | 2021-02-20 05:15 | 2021-02-20 08:30 | 195 | 11kV | 195 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 210389 B Phase DOLF : 31 Amp Excluded OMS 1832971 | February | 2021 | 2021Q3 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2021-02-20 | N | 195 | N | 3 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 2197 | 6262 | 1833071 | 2021-02-20 18:10 | 2021-02-20 18:56 | 46 | 11kV | 29416 | 651 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP46673 Terrigal Penrose Tripped on Relays: OC and Lockout Cause Not ascertained for outage See OMS 1833704 1833705 1833071 | February | 2021 | 2021Q3 | 2021 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2021-02-20 | N | 45.1859 | N | 3 | N | N | 1.1101 | 39.4971 | 21496.3452
[7 empty] | 3176 | 19158 | 1833082 | 2021-02-20 20:39 | 2021-02-20 21:40 | 61 | 11kV | 122000 | 2000 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN1193 Lindfield Panel 15 tripped and reclosed on Relays: A and B phase IOC Field EFI's Mi;l Signals 11kV Trip Cause: B removed from 11kV adjacent to PT1075 Reginald St Abnormal Switching: CP308 Closed, S2961 SW/D open See OMS 1833082 1833084 1833682 | February | 2021 | 2021Q3 | 2021 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Not Veg | 2021-02-20 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 89154.0016
[7 empty] | 3006 | 16732 | 1833123 | 2021-02-21 01:05 | 2021-02-21 02:40 | 95 | 11kV | 174570 | 2148 | HV | Animal Other | Animal | UGOH | Unplanned | No Weather Impact | N | At S 10999 Kogarah Panel 19 Tripped on B and C phase OC Fault Check Cause animal on UGOH between LB30192 to SW A S10614 See OMS 1833719 1833720 1833123 | February | 2021 | 2021Q3 | 2021 | ZN10999:PA19 | ZN10999:PA19 | ZN10999/000019 | BAYSIDE | OH | Not Veg | 2021-02-21 | N | 81.2709 | N | 2 | N | N | 1.1101 | 39.4971 | 127570.6071
[7 empty] | 3281 | 20215 | 1833130 | 2021-02-21 05:28 | 2021-02-21 07:05 | 97 | 11kV | 291 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210396 & 210396/02 DOLF : 10 Amp BOTH THE DOLF AT THE SUB AND USPTREAM LINE DOLF BLEW. Excluded OMS 1833130 | February | 2021 | 2021Q3 | 2021 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2021-02-21 | N | 97 | N | 2 | N | N | 1.1101 | 39.4971 | 212.6542
[7 empty] | 1917 | 2985 | 1833232 | 2021-02-22 03:42 | 2021-02-22 04:54 | 72 | 11kV | 64296 | 893 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven - Pnl.14 tripped on Earth Fault UG cable fault in front line section between Pnl.14 and S18599 Sw/A | February | 2021 | 2021Q3 | 2021 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | UG | Not Veg | 2021-02-22 | N | 72 | N | 16 | N | N | 1.1101 | 39.4971 | 46985.6204
[7 empty] | 2119 | 5327 | 1833239 | 2021-02-22 10:08 | 2021-02-22 12:16 | 128 | 11kV | 768 | 6 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210400 section isolated to repair 33kv crossarm on pole HW-40214. Excluded oms report 1833239 & 1833253 | February | 2021 | 2021Q3 | 2021 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Not Veg | 2021-02-22 | N | 128 | N | 16 | N | N | 1.1101 | 39.4971 | 561.2317
[7 empty] | 3004 | 16718 | 1833405 | 2021-02-22 15:16 | 2021-02-22 16:46 | 90 | 11kV | 69486 | 1223 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2602 Clovellt No28 CB tripped on RelaysL EF IOC, EFI Fault Check Signals: 11kV Trip Field EFI's S3679 through to S79070 Cause: UG fault from S79070 to S2733 to S8436 to S36016 See OMS 1834151 1834152 1833405 | February | 2021 | 2021Q3 | 2021 | ZN2602:PA28 | ZN2602:PA28 | ZN02602/000028 | WAVERLEY | UG | Not Veg | 2021-02-22 | N | 56.816 | N | 16 | N | N | 1.1101 | 39.4971 | 50778.3193
[7 empty] | 2334 | 8016 | 1833419 | 2021-02-22 15:59 | 2021-02-22 17:50 | 111.35 | 11kV | 3785.9 | 34 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | Replaced C Phase 20a Fuse CC1: 06-"Urgent - O.H Mains - No others" | February | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-02-22 | N | 111.35 | N | 16 | N | N | 1.1101 | 39.4971 | 2766.6241
[7 empty] | 3009 | 16757 | 1833421 | 2021-02-22 15:52 | 2021-02-22 18:40 | 168 | 11kV | 15850 | 111 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210404 1 fault operation Overcurrent Excluded OMS 1833421 | February | 2021 | 2021Q3 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-02-22 | N | 142.7928 | N | 16 | N | N | 1.1101 | 39.4971 | 11582.7125
[7 empty] | 1949 | 3336 | 1833424 | 2021-02-22 16:08 | 2021-02-22 18:45 | 156.5333 | 11kV | 3130.6667 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210414 Single phase DOLF : 20 Amp | February | 2021 | 2021Q3 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2021-02-22 | N | 156.5333 | N | 16 | N | N | 1.1101 | 39.4971 | 2287.7989
[7 empty] | 2103 | 5222 | 1833441 | 2021-02-22 17:09 | 2021-02-22 19:29 | 140 | 11kV | 116498 | 996 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210405 A & C phase Overcurrent A Protn A-C 6500 AMPS B Protn A-C Excluded OMS 1833441 | February | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-02-22 | N | 116.9659 | N | 16 | N | N | 1.1101 | 39.4971 | 85133.3023
[7 empty] | 1893 | 2748 | 1833491 | 2021-02-22 20:35 | 2021-02-22 22:05 | 90 | 11kV | 540 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210416 Single phase DOLF : 16 Amp Excluded OMS 1833491 | February | 2021 | 2021Q3 | 2021 | 512:83736 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2021-02-22 | N | 90 | N | 16 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 2901 | 15005 | 1833480 | 2021-02-22 19:53 | 2021-02-22 22:20 | 147 | 11kV | 441 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210418 Single phase DOLF : 10 Amp Excluded OMS 1833480 | February | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-02-22 | N | 147 | N | 16 | N | N | 1.1101 | 39.4971 | 322.2698
[7 empty] | 1804 | 1618 | 1833475 | 2021-02-22 19:23 | 2021-02-22 22:25 | 182 | 11kV | 546 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210417 C Phase DOLF : 16 Amp Excluded OMS 1833475 | February | 2021 | 2021Q3 | 2021 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2021-02-22 | N | 182 | N | 16 | N | N | 1.1101 | 39.4971 | 399.0007
[7 empty] | 1884 | 2604 | 1833490 | 2021-02-22 20:11 | 2021-02-23 00:01 | 229.55 | 11kV | 1836.4 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210420 3 phase DOLF : 16 Amp excluded OMS 1833491 CC1: 22-"Refer to SOp" | February | 2021 | 2021Q3 | 2021 | 512:83736 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2021-02-22 | N | 229.55 | N | 16 | N | N | 1.1101 | 39.4971 | 1341.987
[7 empty] | 2536 | 10490 | 1833471 | 2021-02-22 19:16 | 2021-02-23 00:19 | 303 | 11kV | 303 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210422 A Phase DOLF : 10 Amp Excluded OMS 1833471 | February | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-02-22 | N | 303 | N | 16 | N | N | 1.1101 | 39.4971 | 221.4235
[7 empty] | 2048 | 4628 | 1833498 | 2021-02-22 20:51 | 2021-02-23 00:20 | 209 | 11kV | 836 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210421 B Phase DOLF : 10 Amp Excluded OMS 1833498 | February | 2021 | 2021Q3 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2021-02-22 | N | 209 | N | 16 | N | N | 1.1101 | 39.4971 | 610.9241
[7 empty] | 3200 | 19384 | 1833452 | 2021-02-22 21:30 | 2021-02-23 01:05 | 215 | 11kV | 1935 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210415 tree on mains adj sub 53291 section isolated for removal of tree. Excluded oms 1833452, 1833504 | February | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-02-22 | N | 215 | N | 16 | N | N | 1.1101 | 39.4971 | 1414.0409
[7 empty] | 2274 | 7159 | 1833514 | 2021-02-23 00:31 | 2021-02-23 02:06 | 95 | 11kV | 16751 | 373 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | LID 210426 3 fault operations A & C Phase Earth Fault; Overcurrent UG cable fault between sub 23865 and 55222. DQ Excluded OMS 1833514 | February | 2021 | 2021Q3 | 2021 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | UG | Not Veg | 2021-02-23 | N | 44.9088 | N | 5 | N | N | 1.1101 | 39.4971 | 12241.1367
[7 empty] | 2140 | 5560 | 1833528 | 2021-02-23 07:09 | 2021-02-23 08:10 | 61 | 11kV | 61 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210427 A Phase DOLF : 10 Amp | February | 2021 | 2021Q3 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2021-02-23 | N | 61 | N | 5 | N | N | 1.1101 | 39.4971 | 44.577
[7 empty] | 2353 | 8268 | 1833517 | 2021-02-23 02:48 | 2021-02-23 10:25 | 457 | 11kV | 2800 | 1432 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC45061 Chain Balley Mulloway tripped & reclosed Branch fell through OH mains adj LK41689 and burnt off bond on pole CP1021 See 1834114 1834115 | February | 2021 | 2021Q3 | 2021 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Veg | 2021-02-23 | N | 1.9553 | N | 5 | N | N | 1.1101 | 39.4971 | 2046.1574
[7 empty] | 2931 | 15492 | 1833508 | 2021-02-22 22:36 | 2021-02-23 11:35 | 779 | 11kV | 3910 | 44 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 210419 SUB 51293 Found with 3 blown dolfs leaking tx sub isolated and power restored. sub to be repaired ASAP. | February | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-02-22 | N | 88.8636 | N | 16 | N | N | 1.1101 | 39.4971 | 2857.3127
[7 empty] | 2102 | 5220 | 1833540 | 2021-02-23 07:56 | 2021-02-23 12:20 | 264 | 11kV | 528 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 210430 Single phase DOLF : 10 Amp blown LA replaced Excluded oms 1833540 | February | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-02-23 | N | 264 | N | 5 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 2233 | 6698 | 1833443 | 2021-02-22 17:16 | 2021-02-23 13:30 | 1214 | 11kV | 2428 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210424 Single phase DOLF : 10 Amp defective Tx lid damaged. DQ Excluded oms 1833443, | February | 2021 | 2021Q3 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-02-22 | N | 1214 | N | 16 | N | N | 1.1101 | 39.4971 | 1774.3108
[7 empty] | 2561 | 10741 | 1833618 | 2021-02-23 10:46 | 2021-02-23 23:40 | 774 | 11kV | 26168 | 221 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | REC62705 Jilliby Durren tripped (unable to access recloser for relays) UG cable hit by drainage workers. Outage extended due to defective control box at Rec 45016 and then compounded by Rec 62705 being installed in a blackspot not able to be controlled remotely. See 1834105 1834106 1834107 | February | 2021 | 2021Q3 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | UG | Not Veg | 2021-02-23 | N | 118.4072 | N | 5 | N | N | 1.1101 | 39.4971 | 19122.8026
[7 empty] | 2042 | 4567 | 1833868 | 2021-02-24 11:20 | 2021-02-24 19:40 | 500 | 11kV | 6833 | 20 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 210435 Single phase DOLF : 20 Amp pole EO-10036 hit by lightning. Excluded oms 1833873 | February | 2021 | 2021Q3 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2021-02-24 | N | 341.65 | N | 2 | N | N | 1.1101 | 39.4971 | 4993.3549
[7 empty] | 2020 | 4140 | 1834099 | 2021-02-24 17:57 | 2021-02-24 20:48 | 171 | 11kV | 5130 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC44316 Wisemans Ferry tripeed on: OC Tree branch hit 11kV OH mains between pole WF4 and WF5 | February | 2021 | 2021Q3 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-02-24 | N | 171 | N | 2 | N | N | 1.1101 | 39.4971 | 3748.8527
[7 empty] | 2567 | 10784 | 1834108 | 2021-02-25 12:17 | 2021-02-25 13:13 | 56 | 11kV | 168 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210441 Mmain off xarm FT-33329 refer to oms 1834108 DOP EYEINGTON B | February | 2021 | 2021Q3 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2021-02-25 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 2399 | 8916 | 1834161 | 2021-02-25 14:51 | 2021-02-25 16:35 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210442 2 x 10A Dolf DOP BAXTER M Electrical Storm | February | 2021 | 2021Q3 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2021-02-25 | N | 104 | N | 5 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 3109 | 18314 | 1834213 | 2021-02-25 18:24 | 2021-02-25 21:33 | 189 | 11kV | 241498 | 1627 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.13 tripped on: Earth Fault UG cable fault between S1628 Sw/A, S7026 Sw/A and S1199 Sw/A See 1835335 1835337 GIS 1834222 | February | 2021 | 2021Q3 | 2021 | ZN7481:PA13 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2021-02-25 | N | 148.4315 | N | 5 | N | N | 1.1101 | 39.4971 | 176479.6154
[7 empty] | 2038 | 4516 | 1834176 | 2021-02-25 16:06 | 2021-02-25 22:00 | 354 | 11kV | 167894 | 1600 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | Zn3154 St Ives - Pnl.24 tripped, reclosed & locked out on: B & C phase OC Abnormal: LB3209 closed with AB1552 Open (DMA) Lightning strike (corner Kitchener & Trevaglan) Note: Lightning strike hit HV pole MC13821, Damaging HV insulators and burning HV mains down. HV into LV. Repaired HV hardware and HV mains. Customer installations checked on distributor which was contacted by fallen HV conductor. No damage found. See 18353201835323 1835324 | February | 2021 | 2021Q3 | 2021 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | OH | Not Veg | 2021-02-25 | N | 104.9338 | N | 5 | N | N | 1.1101 | 39.4971 | 122691.9832
[7 empty] | 2784 | 13701 | 1834232 | 2021-02-25 21:19 | 2021-02-25 22:30 | 71 | 11kV | 46588 | 776 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn195 Pymble - Pnl.25 tripped on: Earth Fault Possum on PT1394 See 1835340 1835341 1834235 | February | 2021 | 2021Q3 | 2021 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | OH | Not Veg | 2021-02-25 | N | 60.0361 | N | 5 | N | N | 1.1101 | 39.4971 | 34045.1363
[7 empty] | 2418 | 9237 | 1834246 | 2021-02-26 00:40 | 2021-02-26 03:40 | 180 | 11kV | 186460 | 1358 | HV | Animal Flying Fox | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.18 tripped on: A, B & C phase IOC Bat found on ground near UGOH to S10912 See 1835343 1835344 | February | 2021 | 2021Q3 | 2021 | ZN10998:PA18 | ZN10998:PA18 | ZN10998/000018 | BAYSIDE | OH | Not Veg | 2021-02-26 | N | 137.3049 | N | 2 | N | N | 1.1101 | 39.4971 | 136259.4684
[7 empty] | 1895 | 2770 | 1834383 | 2021-02-26 18:28 | 2021-02-26 21:10 | 162 | 11kV | 40500 | 250 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210445 section isolated for emergency repairs at pole IU-30508 Excluded oms 1834383 & 1834385 | February | 2021 | 2021Q3 | 2021 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Not Veg | 2021-02-26 | N | 162 | N | 2 | N | N | 1.1101 | 39.4971 | 29596.2055
[7 empty] | 1693 | 208 | 1834408 | 2021-02-27 04:20 | 2021-02-27 07:10 | 170 | 11kV | 340 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210446 Single phase DOLF : 10 Amp dead possum at base of pole Excluded oms 1834408 | February | 2021 | 2021Q3 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2021-02-27 | N | 170 | N | 3 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 2455 | 9522 | 1834417 | 2021-02-27 08:16 | 2021-02-27 10:30 | 134 | 11kV | 2412 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210447 DOLF : 10 Amp Excluded OMS 1834417 | February | 2021 | 2021Q3 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2021-02-27 | N | 134 | N | 3 | N | N | 1.1101 | 39.4971 | 1762.6185
[7 empty] | 1762 | 1112 | 1834513 | 2021-02-27 21:58 | 2021-02-27 23:42 | 104 | 11kV | 108442 | 1156 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.35 tripped on B phase OC and EF Note: EFi @ S3128 failed to operate EFI @ S4157 confined space required to check EFI UG cable fault between S49670 Sw/B, S61894 Sw/A and S46284 Sw/B See 1835351 1835352 | February | 2021 | 2021Q3 | 2021 | ZN2835:PA35 | ZN2835:PA35 | ZN02835/000035 | BURWOOD | UG | Not Veg | 2021-02-27 | N | 93.808 | N | 3 | N | N | 1.1101 | 39.4971 | 79246.2151
[7 empty] | 1847 | 2125 | 1834523 | 2021-02-28 05:21 | 2021-02-28 12:33 | 432 | 11kV | 166548 | 1087 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.22 tripped, reclosed & locked out on: O/C & E/F 11kV OH mains down in LV and PT1559 shifted on pole. See 1835282 1835283 1835284 1835285 | February | 2021 | 2021Q3 | 2021 | ZN35500:PA22 | ZN35500:PA22 | ZN35500/000022 | RYDE | OH | Not Veg | 2021-02-28 | N | 153.218 | N | 3 | N | N | 1.1101 | 39.4971 | 121708.3661
[7 empty] | 3076 | 17729 | 1834526 | 2021-02-28 06:56 | 2021-02-28 16:55 | 599 | 11kV | 86715 | 860 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210452 2 fault operations Earth Fault Broken 11KV crossarm,11kv into LV at pole JU-52724. targets 51-N. Excluded OMS report no 1834526 & 1834531. | February | 2021 | 2021Q3 | 2021 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Not Veg | 2021-02-28 | N | 100.8314 | N | 3 | N | N | 1.1101 | 39.4971 | 63368.7643
[7 empty] | 1909 | 2893 | 1834636 | 2021-02-28 23:13 | 2021-03-01 00:19 | 66 | 11kV | 61446 | 931 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn3472 Sefton - Pnl.22 trippedon: A phase OC and IOC Bat on OH mains near AB1867 (N/O) | February | 2021 | 2021Q3 | 2021 | ZN3472:PA22 | ZN3472:PA22 | ZN03472/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-02-28 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 44902.9244
[7 empty] | 2151 | 5714 | 1834746 | 2021-03-01 11:41 | 2021-03-01 13:38 | 117 | 11kV | 152892 | 1616 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210460 1 fault operation Overcurrent, Sensitive Earth Fault | March | 2021 | 2021Q3 | 2021 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2021-03-01 | N | 94.6114 | N | 7 | N | N | 1.1101 | 39.4971 | 111728.964
[7 empty] | 2564 | 10752 | 1834777 | 2021-03-01 13:15 | 2021-03-01 14:05 | 50 | 11kV | 450 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210461 Main off insulator at pole AJ50786- interupted by DOP Excluded OMS 1834777, 1834778, 1834779 | March | 2021 | 2021Q3 | 2021 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2021-03-01 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 1800 | 1576 | 1834768 | 2021-03-01 12:32 | 2021-03-01 14:20 | 108 | 11kV | 648 | 6 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S1610 Homebush Bay Panel 5 tripped on OC and EF Cause: UG cable damaged by contractor - Borer hit UG on CNR of Coombs st and Australia Ave NOTE: DNMS confirmed supply restored @1420 | March | 2021 | 2021Q3 | 2021 | ZN1610:PA5 | ZN1610:PA5 | ZN01610/000005 | PARRAMATTA | UG | Not Veg | 2021-03-01 | N | 108 | N | 7 | N | N | 1.1101 | 39.4971 | 473.5393
[7 empty] | 2958 | 16029 | 1834907 | 2021-03-01 18:30 | 2021-03-01 20:00 | 90 | 11kV | 8820 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | REC44607 Matcham North - Interrupted for repairs to 11kV OH CCT due to tree contact. Tree branch across 11kV CCT and conductor ties broken, SW pulled out of wedge at pole WL2215, ties broken at PT48782 pole WL2214 | March | 2021 | 2021Q3 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-03-01 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 6445.3959
[7 empty] | 2077 | 4933 | 1834827 | 2021-03-01 14:18 | 2021-03-01 20:45 | 387 | 11kV | 774 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 210462 DOLF : 10 Amp A&B phase dolfs found blown, When they were replaced immediately blew taking the recloser with them. Tx to be replaced. Excluded OMS 1834827 | March | 2021 | 2021Q3 | 2021 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2021-03-01 | N | 387 | N | 7 | N | N | 1.1101 | 39.4971 | 565.6164
[7 empty] | 2312 | 7654 | 1834917 | 2021-03-01 19:10 | 2021-03-01 21:08 | 118 | 11kV | 218244 | 1902 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven - Pnl.6 tripped on: Earth Fault Abnormal: S14859 Sw/B Open with S14797 Sw/B Closed. S18599 Sw/A Open & LB44111 Open (DMA - Frontline feeder Pnl.14 OOS) UG cable fault between S.14807, S14740 & S14739 See 1835574 1835575 | March | 2021 | 2021Q3 | 2021 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2021-03-01 | N | 114.7445 | N | 7 | N | N | 1.1101 | 39.4971 | 159486.2781
[7 empty] | 3057 | 17425 | 1834962 | 2021-03-02 01:20 | 2021-03-02 02:45 | 85 | 11kV | 57559 | 753 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | iR77908 Copacabana Koorabel tripped & reclosed on: B & C phase OC Fault current burnt off bond on main line tee off to PT12189 affecting all subs beyond PT12189. See 1835559 1835560 1835561 | March | 2021 | 2021Q3 | 2021 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2021-03-02 | N | 76.4396 | N | 7 | N | N | 1.1101 | 39.4971 | 42062.4195
[7 empty] | 3233 | 19664 | 1834902 | 2021-03-01 13:44 | 2021-03-02 03:00 | 796 | 11kV | 46168 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | S4512 Terrigal Wrragal - Centre phase HV fuse found blown B phase LV fuse found blown as well Cause not ascertained. | March | 2021 | 2021Q3 | 2021 | ZN1673:PA11 | ZN1673:PA11 | ZN01673/000011 | KU-RING-GAI | OH | Veg | 2021-03-01 | N | 796 | N | 7 | N | N | 1.1101 | 39.4971 | 33738.2127
[7 empty] | 2795 | 13800 | 1834961 | 2021-03-02 01:14 | 2021-03-02 04:36 | 202 | 11kV | 64514 | 323 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210469 2 fault operations Excluded OMS 1834961 | March | 2021 | 2021Q3 | 2021 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2021-03-02 | N | 199.7337 | N | 7 | N | N | 1.1101 | 39.4971 | 47144.9284
[7 empty] | 2518 | 10293 | 1835074 | 2021-03-02 12:36 | 2021-03-02 18:22 | 346 | 11kV | 255436 | 2206 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill - Pnl.10 tripped on B & C phase OC Abnormal: LB20398 open with S16746 Sw/B closed. USL24438 Open with S.17159 Sw/B Closed (DMA) Tree brought down OH mains between S17159 Sw/A, S16900 Sw/B and S50262 Sw/B S14159 Dist #1 - is defective. See 1835529 1835530 | March | 2021 | 2021Q3 | 2021 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Veg | 2021-03-02 | N | 115.7915 | N | 7 | N | N | 1.1101 | 39.4971 | 186665.0947
[7 empty] | 3268 | 20047 | 1835167 | 2021-03-02 17:49 | 2021-03-02 18:56 | 67 | 11kV | 81880 | 1225 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.19 tripped (no relay operations) Pnl.19R EFI will not reset Suspect protection malfunction | March | 2021 | 2021Q3 | 2021 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | Exclude | Not Veg | 2021-03-02 | N | 66.8408 | N | 7 | N | N | 1.1101 | 39.4971 | 59835.4889
[7 empty] | 3021 | 16969 | 1835172 | 2021-03-02 18:29 | 2021-03-02 20:20 | 111 | 11kV | 197106 | 1794 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn116 Leichhardt - Pnl.30 tripped on: O/C & E/F UG cable fault between S3502 Sw/B and S35559 Sw/B See 1835507 1835508 | March | 2021 | 2021Q3 | 2021 | ZN116:PA30 | ZN116:PA30 | ZN00116/000030 | INNER WEST | UG | Not Veg | 2021-03-02 | N | 109.8696 | N | 7 | N | N | 1.1101 | 39.4971 | 144039.2512
[7 empty] | 2429 | 9318 | 1835188 | 2021-03-02 22:26 | 2021-03-02 23:01 | 35 | 11kV | 700 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210471 Single phase interupted to remove tree on 11kV ohm | March | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-03-02 | N | 35 | N | 7 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 1752 | 932 | 1835198 | 2021-03-02 21:47 | 2021-03-02 23:02 | 75 | 11kV | 77900 | 1048 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn14144 Wamberal - Pnl.7 tripped, reclosed & locked out on: A & B phase IOC Flashover on 11kV arrestors on UGOH past AB44486 See 1835519 1835520 | March | 2021 | 2021Q3 | 2021 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2021-03-02 | N | 74.3321 | N | 7 | N | N | 1.1101 | 39.4971 | 56927.0223
[7 empty] | 2743 | 13062 | 1835248 | 2021-03-03 09:15 | 2021-03-03 12:50 | 215 | 11kV | 215 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210472 Broken Live Line Lead Excluded OMS 1835248 | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-03-03 | N | 215 | N | 4 | N | N | 1.1101 | 39.4971 | 157.1157
[7 empty] | 2321 | 7772 | 1835376 | 2021-03-03 15:20 | 2021-03-03 17:50 | 150 | 11kV | 150 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210473 Single phase DOLF : 10 Amp Excluded OMS 1835376 | March | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-03-03 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 2636 | 11529 | 1835300 | 2021-03-03 11:40 | 2021-03-03 18:10 | 390 | 11kV | 31250 | 81 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | PT2159 Bridge Patricia - HV Interrupted S46858 Patiricia Bridge - Dist #1 - Interrupted Emergency works for defective pole (NAR71755 - No NECF) See 1835300 1835302 | March | 2021 | 2021Q3 | 2021 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2021-03-03 | N | 385.8025 | N | 4 | N | N | 1.1101 | 39.4971 | 22836.5783
[7 empty] | 1795 | 1536 | 1835318 | 2021-03-03 12:55 | 2021-03-03 18:25 | 330 | 11kV | 53000 | 164 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | iR44753 Bunning Creek - tripped on: OC Section of 11kV interrupted from LB44980 to enable repairs OH mains down near iR44753 See 1835516 1835517 | March | 2021 | 2021Q3 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2021-03-03 | N | 323.1707 | N | 4 | N | N | 1.1101 | 39.4971 | 38730.8368
[7 empty] | 2099 | 5181 | 1835471 | 2021-03-04 09:22 | 2021-03-04 12:50 | 208 | 11kV | 19965.8667 | 96 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of Pnl.17 beyond AB2591 - Foorpath phase bond burnt off @ 2591 Abnormal: LB64433 Closed LB3334 open (PT1270 was in LV//) See 1835471 1837297 | March | 2021 | 2021Q3 | 2021 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Not Veg | 2021-03-04 | N | 207.9778 | N | 2 | N | N | 1.1101 | 39.4971 | 14590.4665
[7 empty] | 2129 | 5443 | 1835637 | 2021-03-04 20:07 | 2021-03-05 00:10 | 243 | 11kV | 331496 | 1383 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At ZN14143 Somersby - Pa12 tripped and reclosed on Relays: E/F, neutral, EFI, trip LED No6 Abnormal switching: S46875 SW/A Open CP44598 CLOSED Fault in section of 11kv fdr from S18442 SW/B to S18171 SW/A. LV // required for phasing. See OMS 1836858, 1836859, 1836860, 1836861, 1836863 & 1836865. | March | 2021 | 2021Q3 | 2021 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2021-03-04 | N | 239.6934 | N | 2 | N | N | 1.1101 | 39.4971 | 242247.4993
[7 empty] | 2526 | 10349 | 1835708 | 2021-03-05 11:23 | 2021-03-05 12:32 | 69 | 11kV | 32775 | 475 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn14144 Wamberal - Pnl.8 tripped on: B & C phase OC Tree hit OH outside 16 Beaufort Rd | March | 2021 | 2021Q3 | 2021 | ZN14144:PA8 | ZN14144:PA8 | ZN14144/000008 | CENTRAL COAST | OH | Veg | 2021-03-05 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 23951.0033
[7 empty] | 2057 | 4767 | 1835804 | 2021-03-05 23:15 | 2021-03-05 23:52 | 37 | 11kV | 1855 | 251 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN2635 Epping Pa51 tripped due to UG cable fault from S65942 to S35643 to S78729. Relays: EFI, Earth fault, OC | March | 2021 | 2021Q3 | 2021 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | UG | Not Veg | 2021-03-05 | N | 7.3904 | N | 2 | N | N | 1.1101 | 39.4971 | 1355.5793
[7 empty] | 2131 | 5465 | 1835923 | 2021-03-06 23:27 | 2021-03-07 00:26 | 59 | 11kV | 40887 | 693 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S711 Blackwattle Bay Panel 21 Tripped on Overcurrent and EFI Abnormal Switching: S7282 SW, Closed S7527 SW/A Openm Cause: UG cable fault See OMS 1836604 1636608 1835926 1835927 1835923 | March | 2021 | 2021Q3 | 2021 | ZN711:PA21 | ZN711:PA18 | ZN00711/000018 | SYDNEY | UG | Not Veg | 2021-03-06 | N | 59 | N | 1 | N | N | 1.1101 | 39.4971 | 29879.0136
[7 empty] | 2290 | 7383 | 1835930 | 2021-03-07 03:35 | 2021-03-07 05:18 | 103 | 33kV Distribution | 898461 | 9202 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At TS16600 Warringah S08 33kV feeder tripped on: A protection A phase & Earth fault zone 1. At S15008 Harbord S08 33kV feeder tripped on: Multi tripped on ITR receive. Abnormal swithcing: S10 feeder OOS defective. All of ZN15009 Manly interrupted. Cause not ascertained. | March | 2021 | 2021Q3 | 2021 | ZN15009:PA11 | ZN15009:PA11 | ZN15009/000011 | NORTHERN BEACHES | UG | Not Veg | 2021-03-07 | N | 97.6376 | N | 4 | N | N | 1.1101 | 39.4971 | 656568.7987
[7 empty] | 2935 | 15539 | 1836080 | 2021-03-07 07:30 | 2021-03-07 07:36 | 6 | 11kV | 432 | 72 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210488 During switching for NAR 69653 Operator inadvertently put the earth on to the feeder rather than the tee off to private HV instalation tripping the recloser that was already on one shot. | March | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2021-03-07 | N | 6 | N | 4 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 2704 | 12363 | 1835938 | 2021-03-07 07:40 | 2021-03-07 19:20 | 700 | 11kV | 2369 | 4 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Recloser CP26228 tripped on OC, IOC, lockout. Suspect 11kV fault beyond HV UGH between PT16261 Davidson Park S to PT16304 Rosevile Reserve. Initially restored to CP22297 and then closed on to fault when trying to energise extent of feeder from CP22297 at 08:41. See OMS 1836142, 1836143 & 1836144. | March | 2021 | 2021Q3 | 2021 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | UG | Not Veg | 2021-03-07 | N | 592.25 | N | 4 | N | N | 1.1101 | 39.4971 | 1731.1953
[7 empty] | 1975 | 3645 | 1836008 | 2021-03-07 19:58 | 2021-03-07 20:48 | 50 | 11kV | 8958 | 195 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 210490 Replace burnt up DOLF. Excluded OMS 1836008, 1836011 | March | 2021 | 2021Q3 | 2021 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2021-03-07 | N | 45.9385 | N | 4 | N | N | 1.1101 | 39.4971 | 6546.2422
[7 empty] | 2868 | 14535 | 1836145 | 2021-03-08 12:34 | 2021-03-08 13:11 | 37 | 11kV | 5217 | 141 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12600 Lisarow - Pnl.5 tripped on: A & B phase IOC Abnormal: S79920 Sw/B Closed with Sw/A Open. S12462 Sw.B Open (DMA) Tree branch on OH mains | March | 2021 | 2021Q3 | 2021 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | OH | Veg | 2021-03-08 | N | 37 | N | 31 | Y | Y | 1.1101 | 39.4971 | 3812.4297
[7 empty] | 1818 | 1809 | 1836133 | 2021-03-08 12:19 | 2021-03-08 13:19 | 60 | 11kV | 8460 | 141 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.17 tripped on: Earth Fault UG cable fault between Pnl17 and S14827 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA17 | ZN12690:PA17 | ZN12690/000017 | CENTRAL COAST | UG | Not Veg | 2021-03-08 | N | 60 | N | 31 | Y | Y | 1.1101 | 39.4971 | 6182.3185
[7 empty] | 2841 | 14320 | 1836063 | 2021-03-08 09:23 | 2021-03-08 13:20 | 237 | 11kV | 185412 | 1317 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN2635 Epping - Panel 43 tripped and reclosed to lockout. Relays: A,B,C phase timed OC, EF, EFI, Fault check, lockout Contractor hit UG cable section of 11kV feeder from S65486/F to S5135/A to S6105/B to S677/B tee S5144. | March | 2021 | 2021Q3 | 2021 | ZN2635:PA43 | ZN2635:PA43 | ZN02635/000043 | PARRAMATTA | UG | Not Veg | 2021-03-08 | N | 140.7836 | N | 31 | Y | Y | 1.1101 | 39.4971 | 135493.6209
[7 empty] | 2597 | 11189 | 1836134 | 2021-03-08 12:03 | 2021-03-08 14:22 | 139 | 11kV | 8463 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn15011 Beacon Hill - Pnl.6R - A phase IOC Tree branch on 11kV OH (cnr Rodborough Rd & Alambie Rd) Fallen tree branch caused one phase hv feeder and two phases of lv distributor wires to clash between poles FF31602 and 31603. Dop on site aware of lv links at pole FF2609 being closed. No switchboard damage found. See 1837254 1837255 | March | 2021 | 2021Q3 | 2021 | ZN15011:PA6 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | OH | Veg | 2021-03-08 | N | 126.3134 | N | 31 | Y | Y | 1.1101 | 39.4971 | 6184.5108
[7 empty] | 3199 | 19381 | 1836248 | 2021-03-08 14:50 | 2021-03-08 18:40 | 230 | 11kV | 1150 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210500 DOLF Excluded OMS 1836248 | March | 2021 | 2021Q3 | 2021 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2021-03-08 | N | 230 | N | 31 | Y | Y | 1.1101 | 39.4971 | 840.3861
[7 empty] | 1916 | 2971 | 1836434 | 2021-03-08 17:16 | 2021-03-08 18:55 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210568 A & B Phase DOLF : 10 Amp Excluded OMS 1836434 | March | 2021 | 2021Q3 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-03-08 | N | 99 | N | 31 | Y | Y | 1.1101 | 39.4971 | 72.3463
[7 empty] | 2437 | 9373 | 1836173 | 2021-03-08 13:43 | 2021-03-08 20:11 | 388 | 11kV | 57314 | 181 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210514 3 fault operations Earth Fault WIre broken at P. 4J-10004 Excluded OMS 1836173 | March | 2021 | 2021Q3 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-03-08 | N | 316.6519 | N | 31 | Y | Y | 1.1101 | 39.4971 | 41883.3807
[7 empty] | 1794 | 1523 | 1836231 | 2021-03-08 14:41 | 2021-03-08 20:15 | 333.7 | 11kV | 12680.6 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210501 A Phase DOLF : 31 Amp | March | 2021 | 2021Q3 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2021-03-08 | N | 333.7 | N | 31 | Y | Y | 1.1101 | 39.4971 | 9266.6085
[7 empty] | 1902 | 2838 | 1836287 | 2021-03-08 14:55 | 2021-03-08 21:00 | 365 | 11kV | 120450 | 330 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210502 2 fault operations 3 phase Overcurrent Branch on mains adjacent sub 3903. | March | 2021 | 2021Q3 | 2021 | 238:34141 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2021-03-08 | N | 365 | N | 31 | Y | Y | 1.1101 | 39.4971 | 88021.3073
[7 empty] | 2473 | 9708 | 1836509 | 2021-03-08 20:46 | 2021-03-08 22:07 | 81 | 11kV | 6723 | 83 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT13205 North Burge Brick Wharf - HDO Operated Possum found on the ground | March | 2021 | 2021Q3 | 2021 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2021-03-08 | N | 81 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4912.9701
[7 empty] | 2621 | 11301 | 1836320 | 2021-03-08 15:23 | 2021-03-08 23:20 | 477 | 11kV | 20034 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210504 B Phase DOLF : 31 Amp LV mains down sub 18074. Excluded OMS 1836320.. | March | 2021 | 2021Q3 | 2021 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2021-03-08 | N | 477 | N | 31 | Y | Y | 1.1101 | 39.4971 | 14640.2563
[7 empty] | 2817 | 14024 | 1836243 | 2021-03-08 14:34 | 2021-03-08 23:54 | 560 | 11kV | 106433 | 225 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210499 & 210505 11kV mains down between poles GQ-87967 & GQ-87968 And single phase DOLF at 50824 : 10 Amp Excluded OMS 1836243 | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-03-08 | N | 473.0356 | N | 31 | Y | Y | 1.1101 | 39.4971 | 77778.0972
[7 empty] | 2972 | 16290 | 1836300 | 2021-03-08 14:56 | 2021-03-09 00:25 | 569 | 11kV | 101055 | 346 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210503 2 fault operation 3 phase Overcurrent 11kV mains down pole JR-14715. Excluded OMS 1836300. | March | 2021 | 2021Q3 | 2021 | 238:34141 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2021-03-08 | N | 292.0665 | N | 31 | Y | Y | 1.1101 | 39.4971 | 73848.0134
[7 empty] | 3245 | 19750 | 1836197 | 2021-03-08 19:57 | 2021-03-09 01:15 | 318 | 11kV | 12084 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210506 A Phase DOLF : 31 Amp Note: customer was also affected by wider area outage prior to this, refer to OMS 1836696 | March | 2021 | 2021Q3 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | SINGLETON | OH | Veg | 2021-03-08 | N | 318 | N | 31 | Y | Y | 1.1101 | 39.4971 | 8830.6308
[7 empty] | 2807 | 13897 | 1836326 | 2021-03-08 15:23 | 2021-03-09 01:16 | 593 | 11kV | 7709 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210507 A Phase DOLF : 20 Amp LV Mains wrapped sub 61932 Excluded OMS 1836317 | March | 2021 | 2021Q3 | 2021 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2021-03-08 | N | 593 | N | 31 | Y | Y | 1.1101 | 39.4971 | 5633.5098
[7 empty] | 2012 | 4076 | 1836237 | 2021-03-08 14:43 | 2021-03-09 04:28 | 825 | 11kV | 3300 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 210512 Wire off pin DP-20114 Excluded OMS 1836237. | March | 2021 | 2021Q3 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2021-03-08 | N | 825 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 2132 | 5467 | 1836532 | 2021-03-09 02:48 | 2021-03-09 04:37 | 109 | 11kV | 2943 | 27 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 210508 No protection operations. Section isolated to replace wire in pins Excluded OMS 1836532 | March | 2021 | 2021Q3 | 2021 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2021-03-09 | N | 109 | N | 9 | N | N | 1.1101 | 39.4971 | 2150.6576
[7 empty] | 2115 | 5302 | 1836336 | 2021-03-08 19:57 | 2021-03-09 04:45 | 528 | 11kV | 82896 | 157 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210510 broken pole FQ-31820 Tree fell on open LV overhead mains and snapped pole FQ31820. Replaced pole and reattached lv and hv mains and re-instated supply. Note: customers also affected by wider area outage prior to this, refer to OMS 1836696 Excluded OMS 1836336 | March | 2021 | 2021Q3 | 2021 | 512:83736 | 512:83736 | ZN00512/083736 | CESSNOCK | OH | Veg | 2021-03-08 | N | 528 | N | 31 | Y | Y | 1.1101 | 39.4971 | 60577.9518
[7 empty] | 2039 | 4526 | 1836544 | 2021-03-09 05:52 | 2021-03-09 08:12 | 140 | 11kV | 79110 | 582 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210534 2 fault operations A Phase Instantaneous Overcurrent Excluded OMS 1836544 | March | 2021 | 2021Q3 | 2021 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Veg | 2021-03-09 | N | 135.9278 | N | 9 | N | N | 1.1101 | 39.4971 | 57811.2547
[7 empty] | 2594 | 11182 | 1836549 | 2021-03-09 06:09 | 2021-03-09 08:15 | 126 | 11kV | 378 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210519 C Phase DOLF : 10 Amp Excluded OMS 1836549 | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2021-03-09 | N | 126 | N | 9 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 3151 | 18812 | 1836215 | 2021-03-08 14:30 | 2021-03-09 08:50 | 1100 | 11kV | 3300 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210520 Single phase DOLF : 10 Amp Excluded OMS 1836215 | March | 2021 | 2021Q3 | 2021 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2021-03-08 | N | 1100 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 2073 | 4882 | 1836487 | 2021-03-08 19:00 | 2021-03-09 09:05 | 845 | 11kV | 4225 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210521 A Phase DOLF : 10 Amp Excluded OMS 1836487 | March | 2021 | 2021Q3 | 2021 | 522:83123 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2021-03-08 | N | 845 | N | 31 | Y | Y | 1.1101 | 39.4971 | 3087.5054
[7 empty] | 1999 | 3802 | 1836185 | 2021-03-08 14:11 | 2021-03-09 09:32 | 1161.4 | 11kV | 18582.4 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210522 A & B Phase DOLF : 20 Amp David Schmierer replaced 2 x 20 DOLF at LF 74388. SA | March | 2021 | 2021Q3 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2021-03-08 | N | 1161.4 | N | 31 | Y | Y | 1.1101 | 39.4971 | 13579.4698
[7 empty] | 2953 | 15957 | 1836416 | 2021-03-08 14:40 | 2021-03-09 11:20 | 1240 | 11kV | 22320 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210509 A Phase DOLF : 16 Amp also replaced A ph dolf (10 Amp) at sub 63627 | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2021-03-08 | N | 1240 | N | 31 | Y | Y | 1.1101 | 39.4971 | 16310.7977
[7 empty] | 2143 | 5610 | 1836180 | 2021-03-08 13:51 | 2021-03-09 11:45 | 1314 | 11kV | 58363 | 138 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 210525 2 fault operations Overcurrent; Earth Fault Pole down@ MD90693. Still to be fixed. Excluded OMS 1836180 | March | 2021 | 2021Q3 | 2021 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2021-03-08 | N | 422.9203 | N | 31 | Y | Y | 1.1101 | 39.4971 | 42649.959
[7 empty] | 1750 | 904 | 1836214 | 2021-03-08 14:09 | 2021-03-09 11:50 | 1301 | 11kV | 91716.75 | 72 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210528 2 fault operations Excluded OMS 1836531 | March | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2021-03-08 | N | 1273.8438 | N | 31 | Y | Y | 1.1101 | 39.4971 | 67023.8957
[7 empty] | 3202 | 19408 | 1836505 | 2021-03-08 20:34 | 2021-03-09 12:00 | 926 | 11kV | 6482 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Note:No LID report raised by the control room, wide area electrical storm at the time of event Replace 10A DOLF at PT - 4640. Supply restored at 12.00. Job complete. | March | 2021 | 2021Q3 | 2021 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Veg | 2021-03-08 | N | 926 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4736.8544
[7 empty] | 2062 | 4787 | 1836186 | 2021-03-08 14:07 | 2021-03-09 12:10 | 1323 | 11kV | 64011 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210529 2 fault operations Excluded OMS 1836186 | March | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2021-03-08 | N | 1123 | N | 31 | Y | Y | 1.1101 | 39.4971 | 46777.3508
[7 empty] | 3253 | 19827 | 1836587 | 2021-03-09 08:39 | 2021-03-09 14:30 | 351.2333 | 11kV | 351.2333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210539 Single phase DOLF : 10 Amp Excluded OMS 1836592 | March | 2021 | 2021Q3 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2021-03-09 | N | 351.2333 | N | 9 | N | N | 1.1101 | 39.4971 | 256.671
[7 empty] | 1788 | 1474 | 1836212 | 2021-03-08 14:14 | 2021-03-09 14:51 | 1477 | 11kV | 1100408 | 998 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210511 and LID 210549 3 phase Trees on mains and wires off pins Sensitive Earth Fault | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-03-08 | N | 1102.6132 | N | 31 | Y | Y | 1.1101 | 39.4971 | 804145.7099
[7 empty] | 2395 | 8850 | 1836191 | 2021-03-08 14:12 | 2021-03-09 15:23 | 1511 | 11kV | 40797 | 27 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210545 Device 40534 A, B & C Phase DOLF : 20 Amp, also LID 210553 Sub 49507 Wire down at pole DD-40201 Excluded OMS 1836357 | March | 2021 | 2021Q3 | 2021 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2021-03-08 | N | 1511 | N | 31 | Y | Y | 1.1101 | 39.4971 | 29813.2443
[7 empty] | 2299 | 7523 | 1836703 | 2021-03-09 12:47 | 2021-03-09 17:50 | 303 | 11kV | 303 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210569 C Phase DOLF : 10 Amp Excluded OMS 1836703 | March | 2021 | 2021Q3 | 2021 | 812:19072 | 812:19072 | ZN00812/019072 | MAITLAND | OH | Veg | 2021-03-09 | N | 303 | N | 9 | N | N | 1.1101 | 39.4971 | 221.4235
[7 empty] | 2905 | 15048 | 1836448 | 2021-03-08 18:30 | 2021-03-09 18:00 | 1410 | 11kV | 7050 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 210571 & 210567 Faulty Transformer replaced sub 1650 Excluded OMS 1836448 | March | 2021 | 2021Q3 | 2021 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2021-03-08 | N | 1410 | N | 31 | Y | Y | 1.1101 | 39.4971 | 5151.9321
[7 empty] | 2163 | 5821 | 1836799 | 2021-03-09 14:00 | 2021-03-09 18:50 | 290 | 11kV | 290 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210538 Broken Live Line Lead | March | 2021 | 2021Q3 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-03-09 | N | 290 | N | 9 | N | N | 1.1101 | 39.4971 | 211.9234
[7 empty] | 2443 | 9465 | 1836192 | 2021-03-08 14:07 | 2021-03-09 20:04 | 1797 | 11kV | 368929 | 274 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 210540 Defective step transformer 59000 excluded OMS 1836192 | March | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-03-08 | N | 1346.4562 | N | 31 | Y | Y | 1.1101 | 39.4971 | 269602.4316
[7 empty] | 2449 | 9482 | 1836220 | 2021-03-08 14:06 | 2021-03-09 20:35 | 1829 | 11kV | 98197 | 200 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Electrical Storm | N | LID 210537 1 fault operation Earth Fault Broken Tie pole. DP-60009. Excluded OMS 1836220 & 1836726 | March | 2021 | 2021Q3 | 2021 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2021-03-08 | N | 490.985 | N | 31 | Y | Y | 1.1101 | 39.4971 | 71759.4713
[7 empty] | 3089 | 17997 | 1836550 | 2021-03-09 06:55 | 2021-03-09 21:30 | 875 | 11kV | 875 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Previous Storm | N | 2 blown dolfs on arrival, blown tank found after testing, replaced tx Note: No LID report raised | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-03-09 | N | 875 | N | 9 | N | N | 1.1101 | 39.4971 | 639.4242
[7 empty] | 1777 | 1379 | 1836490 | 2021-03-08 14:07 | 2021-03-10 00:01 | 2034 | 11kV | 6102 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210575 A Phase DOLF : 5 Amp excluded OMS 1836490 | March | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-03-08 | N | 2034 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4459.1616
[7 empty] | 2061 | 4786 | 1836835 | 2021-03-09 23:07 | 2021-03-10 01:45 | 158 | 11kV | 2212 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210579 A Phase DOLF : 10 Amp Fuse save ripped during storm. Also part of larger outage from Sw 2389. Step up tx fault 59000. So these guys have been off since the start of the larger outage. Excluded OMS 1836835 | March | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-03-09 | N | 158 | N | 9 | N | N | 1.1101 | 39.4971 | 1616.4644
[7 empty] | 2302 | 7552 | 1836879 | 2021-03-10 08:16 | 2021-03-10 10:21 | 125 | 11kV | 7839 | 523 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Section of Panel 8 Berkeley Vale Recloser CP41115 Lakeledge Audie Tripped and reclosed Cause: PT11908 Flashover See OMS 1837289 1837290 1836869 1836872 1836876 1836879 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA8 | ZN12690:PA8 | ZN12690/000008 | CENTRAL COAST | OH | Veg | 2021-03-10 | N | 14.9885 | N | 9 | N | N | 1.1101 | 39.4971 | 5728.51
[7 empty] | 3063 | 17555 | 1836841 | 2021-03-10 05:59 | 2021-03-10 10:55 | 296 | 11kV | 1776 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210577 DOLF : 10 Amp Sub 70437 also had a blown Sub fuse 10amp. On at same time. Excluded OMS 1836841 | March | 2021 | 2021Q3 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-03-10 | N | 296 | N | 9 | N | N | 1.1101 | 39.4971 | 1297.8484
[7 empty] | 2259 | 6981 | 1836730 | 2021-03-09 13:48 | 2021-03-10 12:59 | 1391 | 11kV | 18369 | 107 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC45026 Fountaindale - Tripped Cause not ascertained at the same time as 66kV 88J Feeder See 1837235 1837236 1837237 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2021-03-09 | N | 171.6729 | N | 9 | N | N | 1.1101 | 39.4971 | 13423.5234
[7 empty] | 2539 | 10556 | 1837034 | 2021-03-10 14:21 | 2021-03-10 15:06 | 45 | 11kV | 10980 | 244 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1850 Bass Hill Panel 31 Tripped, Reclosed, Tripped and Locked out on Signals: 11kV Trip Cause: Feeder Protection A relay, A and B phase IOC, Feeder protection B relay, A and B phase IOC, Reclose Attempt Cause: A metalic balloon was found wrapped in the 11kV mains outside 91 Saltash Ave Yagoona See OMS 1837034 1837037 1837038 | March | 2021 | 2021Q3 | 2021 | ZN1850:PA31 | ZN1850:PA31 | ZN01850/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-03-10 | N | 45 | N | 9 | N | N | 1.1101 | 39.4971 | 8023.8601
[7 empty] | 3030 | 17067 | 1836848 | 2021-03-10 07:36 | 2021-03-10 17:05 | 569 | 11kV | 2801 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210582 A Phase DOLF : 5 Amp Fuse saver tripped /Blown 5 amp fuse on Aph. Blown Arrestor at sub 59053 Bph Excluded OMS 1836848 | March | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-03-10 | N | 311.2222 | N | 9 | N | N | 1.1101 | 39.4971 | 2046.8882
[7 empty] | 1860 | 2345 | 1837054 | 2021-03-10 15:55 | 2021-03-10 17:15 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210580 A & B Phase DOLF : 10 Amp no cause found but sub not used often- fuses may have blown during storm sub evening | March | 2021 | 2021Q3 | 2021 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2021-03-10 | N | 80 | N | 9 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 3263 | 19990 | 1837008 | 2021-03-10 14:14 | 2021-03-10 18:00 | 226 | 11kV | 2938 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Section of Panel 12 at Wyong Beyond CP44828 Cause: Interrupted for safety reason - Broken crossarm beyond CP44828 | March | 2021 | 2021Q3 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2021-03-10 | N | 226 | N | 9 | N | N | 1.1101 | 39.4971 | 2147.0037
[7 empty] | 2696 | 12311 | 1837059 | 2021-03-10 16:13 | 2021-03-10 19:58 | 225 | 11kV | 72456 | 711 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210581 Burnt off HV tappings pole JU-70625 Excluded OMS 1837059 | March | 2021 | 2021Q3 | 2021 | 261:81864 | 261:81864 | ZN00261/081864 | LAKE MACQUARIE | OH | Not Veg | 2021-03-10 | N | 101.9072 | N | 9 | N | N | 1.1101 | 39.4971 | 52948.7077
[7 empty] | 2441 | 9437 | 1837238 | 2021-03-10 21:00 | 2021-03-10 21:20 | 20 | 11kV | 40 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 210584 refer to OMS 1837035 Retension service off sub pole | March | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2021-03-10 | N | 20 | N | 9 | N | N | 1.1101 | 39.4971 | 29.2308
[7 empty] | 2153 | 5735 | 1837118 | 2021-03-10 21:42 | 2021-03-10 21:50 | 8 | 11kV | 824 | 103 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 210583 40Amp C phase Fuse Substation DOLF Faulty HV dolf replaced | March | 2021 | 2021Q3 | 2021 | 261:81865 | 261:81865 | ZN00261/081865 | LAKE MACQUARIE | OH | Not Veg | 2021-03-10 | N | 8 | N | 9 | N | N | 1.1101 | 39.4971 | 602.1549
[7 empty] | 2995 | 16589 | 1837415 | 2021-03-11 22:57 | 2021-03-12 04:05 | 308 | 11kV | 1848 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210595 C Phase DOLF : 10 Amp | March | 2021 | 2021Q3 | 2021 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Veg | 2021-03-11 | N | 308 | N | 2 | N | N | 1.1101 | 39.4971 | 1350.4639
[7 empty] | 2644 | 11614 | 1837457 | 2021-03-12 08:46 | 2021-03-12 12:30 | 224 | 11kV | 224 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210596 10 Amp, substation DOLF | March | 2021 | 2021Q3 | 2021 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2021-03-12 | N | 224 | N | 14 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 2369 | 8509 | 1837406 | 2021-03-12 11:55 | 2021-03-12 12:50 | 55 | 11kV | 10450 | 190 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Greenacre Park Pnl.33 - LB2034 to S5828 interrupted for safety to remove palm tree from OH mains | March | 2021 | 2021Q3 | 2021 | ZN1285:PA33 | ZN1285:PA33 | ZN01285/000033 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-03-12 | N | 55 | N | 14 | N | N | 1.1101 | 39.4971 | 7636.5518
[7 empty] | 2806 | 13894 | 1837381 | 2021-03-11 23:15 | 2021-03-12 16:20 | 1025 | 11kV | 147730 | 159 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Section of 11kv FDR interrupted for emergency repairs after car hit pole (pole carrying CP1376). Interrupted from CP909 to CP3045 to CP1240 to S62030/A tee S7701 and PT78812. *Note: CP1376 Bypassed, region to follow up and restore network at later date. S62030 Cheltenham Station - Dist.3 also interrupted for emergency repairs. See OMS 1837407 | March | 2021 | 2021Q3 | 2021 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Not Veg | 2021-03-11 | N | 929.1195 | N | 2 | N | N | 1.1101 | 39.4971 | 107956.7267
[7 empty] | 1968 | 3584 | 1837592 | 2021-03-12 16:29 | 2021-03-12 18:08 | 99 | 11kV | 6094 | 66 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210615 Thunderstorm Overcurrent | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-03-12 | N | 92.3333 | N | 14 | N | N | 1.1101 | 39.4971 | 4453.3155
[7 empty] | 2600 | 11205 | 1837598 | 2021-03-12 16:39 | 2021-03-12 18:25 | 106 | 11kV | 194852 | 2162 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN9252 Jannali - Panel 22 tripped on relays OC, SEF, EFI Abnormal switching: CP79650 Closed CP79656 Open Cause not ascertained, possible lightning strike. | March | 2021 | 2021Q3 | 2021 | ZN9252:PA22 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Veg | 2021-03-12 | N | 90.1258 | N | 14 | N | N | 1.1101 | 39.4971 | 142392.0944
[7 empty] | 2300 | 7534 | 1837636 | 2021-03-12 17:56 | 2021-03-12 19:40 | 104.2 | 11kV | 1979.8 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210608 Thunderstorm 16, B and C Phases, Line DOLF | March | 2021 | 2021Q3 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2021-03-12 | N | 104.2 | N | 14 | N | N | 1.1101 | 39.4971 | 1446.7794
[7 empty] | 3285 | 20324 | 1837594 | 2021-03-12 16:34 | 2021-03-12 20:01 | 207 | 11kV | 31238 | 160 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210606 2 fault operations Overcurrent; Earth Fault Excluded OMS 1837594 | March | 2021 | 2021Q3 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2021-03-12 | N | 195.2375 | N | 14 | N | N | 1.1101 | 39.4971 | 22827.809
[7 empty] | 2776 | 13582 | 1837630 | 2021-03-12 17:34 | 2021-03-12 20:05 | 151 | 11kV | 302 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210609 C Phase DOLF : 10 Amp Excluded OMS 1837630 | March | 2021 | 2021Q3 | 2021 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Veg | 2021-03-12 | N | 151 | N | 14 | N | N | 1.1101 | 39.4971 | 220.6927
[7 empty] | 2509 | 10210 | 1837643 | 2021-03-12 18:26 | 2021-03-12 20:20 | 114 | 11kV | 570 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210611 Thunderstorm 10 Amp, Phase B Substation DOLF | March | 2021 | 2021Q3 | 2021 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2021-03-12 | N | 114 | N | 14 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 2563 | 10751 | 1837696 | 2021-03-12 20:29 | 2021-03-12 23:08 | 159 | 11kV | 3411 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210616 and 210619 Thunderstorm Pole Mounted, RAGCB Overcurrent Refer to oms1837696 tree on mains pole AK-32500 removed tree on mains pole AK-32500 removed" | March | 2021 | 2021Q3 | 2021 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2021-03-12 | N | 110.0323 | N | 14 | N | N | 1.1101 | 39.4971 | 2492.6582
[7 empty] | 2906 | 15051 | 1837600 | 2021-03-12 16:38 | 2021-03-13 00:20 | 462 | 11kV | 32465 | 226 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 210617 Thunderstorm Phases A,B & C (Three Phase) Pole Mounted RAGCB Sensitive Earth Fault Refer to oms1837600 sub 53374 faulty after storm damage. sub isolated for replacement | March | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-03-12 | N | 143.6504 | N | 14 | N | N | 1.1101 | 39.4971 | 23724.4644
[7 empty] | 3278 | 20180 | 1837727 | 2021-03-13 03:29 | 2021-03-13 04:35 | 65.6167 | 11kV | 3871.3833 | 59 | HV | Animal Possum | Animal | Fuse Assembly | Unplanned | No Weather Impact | N | At PT12453 Oakglen North, centre phase 11kV HDO operated. Dead possum found at base of pole. | March | 2021 | 2021Q3 | 2021 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2021-03-13 | N | 65.6167 | N | 9 | N | N | 1.1101 | 39.4971 | 2829.0928
[7 empty] | 3043 | 17242 | 1837725 | 2021-03-13 02:55 | 2021-03-13 05:10 | 135 | 11kV | 141149 | 1342 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN847 Hornsby - Panel 22 tripped on A phase IOC and timed, fault check, efi Cause: UG fault from S5600 to CP65298 tee PT1742. | March | 2021 | 2021Q3 | 2021 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | UG | Not Veg | 2021-03-13 | N | 105.1781 | N | 9 | N | N | 1.1101 | 39.4971 | 103147.526
[7 empty] | 2904 | 15024 | 1837726 | 2021-03-13 02:55 | 2021-03-13 05:53 | 178 | 11kV | 10228 | 66 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210622 2 Fault Operations Phases A & B. Overcurrent Refer to OMS 1837726 Fault detector = A & B phase O/C" | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-03-13 | N | 154.9697 | N | 9 | N | N | 1.1101 | 39.4971 | 7474.3207
[7 empty] | 3188 | 19315 | 1837705 | 2021-03-12 21:34 | 2021-03-13 07:20 | 586 | 11kV | 1172 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210644 A Phase DOLF : 10 Amp TX DOLF blown during storm Excluded OMS 1837705 | March | 2021 | 2021Q3 | 2021 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2021-03-12 | N | 586 | N | 14 | N | N | 1.1101 | 39.4971 | 856.463
[7 empty] | 1855 | 2279 | 1837713 | 2021-03-12 22:27 | 2021-03-13 08:10 | 583 | 11kV | 1166 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210626 A Phase DOLF : 10 Amp DOLF blown on sub during storm Excluded OMS 1837713 | March | 2021 | 2021Q3 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2021-03-12 | N | 583 | N | 14 | N | N | 1.1101 | 39.4971 | 852.0784
[7 empty] | 1708 | 395 | 1837714 | 2021-03-12 22:31 | 2021-03-13 08:15 | 584.3333 | 11kV | 1168.6667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 210624 A & C Phase DOLF : 20 Amp DOLFS blown during storm | March | 2021 | 2021Q3 | 2021 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2021-03-12 | N | 584.3333 | N | 14 | N | N | 1.1101 | 39.4971 | 854.0271
[7 empty] | 2415 | 9206 | 1837738 | 2021-03-13 07:09 | 2021-03-13 11:05 | 236 | 11kV | 472 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210638 Probable blown HV arrester on Pt Sub - 50308. LV and HV fuses opened, warning tag applied, customer from 1070 Hermitage Rd advised of interruption. Could qualified staff attend ASAP thanks Previous Storm 10Amp, C phase, Substation DOLF | March | 2021 | 2021Q3 | 2021 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2021-03-13 | N | 236 | N | 9 | N | N | 1.1101 | 39.4971 | 344.9237
[7 empty] | 2363 | 8366 | 1837754 | 2021-03-13 09:17 | 2021-03-13 11:20 | 123 | 11kV | 246 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210637 A Phase DOLF : 10 Amp excluded OMS 1837754 | March | 2021 | 2021Q3 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2021-03-13 | N | 123 | N | 9 | N | N | 1.1101 | 39.4971 | 179.7695
[7 empty] | 3238 | 19717 | 1837759 | 2021-03-13 09:39 | 2021-03-13 11:40 | 120.5833 | 11kV | 120.5833 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 210640 A Phase DOLF : 10 Amp OMS 1837765 was also rung in by same customer, they assumed sub 50358 was without power but sub checked ok No outage recorded Excluded OMS 1837765 | March | 2021 | 2021Q3 | 2021 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2021-03-13 | N | 120.5833 | N | 9 | N | N | 1.1101 | 39.4971 | 88.1187
[7 empty] | 2601 | 11208 | 1837789 | 2021-03-13 11:18 | 2021-03-13 12:10 | 52 | 11kV | 208 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 210639 Previous Storm 10Amp, Phase C | March | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-03-13 | N | 52 | N | 9 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 2856 | 14414 | 1837616 | 2021-03-12 17:03 | 2021-03-13 15:30 | 1347 | 11kV | 20732.8 | 52 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 210607 Mains down beyond 11kv links 40452. section isolated for repair | March | 2021 | 2021Q3 | 2021 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2021-03-12 | N | 398.7077 | N | 14 | N | N | 1.1101 | 39.4971 | 15150.9187
[7 empty] | 2981 | 16332 | 1837816 | 2021-03-13 13:12 | 2021-03-13 15:40 | 148 | 11kV | 3700 | 25 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 210642 Employee noticed 11kV main on X-arm pole IQ71512 Section isolated by DOP to allow repairs No protecion operations Excluded OMS 1837816 | March | 2021 | 2021Q3 | 2021 | 528:83020 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2021-03-13 | N | 148 | N | 9 | N | N | 1.1101 | 39.4971 | 2703.8509
[7 empty] | 3276 | 20172 | 1837882 | 2021-03-13 22:05 | 2021-03-13 23:29 | 84 | 11kV | 252 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210646 Replaced B & C phase 10A DOLF supply on 2329hrs No Cause Found (Not Storm Condition) | March | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-03-13 | N | 84 | N | 9 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 2844 | 14331 | 1838039 | 2021-03-14 14:08 | 2021-03-14 17:00 | 172 | 11kV | 516 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210653 Heavy Rain Customer reports: phase to water pumps not working still has 2 phases working. Thinks a phase has dropped from transmittor coming from transmissison across river. Clear access, no pets, no iso | March | 2021 | 2021Q3 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-03-14 | N | 172 | N | 7 | N | N | 1.1101 | 39.4971 | 377.0776
[7 empty] | 2957 | 16022 | 1837927 | 2021-03-14 09:26 | 2021-03-14 17:25 | 479 | 11kV | 9323 | 27 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 210652 20 Amp, Phase B & C, Line DOLF Broken insulator at Pole DP 40162- Singleton on call to repair Heavy Rain | March | 2021 | 2021Q3 | 2021 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2021-03-14 | N | 345.2963 | N | 7 | N | N | 1.1101 | 39.4971 | 6812.9734
[7 empty] | 2249 | 6827 | 1838089 | 2021-03-14 17:15 | 2021-03-14 19:30 | 135 | 11kV | 25515 | 189 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | S15937 Molong St - Whole sub interrupted for safety S17026 Monash Ozone - Dist #1 - Interrupted for safety S50239 Pitt Huston - Dist #4 - Interrupted for safety3 S16461 Austin Robertson - Dist #1 - Interrupted for safety Repair defective pole See 1838093 1838092 1838091 1838089 | March | 2021 | 2021Q3 | 2021 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2021-03-14 | N | 135 | N | 7 | N | N | 1.1101 | 39.4971 | 18645.6094
[7 empty] | 2343 | 8143 | 1837999 | 2021-03-14 12:44 | 2021-03-14 20:30 | 466 | 11kV | 19402 | 42 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty - Pnl.20 - USL44413 to PT13827 & PT65322 interrupted to allow repairs after tree fallen onto 11kV mains outside 1 Halloran Lane. | March | 2021 | 2021Q3 | 2021 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Veg | 2021-03-14 | N | 461.9524 | N | 7 | N | N | 1.1101 | 39.4971 | 14178.4093
[7 empty] | 2538 | 10555 | 1838351 | 2021-03-14 20:26 | 2021-03-14 20:31 | 5 | 11kV | 1225 | 245 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | Zn1850 Bass Hill - Pnl.31 - de-energised for safety at the request of DOp due to arcing LB2004 | March | 2021 | 2021Q3 | 2021 | ZN1850:PA31 | ZN1850:PA31 | ZN01850/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-03-14 | N | 5 | N | 7 | N | N | 1.1101 | 39.4971 | 895.1939
[7 empty] | 2393 | 8812 | 1837974 | 2021-03-14 15:48 | 2021-03-14 23:15 | 447 | 11kV | 4023 | 9 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Rain Light | N | PT14484 Mulina Brush interrupted from USL44534 after tree fell onto PT causing LV cross arm to snap. | March | 2021 | 2021Q3 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-03-14 | N | 447 | N | 7 | N | N | 1.1101 | 39.4971 | 2939.8897
[7 empty] | 1913 | 2947 | 1838169 | 2021-03-15 07:58 | 2021-03-15 11:45 | 227 | 11kV | 74120 | 385 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | S1870 Waterloo Macquarie No.4 - Sw/A tripped on Translay Abnormal: S63707 Sw/B to S1853 Sw/A OOS DMA (Ring feeder radial) UG cable hit by star picket at 2-10 Cottonwood Cres See 1838383 | March | 2021 | 2021Q3 | 2021 | ZN2635:PA39 | ZN2635:PA39 | ZN02635/000039 | RYDE | UG | Not Veg | 2021-03-15 | N | 192.5195 | N | 3 | N | N | 1.1101 | 39.4971 | 54164.7098
[7 empty] | 2611 | 11249 | 1838249 | 2021-03-15 10:54 | 2021-03-15 15:00 | 245.5167 | 11kV | 1227.5833 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210658 DOLF : 10 Amp Chat to Annisa if you cant find this one. 3 customers rang in from 2 different subs. and all jobs got rolled up to RAGCB. Only a sub job | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-03-15 | N | 245.5167 | N | 3 | N | N | 1.1101 | 39.4971 | 897.0817
[7 empty] | 2670 | 11990 | 1838062 | 2021-03-14 15:19 | 2021-03-15 16:27 | 1508 | 11kV | 28526 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP554 Recloser tripped and reclosed. Tree brought down HV & LV. L/W has Earths and shorts EMSO and Dop to attend first thing in the morning.11kV feeder Isolated from AB.3252 to LB.76965 tee to PT.656 Rosscommon Rd.AP and CTW issued at PT.656 Interruption at PT.2136 Arcadia Cobah Dist#2 out for safety (OMS1838849). | March | 2021 | 2021Q3 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2021-03-14 | N | 102.2437 | N | 7 | N | N | 1.1101 | 39.4971 | 20845.9594
[7 empty] | 3110 | 18328 | 1838367 | 2021-03-15 14:42 | 2021-03-15 17:55 | 193 | 11kV | 154129 | 1401 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210659 Broken 11kV Crossarm at Pole HS-72457. 11kV mains sitting on non insulated Ballard stay wire. Dropped of feeder 80932 for safety. No Protection operations. Excluded OMS 1838337 & 1838367 | March | 2021 | 2021Q3 | 2021 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2021-03-15 | N | 110.0136 | N | 3 | N | N | 1.1101 | 39.4971 | 112632.9272
[7 empty] | 2201 | 6301 | 1838475 | 2021-03-16 04:17 | 2021-03-16 05:55 | 98 | 11kV | 171912 | 1874 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.2 tripped on: Earth Fault UG cable fault between S114 SwB, S8322 Sw/A and S6874 Sw/B See 1839055 1839057 | March | 2021 | 2021Q3 | 2021 | ZN7900:PA2 | ZN7900:PA2 | ZN07900/000002 | SYDNEY | UG | Not Veg | 2021-03-16 | N | 91.7353 | N | 3 | N | N | 1.1101 | 39.4971 | 125628.2191
[7 empty] | 1699 | 320 | 1838630 | 2021-03-16 14:24 | 2021-03-16 15:26 | 62 | 11kV | 62 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210666 Broken Live Line Lead Excluded OMS 1838630 | March | 2021 | 2021Q3 | 2021 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2021-03-16 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 45.3078
[7 empty] | 3025 | 17023 | 1838708 | 2021-03-16 20:45 | 2021-03-17 00:05 | 200 | 11kV | 1400 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 11kV Feeder isolated for safety from LB44323 to Rec44605 tee PT12757 and PT13306 to clear tree branh on OH mains. Cause on interruption: Tree on OH mains during rain. See OMS1838709 for PT12757 outage. | March | 2021 | 2021Q3 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-03-16 | N | 200 | N | 3 | N | N | 1.1101 | 39.4971 | 1023.0787
[7 empty] | 2779 | 13594 | 1838719 | 2021-03-17 00:16 | 2021-03-17 07:10 | 414 | 11kV | 387689 | 2013 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.2 tripped on: A Phase Earth Fault Abnormal 1: S16618 Sw/B Closed with USL24947 Open (DMA) L/R switching: S17069 Sw/B Closed with S15960 Sw/A Open Abnormal 2:S16734 to S16559 tee pT15755 (DMA) S16559 Sw/B with Sw/A Closed UG cable fault between S16874 Sw/B & S15533 Sw/A tee S16058. Delayed restoration due to multiple DMAs and LV // failures. See 1839036 1839037 1839038 1839039 1838741 | March | 2021 | 2021Q3 | 2021 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | UG | Not Veg | 2021-03-17 | N | 192.5926 | N | 6 | N | N | 1.1101 | 39.4971 | 283311.6863
[7 empty] | 1923 | 3056 | 1838748 | 2021-03-17 05:14 | 2021-03-17 10:35 | 321 | 11kV | 9424 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210668 A & B Phase Fuse Saver No Fault Found Excluded OMS 1838748 | March | 2021 | 2021Q3 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-03-17 | N | 277.1765 | N | 6 | N | N | 1.1101 | 39.4971 | 6886.7812
[7 empty] | 2133 | 5474 | 1838811 | 2021-03-17 10:47 | 2021-03-17 12:31 | 104 | 11kV | 204528 | 2021 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | Zn14892 Charmhaven - Pnl.16 tripped, reclosed, tripped & locked out on (51N) 11kV UGOH ajd S14548 Sw/A failed explosively. See 1839022 1839023 | March | 2021 | 2021Q3 | 2021 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | Unknown | Unknown | 2021-03-17 | N | 101.2014 | N | 6 | N | N | 1.1101 | 39.4971 | 149463.0298
[7 empty] | 2161 | 5818 | 1838739 | 2021-03-17 02:20 | 2021-03-17 17:33 | 913 | 11kV | 336681 | 1258 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12660 Woy Woy - Pnl.14 tripped, reclosed & locked out on: Earth Fault UG cable fault between LB44221, LB43470 to S64363 Sw/A - UGOH broken away to isolate defective section. S64618 (DNA - Woy Woy Hospital, switched away after first failed restoration attempt) See 1839171 1839174 1839177 1839178 1839179 1839182 1839174 1839185 1839176 1839190 1839187 1839176 | March | 2021 | 2021Q3 | 2021 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | UG | Not Veg | 2021-03-17 | N | 267.632 | N | 6 | N | N | 1.1101 | 39.4971 | 246036.5444
[7 empty] | 1705 | 386 | 1838940 | 2021-03-17 17:35 | 2021-03-17 17:40 | 5 | 11kV | 175 | 35 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 210676 No protection operated, isolated to allow staff to make safe. | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-03-17 | N | 5 | N | 6 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 2929 | 15484 | 1838939 | 2021-03-17 17:06 | 2021-03-17 20:58 | 232 | 11kV | 35748 | 504 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 210677 3 phase Overcurrent Pole fire pole SI-91265 Excluded OMS 1838939 | March | 2021 | 2021Q3 | 2021 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2021-03-17 | N | 70.9286 | N | 6 | N | N | 1.1101 | 39.4971 | 26123.584
[7 empty] | 2332 | 7981 | 1838988 | 2021-03-18 00:38 | 2021-03-18 01:49 | 71 | 11kV | 88466 | 1246 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.24 tripped on A & C phase IOC Bat removed off OH mains outside 78 Potts St | March | 2021 | 2021Q3 | 2021 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2021-03-18 | N | 71 | N | 8 | N | N | 1.1101 | 39.4971 | 64648.3435
[7 empty] | 2790 | 13742 | 1838998 | 2021-03-18 05:45 | 2021-03-18 06:45 | 60 | 11kV | 120 | 2 | HV | Animal Other | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 210680 Rat on arrestor. Wrong sub in OMS Excluded OMS 1838998 | March | 2021 | 2021Q3 | 2021 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2021-03-18 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 3244 | 19747 | 1838997 | 2021-03-18 05:00 | 2021-03-18 09:14 | 254 | 11kV | 22256 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210679 2 Fault operation A & B Phases Overcurrent No cause found Excluded OMS 1838997 | March | 2021 | 2021Q3 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2021-03-18 | N | 236.766 | N | 8 | N | N | 1.1101 | 39.4971 | 16264.0284
[7 empty] | 2080 | 4969 | 1839120 | 2021-03-18 12:56 | 2021-03-18 16:27 | 211 | 11kV | 9844 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210683 1 fault operation A & B Phase Overcurrent 6 trip and recloses between 1053 and 1118 before reclose function was switched off. No cause found again. Excluded OMS 1839120 | March | 2021 | 2021Q3 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2021-03-18 | N | 104.7234 | N | 8 | N | N | 1.1101 | 39.4971 | 7193.7049
[7 empty] | 1840 | 2076 | 1839243 | 2021-03-18 15:29 | 2021-03-18 18:30 | 181 | 11kV | 2738 | 758 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn35370 Galston - Pnl.4 tripped & reclosed on: A & C phase O/C Lightning strike to PT2214 Mansfield End - Dist #1- A & B phase fuses blown See 1841091 1841092 | March | 2021 | 2021Q3 | 2021 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2021-03-18 | N | 3.6121 | N | 8 | N | N | 1.1101 | 39.4971 | 2000.8496
[7 empty] | 2839 | 14303 | 1839297 | 2021-03-18 18:52 | 2021-03-18 21:25 | 153 | 11kV | 11364 | 80 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210685 Customer LV fell on fence supplied by sub 50274. no protection operated but ausgrid did open 11kv Sw 79580 for safety. Excluded OMS 1839304 (OUTAGE) & 1839297 (HAZARD) | March | 2021 | 2021Q3 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2021-03-18 | N | 142.05 | N | 8 | N | N | 1.1101 | 39.4971 | 8304.476
[7 empty] | 3044 | 17254 | 1839358 | 2021-03-18 22:21 | 2021-03-19 00:36 | 135 | 11kV | 17808 | 212 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn12610 Long Jetty - Pnl.5 tripped, reclosed & locked out on IOC UG cable fault between S14747 Sw/B to S12805 Sw/3829 tee Tx3 @ S12805. Dop reports there is a hole in the top of No.3 RMI See 1841097 1841098 | March | 2021 | 2021Q3 | 2021 | ZN12610:PA5 | ZN12610:PA5 | ZN12610/000005 | CENTRAL COAST | UG | Not Veg | 2021-03-18 | N | 84 | N | 8 | N | N | 1.1101 | 39.4971 | 13013.5612
[7 empty] | 2527 | 10362 | 1839303 | 2021-03-18 18:50 | 2021-03-19 03:35 | 525 | 11kV | 206694 | 820 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210686 2 fault operations Overcurrent; Earth Fault tree onto mains pole JR-90367 , ABS 998 broken. targets 50TN. Excluded oms report no 1839305, 1839308, 1839307 | March | 2021 | 2021Q3 | 2021 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2021-03-18 | N | 252.0659 | N | 8 | N | N | 1.1101 | 39.4971 | 151045.8788
[7 empty] | 2091 | 5094 | 1839400 | 2021-03-19 10:00 | 2021-03-19 11:02 | 62 | 11kV | 1426 | 23 | HV | Arcing | Equipment Failure | Pole | Unplanned | Rain Heavy | N | LID 210689 Arcing pole GQ-71131 section isolated to replace damaged insulator. Excluded OMS 1839400, 1839487 | March | 2021 | 2021Q3 | 2021 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2021-03-19 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 1042.0787
[7 empty] | 3142 | 18659 | 1839396 | 2021-03-19 07:13 | 2021-03-19 11:40 | 267 | 11kV | 221350 | 2360 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn12570 Avoca - Pnl.39 tripped, reclosed, and locked out on: A & B phase OC Abnormal: LB44314 Closed with AB43862 Open (DMA) LB40423 closed with REC40425 Open (DMA) Tree branch on mains outside Avoca cinemas See 1841178 1841179 1841181 1841182 | March | 2021 | 2021Q3 | 2021 | ZN12570:PA39 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | OH | Veg | 2021-03-19 | N | 93.7924 | N | 8 | N | N | 1.1101 | 39.4971 | 161756.0513
[7 empty] | 1731 | 643 | 1839512 | 2021-03-19 10:15 | 2021-03-19 11:47 | 92 | 11kV | 108560 | 1180 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210691 Sensitive Earth Fault SECTION ISOLATED TO REMOVE TREE FROM MAINS ADJACENT SUB 54569. Excluded OMS1839512, 1839549, 1839526 | March | 2021 | 2021Q3 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2021-03-19 | N | 92 | N | 8 | N | N | 1.1101 | 39.4971 | 79332.446
[7 empty] | 3031 | 17083 | 1839386 | 2021-03-19 06:13 | 2021-03-19 13:16 | 423 | 11kV | 13536 | 32 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 210688 2 fault operations Overcurrent; Earth Fault Large tree brought down 11kv mains into LV mains and onto ground , section isolated for repairs. Targets 50TAB Excluded oms 1839835 | March | 2021 | 2021Q3 | 2021 | 265:81645 | 265:81645 | ZN00265/081645 | PORT STEPHENS | OH | Veg | 2021-03-19 | N | 423 | N | 8 | N | N | 1.1101 | 39.4971 | 9891.7096
[7 empty] | 3248 | 19775 | 1839554 | 2021-03-19 11:39 | 2021-03-19 15:00 | 201 | 11kV | 227015 | 1345 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Heavy | N | LID 210692 B & C Phases Overcurrent SW 33570 PROTN Bph 2600 amp, Cph 2500 amps. Switchgear burnt up East Cessnock Bowling Club sub 29596. Sub isolated for repairs. Customer has been placed in LV parrallel. Excluded OMS 1839560 | March | 2021 | 2021Q3 | 2021 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | UG | Not Veg | 2021-03-19 | N | 168.7844 | N | 8 | N | N | 1.1101 | 39.4971 | 165895.8662
[7 empty] | 3061 | 17476 | 1839511 | 2021-03-19 10:17 | 2021-03-19 16:40 | 383 | 11kV | 11831 | 32 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | USL751 - Interrupted by DOp for safety/ repair after tree on OH mains near PT1921 See 1841168 1841169 | March | 2021 | 2021Q3 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2021-03-19 | N | 369.7188 | N | 8 | N | N | 1.1101 | 39.4971 | 8645.7458
[7 empty] | 2506 | 10154 | 1839602 | 2021-03-19 16:33 | 2021-03-19 18:25 | 111.9167 | 11kV | 21823.75 | 195 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210694 Light Rain 11kV xarm burnt in half pole SW-90638 Customer advises, power pole outside property is on fire at top of pole and about a foot of the crossbar is dangling. Isolated section for repairs Refer to "OMS 1839602, 1839603, 1839663 | March | 2021 | 2021Q3 | 2021 | 223:14393 | 223:14393 | ZN00223/014393 | LAKE MACQUARIE | OH | Not Veg | 2021-03-19 | N | 111.9167 | N | 8 | N | N | 1.1101 | 39.4971 | 15948.1528
[7 empty] | 1866 | 2426 | 1839608 | 2021-03-19 14:18 | 2021-03-19 20:10 | 352 | 11kV | 7392 | 21 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 210695 Burnt off tapping pole GT-13002, SECTION ISOLATED FOR REPAIR. Excluded OMS 1839608 | March | 2021 | 2021Q3 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2021-03-19 | N | 352 | N | 8 | N | N | 1.1101 | 39.4971 | 5401.8556
[7 empty] | 2794 | 13798 | 1839752 | 2021-03-20 05:41 | 2021-03-20 07:38 | 117 | 11kV | 22581 | 193 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC50015 Quarry Old Norther - tripped & locked out on OC Tree on OH mains outside 11 Hemers Rd | March | 2021 | 2021Q3 | 2021 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2021-03-20 | Y | 117 | N | 4 | N | Y | 1.1101 | 39.4971 | 16501.5288
[7 empty] | 2889 | 14817 | 1839781 | 2021-03-20 07:25 | 2021-03-20 09:29 | 124 | 11kV | 222248 | 1802 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | Zn5868 Gore Hill - Pnl.30 tripped on Earth Fault UG cable fault between S6916 Sw/D and S6438 Sw/A to S8079 Sw/D See 1841160 1841161 | March | 2021 | 2021Q3 | 2021 | ZN5868:PA30 | ZN5868:PA30 | ZN05868/000030 | LANE COVE | UG | Not Veg | 2021-03-20 | N | 123.3341 | N | 4 | N | N | 1.1101 | 39.4971 | 162412.2832
[7 empty] | 1765 | 1157 | 1839730 | 2021-03-20 00:08 | 2021-03-20 10:44 | 636 | 11kV | 508548 | 820 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | Y | LID 210698 2 fault operations B & C Phases Overcurrent Broken crossarm Excluded OMS 1839730 | March | 2021 | 2021Q3 | 2021 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Not Veg | 2021-03-20 | Y | 620.1805 | N | 4 | N | Y | 1.1101 | 39.4971 | 371631.8788
[7 empty] | 2192 | 6167 | 1839817 | 2021-03-20 08:35 | 2021-03-20 11:25 | 170 | 11kV | 90950 | 535 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | Y | LID 210704 Heavy Rain interrupt to repair crossarm SW-90777 | March | 2021 | 2021Q3 | 2021 | 223:14393 | 223:14393 | ZN00223/014393 | LAKE MACQUARIE | OH | Not Veg | 2021-03-20 | N | 170 | N | 4 | N | N | 1.1101 | 39.4971 | 66463.5774
[7 empty] | 1815 | 1803 | 1839879 | 2021-03-20 09:34 | 2021-03-20 14:15 | 281 | 11kV | 20209 | 189 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | LID 210703 Earth Fault, Sensitive Earth Fault Hv Down OHM down at sub 1380 Excluded oms 1839884, 886, 893, 879 | March | 2021 | 2021Q3 | 2021 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2021-03-20 | Y | 106.9259 | N | 4 | N | Y | 1.1101 | 39.4971 | 14768.1411
[7 empty] | 2367 | 8434 | 1839984 | 2021-03-20 12:05 | 2021-03-20 14:52 | 167 | 11kV | 23297 | 148 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | At S167 Auburn Panel 12 Tripped on Relays: IOC B phase, EFIm Earth Fault Check Signals: 11kV Check Cause: 11kV UG fault between S7517-S6583 - S8296 Switching Tag left by DOp See OMS 1841146 1841148 1840252 | March | 2021 | 2021Q3 | 2021 | ZN167:PA12 | ZN167:PA12 | ZN00167/000012 | CUMBERLAND | UG | Not Veg | 2021-03-20 | N | 157.4122 | N | 4 | N | N | 1.1101 | 39.4971 | 17024.7605
[7 empty] | 2431 | 9324 | 1840101 | 2021-03-20 15:09 | 2021-03-20 16:45 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | Y | LID 210709 C Phase DOLF : 10 Amp Excluded OMS 1840101 | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-03-20 | N | 96 | N | 4 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 2770 | 13435 | 1840111 | 2021-03-20 15:23 | 2021-03-20 16:50 | 87 | 11kV | 58517 | 730 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | Y | Zn35370 Galston - Pnl.8 tripped on ABC phase OC Car hit pole outside 63 Arcadia Rd Galston See 1841244 1841245 | March | 2021 | 2021Q3 | 2021 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2021-03-20 | Y | 80.1603 | N | 4 | N | Y | 1.1101 | 39.4971 | 42762.4976
[7 empty] | 1726 | 622 | 1840134 | 2021-03-20 15:41 | 2021-03-20 17:02 | 81 | 11kV | 53703 | 663 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | Y | REC40407 The Scenic Bounty tripped, reclosed & tripped. Tree on OH mains outside 9 MacMaster Pde | March | 2021 | 2021Q3 | 2021 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2021-03-20 | Y | 81 | N | 4 | N | Y | 1.1101 | 39.4971 | 39244.5684
[7 empty] | 2411 | 9176 | 1839754 | 2021-03-20 05:58 | 2021-03-20 21:38 | 940 | 11kV | 147571 | 1765 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Heavy | Y | Zn1285 Greenacre Park - Pnl.27 tripped on: Pnl.27R A & C phase IOC & OC End box fault at S4585 Sw/B See 1841270 1841272 1841273 | March | 2021 | 2021Q3 | 2021 | ZN1285:PA27 | ZN1285:PA27 | ZN01285/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-03-20 | Y | 83.6096 | N | 4 | N | Y | 1.1101 | 39.4971 | 107840.5342
[7 empty] | 2148 | 5664 | 1839804 | 2021-03-20 08:06 | 2021-03-20 21:46 | 820 | 11kV | 1197419 | 2129 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn347 Sefton - Pnl.22 tripped on A Phase OC and IOC Abnormal: LB2105 Closed with S7472 Sw/A Open Mini tornado type event caused mutliple issues acrss Chester Hill OMS 1841733/734/735/736/738/739/740/743/744/747/778/780/781/783/787/788/791 1839804 184008 1840393 | March | 2021 | 2021Q3 | 2021 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-03-20 | Y | 562.4326 | N | 4 | N | Y | 1.1101 | 39.4971 | 875038.4873
[7 empty] | 3146 | 18744 | 1840380 | 2021-03-20 20:12 | 2021-03-21 00:54 | 282 | 11kV | 109478 | 405 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC50247 Blackett Faunce - tripped & Locked out Tree on mains near AB44624 See 1841268 1841269 | March | 2021 | 2021Q3 | 2021 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Veg | 2021-03-20 | Y | 270.316 | N | 4 | N | Y | 1.1101 | 39.4971 | 80003.2933
[7 empty] | 2004 | 3932 | 1840446 | 2021-03-20 22:25 | 2021-03-21 01:17 | 172 | 11kV | 193328 | 1124 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | Zn965 Pennant Hills - Pnl.4 tripped on: B Phase OC Front line UG cable fault from Pnl.4 to LB2929 | March | 2021 | 2021Q3 | 2021 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2021-03-20 | Y | 172 | N | 4 | N | Y | 1.1101 | 39.4971 | 141278.4002
[7 empty] | 2971 | 16279 | 1840221 | 2021-03-20 17:24 | 2021-03-21 10:00 | 996 | 11kV | 6372 | 525 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | LID 210715 LV Cct 71884/3 UGM fault. Excluded OMS 1840194 | March | 2021 | 2021Q3 | 2021 | 801:74117 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | UG | Not Veg | 2021-03-20 | Y | 12.1371 | N | 4 | N | Y | 1.1101 | 39.4971 | 4656.4697
[7 empty] | 2225 | 6652 | 1840682 | 2021-03-21 12:57 | 2021-03-21 13:12 | 15 | 11kV | 14487 | 1061 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At An12690 Berkeley Vale Panel 12 was interrupted for emergency rapeirs Cause: Tree on 11kV HV mains between CP43167 and LB40019 - pole on fire See OMS 1841108 1841109 1840822 1840617 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2021-03-21 | N | 13.6541 | N | 12 | N | N | 1.1101 | 39.4971 | 10586.6723
[7 empty] | 2123 | 5391 | 1840518 | 2021-03-21 07:03 | 2021-03-21 13:56 | 413 | 11kV | 201710 | 840 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 210716 Heavy Rain Phase B, Earth Fault OMS NO. 1840518, 1840563, 1840737 Tree brought down 11kV OHM adj. pole HW-80133. | March | 2021 | 2021Q3 | 2021 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2021-03-21 | N | 240.131 | N | 12 | N | N | 1.1101 | 39.4971 | 147403.7186
[7 empty] | 2372 | 8551 | 1840746 | 2021-03-21 11:17 | 2021-03-21 14:40 | 203 | 11kV | 203 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 210724 A Phase DOLF : 10 Amp Carrier also replaced Excluded oms 1840746 | March | 2021 | 2021Q3 | 2021 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2021-03-21 | N | 203 | N | 12 | N | N | 1.1101 | 39.4971 | 148.3464
[7 empty] | 1712 | 428 | 1840617 | 2021-03-21 09:37 | 2021-03-21 16:45 | 428 | 11kV | 294634 | 752 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Section of 11kV (Ex Berkeley Vale - Pa8) has a bond off at Pole BV1211 Cause: feeder isolated from LB41744 - Lk41114 - PT11972 See OMS 1841427 1841429 1840627 1840617 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA8 | ZN12690:PA8 | ZN12690/000008 | CENTRAL COAST | OH | Not Veg | 2021-03-21 | N | 391.8005 | N | 12 | N | N | 1.1101 | 39.4971 | 215309.837
[7 empty] | 3289 | 20418 | 1840443 | 2021-03-20 22:09 | 2021-03-21 17:12 | 1143 | 11kV | 43070 | 174 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | LID 210713 2 fault operations Large tree brough down 11kV OHM at pole MG-90022. Damage at poles MG-90019, MG-90023. Excluded OMS No. 1840443, 1840473, 1840474, 1840475 | March | 2021 | 2021Q3 | 2021 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2021-03-20 | Y | 247.5287 | N | 4 | N | Y | 1.1101 | 39.4971 | 31474.2857
[7 empty] | 2105 | 5227 | 1840694 | 2021-03-21 10:21 | 2021-03-21 18:44 | 503 | 11kV | 684190 | 1503 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S12650 Somersby ZOne 11kV Recloser CP44936 Bently Rd Tripped on Signals: E/F Trip, AUX Supply, Lockout Cause: UG cable fault from S48109 Narani Narooma 0.1 to S48108 Neewora 0.1 See OMS 18141343 18141338 18141335 18141332 1814331 1841339 1840694 | March | 2021 | 2021Q3 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | UG | Not Veg | 2021-03-21 | N | 455.2162 | N | 12 | N | N | 1.1101 | 39.4971 | 499985.8718
[7 empty] | 3138 | 18622 | 1840514 | 2021-03-21 06:47 | 2021-03-21 22:40 | 953 | 11kV | 1906 | 2 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Heavy | N | PT12006 Peats Ridge Euloo 0.4 - Footpath phase HDO blown Storm | March | 2021 | 2021Q3 | 2021 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2021-03-21 | N | 953 | N | 12 | N | N | 1.1101 | 39.4971 | 1392.8486
[7 empty] | 2918 | 15275 | 1840202 | 2021-03-20 17:09 | 2021-03-21 22:50 | 1781 | 11kV | 107125 | 429 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | Y | Ex Peats Ridge Pnl.1 - REC45189 Cooks Peats Ridge 0.5 - tripped, reclosed and locked out on: OC 11kV OH mains down between AB40602 to REC44945 near PT13482 Wise Ferry Oyster Note: AOP reports high into low on single dist PT13482. HV came doe down onto neutral. All SB's checked and no damage found off PT13482 See 1844005 1844006 1844007 844008 | March | 2021 | 2021Q3 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2021-03-20 | Y | 249.7086 | N | 4 | N | Y | 1.1101 | 39.4971 | 78283.7903
[7 empty] | 2093 | 5104 | 1840624 | 2021-03-21 09:33 | 2021-03-21 23:34 | 841 | 11kV | 613014 | 781 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn14143 Somersby - Pnl.17 trippedon: A & B Phase IOC Tree on 11kV mains & PT11619 Dist #1 Pnl.17 tripped during restoration @1853 due to burnt off bond at pole CA83. See 1841758 1841760 1741761 1841762 1841763 1841765 1841766 1841767 | March | 2021 | 2021Q3 | 2021 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2021-03-21 | N | 784.9091 | N | 12 | N | N | 1.1101 | 39.4971 | 447972.5503
[7 empty] | 2642 | 11607 | 1841020 | 2021-03-21 22:50 | 2021-03-22 00:16 | 86 | 11kV | 59426 | 691 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | ZN14144 Wamberal - Panel 10 tripped, reclosed and locked out. Relays A & B phase IOC, EFI and lockout. Tree branch found on rec 44059. Removed by DOp. | March | 2021 | 2021Q3 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-03-21 | N | 86 | N | 12 | N | N | 1.1101 | 39.4971 | 43426.768
[7 empty] | 1912 | 2928 | 1840499 | 2021-03-21 04:15 | 2021-03-22 02:20 | 1325 | 11kV | 26114 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC45026 Fountaindale - tripped & locked out on OC 66kV "88J" FDR tripped at the same time. Tree on 11kV & 66kV feeders See 1841725 1841729 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2021-03-21 | N | 244.0561 | N | 12 | N | N | 1.1101 | 39.4971 | 19083.341
[7 empty] | 2625 | 11370 | 1841078 | 2021-03-22 10:00 | 2021-03-22 12:20 | 140 | 11kV | 2380 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 22/03/21 10:00 second interruption on PT13410 to remove tree. Note: at 0629hrs ZN14891 Wyong 11kV Pa16 tripped an reclosed on: L/O, Timing, FC, A&B phase timed OC, EF, EFI. Cause: Tree came down and clashed OH mains. | March | 2021 | 2021Q3 | 2021 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Veg | 2021-03-22 | N | 140 | N | 8 | N | N | 1.1101 | 39.4971 | 1739.2338
[7 empty] | 3014 | 16829 | 1841306 | 2021-03-22 10:55 | 2021-03-22 13:15 | 140 | 11kV | 4844 | 45 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC44603 Footes Rd was interrupted for safety to remove tree resting on bare 11kV OH mains causing smoking wires. See 1841922 1841923 | March | 2021 | 2021Q3 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-03-22 | N | 107.6444 | N | 8 | N | N | 1.1101 | 39.4971 | 3539.8523
[7 empty] | 2481 | 9868 | 1841142 | 2021-03-22 14:27 | 2021-03-22 15:12 | 45 | 11kV | 14310 | 318 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 210731 Sw 62303 OPENED to interrupt 11kV to safely remove tree Excluded OMS 1841142 | March | 2021 | 2021Q3 | 2021 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Veg | 2021-03-22 | N | 45 | N | 8 | N | N | 1.1101 | 39.4971 | 10457.3259
[7 empty] | 1922 | 3051 | 1841324 | 2021-03-22 11:08 | 2021-03-22 16:41 | 333 | 11kV | 1151 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex Pnl.6 Killarney Zone - Burnt off Bond at USL22297. REC26228 Valley Rd opened at 1409 for repairs See 1841926 1841927 | March | 2021 | 2021Q3 | 2021 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Not Veg | 2021-03-22 | N | 287.75 | N | 8 | N | N | 1.1101 | 39.4971 | 841.1169
[7 empty] | 2031 | 4385 | 1841046 | 2021-03-22 01:23 | 2021-03-22 17:55 | 992 | 11kV | 105781 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC41020 Wattle Tree Rd Nth tripped on Earth Fault Tree brought down OH mains between LB45186 & LB45185, also bond burnt off near REC41020 See 1841862 1841864 1841865 | March | 2021 | 2021Q3 | 2021 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-03-22 | N | 936.115 | N | 8 | N | N | 1.1101 | 39.4971 | 77301.6348
[7 empty] | 2654 | 11784 | 1840676 | 2021-03-21 10:09 | 2021-03-22 18:00 | 1911 | 11kV | 19880 | 261 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | Rain Heavy | N | Ex Zn15013 Terrey Hills - REC1126 Mona Vale tripped on: SEF 11kV OH mains down beyond LB26246 to PT16698 & PT17147 Major land slide, 4 bays of OH down. Customer (Kimbiki Tip) restored via customer supplied generator evening of 22/3 per Ross Macintosh. Assumed time of 1800 11kV remains isolated See 1844214 1844215 | March | 2021 | 2021Q3 | 2021 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2021-03-21 | N | 76.1686 | N | 12 | N | N | 1.1101 | 39.4971 | 14527.7176
[7 empty] | 2245 | 6783 | 1841542 | 2021-03-22 16:26 | 2021-03-22 22:10 | 344 | 11kV | 165259 | 2038 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210735 2 fault operations 33kV pin insulator broke at pole JT-84715. 33kV OHM into 11kV Fdr 80775& onto LV RH Fdr 8280. See LID #210734 Targets required. Excluded OMS No. 1841542 | March | 2021 | 2021Q3 | 2021 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2021-03-22 | N | 81.0888 | N | 8 | N | N | 1.1101 | 39.4971 | 120766.4029
[7 empty] | 1929 | 3105 | 1841680 | 2021-03-23 04:23 | 2021-03-23 06:35 | 132 | 11kV | 8692 | 81 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn2466 Flemington - Pnl.11 tripped on: Earth Fault UG cable fault between Pnl.11, S5298 Sw/A, S5059 tee S2231 See 1841718 1841719 | March | 2021 | 2021Q3 | 2021 | ZN2466:PA11 | ZN2466:PA11 | ZN02466/000011 | STRATHFIELD | UG | Not Veg | 2021-03-23 | N | 107.3086 | N | 7 | N | N | 1.1101 | 39.4971 | 6351.8572
[7 empty] | 1907 | 2875 | 1841637 | 2021-03-22 20:02 | 2021-03-23 12:10 | 968 | 11kV | 223336 | 272 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC527 Catherine Paul tripped on: IOC & OC Abnormal: LB64433 Closed with LB2591 Open (DMA) Tree has taken down D/W and blocking road at pole PY21668 See 1842143 1842145 | March | 2021 | 2021Q3 | 2021 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2021-03-22 | N | 821.0882 | N | 8 | N | N | 1.1101 | 39.4971 | 163207.3615
[7 empty] | 2755 | 13224 | 1841881 | 2021-03-23 11:55 | 2021-03-23 12:35 | 40 | 11kV | 80 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 210741 B Phase DOLF : 10 Amp excluded OMS 1841881 | March | 2021 | 2021Q3 | 2021 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2021-03-23 | N | 40 | N | 7 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 1837 | 2054 | 1841964 | 2021-03-23 11:44 | 2021-03-23 14:09 | 145 | 11kV | 323120 | 2467 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn690 Campsie - Pnl.25 tripped on: C phase IOC & OC UG cable fault between Pnl.25, S1976 Sw/A, S3773 Sw/A and S3834 Sw/B | March | 2021 | 2021Q3 | 2021 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-03-23 | N | 130.9769 | N | 7 | N | N | 1.1101 | 39.4971 | 236126.5656
[7 empty] | 3271 | 20079 | 1840489 | 2021-03-21 02:25 | 2021-03-23 16:30 | 3725 | 11kV | 287497 | 78 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | CP45017 tripped on SEF during Rain/Wind/Storm. LW reported that HV down at PT14819. LW also reported HV open bond found at tee off to PT14778. | March | 2021 | 2021Q3 | 2021 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2021-03-21 | N | 3685.859 | N | 12 | N | N | 1.1101 | 39.4971 | 210094.3279
[7 empty] | 2871 | 14605 | 1841983 | 2021-03-23 14:15 | 2021-03-23 18:00 | 225 | 11kV | 90095 | 829 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Rain Wind Storm | N | Zn12570 Avoca - Pnl.41 - interrupted for safety due to arcing LB44425. Cross arm at LB44425 also broken See 1842441 1842442 1842444 | March | 2021 | 2021Q3 | 2021 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Not Veg | 2021-03-23 | N | 108.6791 | N | 7 | N | N | 1.1101 | 39.4971 | 65838.7686
[7 empty] | 3045 | 17255 | 1841996 | 2021-03-23 12:14 | 2021-03-23 22:10 | 596 | 11kV | 135520 | 692 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn14144 Wamberal - Pnl.10 tripped, reclosed & locked out. OH mains down near Brush Rd. See 1842418 1842419 | March | 2021 | 2021Q3 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2021-03-23 | N | 195.8382 | N | 7 | N | N | 1.1101 | 39.4971 | 99034.0188
[7 empty] | 2291 | 7394 | 1840581 | 2021-03-23 10:48 | 2021-03-23 23:30 | 762 | 11kV | 48536 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Previous Storm | N | REC44946 Kunurra Rd opened by Control Room for safety Tree on HV brining CCT within reach Between pole WL9568 and WL7281 PT18420 Oak Bluegum 0.6 - Dist #1 - Also Interrupted See 1842400 1842401 184202 | March | 2021 | 2021Q3 | 2021 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2021-03-23 | N | 292.3855 | N | 7 | N | N | 1.1101 | 39.4971 | 35468.6772
[7 empty] | 2235 | 6715 | 1840280 | 2021-03-20 18:14 | 2021-03-24 12:00 | 5386 | 11kV | 328368 | 78 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 210743 3 phase suggest an outage on Rec 42091 (no SCADA indication). Crews isolate faulty section beyond 11kV Lks 41580 on 23/03/21. Sw 42091 closed 1142. No access beyond Lks 41580 due to floodwaters. Excluded OMS jobs 1840280 & 1840669 | March | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-03-20 | Y | 4209.8462 | N | 4 | N | Y | 1.1101 | 39.4971 | 239961.6492
[7 empty] | 2558 | 10704 | 1842062 | 2021-03-23 17:34 | 2021-03-24 12:30 | 1136 | 11kV | 67039 | 109 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 210747 Overcurrent Tree on mains pole 5N-50036 Grading issue with Sw 74773 and Sw 82225. 74773 was on 1 shot.....ON 1 close of sw 74773. Sw 82225 triped and reclosed at 21.26. It didnt do it the other 2 times. Excluded oms 1842192 | March | 2021 | 2021Q3 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2021-03-23 | N | 615.0367 | Y | 7 | N | Y | 1.1101 | 39.4971 | 48990.1239
[7 empty] | 2570 | 10860 | 1842280 | 2021-03-24 05:06 | 2021-03-24 14:40 | 574 | 11kV | 81916 | 859 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210754 2 fault operations B & C Phase Overcurrent 50T BC tree on OHM pole JU 54963 DQ excluded OMS 1842280 ## | March | 2021 | 2021Q3 | 2021 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Veg | 2021-03-24 | N | 95.362 | N | 8 | N | N | 1.1101 | 39.4971 | 59861.7967
[7 empty] | 2955 | 15980 | 1840433 | 2021-03-20 21:32 | 2021-03-24 16:25 | 5453 | 11kV | 553834 | 206 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC349 Berowra Waters tripped on Earth Fault Tree brought down OH mains. Flooding delayed restoration See 1843784 1843785 | March | 2021 | 2021Q3 | 2021 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2021-03-20 | Y | 2688.5146 | N | 4 | N | Y | 1.1101 | 39.4971 | 404725.5519
[7 empty] | 3023 | 16988 | 1842547 | 2021-03-24 15:18 | 2021-03-24 17:11 | 113 | 11kV | 97858 | 866 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC62226 Connels Terry - tripped on OC Cause not ascertained | March | 2021 | 2021Q3 | 2021 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2021-03-24 | N | 113 | N | 8 | N | N | 1.1101 | 39.4971 | 71511.7401
[7 empty] | 3230 | 19649 | 1842394 | 2021-03-24 15:50 | 2021-03-24 18:20 | 150 | 11kV | 900 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT11131 George Downes Hall 0.5 interrupted from USL43383 Pole CM680 live to potential of 280V resulting from bare 11kV conductor resting on crossarm. Linecrew have arrived on site. Operator please attend to isolate feeder urgently. EmSO Jamie 0407907136 (access to pole CM680 through 136 Hallards Lane). | March | 2021 | 2021Q3 | 2021 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2021-03-24 | N | 150 | N | 8 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 2067 | 4824 | 1839755 | 2021-03-20 05:59 | 2021-03-24 18:30 | 6511 | 11kV | 584173 | 92 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | LID 210702 1 fault operation Sensitive Earth Fault 11kV on ground near pole DV-91764 Flooding caused lengthy delay in restoration Excluded OMS 1839755 | March | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-03-20 | Y | 6349.7065 | N | 4 | N | Y | 1.1101 | 39.4971 | 426896.3982
[7 empty] | 3182 | 19252 | 1842300 | 2021-03-24 07:33 | 2021-03-24 21:43 | 850 | 11kV | 43452 | 83 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC47878 Pacific Palmdale 0.5 tripped on Earth Fault tree brought down OH mains adjacent PT12237, bays of CCT between OU-28 and OU-34(6 bays) and damaged LV ABC also. Snapped pole OU-31. Replaced pole. Restrung and repaired all HV. New pin arms installed at OU-30 and OU-32. Both these poles have active termites in them. See 1842800 1842801 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2021-03-24 | N | 523.5181 | N | 8 | N | N | 1.1101 | 39.4971 | 31753.44
[7 empty] | 3260 | 19949 | 1842666 | 2021-03-25 04:04 | 2021-03-25 05:32 | 88 | 11kV | 94714 | 1423 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1193 Lindfield - Pnl.27 tripped on Earth Fault Abnormal: LB2834 Open (DMA) with S899 Sw/B closed UG cable fault between S899 Sw/B, LB2834 & LB210 See 18439535 1843936 1843937 | March | 2021 | 2021Q3 | 2021 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | UG | Not Veg | 2021-03-25 | N | 66.5594 | N | 3 | N | N | 1.1101 | 39.4971 | 69214.1976
[7 empty] | 2150 | 5678 | 1841696 | 2021-03-23 06:09 | 2021-03-25 08:47 | 3038 | 11kV | 160119 | 380 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REC47749 Palmtree Neera - tripped, reclosed & locked out on OC Tree brought HV & LV mains down near PT11227 Little Patonga No.2 (beyond LB41166 - water crossing) Note: PT11227 restored by Tcon using mobile generator, 25/03/2021 08:47 t43476: Customers on portable generators, 6 bays down boat access only. Based on customer calls and contact centre comments in OMS #1843660, restoration time was approx 15:19 29/3 See 1843951 1843953 1843955 1843956 | March | 2021 | 2021Q3 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2021-03-23 | N | 421.3658 | N | 7 | N | N | 1.1101 | 39.4971 | 117010.2425
[7 empty] | 1970 | 3609 | 1842602 | 2021-03-24 20:24 | 2021-03-25 12:30 | 966 | 11kV | 19320 | 20 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Flood | N | LID 210759 Tree blown into mains Excluded OMS 1842602 | March | 2021 | 2021Q3 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-03-24 | N | 966 | N | 8 | N | N | 1.1101 | 39.4971 | 14118.4862
[7 empty] | 2138 | 5505 | 1842393 | 2021-03-24 10:40 | 2021-03-25 12:45 | 1565 | 11kV | 117800 | 1027 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn9035 Caringbah - Pnl.2 tripped, reclosed, tripped & locked out on: A & C phase IOC Abnormal: S63370 Sw/B Closed, AB35376 Open, S9364 Sw/A Open 11kV end box fault @ S9342 Captain Crammond See 1843929 1843930 | March | 2021 | 2021Q3 | 2021 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | UG | Not Veg | 2021-03-24 | N | 114.703 | N | 8 | N | N | 1.1101 | 39.4971 | 86084.7655
[7 empty] | 2864 | 14473 | 1842372 | 2021-03-24 10:09 | 2021-03-25 14:00 | 1671 | 11kV | 144395 | 89 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 210750 2 fault operations Instantaneous Overcurrent; Earth Fault pole GQ-30005 on fire Excluded OMS 1842372 | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-03-24 | N | 1622.4157 | N | 8 | N | N | 1.1101 | 39.4971 | 105519.6071
[7 empty] | 2112 | 5285 | 1841972 | 2021-03-20 21:00 | 2021-03-25 15:20 | 6860 | 11kV | 61740 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | Y | Ex Wyonf Pnl.12 - Autolink 78535 Kiddman North Customer comments indicate outage since 2100 20/3/21 Restoration step for this device found in outage report for downstream issue @ 1520 25/3 Weather event NOTE: Yarramalong Rd closed due to flood water, unable to contact customer by phone, please re-issue 24/3 for another attempt for access once flood water recedes. all work on Wyong Pnl-12 was completed by Dops and Russell Glen on Thu 25/03. The Fdr was progressily re-energised as the work crew and dops worked their way along. All customers had supply by 1600 on Thu 25/03 | March | 2021 | 2021Q3 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2021-03-20 | Y | 6860 | N | 4 | N | Y | 1.1101 | 39.4971 | 45117.771
[7 empty] | 3197 | 19359 | 1842838 | 2021-03-25 12:57 | 2021-03-25 15:45 | 168 | 11kV | 2688 | 16 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 210763 overcurrent Mains of pins at poles 6F-70008 and 6F-70009. Excluded OMS 1842838 | March | 2021 | 2021Q3 | 2021 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2021-03-25 | N | 168 | N | 3 | N | N | 1.1101 | 39.4971 | 1964.3111
[7 empty] | 2895 | 14878 | 1835325 | 2021-03-20 19:17 | 2021-03-25 19:00 | 7183 | 11kV | 2359568 | 402 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | Y | Ex Pnl.12 Wyong Zn: 20/3 @ 1917 - CP46228 Aux supply fail alarm received - due to loss of phase from suspected Bond off 21/3 @ 0914 - REC50630 Yarramalong Chandler 0.1 - tripped & locked out Abnormal: REC48813 Bypass LB closed Suspected 11kv Bond off between PT14599 and REC40630 (Dop checked healthy volts at PT14599) - Interruption created beyond AB43930 Patrol required beyond REC50630. area cunable to be accessed due to widespread flooding See 1843983 1843984 1843985 1843986 1843987 1843988 1843989 | March | 2021 | 2021Q3 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2021-03-20 | Y | 5869.5721 | N | 4 | N | Y | 1.1101 | 39.4971 | 1724302.6989
[7 empty] | 2229 | 6667 | 1841750 | 2021-03-23 06:29 | 2021-03-25 19:10 | 3641 | 11kV | 239862 | 80 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 210762 Overcurrent 11kVMains on ground near sub 15390. Reported wires down, AG unable to access local isolation. For safety feeder isolated at nearest accessible upstream device. Note: Delay in restoration due to crews cannot access area due to flooded creek crossing (2 meter flood level indicator is underwater). Local RFS will notify Singleton crews when floodwater has subsided Excluded OMS 1841750 | March | 2021 | 2021Q3 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-03-23 | N | 2998.275 | Y | 7 | N | Y | 1.1101 | 39.4971 | 175284.0749
[7 empty] | 1842 | 2096 | 1842738 | 2021-03-25 09:53 | 2021-03-25 20:23 | 630.0833 | 11kV | 23313.0833 | 37 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N |  | March | 2021 | 2021Q3 | 2021 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2021-03-25 | N | 630.0833 | N | 3 | N | N | 1.1101 | 39.4971 | 17036.5137
[7 empty] | 2730 | 12743 | 1843002 | 2021-03-26 09:20 | 2021-03-26 11:30 | 130 | 11kV | 130 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210767 Single phase Broken LL lead. Exculded OMS 1843002 | March | 2021 | 2021Q3 | 2021 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-03-26 | N | 130 | N | 7 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 1791 | 1497 | 1842976 | 2021-03-26 07:55 | 2021-03-26 13:23 | 328 | 11kV | 25912 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Flood | N | LID 210766 3 fault operations Hunter River Flooded in the area. | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-03-26 | N | 328 | N | 7 | N | N | 1.1101 | 39.4971 | 18935.7253
[7 empty] | 2800 | 13861 | 1843015 | 2021-03-24 10:20 | 2021-03-26 14:10 | 3110 | 11kV | 18650 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Flood | N | LID 210768 11kV link 40875 Opened due to rising flood waters in Rose point Park. Singleton. LV was being inundated. Subs 49064 & 53174 energised today at 1405 & 1410. Sub 53504 to be energised at an undetermined time. Customers LV will need to be meggered before it is energised. Excluded OMS 1843015. | March | 2021 | 2021Q3 | 2021 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2021-03-24 | N | 3108.3333 | N | 8 | N | N | 1.1101 | 39.4971 | 13628.8699
[7 empty] | 3198 | 19379 | 1843029 | 2021-03-26 10:34 | 2021-03-26 15:15 | 281 | 11kV | 1967 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210769 C Phase DOLF : 40 Amp C phase DOLF blown, no cause found Excluded OMS 1843029 | March | 2021 | 2021Q3 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2021-03-26 | N | 281 | N | 7 | N | N | 1.1101 | 39.4971 | 1437.4256
[7 empty] | 2387 | 8728 | 1843106 | 2021-03-26 14:29 | 2021-03-26 18:55 | 266 | 11kV | 88578 | 333 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210771 Wire down at DP40143 Excluded OMS 1842106 | March | 2021 | 2021Q3 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2021-03-26 | N | 266 | N | 7 | N | N | 1.1101 | 39.4971 | 64730.1898
[7 empty] | 2223 | 6631 | 1843158 | 2021-03-26 17:15 | 2021-03-26 19:00 | 105 | 11kV | 315 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210772 B Phase DOLF : 10 Amp Excluded OMS 1843158 | March | 2021 | 2021Q3 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-03-26 | N | 105 | N | 7 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 1704 | 385 | 1843168 | 2021-03-26 17:22 | 2021-03-26 21:30 | 248 | 11kV | 122337 | 1570 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | ZN1285 Greenacre Park - Panel 24 has tripped on OC, IOC, EFI, Reclose & Lockout after Vehicle hit pole on cnr Wattle and Noble Ave Punchbowl. | March | 2021 | 2021Q3 | 2021 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-03-26 | N | 77.9217 | N | 7 | N | N | 1.1101 | 39.4971 | 89400.2713
[7 empty] | 3095 | 18076 | 1843194 | 2021-03-26 21:15 | 2021-03-26 22:50 | 95 | 11kV | 71210 | 758 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN5868 Gore Hill - 11kv FDR Panel 5 tripped on relays 5L B phase O/C, EFI, fault check. UG fault in section of 11kV fdr from S8474/B to S8156/A to S2379/A. | March | 2021 | 2021Q3 | 2021 | ZN5868:PA5 | ZN5868:PA5 | ZN05868/000005 | WILLOUGHBY | UG | Not Veg | 2021-03-26 | N | 93.9446 | N | 7 | N | N | 1.1101 | 39.4971 | 52038.1677
[7 empty] | 2629 | 11405 | 1843200 | 2021-03-27 06:53 | 2021-03-27 13:45 | 412 | 11kV | 412 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210781 DOLF : 6 Amp Excluded OMS 1843200 | March | 2021 | 2021Q3 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-03-27 | N | 412 | N | 3 | N | N | 1.1101 | 39.4971 | 301.0774
[7 empty] | 2058 | 4771 | 1843251 | 2021-03-27 13:08 | 2021-03-27 14:14 | 66 | 11kV | 53918 | 846 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 210783 3 fault operations A & B Phase Overcurrent UGM fault Excluded OMS 1843251 | March | 2021 | 2021Q3 | 2021 | 257:81994 | 257:81994 | ZN00257/081994 | NEWCASTLE | UG | Not Veg | 2021-03-27 | N | 63.7329 | N | 3 | N | N | 1.1101 | 39.4971 | 39401.6841
[7 empty] | 2899 | 14987 | 1841055 | 2021-03-22 03:52 | 2021-03-27 15:30 | 7898 | 11kV | 1534253 | 371 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC45189 Cooks Peats Ridge 0.55 tripped Abnormal: REC44945 Open with LB44077 Closed (see previous interruption to REC45189) OH mains down between AB43713 to LB40596. Delays in restoration due to rising flood waters since previous outage. See 1844025 1844026 1844027 1844028 1844029 1844030 1844031 1844032 1844033 | March | 2021 | 2021Q3 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-03-22 | N | 4135.4528 | N | 8 | N | N | 1.1101 | 39.4971 | 1121186.8396
[7 empty] | 2494 | 10067 | 1843297 | 2021-03-27 16:08 | 2021-03-27 17:33 | 85 | 11kV | 115830 | 1447 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | at ZN 1788 Matraville, 11kV Pnl 43 CB tripped on EF UG feeder fault from Sw.B @ s.36055 to Sw.A @ S.7118 to Sw.B @ S.1004 see also see 1843883 for restoration step | March | 2021 | 2021Q3 | 2021 | ZN1788:PA43 | ZN1788:PA43 | ZN01788/000043 | RANDWICK | UG | Not Veg | 2021-03-27 | N | 80.0484 | N | 3 | N | N | 1.1101 | 39.4971 | 84645.1476
[7 empty] | 2101 | 5201 | 1843344 | 2021-03-28 05:12 | 2021-03-28 06:19 | 67 | 11kV | 49532 | 792 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210786 Dead possum found on incoming side of Sw 19722 Kirrang Dr RAGCB. Targets: OCEF relay - 51B Excluded OMS No. 1843344 | March | 2021 | 2021Q3 | 2021 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2021-03-28 | N | 62.5404 | N | 6 | N | N | 1.1101 | 39.4971 | 36196.5247
[7 empty] | 2932 | 15493 | 1843361 | 2021-03-28 09:02 | 2021-03-28 14:05 | 303 | 11kV | 23873 | 79 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210788 3 fault operations 2 spans 11kV down between FP-60759 & FP60032. Dead birds below power line. Excluded OMS 1843361 | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-03-28 | N | 302.1899 | N | 6 | N | N | 1.1101 | 39.4971 | 17445.6843
[7 empty] | 3252 | 19801 | 1843343 | 2021-03-28 04:03 | 2021-03-28 14:55 | 652 | 11kV | 3140 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210787 B & C Phase DOLF's : 20 Amp No Fault found. Possibly birds off the flood waters. Excluded OMS 1843343 | March | 2021 | 2021Q3 | 2021 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2021-03-28 | N | 628 | N | 6 | N | N | 1.1101 | 39.4971 | 2294.6194
[7 empty] | 2880 | 14696 | 1843400 | 2021-03-28 14:54 | 2021-03-28 15:55 | 61 | 11kV | 6047 | 2027 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn12640 Umina - Pnl.13 tripped & reclosed on OC @ PT18022 Lcae Cowper - A & B Phase HDOs blown Abnormal: PT11227 still interrupted from LB41166 due to previous storm Bird caused flash over at PT18022 See 1843806 1843807 | March | 2021 | 2021Q3 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2021-03-28 | N | 2.9832 | N | 6 | N | N | 1.1101 | 39.4971 | 4418.9692
[7 empty] | 1817 | 1807 | 1843395 | 2021-03-28 14:23 | 2021-03-28 19:20 | 297 | 11kV | 82289 | 324 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210789 Removed stich from OHM pole GW-97060 Excluded OMS No. 1843395 | March | 2021 | 2021Q3 | 2021 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2021-03-28 | N | 253.9784 | N | 6 | N | N | 1.1101 | 39.4971 | 60134.3741
[7 empty] | 2283 | 7243 | 1843466 | 2021-03-29 00:04 | 2021-03-29 02:33 | 149 | 11kV | 257957 | 1908 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn180 Mosman - Pnl.21 tripped on Earth Fault UG cable fault in front line section of feeder between Pnl.21, S2989 Sw/A and S325 Sw/A | March | 2021 | 2021Q3 | 2021 | ZN180:PA21 | ZN180:PA21 | ZN00180/000021 | MOSMAN | UG | Not Veg | 2021-03-29 | N | 135.1976 | N | 4 | N | N | 1.1101 | 39.4971 | 188507.3672
[7 empty] | 2160 | 5817 | 1843426 | 2021-03-28 18:50 | 2021-03-29 04:42 | 592 | 11kV | 51410 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | REC44602 Ourimbah Creek Rd - Interrupted by AOp for safety @ 1850 Tree brought down multiple bays of CCT and snapped cross arm at pole OU-583 11kV isolated between AB44083 to LB47975 tee PT13164, PT13783 See 1843800 1843801 1843802 | March | 2021 | 2021Q3 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-03-28 | N | 485 | N | 6 | N | N | 1.1101 | 39.4971 | 37568.9117
[7 empty] | 3223 | 19618 | 1843670 | 2021-03-29 15:44 | 2021-03-29 17:10 | 86 | 11kV | 3134 | 66 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 210795 Private pole off sub 51457 fallen. Service to fallen pole had been disconnected at private T-off pole however due to fallen pole lowering OHM the disconnected service had made contact with live service. Crew cut away service & made safe. Fdr deenergised until crew arrived & isolated sub. Excluded OMS 1843659 | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | Unknown | Not Veg | 2021-03-29 | N | 47.4848 | N | 4 | N | N | 1.1101 | 39.4971 | 2290.2348
[7 empty] | 1696 | 247 | 1843698 | 2021-03-29 16:48 | 2021-03-29 18:30 | 102 | 11kV | 73161 | 871 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.17 tripped on B phase OC & Earth Fault Abnormal: LB2591 Open with LB64433 Closed HV UGOH at pole PY-37056 is visibly burnt. See 1843790 1843792 1843794 1843795 | March | 2021 | 2021Q3 | 2021 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | Unknown | Unknown | 2021-03-29 | N | 83.9966 | N | 4 | N | N | 1.1101 | 39.4971 | 53463.9009
[7 empty] | 1826 | 1882 | 1843708 | 2021-03-29 17:26 | 2021-03-29 18:33 | 67 | 11kV | 149812 | 2236 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.4 tripped, reclosed & locked out on: IOC Helium balloon into 11kV mains outside 5 Kemp St | March | 2021 | 2021Q3 | 2021 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Veg | 2021-03-29 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 109478.1909
[7 empty] | 2023 | 4194 | 1843778 | 2021-03-30 08:25 | 2021-03-30 09:33 | 68 | 11kV | 15232 | 224 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 210798 interupted to repair tapping on pole JU62093 Excluded OMS 1843778 | March | 2021 | 2021Q3 | 2021 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2021-03-30 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 11131.0963
[7 empty] | 3038 | 17214 | 1843791 | 2021-03-30 08:59 | 2021-03-30 09:43 | 44 | 11kV | 4708 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12690 Berkeley Vale Exiting panel 16 11kV Recloser CP45026 Fountaindale Tripped on Relays: OC Trip, Lockout Signals: CP45026 Trip - Lockout Cause: Branch on OH mains adjacent to USL43843 | March | 2021 | 2021Q3 | 2021 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2021-03-30 | N | 44 | N | 9 | N | N | 1.1101 | 39.4971 | 3440.4675
[7 empty] | 3160 | 18944 | 1843843 | 2021-03-30 10:04 | 2021-03-30 10:32 | 28 | 11kV | 28 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 210799 Customer advised DOLF blew energising 11kV up to a bore pump. | March | 2021 | 2021Q3 | 2021 |  |  |  | SINGLETON | Unknown | Not Veg | 2021-03-30 | N | 28 | N | 9 | N | N | 1.1101 | 39.4971 | 20.4616
[7 empty] | 2896 | 14880 | 1843751 | 2021-03-30 06:14 | 2021-03-30 13:00 | 406 | 11kV | 109902 | 1671 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT ZN12580 Erina Panel 10 tripoped on Relays: C phase IOC Signals 11kV Trip, CB10 Open Cause: 11kV OH down in Bebmoola Rd Greenpoint See OMS 1843949 1843950 1843783 1843765 NOTE: Inspections carried out for HV into LV (See OMS 1843765) no damage found | March | 2021 | 2021Q3 | 2021 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Not Veg | 2021-03-30 | N | 65.7702 | N | 9 | N | N | 1.1101 | 39.4971 | 80313.14
[7 empty] | 2419 | 9239 | 1843815 | 2021-03-30 14:10 | 2021-03-30 15:00 | 50 | 11kV | 100 | 2 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 210800 Single phase Isolated for safety & repair of service & LVF Excluded OMS 1843815 | March | 2021 | 2021Q3 | 2021 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | Unknown | Not Veg | 2021-03-30 | N | 50 | N | 9 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 2186 | 6107 | 1844004 | 2021-03-30 16:58 | 2021-03-30 19:03 | 125 | 11kV | 173256 | 1699 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | ZN35800 Bankstown 11kV Panel 22 - Tripped on Relays A,B & C phase IOC. Cause: End box fault. SW/B end box at S6407 Eva Bonds. | March | 2021 | 2021Q3 | 2021 | ZN35800:PA22 | ZN35800:PA22 | ZN35800/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-03-30 | N | 101.9753 | N | 9 | N | N | 1.1101 | 39.4971 | 126610.3746
[7 empty] | 1853 | 2264 | 1844016 | 2021-03-30 20:15 | 2021-03-30 21:50 | 95 | 11kV | 1805 | 19 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210802 interupted to repair main off pin pole HV20226 DQ Excluded OMS 1844016 | March | 2021 | 2021Q3 | 2021 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2021-03-30 | N | 95 | N | 9 | N | N | 1.1101 | 39.4971 | 1319.0408
[7 empty] | 2483 | 9884 | 1844050 | 2021-03-30 19:30 | 2021-03-31 00:35 | 305 | 11kV | 98618 | 903 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN2835 Burwood 11kV FDR Panel 24 - Tripped on realy B phase overcurrent with fault check. Cable fault located between S8461, S3552 tee S5817 (S5817 Dist.2 in LV // and Dist.1 & Dist.3 interrupted). | March | 2021 | 2021Q3 | 2021 | ZN2835:PA24 | ZN2835:PA24 | ZN02835/000024 | CANADA BAY | UG | Not Veg | 2021-03-30 | N | 109.2115 | N | 9 | N | N | 1.1101 | 39.4971 | 72067.1257
[7 empty] | 2199 | 6267 | 1844084 | 2021-03-30 23:52 | 2021-03-31 00:52 | 60 | 11kV | 104220 | 1737 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Recloser 41873 tripped on O/C (Recloser 47817 also tripped on E/F). Cause: Possum found burnt across CB insulators at Recloser 47817. | March | 2021 | 2021Q3 | 2021 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2021-03-30 | N | 60 | N | 9 | N | N | 1.1101 | 39.4971 | 76160.902
[7 empty] | 3053 | 17380 | 1844092 | 2021-03-31 06:07 | 2021-03-31 07:48 | 101 | 11kV | 86276 | 1276 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn15005 Belrose - Pnl.6 tripped & reclosed on: OC & EF REC24831 Lockwood Peacock tripped on IOC & OC at the same time Cause not ascertained See 1844419 1844420 | March | 2021 | 2021Q3 | 2021 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Veg | 2021-03-31 | N | 67.6144 | N | 4 | N | N | 1.1101 | 39.4971 | 63047.9561
[7 empty] | 2342 | 8133 | 1844147 | 2021-03-31 09:21 | 2021-03-31 11:37 | 136 | 11kV | 38689 | 301 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14144 Wamberal - Pnl.5 tripped, reclosed & locked out on: B Phase OC Cause not ascertained See 1844414 1844415 1844416 | March | 2021 | 2021Q3 | 2021 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2021-03-31 | N | 128.5349 | N | 4 | N | N | 1.1101 | 39.4971 | 28272.7801
[7 empty] | 2846 | 14344 | 1844194 | 2021-03-31 11:15 | 2021-03-31 14:10 | 175 | 11kV | 875 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210807 Burnt connection bottom of dolf, no fuse blew. OMS job in singleton queueu not sent to the Control Room. Excluded oms 1844194 | March | 2021 | 2021Q3 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-03-31 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 639.4242
[7 empty] | 1882 | 2584 | 1844274 | 2021-03-31 16:25 | 2021-03-31 17:34 | 69 | 11kV | 62238 | 902 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 210808 2 fault operations Earth Fault HV cable fault between sw 12213 and sw 29752. Excluded OMS 1844274. | March | 2021 | 2021Q3 | 2021 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | UG | Not Veg | 2021-03-31 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 45481.6947
[7 empty] | 2928 | 15482 | 1844526 | 2021-04-02 03:50 | 2021-04-02 04:57 | 67 | 11kV | 47823 | 740 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn630 Mascot - Pnl.24 tripped on Earth Fault UG cable fault between S64258 Sw/B and S7937 Sw/A See 1845596 1845597 | April | 2021 | 2021Q4 | 2021 | ZN630:PA24 | ZN630:PA24 | ZN00630/000024 | SYDNEY | UG | Not Veg | 2021-04-02 | N | 64.6257 | N | 5 | N | N | 1.1101 | 39.4971 | 34947.6379
[7 empty] | 1861 | 2354 | 1844553 | 2021-04-02 09:39 | 2021-04-02 11:05 | 86 | 11kV | 86 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210813 C Phase DOLF : 10 Amp Excluded OMS 1844553 | April | 2021 | 2021Q4 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-04-02 | N | 86 | N | 5 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 2406 | 9104 | 1844590 | 2021-04-02 15:03 | 2021-04-02 16:25 | 82 | 11kV | 7544 | 92 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC47746 patonga Meroo tripped on : OC Sail boat hit 11kV OH mains. CC1: 22-"Refer to SOp" | April | 2021 | 2021Q4 | 2021 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2021-04-02 | N | 82 | N | 5 | N | N | 1.1101 | 39.4971 | 5512.9327
[7 empty] | 3213 | 19520 | 1844603 | 2021-04-02 19:01 | 2021-04-03 00:45 | 344 | 11kV | 6987 | 92 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210815 Single phase CCT OHM off insulator pole EV-91781 11kV OHM on ground near sub 6158 OHM (CCT) off insulator pole EV-91781 Excluded OMS 1844603 | April | 2021 | 2021Q4 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-04-02 | N | 75.9457 | N | 5 | N | N | 1.1101 | 39.4971 | 5105.8935
[7 empty] | 2989 | 16521 | 1844615 | 2021-04-02 20:48 | 2021-04-03 02:00 | 312 | 11kV | 148608 | 2009 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | 11kV USL41908 was HR on roadside phase. Whilst DOp was opened the middle phase, insulators fell apart and feeders either side had to be de-energised for safety Pnl.34 Avoca and REC44855 lake Tramway both opened at 2048 Abnormal: AB40076 Closed with USL41908 Open, AB44314 Closed with AB43862 Open, AB40423 closed with REC40425 Open (DMAs) See 1845625 1845626 1845627 1845628 1845630 | April | 2021 | 2021Q4 | 2021 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2021-04-02 | N | 73.9711 | N | 5 | N | N | 1.1101 | 39.4971 | 108598.3432
[7 empty] | 2280 | 7209 | 1844723 | 2021-04-03 16:07 | 2021-04-03 16:38 | 31 | 11kV | 38378 | 1238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn1673 Turramurra Pnl.7 tripped on C Phase IOC Abnormal: LB203 closed with iR63174 Open (DMA) Tree on OH mains outside 29 Morris Ave Turramurra | April | 2021 | 2021Q4 | 2021 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Veg | 2021-04-03 | N | 31 | N | 2 | N | N | 1.1101 | 39.4971 | 28045.5104
[7 empty] | 2250 | 6832 | 1844744 | 2021-04-03 21:08 | 2021-04-03 22:46 | 98 | 11kV | 120270 | 1302 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12650 West Gosford - Pnl.6 tripped on Earth Fault EFI @ UGOH near S13071 defective, unable to reset,unable to determine if down down due defective or failure UG cable fault between LB40300 to S14851 Sw/A to S13071 Sw/A See 1845537 1845539 | April | 2021 | 2021Q4 | 2021 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | UG | Not Veg | 2021-04-03 | N | 92.3733 | N | 2 | N | N | 1.1101 | 39.4971 | 87889.7686
[7 empty] | 2211 | 6391 | 1844797 | 2021-04-04 17:11 | 2021-04-04 19:06 | 115 | 11kV | 71665 | 1442 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.9 tripped on Earth Fault While attempting restoration, pnl.10 tripped twice due to inconclusive EFIs UG cable fault between S35874 Sw/B and S2006 Sw/A See 1845569 1845570 1845573 1845574 | April | 2021 | 2021Q4 | 2021 | ZN398:PA9 | ZN398:PA9 | ZN00398/000009 | INNER WEST | UG | Not Veg | 2021-04-04 | N | 49.6983 | N | 2 | N | N | 1.1101 | 39.4971 | 52370.6682
[7 empty] | 2559 | 10705 | 1844793 | 2021-04-04 16:21 | 2021-04-04 19:18 | 177 | 11kV | 3949 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210818 3 fault operation B & C Phases Overcurrent Fault current: B phase - 437A, C phase - 434A Excluded OMS No. 1844793 | April | 2021 | 2021Q4 | 2021 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Veg | 2021-04-04 | N | 164.5417 | N | 2 | N | N | 1.1101 | 39.4971 | 2885.8127
[7 empty] | 2458 | 9533 | 1844926 | 2021-04-05 20:49 | 2021-04-05 23:00 | 131 | 11kV | 131 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 210825 3 phase HV Fuse : 31 Amp no oil in sight glass Excluded OMS 1844926 | April | 2021 | 2021Q4 | 2021 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2021-04-05 | N | 131 | N | 1 | N | N | 1.1101 | 39.4971 | 95.7309
[7 empty] | 3147 | 18754 | 1845047 | 2021-04-06 11:19 | 2021-04-06 12:15 | 56 | 11kV | 56 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210828 B Phase DOLF : 10 Amp Excluded OMS 1845047 | April | 2021 | 2021Q4 | 2021 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2021-04-06 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 2771 | 13453 | 1840546 | 2021-03-21 07:46 | 2021-04-06 12:44 | 23338 | 11kV | 47270 | 160 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REC45071 tripped, reclosed & locked out on OC Tree brought down OH mains during major rain storm. Bonds broken from Pole CM487 to PT12308. Customer advised no access long outage. See 1845498 1845500 1845501 | March | 2021 | 2021Q3 | 2021 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2021-03-21 | N | 295.4375 | N | 12 | N | N | 1.1101 | 39.4971 | 34543.5218
[7 empty] | 2674 | 12038 | 1845131 | 2021-04-06 16:55 | 2021-04-06 17:35 | 40 | 11kV | 9520 | 238 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Bond | Unplanned | No Weather Impact | N | LID 210830 NAR 72506 Outage to break taps to damaged sub 24707. Excluded OMS 1845131 1845132 1845133 | April | 2021 | 2021Q4 | 2021 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2021-04-06 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 6956.9352
[7 empty] | 3020 | 16954 | 1845167 | 2021-04-06 22:12 | 2021-04-07 01:35 | 203 | 11kV | 21518 | 106 | HV | Overload LV Parallel | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | @ CP342 Redan Raglan - Middle and Right side phase fuses blown Section of 11kV from S35371 Sw/B, S2404 Sw/A, tee CP342 and S5737 found in LV // which caused the fuses to operate See 1845170 1845227 | April | 2021 | 2021Q4 | 2021 | ZN180:PA10 | ZN180:PA10 | ZN00180/000010 | MOSMAN | Unknown | Not Veg | 2021-04-06 | N | 203 | N | 4 | N | N | 1.1101 | 39.4971 | 15724.7197
[7 empty] | 2542 | 10560 | 1845154 | 2021-04-06 19:57 | 2021-04-07 06:40 | 643 | 11kV | 78071 | 901 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.24 tripped on Earth Fault UG cable fault between S.8461 Sw/B, S3552 Sw/A tee S5817 Bennett Par S2585 Gipps Loftus - Dist #2 - In LV // See 1845514 1845515 1845516 1845517 1845518 1845159 | April | 2021 | 2021Q4 | 2021 | ZN2835:PA24 | ZN2835:PA24 | ZN02835/000024 | CANADA BAY | UG | Not Veg | 2021-04-06 | N | 86.6493 | N | 4 | N | N | 1.1101 | 39.4971 | 57051.9841
[7 empty] | 3286 | 20336 | 1845180 | 2021-04-07 06:06 | 2021-04-07 11:15 | 309 | 11kV | 14832 | 48 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | CP46914 Old Pittwater Cross - A & C phase HV fuses blown Tree on 11kV OH mains adjacent to CP46914. Removed by DOp | April | 2021 | 2021Q4 | 2021 | ZN15001:PA11 | ZN15001:PA11 | ZN15001/000011 | NORTHERN BEACHES | OH | Veg | 2021-04-07 | N | 309 | N | 9 | N | N | 1.1101 | 39.4971 | 10838.7881
[7 empty] | 2500 | 10114 | 1845248 | 2021-04-07 10:43 | 2021-04-07 11:58 | 75 | 11kV | 14025 | 187 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4853 Strahtfield South - Pnl.8 tripped on: OC & EF UG cable fault between Pnl.8 and S3861 Sw/A | April | 2021 | 2021Q4 | 2021 | ZN4853:PA8 | ZN4853:PA8 | ZN04853/000008 | STRATHFIELD | UG | Not Veg | 2021-04-07 | N | 75 | N | 9 | N | N | 1.1101 | 39.4971 | 10249.0563
[7 empty] | 3099 | 18128 | 1845499 | 2021-04-07 10:05 | 2021-04-07 12:35 | 150 | 11kV | 450 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 210846 Broken x arm on pole MD-20163, section isolated for repair. | April | 2021 | 2021Q4 | 2021 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2021-04-07 | N | 150 | N | 9 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 2275 | 7160 | 1845338 | 2021-04-07 15:30 | 2021-04-07 16:55 | 85 | 11kV | 20230 | 238 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 210845 NAR 73506. Interrupted to restore failed TX at 24707. See also LID 210830 Excluded OMS 1845338. | April | 2021 | 2021Q4 | 2021 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2021-04-07 | N | 85 | N | 9 | N | N | 1.1101 | 39.4971 | 14783.4873
[7 empty] | 2011 | 4070 | 1845356 | 2021-04-07 16:42 | 2021-04-07 17:03 | 21 | 11kV | 14700 | 700 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | iR62731 Narra Creek Manns - tripped on OC Bird on mains | April | 2021 | 2021Q4 | 2021 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2021-04-07 | N | 21 | N | 9 | N | N | 1.1101 | 39.4971 | 10742.3264
[7 empty] | 3165 | 19034 | 1845348 | 2021-04-07 16:02 | 2021-04-07 17:10 | 68 | 11kV | 272 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 210843 Single phase DOLF : 10 Amp Excluded OMS 1845348 Note: customers also affected by T&R event @ 07/04/2021 16:56, see OMS 1845493 | April | 2021 | 2021Q4 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-04-07 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 3264 | 19994 | 1845352 | 2021-04-07 16:32 | 2021-04-07 17:55 | 83.0667 | 11kV | 14702.8 | 177 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT61317 Ridge Barrenjoey - Centre phase HDO blown Possible lightning strike | April | 2021 | 2021Q4 | 2021 | ZN12640:PA12 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Not Veg | 2021-04-07 | N | 83.0667 | N | 9 | N | N | 1.1101 | 39.4971 | 10744.3726
[7 empty] | 2036 | 4480 | 1845365 | 2021-04-07 16:58 | 2021-04-07 18:20 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210848 C Phase DOLF : 10 Amp Excluded OMS 1845365 | April | 2021 | 2021Q4 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2021-04-07 | N | 82 | N | 9 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 3262 | 19976 | 1845357 | 2021-04-07 16:51 | 2021-04-07 18:50 | 119 | 11kV | 357 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210849 A Phase DOLF : 10 Amp Excluded OMS 1845357 | April | 2021 | 2021Q4 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2021-04-07 | N | 119 | N | 9 | N | N | 1.1101 | 39.4971 | 260.8851
[7 empty] | 1787 | 1473 | 1845428 | 2021-04-08 02:26 | 2021-04-08 04:15 | 109 | 11kV | 68336 | 884 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn2835 Burwood - Pnl.24 tripped on: Earth Fault UG cable fault between S8461 Sw/B, S3552 Sw/A tee S8517 S8517 restored via LV // See 1845456 1845457 1845458 | April | 2021 | 2021Q4 | 2021 | ZN2835:PA24 | ZN2835:PA24 | ZN02835/000024 | CANADA BAY | UG | Not Veg | 2021-04-08 | N | 77.3032 | N | 2 | N | N | 1.1101 | 39.4971 | 49937.9332
[7 empty] | 2142 | 5583 | 1845614 | 2021-04-08 14:18 | 2021-04-08 17:13 | 175 | 11kV | 124372 | 866 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC62226 Connells Terry - tripped on OC & SEF Cause not ascertained. See 1845791 / 92 / 93 / 94 / 95 / 96 | April | 2021 | 2021Q4 | 2021 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2021-04-08 | N | 143.6166 | N | 2 | N | N | 1.1101 | 39.4971 | 90887.3892
[7 empty] | 2466 | 9575 | 1845715 | 2021-04-09 12:40 | 2021-04-09 13:20 | 40 | 11kV | 7520 | 188 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210856 Section isolated to remove debris at IU-40514 Excluded OMS 1845715 1845775 | April | 2021 | 2021Q4 | 2021 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2021-04-09 | N | 40 | N | 2 | N | N | 1.1101 | 39.4971 | 5495.3942
[7 empty] | 2590 | 11138 | 1845742 | 2021-04-09 10:58 | 2021-04-09 16:55 | 357 | 11kV | 14394 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12630 Peats Ridge section of panel 1 from CP44945 Lower Mangrove Tripped Cause: Broken Cross arm near link LK44097 OH down See OMS1846290 1846291 1845742 1845846 | April | 2021 | 2021Q4 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2021-04-09 | N | 248.1724 | N | 2 | N | N | 1.1101 | 39.4971 | 10518.7106
[7 empty] | 2241 | 6753 | 1845890 | 2021-04-10 08:16 | 2021-04-10 13:13 | 297 | 11kV | 1188 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At Zn 12690 Berkely Vale Exiting Panel 26R labelled wyong Rd PT12862 Fowler Pacific - 11kV HDO fuse fatigue See OMS 1846756 1845890 | April | 2021 | 2021Q4 | 2021 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2021-04-10 | N | 297 | N | 3 | N | N | 1.1101 | 39.4971 | 868.1554
[7 empty] | 3171 | 19114 | 1845973 | 2021-04-10 20:53 | 2021-04-10 22:16 | 83 | 11kV | 199944 | 2644 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Panel 14 tripped on Relays: IOC, Earth Fault, Fault Check. Signals:11KV Trip, TX3 group earth, Zone Earth Cause: SW/B Closed @ S1886, SW/A Open @ S2379 Cause: UG fault - S5868 Gore Hill 11kV UG fault from S5649 to S804 to S4458 to S3231 See OMS 1846295 1846297 1845973 1845974 | April | 2021 | 2021Q4 | 2021 | ZN5868:PA14 | ZN5868:PA14 | ZN05868/000014 | WILLOUGHBY | UG | Not Veg | 2021-04-10 | N | 75.6218 | N | 3 | N | N | 1.1101 | 39.4971 | 146113.1779
[7 empty] | 2554 | 10639 | 1845992 | 2021-04-11 00:19 | 2021-04-11 02:00 | 101 | 11kV | 606 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210866 A Phase DOLF : 10 Amp Excluded OMS 1845992 | April | 2021 | 2021Q4 | 2021 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2021-04-11 | N | 101 | N | 2 | N | N | 1.1101 | 39.4971 | 442.8469
[7 empty] | 2802 | 13863 | 1845995 | 2021-04-10 23:46 | 2021-04-11 08:00 | 494 | 11kV | 988 | 2 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210867 Single phase DOLF : 10 Amp J Fraser advised possum was the cause. 10A sub DOLF Excluded OMS 1845995 note: time updated to first NS call received refer to OMS 1845990 | April | 2021 | 2021Q4 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-04-10 | N | 494 | N | 3 | N | N | 1.1101 | 39.4971 | 722.0013
[7 empty] | 2917 | 15246 | 1846079 | 2021-04-11 18:53 | 2021-04-11 19:53 | 60 | 11kV | 35580 | 593 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN10994 Mortdale Panel 7 Recloser CP62226 Connells Terry tripped on O/C and SEF and Lockout Abnormal Switching: LB31014 Open and AB39353 is Open with S10156 DOp Chicco patrolled feeder - No canse found for sef trip See OMS 1846774 1846079 | April | 2021 | 2021Q4 | 2021 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2021-04-11 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 26000.8146
[7 empty] | 2146 | 5661 | 1846149 | 2021-04-12 09:55 | 2021-04-12 18:30 | 515 | 11kV | 33990 | 66 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | At S7948 Forbes Bourke 75A fuse was found to have operated Cause: Truck reversed into S7948 | April | 2021 | 2021Q4 | 2021 | ZN931:PA26 | ZN931:PA26 | ZN00931/000026 | SYDNEY | Unknown | Not Veg | 2021-04-12 | N | 515 | N | 2 | N | N | 1.1101 | 39.4971 | 24838.8895
[7 empty] | 2669 | 11983 | 1846296 | 2021-04-12 16:17 | 2021-04-12 23:20 | 423 | 11kV | 72699 | 473 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | 11Kv CP59684 Brisbane Water Lara Tripped reclosed and locked out Section of 11kV feeder panel 10 Cause: Vehcile hit pole 36 Brisbane Water drive. HV and LV down mains onsite carry out repairs MVA pole WW5916 broken 11KV xarm centre phase down, PT18773-D2, MSB's checked in vicintiy (No32/34/36/38/40) & at LV // - no damage, no protection operated, earthing & metering found in order, advised supervisor & AOp supply can be restored when work complete. See OMS 1846899 1846900 1846901 | April | 2021 | 2021Q4 | 2021 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Not Veg | 2021-04-12 | N | 153.6977 | N | 2 | N | N | 1.1101 | 39.4971 | 53126.2849
[7 empty] | 3247 | 19767 | 1846470 | 2021-04-13 14:08 | 2021-04-13 15:42 | 94 | 11kV | 232237 | 2643 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | The 11kV Panel 21 CB tripped on Signals: 11kV Trip, TX4 Group Earth Relays: B phase OC, E/F and EFI Filed EFI's NIL Cause: Contractor hit the 11kV Cable with and excavator outside 175 Glenmore Rd Paddington See OMS 1846881 1846470 | April | 2021 | 2021Q4 | 2021 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2021-04-13 | N | 87.8687 | N | 3 | N | N | 1.1101 | 39.4971 | 169711.9498
[7 empty] | 2104 | 5224 | 1846469 | 2021-04-13 15:11 | 2021-04-13 17:40 | 149 | 11kV | 5545 | 100 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210873 Tree on mains pole EU-51524 SW 42062 opened for safety, section isolated for abs 49128 repair and tree removal. Excluded oms 1846469, 1846510 | April | 2021 | 2021Q4 | 2021 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2021-04-13 | N | 55.45 | N | 3 | N | N | 1.1101 | 39.4971 | 4052.1225
[7 empty] | 1697 | 260 | 1846543 | 2021-04-14 06:00 | 2021-04-14 07:45 | 105 | 11kV | 735 | 7 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210875 B & C Phase DOLF : 10 Amp Excluded OMS 1846543 | April | 2021 | 2021Q4 | 2021 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2021-04-14 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 537.1163
[7 empty] | 2227 | 6660 | 1846536 | 2021-04-13 20:56 | 2021-04-14 12:20 | 924 | 11kV | 2772 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210877 B Phase DOLF : 10 Amp Excluded OMS 1846536 | April | 2021 | 2021Q4 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-04-13 | N | 924 | N | 3 | N | N | 1.1101 | 39.4971 | 2025.6958
[7 empty] | 1998 | 3799 | 1846751 | 2021-04-15 05:08 | 2021-04-15 06:16 | 68 | 11kV | 37866 | 560 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S35900 Potts Hill - 11kv Panel 25 tripped on earth fault, EFI Section of fdr defective from Pa7 Sefton to S35085 Betty Grevillia. | April | 2021 | 2021Q4 | 2021 | ZN35900:PA25 | ZN3472:PA7 | ZN03472/000007 | CUMBERLAND | UG | Not Veg | 2021-04-15 | N | 67.6179 | N | 7 | N | N | 1.1101 | 39.4971 | 27671.3559
[7 empty] | 2726 | 12708 | 1846792 | 2021-04-15 09:48 | 2021-04-15 13:50 | 242 | 11kV | 726 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210884 A Phase DOLF : 10 Amp Excluded OMS 1846792 | April | 2021 | 2021Q4 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2021-04-15 | N | 242 | N | 7 | N | N | 1.1101 | 39.4971 | 530.5394
[7 empty] | 2914 | 15190 | 1846848 | 2021-04-15 13:37 | 2021-04-15 14:27 | 50 | 11kV | 19823 | 401 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210880 Tree branch on mains at pole JQ-77091 Excluded OMS 1846848/6864/6875 | April | 2021 | 2021Q4 | 2021 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2021-04-15 | N | 49.4339 | N | 7 | N | N | 1.1101 | 39.4971 | 14486.0637
[7 empty] | 2695 | 12308 | 1846675 | 2021-04-14 14:15 | 2021-04-15 15:00 | 1485 | 11kV | 134606 | 416 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | ZN9550 Gwawley Bay - Panel 11 (11kV) tripped on (all relays had self reset by the time DOp arrived). 11kv end box at S9896 failed explosively. Feeder was restored at 15:17 from panel 11 but found to be only alive on 2 HV phases. Panel 11 was then opened again at 18:03 to safely isolate second faulty section of feeder. Restoration time at S9896 confirmed by DNMS to be 15:28 | April | 2021 | 2021Q4 | 2021 | ZN9550:PA11 | ZN9550:PA11 | ZN09550/000011 | SUTHERLAND | UG | Not Veg | 2021-04-14 | N | 323.5721 | N | 2 | N | N | 1.1101 | 39.4971 | 98366.0946
[7 empty] | 3270 | 20078 | 1846802 | 2021-04-15 10:24 | 2021-04-15 15:10 | 286 | 11kV | 2232 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1290 Leightonfield Pa11 tripped and locked out due to UG fault between Pa11 to S7614. S6355 had to be restored via lv network due to secondary fault found between LB24 and LB145 (tree on HV mains). | April | 2021 | 2021Q4 | 2021 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-04-15 | N | 279 | N | 7 | N | N | 1.1101 | 39.4971 | 1631.0798
[7 empty] | 3194 | 19336 | 1846829 | 2021-04-15 12:41 | 2021-04-15 15:15 | 154 | 11kV | 462 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT12629 Goolara Niclins - 11kV HDO centre Phase fuse replacement required | April | 2021 | 2021Q4 | 2021 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2021-04-15 | N | 154 | N | 7 | N | N | 1.1101 | 39.4971 | 337.616
[7 empty] | 2842 | 14321 | 1846924 | 2021-04-15 17:20 | 2021-04-15 19:05 | 105 | 11kV | 5337 | 59 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3288 City South - 43/44G tripped on Earth Fault UG cable fault on the 43F Feeder leg See 1846926 1846925 1846924 | April | 2021 | 2021Q4 | 2021 | ZN3288:PA43 44GHJ | ZN3288:PA43 44GHJ | ZN03288/43 44GHJ | SYDNEY | UG | Not Veg | 2021-04-15 | N | 90.4576 | N | 7 | N | N | 1.1101 | 39.4971 | 3900.1222
[7 empty] | 2125 | 5411 | 1846934 | 2021-04-15 19:25 | 2021-04-15 20:00 | 35 | 11kV | 32340 | 924 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | IR 79642 tripped and locked out. Cause: Bat on mains caused flash over 1 bay adj to PT124 | April | 2021 | 2021Q4 | 2021 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2021-04-15 | N | 35 | N | 7 | N | N | 1.1101 | 39.4971 | 23633.1181
[7 empty] | 2400 | 8942 | 1847076 | 2021-04-16 17:50 | 2021-04-16 17:55 | 5 | 11kV | 130 | 26 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT11613 Monastir Phegans Bay - All 3 phases interruped to remove dead possum found on PT. Dead possum on LV transformer bushing, smoking and crackling. PT 11613 will need isolating to remove, | April | 2021 | 2021Q4 | 2021 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2021-04-16 | N | 5 | N | 2 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 2003 | 3917 | 1847098 | 2021-04-17 05:51 | 2021-04-17 07:16 | 85 | 11kV | 112540 | 1324 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN547 Hornsby Panel 7 tripped on Earth fault C phase. Attempt to restore to S8054 SW/B failed at 07:03 Cause: UG fault between Panel 7 and S8054 SW/A | April | 2021 | 2021Q4 | 2021 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | UG | Not Veg | 2021-04-17 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 82240.9126
[7 empty] | 1684 | 35 | 1847119 | 2021-04-17 09:03 | 2021-04-17 10:40 | 97 | 11kV | 91665 | 945 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | at ZN1287 Revesby, 11kV Pnl 22 CB tripped on C phase OC, EF. Caused by bird damaging HVDOs at PT1914 | April | 2021 | 2021Q4 | 2021 | ZN1287:PA22 | ZN1287:PA22 | ZN01287/000022 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-04-17 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 66986.0783
[7 empty] | 2207 | 6338 | 1847090 | 2021-04-16 22:05 | 2021-04-17 13:25 | 920 | 11kV | 73398 | 1092 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 210886 2 fault operations B & C Phase Overcurrent truck hit pole HU-80116 dq Excluded OMS 1847090 | April | 2021 | 2021Q4 | 2021 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2021-04-16 | N | 67.2143 | N | 2 | N | N | 1.1101 | 39.4971 | 53637.0935
[7 empty] | 2782 | 13690 | 1847186 | 2021-04-17 18:28 | 2021-04-17 18:40 | 12 | 11kV | 1728 | 144 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | * Follows on from 1847410 (Pa18 trip at ZN1673 Turramurra) Section of 11kV between CP238 and CP3019 interrupted to remove tree/branch from OH mains. PT1917 also interrupted due to PT1344 supplying via LV // Abnormail state: DMA CP373 Bogan Campbell to AB3019 tee PT1917. LB 2209 Closed. | April | 2021 | 2021Q4 | 2021 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2021-04-17 | N | 12 | N | 6 | N | N | 1.1101 | 39.4971 | 1262.7714
[7 empty] | 2075 | 4904 | 1847121 | 2021-04-17 09:13 | 2021-04-17 19:05 | 592 | 11kV | 5261 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT18146 Hershon Ironbark - All 3 HDOs found operated. Cause: Tree/Branch brought down OH. 3ph service down between private pole and AG pole PO-3034. See 1847303 for extension of isolation to allow repairs. | April | 2021 | 2021Q4 | 2021 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2021-04-17 | N | 263.05 | N | 6 | N | N | 1.1101 | 39.4971 | 3844.5836
[7 empty] | 3137 | 18592 | 1847195 | 2021-04-17 19:55 | 2021-04-17 20:40 | 45 | 11kV | 225 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | CP43412 to PT12537 & PT12553 interrupted to remove large tree resting on HV & LV. | April | 2021 | 2021Q4 | 2021 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-04-17 | N | 45 | N | 6 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 2364 | 8376 | 1847175 | 2021-04-17 15:55 | 2021-04-18 13:10 | 1275 | 11kV | 28092 | 389 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Wyong Zn S.14891, Ex 11kV Panel 12, CP 50630 tripped on SEF, OC. tree branch brought down mains tee to PT 14375. see also 1847185 | April | 2021 | 2021Q4 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2021-04-17 | N | 72.2159 | N | 6 | N | N | 1.1101 | 39.4971 | 20528.805
[7 empty] | 1877 | 2532 | 1847245 | 2021-04-18 13:23 | 2021-04-18 16:45 | 202 | 11kV | 404 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210890 C Phase Repair LL lead Excluded OMS 1847245 | April | 2021 | 2021Q4 | 2021 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2021-04-18 | N | 202 | N | 3 | N | N | 1.1101 | 39.4971 | 295.2313
[7 empty] | 1825 | 1864 | 1847267 | 2021-04-18 17:12 | 2021-04-18 18:39 | 87 | 11kV | 174481 | 2091 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | at S36000 Olympic park, 11kV Pnl 7 CB tripped on A phase OC, EF. | April | 2021 | 2021Q4 | 2021 | ZN36000:PA7 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2021-04-18 | N | 83.4438 | N | 3 | N | N | 1.1101 | 39.4971 | 127505.5685
[7 empty] | 1883 | 2601 | 1847279 | 2021-04-18 18:38 | 2021-04-18 19:27 | 49 | 11kV | 32144 | 656 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | at Pennant Hills Zn 965, 11kV Pnl 39 tripped on EF. abnormal switching LB1903 closed, AB 1906 open. | April | 2021 | 2021Q4 | 2021 | ZN965:PA39 | ZN965:PA39 | ZN00965/000039 | PARRAMATTA | OH | Not Veg | 2021-04-18 | N | 49 | N | 3 | N | N | 1.1101 | 39.4971 | 23489.8871
[7 empty] | 1746 | 844 | 1847307 | 2021-04-19 18:40 | 2021-04-19 21:50 | 190 | 11kV | 1900 | 10 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | at PT 16119, Tx tails to LV fuse assembly connection high resistance. A and B phases interrupted. | April | 2021 | 2021Q4 | 2021 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2021-04-19 | N | 190 | N | 1 | N | N | 1.1101 | 39.4971 | 1388.464
[7 empty] | 2051 | 4668 | 1847573 | 2021-04-20 09:58 | 2021-04-20 11:30 | 92 | 11kV | 92 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210893 C Phase DOLF : 10 Amp Excluded OMS 1847573 | April | 2021 | 2021Q4 | 2021 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-04-20 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 67.2309
[7 empty] | 3104 | 18209 | 1847581 | 2021-04-20 10:31 | 2021-04-20 12:05 | 94 | 11kV | 94 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210894 B & C Phase DOLF : 10 Amp Excluded OMS 1847581 | April | 2021 | 2021Q4 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-04-20 | N | 94 | N | 3 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 2622 | 11305 | 1847691 | 2021-04-20 19:35 | 2021-04-20 20:24 | 49 | 11kV | 14632 | 792 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | at ZN 2635 Epping, 11kV Pnl 50 tripped on A Phase IOC, EF. UG feeder fault between S.62143 to S.35271 to S.77835. restoration steps 1847923,4 | April | 2021 | 2021Q4 | 2021 | ZN2635:PA50 | ZN2635:PA50 | ZN02635/000050 | RYDE | UG | Not Veg | 2021-04-20 | N | 18.4747 | N | 3 | N | N | 1.1101 | 39.4971 | 10692.634
[7 empty] | 3255 | 19861 | 1847711 | 2021-04-21 06:43 | 2021-04-21 08:55 | 132 | 11kV | 396 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210897 A Phase DOLF : 10 Amp Excluded OMS 1847711 | April | 2021 | 2021Q4 | 2021 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2021-04-21 | N | 132 | N | 1 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 2244 | 6774 | 1847928 | 2021-04-22 10:56 | 2021-04-22 11:45 | 49 | 11kV | 81879 | 1671 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | at S 12580 Erina Zn, 11kV CB panel 10 tripped on C phase OC / IOC. Tree branch on mains. | April | 2021 | 2021Q4 | 2021 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2021-04-22 | N | 49 | N | 2 | N | N | 1.1101 | 39.4971 | 59834.7582
[7 empty] | 2833 | 14216 | 1847989 | 2021-04-22 14:13 | 2021-04-22 22:30 | 497 | 11kV | 71564 | 667 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | S35800 Bankstown ZN - 11kV Panel 6L tripped on Relays: A & B phase O/C, 50T AB phase. Cause: Vehicle hit pole. See 1848034 for associated interruption to LV out of panel 18. | April | 2021 | 2021Q4 | 2021 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-04-22 | N | 107.2924 | N | 2 | N | N | 1.1101 | 39.4971 | 52296.8604
[7 empty] | 2090 | 5090 | 1848070 | 2021-04-23 06:41 | 2021-04-23 12:45 | 364.0167 | 11kV | 1456.0667 | 4 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 210903 B Phase B phase live line clamp broken Excluded OMS 1848086 | April | 2021 | 2021Q4 | 2021 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2021-04-23 | N | 364.0167 | N | 2 | N | N | 1.1101 | 39.4971 | 1064.0506
[7 empty] | 1979 | 3661 | 1848170 | 2021-04-23 13:41 | 2021-04-23 15:19 | 98 | 11kV | 84238 | 910 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zetland ZN188 Panel 3 tripped due to UG cable fault found between S1970 & S8609. Relays: Earth Fault, EFI, Fault check | April | 2021 | 2021Q4 | 2021 | ZN188:PA3 | ZN188:PA3 | ZN00188/000003 | SYDNEY | UG | Not Veg | 2021-04-23 | N | 92.5692 | N | 2 | N | N | 1.1101 | 39.4971 | 61558.6458
[7 empty] | 2476 | 9785 | 1848279 | 2021-04-24 14:00 | 2021-04-24 15:00 | 60 | 11kV | 4920 | 82 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210910 3 phase No protection operations. 11kV deadend broken JU-31652. LV siolated for repairs Excluded OMS 1848279. | April | 2021 | 2021Q4 | 2021 | 204:82703 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Not Veg | 2021-04-24 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 3595.3909
[7 empty] | 3159 | 18912 | 1848300 | 2021-04-24 17:52 | 2021-04-24 18:42 | 50 | 11kV | 38586 | 777 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | see also 1848300 At S 8100 Green Square Zone, 11kV Pnl 20 tripped on EF. 11kv underground fault between S4729 and S2752. See also 1848686 for restoration step. | April | 2021 | 2021Q4 | 2021 | ZN8100:PA20 | ZN384:PA68 | ZN00384/000068 | SYDNEY | UG | Not Veg | 2021-04-24 | N | 49.6602 | N | 2 | N | N | 1.1101 | 39.4971 | 28197.5107
[7 empty] | 2890 | 14822 | 1848326 | 2021-04-25 06:28 | 2021-04-25 07:16 | 48 | 11kV | 2558 | 55 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | at Zn 630 Mascot, 11kV cb pnl 33 tripped on EF, C phase OC, EFI. UG fault from Pnl 33 CB to S.2999 Sw/B to S.6359 sw/b to S.78611 Sw/B. see also 1848822 | April | 2021 | 2021Q4 | 2021 | ZN630:PA33 | ZN630:PA33 | ZN00630/000033 | SYDNEY | UG | Not Veg | 2021-04-25 | N | 46.5091 | N | 1 | N | N | 1.1101 | 39.4971 | 1869.311
[7 empty] | 2867 | 14527 | 1848382 | 2021-04-26 03:27 | 2021-04-26 04:29 | 62 | 11kV | 86056 | 1388 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | at S10997 Sans Souci Zone, 11kV CB panel 12 tripped, reclosed, tripped and locked out on IOC, EFI. Possum found at base of UGOH to S10348 | April | 2021 | 2021Q4 | 2021 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2021-04-26 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 62887.1866
[7 empty] | 2314 | 7666 | 1848383 | 2021-04-26 03:44 | 2021-04-26 06:22 | 158 | 11kV | 216703 | 1586 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn9037 Miranda - Pnl.8 tripped on A Phase OC, B Phase OC & Earth Fault Abnormal: S9809 Sw/A open with Sw/B closed, S8471 Sw/B Open with S9494 Sw/B closed Suspected tree on OH mains See 1848835 1848836 | April | 2021 | 2021Q4 | 2021 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Veg | 2021-04-26 | N | 136.6349 | N | 4 | N | N | 1.1101 | 39.4971 | 158360.1607
[7 empty] | 2587 | 11115 | 1848437 | 2021-04-26 10:47 | 2021-04-26 13:35 | 168.3333 | 11kV | 7070 | 42 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210911 A & B Phase DOLF : 20 Amp Remove tree branch from OHM near spur fuse 14661 Excluded oms 1848451 | April | 2021 | 2021Q4 | 2021 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2021-04-26 | N | 168.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 5166.5475
[7 empty] | 2074 | 4897 | 1848440 | 2021-04-26 10:53 | 2021-04-26 14:55 | 242 | 11kV | 18094.5 | 75 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S233 kardina Rd - Centre phase 11kV fuse operated Cause not ascertained at the time. See further interruption due to Tx failure | April | 2021 | 2021Q4 | 2021 | ZN180:PA30 | ZN180:PA30 | ZN00180/000030 | MOSMAN | UG | Not Veg | 2021-04-26 | N | 241.26 | N | 4 | N | N | 1.1101 | 39.4971 | 13222.9269
[7 empty] | 1990 | 3735 | 1848583 | 2021-04-27 04:17 | 2021-04-27 04:54 | 37 | 11kV | 34595 | 935 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 210913 2 fault operations Overcurrent faulty LAs pole DP-30812 | April | 2021 | 2021Q4 | 2021 | 513:83493 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Not Veg | 2021-04-27 | N | 37 | N | 4 | N | N | 1.1101 | 39.4971 | 25281.0056
[7 empty] | 1797 | 1548 | 1848652 | 2021-04-27 12:55 | 2021-04-27 14:03 | 68 | 11kV | 33492 | 546 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.2 tripped on: Earth fault & B phase OC UG cable fault between S4965 Sw/B adn S4964 Sw/A See 1848830 1848831 | April | 2021 | 2021Q4 | 2021 | ZN965:PA2 | ZN965:PA2 | ZN00965/000002 | HORNSBY | UG | Not Veg | 2021-04-27 | N | 61.3407 | N | 4 | N | N | 1.1101 | 39.4971 | 24474.9658
[7 empty] | 2738 | 13012 | 1848648 | 2021-04-27 12:41 | 2021-04-27 23:40 | 659 | 11kV | 659 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 210914 B & C Phase DOLF : 10 Amp Sub 15931 B&C 10A DOLF replaced plus 100A LVF. Tx found defective replace Excluded OMS 1848668, 1848648 | April | 2021 | 2021Q4 | 2021 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2021-04-27 | N | 659 | N | 4 | N | N | 1.1101 | 39.4971 | 481.5778
[7 empty] | 2575 | 10892 | 1848727 | 2021-04-27 20:50 | 2021-04-27 23:50 | 180 | 11kV | 33685 | 474 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | iR62226 Connells Terry tripped on SEF Abnormal: S10133 Sw/B closed with LB31014 Open Suspected protection malfunction. iR has tripped multiple times in previous weeks. To be inspected Wed business hours See 1848828 1848829 | April | 2021 | 2021Q4 | 2021 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Not Veg | 2021-04-27 | N | 71.0654 | N | 4 | N | N | 1.1101 | 39.4971 | 24616.0045
[7 empty] | 1896 | 2775 | 1848777 | 2021-04-28 09:23 | 2021-04-28 10:30 | 67 | 11kV | 63784 | 952 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | iR62730 Manns Narara Creek tripped on: OC Branch found on 11kV OH PT13681 | April | 2021 | 2021Q4 | 2021 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2021-04-28 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 46611.4659
[7 empty] | 2728 | 12721 | 1848756 | 2021-04-28 07:10 | 2021-04-28 16:21 | 551 | 11kV | 34772 | 111 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210918 1 fault operation Overcurrent insulator at pole FN-60066 Excluded OMS 1848756, 1848797 | April | 2021 | 2021Q4 | 2021 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-04-28 | N | 313.2613 | N | 2 | N | N | 1.1101 | 39.4971 | 25410.352
[7 empty] | 3141 | 18648 | 1848934 | 2021-04-29 06:58 | 2021-04-29 12:48 | 350 | 11kV | 88509 | 575 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 210920 11kv cable fault between sw 19111 and ABS 8798 section isolated for repair. ABS 998 on Fdr 82132 is abnormal due to DMA so customers beeyond ABS 998 were also interrupted. Excluded oms 1848934 | April | 2021 | 2021Q4 | 2021 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | UG | Not Veg | 2021-04-29 | N | 153.9287 | N | 1 | N | N | 1.1101 | 39.4971 | 64679.7666
[7 empty] | 2843 | 14323 | 1849177 | 2021-04-30 12:21 | 2021-04-30 14:35 | 134 | 11kV | 134 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210923 Burnt off tapping to DOLF Excluded OMS 1849177 | April | 2021 | 2021Q4 | 2021 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2021-04-30 | N | 134 | N | 1 | N | N | 1.1101 | 39.4971 | 97.9232
[7 empty] | 2702 | 12343 | 1849282 | 2021-05-01 09:40 | 2021-05-01 10:23 | 43 | 11kV | 47902 | 1114 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN188 Zetland - Pamel 16 tripped on earth fault, EFI, fault check. Cause: Feeder fault found between pnl 16 and S4552 SW/A | May | 2021 | 2021Q4 | 2021 | ZN188:PA16 | ZN188:PA16 | ZN00188/000016 | SYDNEY | UG | Not Veg | 2021-05-01 | N | 43 | N | 2 | N | N | 1.1101 | 39.4971 | 35005.3687
[7 empty] | 2999 | 16651 | 1849337 | 2021-05-01 17:38 | 2021-05-01 19:40 | 122 | 11kV | 11631 | 103 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12580 Erina Panel 13 tripped under fault. Relays: FDR C phase IOC trip (FIU No.3 FDR) Suspected cable fault in front line of Panel 13 in cable basement at Zone Sub. DOp reported burnt odour and smoke in Erina Sub on arrival. | May | 2021 | 2021Q4 | 2021 | ZN12580:PA13 | ZN12580:PA13 | ZN12580/000013 | CENTRAL COAST | UG | Not Veg | 2021-05-01 | N | 112.9223 | N | 2 | N | N | 1.1101 | 39.4971 | 8499.5917
[7 empty] | 2640 | 11574 | 1849464 | 2021-05-03 08:43 | 2021-05-03 10:00 | 77 | 11kV | 67361 | 953 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN15001 BROOKVALE 11kV CB Panel 11 Left 'Old Pittwater Roger etc' fdr tripped on: Relays: B Phase IOC Signals: 11kv trip, Zone Earth EFI: Pa11 to S16546 Remarks: Cable damaged between S16546 to S16221 See 1849952,3 Ex 1849464,5 | May | 2021 | 2021Q4 | 2021 | ZN15001:PA11 | ZN15001:PA11 | ZN15001/000011 | NORTHERN BEACHES | UG | Not Veg | 2021-05-03 | N | 70.6831 | N | 2 | N | N | 1.1101 | 39.4971 | 49225.432
[7 empty] | 2812 | 13990 | 1849631 | 2021-05-03 19:00 | 2021-05-03 21:00 | 120 | 11kV | 17760 | 148 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 210929 Rusted 11kV insulators pole NB-50008, cross arm also cracked. Replaced both. Excluded OMS 1849631 | May | 2021 | 2021Q4 | 2021 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2021-05-03 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 12978.4842
[7 empty] | 2823 | 14082 | 1849406 | 2021-05-02 14:19 | 2021-05-04 01:00 | 2081 | 11kV | 30596 | 31 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S.2635 Epping Zn, 11kV CB Pnl 62 tripped on: B phase IOC, EF. UG cable fault see 1849778 for restoration step | May | 2021 | 2021Q4 | 2021 | ZN2635:PA62 | ZN2635:PA62 | ZN02635/000062 | RYDE | UG | Not Veg | 2021-05-02 | N | 986.9677 | N | 1 | N | N | 1.1101 | 39.4971 | 22358.6544
[7 empty] | 3174 | 19126 | 1849658 | 2021-05-04 08:11 | 2021-05-04 09:16 | 65 | 11kV | 3835 | 59 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN3425 CASTLE COVE 11kV CB Panel 21 tripped on Relays: C Phase OC, EF and EF check and EFI Tx2 Panel: 3 Phase fault check, EF Check Singals: Tx2 Group Earth, 11kv trip EFI's: Nil Cause: UG Fault from ZN3425 Castle Cove Panel 21 to S35105 SwA. Frontline Feeder Fault | May | 2021 | 2021Q4 | 2021 | ZN3425:PA21 | ZN3425:PA21 | ZN03425/000021 | WILLOUGHBY | UG | Not Veg | 2021-05-04 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 2802.5049
[7 empty] | 1744 | 825 | 1849775 | 2021-05-04 14:12 | 2021-05-04 19:00 | 288 | 11kV | 2405 | 16 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 210932 3 fault operations Blown Lightning Arrestor Excluded OMS 1849775 | May | 2021 | 2021Q4 | 2021 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2021-05-04 | N | 150.3125 | N | 2 | N | N | 1.1101 | 39.4971 | 1757.5031
[7 empty] | 1835 | 2035 | 1849840 | 2021-05-05 01:46 | 2021-05-05 03:07 | 81 | 11kV | 101038 | 1301 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35555 Croydon - Pnl.8 tripped on: A & C phase OC, IOC UG cable fault between S1558, S7073 & S4901 See 1850229 1850230 1850232 | May | 2021 | 2021Q4 | 2021 | ZN35555:PA8 | ZN35555:PA8 | ZN35555/000008 | CANADA BAY | UG | Not Veg | 2021-05-05 | N | 77.6618 | N | 6 | N | N | 1.1101 | 39.4971 | 73835.5903
[7 empty] | 2106 | 5240 | 1849846 | 2021-05-05 04:10 | 2021-05-05 05:45 | 95 | 11kV | 70720 | 812 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn3154 St Ives - Pnl.11 tripped on C phase O/C Dop Patrolled feeder and found tree branch on 11kV OH mains near S35365. Pnl.11 was shooting through and did not close after several attempts. No relay operations on each attempt close. CB racked out and closed on the floor and still shooting through See 1850239 1850242 1850245 | May | 2021 | 2021Q4 | 2021 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2021-05-05 | N | 87.0936 | N | 6 | N | N | 1.1101 | 39.4971 | 51680.0901
[7 empty] | 1782 | 1416 | 1849947 | 2021-05-05 11:22 | 2021-05-05 12:00 | 38 | 11kV | 76 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 210936 A Phase DOLF : 10 Amp Excluded OMS 1849947 | May | 2021 | 2021Q4 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-05-05 | N | 38 | N | 6 | N | N | 1.1101 | 39.4971 | 55.5386
[7 empty] | 3105 | 18225 | 1850073 | 2021-05-05 22:09 | 2021-05-06 00:25 | 136 | 11kV | 96918 | 723 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210939 faulty tapping at abs 40013 cut away. Excluded OMS 1850073 | May | 2021 | 2021Q4 | 2021 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Not Veg | 2021-05-05 | N | 134.0498 | N | 6 | N | N | 1.1101 | 39.4971 | 70824.8158
[7 empty] | 2257 | 6951 | 1850049 | 2021-05-05 19:21 | 2021-05-06 03:30 | 489 | 11kV | 489 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 210938 MVA at sub pole 62177, dolf found open on arrival, sub fully isolated to make repairs to damaged earth wire & change damaged transformer . Excluded OMS 1850049 | May | 2021 | 2021Q4 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-05-05 | N | 489 | N | 6 | N | N | 1.1101 | 39.4971 | 357.3468
[7 empty] | 2232 | 6684 | 1850117 | 2021-05-06 07:19 | 2021-05-06 08:11 | 52 | 11kV | 58604 | 1127 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN 1193 LINDFIELD 11kv Pnl 27 "Havilah Nelson" feeder tripped on: Relays: A and B phase IOC with lock-out Signals: 11kv trip with efi Field efi's: nil Cause of Interruption : Tree branch contact - other 3 Havilah NB: feeder reclosed at 06:38 and 07:18 and locked out at 07:19 | May | 2021 | 2021Q4 | 2021 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Veg | 2021-05-06 | N | 52 | N | 10 | N | N | 1.1101 | 39.4971 | 42826.0747
[7 empty] | 2680 | 12141 | 1850118 | 2021-05-06 07:19 | 2021-05-06 08:27 | 68 | 11kV | 98076 | 1473 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | S 12570 Avoca Zone 11Kv Panel 39 " S 14134 Avoca Avoca Motor Inn " reclosed and tripped on Signals:11kv trip Relays:A & B phase O/C, Earth Fault, EFI Lockout Field EFI: Sub 14134, Sub 18035 Cause of Interruption : Tree/branch on OH Mains Branch removed by Dop vicinity LB 45056 See 1850746,7 ex 1850118 | May | 2021 | 2021Q4 | 2021 | ZN12570:PA39 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | OH | Veg | 2021-05-06 | N | 66.5825 | N | 10 | N | N | 1.1101 | 39.4971 | 71671.048
[7 empty] | 2777 | 13584 | 1850087 | 2021-05-06 06:18 | 2021-05-06 08:45 | 147 | 11kV | 153249 | 1220 | HV | Animal Possum | Animal | UGOH | Unplanned | Rain Heavy | N | At ZN 9245 Engadine 11kv feeder Panel No : 1 "S48147 " feeder TRIPPED and RECLOSED to LOCKOUT on: RELAYS :E/F , EFI, reclose , timing , lockout FIELD EFIs :S48147,S9287,S78335,S9642,SUGOH PrincessNr Boronia,S9358,S9065,UGOH Achilles Rd Nr Lantana Cause of Interruption : Animals/Birds Possum caused flashover at UGOH to PT9347,removed by Dop See 1850488,9 Ex 1850087,98,9 | May | 2021 | 2021Q4 | 2021 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2021-05-06 | N | 125.6139 | N | 10 | N | N | 1.1101 | 39.4971 | 111989.8491
[7 empty] | 2804 | 13890 | 1850128 | 2021-05-06 07:28 | 2021-05-06 09:10 | 102 | 11kV | 155222 | 1965 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN3472 Sefton Panel 27 tripped on Signals: 11kV Trip Relays: EF check, A phase OC , A phase IOC, Earth Fault, EFI EFI S4003,S8762,S47550,S47549,S47546,S35161,S47553,S47552,S35051 Cause: ZN3472 Sefton Panel 27 had an 11kV feeder fault S35051 - S4466 tee PT929. Regio required to Earth 11kV UGOH DOp suspects there could be damage on UGOH connection LV// Links 17920 11639 23955 13758 event ID16843 See OMS 1850455 1850560 1850561 1850128 | May | 2021 | 2021Q4 | 2021 | ZN3472:PA27 | ZN3472:PA27 | ZN03472/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-05-06 | N | 78.9934 | N | 10 | N | N | 1.1101 | 39.4971 | 113431.6593
[7 empty] | 2964 | 16114 | 1850174 | 2021-05-06 08:14 | 2021-05-06 09:54 | 100 | 11kV | 13071 | 132 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN15013 TERREY HILLS section of 11kV Panel 4 RE21350 Booralie Kulgoa tripped on overcurrent Cause: tree branch on OH mains. Large tree See 1850761,2 Ex 1850174 | May | 2021 | 2021Q4 | 2021 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2021-05-06 | N | 99.0227 | N | 10 | N | N | 1.1101 | 39.4971 | 9551.9013
[7 empty] | 2727 | 12713 | 1850127 | 2021-05-06 07:25 | 2021-05-06 10:08 | 163 | 11kV | 108721 | 667 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN9037 Miranda 11kv feeder Panel No :7 " Bates Drive " feeder TRIPPED on: RELAYS : Aphase O/C FIELD EFIs :Nil Cause of Interruption : Tree/branch on OH Mains Removed tree branch with assistance from L/Men | May | 2021 | 2021Q4 | 2021 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Veg | 2021-05-06 | N | 163 | N | 10 | N | N | 1.1101 | 39.4971 | 79450.1001
[7 empty] | 2356 | 8294 | 1850001 | 2021-05-05 14:35 | 2021-05-06 11:30 | 1255 | 11kV | 177345 | 424 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Zn12630 Peats Ridge - Pnl.3 tripped on SEL Tripped on SEL - no other comments provided by CR Suspect due to restoration steps, mutliple issues along feeder due to rain. See 1850428 1850429 1850430 1850431 1850434 1850435 1850436 1850437 1850439 | May | 2021 | 2021Q4 | 2021 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2021-05-05 | N | 418.2665 | N | 6 | N | N | 1.1101 | 39.4971 | 129598.4952
[7 empty] | 2425 | 9285 | 1850231 | 2021-05-06 08:49 | 2021-05-06 13:55 | 306 | 11kV | 106587 | 745 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN36200 EMPIRE BAY section of 11kV Panel 8 IR63104 Wards Hill Stewart 0.4 tripped on Signals: OC Trip Cause of Interruption : Tree/branch brought down OH 11Kv feeder from AB 40697 to LB 48547 tee PT 11106 AP issued to Linworker See 1850749,50,1 Ex 1850231 | May | 2021 | 2021Q4 | 2021 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2021-05-06 | N | 143.0698 | N | 10 | N | N | 1.1101 | 39.4971 | 77890.6358
[7 empty] | 2707 | 12385 | 1850190 | 2021-05-06 08:01 | 2021-05-06 15:44 | 463 | 11kV | 29249 | 693 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | S 14144 Wamberal Zone 11Kv Panel 10 " S 18824 Wamberal Aux No 2" tripped and reclosed Also Rec 44607 tripped and locked out on overcurrent Signals: 11Kv Trip Relays: O/C, EFI Field EFI: S 18826, S 48880 Cause: 11Kv on ground 302 Matcham Rd AP & CTW issued to Lineworkers @ PT 11815 See 1850768,70,1 Ex 1850172,6,233 | May | 2021 | 2021Q4 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2021-05-06 | N | 42.2063 | N | 10 | N | N | 1.1101 | 39.4971 | 21374.3065
[7 empty] | 1967 | 3572 | 1850528 | 2021-05-06 16:00 | 2021-05-06 17:15 | 75 | 11kV | 2025 | 27 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 10 Isolated at CP48995 to CP62765 Cause: interrupted for safety reasons. Tree on Mains | May | 2021 | 2021Q4 | 2021 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2021-05-06 | N | 75 | N | 10 | N | N | 1.1101 | 39.4971 | 1479.8103
[7 empty] | 1976 | 3651 | 1850545 | 2021-05-06 18:15 | 2021-05-06 18:30 | 15 | 11kV | 15 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210945 Isolated to repair loose connection. OMS 1850545 | May | 2021 | 2021Q4 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-05-06 | N | 15 | N | 10 | N | N | 1.1101 | 39.4971 | 10.9616
[7 empty] | 2287 | 7291 | 1850622 | 2021-05-07 05:10 | 2021-05-07 06:32 | 82 | 11kV | 231076 | 2987 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | at ZN3600 Kingsford, 11kV CB pnl 9 tripped on C phase OC, EFI. section of UG feeder faulted between S35600 Pnl 9 to S2276, S8560, S3158. | May | 2021 | 2021Q4 | 2021 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2021-05-07 | N | 77.3606 | N | 8 | N | N | 1.1101 | 39.4971 | 168863.5252
[7 empty] | 1685 | 36 | 1850620 | 2021-05-07 03:57 | 2021-05-07 06:57 | 180 | 11kV | 156428 | 926 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | Rain Heavy | N | at ZN 965 Pennant Hills, 11kv CB Pnl 26 tripped, reclosed and LO on C Phase OC. EFI at S6153. UG feeder cable fault from S6153 to S2696 to S4988 to S4491. | May | 2021 | 2021Q4 | 2021 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2021-05-07 | N | 168.9287 | N | 8 | N | N | 1.1101 | 39.4971 | 114312.9686
[7 empty] | 2096 | 5153 | 1850661 | 2021-05-07 07:46 | 2021-05-07 12:10 | 264 | 11kV | 1056 | 4 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Heavy | N | at PT18459, 11kV roadside HV fuse operated due to stick contacting Tx bushing / tank. | May | 2021 | 2021Q4 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-05-07 | N | 264 | N | 8 | N | N | 1.1101 | 39.4971 | 771.6937
[7 empty] | 2482 | 9869 | 1850763 | 2021-05-07 10:47 | 2021-05-07 12:22 | 95 | 11kV | 78584 | 886 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN965 PENNANT HILLS 11kV CB Panel 20 S44292 New Farm John Savage' fdr tripped on Signals: 11kv trip Relays: Earth Fault, EFI Cause: UG Fault between Zn965 Panel 20 to S48292SwA tee S5370 No.1 Tx See 1851462,3 ex 1850763 | May | 2021 | 2021Q4 | 2021 | ZN965:PA20 | ZN965:PA20 | ZN00965/000020 | HORNSBY | UG | Not Veg | 2021-05-07 | N | 88.6953 | N | 8 | N | N | 1.1101 | 39.4971 | 57426.8694
[7 empty] | 1906 | 2857 | 1850801 | 2021-05-07 12:00 | 2021-05-07 13:35 | 95 | 11kV | 190 | 2 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 210951 Trees found grown between phases (11kV) between poles HR-51116 & HR 51117 Excluded OMS 1850801 | May | 2021 | 2021Q4 | 2021 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2021-05-07 | N | 95 | N | 8 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 2813 | 13991 | 1850839 | 2021-05-07 17:10 | 2021-05-07 18:15 | 65 | 11kV | 1820 | 28 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 210953 Conductor off insulator pole LQ-50003 Excluded OMS 1850839 | May | 2021 | 2021Q4 | 2021 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2021-05-07 | N | 65 | N | 8 | N | N | 1.1101 | 39.4971 | 1330.0023
[7 empty] | 2462 | 9561 | 1850871 | 2021-05-07 15:59 | 2021-05-07 18:30 | 151 | 11kV | 302 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 210957 LLC lead fell off OHM. no fuse operations Excluded OMS 1850871 | May | 2021 | 2021Q4 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-05-07 | N | 151 | N | 8 | N | N | 1.1101 | 39.4971 | 220.6927
[7 empty] | 1745 | 841 | 1850896 | 2021-05-07 17:35 | 2021-05-07 19:40 | 125.1333 | 11kV | 15641.6667 | 125 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S 1868 Leonie Cres 11kv HV fuse blown, Left hand side, 40A OC10M Cause of Interruption : Vehicle Hit Mains High vehicle hit foxtel mains causing LV mains to clash, possible grading issue. | May | 2021 | 2021Q4 | 2021 | ZN3472:PA12 | ZN3472:PA12 | ZN03472/000012 | CUMBERLAND | OH | Not Veg | 2021-05-07 | N | 125.1333 | N | 8 | N | N | 1.1101 | 39.4971 | 11430.4686
[7 empty] | 2092 | 5096 | 1851046 | 2021-05-08 20:13 | 2021-05-08 21:40 | 87.3667 | 11kV | 11969.2333 | 137 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210961 no protection operation Blown 11kV tapping pole TB-50233. PT 12999 & 27492 put into LV parallel until repairs completed. | May | 2021 | 2021Q4 | 2021 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2021-05-08 | N | 87.3667 | N | 1 | N | N | 1.1101 | 39.4971 | 8746.7627
[7 empty] | 2772 | 13461 | 1851106 | 2021-05-09 12:57 | 2021-05-09 14:29 | 92 | 11kV | 93472 | 1016 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | @ ZN.10994 Mortdale Exiting Panel 19 labelled "S.50482 Roberts Fairway No.1" tripped , re-closed & tripped. RELAYS - B & C Phase Overcurrent , Earth Fault SIGNALS - CB.19 open , CB.19 closed , AR lockout FIELD EFI's -Nil IR 79687 Forest Valentia tripped and locked out at 1256 Relays- Lock out OC trip Cause of Interruption : Vehicle Hit Pole car hit pole at 8 Moons Avenue Lugarno See 1851512 2nd 1851513 Ex 1851106,11,2 | May | 2021 | 2021Q4 | 2021 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2021-05-09 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 68306.5806
[7 empty] | 3232 | 19661 | 1851137 | 2021-05-09 17:08 | 2021-05-09 18:15 | 67 | 11kV | 61716.5667 | 1256 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S129 Hunters Hill Zone, 11kV CB Panel 40 tripped on C Phase IOC, EF. Abnormal switching at time of event: Sw/B @ S.5263 closed, Sw/A @ S.49184 open and Sw/B @ S.5262 Open due to cable fault between S.5262 and S.49184. S62084 also in LV // with S.3322 due to previous DMA. | May | 2021 | 2021Q4 | 2021 | ZN129:PA40 | ZN129:PA40 | ZN00129/000040 | RYDE | UG | Not Veg | 2021-05-09 | N | 49.1374 | N | 3 | N | N | 1.1101 | 39.4971 | 45100.6466
[7 empty] | 2279 | 7197 | 1851063 | 2021-05-09 06:21 | 2021-05-09 21:16 | 895.3333 | 11kV | 195746.4167 | 1279 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN1290 LEIGHTONFIELD 11kV CB Panel 9 'S664 & S7472' tripped, reclosed & tripped Relays: Trip, Relay: Earth Fault, EFI, Lock Out Signals: CB9 open, 11kv trip, Zone Earth, Tx3 Group Earth, AR Lock Out EFI: S7472 S4285 S47019 Cause: OH Down Fault 1: 11kV OH down from SwB S47019 to S35957 Fault 2: 11kV OH down from SwB S35957 to LB884 tee PT1737 See 1851497,8,9,500 ex 1851063,88,119,27,33 | May | 2021 | 2021Q4 | 2021 | ZN1290:PA9 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-05-09 | N | 153.0465 | N | 3 | N | N | 1.1101 | 39.4971 | 143045.7078
[7 empty] | 2221 | 6606 | 1851161 | 2021-05-10 03:12 | 2021-05-10 07:23 | 251 | 11kV | 413193 | 1837 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | at S 35500 Top Ryde Zn, 11kV CB Pnl 36 reclosed and locked out on A & C O/C, SEL. Cause of original fault not found, 11kV bond burnt off between S5334 and LB 737. This is likely secondary fault as EFI downstream operated at S49437. Sub 7493 was also affected in this outage due to abnormal switching - SwB closed @ S7493 and AB.375 open. (see 1851508) | May | 2021 | 2021Q4 | 2021 | ZN35500:PA36 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2021-05-10 | N | 224.9281 | N | 2 | N | N | 1.1101 | 39.4971 | 301949.2573
[7 empty] | 3115 | 18365 | 1851317 | 2021-05-10 14:41 | 2021-05-10 18:35 | 233.6833 | 11kV | 8879.9667 | 38 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex ZN35370 GALSTON section of 11kV Panel 10 'Galston Au #2' fdr DOp Isolated 11kv mains beyond LB78892 in Galston Cause: interrupted for safety reasons. Car hit pole from earlier in the day. PT811 See 1851317 ex 1851212 | May | 2021 | 2021Q4 | 2021 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2021-05-10 | N | 233.6833 | N | 2 | N | N | 1.1101 | 39.4971 | 6489.2177
[7 empty] | 1756 | 963 | 1851548 | 2021-05-11 15:49 | 2021-05-11 17:15 | 86 | 11kV | 774 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 210975 A Phase DOLF : 16 Amp Excluded OMS 1851548 | May | 2021 | 2021Q4 | 2021 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2021-05-11 | N | 86 | N | 1 | N | N | 1.1101 | 39.4971 | 565.6164
[7 empty] | 1914 | 2961 | 1851595 | 2021-05-12 00:06 | 2021-05-12 01:32 | 86 | 11kV | 163549 | 1961 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.15 tripped on: Earth fault, OC Bird on 11kV UGOH between LB524 to S49378 tee PT1384 See 1851944 1851945 | May | 2021 | 2021Q4 | 2021 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-05-12 | N | 83.4008 | N | 4 | N | N | 1.1101 | 39.4971 | 119516.7853
[7 empty] | 1984 | 3707 | 1851786 | 2021-05-12 18:15 | 2021-05-12 19:36 | 81 | 11kV | 90767 | 1207 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn129 Hunters Hill -Pnl.38 tripped on: A & C phase IOC & E/F Possum found on ground near first UGOH to PT327 Betts Park See 1851947 1851948 | May | 2021 | 2021Q4 | 2021 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2021-05-12 | N | 75.2005 | N | 4 | N | N | 1.1101 | 39.4971 | 66329.8464
[7 empty] | 1727 | 628 | 1851797 | 2021-05-12 19:16 | 2021-05-12 20:25 | 69 | 11kV | 828 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 210977 A & C Phase DOLF : 31 Amp Excluded OMS 1851797 | May | 2021 | 2021Q4 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-05-12 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 605.078
[7 empty] | 2705 | 12376 | 1851807 | 2021-05-12 19:28 | 2021-05-12 22:00 | 152 | 11kV | 3560 | 87 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | REC44582 Erina - tripped & reclosed on: OC @ PT18556 Gooriwa Carlton - Footpath phase HDO blown Lightning See 1851954 1951955 | May | 2021 | 2021Q4 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2021-05-12 | N | 40.9195 | N | 4 | N | N | 1.1101 | 39.4971 | 2601.543
[7 empty] | 1720 | 484 | 1851838 | 2021-05-13 01:36 | 2021-05-13 02:22 | 46 | 11kV | 46 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn116 Leichhardt - Pnl.7 tripped on O/C & E/F Car hit pole LE-7307 opposite 28 Robert St | May | 2021 | 2021Q4 | 2021 |  |  |  | INNER WEST | OH | Not Veg | 2021-05-13 | N | 46 | N | 3 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 2264 | 7044 | 1851843 | 2021-05-13 06:37 | 2021-05-13 10:37 | 240 | 11kV | 4560 | 19 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | No Weather Impact | N | LID 210980 A & B Phase DOLF : 32 Amp LV service blown at pillar IU-90363. DOLF's may not have graded with LV fault. dq Excluded OMS 1851845## | May | 2021 | 2021Q4 | 2021 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | UG | Not Veg | 2021-05-13 | N | 240 | N | 3 | N | N | 1.1101 | 39.4971 | 3332.3135
[7 empty] | 2182 | 6065 | 1852079 | 2021-05-13 23:41 | 2021-05-14 01:40 | 119 | 11kV | 595 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12620 NORAVILLE section of 11kV Panel 11 PT49314 SOLDIERS POINT VICTORIA 0.6 11kv HDO centre phase operated 31.5Amp Fatigue HDO, failed to drop due to sea salt corrosion. DOp replaced and restored supply See 1852694 ex 1852079 | May | 2021 | 2021Q4 | 2021 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2021-05-13 | N | 119 | N | 3 | N | N | 1.1101 | 39.4971 | 434.8085
[7 empty] | 3235 | 19675 | 1852089 | 2021-05-14 08:08 | 2021-05-14 12:05 | 237 | 11kV | 49221 | 456 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210982 B Phase No protection operation. Blown tapping b phase line side of ABS 13340. Customers reported low volts starting at 808am. Excluded OMS 1852089 | May | 2021 | 2021Q4 | 2021 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2021-05-14 | N | 107.9408 | N | 5 | N | N | 1.1101 | 39.4971 | 35969.255
[7 empty] | 3161 | 18951 | 1852251 | 2021-05-14 16:00 | 2021-05-14 19:03 | 183 | 11kV | 19947 | 109 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | LID 210985 Tree fell in CCT 11kV broke x arm straps at pole IS82140 11kV OMS 1852251 lid 210985 33kV OMS 1852257 LID 210986 | May | 2021 | 2021Q4 | 2021 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2021-05-14 | N | 183 | N | 5 | N | N | 1.1101 | 39.4971 | 14576.6793
[7 empty] | 2309 | 7635 | 1852262 | 2021-05-14 17:53 | 2021-05-14 19:30 | 97 | 11kV | 97 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 210987 dead bird found at sub. Excluded oms 1852262 | May | 2021 | 2021Q4 | 2021 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2021-05-14 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 70.8847
[7 empty] | 1719 | 481 | 1852290 | 2021-05-14 20:12 | 2021-05-14 21:10 | 57.55 | 11kV | 2935.05 | 51 | HV | Animal Possum | Animal | Pole | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 16 PT13099 PALMER WOLSELEY 31.5Amp footpath side HDO operated. possum on pole has shorted out the lines - customer has no power See 1852290 ex 1852293 | May | 2021 | 2021Q4 | 2021 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2021-05-14 | N | 57.55 | N | 5 | N | N | 1.1101 | 39.4971 | 2144.848
[7 empty] | 2486 | 9907 | 1852306 | 2021-05-14 21:57 | 2021-05-14 22:50 | 53 | 11kV | 4021 | 1369 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 16 CP40118 Murrawal Kilpa 0.2 tripped and reclosed Relays: O/C Trip PT13099 Palmer Wolseley. Footpath and centre phase HDO operated 31.5Amp Possum caused flashover at PT13099. DOp cleared and restored supply See 1852734,5 Ex 1852306,8 | May | 2021 | 2021Q4 | 2021 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2021-05-14 | N | 2.9372 | N | 5 | N | N | 1.1101 | 39.4971 | 2938.4282
[7 empty] | 2829 | 14129 | 1852312 | 2021-05-15 03:00 | 2021-05-15 03:46 | 46 | 11kV | 91816 | 2021 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN9118 CRONULLA 11kV CB Panel 11 'Toknin Waratah' fdr tripped on Relays: B & C Phase IOC EFI: S64758 @RE35756 Bundeena Tripped/Reclosed and prior reclsoing zone CB tripped Relays: O/C Cause: not ascertained. fdr patrol required beyond RE35756 Bundeena, when staff available Note: Refer TPE to investigate greading between Recloser and Zone CB. Zone CB picked up adn tripped prior to successful attempt of Recloser to reclose See 1852743,4 Ex 1852312 | May | 2021 | 2021Q4 | 2021 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2021-05-15 | N | 45.431 | N | 3 | N | N | 1.1101 | 39.4971 | 67096.4247
[7 empty] | 2722 | 12639 | 1852366 | 2021-05-15 12:40 | 2021-05-15 16:17 | 217 | 11kV | 658713 | 3342 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN10994 MORTDALE 11kV CB Panel 12 'Mortdale Aux #2' tripped on Relays: A & B Phase IOC EFI: Nil Abnormal: AB30266 closed with LB30349 open (NAR72803) Cause: not ascertained. DOp patrolled. No cause found See 1852766,70,1,2,5,6,7 Ex 1852366,7 | May | 2021 | 2021Q4 | 2021 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Veg | 2021-05-15 | N | 197.1014 | N | 3 | N | N | 1.1101 | 39.4971 | 481368.0317
[7 empty] | 2798 | 13839 | 1852432 | 2021-05-15 18:15 | 2021-05-15 20:22 | 127 | 11kV | 231281 | 2041 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | ZN195 PYMBLE 11kV CB Panel 30 'Suakin Council Works' tripped on Relays: Fault Check EF and EFi Sgianls: Zone Earth, Tx1 Group Earth, 11kv trip EFI's S49345 S7562 S4938 S4939 S47451 did not operate S4940 Cause: 11kv UG fault from S4939 to S47451 See 1852759,61 ex 1852432,3 | May | 2021 | 2021Q4 | 2021 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | UG | Not Veg | 2021-05-15 | N | 113.3175 | N | 3 | N | N | 1.1101 | 39.4971 | 169013.3332
[7 empty] | 3056 | 17418 | 1852501 | 2021-05-16 14:06 | 2021-05-16 20:23 | 377 | 11kV | 106519 | 924 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | ZN3154 ST IVES 11kV CB Panel 19 'Durham Memorial' Signals: 11kv trip, Zone Earth, Tx3 Group Earth Relays: EFI, SEF EFI's S1724 S4456 S484 S1086 @PT1371 Waugoola Mt Ida C phase HDO 63amp has blown Abnormal: AB1853 close LB3238 open RE1622 Eastern Arterial Open Cause: Transformer Failure @PT1371 possible Tx failure. Regio to organise repairs PT restored via LV// Event ID 17061 LV// mains down due to LV// collapsed at S4456 Dist 1. Outside 5 Pentecost See 1853142,4,5,6 2nd 1853143 Ex 1852501,3,9,10,23,8,37 | May | 2021 | 2021Q4 | 2021 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Not Veg | 2021-05-16 | N | 115.2803 | N | 1 | N | N | 1.1101 | 39.4971 | 77840.9434
[7 empty] | 2018 | 4123 | 1852865 | 2021-05-17 10:04 | 2021-05-17 10:21 | 17 | 11kV | 17 | 1 | HV | Animal Bird | Animal | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 210993 1 fault operation In customers installation Bird on private equipment | May | 2021 | 2021Q4 | 2021 |  |  |  | SINGLETON | OH | Not Veg | 2021-05-17 | N | 17 | N | 3 | N | N | 1.1101 | 39.4971 | 12.4231
[7 empty] | 2809 | 13909 | 1852610 | 2021-05-17 09:37 | 2021-05-17 15:45 | 368 | 11kV | 368 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex ZN116 LEICHHARDT section of 11kV Panel 7 CP64632 Maritime Service No.3 11kv HV supply was down 2 phases/ THere was no protection operations on Panel Leichhardt Cause: UG Fault There is open circuit on 2 phases between Zn116 Panel 7 and S3824SwA S557SwB and S50016SwB and CP64632 See 1853162 ex 1852610 | May | 2021 | 2021Q4 | 2021 |  |  |  | INNER WEST | UG | Not Veg | 2021-05-17 | N | 368 | N | 3 | N | N | 1.1101 | 39.4971 | 268.9235
[7 empty] | 2095 | 5152 | 1853167 | 2021-05-17 21:44 | 2021-05-17 21:57 | 13 | 11kV | 806 | 62 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 8 Recloser 44994 Mangrove Creek tripped and reclosed Relays: OC, IOC EFI: N/A To be patrolled | May | 2021 | 2021Q4 | 2021 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-05-17 | N | 13 | N | 3 | N | N | 1.1101 | 39.4971 | 589.001
[7 empty] | 2913 | 15184 | 1852834 | 2021-05-18 02:54 | 2021-05-18 05:02 | 128 | 11kV | 129152 | 1009 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 210999 - Part 2 Blown tapping at UGOH JU-70733 Protection details 50T BC see also OMS 1852853 for Trip and Reclose Excluded OMS 1852854 | May | 2021 | 2021Q4 | 2021 | 261:81864 | 261:81864 | ZN00261/081864 | LAKE MACQUARIE | OH | Not Veg | 2021-05-18 | N | 128 | N | 3 | N | N | 1.1101 | 39.4971 | 94380.4723
[7 empty] | 3157 | 18864 | 1852860 | 2021-05-18 07:27 | 2021-05-18 09:02 | 95 | 11kV | 16872 | 180 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN12580 ERINA 11kV CB Panel 7 'North Gosford' fdr has tripped Signals: 11kv trip Relays: B Phase timed OC EFI EFI Nil Cause: Frontline UG Fault between Zn12580 Erina Panel 7 LB61759 & S18675SwA See 1853181 ex 1852860 | May | 2021 | 2021Q4 | 2021 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | UG | Not Veg | 2021-05-18 | N | 93.7333 | N | 3 | N | N | 1.1101 | 39.4971 | 12329.56
[7 empty] | 1789 | 1476 | 1852901 | 2021-05-18 10:18 | 2021-05-18 16:45 | 387 | 11kV | 387 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211001 LLC broken at pole XC10003 Excluded OMS 1852901 | May | 2021 | 2021Q4 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-05-18 | N | 387 | N | 3 | N | N | 1.1101 | 39.4971 | 282.8082
[7 empty] | 2731 | 12751 | 1853107 | 2021-05-19 10:57 | 2021-05-19 13:20 | 143 | 11kV | 572 | 4 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 12 PT11302 SUMMERLEES YARRAM NO 1 11kV HDO B Phase 10K fuse operated Cause: tree branch contact - other. Bark on PT See 1853271 ex 1853107 | May | 2021 | 2021Q4 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2021-05-19 | N | 143 | N | 2 | N | N | 1.1101 | 39.4971 | 418.0007
[7 empty] | 2480 | 9857 | 1853113 | 2021-05-19 17:15 | 2021-05-19 18:12 | 57 | 11kV | 171 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211002 Broken Insulator on Pole AJ-30267 Excluded OMS 1851113 | May | 2021 | 2021Q4 | 2021 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2021-05-19 | N | 57 | N | 2 | N | N | 1.1101 | 39.4971 | 124.9618
[7 empty] | 2923 | 15341 | 1853236 | 2021-05-20 03:11 | 2021-05-20 04:58 | 107 | 11kV | 160069 | 1615 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN2310 PUNCHBOWL 11kV CB Panel 19 'Roselands Resview etc' fdr tripped on Relays: A Prot: C Phase OCm Neutral OC, IOC, EF B Prot: C Phase OC, Neutral OC, IOC, EF, EFI EFI: S1039 S3543 S1094 Cause: Ug Fault from S1094 to S2027 to S3249 to S722 Note Haz @ S2027 LV//'s and extension required. See 1853324,6,7 GIS 1853238 EX 1853236 | May | 2021 | 2021Q4 | 2021 | ZN2310:PA19 | ZN2310:PA19 | ZN02310/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-05-20 | N | 99.1139 | N | 1 | N | N | 1.1101 | 39.4971 | 116973.704
[7 empty] | 2078 | 4954 | 1853579 | 2021-05-21 18:55 | 2021-05-21 20:45 | 110 | 11kV | 110 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211011 interrupt to make unplanned OH repair in conjuction with 33kV emergency hotspot repairs on Fdr 3231 Excluded oms 1853579 | May | 2021 | 2021Q4 | 2021 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2021-05-21 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 2190 | 6159 | 1853590 | 2021-05-21 20:57 | 2021-05-21 22:35 | 98 | 11kV | 5853 | 78 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1610 HOMEBUSH BAY 11kV CB Panel 20 ' Relays: B phase OC and EF (FNG1BN*_*) EFI's S1320 S36128 S8930 Cause: UG Fault from S2837 SwD to S2283 SwA See 1853882,3,4 Ex 1853590 | May | 2021 | 2021Q4 | 2021 | ZN1610:PA20 | ZN1610:PA20 | ZN01610/000020 | PARRAMATTA | UG | Not Veg | 2021-05-21 | N | 75.0385 | N | 2 | N | N | 1.1101 | 39.4971 | 4277.1998
[7 empty] | 2523 | 10329 | 1853692 | 2021-05-22 18:30 | 2021-05-22 21:05 | 155 | 11kV | 66495 | 429 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 1 'Gunderman' additonal 11kv load due to abnormal switching for NAR75278 created low 11kv Votls. 11kV Regulator CP18836 Cooks Peats Ridge 0.55 made manual taps added to increase voltage output Cause: Voltage Problem (High or Low) See 1853926 ex 1853692 | May | 2021 | 2021Q4 | 2021 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2021-05-22 | N | 155 | N | 1 | N | N | 1.1101 | 39.4971 | 48592.5847
[7 empty] | 2285 | 7265 | 1853714 | 2021-05-23 00:05 | 2021-05-23 00:50 | 45 | 11kV | 6840 | 152 | HV | Burnt Contacts | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211017 interrupt sub 27101 & 10274 to repair LV connection near sub 27101 and LV DMA at sub 10274(burnt up Aph LVF) Excluded oms 1853714 | May | 2021 | 2021Q4 | 2021 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2021-05-23 | N | 45 | N | 2 | N | N | 1.1101 | 39.4971 | 4998.4703
[7 empty] | 1908 | 2876 | 1853774 | 2021-05-23 14:04 | 2021-05-23 15:20 | 76 | 11kV | 228 | 3 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211018 A Phase DOLF : 10 Amp sub dolf 70145 & line dolf 74993 Aph blown. Birds. Excluded OMS 1853774 | May | 2021 | 2021Q4 | 2021 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-05-23 | N | 76 | N | 2 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 2389 | 8755 | 1853851 | 2021-05-24 08:22 | 2021-05-24 11:45 | 203 | 11kV | 36134 | 178 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Ex ZN180 MOSMAN section of 11kV Panel 30 @Mosman zone Tx2 Group Earth, Zone Earth S233 KARDINIA RD tee off 11kv fuses blown due to suspected transformer failure See 1853851 GIS 1853880 ex 1853855 | May | 2021 | 2021Q4 | 2021 | ZN180:PA30 | ZN180:PA30 | ZN00180/000030 | MOSMAN | UG | Not Veg | 2021-05-24 | N | 203 | N | 1 | N | N | 1.1101 | 39.4971 | 26405.6614
[7 empty] | 2498 | 10096 | 1854064 | 2021-05-25 00:05 | 2021-05-25 01:50 | 105 | 11kV | 9034 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211022 Overcurret Nothing found | May | 2021 | 2021Q4 | 2021 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2021-05-25 | N | 91.2525 | N | 5 | N | N | 1.1101 | 39.4971 | 6601.7807
[7 empty] | 2200 | 6281 | 1854066 | 2021-05-25 03:48 | 2021-05-25 07:40 | 232 | 11kV | 26731 | 2476 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | ZN9700 KIRRAWEE 11kV CB Panel 18 tripped and reclosed on Relays: C Phase IOC, TImed OC, Lock out timming EFI, Fault CHeck Signals: Tx1 Group Earth, 11kv Trip EFI: Nil operated PT9654 Fauna Pl 11kv HDO ABB 50amp foot path side fuse blown due to Possum at PT9654 See 1854368,9 ex 1854066 | May | 2021 | 2021Q4 | 2021 | ZN9700:PA18 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | OH | Not Veg | 2021-05-25 | N | 10.796 | N | 5 | N | N | 1.1101 | 39.4971 | 19534.2264
[7 empty] | 2661 | 11864 | 1854146 | 2021-05-25 11:24 | 2021-05-25 12:26 | 62 | 11kV | 35087 | 572 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN35370 GALSTON 11kV CB Panel 10 fdr tripped signals: 11kv trip Relays: 50TAC EFI REC EFI S48711 Cause: tree branch on oh mains Branch near AB498 See 1854390,1 ex 1854146 | May | 2021 | 2021Q4 | 2021 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2021-05-25 | N | 61.3409 | N | 5 | N | N | 1.1101 | 39.4971 | 25640.5447
[7 empty] | 1919 | 3020 | 1854167 | 2021-05-25 13:37 | 2021-05-25 14:25 | 48 | 11kV | 1776 | 37 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211023 Trees Growing into Mains, remove overhanging tree at Pole 8L-40016 | May | 2021 | 2021Q4 | 2021 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2021-05-25 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 1297.8484
[7 empty] | 2894 | 14861 | 1854216 | 2021-05-25 17:08 | 2021-05-25 18:15 | 67 | 11kV | 54069 | 807 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Delayed operation of Panel 32 @ ZN.4545 Meadowbank labelled "S.47567 Victoria Linton" after DNMS , SCADA and Manual Operation of 11KV CB when carrying out NAR#74575 Attempted DNMS operation @ 1539 Attempted SCADA & Manual operation @ 1600 approx. CB.32 opened @ 1708 | May | 2021 | 2021Q4 | 2021 | ZN4545:PA32 | ZN4545:PA32 | ZN04545/000032 | RYDE | Unknown | Not Veg | 2021-05-25 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 39512.0304
[7 empty] | 2501 | 10122 | 1854260 | 2021-05-26 08:08 | 2021-05-26 09:17 | 69 | 11kV | 46633 | 684 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN7481 DARLING HARBOUR 132 11kV 11kV CB Panel 3 tripped on Relays: 3L protection, Earth Fault, EFI Signals: 11kv trip, Tx11 GE EFI: S78517 S7819 S35171 S36172 S35299 Cause: contractor error caused failure Sydney Civil Thaigo Gwadera (0478198091) has hit cable during jackhammering at 104 Miller st Pyrmont. Section of 11kv fdr from S35299 to S808 See 1854461,2 ex 1854260 | May | 2021 | 2021Q4 | 2021 | ZN7481:PA3 | ZN7481:PA3 | ZN07481/000003 | SYDNEY | UG | Not Veg | 2021-05-26 | N | 68.1769 | N | 1 | N | N | 1.1101 | 39.4971 | 34078.021
[7 empty] | 2258 | 6977 | 1854775 | 2021-05-28 18:32 | 2021-05-28 19:15 | 43.0667 | 11kV | 6416.9333 | 149 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211034 B Phase DOLF : 40 Amp Excluded OMS 1854777 | May | 2021 | 2021Q4 | 2021 | 256:80640 | 256:80640 | ZN00256/080640 | NEWCASTLE | OH | Veg | 2021-05-28 | N | 43.0667 | N | 1 | N | N | 1.1101 | 39.4971 | 4689.3056
[7 empty] | 2423 | 9265 | 1854811 | 2021-05-29 08:02 | 2021-05-29 13:45 | 343 | 11kV | 38920 | 510 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211036 Burnt off 11kV tapping at P. SI 90702. A Prot A-C Ph OC B Prot A-C to N EF Excluded OMS 1854811 1854833 | May | 2021 | 2021Q4 | 2021 | 513:83504 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Not Veg | 2021-05-29 | N | 76.3137 | N | 1 | N | N | 1.1101 | 39.4971 | 28441.5881
[7 empty] | 1688 | 187 | 1855015 | 2021-05-30 18:20 | 2021-05-30 23:52 | 332 | 11kV | 145189 | 488 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 211044 interrupt to put out fire and repair pole OS-20350 Excluded OMS 1855015 | May | 2021 | 2021Q4 | 2021 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2021-05-30 | N | 297.5184 | N | 1 | N | N | 1.1101 | 39.4971 | 106099.8388
[7 empty] | 3058 | 17450 | 1855057 | 2021-05-31 06:06 | 2021-05-31 07:20 | 74 | 11kV | 3468 | 48 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | ZN2635 EPPING 11kV CB Panel 62 fdr has tripped Signals: 11kv trip Relays: IOC ABC EFI EFI: S77523 S6354 Cause: 11kv endbox fault at S6353SwD. 11kv fdr isolated from S6354SwB open to S6353SwB Tx2 415V Links 415V BS closed See 1855366,7 ex 1855057 | May | 2021 | 2021Q4 | 2021 | ZN2635:PA62 | ZN2635:PA62 | ZN02635/000062 | RYDE | UG | Not Veg | 2021-05-31 | N | 72.25 | N | 1 | N | N | 1.1101 | 39.4971 | 2534.3121
[7 empty] | 2386 | 8724 | 1855572 | 2021-06-02 13:35 | 2021-06-02 14:25 | 50 | 11kV | 2650 | 53 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211050 Broken x arm pole BK-70104. | June | 2021 | 2021Q4 | 2021 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2021-06-02 | N | 50 | N | 2 | N | N | 1.1101 | 39.4971 | 1936.5418
[7 empty] | 3134 | 18555 | 1855663 | 2021-06-02 22:37 | 2021-06-03 00:04 | 87 | 11kV | 696 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1290 LEIGHTONFIELD 11kV CB Panel 11 'Biloela Gurr # 2' tripped on: Relays: C Phase IOC Signals: 11kv trip, Group # 3 and zone earth EFI: Nil Cause: UG Fault. Zn1290 Leightonfield Pa11 to S7614 | June | 2021 | 2021Q4 | 2021 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-06-02 | N | 87 | N | 2 | N | N | 1.1101 | 39.4971 | 508.6163
[7 empty] | 1996 | 3793 | 1855743 | 2021-06-03 11:56 | 2021-06-03 14:14 | 138 | 11kV | 276 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211056 Switched to repair broken dead end insulator on pole JS-50215. | June | 2021 | 2021Q4 | 2021 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2021-06-03 | N | 138 | N | 1 | N | N | 1.1101 | 39.4971 | 201.6927
[7 empty] | 3221 | 19609 | 1855913 | 2021-06-04 10:20 | 2021-06-04 12:05 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211058 Phases A,B & C (Three Phase) "Thermal imaging showed elevated temperatures on surge arrestors pole JS 50390. Section isolated for emergency replacement. refer to 1855913" SYSOP FITZPATRICK S DOP LEWIS C | June | 2021 | 2021Q4 | 2021 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Not Veg | 2021-06-04 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 3275 | 20142 | 1856026 | 2021-06-04 22:29 | 2021-06-04 23:49 | 80 | 11kV | 42695 | 983 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12690 BERKELEY VALE 11kV CB Panel 6 'Krone Enterprise' triupped and reclosed on: Relays: OC & EF, EFI, Reclose Lockout Signals: 11kv trip EFI: S18124 Cause: not ascertained Likely possum caused original fault but not found by DOp. Fault current caused bond off at LB42262 See 1856935,7 ex 1856026 | June | 2021 | 2021Q4 | 2021 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2021-06-04 | N | 43.4334 | N | 2 | N | N | 1.1101 | 39.4971 | 31200.2467
[7 empty] | 2185 | 6091 | 1856039 | 2021-06-05 02:01 | 2021-06-05 04:25 | 144 | 11kV | 100826 | 899 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | ZN195 PYMBLE 11kV CB Panel 28 'Bridge Pacific' tripped on: Relays: EF, Fault CHeck, EFI Signals: 11kv trip EFI: S6056 S6363 S77144 S8728 S4933 Cause: Possum across PT1109 HDO See 1856039,40 | June | 2021 | 2021Q4 | 2021 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | OH | Not Veg | 2021-06-05 | N | 112.1535 | N | 4 | N | N | 1.1101 | 39.4971 | 73680.6669
[7 empty] | 2320 | 7754 | 1856036 | 2021-06-05 00:58 | 2021-06-05 05:48 | 290 | 11kV | 366551 | 1309 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN690 CAMPSIE 11kV CB Panel 36 'Mooney Willcott' tripped on: Relays: EF, EFI, Fault CHeck Signals: 11kv trip EFI: S4925 S1999 S8754 S3339 (S2498 did not flag) Cause: 11kv UG fault from S3339 SwB to S2380 SwA to S3557 SwA to S3380 SwA. At Campsie 11kv No.36 CB would not close to restore the feeder and also has a DMA now to repair it which substantially increased restoration times. See 1857049 ex 1856036 | June | 2021 | 2021Q4 | 2021 | ZN690:PA36 | ZN690:PA36 | ZN00690/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-06-05 | N | 280.0237 | N | 4 | N | N | 1.1101 | 39.4971 | 267864.6594
[7 empty] | 2667 | 11915 | 1856095 | 2021-06-05 10:48 | 2021-06-05 12:10 | 82 | 11kV | 164 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 211060 supply back on B ph fuse 100amp - old age Sop CARSON S DOP RICHARDSON A | June | 2021 | 2021Q4 | 2021 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2021-06-05 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 1875 | 2516 | 1856115 | 2021-06-05 19:42 | 2021-06-05 20:00 | 18 | 11kV | 2376 | 132 | HV | Burnt Contacts | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | at S.10107, Entire sub interrupted for safety to allow replacement of HR fuse on LV Dist 3, C Phase. (St George type LV Board). | June | 2021 | 2021Q4 | 2021 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2021-06-05 | N | 18 | N | 4 | N | N | 1.1101 | 39.4971 | 1736.3107
[7 empty] | 2459 | 9535 | 1856221 | 2021-06-06 16:30 | 2021-06-06 18:30 | 119.5833 | 11kV | 7414.1667 | 62 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211064 TAYLOR, BEN - neighbour was cutting back trees, branches came into contact with wires, wires did clash 20 Amp, Phases A & B. Line DOLF SOP HOLLAND P DOP WILLIAMS S CC1: 22-"Refer to SOp" | June | 2021 | 2021Q4 | 2021 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2021-06-06 | N | 119.5833 | N | 1 | N | N | 1.1101 | 39.4971 | 5418.0543
[7 empty] | 2773 | 13545 | 1856295 | 2021-06-07 08:30 | 2021-06-07 10:45 | 135 | 11kV | 1485 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 11 PT13235 BRIESES PEATS RIDGE 0.8 HDO operated 31.5 Amp Cause: not ascertained. Supply checked ok See 1857082 ex 1856295,326 | June | 2021 | 2021Q4 | 2021 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2021-06-07 | N | 135 | N | 3 | N | N | 1.1101 | 39.4971 | 1085.1942
[7 empty] | 2088 | 5073 | 1856433 | 2021-06-07 18:26 | 2021-06-07 20:20 | 114 | 11kV | 99507 | 1543 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211072 Phase A No protection operations. Burnt 11kv tapping JU-61971 (subs beyond 15179) Also refer to OMS 186433. SOP HODDA J DOP HICKEY V | June | 2021 | 2021Q4 | 2021 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2021-06-07 | N | 64.4893 | N | 3 | N | N | 1.1101 | 39.4971 | 72716.7806
[7 empty] | 2663 | 11883 | 1856478 | 2021-06-07 22:39 | 2021-06-07 23:40 | 61 | 11kV | 5978 | 98 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn14144 wAMBERAL pANEL 10 - RECLOSER Matcham North has tripped Cause: Bat NEAR 306 Matcham Rd - CP44607 is in scan fail See 1857174 ex 1856478,9,82 | June | 2021 | 2021Q4 | 2021 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2021-06-07 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 4368.5461
[7 empty] | 2333 | 7995 | 1856713 | 2021-06-08 19:58 | 2021-06-08 21:16 | 78 | 11kV | 28860 | 370 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN35370 GALSTON 11kV CB Panel 2 'Galston High School' fdr tripped, reclosed and locked out on: Relays: 51BC, EFI, LO EFI: CP2831 Cause: tree/branch on OH mains Branch on mains on Taylors Rd | June | 2021 | 2021Q4 | 2021 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2021-06-08 | N | 78 | N | 1 | N | N | 1.1101 | 39.4971 | 21090.0368
[7 empty] | 2396 | 8885 | 1856750 | 2021-06-09 04:43 | 2021-06-09 10:05 | 321.85 | 11kV | 1931.1 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV Panel 24 PT62874 CULLENS WONGARI 1.0 Footpath & Middle 31.5 HDO's operated CC1: 22-"Refer to SOp" FRC1: 329-"High Voltage Fuse - Requires replacement" | June | 2021 | 2021Q4 | 2021 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2021-06-09 | N | 321.85 | N | 6 | N | N | 1.1101 | 39.4971 | 1411.1909
[7 empty] | 3113 | 18359 | 1856815 | 2021-06-09 09:49 | 2021-06-09 11:15 | 86 | 11kV | 89920 | 1110 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN36100 ROSE BAY 11kV CB Panel 2 tripped on Relays: EF Check Relayt, EFI, EF Signals: Tx1 Group E EFI: S35191 S102 S809 S5287 Note: S78835 EFI failed to indicate (electronic indication) Cause: Contractor error caused failure. UG digging contractor bore thorugh HV cable outside 274 old south head rd corner Russell st Vaucluse See 1857132,3 ex 1856815 | June | 2021 | 2021Q4 | 2021 | ZN36100:PA2 | ZN36100:PA2 | ZN36100/000002 | WAVERLEY | UG | Not Veg | 2021-06-09 | N | 81.009 | N | 6 | N | N | 1.1101 | 39.4971 | 65710.8838
[7 empty] | 3121 | 18414 | 1856862 | 2021-06-09 12:37 | 2021-06-09 14:52 | 135 | 11kV | 9180 | 68 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211079 Refer to NAR 77205 - LID 211080 - 1858085 11kV feeder taken out to repair 33kv feeder x aRM AT POLE ls-20168 SOP O'BRIEN B DOP TOWLE R | June | 2021 | 2021Q4 | 2021 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2021-06-09 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 6708.4732
[7 empty] | 2886 | 14760 | 1856969 | 2021-06-09 17:48 | 2021-06-09 18:41 | 53 | 11kV | 12508 | 236 | HV | Overload Operational | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN2400 BEROWRA section of 11kV Panel 21 CP3202 Pacific South Cowan interrupted due to high load on Berowra Cause: Load shedding High loads on Berowra Panel 21 due to abnormal swithcing from DMA on LB2295 See also Berowra interruptions on CP3281 @ 1822 and CP349 @ 1826 | June | 2021 | 2021Q4 | 2021 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2021-06-09 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 9140.4775
[7 empty] | 2281 | 7222 | 1857155 | 2021-06-09 18:22 | 2021-06-09 18:52 | 30 | 11kV | 1680 | 56 | HV | Load Shed - Ausgrid | Load Shed | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN2400 BEROWRA section of 11kV Panel 18 CP32181 Bay Cooper interrupted due to high loads on berowra Panel 21 Abnormal: LB2295 open LB473 closed Cause: Load SHedding High Loads on Berowra Panel 21 due to abnormal swithcing from DMA on LB2295 See also Berowra interruptions on CP3202 @1748 and CP349 @1826 | June | 2021 | 2021Q4 | 2021 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | Exclude | Not Veg | 2021-06-09 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 2054 | 4753 | 1856975 | 2021-06-09 18:26 | 2021-06-09 18:52 | 26 | 11kV | 3874 | 149 | HV | Load Shed - Ausgrid | Load Shed | Air Break Switch | Unplanned | No Weather Impact | N | Ex ZN2400 BEROWRA section of 11kV Panel 18 'Berowra Waters' CP349 Berowra Waters interrupted fue to high loads on Berowra Panel 21 Abnormal: LB2295 Open, LB473 Closed, CP3281 Open Cause: Load Shedding. High Loads on Berowra Panel 21 due to abnormal switching from DMA on LB2295 See also Berowra interruptions on CP3281 @ 1822 and CP3202 @ 1748 See 1857149 ex 1856975 | June | 2021 | 2021Q4 | 2021 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | Exclude | Not Veg | 2021-06-09 | N | 26 | N | 6 | N | N | 1.1101 | 39.4971 | 2831.0049
[7 empty] | 2822 | 14073 | 1857006 | 2021-06-10 06:26 | 2021-06-10 07:45 | 79 | 11kV | 64623 | 837 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN4853 STRATHFIELD SOUTH 11kV CB Panel 17 fdr tripped on signals: 11kv trip Relays: B phase inst, Earth Fault A & B protection, EFI, B Protection Cause: UG Fault from Zn4853 Pa17 to S2638SwA See 1857196 ex 1857006 | June | 2021 | 2021Q4 | 2021 | ZN4853:PA17 | ZN4853:PA17 | ZN04853/000017 | STRATHFIELD | UG | Not Veg | 2021-06-10 | N | 77.2079 | N | 5 | N | N | 1.1101 | 39.4971 | 47224.5823
[7 empty] | 2875 | 14646 | 1857008 | 2021-06-10 06:36 | 2021-06-10 08:05 | 89 | 11kV | 25018 | 758 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Cold <10C | N | ZN2196 MILPERRA 11kV CB Panel 2 'Bullecourt Horseley UWS #2' tripped on Relays: earth fault, overcurrent Signals: 11kv trip, zone and group 3 earth with EFI EFI: Panel 2 to sub 5575 Cause not ascertained. Patrolled and okay See 1857191,2,3,4 Ex 1857008,9 | June | 2021 | 2021Q4 | 2021 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-06-10 | N | 33.0053 | N | 5 | N | N | 1.1101 | 39.4971 | 18282.4165
[7 empty] | 2583 | 11007 | 1857269 | 2021-06-10 20:00 | 2021-06-10 21:38 | 98 | 11kV | 62496 | 1765 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 211086 Phase C Earth Fault Refer to OMS No. 1857269 11kV UGM fault between Sw 33409 & ABS 62770. SOP WILKINSON T DOP WILKINSON P | June | 2021 | 2021Q4 | 2021 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | UG | Not Veg | 2021-06-10 | N | 35.4085 | N | 5 | N | N | 1.1101 | 39.4971 | 45670.2335
[7 empty] | 2998 | 16634 | 1857274 | 2021-06-10 20:27 | 2021-06-10 21:46 | 79 | 11kV | 122734 | 1722 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15004 Newport - Pnl.1 - tripped on: O/C & E/F UG cable fault See 1857515 1857516 | June | 2021 | 2021Q4 | 2021 | ZN15004:PA1 | ZN15004:PA1 | ZN15004/000001 | NORTHERN BEACHES | UG | Not Veg | 2021-06-10 | N | 71.2741 | N | 5 | N | N | 1.1101 | 39.4971 | 89690.3872
[7 empty] | 3078 | 17744 | 1857281 | 2021-06-10 20:52 | 2021-06-11 08:08 | 675.8833 | 11kV | 3084.7333 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S1290 Leightonfield Panel 11 tripped on Relays: C phase IOC, Reclose Lockout and EFI Signals: Zone earth No2 Group Earth Cause: UG cable fault between Panel 11 and S7614 SW/A | June | 2021 | 2021Q4 | 2021 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-06-10 | N | 385.5917 | N | 5 | N | N | 1.1101 | 39.4971 | 2254.2321
[7 empty] | 3152 | 18830 | 1857312 | 2021-06-11 07:26 | 2021-06-11 10:33 | 186.7333 | 11kV | 373.4667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211087 No Cause Found (Not Storm Condition) 2 Amp, Single Phase, Line DOLF SOP ARLITSCH E DOP ROBERTSON D | June | 2021 | 2021Q4 | 2021 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2021-06-11 | N | 186.7333 | N | 4 | N | N | 1.1101 | 39.4971 | 272.9184
[7 empty] | 2076 | 4921 | 1857388 | 2021-06-11 10:20 | 2021-06-11 12:20 | 120 | 11kV | 8400 | 70 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | At S10823 The Avenure Westfield TX1 and TX2 RMCBs tripped due to RMCB 2 low Gas (Parallel tripping) See OMS 1858668 1858667 18587388 | June | 2021 | 2021Q4 | 2021 | ZN10993:PA26 | ZN10993:PA26 | ZN10993/000026 | GEORGES RIVER | UG | Not Veg | 2021-06-11 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 6138.4722
[7 empty] | 3144 | 18690 | 1857407 | 2021-06-11 14:10 | 2021-06-11 14:50 | 40 | 11kV | 1240 | 31 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 211089 Car hit pole SI-90927. Broken tie on pin insulator. RepAIRED UNDER AP. DOP O'BRIEN B SOP WATTERS L CC1: 06-"Urgent - O.H Mains - No others" | June | 2021 | 2021Q4 | 2021 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-06-11 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 906.1554
[7 empty] | 2898 | 14956 | 1857495 | 2021-06-11 17:01 | 2021-06-11 17:09 | 8 | 11kV | 10248 | 3300 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Cold <10C | N | ZN35400 NORTH SYDNEY 11kV Sect A & Sect B Busbar Interrupted due to Staff Error Abnormal: Tx No. 11 was being RTS Closed Pa63 'B-C' Bus Coupler Opened Pa55 'Tx11A' Refer to Steve Longhurst See 1858743,4 Ex 1857495 | June | 2021 | 2021Q4 | 2021 | ZN35400:PA53 | ZN35400:PA53 | ZN35400/000053 | NORTH SYDNEY | Unknown | Not Veg | 2021-06-11 | N | 3.1055 | N | 4 | N | N | 1.1101 | 39.4971 | 7488.9361
[7 empty] | 2505 | 10151 | 1857567 | 2021-06-12 09:00 | 2021-06-12 10:15 | 75 | 11kV | 29850 | 398 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7900 Campbell St Panel 14 has tripped on Relays: C phase OC and earth fault, Earth fault check and EFI Signals: 11kV TRip, TX2 Group Earth Cause: 11kV UG fault from SW/F at S6862 - SW/B @ S47148 | June | 2021 | 2021Q4 | 2021 | ZN7900:PA14 | ZN7900:PA14 | ZN07900/000014 | SYDNEY | UG | Not Veg | 2021-06-12 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 21813.4996
[7 empty] | 2256 | 6941 | 1857562 | 2021-06-12 08:32 | 2021-06-12 12:30 | 238 | 11kV | 18088 | 76 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT11644 Jenkins Emora Roadside HDO blwon Cause: Animals/bird See OMS 185643 1857562 1857563 | June | 2021 | 2021Q4 | 2021 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Not Veg | 2021-06-12 | N | 238 | N | 3 | N | N | 1.1101 | 39.4971 | 13218.1769
[7 empty] | 1807 | 1659 | 1857608 | 2021-06-12 11:20 | 2021-06-12 13:05 | 105 | 11kV | 84142 | 848 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S9900 Menai the 11kV panel 13 feeder tripped on Relays: B phase OC, TX2 group earth efi Cause: UGOH fault between S9254 SW/B and S9817 and S9667 See OMS 1858661 1858664 1857608 | June | 2021 | 2021Q4 | 2021 | ZN9900:PA13 | ZN9900:PA13 | ZN09900/000013 | SUTHERLAND | UG | Not Veg | 2021-06-12 | N | 99.2241 | N | 3 | N | N | 1.1101 | 39.4971 | 61488.4918
[7 empty] | 2598 | 11203 | 1857816 | 2021-06-14 06:05 | 2021-06-14 07:07 | 62 | 11kV | 4960 | 80 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 211093 31 Amp, Phase A, Substation DOLF Refer to OMS REPORT 1857816. FUSE FATIGUE. DOP WILKINSON J SOP MULVANEY G | June | 2021 | 2021Q4 | 2021 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2021-06-14 | N | 62 | N | 2 | N | N | 1.1101 | 39.4971 | 3624.6217
[7 empty] | 2840 | 14313 | 1857812 | 2021-06-13 23:30 | 2021-06-14 08:25 | 535 | 11kV | 2140 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211094 Re instated fuses after line patrol. Replaced 2 x blown hv 10 amp fuses at spur fuse 79031. (Roadside and middle phase). Supply restored at 0805 hrs. Cause unknown. SOP CARSON S DOP GEDDES S | June | 2021 | 2021Q4 | 2021 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2021-06-13 | N | 535 | N | 1 | N | N | 1.1101 | 39.4971 | 1563.8489
[7 empty] | 2027 | 4231 | 1857832 | 2021-06-14 09:07 | 2021-06-14 11:25 | 137.9167 | 11kV | 3310 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211095 Phase A SOP De VRIES M DOP BLACKADDER B CC1: 22-"Refer to SOp" | June | 2021 | 2021Q4 | 2021 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-06-14 | N | 137.9167 | N | 2 | N | N | 1.1101 | 39.4971 | 2418.8504
[7 empty] | 2757 | 13236 | 1857932 | 2021-06-15 05:10 | 2021-06-15 06:18 | 68 | 11kV | 45446 | 670 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | No Weather Impact | N | ZN12690 BERKELEY VALE 11kV CB Panel 17 fdr tripped Relays: OC & EF Relay led's flickering Signals: 11kv trip EFI: Nil Abnormal: LB40026 is closed with LB42262 open Cause: Protection malfunction SPAJ 140C Relay LED's flickering. Suspect Faulty Relay See 1858679 ex 1587932,3 | June | 2021 | 2021Q4 | 2021 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | Exclude | Not Veg | 2021-06-15 | N | 67.8299 | N | 3 | N | N | 1.1101 | 39.4971 | 33210.5964
[7 empty] | 3092 | 18037 | 1858074 | 2021-06-15 13:37 | 2021-06-15 15:30 | 113 | 11kV | 339 | 3 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex ZN12630 PEATS RIDGE section of 11kV Panel 10 PT12833 GEORGE DOWNES FERRY 0.4 Centre Phase HDO 20K Operated Cause: Possum caused centre phase HDO to operate See 1858671 ex 1858074 | June | 2021 | 2021Q4 | 2021 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2021-06-15 | N | 113 | N | 3 | N | N | 1.1101 | 39.4971 | 247.7312
[7 empty] | 2540 | 10557 | 1858082 | 2021-06-15 15:32 | 2021-06-16 01:45 | 613 | 11kV | 11034 | 18 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 211098 Car hit pole KT-40497 SECTION ISOLATED FOR REPAIRS. LVF 79460/2 ISOLATED. Excluded OMS 1858081 | June | 2021 | 2021Q4 | 2021 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2021-06-15 | N | 613 | N | 3 | N | N | 1.1101 | 39.4971 | 8063.3218
[7 empty] | 2391 | 8769 | 1858346 | 2021-06-16 17:39 | 2021-06-16 19:07 | 88 | 11kV | 15312 | 174 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S36800 Waverley Panel 14 tripped Cause: UG cable fault between S5372 to S3358 | June | 2021 | 2021Q4 | 2021 | ZN36800:PA47 | ZN36800:PA47 | ZN36800/000047 | WAVERLEY | UG | Not Veg | 2021-06-16 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 11189.558
[7 empty] | 2944 | 15790 | 1858337 | 2021-06-16 16:35 | 2021-06-16 19:35 | 180 | 11kV | 180 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211105 A phase DOLF : 10 Amp Faulty LA replaced Excluded OMS 1858337 | June | 2021 | 2021Q4 | 2021 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2021-06-16 | N | 180 | N | 4 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 2375 | 8607 | 1858350 | 2021-06-16 18:27 | 2021-06-16 19:40 | 73.0833 | 11kV | 5700.5 | 78 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At PT396 Donald St A phase TX connection HR. PT isolated on HV and LV and supply restored via LV parallel. | June | 2021 | 2021Q4 | 2021 | ZN1287:PA12 | ZN1287:PA12 | ZN01287/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-06-16 | N | 73.0833 | N | 4 | N | N | 1.1101 | 39.4971 | 4165.7573
[7 empty] | 2121 | 5350 | 1858385 | 2021-06-17 00:33 | 2021-06-17 01:49 | 76 | 11kV | 43032 | 580 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn15013 Terrey Hills Panel 10 HV bond blown at first UGOH on pole TH-7453. Abnormal: USL24212 Open, See OMS 1858551 1858385 | June | 2021 | 2021Q4 | 2021 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2021-06-17 | N | 74.1931 | N | 3 | N | N | 1.1101 | 39.4971 | 31446.5164
[7 empty] | 3122 | 18418 | 1858390 | 2021-06-17 00:44 | 2021-06-17 07:17 | 393 | 11kV | 43424 | 461 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN3472 SEFTON 11kV CB Panel 11 tripped and reclosed and locked out Relays: OC, EF, Minor alarm trip, EFI, Fault check and lock out Signals: Tx3 Group Earth and Group Earth EFI S3366 Cause: UG Fault from S3366 to S8148 to S4405 See 1858692 ex 1858390,1 | June | 2021 | 2021Q4 | 2021 | ZN3472:PA11 | ZN3472:PA11 | ZN03472/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-06-17 | N | 94.1952 | N | 3 | N | N | 1.1101 | 39.4971 | 31732.9784
[7 empty] | 2915 | 15216 | 1858483 | 2021-06-17 12:31 | 2021-06-17 19:20 | 409 | 11kV | 47740 | 280 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211108 Trees Blown onto Mains along shared driveways, wires on ground, near 4474 Great North Rd, Laguna Single Phase, Earth Fault SOP ARLITSCH E DOP JOHNS G | June | 2021 | 2021Q4 | 2021 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-06-17 | N | 170.5 | N | 3 | N | N | 1.1101 | 39.4971 | 34886.9839
[7 empty] | 2753 | 13204 | 1858778 | 2021-06-18 19:04 | 2021-06-18 20:51 | 107 | 11kV | 118703 | 1124 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN965 PENNANT HILLS 11kV CB Panel 4 'New Line Elabana' tripped and locked out Relays: A&B O/C, A&C IOC, Times OC, Lock out and EFI Signals: 11kv trip, Zone Earth and Tx1 Group Earth EFI: Cause: UG Fault Zn965 Pennant Hills Panel 4 Fron Line was DMA and had just been returned to service and was in service for less than an hour See 1859261 ex 1858778 | June | 2021 | 2021Q4 | 2021 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2021-06-18 | N | 105.6077 | N | 2 | N | N | 1.1101 | 39.4971 | 86744.6513
[7 empty] | 2811 | 13984 | 1858782 | 2021-06-18 19:34 | 2021-06-18 21:15 | 101 | 11kV | 8888 | 88 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Ex ZN35500 TOP RYDE section of 11kV Panel 26 PT1838 WICKS COX S HVDO fuse operated roadside phase 31.5 Amp Fuse Cause: Possum found on ground beside PT1838 See 1858783 Ex 1858782,5,6,7 | June | 2021 | 2021Q4 | 2021 | ZN35500:PA26 | ZN35500:PA26 | ZN35500/000026 | RYDE | OH | Not Veg | 2021-06-18 | N | 101 | N | 2 | N | N | 1.1101 | 39.4971 | 6495.0882
[7 empty] | 2750 | 13153 | 1858874 | 2021-06-19 12:39 | 2021-06-19 13:43 | 64 | 11kV | 576 | 9 | HV | Vandalism | 3rd Party Impact | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 211111 A Phase DOLF : 10 Amp Excluded OMS 1858874 | June | 2021 | 2021Q4 | 2021 | 801:74117 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | OH | Not Veg | 2021-06-19 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 2124 | 5399 | 1858934 | 2021-06-19 16:36 | 2021-06-19 16:44 | 8 | 11kV | 1768 | 221 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | Rain Heavy | N | ZN116 LEICHHARDT 11kV CB Panel 1 tripped on Relays: SEL Signals: 11kv trip Abnormal: S1530 SwA Closed. CP64632 SwA Open Cause: UG Fault After proving panel 7 at Leichardt with SEL on Panel 1 Auto, DOps closed SwA @ CP64632 Maritime Service No.3 to phase up spouts on Panel 7. fdr then tripped on SEL See 1859341 GIS 1858935 ex 1858934 | June | 2021 | 2021Q4 | 2021 | ZN116:PA1 | ZN116:PA1 | ZN00116/000001 | INNER WEST | Exclude | Not Veg | 2021-06-19 | N | 8 | N | 3 | N | N | 1.1101 | 39.4971 | 1292.0023
[7 empty] | 2260 | 6982 | 1858951 | 2021-06-19 17:29 | 2021-06-19 21:00 | 211 | 11kV | 1055 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN35370 GALSTON section of 11kV Panel 10 PT2108 DONS QUARRY 11kv centre phase HDO and 415V Dist 1 B phase fuse operated Cause: tree branch on oh mains See 1859346 ex 1858951 | June | 2021 | 2021Q4 | 2021 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2021-06-19 | N | 211 | N | 3 | N | N | 1.1101 | 39.4971 | 770.9629
[7 empty] | 1892 | 2746 | 1859046 | 2021-06-20 08:36 | 2021-06-20 09:31 | 55 | 11kV | 40645 | 739 | HV | Animal Other | Animal | Air Break Switch | Unplanned | Rain Heavy | N | ZN2196 MILPERRA 11kV CB Panel 26 tripped Relays: OC B & C Phase (Code 51 B+C) Signals: CB26 open, 11kv EFI Cause: 6th Avenue - Bin Chicken adjacent LB821 | June | 2021 | 2021Q4 | 2021 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-06-20 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 29702.1672
[7 empty] | 2921 | 15333 | 1859064 | 2021-06-20 14:15 | 2021-06-20 16:25 | 130 | 11kV | 1820 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 211115 & 211116 SECTION ISOLATED TO REPAIR BROKEN 11KV INSULATOR AT POLE OR-90320. Excluded OMS REPORT NO 1859064. | June | 2021 | 2021Q4 | 2021 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2021-06-20 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 1330.0023
[7 empty] | 2282 | 7231 | 1859057 | 2021-06-20 09:12 | 2021-06-20 17:15 | 483 | 11kV | 254290 | 2411 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 211114 1 fault operation 3 phase Earth Fault HV into LV. 11kv main down at pole JU-61666. Excluded oms 1859060, 1859059, 1859061, 1859057. | June | 2021 | 2021Q4 | 2021 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2021-06-20 | N | 105.4708 | N | 4 | N | N | 1.1101 | 39.4971 | 185827.6317
[7 empty] | 2450 | 9509 | 1859123 | 2021-06-20 13:34 | 2021-06-20 21:40 | 486 | 11kV | 253862 | 1581 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 211117 1 fault operation Sensitive Earth Fault faulty 11kv insulators at pole KT-40828 & faulty ugoh pole KT-10007 Excluded oms 1859123 | June | 2021 | 2021Q4 | 2021 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2021-06-20 | N | 160.5705 | N | 4 | N | N | 1.1101 | 39.4971 | 185514.8619
[7 empty] | 2911 | 15174 | 1859195 | 2021-06-21 04:34 | 2021-06-21 12:55 | 501 | 11kV | 261920 | 1676 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ZN10993 HURSTVILLE NORTH 11kV CB Panel 23 'Lyle St' fdr tripped, reclosed and tripped on: Relays: B+C Phase OC, EFI, Reclose, Timing EFI: Nil Cause: Possum found on 11kV adjacent Pole KO7636 section of 11kv OH fdr from LB62431 to AB31016 tee S63007 SwA See 1859784,5,6,7,8,9 Ex 1859195,221 | June | 2021 | 2021Q4 | 2021 | ZN10993:PA23 | ZN10993:PA23 | ZN10993/000023 | BAYSIDE | OH | Not Veg | 2021-06-21 | N | 156.2768 | N | 3 | N | N | 1.1101 | 39.4971 | 191403.4107
[7 empty] | 1930 | 3155 | 1859318 | 2021-06-21 11:35 | 2021-06-21 14:45 | 190 | 11kV | 190 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211122 Single phase DOLF : 10 Amp Excluded OMS 1859318 | June | 2021 | 2021Q4 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-06-21 | N | 190 | N | 3 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 2219 | 6573 | 1859365 | 2021-06-21 13:30 | 2021-06-21 15:05 | 95 | 11kV | 15010 | 158 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211123 Isolated 11kV section to repair faulty dead end at pole JU-73609. Excluded oms 1859365 | June | 2021 | 2021Q4 | 2021 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2021-06-21 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 10968.8653
[7 empty] | 2659 | 11855 | 1859821 | 2021-06-22 07:43 | 2021-06-22 07:54 | 11 | 11kV | 11 | 1 | HV | 3rd Party Action | 3rd Party Impact | 3rd Party Asset | Unplanned | No Weather Impact | N | ZN188 ZETLAND 11kV CB Panel 46 tripped on: Relays: Earth Fault with fault check Signals: 11kv trip with EFI EFI: Nil Abnormal: S5357 SwC Closed SwD Open Cause: customer installation. Customer closed onto Earth on their system while switching NAR75380 | June | 2021 | 2021Q4 | 2021 |  |  |  | SYDNEY | Unknown | Not Veg | 2021-06-22 | N | 11 | N | 3 | N | N | 1.1101 | 39.4971 | 8.0385
[7 empty] | 3210 | 19500 | 1859540 | 2021-06-22 08:55 | 2021-06-22 10:05 | 70 | 11kV | 19180 | 274 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN12690 BERKELEY VALE section of 11kV Panel 6 USL43476 11kV Bond Burnt off below tee off to PT13418 See 1859824 ex 1859535 | June | 2021 | 2021Q4 | 2021 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2021-06-22 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 14016.1783
[7 empty] | 1820 | 1840 | 1859671 | 2021-06-22 15:30 | 2021-06-22 17:25 | 115 | 11kV | 230 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211125 A Phase DOLF : 10 Amp Blown DOLF Excluded OMS 1859671 | June | 2021 | 2021Q4 | 2021 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2021-06-22 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 2394 | 8820 | 1859739 | 2021-06-23 05:20 | 2021-06-23 07:50 | 150.1 | 11kV | 3002 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211127 B & C Phase DOLF : 20 Amp | June | 2021 | 2021Q4 | 2021 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2021-06-23 | N | 150.1 | N | 5 | N | N | 1.1101 | 39.4971 | 2193.7731
[7 empty] | 2380 | 8645 | 1859811 | 2021-06-23 10:39 | 2021-06-23 12:00 | 81 | 11kV | 114240 | 2089 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211128 Magpie across mains pole IR-41135 Excluded oms 1859811, 1859814 & 1859826 | June | 2021 | 2021Q4 | 2021 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2021-06-23 | N | 54.6865 | N | 5 | N | N | 1.1101 | 39.4971 | 83483.2225
[7 empty] | 2352 | 8252 | 1859773 | 2021-06-23 08:40 | 2021-06-23 14:55 | 375 | 11kV | 36335 | 98 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex ZN12570 AVOCA section of 11kV Panel 21 from S14890 SwB to S14356 SwA tee to S14354 SwA to CP44545 interrupted for ermegency safety repairs Cause: Vehicle hit pole. Car hit pole WL438 requires replacement. See 1860034,5 Ex 1859773,4 | June | 2021 | 2021Q4 | 2021 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2021-06-23 | N | 370.7653 | N | 5 | N | N | 1.1101 | 39.4971 | 26552.5463
[7 empty] | 1858 | 2320 | 1859896 | 2021-06-23 11:11 | 2021-06-23 17:15 | 364 | 11kV | 48643 | 150 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211130 Faulted LA leads between incoming & outgoing phases at RAGCB 42060 Excluded OMS 1859823 & 1859896 | June | 2021 | 2021Q4 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2021-06-23 | N | 324.2867 | N | 5 | N | N | 1.1101 | 39.4971 | 35546.8697
[7 empty] | 2173 | 5905 | 1861093 | 2021-06-23 16:00 | 2021-06-23 18:20 | 140 | 11kV | 560 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 211132 Tripped after return of oms 1858378. Sw 74812 to Sw 74815 all on at 18:20. Excluded oms 1859899 & 1860230 | June | 2021 | 2021Q4 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-06-23 | N | 140 | N | 5 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 2980 | 16331 | 1859966 | 2021-06-24 08:17 | 2021-06-24 08:39 | 22 | 11kV | 28006 | 1273 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN1193 LINDFIELD 11kV CB Panel 20 Based on customer calls and recorded loads on Panel 20. No recorded trip or Open operation on ZN1193 Lindfield Panel 20. Abnormal: CP2303 closed, S4625SwB Closed, S5124SwA Open, S47451SwA Open See 1860841 ex 1859966 | June | 2021 | 2021Q4 | 2021 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2021-06-24 | N | 22 | N | 5 | N | N | 1.1101 | 39.4971 | 20465.9588
[7 empty] | 2569 | 10826 | 1860562 | 2021-06-24 08:50 | 2021-06-24 09:55 | 65 | 11kV | 65 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | ZN263 DALLEY ST 11kV CB Panel 31/32E fdr CB tripped on Relays: BZ Signals: 11kv trip S77846 Bligh Hunter temp 1 Relays: ITR Send Cause: failed on energising. Fdr tripped on energising 21 E Tx NAR77217. 31/32E fdr restored @9:41 See 1860563 GIS 1860562 | June | 2021 | 2021Q4 | 2021 |  |  |  | SYDNEY | UG | Not Veg | 2021-06-24 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 2198 | 6266 | 1859963 | 2021-06-24 08:17 | 2021-06-24 10:00 | 103 | 11kV | 7931 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN195 PYMBLE section of 11kV Panel 30 Re46113 Fiddens Wharf Coronga tripped on SEF locked out Abnormal: AB2303 Closed, S47451 SwA Open Cause nto ascertained. DOp patrolled fdr and checked all Subs and PT off the network See 1860593 ex 1859963,7,82,8 | June | 2021 | 2021Q4 | 2021 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2021-06-24 | N | 103 | N | 5 | N | N | 1.1101 | 39.4971 | 5795.7409
[7 empty] | 2504 | 10145 | 1850002 | 2021-06-24 07:30 | 2021-06-24 13:25 | 355 | 11kV | 6261 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211135 2 fault operations Single phase Overcurrent tree brought down mains adj pole 7E-90035 Excluded oms 1859972 | June | 2021 | 2021Q4 | 2021 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-06-24 | N | 208.7 | N | 5 | N | N | 1.1101 | 39.4971 | 4575.3541
[7 empty] | 1753 | 950 | 1858378 | 2021-06-16 22:23 | 2021-06-24 17:45 | 11242 | 11kV | 183378 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 211107 Sw 74812 found open . DOLF replaced sub 17938. Mains down pole EF-60070 Excluded OMS 1858378. | June | 2021 | 2021Q4 | 2021 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-06-16 | N | 7335.12 | N | 4 | N | N | 1.1101 | 39.4971 | 134007.2337
[7 empty] | 2799 | 13846 | 1860152 | 2021-06-24 16:03 | 2021-06-24 20:30 | 266.6833 | 11kV | 3733.5667 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211136 1 fault operation A Phase Overcurrent Adam Pople understands some strong winds and small localised storm occured earlier this afternoon, could not find cause of fault. | June | 2021 | 2021Q4 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-06-24 | N | 266.6833 | N | 5 | N | N | 1.1101 | 39.4971 | 2728.3804
[7 empty] | 2032 | 4394 | 1860271 | 2021-06-25 11:06 | 2021-06-25 17:40 | 394 | 11kV | 130506 | 824 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211141 Tapping broken at ABS 40044 Excluded oms 1860271 | June | 2021 | 2021Q4 | 2021 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-06-25 | N | 158.3811 | N | 1 | N | N | 1.1101 | 39.4971 | 95369.9355
[7 empty] | 3024 | 17013 | 1860399 | 2021-06-26 12:45 | 2021-06-26 14:51 | 126 | 11kV | 126 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211143 No fuse or preotection operated burnt off LLC Excluded OMS 1860399 | June | 2021 | 2021Q4 | 2021 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-06-26 | N | 126 | N | 2 | N | N | 1.1101 | 39.4971 | 92.0771
[7 empty] | 3218 | 19591 | 1860421 | 2021-06-26 18:04 | 2021-06-26 19:47 | 103 | 11kV | 115463 | 1121 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN1610 HOMEBUSH BAY 11kV CB Panel 19 tripped on Relays: Earth Fault, EFI Signals: Tx2 Group Earth, 11kv trip EFI: S36068 S6305 S3019 S4804 S4819 S6307 Cause: UG fault 11kv fdr defective from Zn1610 Homebush Bay Panel 19 to S36068 SwA. Multiple EFI found down with no apparent cause | June | 2021 | 2021Q4 | 2021 | ZN1610:PA19 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2021-06-26 | N | 103 | N | 2 | N | N | 1.1101 | 39.4971 | 84376.9548
[7 empty] | 3229 | 19647 | 1860444 | 2021-06-27 07:07 | 2021-06-27 09:10 | 123 | 11kV | 9840 | 80 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211147 B Phase DOLF : 63 Amp SURGE ARRESTOR ON B PHSE FAILED BLOWING DOLF ALL THREE SURGE ARRESTORS REPLACED. Excluded OMS 1860444 | June | 2021 | 2021Q4 | 2021 | 522:83129 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Not Veg | 2021-06-27 | N | 123 | N | 2 | N | N | 1.1101 | 39.4971 | 7190.7818
[7 empty] | 2938 | 15625 | 1860509 | 2021-06-27 19:36 | 2021-06-27 20:35 | 59 | 11kV | 118 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 211149 suspect fuse element overtightened previously. Excluded oms 1860509 | June | 2021 | 2021Q4 | 2021 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-06-27 | N | 59 | N | 2 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 2499 | 10108 | 1860574 | 2021-06-28 09:54 | 2021-06-28 11:30 | 96 | 11kV | 90624 | 944 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S 10998 Rockdale 11kv panel No 19 tripped on- Relays-A prot panel: SEL 751A relay- Trip A, A + C phase, Neutral, IOC B prot panel: Micom P142 relay- Trip, alarm, IOC, EFI Cause: 11kV UG front line fault from S10998 Rockdale to Pa19 to AB31209 | June | 2021 | 2021Q4 | 2021 | ZN10998:PA19 | ZN10998:PA19 | ZN10998/000019 | BAYSIDE | UG | Not Veg | 2021-06-28 | N | 96 | N | 1 | N | N | 1.1101 | 39.4971 | 66225.3462
[7 empty] | 3125 | 18424 | 1860755 | 2021-06-29 05:03 | 2021-06-29 06:32 | 89 | 11kV | 174519 | 2015 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN690 CAMPSIE 11kV CB Panel 12 tripped on Relays: IO OC B & C Phase, TImed OC C Phase, EFI, Fault Check Signals: 11kv trip, Zone Earth, Tx2 Group Earth EFI: Nil Cause: UG Fault in frontline section of 11kv fdr between Zn690 Campsie Panel 12 and S266 See 1861070,1 Ex 1860755 | June | 2021 | 2021Q4 | 2021 | ZN690:PA12 | ZN690:PA12 | ZN00690/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-06-29 | N | 86.6099 | N | 3 | N | N | 1.1101 | 39.4971 | 127533.3378
[7 empty] | 2181 | 6054 | 1860756 | 2021-06-29 05:46 | 2021-06-29 06:45 | 59 | 11kV | 4779 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN36200 EMPIRE BAY section of 11kV Panel 8 PT13215 POMONA WARDS HILL 31.5K HDO footpath phase blown Cause: tree branch contact other Twig on bushing See 1861073 ex 1860756,60 | June | 2021 | 2021Q4 | 2021 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2021-06-29 | N | 59 | N | 3 | N | N | 1.1101 | 39.4971 | 3492.3522
[7 empty] | 2752 | 13172 | 1860854 | 2021-06-29 12:19 | 2021-06-29 15:41 | 202 | 11kV | 39996 | 198 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | Ex ZN12580 ERINA section of 11kV Panel 4 Section Between LB41764 to AB41763 tee PT11847 PT12453 PT11621 interrupted for safety Emergency repair to pin insulator See 1861078 ex 1860854 | June | 2021 | 2021Q4 | 2021 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2021-06-29 | N | 202 | N | 3 | N | N | 1.1101 | 39.4971 | 29227.8971
[7 empty] | 2870 | 14595 | 1860980 | 2021-06-30 07:08 | 2021-06-30 08:10 | 62 | 11kV | 186 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211156 Single phase DOLF : 10 Amp Excluded OMS 1860980 | June | 2021 | 2021Q4 | 2021 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Veg | 2021-06-30 | N | 62 | N | 6 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 1995 | 3779 | 1860977 | 2021-06-30 06:44 | 2021-06-30 08:15 | 91 | 11kV | 10647 | 117 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211157 B Phase DOLF : 31 Amp Excluded OMS 1860978 | June | 2021 | 2021Q4 | 2021 | 258:80781 | 258:80781 | ZN00258/080781 | NEWCASTLE | OH | Veg | 2021-06-30 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 7780.5136
[7 empty] | 2049 | 4651 | 1861015 | 2021-06-30 09:16 | 2021-06-30 13:00 | 224 | 11kV | 896 | 4 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex ZN14891 WYONG section of 11kV Panel 12 PT13288 BUNNING CK YARRA 2.4 A & B Phase 10k HDO Cause: tree branch contact - other Twig on arrestors See 1861404 ex 1861015 | June | 2021 | 2021Q4 | 2021 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2021-06-30 | N | 224 | N | 6 | N | N | 1.1101 | 39.4971 | 654.7704
[7 empty] | 1887 | 2688 | 1860970 | 2021-06-30 03:05 | 2021-06-30 14:35 | 690 | 11kV | 36876 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211155 Tree brought down mains adj to pole 9T-60002 Excluded OMS 1860970 | June | 2021 | 2021Q4 | 2021 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-06-30 | N | 376.2857 | N | 6 | N | N | 1.1101 | 39.4971 | 26947.8931
[7 empty] | 2336 | 8091 | 1861172 | 2021-06-30 18:36 | 2021-06-30 19:57 | 81 | 11kV | 3888 | 48 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211161 A Phase Faulty D clamp at sub Excluded oms 1861172 | June | 2021 | 2021Q4 | 2021 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2021-06-30 | N | 81 | N | 6 | N | N | 1.1101 | 39.4971 | 2841.2357
[7 empty] | 3216 | 19565 | 1861181 | 2021-06-30 23:00 | 2021-07-01 00:15 | 75 | 11kV | 7050 | 94 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211162 subs isolated to repair D clamp at sub 13852 Excluded OMS 1861198 | June | 2021 | 2021Q4 | 2021 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2021-06-30 | N | 75 | N | 6 | N | N | 1.1101 | 39.4971 | 5151.9321
[7 empty] | 467 | 5732 | 1861235 | 2021-07-01 08:27 | 2021-07-01 12:15 | 228 | 11kV | 228 | 1 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211165 Refer to OMS 1861241 & 1861235 LV cable faulty between Tx & LVF. Intermittent supply SOP APPS S DOP PASCOE D | July | 2021 | 2022Q1 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-07-01 | N | 228 | N | 3 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 1185 | 14772 | 1861437 | 2021-07-01 19:53 | 2021-07-01 21:05 | 72 | 11kV | 29160 | 405 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | ZN847 HORNSBY 11kV CB Panel 14 'S8506 King Salisbury' tripped Relays: B&C phase IOC, EFI, Fault check Signals: Tx1 Group Earth, ZOne Earth, 11kv trip, CB14 Open EFI: S8506 S8556 Cause: AIr Breack switch Normally Open AB1714 failed explosively. Requires replacement | July | 2021 | 2022Q1 | 2022 | ZN847:PA14 | ZN847:PA14 | ZN00847/000014 | HORNSBY | OH | Not Veg | 2021-07-01 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 21309.2679
[7 empty] | 1289 | 15700 | 1861274 | 2021-07-01 09:18 | 2021-07-01 23:59 | 881 | 11kV | 119511 | 1130 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN1193 LINDFIELD 11kV CB Panel 27 'tripped and reclosed and locked out: Signals: 11kv trip, T4 Group Earth Realys: Earth Fault, EFI, Reclose Lockout EFI: Cause: Vehicle hit mains. Truck brought down 11kv mains outside 72 Tryon Rd, East Lindifeld See 1861508,9,10 Ex 1861259 | July | 2021 | 2022Q1 | 2022 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2021-07-01 | N | 105.7619 | N | 3 | N | N | 1.1101 | 39.4971 | 87335.1138
[7 empty] | 817 | 10115 | 1861558 | 2021-07-02 13:13 | 2021-07-02 14:14 | 61 | 11kV | 67405 | 1105 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3425 Castle Cove - Pnl.22 tripped on: O/C UG cable fault between S3538 Sw/B and S49097 Sw/A | July | 2021 | 2022Q1 | 2022 | ZN3425:PA22 | ZN3425:PA22 | ZN03425/000022 | WILLOUGHBY | UG | Not Veg | 2021-07-02 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 49257.5859
[7 empty] | 681 | 8692 | 1861633 | 2021-07-02 17:52 | 2021-07-02 22:50 | 298 | 11kV | 68297 | 1209 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211169 Feeder opend at Sw 19071 due to HV mains beign reported within touch from the crowd. Tree trimming work damaged the line on the tee to sub 61995. 11kV Link 75072 C phase link replaced was reported glowing. Excluded OMS 1861633 | July | 2021 | 2022Q1 | 2022 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2021-07-02 | N | 56.4905 | N | 2 | N | N | 1.1101 | 39.4971 | 49909.4332
[7 empty] | 1535 | 18852 | 1861797 | 2021-07-04 08:38 | 2021-07-04 10:00 | 82 | 11kV | 5494 | 67 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT14000 Japoica Gorokan - HDO fuse operated on C phase Cockatoo across C phase 11kV bushing. | July | 2021 | 2022Q1 | 2022 | ZN14892:PA21 | ZN14892:PA21 | ZN14892/000021 | CENTRAL COAST | OH | Not Veg | 2021-07-04 | N | 82 | N | 5 | N | N | 1.1101 | 39.4971 | 4014.8532
[7 empty] | 1055 | 13508 | 1861844 | 2021-07-04 14:17 | 2021-07-04 18:41 | 264 | 11kV | 54638 | 429 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC45189 Cook Peats Ridge 0.5 tripped on OC Cause not ascertained after Dop patrol See 1862147 1862148 | July | 2021 | 2022Q1 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-07-04 | N | 127.3613 | N | 5 | N | N | 1.1101 | 39.4971 | 39927.8389
[7 empty] | 35 | 420 | 1861858 | 2021-07-04 17:45 | 2021-07-04 19:08 | 83 | 11kV | 135532 | 1682 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211175 Burnt off tapping 11kV Links 19255 Repairs completed Excluded OMS 1861858 | July | 2021 | 2022Q1 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2021-07-04 | N | 80.5779 | N | 5 | N | N | 1.1101 | 39.4971 | 99042.7881
[7 empty] | 362 | 4909 | 1861812 | 2021-07-04 12:06 | 2021-07-04 19:10 | 424 | 11kV | 21624 | 51 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211174 Large tree on stay wire for pole HR-33321 Sobies Lane Maitland section isolated for repairs. Excluded oms 1861812 | July | 2021 | 2022Q1 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2021-07-04 | N | 424 | N | 5 | N | N | 1.1101 | 39.4971 | 15802.1814
[7 empty] | 661 | 8521 | 1861891 | 2021-07-04 22:22 | 2021-07-04 23:23 | 61.0833 | 11kV | 6230.5 | 102 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211177 Dead possum found at PT Excluded OMS 1861891 | July | 2021 | 2022Q1 | 2022 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Not Veg | 2021-07-04 | N | 61.0833 | N | 5 | N | N | 1.1101 | 39.4971 | 4553.0656
[7 empty] | 1486 | 18336 | 1861956 | 2021-07-05 09:27 | 2021-07-05 20:20 | 653 | 11kV | 41992 | 629 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | ZN188 ZETLAND 11kV CB Panel 2 'S5974 McEvoy' fdr tripped on Signals: 11kv trip, No.1 Group Earth, Zone Earth Relays: Earth Fault, Fault Check, EFI Cause: RMI failure @ S5974 McEvoy Elizabeth See 1862390,2,3,4 Ex 1861956,2068 | July | 2021 | 2022Q1 | 2022 | ZN188:PA2 | ZN188:PA2 | ZN00188/000002 | SYDNEY | Unknown | Not Veg | 2021-07-05 | N | 66.7599 | N | 1 | N | N | 1.1101 | 39.4971 | 30686.515
[7 empty] | 419 | 5299 | 1862257 | 2021-07-06 13:48 | 2021-07-06 15:18 | 90 | 11kV | 12572 | 140 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN14143 SOMERSBY 11kV CB Panel 21 'Somersby' fdr tripped on: Earth Fault C Phase to Neutral, EFI EFI: S18108 Cause: UG Fault 11kV fdr fault in cable from S18108:B to S18052:A See 1862444,5 Ex 1862257 | July | 2021 | 2022Q1 | 2022 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | UG | Not Veg | 2021-07-06 | N | 89.8 | N | 3 | N | N | 1.1101 | 39.4971 | 9187.2468
[7 empty] | 865 | 10703 | 1862416 | 2021-07-06 12:40 | 2021-07-06 16:05 | 205 | 11kV | 11255 | 56 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211181 1 fault operation Sw 61176 tripped when closing ABS 62973 as part of NAR 77426 restoration. Excluded OMS 1862263 | July | 2021 | 2022Q1 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2021-07-06 | N | 200.9821 | N | 3 | N | N | 1.1101 | 39.4971 | 8224.822
[7 empty] | 1413 | 17405 | 1862191 | 2021-07-06 10:14 | 2021-07-06 16:15 | 361 | 11kV | 1444 | 4 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 211182 Single phase LLC burnt of at Tee off pole 8K-60300 affecting supply to 3 subs. Excluded OMS 1862191 | July | 2021 | 2022Q1 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-07-06 | N | 361 | N | 3 | N | N | 1.1101 | 39.4971 | 1055.2326
[7 empty] | 482 | 5855 | 1862350 | 2021-07-07 07:50 | 2021-07-07 08:49 | 59 | 11kV | 45831 | 779 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211189 Cloudy day Solar and customer loads jumped by 35 to 40 amps.. Extra load shift required during Nar 75160. Ambornally switched as per Nar 75160 step 21 completed Overload Phase B & C, Overcurrent Also refer to oms 1862350 1862353. SOP CARSON S DOP McINTOSH G | July | 2021 | 2022Q1 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-07-07 | N | 58.8331 | N | 1 | N | N | 1.1101 | 39.4971 | 33491.943
[7 empty] | 1252 | 15233 | 1862569 | 2021-07-08 04:46 | 2021-07-08 07:46 | 180 | 11kV | 155821 | 1544 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | Zn36300 Balgowlah North - Pnl.8 tripped, reclosed & tripped on: IOC & OC @LB61269 - ABC phase OC detection, EF detection Possible UG cable fault. See 1862798 1862800 1862804 | July | 2021 | 2022Q1 | 2022 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | UG | Not Veg | 2021-07-08 | N | 100.9203 | N | 4 | N | N | 1.1101 | 39.4971 | 113869.3909
[7 empty] | 556 | 6869 | 1862617 | 2021-07-08 09:52 | 2021-07-08 11:34 | 102 | 11kV | 177078 | 1876 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.22 tripped on: A Phase OC Damien from Mainmark was doing chemical underpinning and drilled though 11kV cable. See also outage to Pnl.2 See 1862822 1862823 | July | 2021 | 2022Q1 | 2022 | ZN1610:PA22 | ZN1610:PA22 | ZN01610/000022 | PARRAMATTA | UG | Not Veg | 2021-07-08 | N | 94.3913 | N | 4 | N | N | 1.1101 | 39.4971 | 129403.3795
[7 empty] | 1307 | 15923 | 1862596 | 2021-07-08 08:45 | 2021-07-08 14:24 | 339.5167 | 11kV | 339.5167 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 211191 Substation DOLF Tx fault. replace tank. Note:Field staff mentioned customer said power went out at 12.30 in the night. but didnt call in until 0844 as per oms. SOP CARSON S DOP FRAZER J | July | 2021 | 2022Q1 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-07-08 | N | 339.5167 | N | 4 | N | N | 1.1101 | 39.4971 | 248.1088
[7 empty] | 266 | 3444 | 1862926 | 2021-07-09 15:16 | 2021-07-09 17:15 | 118.9 | 11kV | 5350.5 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211194 B Phase DOLF : 50 Amp excluded OMS 1862933 CC1: 11-"Despatch to re-issue" | July | 2021 | 2022Q1 | 2022 | 513:83504 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Veg | 2021-07-09 | N | 118.9 | N | 1 | N | N | 1.1101 | 39.4971 | 3909.9876
[7 empty] | 1393 | 17082 | 1862616 | 2021-07-08 09:53 | 2021-07-09 18:30 | 1957 | 11kV | 69958 | 612 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S1610 Homebush Bay Panel 2 Tripped on Relays: A phase OC and Earth Fault Signals: Trip Cause: Damian from Mainmark was doing chemical underpinning and drilled through and 11kV cable Note: Jointer advises that cable runs uinder large brick wall, extremely difficult and time consuming repair. Will not be done until the afternoon/night of Friday 09/07. See OMS 1863425 1863428 1862616 1862681 | July | 2021 | 2022Q1 | 2022 | ZN1610:PA2 | ZN1610:PA2 | ZN01610/000002 | PARRAMATTA | UG | Not Veg | 2021-07-08 | N | 114.3105 | N | 4 | N | N | 1.1101 | 39.4971 | 51123.243
[7 empty] | 742 | 9381 | 1863118 | 2021-07-10 15:19 | 2021-07-10 15:52 | 33 | 11kV | 28050 | 850 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12570 Avoca 11kV Panel 34 tripped, rec;losed and tripped on Relauys: A and B phase OC, AR Lockout Signals: CB34 Open, CB 34 CLosed, CB34 Open, CB34 AR lockout Field EFIs: Nil Cause: Tree branch on OH mains - Surf Rider Ave near Easter Pde North Avoca | July | 2021 | 2022Q1 | 2022 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2021-07-10 | N | 33 | N | 2 | N | N | 1.1101 | 39.4971 | 20498.1127
[7 empty] | 352 | 4818 | 1863109 | 2021-07-10 14:39 | 2021-07-10 16:30 | 111 | 11kV | 134974 | 1665 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35555 Croydon the 11kV panel 20 has tripped on RelaysL 50TN, EFI Cause: UG fault - 11kV UG fault from S49765 Allum St No1 - SW/A to S6318 Wolsley Parra SW/B tee S1907 Tiana St 1863439 1863440 1863109 | July | 2021 | 2022Q1 | 2022 | ZN35555:PA20 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | UG | Not Veg | 2021-07-10 | N | 81.0655 | N | 2 | N | N | 1.1101 | 39.4971 | 98635.0181
[7 empty] | 1040 | 13277 | 1863164 | 2021-07-11 05:57 | 2021-07-11 08:35 | 158 | 11kV | 948 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At PT14507 Arundel Milina 11kV Centre Phase HDO Operated Cause not ascertained for outage See OMS 1863497 1863164 1863167 | July | 2021 | 2022Q1 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-07-11 | N | 158 | N | 2 | N | N | 1.1101 | 39.4971 | 692.7704
[7 empty] | 304 | 3915 | 1863234 | 2021-07-11 15:22 | 2021-07-11 17:11 | 109 | 11kV | 74305 | 923 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1068 Lidcombe Panel 17 tripped on Relays: EF, OC, EFI Signals: Zone Earth, TX3 Group Earth Cause: 11kV UG fault between S65271 - S5490 - S2663 See OMS 1863485 1863486 1863234 1863235 | July | 2021 | 2022Q1 | 2022 | ZN1068:PA17 | ZN1068:PA17 | ZN01068/000017 | CUMBERLAND | UG | Not Veg | 2021-07-11 | N | 80.5038 | N | 2 | N | N | 1.1101 | 39.4971 | 54299.9024
[7 empty] | 1628 | 19720 | 1863577 | 2021-07-13 07:18 | 2021-07-13 09:05 | 107 | 11kV | 107 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211204 C Phase DOLF : 10 Amp Excluded OMS 1863577 | July | 2021 | 2022Q1 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2021-07-13 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 78.1924
[7 empty] | 471 | 5762 | 1863636 | 2021-07-13 10:00 | 2021-07-13 15:30 | 330 | 11kV | 9240 | 28 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 12 from LK40827 to AL4476 Brush Creek Cause: tree trimming in area NAR77505 for contract tree trimming has been extended due to tree on 11kv OH. interrupted for safety and repair. | July | 2021 | 2022Q1 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2021-07-13 | N | 330 | N | 4 | N | N | 1.1101 | 39.4971 | 6752.3195
[7 empty] | 395 | 5143 | 1863703 | 2021-07-13 14:42 | 2021-07-13 15:32 | 50 | 11kV | 350 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 211208 Section isolated for repair of broken dolf sub 17411. Excluded OMS 1863703 | July | 2021 | 2022Q1 | 2022 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2021-07-13 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 779 | 9815 | 1863708 | 2021-07-13 15:55 | 2021-07-13 18:15 | 140 | 11kV | 30940 | 221 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex ZN12610 LONG JETTY section of 11kV Panel 20 HV fdr isolated & earthed from AB45005 to LB41104 to LB61289 tee PT11163 PT46128 PT11026 Abnormal: LK41500 open (DMA), RE45000 open and DMA, LB61289 Cause: Pole Defective Failure Broken LV Cross arm outside 23 Tumbi Umbi. at pole BV2517, HV required out of service, could not be switched due to DMA USL LK41500, PT11163 & PT46128 interrupted. AP and CTW issued @1630 See 1864122 ex 1863708,12,28,30,5,53 | July | 2021 | 2022Q1 | 2022 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2021-07-13 | N | 140 | N | 4 | N | N | 1.1101 | 39.4971 | 22610.0394
[7 empty] | 754 | 9483 | 1863804 | 2021-07-14 04:23 | 2021-07-14 05:28 | 65 | 11kV | 29185 | 449 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn36000 Olympic Park Panel 10 Trippe donb A Relays: IOC, C phase OC, Neutralk< Trip B Relays: IOOC, C phase OC, EFI and Trip Field EFI's Nil Cause: Suspect Excavation damagaed by company - Twin Connect On Australia Avenue | July | 2021 | 2022Q1 | 2022 | ZN36000:PA10 | ZN36000:PA10 | ZN36000/000010 | STRATHFIELD | UG | Not Veg | 2021-07-14 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 21327.5372
[7 empty] | 397 | 5149 | 1863852 | 2021-07-14 11:25 | 2021-07-14 14:18 | 173 | 11kV | 1211 | 7 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211212 broken x-arm replaced under permit. No trip. Excluded OMS 1863852 | July | 2021 | 2022Q1 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-07-14 | N | 173 | N | 5 | N | N | 1.1101 | 39.4971 | 884.9631
[7 empty] | 1352 | 16506 | 1863919 | 2021-07-14 14:49 | 2021-07-14 17:15 | 146 | 11kV | 292 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Heavy | N | Ex ZN14891 WYONG section of 11kV Panel 5 PT14855 DICKSONS DURREN 1.1 road side HDO blown and surge arrestors blown. Surge arrestors cut away by DOp See separate trip and reclose from RE45083 See 1864162 ex 1863919 | July | 2021 | 2022Q1 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2021-07-14 | N | 146 | N | 5 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 1125 | 14254 | 1863911 | 2021-07-14 16:12 | 2021-07-14 17:55 | 103 | 11kV | 103 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211215 11kV OHM broken away from termination crossarm at pole HR-52009. Excluded OMS No. 1863911 | July | 2021 | 2022Q1 | 2022 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2021-07-14 | N | 103 | N | 5 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 944 | 11453 | 1864015 | 2021-07-14 21:59 | 2021-07-14 23:10 | 71 | 11kV | 994 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211216 C Phase DOLF : 10 Amp excluded OMS 1864015 | July | 2021 | 2022Q1 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-07-14 | N | 71 | N | 5 | N | N | 1.1101 | 39.4971 | 726.3859
[7 empty] | 1099 | 13979 | 1864282 | 2021-07-16 11:37 | 2021-07-16 11:51 | 14 | 11kV | 3528 | 252 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN630 MASCOT 11kV CB Panel 24 'Birmingham Ellis' fdr tripped on: Relays: EFI, B Phase OC Signals: Tx3 Group Earth, 11kV trip EFI: S8459 S49580 S7766 S77507 S64258 Abnormal: Open S62458/SwB Open S7937/SwA Closed S8678/SwB Cause: Failed on energising. Existing fault between S64285 SwB to S7937 SwA failed on energizing See 1865494 ex 1864282 | July | 2021 | 2022Q1 | 2022 | ZN630:PA24 | ZN630:PA24 | ZN00630/000024 | SYDNEY | UG | Not Veg | 2021-07-16 | N | 14 | N | 13 | N | N | 1.1101 | 39.4971 | 2578.1583
[7 empty] | 621 | 7994 | 1864265 | 2021-07-16 10:46 | 2021-07-16 12:07 | 81 | 11kV | 29970 | 370 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN35370 GALSTON 11kV CB Panel 2 fdr tripped, reclosed and tripped on: Relays: 51AC (OC A and C phase) EFI: Nil Cause: Tree/Branch on OH Mains Tree Branch on OH mains adjacent to LLC's near PT2110 | July | 2021 | 2022Q1 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2021-07-16 | N | 81 | N | 13 | N | N | 1.1101 | 39.4971 | 21901.192
[7 empty] | 332 | 4543 | 1864255 | 2021-07-16 11:05 | 2021-07-16 12:30 | 85 | 11kV | 5865 | 69 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | PT12592 ILUKA LIAMENA 11kV/415V tx bond is burnt up and gone high resistance. Dist 1 and Dist 2 A Phase opened by EMSO See 1865481 Ex 1864255,78 | July | 2021 | 2022Q1 | 2022 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2021-07-16 | N | 85 | N | 13 | N | N | 1.1101 | 39.4971 | 4285.969
[7 empty] | 757 | 9506 | 1864317 | 2021-07-16 12:36 | 2021-07-16 13:29 | 53 | 11kV | 31270 | 590 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Ex ZN10994 MORTDALE section of 11kV Panel 19 CP79687 Intelliruptor Forest Valentia, trippedm, reclosed and locked out on: Relays over current trip, lockout Cause: not ascertained Maybe wind related | July | 2021 | 2022Q1 | 2022 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2021-07-16 | N | 53 | N | 13 | N | N | 1.1101 | 39.4971 | 22851.1937
[7 empty] | 432 | 5401 | 1864307 | 2021-07-16 12:34 | 2021-07-16 13:53 | 79 | 11kV | 24964 | 316 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN35370 GALSTON section of 11kV Panel 2 LB196 HV centre phase bond (load side) open Cause: Bond Open Open Bond Load side middle phase at LB196 See 1865539 ex 1864307 | July | 2021 | 2022Q1 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2021-07-16 | N | 79 | N | 13 | N | N | 1.1101 | 39.4971 | 18242.9549
[7 empty] | 552 | 6760 | 1864401 | 2021-07-16 13:27 | 2021-07-16 14:44 | 77 | 11kV | 134134 | 1742 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN12600 LISAROW 11kV CB Panel 3 tripped and locked out on: Signals: 11kv trip, CB3 Open, RTU Prot, Trip Reset Relays: C Phase timed OC, EFI EFI: S14623 S14247 Cause: Tree Branch on OH Mains 32 Bourbon St Wyoming adjacent Normally Open LB77492 | July | 2021 | 2022Q1 | 2022 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2021-07-16 | N | 77 | N | 13 | N | N | 1.1101 | 39.4971 | 98021.1709
[7 empty] | 1439 | 17717 | 1864394 | 2021-07-16 13:21 | 2021-07-16 15:05 | 104 | 11kV | 104 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Wind Strong | N | LID 211225 10Amp, Phase B, Substation DOLF Lightning has hit pole and blown capacitor. No power. Clear access, no animals, no iso. Adv stay 8m away from hazard. SOP De VRIES M DOP BLACKADDER B | July | 2021 | 2022Q1 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Not Veg | 2021-07-16 | N | 104 | N | 13 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 936 | 11340 | 1864521 | 2021-07-16 15:00 | 2021-07-16 17:20 | 140 | 11kV | 280 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211224 11KV OFF PIN INSUALTOR AT SUB 62990. Excluded OMS 1864521 | July | 2021 | 2022Q1 | 2022 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Not Veg | 2021-07-16 | N | 140 | N | 13 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 665 | 8564 | 1864500 | 2021-07-16 15:23 | 2021-07-16 19:30 | 247 | 11kV | 50710 | 229 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | ZN15013 TERREY HILLS 11kV CB Panel 6 fdr has tripped Singals: 11kv trip Relays: Timming relay, lock out, EFI, IOC A, C phase, OC ABC phase EFI: Cause: tree branch brought down OH Tree brought down HV mains and 11kv Pole at 44 Cooyong Rd 11kv fdr is isolated from LK24466 to AB25104 to LK23602 tee to PT15908 PT15908 DIst 1 CTW issued. Dist 2 restored via LV// at 1930 16/7/21 via links 7013,32131 See 1865542,3,4 Ex 1864500,648 | July | 2021 | 2022Q1 | 2022 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2021-07-16 | N | 221.441 | N | 13 | N | N | 1.1101 | 39.4971 | 37057.3723
[7 empty] | 330 | 4541 | 1864408 | 2021-07-16 13:34 | 2021-07-16 19:45 | 371 | 11kV | 1855 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex ZN12600 LISAROW section of 11kV Panel 11 PT11370 CHAMBERLAIN NEWLING 11kV HDO footpath 16 Amp ABB fuse Cause weather related Storm Rain Wind See 1865749 ex 1864410 | July | 2021 | 2022Q1 | 2022 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Veg | 2021-07-16 | N | 371 | N | 13 | N | N | 1.1101 | 39.4971 | 1355.5793
[7 empty] | 712 | 9182 | 1864573 | 2021-07-16 16:50 | 2021-07-16 20:40 | 230 | 11kV | 230 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 211228 Single phase DOLF : 10 Amp excluded OMS 1864573 | July | 2021 | 2022Q1 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-07-16 | N | 230 | N | 13 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 910 | 11218 | 1864414 | 2021-07-16 13:32 | 2021-07-16 22:55 | 563 | 11kV | 24302 | 174 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211223 Tree brought HV into LV between ABS 64673 and sub 15933 Excluded oms 18644114 & 1864468 | July | 2021 | 2022Q1 | 2022 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2021-07-16 | N | 139.6667 | N | 13 | N | N | 1.1101 | 39.4971 | 17759.1848
[7 empty] | 1271 | 15536 | 1864702 | 2021-07-17 05:22 | 2021-07-17 09:40 | 258 | 11kV | 13416 | 52 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | N | PT.15164 Darmour Av (ex Beacon Hill Pa.2) 11kV HVDO operated: 31Amp, Roadside phase Possum found deceased at base of PT pole. Note, separate outage at same time on PT.15164 Dist No.2 due to wind related damage (OMS#1864363). | July | 2021 | 2022Q1 | 2022 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2021-07-17 | N | 258 | N | 8 | N | N | 1.1101 | 39.4971 | 9804.0171
[7 empty] | 369 | 4938 | 1864716 | 2021-07-17 08:23 | 2021-07-17 10:50 | 147 | 11kV | 294 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211235 Broken Live Line lead excluded OMS 1864716 | July | 2021 | 2022Q1 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2021-07-17 | N | 147 | N | 8 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 1499 | 18453 | 1864717 | 2021-07-17 07:39 | 2021-07-17 10:55 | 196 | 11kV | 2416 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 211234 Single phase DOLF : 10 Amp Blown L/F 75014 and sub 72827 | July | 2021 | 2022Q1 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-07-17 | N | 185.8462 | N | 8 | N | N | 1.1101 | 39.4971 | 1765.5415
[7 empty] | 1543 | 18909 | 1864781 | 2021-07-17 10:25 | 2021-07-17 11:41 | 76 | 11kV | 114748 | 1722 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn847 Hornsby -Pnl.39 tripped on SEF Burnt off bond resting on cross arm due to wind at pole MC-15739 See 1865697 1865700 1865701 | July | 2021 | 2022Q1 | 2022 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2021-07-17 | N | 66.6365 | N | 8 | N | N | 1.1101 | 39.4971 | 83854.4539
[7 empty] | 921 | 11266 | 1864672 | 2021-07-16 20:28 | 2021-07-17 15:50 | 1162 | 11kV | 25751 | 240 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn12630 Peats Ridge - Pnl.11 - tripped, reclosed & locked out on: ABC IOC OH mains down between USL41794 and LB40831 PT13698 Wise Ferry Smith Dist #1 - Isolated for repairs See 1865654 1865656 1865657 1865658 1865659 1865660 | July | 2021 | 2022Q1 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2021-07-16 | N | 107.2958 | N | 13 | N | N | 1.1101 | 39.4971 | 18818.0713
[7 empty] | 1536 | 18856 | 1864939 | 2021-07-17 15:35 | 2021-07-17 16:48 | 73 | 11kV | 75847 | 1039 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN1850 BASS HILL 11kV CB Panel 40 fdr tripped and locked out Relays: B&C Phase IOC Signals: 11kv trip EFI: Nil Cause: tree branch clashed 11kv mains at 177 Henry Lawson Drive | July | 2021 | 2022Q1 | 2022 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-07-17 | N | 73 | N | 8 | N | N | 1.1101 | 39.4971 | 55426.7505
[7 empty] | 1191 | 14782 | 1864950 | 2021-07-17 15:49 | 2021-07-17 18:02 | 132.5667 | 11kV | 345468.7333 | 2606 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN10999 KOGARAH 11kV CB Panel 12 tripped, reclosed and locked out on: Relays: A&B Phase IOC, EFI, Timing and lockout Signals: 11kv trip EFI: Nil Tree on 11kv OH Mains 28 DUnmore St KOgarah | July | 2021 | 2022Q1 | 2022 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Veg | 2021-07-17 | N | 132.5667 | N | 8 | N | N | 1.1101 | 39.4971 | 252458.3607
[7 empty] | 312 | 4118 | 1864842 | 2021-07-17 12:39 | 2021-07-17 19:25 | 406.1667 | 11kV | 39398.1667 | 97 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211240 1 fault operation Earth Fault Tree on mains | July | 2021 | 2022Q1 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-07-17 | N | 406.1667 | N | 8 | N | N | 1.1101 | 39.4971 | 28791.0182
[7 empty] | 1233 | 15121 | 1865002 | 2021-07-17 17:58 | 2021-07-17 22:25 | 267 | 11kV | 1335 | 5 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Air Break Switch | Unplanned | Wind Strong | N | Ex ZN12570 AVOCA section of 11kV Panel 22 11kV USL 45430 one link was found hanging DOP advised link was in need of maintenance and repair See 1865785 ex 1865002 | July | 2021 | 2022Q1 | 2022 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2021-07-17 | N | 267 | N | 8 | N | N | 1.1101 | 39.4971 | 975.5786
[7 empty] | 1404 | 17235 | 1865148 | 2021-07-18 21:29 | 2021-07-18 23:33 | 124 | 11kV | 72990 | 589 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN2466 FLEMINGTON 11kV CB Panel 15 tripped on: Relays: A phase timed OC, EFI, Fault Check Singals: Tx4 Group Earth, one Earth, 111kv Trip EFI: S1150 Cause: UG Fault in section of 11kv fdr from S1150 SwB to S6145 SwA. LV// and extension required for testing See 1865788,90 ex 1865148 | July | 2021 | 2022Q1 | 2022 | ZN2466:PA15 | ZN2466:PA15 | ZN02466/000015 | CUMBERLAND | UG | Not Veg | 2021-07-18 | N | 123.9219 | N | 1 | N | N | 1.1101 | 39.4971 | 53338.9392
[7 empty] | 543 | 6556 | 1865409 | 2021-07-20 09:20 | 2021-07-20 10:22 | 62 | 11kV | 55118 | 889 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Section of Pnl.24 Avoca - 11kV Bond burnt off AB41387 road side Emergency repairs required as Bond may possibly clash into OH mains | July | 2021 | 2022Q1 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2021-07-20 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 40278.6087
[7 empty] | 34 | 419 | 1865552 | 2021-07-20 17:13 | 2021-07-20 19:15 | 122 | 11kV | 171503 | 1579 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | N | LID 211249 11kV UGOH failed at pole KT-70080 Excluded OMS 1865552 | July | 2021 | 2022Q1 | 2022 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | Unknown | Unknown | 2021-07-20 | N | 108.6149 | N | 3 | N | N | 1.1101 | 39.4971 | 125329.3339
[7 empty] | 284 | 3638 | 1865598 | 2021-07-20 22:38 | 2021-07-21 00:26 | 108 | 11kV | 16848 | 156 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 211251 Secition isolated to remove tree from 11kV OHM at iv20774 Excluded OMS 1865598 | July | 2021 | 2022Q1 | 2022 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Veg | 2021-07-20 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 12312.0215
[7 empty] | 131 | 1609 | 1865614 | 2021-07-21 00:12 | 2021-07-21 01:25 | 73 | 11kV | 107762 | 2306 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.17 tripped, reclosed & locked out on A Phase IOC & OC UGOH fault between S9807 and LB35356 tee PT63623 See 1865633 1865634 1865635 | July | 2021 | 2022Q1 | 2022 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | Unknown | Unknown | 2021-07-21 | N | 46.7311 | N | 5 | N | N | 1.1101 | 39.4971 | 78749.2912
[7 empty] | 751 | 9467 | 1865618 | 2021-07-21 04:36 | 2021-07-21 07:50 | 194 | 11kV | 20176 | 104 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Wind Strong | N | LID 211253 NAR 77367 Generator connected to sub 52271 stopped working Excluded OMS 1865618 | July | 2021 | 2022Q1 | 2022 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | Unknown | Not Veg | 2021-07-21 | N | 194 | N | 5 | N | N | 1.1101 | 39.4971 | 14744.0257
[7 empty] | 474 | 5774 | 1865686 | 2021-07-21 09:34 | 2021-07-21 11:30 | 116 | 11kV | 116 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 211254 Burnt off tapping pole KT-70069. Fdr abnormal due to blown UGOH KT-70080. 12553 closed 8203 open. Excluded OMS 1865686 | July | 2021 | 2022Q1 | 2022 | 228:7490 | 228:85413 | ZN00228/085413 | NEWCASTLE | OH | Not Veg | 2021-07-21 | N | 116 | N | 5 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 1420 | 17483 | 1865782 | 2021-07-21 14:35 | 2021-07-21 17:15 | 160 | 11kV | 160 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 211255 B Phase DOLF : 10 Amp Excluded OMS 1865782 | July | 2021 | 2022Q1 | 2022 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2021-07-21 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 46 | 612 | 1865791 | 2021-07-21 21:08 | 2021-07-21 23:04 | 116 | 11kV | 3596 | 31 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 211256 Broken x-arm JR-55061 Excluded OMS 1865791 | July | 2021 | 2022Q1 | 2022 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2021-07-21 | N | 116 | N | 5 | N | N | 1.1101 | 39.4971 | 2627.8507
[7 empty] | 717 | 9223 | 1865870 | 2021-07-22 00:25 | 2021-07-22 01:50 | 85 | 11kV | 4420 | 52 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211258 Blown tapping KT70069 subs 13221 & 15491 interrupted for repairs Excluded OMS 1865870 & 1865871 | July | 2021 | 2022Q1 | 2022 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2021-07-22 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 3230.0056
[7 empty] | 1605 | 19547 | 1865885 | 2021-07-22 07:29 | 2021-07-22 10:00 | 151 | 11kV | 64236 | 572 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN874 CONCORD 11kV CB Panel 8 tripped on Relays: Earth Fault Singals: Group Earth, 11kv trip EFI: S3599 S4122 Cause: Ug Fault UG Fault from S4122:B to S8553:D to S35339:A See 1866652,3 ex 1865885 1865897 | July | 2021 | 2022Q1 | 2022 | ZN874:PA8 | ZN874:PA8 | ZN00874/000008 | CANADA BAY | UG | Not Veg | 2021-07-22 | N | 112.3007 | N | 4 | N | N | 1.1101 | 39.4971 | 46941.7742
[7 empty] | 1336 | 16324 | 1866033 | 2021-07-22 17:00 | 2021-07-22 18:14 | 74 | 11kV | 1702 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211262 Emergency switching to remove tree from OHM at pole reported by field crew. | July | 2021 | 2022Q1 | 2022 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2021-07-22 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 1243.7714
[7 empty] | 1164 | 14602 | 1866036 | 2021-07-22 17:26 | 2021-07-22 22:10 | 284 | 11kV | 17018 | 140 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211263 2 fault operations 11kV OHM down between poles MD-90675 & MD-60676. Excluded OMS 1866036 + 1866037 + 1866050 | July | 2021 | 2022Q1 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2021-07-22 | N | 121.5571 | N | 4 | N | N | 1.1101 | 39.4971 | 12436.2525
[7 empty] | 1245 | 15187 | 1866154 | 2021-07-23 12:53 | 2021-07-23 13:10 | 17.1 | 11kV | 1419.3 | 83 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211266 NO protection operation, report from field staff and emergency isolation to remove tree from OHM pole HW-80133. | July | 2021 | 2022Q1 | 2022 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2021-07-23 | N | 17.1 | N | 1 | N | N | 1.1101 | 39.4971 | 1037.1826
[7 empty] | 947 | 11481 | 1866306 | 2021-07-24 16:23 | 2021-07-24 18:04 | 101 | 11kV | 26239 | 302 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN195 PYMBLE 11kV CB Panel 3 tripped on Relays: Earth Fault, EFI, Fault Check Signals: Zone Earth, Tx2 Group Earth 11kv trip EFI: Nil Cause not ascertained See 1866700,1,2,3 Ex 1866306 | July | 2021 | 2022Q1 | 2022 | ZN195:PA3 | ZN195:PA3 | ZN00195/000003 | KU-RING-GAI | OH | Veg | 2021-07-24 | N | 86.8841 | N | 3 | N | N | 1.1101 | 39.4971 | 19174.6873
[7 empty] | 934 | 11319 | 1866331 | 2021-07-24 22:32 | 2021-07-24 23:30 | 58 | 11kV | 6786 | 117 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 211273 C Phase DOLF : 40 Amp Fatigued fuse Excluded OMS 1866331 | July | 2021 | 2022Q1 | 2022 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2021-07-24 | N | 58 | N | 3 | N | N | 1.1101 | 39.4971 | 4959.0086
[7 empty] | 1402 | 17151 | 1866337 | 2021-07-24 23:20 | 2021-07-25 10:00 | 640 | 11kV | 196963 | 1096 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211274 Tree branch on OHM pole HU-40516. Targets = AB O/C 1 span 2 phases of 11kV OHM on ground between ABS 49779 & pole HU-90061. Targets = BGT, Hi set EF, SEL Excluded OMS 1866335 | July | 2021 | 2022Q1 | 2022 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2021-07-24 | N | 179.7108 | N | 3 | N | N | 1.1101 | 39.4971 | 143934.751
[7 empty] | 958 | 11628 | 1866372 | 2021-07-25 08:25 | 2021-07-25 12:06 | 221 | 11kV | 1989 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211282 No protection operations. Tree on 11kV mains pole GV-80203 | July | 2021 | 2022Q1 | 2022 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2021-07-25 | N | 221 | N | 5 | N | N | 1.1101 | 39.4971 | 1453.5025
[7 empty] | 1479 | 18295 | 1866349 | 2021-07-25 02:02 | 2021-07-25 15:20 | 798 | 11kV | 81407 | 112 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 211277 3 fault operations single phase Broken insulator pole GW-70122 Excluded OMS 1866345 | July | 2021 | 2022Q1 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2021-07-25 | N | 726.8482 | N | 5 | N | N | 1.1101 | 39.4971 | 59489.8345
[7 empty] | 1504 | 18483 | 1866481 | 2021-07-25 15:43 | 2021-07-25 16:25 | 42.3333 | 11kV | 296.3333 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 5 CP48568 Autolink Private Dickson Interrupted to refix CCT Bank onto insulator | July | 2021 | 2022Q1 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2021-07-25 | N | 42.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 216.5517
[7 empty] | 207 | 2603 | 1866470 | 2021-07-25 15:25 | 2021-07-25 17:06 | 101 | 11kV | 126220 | 1252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | ZN35800 BANKSTOWN 11kV CB Panel 7 tripped on Relays: IOC A & B Phase Signals: 11kv trip EFI: Nil Cause not ascertained See 1866740,1 Ex 1866470 | July | 2021 | 2022Q1 | 2022 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-07-25 | N | 100.8147 | N | 5 | N | N | 1.1101 | 39.4971 | 92237.8531
[7 empty] | 714 | 9207 | 1866346 | 2021-07-25 01:33 | 2021-07-25 19:15 | 1062 | 11kV | 4003 | 1896 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211278 Mains down2 spans near sub 12059 poles JT-71146 & JT-70495 Excluded OMS 1866346 | July | 2021 | 2022Q1 | 2022 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2021-07-25 | N | 2.1113 | N | 5 | N | N | 1.1101 | 39.4971 | 2925.2743
[7 empty] | 348 | 4788 | 1866517 | 2021-07-26 01:39 | 2021-07-26 04:34 | 175 | 11kV | 2851 | 63 | HV | Vandalism | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 211289 PT 71503 & pole on ground, cut down with chain saw, most of the copper stolen, started grass fire. Excluded OMS 1866517 | July | 2021 | 2022Q1 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2021-07-26 | N | 45.254 | N | 7 | N | N | 1.1101 | 39.4971 | 2083.4267
[7 empty] | 1117 | 14090 | 1866521 | 2021-07-26 11:20 | 2021-07-26 12:10 | 50 | 11kV | 7150 | 143 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211291 No protection operations. HV tapping SW-60032 burnt off (but fell on smae phase below to maintain all supply. Excluded OMS 1866521. | July | 2021 | 2022Q1 | 2022 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2021-07-26 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 5225.0091
[7 empty] | 1138 | 14333 | 1866541 | 2021-07-26 07:57 | 2021-07-26 12:40 | 283 | 11kV | 4370 | 45 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211290 Excavator contacted brought down 11kV OHM between poles EO-10422 & EO-10538. Excluded OMS 1866541, 1866542, 1866623 | July | 2021 | 2022Q1 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-07-26 | N | 97.1111 | N | 7 | N | N | 1.1101 | 39.4971 | 3193.4671
[7 empty] | 430 | 5388 | 1866694 | 2021-07-26 14:05 | 2021-07-26 17:55 | 230 | 11kV | 55660 | 242 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN9245 ENGADINE section of 11kV Panel 1 HV Bond Burnt off at AB35715 See 1866918 ex 1866694 | July | 2021 | 2022Q1 | 2022 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2021-07-26 | N | 230 | N | 7 | N | N | 1.1101 | 39.4971 | 40674.6863
[7 empty] | 738 | 9371 | 1866744 | 2021-07-26 16:12 | 2021-07-26 18:10 | 118 | 11kV | 118 | 1 | HV | Overload | Utility Process Issue | Fuse | Unplanned | No Weather Impact | N | Ex ZN2196 MILPERRA section of 11kV Panel 18 S7475 WILLFOX ILMA NO.2 11kV No.1 Tx HV Fuses operated Cause not ascertained possibly load related See 1866921 ex 1866744 | July | 2021 | 2022Q1 | 2022 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-07-26 | N | 118 | N | 7 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 1529 | 18777 | 1866766 | 2021-07-26 17:28 | 2021-07-26 20:15 | 167 | 11kV | 334 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211293 Broken Live Line Lead Excluded OMS 1866766 | July | 2021 | 2022Q1 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-07-26 | N | 167 | N | 7 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 69 | 846 | 1866784 | 2021-07-26 21:05 | 2021-07-26 22:02 | 57 | 11kV | 2907 | 51 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex ZN14891 WYONG section of 11kV Panel 16 PT13099 PALMER WOLSELEY X2 HDO 31.5 Amp fuses blown due to Possum on PT | July | 2021 | 2022Q1 | 2022 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2021-07-26 | N | 57 | N | 7 | N | N | 1.1101 | 39.4971 | 2124.3499
[7 empty] | 377 | 5013 | 1866802 | 2021-07-27 03:13 | 2021-07-27 04:15 | 62 | 11kV | 62 | 1 | HV | Customer Installation Fault | Customer Installation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211294 1 fault operation | July | 2021 | 2022Q1 | 2022 |  |  |  | LAKE MACQUARIE | Unknown | Unknown | 2021-07-27 | N | 62 | N | 2 | N | N | 1.1101 | 39.4971 | 45.3078
[7 empty] | 726 | 9270 | 1866922 | 2021-07-27 13:12 | 2021-07-27 17:30 | 258 | 11kV | 1032 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 211297 Replaced Burnt up A phase underslung fuse on Pt Excluded OMS 1866922 | July | 2021 | 2022Q1 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2021-07-27 | N | 258 | N | 2 | N | N | 1.1101 | 39.4971 | 754.1552
[7 empty] | 27 | 283 | 1867057 | 2021-07-28 11:30 | 2021-07-28 14:45 | 195 | 11kV | 390 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211300 C Phase DOLF : 10 Amp Excluded OMS 1867057 | July | 2021 | 2022Q1 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2021-07-28 | N | 195 | N | 3 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 169 | 2161 | 1867071 | 2021-07-28 12:02 | 2021-07-28 15:10 | 188 | 11kV | 376 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211301 Broken Live Line lead Excluded OMS 1867071 | July | 2021 | 2022Q1 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2021-07-28 | N | 188 | N | 3 | N | N | 1.1101 | 39.4971 | 274.7697
[7 empty] | 568 | 7038 | 1867119 | 2021-07-28 14:34 | 2021-07-28 16:04 | 90 | 11kV | 1710 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | LID 211302 11kV links 40430 broke whilst operating on NAR 78974. No protection operation. | July | 2021 | 2022Q1 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2021-07-28 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 1249.6176
[7 empty] | 1471 | 18185 | 1867348 | 2021-07-29 19:23 | 2021-07-29 20:45 | 82 | 11kV | 328 | 4 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211306 Single phase DOLF : 10 Amp possum found at base of sub. Excluded oms 1867348 | July | 2021 | 2022Q1 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2021-07-29 | N | 82 | N | 2 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 1122 | 14230 | 1867256 | 2021-07-29 21:15 | 2021-07-29 23:05 | 110 | 11kV | 220 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211307 Faulty pole GW-87012 Excluded OMS 1867256 | July | 2021 | 2022Q1 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2021-07-29 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 595 | 7580 | 1867522 | 2021-07-31 09:41 | 2021-07-31 14:00 | 259 | 11kV | 518 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211313 Single phase Broken Live Line Lead Excluded OMS 1867522 | July | 2021 | 2022Q1 | 2022 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2021-07-31 | N | 259 | N | 2 | N | N | 1.1101 | 39.4971 | 378.5391
[7 empty] | 1580 | 19310 | 1867666 | 2021-07-31 19:21 | 2021-07-31 20:39 | 78 | 11kV | 118077 | 1576 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kv Panel 16 CB "Frederick Church" at ZN35555 Croydon tripped and locked out on: Signals: 11kv trip Relays: 50TC, IOC and EFI Field EFI's: S.3562 Frederick Church, S.2558 John Frederick, S.35720 Taringa Church Remarks: UG fault. There is an UG fault on the 11kv feeder between S.35720 and S.3671 | July | 2021 | 2022Q1 | 2022 | ZN35555:PA16 | ZN35555:PA16 | ZN35555/000016 | INNER WEST | UG | Not Veg | 2021-07-31 | N | 74.922 | N | 2 | N | N | 1.1101 | 39.4971 | 86287.1889
[7 empty] | 803 | 10006 | 1867777 | 2021-08-02 00:52 | 2021-08-02 03:14 | 142 | 11kV | 99993 | 744 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211315 Fdr patrolled. No cause found Excluded OMS 1867777. | August | 2021 | 2022Q1 | 2022 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2021-08-02 | N | 134.3992 | N | 3 | N | N | 1.1101 | 39.4971 | 73071.9351
[7 empty] | 339 | 4744 | 1867957 | 2021-08-02 16:25 | 2021-08-02 17:05 | 40 | 11kV | 360 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211317 Wire off pin pole FP-40107 | August | 2021 | 2022Q1 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-08-02 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 1509 | 18536 | 1867920 | 2021-08-02 17:00 | 2021-08-02 17:55 | 55 | 11kV | 41855 | 958 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN9550 Gwawley Bay 11kv VCB panel 1 S-48721 feeder tripped on Relays: Timmed O/C eart fault, EFI Field EFIs: S48721, 48723, 9083, 9816, 9772, 77882, 78241 Signals: 11kv trip Remarks: UG fault. 11kv UG fault between S9178 Miranda Urunga to S9114 Malvern Rd Sw/A tee to PT9636 Bimbadeen Ave. Pt 9636 restored via LV// event ID 18928 | August | 2021 | 2022Q1 | 2022 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2021-08-02 | N | 43.69 | N | 3 | N | N | 1.1101 | 39.4971 | 30586.3995
[7 empty] | 1448 | 17853 | 1867948 | 2021-08-03 01:41 | 2021-08-03 02:40 | 59 | 11kV | 5371 | 905 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ ZN3154 St Ives - 11kv Panel No.17 "S.62840 Rosedale Shinfield" feeder tripped & reclosed Relays: EFI, EF, Rec timing relay, lockout relay Signals: 11kv trip, zone earth, no.3 group earth Field EFIs: S62840, S35868, S4914, S4020, S7416, S7417 At PT39 Waterhouse Torrens centre phase HDO blown 31.5A Remarks: tree branch contact | August | 2021 | 2022Q1 | 2022 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2021-08-03 | N | 5.9348 | N | 4 | N | N | 1.1101 | 39.4971 | 3924.9684
[7 empty] | 1427 | 17561 | 1868169 | 2021-08-03 20:04 | 2021-08-03 22:20 | 136 | 11kV | 65568 | 503 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S3542 Love NB No.1 11kv OCB "Sw-D" tripped on Relays: 3 phase O/C Field EFIs: sub 7239 Ex panel 13 at S1648 Enfield Abnormal: s3564 Sw/B closed. S78831 Sw/A opened panel 2 Enfield (Nar 66855) Remarks: 11kv U/G fault between S7239 Hume Gould Sw/B to S4478 Roberts Hume Sw/B to S4687 Jean St Sw/A to S3564 Gould Hume Sw/B | August | 2021 | 2022Q1 | 2022 | ZN1648:PA2 | ZN4853:PA27 | ZN04853/000027 | STRATHFIELD | UG | Not Veg | 2021-08-03 | N | 130.3539 | N | 4 | N | N | 1.1101 | 39.4971 | 47915.1605
[7 empty] | 376 | 4972 | 1868155 | 2021-08-03 17:13 | 2021-08-04 00:55 | 462 | 11kV | 924 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211321 Single phase broken insulator at pole KP-70673. Excluded OMS No. 1868155 | August | 2021 | 2022Q1 | 2022 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2021-08-03 | N | 462 | N | 4 | N | N | 1.1101 | 39.4971 | 675.2319
[7 empty] | 1491 | 18378 | 1868196 | 2021-08-04 04:43 | 2021-08-04 07:54 | 191 | 11kV | 226823 | 1619 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN4853 Strathfield South Panel 26 feeder tripped on Relays: A & B IOC Signals: 11kv trip with efi Field efis: Pnl 26 to s35630 Abnormal: Sw/A closed 2631, Sw/D open 825, Sw/B closed 79652, Sw/B open 79653, Sw/E closed 825, Sw/B open 7335, Sw/B closed S76918, Panel 17 OOS at Strathfield Sth, Sw/B closed S2513, Panel 2 at Enfield OOS, Sw/F closed at S7534 Remarks: UG cable fault with other existing faults/adjacent panels OOS | August | 2021 | 2022Q1 | 2022 | ZN4853:PA17 | ZN4853:PA17 | ZN04853/000017 | STRATHFIELD | UG | Not Veg | 2021-08-04 | N | 140.1007 | N | 5 | N | N | 1.1101 | 39.4971 | 165755.5583
[7 empty] | 898 | 11073 | 1868205 | 2021-08-04 06:33 | 2021-08-04 11:05 | 272 | 11kV | 27748 | 314 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S13000 Lake Munmorah the 11kv Panel 4 "Pacific Hwy Nth" feeder tripped, reclosed, tripped and locked out on: Relays: Not reset before panel tripped again see interruption report @ 1105 Remarks: OH down. OH broken at crimp, appears to be fatigue. | August | 2021 | 2022Q1 | 2022 | ZN13000:PA4 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2021-08-04 | N | 88.3694 | N | 5 | N | N | 1.1101 | 39.4971 | 20277.42
[7 empty] | 1434 | 17672 | 1868278 | 2021-08-04 11:05 | 2021-08-04 11:55 | 50 | 11kV | 49340 | 1642 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S13000 Lake Munmorah the 11kv Panel 4 "Pacific Hwy Nth" feeder tripped, reclosed, tripped and locked out on: Relays: B+C OC, Rec Timer (Relays had not been reset from previous fault) Abnormal: LB40172 closed, LB61965, open, AB44625 closed, LB45069 open Remarks: tree/branch on OH mains. Branch found on OH, dop removed | August | 2021 | 2022Q1 | 2022 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Veg | 2021-08-04 | N | 30.0487 | N | 5 | N | N | 1.1101 | 39.4971 | 36056.2167
[7 empty] | 985 | 12053 | 1868305 | 2021-08-04 12:07 | 2021-08-04 12:45 | 38 | 11kV | 3762 | 99 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Wind Strong | N | The 11kv R.44607 Matcham North, Ex Wamberal Panel 10 "Wamberal Aux No.2" tripped, reclosed, tripped and locked out Remarks: Tree/branch brought down OH. Branch on OH, dop removed | August | 2021 | 2022Q1 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-08-04 | N | 38 | N | 5 | N | N | 1.1101 | 39.4971 | 2749.1586
[7 empty] | 1631 | 19751 | 1868418 | 2021-08-04 17:53 | 2021-08-04 18:52 | 59 | 11kV | 118 | 2 | HV | Staff Operation | Utility Process Issue | Fuse Assembly | Unplanned | Wind Strong | N | LID 211324 Single phase DOLF possibly fell out during works on NAR 76840. Opened as a DG224 sub. Excluded OMS 1868418 | August | 2021 | 2022Q1 | 2022 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Not Veg | 2021-08-04 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 619 | 7968 | 1868030 | 2021-08-03 10:31 | 2021-08-04 20:15 | 2024 | 11kV | 132750 | 737 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 211320 UG Cable faulty at pole NR-60355 to sub 24707 Excluded OMS 1868030 etc | August | 2021 | 2022Q1 | 2022 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | UG | Not Veg | 2021-08-03 | N | 180.1221 | N | 4 | N | N | 1.1101 | 39.4971 | 97009.7845
[7 empty] | 1497 | 18431 | 1868560 | 2021-08-05 13:40 | 2021-08-05 14:05 | 25 | 11kV | 225 | 9 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 211326 section isolated for repairs to pole SF-50076 Excluded oms 1868560 | August | 2021 | 2022Q1 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-08-05 | N | 25 | N | 2 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 542 | 6529 | 1868588 | 2021-08-05 15:50 | 2021-08-05 19:30 | 220 | 11kV | 97680 | 444 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Ex Zn15009 Manly ex panel 7 "S.16923 etc" feeder, section of feeder from S.16923 Birkley Raglan to LB 77355 was interrupted for safety to repair LV cross arm. See NAR80806. Abnormal: Dist No.2 from S.15762 Birkelhy Rd 24 is in LV// due to a DMA and was not interrupted. Remarks: Interrupted for safety reasons. Section of HV from S.46402 Augusta Quinton to LB77355 was required to be under access for safety under NAR80806 to repair a Cat 1 LV crossarm. However, S.46402 was in Low Gas alarm and could not be operated causing the extension of the isoalted area to S.16923 Birkley Raglan | August | 2021 | 2022Q1 | 2022 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Not Veg | 2021-08-05 | N | 220 | N | 2 | N | N | 1.1101 | 39.4971 | 71381.6629
[7 empty] | 1330 | 16211 | 1868627 | 2021-08-06 03:38 | 2021-08-06 05:14 | 96 | 11kV | 112800 | 1175 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12580 Erina the 11kv Panel 1 "Green Point" feeder tripped, reclosed, tripped and locked out on: Relays: A phase IOC, EF, EFI, Timer, LO Signals: 11kv trip Field EFIs: Nil Remarks: 11kv UG feeder fault from Erina Panel 1 to S18318 Entrance Avoca Sw/A | August | 2021 | 2022Q1 | 2022 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | UG | Not Veg | 2021-08-06 | N | 96 | N | 2 | N | N | 1.1101 | 39.4971 | 82430.913
[7 empty] | 916 | 11251 | 1868712 | 2021-08-06 13:07 | 2021-08-06 18:10 | 303 | 11kV | 606 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211330 Mains pulled down by excavator at pole HR-62012 Excluded OMS 1868704 | August | 2021 | 2022Q1 | 2022 | 528:83024 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2021-08-06 | N | 303 | N | 2 | N | N | 1.1101 | 39.4971 | 442.8469
[7 empty] | 148 | 1791 | 1868769 | 2021-08-07 06:16 | 2021-08-07 13:50 | 454 | 11kV | 6610 | 19 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211332 Blown tapping. On main line adjacent to sub 52041 Excluded oms 1868769 | August | 2021 | 2022Q1 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-08-07 | N | 347.8947 | N | 3 | N | N | 1.1101 | 39.4971 | 4830.393
[7 empty] | 174 | 2273 | 1868802 | 2021-08-07 14:38 | 2021-08-07 16:05 | 87 | 11kV | 2436 | 28 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Zn14891 Wyong - Ex Pnl.12 - USL40827 is arcing Appeared to not be in the fully closed position. Dop opened link and shut it firmly to restore supply | August | 2021 | 2022Q1 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2021-08-07 | N | 87 | N | 3 | N | N | 1.1101 | 39.4971 | 1780.157
[7 empty] | 1000 | 12354 | 1868874 | 2021-08-07 22:49 | 2021-08-08 07:46 | 537 | 11kV | 37611 | 91 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of 11kv Pnl 10 "Mona Vale Alumuna" feeder at ZN15013 Terrey Hills. 11kv recloser 20852 McCarrs Ck Rd tripped and reclosed on IOC. Sect CP49122 opened on B and C phase IOC Remarks: cause not ascertained. Dayshift to patrol. Dop patrolled and didn't find anything | August | 2021 | 2022Q1 | 2022 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2021-08-07 | N | 413.3077 | N | 3 | N | N | 1.1101 | 39.4971 | 27485.0095
[7 empty] | 771 | 9663 | 1868920 | 2021-08-08 11:39 | 2021-08-08 12:26 | 47 | 11kV | 53956 | 1148 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S15014 Mona Vale ex panel No.14, Rec 22381 Lane Cove Walter tripped on Relays: overcurrent, IOC, Lockout Abnormal: IS21573 closed, REC1126 Mona Vale Rd opens Remarks: tree/branch on OH mains. Tree branch found across 3 phases near PT15407, removed by dop | August | 2021 | 2022Q1 | 2022 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2021-08-08 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 39429.4534
[7 empty] | 380 | 5038 | 1868899 | 2021-08-08 09:38 | 2021-08-08 12:35 | 177 | 11kV | 177 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211335 LLC lead broken excluded oms 1868899 | August | 2021 | 2022Q1 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2021-08-08 | N | 177 | N | 3 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 897 | 11045 | 1868940 | 2021-08-08 13:57 | 2021-08-08 21:18 | 441 | 11kV | 24631 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12650 West Gosford, Ex Panel 1 "Dog Trap Road" feeder, Rec 44853 Ourimbah Bumble has tripped on OC, IOC and EF Remarks: tree/branch on OH mains. Bays of 11kv down due to branch at PT12618. Second Fault was a burnt bond @ pole OU 642 | August | 2021 | 2022Q1 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-08-08 | N | 439.8393 | N | 3 | N | N | 1.1101 | 39.4971 | 17999.6083
[7 empty] | 1272 | 15538 | 1868992 | 2021-08-09 06:17 | 2021-08-09 12:00 | 343.2833 | 11kV | 5835.8167 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211337 1 fault operation A & B Phase DOLF : 5 Amp no cause found | August | 2021 | 2022Q1 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-08-09 | N | 343.2833 | N | 1 | N | N | 1.1101 | 39.4971 | 4264.6427
[7 empty] | 657 | 8488 | 1869480 | 2021-08-11 13:10 | 2021-08-11 15:00 | 110 | 11kV | 8250 | 75 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of Panel No.1 'Dog Trap Rd' feeder Isolated from AB 43611 to LB 47975 tee PT13783 Remarks: tree/branch on OH mains. Treebranch on 11kv OH o/s 255 Ourimbah Creek Rd | August | 2021 | 2022Q1 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-08-11 | N | 110 | N | 1 | N | N | 1.1101 | 39.4971 | 6028.8567
[7 empty] | 885 | 10890 | 1869835 | 2021-08-13 15:14 | 2021-08-13 16:05 | 51 | 11kV | 44307 | 923 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S10998 Rockdale the 11kv Panel 26 "Kyle Charles No.2" feeder tripped, reclosed, tripped and locked out on: Relays: EF, EFI, Reclose L/O Field EFIs: all down to and including S46425 Remarks: UG fault. 11kv UG fault between S46425 Guess Arncliffe Sw/B to S63302 Bonar Lusty SwA | August | 2021 | 2022Q1 | 2022 | ZN10998:PA26 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | UG | Not Veg | 2021-08-13 | N | 48.0033 | N | 4 | N | N | 1.1101 | 39.4971 | 32378.2488
[7 empty] | 280 | 3602 | 1869830 | 2021-08-13 14:49 | 2021-08-13 16:47 | 118 | 11kV | 118 | 1 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211345 Single phase DOLF : 10 Amp Flying fox Excluded OMS 1869830 | August | 2021 | 2022Q1 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2021-08-13 | N | 118 | N | 4 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 96 | 1211 | 1869822 | 2021-08-13 15:15 | 2021-08-13 17:45 | 150 | 11kV | 1885 | 15 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | LID 211346 Ground fire ( from local burn-off ) burnt poles MS10010, MS10030 & MS10031 beyond 11kV links 5534. | August | 2021 | 2022Q1 | 2022 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2021-08-13 | N | 125.6667 | N | 4 | N | N | 1.1101 | 39.4971 | 1377.5024
[7 empty] | 731 | 9331 | 1869856 | 2021-08-13 18:45 | 2021-08-13 20:20 | 95 | 11kV | 16438 | 248 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex ZN2635 Epping 11kv VCB panel 51 'S-65940" feeder tripped on: Relays: Bassler 50TC, 150TN Field EFIs: Nil Signals: 11kv trip Remarks: 11kv UG fault between S65942 Maquarie unit No.3 Sw/B to S65643 Talavera Christie No.3 Sw/B tee S78729 Maquarie Uni No.20 Sw/F. EFIs @ S65940, 65941, 65942 did not operate scada defects created | August | 2021 | 2022Q1 | 2022 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | UG | Not Veg | 2021-08-13 | N | 66.2823 | N | 4 | N | N | 1.1101 | 39.4971 | 12012.4056
[7 empty] | 1487 | 18352 | 1869929 | 2021-08-14 13:37 | 2021-08-14 15:10 | 93.3 | 11kV | 73053.9 | 783 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Ex ZN13000 Lake Munmorah 11kv Panel 7 "Summerland point" @Rec 45138 Yeramba Illawong tripped on earth fault - centre phase load side on a lightning arrestor blown Remarks: lightning/surge arrestor. @REc 45138 Yeramba Illawong centre phase load side on lightning arrestor blown. RTU failed on signal on DNMS | August | 2021 | 2022Q1 | 2022 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2021-08-14 | N | 93.3 | N | 1 | N | N | 1.1101 | 39.4971 | 53385.6354
[7 empty] | 23 | 256 | 1869973 | 2021-08-15 02:55 | 2021-08-15 04:36 | 101 | 11kV | 3232 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211348 A & B Phase DOLF : 20 Amp Excluded OMS 1869973 | August | 2021 | 2022Q1 | 2022 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | OH | Veg | 2021-08-15 | N | 101 | N | 2 | N | N | 1.1101 | 39.4971 | 2361.8503
[7 empty] | 1251 | 15225 | 1869989 | 2021-08-15 08:52 | 2021-08-15 12:25 | 213 | 11kV | 50907 | 239 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN13000 Lake Munmorah 11kv Panel 7 "Summerland Point" 11kv Bond Burnt off in section of 11kv feeder to PT13691 Birrabang Kullaroo and PT11705 Bambara Kullaroo. AB42908 closed and defective, PT12234 Nungan Muraban interrupted to repair HV bond Remarks: bond. Section of feeder defective from LK42907 to LB45141 to AB43524 tee PT13691 Birrabang Kullaroo, PT11705 Bambara Kullaroo and PT12234 Nungan Muraban | August | 2021 | 2022Q1 | 2022 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2021-08-15 | N | 213 | N | 2 | N | N | 1.1101 | 39.4971 | 37201.3341
[7 empty] | 1592 | 19429 | 1870066 | 2021-08-16 05:38 | 2021-08-16 07:22 | 104 | 11kV | 157456 | 1514 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN10995 Riverwood, 11kv Panel NO.5 tripped and reclosed under fault. Protection Relay operations at Zone Sub: A phase IOC & Time, reclose, lockout. Field EFI operations: Nil Remarks: Bond. 11kv bond burnt off Pole PE 00028 CC1: 22-"Refer to SOp" | August | 2021 | 2022Q1 | 2022 | ZN10995:PA5 | ZN10995:PA5 | ZN10995/000005 | GEORGES RIVER | OH | Not Veg | 2021-08-16 | N | 104 | N | 2 | N | N | 1.1101 | 39.4971 | 115064.2006
[7 empty] | 597 | 7589 | 1870198 | 2021-08-16 13:54 | 2021-08-16 15:15 | 81 | 11kV | 891 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211353 Section isolated to repair insulators pole CN-70386 excluded OMS 1870198 | August | 2021 | 2022Q1 | 2022 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2021-08-16 | N | 81 | N | 2 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 797 | 9945 | 1870284 | 2021-08-17 12:07 | 2021-08-17 13:45 | 98 | 11kV | 7938 | 81 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN12610 Long Jetty 11kv VCB panel 25 "S-14067" feeder PT11115 interrupted for safety reasons due to 11kv feeder hanging low Remarks: interrupted for safety reasonns due to 11kv feeder hanging low | August | 2021 | 2022Q1 | 2022 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2021-08-17 | N | 98 | N | 2 | N | N | 1.1101 | 39.4971 | 5800.8563
[7 empty] | 1224 | 15041 | 1870362 | 2021-08-17 15:48 | 2021-08-17 15:55 | 7 | 11kV | 13867 | 1981 | HV | Staff Other | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S14891 Wyong 11kv Pa8 "Betty Anne Green etc" CB tripped on: Relays: SEF Abnormal: Rec45080 was closed with LK44890 open Remarks: staff error - details below. SEF not made N/A during switching. Wyong Pa.8 CB SCADA out of scan since 05/05/2020 | August | 2021 | 2022Q1 | 2022 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2021-08-17 | N | 7 | N | 2 | N | N | 1.1101 | 39.4971 | 10133.5946
[7 empty] | 446 | 5495 | 1870438 | 2021-08-18 07:35 | 2021-08-18 07:45 | 10 | 11kV | 1530 | 153 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | The 11kv Rec 530 Greville Wilfred tripped on OC during switching of NAR79575 Abnormal: Sw/B at S4737 Fullers Millwood is closed. LB 308 is open Remarks: during switching of NAR79575 whilst paralling Panel 15 at Lindfield and Panel 31 at Chatswood, Rec530 Greville Wilfred tripped on OC after closing Sw/A at S8704 Greville Beaconsfield. Rec530 Greville Wilfred was in scan fail so was not visible on DNMS. Interruption occured when Sw/A was opened by Dop at S.5122 per switching. | August | 2021 | 2022Q1 | 2022 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | KU-RING-GAI | Unknown | Not Veg | 2021-08-18 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 1118.0789
[7 empty] | 1478 | 18274 | 1870482 | 2021-08-18 16:19 | 2021-08-18 17:04 | 45 | 11kV | 31490 | 709 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | @ZN8000 Macquarie Park 11kv Panel 6 labelled "S.8150 Lane Cove Talavera No.3" tripped: Relays - Basler Relay (51N-Earth fault) Signals - Tx1 Group Earth, CB.6 trip, CB.6 open, 11kv CB.6 Earth Fault Indication Field EFIs - S.8150, S.8235, S.8604, S.5446 Remarks: UG cable damaged by contractor. 11kv underground fault from Sw.B@5446 Bolwarra Wyuna to Sw.A@S4645 Camira Bingara tee Sw/B @ S.4644 Wyuna Ryde | August | 2021 | 2022Q1 | 2022 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2021-08-18 | N | 44.4147 | N | 3 | N | N | 1.1101 | 39.4971 | 23011.9632
[7 empty] | 1609 | 19569 | 1870611 | 2021-08-19 03:43 | 2021-08-19 05:10 | 87 | 11kV | 5916 | 68 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | No LID report OMS operator trail A & B ph 20A possum at base of pole restored via LV// ## DQ NIL LID part of OMS trail | August | 2021 | 2022Q1 | 2022 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Not Veg | 2021-08-19 | N | 87 | N | 2 | N | N | 1.1101 | 39.4971 | 4323.2383
[7 empty] | 1449 | 17864 | 1870603 | 2021-08-18 22:44 | 2021-08-19 17:00 | 1096 | 11kV | 249034 | 1404 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At Zn12610 Long Jetty Panel 16 tripped on IOC and Lockout Signals: 11kV Trip Cause: Pole Snapped by truck rolling over and being susopended by wires EMSO and AOP reported possible HV into LV out of PT12162. No damage found, checked all services off Pole, see OMS 1870858 1870859 1870860 1870603 1870607 1870610 | August | 2021 | 2022Q1 | 2022 | ZN12610:PA16 | ZN12610:PA16 | ZN12610/000016 | CENTRAL COAST | OH | Not Veg | 2021-08-18 | N | 177.3746 | N | 3 | N | N | 1.1101 | 39.4971 | 181986.7019
[7 empty] | 1531 | 18820 | 1870796 | 2021-08-19 17:48 | 2021-08-19 19:06 | 78 | 11kV | 70372 | 1029 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S7481 Darling Harbour Panel 17 tripped on Signals: 11kV Trip, No2 TX Group Earth 17 Right Feeder relays: Earth Fault, EFI Cause: UG fault between S7481 Pa17 - S1742 - S75996 See OMS 1870850 187852 1870796 | August | 2021 | 2022Q1 | 2022 | ZN7481:PA17 | ZN7481:PA17 | ZN07481/000017 | SYDNEY | UG | Not Veg | 2021-08-19 | N | 68.3887 | N | 2 | N | N | 1.1101 | 39.4971 | 51425.782
[7 empty] | 1015 | 12793 | 1870882 | 2021-08-20 10:37 | 2021-08-20 15:45 | 308 | 11kV | 616 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211359 A Phase DOLF : 10 Amp Replace blown arrestor Excluded OMS 1870882 | August | 2021 | 2022Q1 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2021-08-20 | N | 308 | N | 2 | N | N | 1.1101 | 39.4971 | 450.1546
[7 empty] | 766 | 9553 | 1870943 | 2021-08-20 18:27 | 2021-08-20 20:35 | 128 | 11kV | 512 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211360 C Phase DOLF : 10 Amp Possible fire <1m2. at pole SF-10074. Excluded OMS 1870943. Wrong sub in OMS. | August | 2021 | 2022Q1 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-08-20 | N | 128 | N | 2 | N | N | 1.1101 | 39.4971 | 374.1545
[7 empty] | 327 | 4445 | 1871063 | 2021-08-22 08:54 | 2021-08-22 11:25 | 151 | 11kV | 302 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211365 A Phase DOLF : 10 Amp Lightning arrestor replaced Excluded OMS 1871063 | August | 2021 | 2022Q1 | 2022 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2021-08-22 | N | 151 | N | 3 | N | N | 1.1101 | 39.4971 | 220.6927
[7 empty] | 973 | 11888 | 1871065 | 2021-08-22 09:25 | 2021-08-22 12:18 | 173 | 11kV | 519 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | replaced burnt out arrestor power restored | August | 2021 | 2022Q1 | 2022 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2021-08-22 | N | 173 | N | 3 | N | N | 1.1101 | 39.4971 | 379.2699
[7 empty] | 1374 | 16841 | 1871104 | 2021-08-22 16:54 | 2021-08-22 17:39 | 45 | 11kV | 68850 | 1530 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211366 2 fault operations Overcurrent Excluded OMS 1871112 member of public received electric shock while cutting bamboo. Remove bamboo from OHM pole IV-61016. Targets = A to B phase O/C & second trip B to C phase | August | 2021 | 2022Q1 | 2022 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | OH | Veg | 2021-08-22 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 50313.5493
[7 empty] | 1275 | 15548 | 1871177 | 2021-08-23 10:05 | 2021-08-23 11:30 | 85.4 | 11kV | 6661.2 | 78 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex ZN.36000 Olympic Park, 11kv Panel 7 'S.5609 Crescent Richmond No.1' At S.4890 Bates Badgery, blown 11kv 20 Soldd HRC Transformer Fuse Remarks: Vehicle hit pole. Car hit pole 2 Bates Street. Assumed protection grading issue from clashed mains. | August | 2021 | 2022Q1 | 2022 | ZN36000:PA7 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | OH | Not Veg | 2021-08-23 | N | 85.4 | N | 3 | N | N | 1.1101 | 39.4971 | 4867.8085
[7 empty] | 982 | 12031 | 1871304 | 2021-08-23 20:40 | 2021-08-23 21:50 | 70 | 11kV | 5110 | 73 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211369 A & B Phase DOLF : 31 Amp possum on trans 242 volts, 200, 120, 100 amps Excluded oms 1871304 | August | 2021 | 2022Q1 | 2022 | 261:81865 | 261:81865 | ZN00261/081865 | LAKE MACQUARIE | OH | Not Veg | 2021-08-23 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 3734.2373
[7 empty] | 592 | 7481 | 1871316 | 2021-08-23 23:40 | 2021-08-24 00:21 | 41 | 11kV | 51742 | 1262 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN4545 Meadowbank, ex Panel 31, Rec 46117 Balaclava Vimeiera has tripped Relays: OC trip and LO Remarks: tree branch on OH mains adjacent LB794 | August | 2021 | 2022Q1 | 2022 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | PARRAMATTA | OH | Veg | 2021-08-23 | N | 41 | N | 3 | N | N | 1.1101 | 39.4971 | 37811.5275
[7 empty] | 119 | 1500 | 1871331 | 2021-08-24 04:58 | 2021-08-24 07:50 | 172 | 11kV | 85219 | 870 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 211370 Branch across 11kV main sub 12795. Targets 80083 B & C O/C. B & C DOLF 12795 16A. Excluded oms 1871331 | August | 2021 | 2022Q1 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2021-08-24 | N | 97.9529 | N | 21 | Y | Y | 1.1101 | 39.4971 | 62275.5317
[7 empty] | 1459 | 18009 | 1871349 | 2021-08-24 06:58 | 2021-08-24 09:27 | 149 | 11kV | 39667 | 322 | HV | Arcing | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 211371 3 fault operations B Phase Earth Fault Arcing fault observed on Bph tank insulator. Also possible arrestor issue. Excluded OMS No. 1871349, 1871352, 1871370 | August | 2021 | 2022Q1 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2021-08-24 | N | 123.1894 | N | 21 | Y | Y | 1.1101 | 39.4971 | 28987.4736
[7 empty] | 1082 | 13879 | 1871375 | 2021-08-24 08:46 | 2021-08-24 09:42 | 56 | 11kV | 15297 | 278 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN 847 Hornsby 11kv Panel '38', labelled 'S.6485 Hunter lane Burdett No.1" tripped on: Relays: C phase Earth fault, fault check, EFI Signals: 11kv trip, zone earth, Tx3 group earth Field efis: S.6485 Remarks: section of 11kv feeder Ex panel 38 ZN847 defective between S.6485 Sw B to S.6491 Sw A to CP.1136 Sw M | August | 2021 | 2022Q1 | 2022 | ZN847:PA38 | ZN847:PA38 | ZN00847/000038 | HORNSBY | UG | Not Veg | 2021-08-24 | N | 55.0252 | N | 21 | Y | Y | 1.1101 | 39.4971 | 11178.5964
[7 empty] | 1419 | 17461 | 1871395 | 2021-08-24 09:56 | 2021-08-24 10:52 | 56 | 11kV | 65352 | 1167 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At ZN1673 Turramurra 11kv Panel '6' labelled 'AB3326" tripped, reclosed and locked out on: Relays: A & B phase OC, timing and lockout Signals: 11kv trip Field efis: Nil Abnormal: LB1370 closed, LB1395 open Remarks: tree branch on 11kv mains adjacent LB63921, removed and restored | August | 2021 | 2022Q1 | 2022 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2021-08-24 | N | 56 | N | 21 | Y | Y | 1.1101 | 39.4971 | 47757.314
[7 empty] | 643 | 8333 | 1871413 | 2021-08-24 10:51 | 2021-08-24 11:28 | 37 | 11kV | 3663 | 99 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12630 Peats Ridge, Ex Panel 8, IR 44995 Kulnura has tripped on OC trip Remarks: tree branch found on 11kv mains adjacent PT 13322 George Downs Kyola 2.1 | August | 2021 | 2022Q1 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-08-24 | N | 37 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2676.8124
[7 empty] | 394 | 5142 | 1871565 | 2021-08-24 16:54 | 2021-08-24 18:01 | 67 | 11kV | 8107 | 121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex ZN12630 Peats Ridge ex Panel 11 "Somersby", the Recloser 46803 Wise Ferry Dog Trap 0.1 tripped, reclosed, tripped, reclosed and tripped on: Relays: OC, Lockout Remarks: tree/branch on OH mains. Tree branch found on OH mains outside NO 1051 Wiseman Ferry Rd. Removed by Dop. OH mains to inspect | August | 2021 | 2022Q1 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2021-08-24 | N | 67 | N | 21 | Y | Y | 1.1101 | 39.4971 | 5924.3565
[7 empty] | 830 | 10220 | 1871480 | 2021-08-24 14:37 | 2021-08-24 18:20 | 223 | 11kV | 669 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | The 11kv/415 PT1876 MWS & DB Kenneth St is defective and has no voltage on C phase (Ex Zn.1850 Bass Hill Panel 40) Remarks: transformer failure. The 11kv/415v PT1876 MWS & DB Kenneth St is defective and has no voltage on C phase on the LV side of the Tx. Restored via LV// 11747 | August | 2021 | 2022Q1 | 2022 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-08-24 | N | 223 | N | 21 | Y | Y | 1.1101 | 39.4971 | 488.8855
[7 empty] | 1545 | 18918 | 1871562 | 2021-08-24 16:51 | 2021-08-24 18:55 | 124 | 11kV | 30920 | 302 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S195 Pymble 11kv Panel No3 tripped on Relays: Earth fault, EFI, Fault check Signals: 11kv trip Field EFI's: S35483 Note: EFI at S78687 did not work Remarks: 11kv UG fault from S78687 Pacific Bushlands SW/B to LB 3225 | August | 2021 | 2022Q1 | 2022 | ZN195:PA3 | ZN195:PA3 | ZN00195/000003 | KU-RING-GAI | UG | Not Veg | 2021-08-24 | N | 102.3841 | N | 21 | Y | Y | 1.1101 | 39.4971 | 22595.424
[7 empty] | 634 | 8232 | 1871497 | 2021-08-24 15:06 | 2021-08-24 18:59 | 233 | 11kV | 190584 | 1388 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | @ ZN15013 11kv VCB panel 4 "S-16440" feeder tripped and reclosed on Relays: IOC C phase and earth, C phase timed, timing, lockout, fault check, EFI Signals: 11kv trip, ZN earth REC 21350 Booralie Kalgo a tripped locked out on SEL Abnormal: LB64842 closed, LK23602 opened open and defective, AB25114 closed, LK24212 open and defective, LB20561 closed, REC 1126 open, IS21573 closed, SW/A open @ S16910 Remarks: 11kv b phase bond on UGOH between 16934 Myoora Alumna and LK's 21778. REC21350 Booralie Kalgo tripped at same time fault did not grade. Bark removed by L/man found on 11kv fdr adj PT16215 Eurabba rd | August | 2021 | 2022Q1 | 2022 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2021-08-24 | N | 137.3084 | N | 21 | Y | Y | 1.1101 | 39.4971 | 139273.1659
[7 empty] | 1375 | 16860 | 1871572 | 2021-08-24 17:22 | 2021-08-24 19:00 | 98 | 11kV | 49613 | 783 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Wind Storm | N | @ZN3154 St Ives 11kv VCB panel 19 S-1724 feeder tripped on Relays: INST EF, EFI Field EFIs: S1724(not working) DMA created, S4456 Signals: 11kv trip ZN E, Group E @ PT1127 Vista Darlymple - Footpath phase HVDO operated fault did not grade Remarks: Transformer failure, @ PT1127 Vista Darlymple 11kv footpath phase HVDO operated. Dop suspects transformer failure. LV// event ID 19343 | August | 2021 | 2022Q1 | 2022 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | UG | Not Veg | 2021-08-24 | N | 63.3627 | N | 21 | Y | Y | 1.1101 | 39.4971 | 36255.7171
[7 empty] | 370 | 4949 | 1871628 | 2021-08-24 19:09 | 2021-08-24 19:55 | 46.1 | 11kV | 39968.7 | 867 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | ZN10994 Mortdale Panel 7 Panel did not trip. Tx 1 Group earth Remarks: Bond. 11kv Bond off @ Rec 62226 Connells Terry foot path phase | August | 2021 | 2022Q1 | 2022 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Not Veg | 2021-08-24 | N | 46.1 | N | 21 | Y | Y | 1.1101 | 39.4971 | 29207.9471
[7 empty] | 949 | 11512 | 1871617 | 2021-08-24 18:23 | 2021-08-24 20:28 | 125 | 11kV | 21942 | 187 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 211377 2 fault operations A & B Phase Overcurrent Excluded OMS 1871617 | August | 2021 | 2022Q1 | 2022 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Veg | 2021-08-24 | N | 117.3369 | N | 21 | Y | Y | 1.1101 | 39.4971 | 16034.5664
[7 empty] | 1230 | 15079 | 1871583 | 2021-08-24 17:31 | 2021-08-24 21:34 | 243 | 11kV | 433266 | 2103 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S2635 Epping 11kv Panel No.58 tripped on Relays: C phase overcurrent, IOC C Phase, EFI, rec lockout, trip, earth fault Signals: 11kv trip EFI's: S3800, S5134, S5145, S5822, S5136 Remarks: 11kv UG fault from S5145 Kent Fernhill Sw/B to S5822 Dawson Elgata Sw/A tee to PT58 Magnolia Plympton | August | 2021 | 2022Q1 | 2022 | ZN2635:PA58 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | UG | Not Veg | 2021-08-24 | N | 206.0228 | N | 21 | Y | Y | 1.1101 | 39.4971 | 316618.0136
[7 empty] | 688 | 8764 | 1871648 | 2021-08-24 19:30 | 2021-08-24 21:36 | 126 | 11kV | 125397 | 1229 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN10994 Mortdale Panel 9 tripped on Relays: IOC B & C phase, E/F check and reclose and lockout Signals: Tx 1 grou earth, IOC B and C phase and trip, IEF and EFI Remarks: 11kv UGOH fault near 11kv USL 30752 C phase on the UGOH HR | August | 2021 | 2022Q1 | 2022 | ZN10994:PA9 | ZN10994:PA9 | ZN10994/000009 | GEORGES RIVER | Unknown | Unknown | 2021-08-24 | N | 102.0317 | N | 21 | Y | Y | 1.1101 | 39.4971 | 91636.429
[7 empty] | 590 | 7471 | 1871609 | 2021-08-24 17:54 | 2021-08-24 21:45 | 231 | 11kV | 10189 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 211380 1 fault operation Sensitive Earth Fault Excluded OMS 1871609 | August | 2021 | 2022Q1 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2021-08-24 | N | 203.78 | N | 21 | Y | Y | 1.1101 | 39.4971 | 7445.8207
[7 empty] | 1611 | 19600 | 1871515 | 2021-08-24 15:29 | 2021-08-24 22:00 | 391 | 11kV | 124729 | 319 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 211378 pole fire pole 5I-80683,, section isolated for repairs. Excluded oms 1871515 | August | 2021 | 2022Q1 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-08-24 | N | 391 | N | 21 | Y | Y | 1.1101 | 39.4971 | 91148.2743
[7 empty] | 545 | 6646 | 1871719 | 2021-08-24 21:50 | 2021-08-24 22:11 | 21 | 11kV | 2898 | 138 | HV | Load Shed - Ausgrid | Load Shed | Feeder/Distributor O/H | Unplanned | Cold <10C | N | LID 211381 Opened Fdr 74050 due to critical high limit on Tx 2. | August | 2021 | 2022Q1 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | Exclude | Not Veg | 2021-08-24 | N | 21 | N | 21 | Y | Y | 1.1101 | 39.4971 | 2117.7729
[7 empty] | 187 | 2434 | 1871754 | 2021-08-24 22:58 | 2021-08-25 03:15 | 257 | 11kV | 353432 | 1378 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At S14891 Wyong, 11kv Panel 8 has tripped on Relays: A phase OC and EF, fault check, EFI Signals: 11kv trip, Tx1 GE Field EFI's: N/A Remarks: cause not ascertained. Pa 8 at Wyong is still in scan fail | August | 2021 | 2022Q1 | 2022 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2021-08-24 | N | 256.4819 | N | 21 | Y | Y | 1.1101 | 39.4971 | 258277.6811
[7 empty] | 1542 | 18882 | 1871793 | 2021-08-25 01:51 | 2021-08-25 05:22 | 211 | 11kV | 360469 | 1845 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12570 Avoca, 11kv Panel 25 tripped on Relays: B and C phase OC, FC, EFI, Reclose and Lockout Signals: 11kv trip Field EFI's: N/A Abnormal: Sw/B closed at S187705 Barnhill Grosvenor, open on Panel 34 Avoca Remarks: tree/branch on OH mains. Tree on mains at 69 Hillcrest St Terrigal | August | 2021 | 2022Q1 | 2022 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Veg | 2021-08-25 | N | 195.3762 | N | 5 | N | N | 1.1101 | 39.4971 | 263420.1132
[7 empty] | 994 | 12169 | 1871861 | 2021-08-25 08:09 | 2021-08-25 08:28 | 19 | 11kV | 13266 | 714 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Wind Strong | N | @ZN14891 Wyong exiting Panel 21 labelled "Virginia Rd" REC.45070 Sparks Rd tripped Relays: OC trip, lockout Abnormal: closed @ REC4507o sparks, open @ LB40841 Remarks: overload. Tripped on overload during switching | August | 2021 | 2022Q1 | 2022 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2021-08-25 | N | 18.5798 | N | 5 | N | N | 1.1101 | 39.4971 | 9694.4015
[7 empty] | 130 | 1602 | 1871774 | 2021-08-24 23:12 | 2021-08-25 09:56 | 644 | 11kV | 8372 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Cold <10C | N | LID 211384 Overcurrent | August | 2021 | 2022Q1 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-08-24 | N | 644 | N | 21 | Y | Y | 1.1101 | 39.4971 | 6118.0107
[7 empty] | 452 | 5601 | 1871795 | 2021-08-25 01:54 | 2021-08-25 11:40 | 586 | 11kV | 427440 | 1528 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12570 Avoca 11kV Panel 37 has tripped on Relays: B and C phase IOC, FC, EFI, Recloser and ockout Section of 11kV OH adjacent pole AV693 See OMS 1872418 1872419 1872420 1872421 1871795 1871845 | August | 2021 | 2022Q1 | 2022 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2021-08-25 | N | 279.7382 | N | 5 | N | N | 1.1101 | 39.4971 | 312360.5447
[7 empty] | 239 | 2948 | 1871739 | 2021-08-24 22:35 | 2021-08-25 12:20 | 825 | 11kV | 148273 | 584 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211382 tree on OHM adjacent pole IQ-71563 HV into LV sub 50221 LH Excluded oms 1871739 | August | 2021 | 2022Q1 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2021-08-24 | N | 253.8921 | N | 21 | Y | Y | 1.1101 | 39.4971 | 108353.5351
[7 empty] | 904 | 11137 | 1871683 | 2021-08-24 20:33 | 2021-08-25 15:00 | 1107 | 11kV | 110593 | 429 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN12630 Peats Ridge, ex panel 1 "Gundermann" feeder, the 11kv recloser 45189 Cooks Peats Ridge 0.5 tripped on: (No relay detected due to scan fail at time of fault. Current trended at 180A just prior to fault) Abnormal: Rec 44945 Lower Mangrove Open with Bypass closed Remarks: cause not ascertained. Feeder patrolled by Trent Oliver. Tree branch removed from 11kv mains near pole #PO-132. Ready for service | August | 2021 | 2022Q1 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-08-24 | N | 257.7925 | N | 21 | Y | Y | 1.1101 | 39.4971 | 80818.1025
[7 empty] | 1176 | 14721 | 1872173 | 2021-08-25 17:15 | 2021-08-25 19:15 | 120 | 11kV | 960 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn12600 Lisarow ex Panel 2. 11kv fdr has been isolated to remove large tree from 11kv and 415v mains and make repairs to network 11kv feeder isolated from LB41934 to Lk41935 tee to Pt47611 and PT12365. Pt47611 was place in LV//. PT12365 required to be interrupted to remove tree Remarks: tree/branch on OH mains | August | 2021 | 2022Q1 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-08-25 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 678 | 8674 | 1872207 | 2021-08-25 21:32 | 2021-08-26 00:01 | 149 | 11kV | 402187 | 2798 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At ZN188 Zetland Panel 41R 'S.35153' feeder has tripped Signals: 11kv trip Relays: A, B phases IOC, EF, EFI Field EFI's @ Subs: S35153 Abonormal: Sw/A @ S35153 closed with Panel 42 open for switching @ Clovelly Remarks: UG cable damaged by contractor. 11kv feeder fault from Sw/B at S8814 Ascot Anzac to Sw/A at S35514 Doncaster Abbotsford to Sw/B at S62917 Goodwood Elsmere. Contractor hit cable at 13 Doncastor ave Kensington. Pascal Paises Plumbing 0415656569 | August | 2021 | 2022Q1 | 2022 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2021-08-25 | N | 143.7409 | N | 5 | N | N | 1.1101 | 39.4971 | 293906.3971
[7 empty] | 351 | 4816 | 1872331 | 2021-08-26 11:39 | 2021-08-26 14:35 | 176 | 11kV | 352 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 211391 SOP APPS S DOP SUMMERS L CHRIS COX LINE INPSPECTOR AUSGRID live line clamp has broken away on single phase transformer pole ns27009 and 1 has broken away and dangling down from dolf potentially live. Access 1 way trees across road have not been cleared but there is anotheraccess track to get in | August | 2021 | 2022Q1 | 2022 | 232:33407 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2021-08-26 | N | 176 | N | 4 | N | N | 1.1101 | 39.4971 | 257.2312
[7 empty] | 347 | 4785 | 1872377 | 2021-08-26 14:05 | 2021-08-26 15:45 | 99.8333 | 11kV | 7986.6667 | 80 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211390 stranded conductor adj pole 9U-10039 SOP ARLITSCH E DOP FRAZER J | August | 2021 | 2022Q1 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-08-26 | N | 99.8333 | N | 4 | N | N | 1.1101 | 39.4971 | 5836.4204
[7 empty] | 1206 | 14968 | 1872450 | 2021-08-26 20:49 | 2021-08-26 21:48 | 59.3 | 11kV | 3676.6 | 62 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211394 31 Amp, Phase B & C Substation DOLF No Cause Found (Not Storm Condition) SOP WATSON J DOP FITZPATRICK S | August | 2021 | 2022Q1 | 2022 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Veg | 2021-08-26 | N | 59.3 | N | 4 | N | N | 1.1101 | 39.4971 | 2686.7508
[7 empty] | 1213 | 15017 | 1872452 | 2021-08-26 21:00 | 2021-08-26 23:35 | 155 | 11kV | 34255 | 221 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211393 section isolated to repair 33kV xarm at pole JU-50248 Excluded OMS 1872452 | August | 2021 | 2022Q1 | 2022 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2021-08-26 | N | 155 | N | 4 | N | N | 1.1101 | 39.4971 | 25032.5436
[7 empty] | 1035 | 13097 | 1872545 | 2021-08-27 11:20 | 2021-08-27 13:32 | 132 | 11kV | 8712 | 66 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 211395 'Phase B sub 75484 Broken Bph DOLF Assy all 3 phases replaced SOP E Arlitsch DOP D Davies | August | 2021 | 2022Q1 | 2022 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2021-08-27 | N | 132 | N | 2 | N | N | 1.1101 | 39.4971 | 6366.4726
[7 empty] | 310 | 4074 | 1872589 | 2021-08-27 15:06 | 2021-08-27 16:35 | 89 | 11kV | 89 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211396 B & C Phase DOLF : 10 Amp Sub 71129 B&Cph DOLFs blown on energisation following NAR 81201. Excluded OMS 1872589 | August | 2021 | 2022Q1 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2021-08-27 | N | 89 | N | 2 | N | N | 1.1101 | 39.4971 | 65.0386
[7 empty] | 836 | 10281 | 1872635 | 2021-08-28 00:55 | 2021-08-28 07:33 | 398 | 11kV | 12544 | 98 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kv Rec.44995 Kulnurra Ex Peats Ridge Panel 8 "Kulnurra" tripped, reclosed, tripped and locked out Remarks: OH down. 11kv OH down adj PT11874 | August | 2021 | 2022Q1 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2021-08-28 | N | 128 | N | 5 | N | N | 1.1101 | 39.4971 | 9166.7852
[7 empty] | 1530 | 18809 | 1872645 | 2021-08-28 07:48 | 2021-08-28 09:16 | 88 | 11kV | 27256 | 328 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S874 Concord 11kv Panel No 25 tripped on: Relays: Earth Fault, EFI Signals: 11kv trip, Tx2 group earth, Zone earth EFI's: S62988, S7014 Remarks: UG fault. 11kv UG cable fault from S7014 Concord Mary Sw/B to S8671 Leeds Cavell No2 Sw/A to S4369 Leeds Blaxland Sw/B | August | 2021 | 2022Q1 | 2022 | ZN874:PA25 | ZN874:PA25 | ZN00874/000025 | CANADA BAY | UG | Not Veg | 2021-08-28 | N | 83.0976 | N | 5 | N | N | 1.1101 | 39.4971 | 19917.8809
[7 empty] | 1561 | 19119 | 1872743 | 2021-08-28 20:12 | 2021-08-28 21:32 | 80.35 | 11kV | 321.4 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211399 B Phase DOLF : 16 Amp Excluded OMS 1872744 | August | 2021 | 2022Q1 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-08-28 | N | 80.35 | N | 5 | N | N | 1.1101 | 39.4971 | 234.8696
[7 empty] | 1328 | 16201 | 1872751 | 2021-08-28 22:17 | 2021-08-28 23:20 | 63 | 11kV | 252 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211400 A Phase DOLF : 16 Amp See report 211399, A phase did not drop so was not replaced at that stage. Now replaced & supply OK. Excluded OMS 1872751 | August | 2021 | 2022Q1 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-08-28 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 1576 | 19277 | 1872719 | 2021-08-28 17:15 | 2021-08-29 11:20 | 1085 | 11kV | 3255 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | The 11kv/415v PT18794 Wise Ferry Elwins 0.2N was interrupted due to a large branch on HV and LV at 17:15 Remarks: tree/branch brought down OH. Large branch fell on HV and LV mains near PT.18794 Wise Ferry Elwins 0.2N, HV was tangled in LV. Not repaired till Sunday morning due to difficult access and needing traffic control. | August | 2021 | 2022Q1 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2021-08-28 | N | 1085 | N | 5 | N | N | 1.1101 | 39.4971 | 2378.658
[7 empty] | 630 | 8158 | 1872832 | 2021-08-29 21:20 | 2021-08-29 22:19 | 58.6333 | 11kV | 28319.9 | 483 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | LID 211403 A & C Phase Sensitive Earth Fault fdr tripped on SEF after SEF made auto after switching Nar 82154. Flicker blades were still closed on abs 40884. Fliicker blades cleared and fdr restored. Excluded OMS 1872837 | August | 2021 | 2022Q1 | 2022 | 523:33509 | 523:33509 | ZN00523/033509 | SINGLETON | OH | Not Veg | 2021-08-29 | N | 58.6333 | N | 1 | N | N | 1.1101 | 39.4971 | 20695.3476
[7 empty] | 614 | 7902 | 1872844 | 2021-08-30 05:17 | 2021-08-30 07:51 | 154 | 11kV | 320699 | 2303 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN10999 Kogarah 11kv Panel '16L', labelled 'S.10844 Jubilee Park", tripped, reclosed and locked out on: Relays: SEF Signals: 11kv trip Field EFI's: nil Abnormal: S.10011 Jubilee ROcky Sw/C Closed. Zn10999 Kogarah Panel No.39L CB open Remarks: Bond. Burnt off bond @ a decommissioned AB between UGOH to Sub 10277 (Sw/B) and the tee off to PT 10363 Stubbs Ferry to LB 31253 | August | 2021 | 2022Q1 | 2022 | ZN10999:PA16 | ZN10999:PA16 | ZN10999/000016 | BAYSIDE | OH | Not Veg | 2021-08-30 | N | 139.2527 | N | 2 | N | N | 1.1101 | 39.4971 | 234357.3702
[7 empty] | 1203 | 14918 | 1872940 | 2021-08-30 10:57 | 2021-08-30 12:35 | 98 | 11kV | 294 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | The 11kv 31.5Amp roadside phase HDO was found to be operated explosively at PT18794 Wise Ferry Elwins 0.2N (Ex Zn12630 Peats Ridge-Panel 11) Remarks: fuse failure | August | 2021 | 2022Q1 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2021-08-30 | N | 98 | N | 2 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 354 | 4826 | 1873213 | 2021-08-31 17:10 | 2021-08-31 19:25 | 134.9667 | 11kV | 137935.9333 | 1022 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Intellirupter #63103 Pine Avenue tripped and locked out under fault (Ex-ZN36200 Empire Bay, Panel 1L) Protection operations at Intellirupter: nil (Scan Fail) Dop reports finding recloser open Remarks: tree/branch on OH mains. Tree branch removed from 11kv O/H mains adjacent to N/O LB63105 CC1: 22-"Refer to SOp" | August | 2021 | 2022Q1 | 2022 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Veg | 2021-08-31 | N | 134.9667 | N | 2 | N | N | 1.1101 | 39.4971 | 100799.5117
[7 empty] | 84 | 998 | 1873252 | 2021-08-31 17:00 | 2021-09-01 01:00 | 480 | 11kV | 7680 | 16 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Emergency Pole Replacement NAR 82470 | August | 2021 | 2022Q1 | 2022 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2021-08-31 | N | 480 | N | 2 | N | N | 1.1101 | 39.4971 | 5612.3175
[7 empty] | 1123 | 14246 | 1873289 | 2021-09-01 09:09 | 2021-09-01 10:06 | 57 | 11kV | 912 | 16 | HV | Staff Other | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | Refer to NAR 79582. Customers on spur beyond 41275 were part of a planned outage but were not advised of the outage due to an incomplete carding Pack causing an NECF breach SCADA events show the interruption was from 0909 to 1006. | September | 2021 | 2022Q1 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2021-09-01 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 666.4627
[7 empty] | 600 | 7600 | 1873333 | 2021-09-01 13:24 | 2021-09-01 15:23 | 118.5667 | 11kV | 1897.0667 | 16 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211417 A Phase DOLF : 10 Amp Bird at base of sub 51840, Blown sub dolf 10A & Line Dolf 40607 10A | September | 2021 | 2022Q1 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-09-01 | N | 118.5667 | N | 5 | N | N | 1.1101 | 39.4971 | 1386.3204
[7 empty] | 775 | 9762 | 1873295 | 2021-09-01 09:36 | 2021-09-01 16:35 | 419 | 11kV | 838 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 211414 B Phase DOLF : 10 Amp Blown Bph LA. Sub LVFs left open until tree trimming was completed. Excluded oms 1873295 | September | 2021 | 2022Q1 | 2022 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2021-09-01 | N | 419 | N | 5 | N | N | 1.1101 | 39.4971 | 612.3857
[7 empty] | 1109 | 14042 | 1873372 | 2021-09-01 17:03 | 2021-09-01 19:30 | 147 | 11kV | 60709 | 515 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 211415 3 fault operations 3 phase Earth Fault suspected defective cable Excluded OMS 1873372 | September | 2021 | 2022Q1 | 2022 | 257:82000 | 257:82000 | ZN00257/082000 | NEWCASTLE | UG | Not Veg | 2021-09-01 | N | 117.8816 | N | 5 | N | N | 1.1101 | 39.4971 | 44364.3466
[7 empty] | 1548 | 18962 | 1873391 | 2021-09-01 19:30 | 2021-09-01 22:10 | 160 | 11kV | 160 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211418 sub isolated to repair broken dropper Excluded oms 1873391 | September | 2021 | 2022Q1 | 2022 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2021-09-01 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 710 | 9154 | 1873676 | 2021-09-03 10:10 | 2021-09-03 12:25 | 135 | 11kV | 285 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211422 Broken 11kV insulators at pole HQ-25510. Excluded OMS No. 1873676 | September | 2021 | 2022Q1 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2021-09-03 | N | 95 | N | 1 | N | N | 1.1101 | 39.4971 | 208.2696
[7 empty] | 855 | 10585 | 1873905 | 2021-09-04 18:48 | 2021-09-04 20:04 | 76 | 11kV | 84658 | 1172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN129 Hunters Hill 11kv VCB panel 52 "S-6209" feeder tripped on: Relays: A protection IOC + E fault, trip A phase + Neutral B protection-IOC + E fault, trip A phase + Neutral Field EFIs S6209 Signals: 11kv trip Remarks: 11kv UG feeder fault between S6209 Pittwater Thompson SW/B and S47499 Gannet Pittwater Sw/A | September | 2021 | 2022Q1 | 2022 | ZN129:PA52 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2021-09-04 | N | 72.2338 | N | 1 | N | N | 1.1101 | 39.4971 | 61865.5694
[7 empty] | 1598 | 19491 | 1873948 | 2021-09-05 02:59 | 2021-09-05 16:10 | 791 | 11kV | 373225 | 2054 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN129 Hunters Hill 11kv CB panel 64 "East Ryde" feeder tripped reclosed and tripped onL Relays: A protection - E Fault, Trip A phase + Neutral B protection - E Fault, trip A phase + Neutral, EFI, reclose attempt Abnormal: Sw/A closed at S.2337 to supply section of Pa.52. Sw/A open at S.47499 and Sw/A open at S.78102 Remarks: Bond failure at LB1446, HV contacted neutral, DESO advised for inspection of premises. Section of 11kv feeder from LB341 to LB1446 tee PT231 High Blaxland extended to Sw/B @ S5269 Barons Gaza tee S2560 Park High, placed in LV// | September | 2021 | 2022Q1 | 2022 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2021-09-05 | N | 181.7064 | N | 5 | N | N | 1.1101 | 39.4971 | 272741.8217
[7 empty] | 257 | 3242 | 1874013 | 2021-09-05 13:29 | 2021-09-05 16:35 | 186 | 11kV | 5462 | 67 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211428 B Phase bond Excluded OMS 1874013 | September | 2021 | 2022Q1 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-09-05 | N | 81.5224 | N | 5 | N | N | 1.1101 | 39.4971 | 3991.4685
[7 empty] | 1214 | 15027 | 1874043 | 2021-09-05 16:14 | 2021-09-05 18:25 | 131 | 11kV | 655 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 211430 Broken Live Line Clamp Excluded OMS 1874043 | September | 2021 | 2022Q1 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-09-05 | N | 131 | N | 5 | N | N | 1.1101 | 39.4971 | 478.6547
[7 empty] | 1373 | 16814 | 1874055 | 2021-09-05 18:13 | 2021-09-05 20:31 | 138 | 11kV | 320950 | 2339 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S12570 Avoca, 11kv Panel 21L has tripped on Relays: SEF Signals: 11kv trip Field EFI's - N/A Remarks: Bond. 11kv Bond off on LB 41357 | September | 2021 | 2022Q1 | 2022 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2021-09-05 | N | 137.2168 | N | 5 | N | N | 1.1101 | 39.4971 | 234540.7936
[7 empty] | 631 | 8172 | 1874051 | 2021-09-05 17:24 | 2021-09-06 02:54 | 570 | 11kV | 126152 | 428 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211431 1 fault operation 3 phase Overcurrent Tree onto mains GT-92220 Excluded OMS 1874051/52/75 | September | 2021 | 2022Q1 | 2022 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2021-09-05 | N | 294.7477 | N | 5 | N | N | 1.1101 | 39.4971 | 92188.1607
[7 empty] | 733 | 9337 | 1874168 | 2021-09-06 11:49 | 2021-09-06 12:31 | 42 | 11kV | 27846 | 663 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kv iR.50407 The Scenic Bounty, tripped Relays: O/C trip, Lockout Section of 11kv Panel 33 "MacMasters Beach" feeder at ZN12570 Avoca Remarks: tree/branch on OH mains. Dead branch has fallen on DW | September | 2021 | 2022Q1 | 2022 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2021-09-06 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 20349.0355
[7 empty] | 518 | 6174 | 1874274 | 2021-09-06 18:26 | 2021-09-06 19:17 | 51 | 11kV | 7114 | 146 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | (Ex-ZN 9245 Engadine Pnl 13 "Cooper St" feeder): Section of feeder from AB35043 Remarks: Air break switch - details below. 11kv AB 35043 (Ex-ZN 9245 Engadine Pnl 13): Footpath side phase arcing/damaged. Section of feeder from LB 35744 to LB 35790 de-energised to allow AB35043 to be opened safely | September | 2021 | 2022Q1 | 2022 | ZN9245:PA13 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Not Veg | 2021-09-06 | N | 48.726 | N | 3 | N | N | 1.1101 | 39.4971 | 5198.7014
[7 empty] | 1498 | 18448 | 1874298 | 2021-09-06 19:24 | 2021-09-06 20:14 | 50 | 11kV | 23350 | 467 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN965 Pennant Hills 11kv Panel '44', labelled 'S.49399 Leith Malahide", tripped on: Relays: O/C A & C phase, E/F, EFI Signals: 11kv T, Z/E, Tx G/E Remarks: Animals/birds. Possum climbed on 11kv UGOH in Thorn St nr Bellamy St, caused flash over, no damage | September | 2021 | 2022Q1 | 2022 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Not Veg | 2021-09-06 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 17063.4913
[7 empty] | 258 | 3291 | 1874316 | 2021-09-07 06:15 | 2021-09-07 06:47 | 32 | 11kV | 10016 | 313 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S.384 Camperdown - 11kv No.4 CB "Mitchell Glebe" tripped on: Relays: A phase & Earth fault timed OC Signals: 11kv trip Field EFIs: nil Remarks: UG fault Zn 384 Camperdown Pnl4 CB to S.5759 Mitchell Glebe Sw/A | September | 2021 | 2022Q1 | 2022 | ZN384:PA4 | ZN384:PA4 | ZN00384/000004 | SYDNEY | UG | Not Veg | 2021-09-07 | N | 32 | N | 1 | N | N | 1.1101 | 39.4971 | 7319.3974
[7 empty] | 461 | 5679 | 1874509 | 2021-09-08 03:35 | 2021-09-08 06:00 | 145 | 11kV | 10149.5667 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At PT9570 Ortona Pde Ex Jannali Panel 21 "Roberts Box" the footpath side HDO blew 50k fuse Remarks: cause not ascertained. Restored via LV//s 537, 538, 1001 fuse replaced LV//s removed | September | 2021 | 2022Q1 | 2022 | ZN9252:PA21 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Veg | 2021-09-08 | N | 144.9938 | N | 1 | N | N | 1.1101 | 39.4971 | 7417.004
[7 empty] | 1483 | 18320 | 1874702 | 2021-09-09 07:09 | 2021-09-09 08:22 | 73 | 11kV | 12801 | 337 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ZN35900 Potts Hill 11kv VCB panel 6 'S-3860" feeder tripped and reclosed tripped and locked out on Relays: 51AB, O/C A + B phase, EFI, reclose timing/lockout Field EFI's: S3860, 62911 Signals: 11kv trip Remarks: cause not ascertained. Dop patrolled feeder nothing found | September | 2021 | 2022Q1 | 2022 | ZN35900:PA6 | ZN35900:PA6 | ZN35900/000006 | CUMBERLAND | OH | Veg | 2021-09-09 | N | 37.9852 | N | 2 | N | N | 1.1101 | 39.4971 | 9354.5932
[7 empty] | 1468 | 18152 | 1874827 | 2021-09-09 15:40 | 2021-09-10 13:00 | 1280 | 11kV | 9846 | 113 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S12600 Lisarow ex panel No 2, Rec41020 Wattle Tree rd North tripped on: Relays: overcurrent trip, Lockout Remarks: tree/branch brought down OH. At S12600 Lisarow ex panel No.2 11kv mains down from LK40323 to Rec 44605 Ridgeway Rd tee PT18621 the Ridgeway Awabaki | September | 2021 | 2022Q1 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-09-09 | N | 87.1327 | N | 2 | N | N | 1.1101 | 39.4971 | 7195.1664
[7 empty] | 1067 | 13737 | 1875020 | 2021-09-11 07:34 | 2021-09-11 11:20 | 226 | 11kV | 150712 | 1114 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At ZN9550 Gwawley Bay 11kv Panel '43' labelled S.48722 Gwawly Bay Aux No.2', tripped onL Relays: B & C phase O/C, E/F, EFI Signals: 11kv trip, Z/E, G/E No.11 Tx Field efis: S.48722, S.9073 Remarks: ligthning/surge arrestor. Blown lightning arrestor at 11kv UGOH on main line of feeder above PT9483 Holt Corea. Repairs completed by Line worker | September | 2021 | 2022Q1 | 2022 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2021-09-11 | N | 135.289 | N | 2 | N | N | 1.1101 | 39.4971 | 110135.8843
[7 empty] | 628 | 8112 | 1875115 | 2021-09-11 19:58 | 2021-09-11 20:30 | 32 | 11kV | 320 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211447 One phase of 11kV links 75229 was glowing due to high resistance contacts. Note Muswellbrrook Zone of loaded. Excluded OMS 1875115 | September | 2021 | 2022Q1 | 2022 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2021-09-11 | N | 32 | N | 2 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 7 | 122 | 1875327 | 2021-09-13 10:40 | 2021-09-13 16:30 | 350 | 11kV | 116200 | 332 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211452 crossarm off pole TB-10114 Excluded OMS 1875327 | September | 2021 | 2022Q1 | 2022 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2021-09-13 | N | 350 | N | 4 | N | N | 1.1101 | 39.4971 | 84915.5327
[7 empty] | 1676 | 20378 | 1875471 | 2021-09-13 19:30 | 2021-09-13 21:30 | 120 | 11kV | 12371 | 284 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN5868 Gore Hill 11kv VCB panel 10 "S-47276" feeder tripped on Relays: O/C B phase, EFI, fault check Field EFIs: S47276, 3727, 8964 Signals: 11kv trip Remarks: 11kv UG fault between S-8964 Hotham McLachlan Sw/B to S1402 Hotham Pde Sw/A | September | 2021 | 2022Q1 | 2022 | ZN5868:PA10 | ZN5868:PA10 | ZN05868/000010 | WILLOUGHBY | UG | Not Veg | 2021-09-13 | N | 43.5599 | N | 4 | N | N | 1.1101 | 39.4971 | 9040.3619
[7 empty] | 1414 | 17409 | 1875475 | 2021-09-13 20:33 | 2021-09-13 21:35 | 61.8833 | 11kV | 371.3 | 6 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Wind Strong | N | Nil Operation of protection Remarks: interrupted for safety reasons. Copper theft. CCT surge arresters missing copper earth to ground. 2kv measured at open circuit earth | September | 2021 | 2022Q1 | 2022 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2021-09-13 | N | 61.8833 | N | 4 | N | N | 1.1101 | 39.4971 | 271.3351
[7 empty] | 282 | 3617 | 1875483 | 2021-09-13 22:15 | 2021-09-14 00:27 | 132 | 11kV | 58657 | 451 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN129 Hunters Hill, Panel '41' labelled 'S8345 Pittwater Gannet' 11kv intelliruptor CP63182 Riverview College, tripped on: Relays: O/C Abnormal: LB3030 closed, AB3102 Open Remarks; tree/branch on OH mains. Cleared by dop | September | 2021 | 2022Q1 | 2022 | ZN129:PA41 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2021-09-13 | N | 130.0599 | N | 4 | N | N | 1.1101 | 39.4971 | 42864.8055
[7 empty] | 1132 | 14310 | 1875498 | 2021-09-14 00:07 | 2021-09-14 01:25 | 78 | 11kV | 121914 | 1563 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN129 Hunters Hill 11kv Panel '64', labelled 'S8078 Otaes Westminster', tripped, reclosed and locked out on: Relays: A protection - O/C, B protection - O/C, reclose Signals: 11kv trip Abnormal: Sw/A at S2337 Meyers Ave closed, Sw/A at S47499 Gannet Pittwater open. Sw/A at S78102 Burton Linley open, LB1766 open Remarks: tree/branch on OH mains. Tree branch removed by Dop | September | 2021 | 2022Q1 | 2022 | ZN129:PA64 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2021-09-14 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 89091.1553
[7 empty] | 1428 | 17593 | 1875504 | 2021-09-14 00:56 | 2021-09-14 03:40 | 164 | 11kV | 112176 | 814 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At ZN3154 St Ives 11kv Panel '11', labelled 'Ellalong Rd' tripped on: Relays: C phase IOC, timed O/C Signals: 11kv trip Remarks: cause not ascertained. Fault on 11kv O/H between LB65653, LB2549 & PT1703 dop couldn't spot fault. LV// event ID 19801 | September | 2021 | 2022Q1 | 2022 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2021-09-14 | N | 137.8084 | N | 4 | N | N | 1.1101 | 39.4971 | 81974.9122
[7 empty] | 780 | 9839 | 1875589 | 2021-09-14 10:13 | 2021-09-14 10:55 | 42 | 11kV | 52878 | 1259 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | At S12610 Long Jetty ex "entrance SBS B1" fdr panel No.16, centre phase bond burnt off on bottom side of LK43537 Remarks: air break switch - details below. At S12610 Long Jetty ex panel No.16, centre phase bond burnt off on bottom side of LK43537 | September | 2021 | 2022Q1 | 2022 | ZN12610:PA16 | ZN12610:PA16 | ZN12610/000016 | CENTRAL COAST | OH | Not Veg | 2021-09-14 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 38641.6828
[7 empty] | 1045 | 13378 | 1875673 | 2021-09-14 13:39 | 2021-09-14 15:50 | 131 | 11kV | 102085 | 935 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At S1287 Revesby the 11kv Panel 12 "Tyalgum Av" tripped on: Relays: EF/OC, FC, EFI Field EFI's: all down to including S8003 Remarks: 11kv UG fault from S8003 Lawler Malvern to S8587 Henry Picnic to S8172 Amberdale Picnic tee PT396 Donald St | September | 2021 | 2022Q1 | 2022 | ZN1287:PA12 | ZN1287:PA12 | ZN01287/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-09-14 | N | 109.1818 | N | 4 | N | N | 1.1101 | 39.4971 | 74600.707
[7 empty] | 1621 | 19678 | 1875797 | 2021-09-15 07:49 | 2021-09-15 10:41 | 172 | 11kV | 233470 | 1647 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211458 2 fault operations No scada on IR 10072. no cause found. 2 trips is a guess. Excluded OMS 1875797 | September | 2021 | 2022Q1 | 2022 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2021-09-15 | N | 141.7547 | N | 3 | N | N | 1.1101 | 39.4971 | 170612.9898
[7 empty] | 1100 | 13980 | 1875893 | 2021-09-15 13:22 | 2021-09-15 17:40 | 258 | 11kV | 11610 | 45 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211459 Isolated to repair broken xarm pole IR-32446. OMS 1875893 | September | 2021 | 2022Q1 | 2022 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2021-09-15 | N | 258 | N | 3 | N | N | 1.1101 | 39.4971 | 8484.2456
[7 empty] | 549 | 6704 | 1875962 | 2021-09-15 19:08 | 2021-09-15 20:35 | 87 | 11kV | 2436 | 28 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211463 Sub 79758 interrupted for emergency repairs of 33kv Fdr at pole KS-90331 | September | 2021 | 2022Q1 | 2022 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2021-09-15 | N | 87 | N | 3 | N | N | 1.1101 | 39.4971 | 1780.157
[7 empty] | 513 | 6135 | 1875979 | 2021-09-16 01:31 | 2021-09-16 02:17 | 46.0167 | 11kV | 20017.25 | 435 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn3154 St Ive 11kV Panel 14 tripped on RelaysL Overcurrent E?F IOC EFI Trip Signals - 11kV Trip, ZOne Earth, TX 1 Group Earth Cause: Possum at base of PT1258 Benarooon Ave | September | 2021 | 2022Q1 | 2022 | ZN3154:PA14 | ZN3154:PA14 | ZN03154/000014 | KU-RING-GAI | OH | Not Veg | 2021-09-16 | N | 46.0167 | N | 2 | N | N | 1.1101 | 39.4971 | 14628.0159
[7 empty] | 374 | 4967 | 1876010 | 2021-09-16 09:30 | 2021-09-16 10:15 | 45 | 11kV | 4126 | 110 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At ZN12690 Berkeley Vale Ex Panel 26R CP50096 Tonkis Pacififc Has tripped on 11kV Trip and OC Trip Cause: Surge arrestors have failed See OMS1876225 1876227 1876010 | September | 2021 | 2022Q1 | 2022 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2021-09-16 | N | 37.5091 | N | 2 | N | N | 1.1101 | 39.4971 | 3015.1591
[7 empty] | 267 | 3457 | 1876260 | 2021-09-17 13:09 | 2021-09-17 14:30 | 81 | 11kV | 405 | 5 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211465 A Phase DOLF : 10 Amp Bird against arrestor Excluded OMS 1876260 | September | 2021 | 2022Q1 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-09-17 | N | 81 | N | 2 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 521 | 6202 | 1876266 | 2021-09-17 14:05 | 2021-09-17 15:34 | 89 | 11kV | 21626 | 250 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2635 Epping 11kv Pa.51 'Macquarie Uni etc' feeder tripped on: Relays: 50TC (IOC c phase), 150TN (IOC trip), EFI. Note: EFIs also flagged on Pa.39 & Pa.40 Signals: 11kv trip, underfrequency Field EFI's: S.65940, S.65941, S.65942 Remarks: UG fault on 11kv feeder between S.65942 to S.35643 tee to S.78729 | September | 2021 | 2022Q1 | 2022 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | UG | Not Veg | 2021-09-17 | N | 86.504 | N | 2 | N | N | 1.1101 | 39.4971 | 15803.6429
[7 empty] | 311 | 4095 | 1876362 | 2021-09-18 11:11 | 2021-09-18 13:29 | 138 | 11kV | 97152 | 704 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kv Panel 5 CB "Manly Hospital No 1 etc" at ZN.15015 North Head tripped on: Signals: 11kv trip, Zone Earth Relays: B phase OC, Fault Check, EFI, Tx1 and Tx2 fault check, Panel 4, 7, 9 and 13 EFI's Field EFI's: Nil Abnormal: Sw/B open at S.15820 Addison Rd 146 and Sw A open at S.50491 Bower Shelly. Sw/B closed at S.16909 South Steyne Victoria | September | 2021 | 2022Q1 | 2022 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2021-09-18 | N | 138 | N | 1 | N | N | 1.1101 | 39.4971 | 70995.8161
[7 empty] | 163 | 2059 | 1876437 | 2021-09-19 06:32 | 2021-09-19 11:15 | 282.6167 | 11kV | 7348.0333 | 26 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211467 Burnt off tapping 9J-50055 Excluded OMS 1876437 CC1: 22-"Refer to SOp" | September | 2021 | 2022Q1 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-09-19 | N | 282.6167 | N | 5 | N | N | 1.1101 | 39.4971 | 5369.726
[7 empty] | 784 | 9870 | 1876477 | 2021-09-19 15:46 | 2021-09-19 17:46 | 120 | 11kV | 166146 | 1912 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S5868 Gore Hill Panel 14 tripped on Rignals: 11kV Trip, Zone Earth, TX3 Group Earth Relays: Timed Earth Fault, Fault Check, EFI Field EFI's S5649 Cause: UG fault between S5649 - S804 - S3231 and S4458 OMS 1876539 1876540 1876477 See OMS 1876539 1876540 18769477 | September | 2021 | 2022Q1 | 2022 | ZN5868:PA14 | ZN5868:PA14 | ZN05868/000014 | WILLOUGHBY | UG | Not Veg | 2021-09-19 | N | 86.8964 | N | 5 | N | N | 1.1101 | 39.4971 | 121414.5963
[7 empty] | 496 | 5977 | 1876504 | 2021-09-19 20:50 | 2021-09-19 22:35 | 105 | 11kV | 279987 | 2789 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2602 Clovelly 11kV Panel 42 feeder tripped on Relays: Fault Check, EFI, NO other operations visible on relays Signals: TX2 groupn earth, Zone earth Cause: UG fault - feeder isolated and earthed at S35439 Todman Doncaster SW/B to S8951 SW/A 1876528 1876529 1876504 | September | 2021 | 2022Q1 | 2022 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2021-09-19 | N | 100.3897 | N | 5 | N | N | 1.1101 | 39.4971 | 204606.2414
[7 empty] | 464 | 5691 | 1876480 | 2021-09-19 17:53 | 2021-09-20 11:00 | 1027 | 11kV | 1027 | 1 | HV | Vegetation Grow In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | Location of OMS Incident: 38 Driver Ave, Moore Park. Asset ID: SY16720/21 Further Works Required?: Yes 19.9 > Reported By: David Mcandrew. Completion/Follow-up Comments: Tree branch rubbing on service, 2 exposed phases arc'ed together, repaired but techo or emso required for RF11 20.9> Reported By: Anthony Huckstepp. Completion/Follow-up Comments: Ran new service, supply restored. E/C to carry out phase rotation CC1: 22-"Refer to SOp" | September | 2021 | 2022Q1 | 2022 |  |  |  | SYDNEY | OH | Veg | 2021-09-19 | N | 1027 | N | 5 | N | N | 1.1101 | 39.4971 | 750.5013
[7 empty] | 1630 | 19738 | 1876593 | 2021-09-20 10:29 | 2021-09-20 11:50 | 81 | 11kV | 9234 | 114 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211470 Magpie dead at pole IS-68519. Secondary fault at pole IS-68513 broken dead end insulator. C phase OC at Tarro sub and C phase dirrectional OC at Steggles sub. excluded OMS 1876591/92/93 | September | 2021 | 2022Q1 | 2022 | 235:8685 | 235:8685 | ZN00235/008685 | NEWCASTLE | OH | Not Veg | 2021-09-20 | N | 81 | N | 4 | N | N | 1.1101 | 39.4971 | 6747.9348
[7 empty] | 355 | 4827 | 1876658 | 2021-09-20 14:36 | 2021-09-20 15:19 | 43 | 11kV | 4558 | 106 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP44602 Ourimbah Creek Rd tripped reclosed and locked out on Relays: OC trip Field EFIs NIL Tree branch on 11kV Mains Adjacent to LB 47975 | September | 2021 | 2022Q1 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-09-20 | N | 43 | N | 4 | N | N | 1.1101 | 39.4971 | 3330.852
[7 empty] | 1127 | 14265 | 1876722 | 2021-09-20 19:09 | 2021-09-20 20:26 | 77 | 11kV | 217582 | 3040 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN4545 Meadowbank Panel 31 has tripped Signals: 11kV Trip, TX3 group earth Relays: EFI, Fault Check, B phase Earth Failt Cause: Possum found on the 11kV UGOH adjuacent to S4549 See OMS 1876722 1876760 1876761 | September | 2021 | 2022Q1 | 2022 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | OH | Not Veg | 2021-09-20 | N | 71.573 | N | 4 | N | N | 1.1101 | 39.4971 | 159002.508
[7 empty] | 495 | 5975 | 1876734 | 2021-09-20 22:12 | 2021-09-21 00:14 | 122 | 11kV | 39284 | 322 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN12610 Long Jetty Panel 25 HV bond has burnt off at UGOH pole TE495 (First UGOH below S18655 Oakland Battley See OMS 1876759 1876735 1876734 | September | 2021 | 2022Q1 | 2022 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2021-09-20 | N | 122 | N | 4 | N | N | 1.1101 | 39.4971 | 28707.5885
[7 empty] | 884 | 10887 | 1876429 | 2021-09-19 04:36 | 2021-09-21 13:00 | 3384 | 11kV | 486486 | 169 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kv centre phase fuse was found operated and efi flagged on Sw/C at CP25760 Woorak Nabilla (Ex ZN.15010 Careel Bay - Panel 28). Remarks: UG fault. There is an UG fault in the 11kv submarine cable between S-15682 Currawong PK Sw-A tee to S-15681 WT Digger CR and S15680 WT Mackerall beach. | September | 2021 | 2022Q1 | 2022 | ZN15010:PA28 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | UG | Not Veg | 2021-09-19 | N | 2878.6154 | N | 5 | N | N | 1.1101 | 39.4971 | 355509.6199
[7 empty] | 1584 | 19335 | 1876914 | 2021-09-21 09:25 | 2021-09-21 17:50 | 505 | 11kV | 2020 | 4 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | No Weather Impact | N | Ex ZN11630 Peats Ridge 11kv Panel 3 'Mangrove Mountain' A, B & C phase 11kv HDO's found open at PT11630 Wise Ferry Fairymeade. Appears HDOs may have not been closed during restoration of NAR-82197 Remarks: Staff error - details below. Assumed staff error. HDOs may have not been closed during restoration of NAR-82197. Interruption time reported by customer OMS-1876914 | September | 2021 | 2022Q1 | 2022 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2021-09-21 | N | 505 | N | 4 | N | N | 1.1101 | 39.4971 | 1476.1564
[7 empty] | 390 | 5124 | 1876990 | 2021-09-21 19:12 | 2021-09-21 20:23 | 71 | 11kV | 67410 | 955 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S9550 Gwawley Bay 11kv Panel 1 has tripped on Relays: Earth fault, efi Signals: 11kv trip, Tx1 group earth, Zone earth Field EFIs - S48721, S48723, S9083 Remarks: UG fault. Cable fault in section of 11kv feeder from S9083 Port Hackng Box No.2 to S9816 Miranda Windmeer | September | 2021 | 2022Q1 | 2022 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2021-09-21 | N | 70.5864 | N | 4 | N | N | 1.1101 | 39.4971 | 49261.2397
[7 empty] | 1128 | 14274 | 1877002 | 2021-09-21 21:34 | 2021-09-22 00:46 | 192 | 11kV | 89224 | 504 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S3542 Love NB No.1 "11kv Sw/D CB tripped under fault" (ex-ZN 1648 Enfield Panel #13) Protection Relay Operations at S3542 Sw/D: B & C Phase IOC Field EFI Operations: S7239 Hume Gould Abnormal: Sw/B closed at S3564, At S7534, Sw/F closed. Sw/P open, Sw/A at S78831 Open (Enfield Pnl 2 OOS Under AP) Remarks: Underground cable fault between S7239 Hume Gould Sw/B, S-4687 Jean St Sw/A, S-4478 Roberts Hume Sw/B and S3564 Gould Hume Sw/B. | September | 2021 | 2022Q1 | 2022 | ZN1648:PA2 | ZN4853:PA27 | ZN04853/000027 | STRATHFIELD | UG | Not Veg | 2021-09-21 | N | 177.0317 | N | 4 | N | N | 1.1101 | 39.4971 | 65202.2675
[7 empty] | 1240 | 15153 | 1876941 | 2021-09-21 16:41 | 2021-09-22 01:38 | 537 | 11kV | 34905 | 65 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211475 2 fault operations A & C Phase Overcurrent Tree has brought down 11kV mains at pole WB-13952. | September | 2021 | 2022Q1 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-09-21 | N | 537 | N | 4 | N | N | 1.1101 | 39.4971 | 25507.5445
[7 empty] | 1578 | 19299 | 1877122 | 2021-09-22 20:45 | 2021-09-22 22:02 | 77 | 11kV | 71610 | 930 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211479 interrupt to repair 33kV pin insulator Excluded OMS 1877122 | September | 2021 | 2022Q1 | 2022 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2021-09-22 | N | 77 | N | 1 | N | N | 1.1101 | 39.4971 | 52330.4759
[7 empty] | 1318 | 16086 | 1877183 | 2021-09-23 00:11 | 2021-09-23 12:06 | 715 | 11kV | 224349 | 765 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211481 Earth Fault wire down at pole FQ 61139 SOP BURGMANN S DOP ROBERTSON D | September | 2021 | 2022Q1 | 2022 | 512:83733 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2021-09-23 | N | 293.2667 | N | 3 | N | N | 1.1101 | 39.4971 | 163947.632
[7 empty] | 846 | 10473 | 1877277 | 2021-09-23 11:38 | 2021-09-23 14:01 | 143 | 11kV | 214991 | 1617 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211484 No Cause Found (Not Storm Condition) SOP ARLITSCH E DOP LEWIS C "## OMS 1877277 No scada on IR 10072, DMA tagged since 12/4/2021. no cause found. possibly 2 trips just a guess." | September | 2021 | 2022Q1 | 2022 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2021-09-23 | N | 132.9567 | N | 3 | N | N | 1.1101 | 39.4971 | 157109.0816
[7 empty] | 420 | 5300 | 1877397 | 2021-09-23 22:37 | 2021-09-23 23:24 | 47 | 11kV | 84271 | 1793 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN12570 Avoca, 11kv Panel 24 "Woodfield Waldron" tripped Relays: 'A & B' phase IOC, AR Lockout Signals: 11kv trip Remarks: tree/branch on OH mains. Tree branch removed off mains near 140-144 Cullens Rd Kincumber | September | 2021 | 2022Q1 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2021-09-23 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 61582.7612
[7 empty] | 1135 | 14325 | 1877409 | 2021-09-24 07:08 | 2021-09-24 09:40 | 152 | 11kV | 152 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 211485 Refer to OMS 1877409 Reattach LLC SOP McGUIRE L DOP CAREY J | September | 2021 | 2022Q1 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-09-24 | N | 152 | N | 2 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 652 | 8446 | 1877420 | 2021-09-24 11:00 | 2021-09-24 13:30 | 150 | 11kV | 2100 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kv feeder (Ex Lisarow Pa.2 feeder) interrupted from USL.40246 to Normally open AB.41711 tee to PT.13767 Toomey Taylors 0.3 due to safety concerns at PT.13767 Remarks: interrupted for safety reasons. Feeder interrupted due to burnt off Neutral at PT.13767 Toomey Taylors 0.3. Repaired and restored. | September | 2021 | 2022Q1 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2021-09-24 | N | 150 | N | 2 | N | N | 1.1101 | 39.4971 | 1534.6181
[7 empty] | 262 | 3366 | 1877586 | 2021-09-25 08:57 | 2021-09-25 11:30 | 153 | 11kV | 153 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211487 Broken LLC lead excluded oms 1877586 | September | 2021 | 2022Q1 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-09-25 | N | 153 | N | 4 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 1162 | 14578 | 1877637 | 2021-09-25 14:58 | 2021-09-25 15:52 | 54 | 11kV | 54 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211489 Single phase DOLF : 10 Amp Cockatoos dropping tree branches on top of Transformer. | September | 2021 | 2022Q1 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2021-09-25 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 39.4616
[7 empty] | 140 | 1711 | 1877661 | 2021-09-25 22:22 | 2021-09-25 22:57 | 35 | 11kV | 29428 | 869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9118 Cronulla Panel 2 'S9091' feeder has tripped Signals: 11kv trip Relays: EF, EFI, Sealing Contact Field EFI's @ Subs: First 2 Subs down Remarks: UG fault. Located between Sw/B @ Sub 9463 Dolans Kingsway and Sw/A @ Sub 9497 Caringbah Gannons | September | 2021 | 2022Q1 | 2022 | ZN9118:PA2 | ZN9118:PA2 | ZN09118/000002 | SUTHERLAND | UG | Not Veg | 2021-09-25 | N | 33.8642 | N | 4 | N | N | 1.1101 | 39.4971 | 21505.1144
[7 empty] | 97 | 1227 | 1877672 | 2021-09-26 06:30 | 2021-09-26 07:11 | 41.1333 | 11kV | 39940.4667 | 971 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12650 West Gosford, 11kv R63069 Coolarn Wendy has tripped on OC trip Remarks: tree/branch on OH mains. Tree branch on mains at 213 Brisbane water drive Point Claire. R63069 Coolarn Wendy is in Scan Fail and did not alarm on the DNMS | September | 2021 | 2022Q1 | 2022 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Veg | 2021-09-26 | N | 41.1333 | N | 3 | N | N | 1.1101 | 39.4971 | 29187.315
[7 empty] | 16 | 206 | 1877655 | 2021-09-25 18:11 | 2021-09-26 11:00 | 1009 | 11kV | 49434.6 | 49 | HV | Overload | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Sub 15680 MACKEREL BEACH 11kv transformer interrupted due to overload Supply with genset due HV cable fault. Genset tripped on overload | September | 2021 | 2022Q1 | 2022 | ZN15010:PA28 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | Unknown | Not Veg | 2021-09-25 | N | 1008.8694 | N | 4 | N | N | 1.1101 | 39.4971 | 36125.3476
[7 empty] | 810 | 10061 | 1877707 | 2021-09-26 10:44 | 2021-09-26 12:08 | 84 | 11kV | 199553 | 3603 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12600 Lisarow. 11kv Panel 13 & Tx2 has tripped on Panel 13 Relays - B & C phase overcurrent, reclose and lockout. BUOC also operated causing Tx2 and Group 2 to trip. Tx2 Relays - Tx2 Multitrip, Overload prohibition. A-B Bus section - BUOC multitrip Group 2. Signals: 11kv trip, 33kv trip Field EFI's: Nil Remarks: tree/branch on OH mains. Tree branch has made contact with 11kv Mains at 25 Shirley St Ourimbah. Panel 13 did not trip and BUOC has operated, tripping Tx2 and Group 2 busbar. | September | 2021 | 2022Q1 | 2022 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2021-09-26 | N | 55.3852 | N | 3 | N | N | 1.1101 | 39.4971 | 145827.4466
[7 empty] | 1004 | 12537 | 1877737 | 2021-09-26 14:58 | 2021-09-26 17:23 | 145 | 11kV | 580 | 4 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211490 A & B Phase DOLF : 16 Amp possibly trees blown onto mains or mains clash Excluded oms 1877737 | September | 2021 | 2022Q1 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-09-26 | N | 145 | N | 3 | N | N | 1.1101 | 39.4971 | 423.8469
[7 empty] | 308 | 4049 | 1877890 | 2021-09-27 09:00 | 2021-09-27 10:30 | 90 | 11kV | 10800 | 120 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | SOP arrange tree trimming unplanned job | September | 2021 | 2022Q1 | 2022 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | Unknown | Not Veg | 2021-09-27 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 7892.3215
[7 empty] | 534 | 6365 | 1877867 | 2021-09-27 11:58 | 2021-09-27 13:00 | 62 | 11kV | 10230 | 165 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211492 section isolated to make repairs at pole HW-40007 (xarm strap) Excluded oms 1877867 & 1877869 | September | 2021 | 2022Q1 | 2022 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2021-09-27 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 7475.7823
[7 empty] | 1620 | 19676 | 1877842 | 2021-09-27 11:00 | 2021-09-27 13:31 | 151 | 11kV | 243152 | 1617 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211493 No Fault found | September | 2021 | 2022Q1 | 2022 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2021-09-27 | N | 150.3723 | N | 3 | N | N | 1.1101 | 39.4971 | 177688.3098
[7 empty] | 888 | 10911 | 1877995 | 2021-09-28 08:36 | 2021-09-28 14:20 | 344 | 11kV | 688 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211494 A Phase DOLF : 10 Amp Bird | September | 2021 | 2022Q1 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-09-28 | N | 344 | N | 1 | N | N | 1.1101 | 39.4971 | 502.7701
[7 empty] | 786 | 9876 | 1878319 | 2021-09-30 05:40 | 2021-09-30 08:05 | 145 | 11kV | 30468 | 2388 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn15001 Brookvale - Pnl.18 tripped & reclosed on B & C phase OC Bird on 11kV mains, 11kV Bond burnt off 11kV between S46892 and S50262 Suspected open circuit at pole FF46066 but could not confirm See 1879036 1879037 | September | 2021 | 2022Q1 | 2022 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Not Veg | 2021-09-30 | N | 12.7588 | N | 4 | N | N | 1.1101 | 39.4971 | 22265.1157
[7 empty] | 1074 | 13802 | 1878314 | 2021-09-30 05:12 | 2021-09-30 09:12 | 240 | 11kV | 97020 | 569 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211496 Overcurrent 11kV mains found twisted at pole AL10360 Excluded OMS 1878314 | September | 2021 | 2022Q1 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-09-30 | N | 170.5097 | N | 4 | N | N | 1.1101 | 39.4971 | 70899.3544
[7 empty] | 909 | 11212 | 1878456 | 2021-09-30 17:40 | 2021-09-30 18:20 | 40 | 11kV | 160 | 4 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211498 sub isolated for lv repair power restored 1820. MdV Excluded OMS 1878456 | September | 2021 | 2022Q1 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2021-09-30 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 1220 | 15037 | 1878487 | 2021-09-30 20:45 | 2021-09-30 21:44 | 59 | 11kV | 37784 | 670 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.18 tripped on translay 18L UG cable fault in frontline section between Pnl.18, S35424 Sw/A, S36107 Sw/A and S46974 Sw/F See 1879028 | September | 2021 | 2022Q1 | 2022 | ZN931:PA18 | ZN931:PA18 | ZN00931/000018 | SYDNEY | UG | Not Veg | 2021-09-30 | N | 56.394 | N | 4 | N | N | 1.1101 | 39.4971 | 27611.4328
[7 empty] | 1110 | 14053 | 1878501 | 2021-10-01 02:52 | 2021-10-01 04:43 | 111 | 11kV | 140924 | 1484 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S1850 Bass Hill Panel 32 feeder tripped Signals: 11kV Trip Relays: AB and C phase OC Cause not ascertained SWA Closed at S4343, LB3297 Open DMA See OMS 1878541 1878542 1878501 1878502 1878509 | October | 2021 | 2022Q2 | 2022 | ZN1850:PA32 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-10-01 | N | 94.9623 | N | 10 | N | N | 1.1101 | 39.4971 | 102983.1026
[7 empty] | 435 | 5420 | 1878510 | 2021-10-01 04:22 | 2021-10-01 06:50 | 148 | 11kV | 11389 | 1687 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn2196 Millperra - Panel 5 tripped & reclosed on C phase O/C @ PT2257 Mactie Ave - 11kV HDO blown on footpath phase Possum found at base of PT See 1879024 1879025 | October | 2021 | 2022Q2 | 2022 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-10-01 | N | 6.751 | N | 10 | N | N | 1.1101 | 39.4971 | 8322.7453
[7 empty] | 382 | 5045 | 1878604 | 2021-10-01 14:44 | 2021-10-01 15:31 | 47 | 11kV | 1442 | 32 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35700 Port Botany - Pnl.12 tripped on Earth Fault UG cable fault between S7169 Sw/B and S6789 Sw/A See 1879021 1879022 | October | 2021 | 2022Q2 | 2022 | ZN35700:PA12 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | UG | Not Veg | 2021-10-01 | N | 45.0625 | N | 10 | N | N | 1.1101 | 39.4971 | 1053.7711
[7 empty] | 325 | 4364 | 1878609 | 2021-10-01 14:57 | 2021-10-01 16:30 | 93 | 11kV | 86143 | 984 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | Zn12690 Berkeley Vale - Pnl.6 tripped, reclosed & locked out on Earth Fault PT14043 Jane Ellen Aston lightning hit arrestors - restored via LV // See 1879060 1879061 1879062 | October | 2021 | 2022Q2 | 2022 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2021-10-01 | N | 87.5437 | N | 10 | N | N | 1.1101 | 39.4971 | 62950.7636
[7 empty] | 29 | 296 | 1878612 | 2021-10-01 15:14 | 2021-10-01 16:30 | 76 | 11kV | 152 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 211507 B Phase DOLF : 10 Amp Excluded OMS 1878612 | October | 2021 | 2022Q2 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2021-10-01 | N | 76 | N | 10 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 769 | 9627 | 1878643 | 2021-10-01 16:53 | 2021-10-01 17:45 | 52 | 11kV | 260 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 211509 DOLF : 10 Amp Excluded OMS 1878643 | October | 2021 | 2022Q2 | 2022 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2021-10-01 | N | 52 | N | 10 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 168 | 2158 | 1878642 | 2021-10-01 16:46 | 2021-10-01 17:59 | 73 | 11kV | 51903 | 711 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | REC46116 Lancaster Andrew tripped, reclosed & locked out on OC Tree found on 11kV OH below S4666 | October | 2021 | 2022Q2 | 2022 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Veg | 2021-10-01 | N | 73 | N | 10 | N | N | 1.1101 | 39.4971 | 37929.1815
[7 empty] | 1596 | 19472 | 1878636 | 2021-10-01 16:45 | 2021-10-01 19:20 | 155 | 11kV | 1085 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex Peats Ridge Zn Pnl.10 - Section of 11kV feeder between LB45002 and LB45014 tee PTs 14537 & 18573 interrupted to remove trees near CCT See 187836 1878637 | October | 2021 | 2022Q2 | 2022 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2021-10-01 | N | 155 | N | 10 | N | N | 1.1101 | 39.4971 | 792.886
[7 empty] | 1526 | 18706 | 1878690 | 2021-10-01 22:02 | 2021-10-01 23:00 | 58.0667 | 11kV | 6271.2 | 108 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211511 A & B Phase DOLF : 40 Amp Possum on PT excluded OMS 1878691/93 | October | 2021 | 2022Q2 | 2022 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2021-10-01 | N | 58.0667 | N | 10 | N | N | 1.1101 | 39.4971 | 4582.808
[7 empty] | 1061 | 13591 | 1878606 | 2021-10-01 14:54 | 2021-10-02 11:50 | 1256 | 11kV | 3664 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 211512 Single phase DOLF : 20 Amp L/A's blown at PT 7253. trans change PT 7253 sao required Excluded OMS 187606/1878694 | October | 2021 | 2022Q2 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2021-10-01 | N | 732.8 | N | 10 | N | N | 1.1101 | 39.4971 | 2677.5431
[7 empty] | 922 | 11270 | 1878734 | 2021-10-02 11:11 | 2021-10-02 13:53 | 162 | 11kV | 258909 | 1617 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211513 no fault found Sw 10072 bypassed Excluded oms 1878734 | October | 2021 | 2022Q2 | 2022 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2021-10-02 | N | 160.1169 | N | 2 | N | N | 1.1101 | 39.4971 | 189203.0607
[7 empty] | 1417 | 17421 | 1878786 | 2021-10-02 22:04 | 2021-10-03 00:39 | 155 | 11kV | 620 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 211514 B & C Phase DOLF : 20 Amp Excluded OMS 1878786 | October | 2021 | 2022Q2 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-10-02 | N | 155 | N | 2 | N | N | 1.1101 | 39.4971 | 453.0777
[7 empty] | 503 | 6018 | 1878858 | 2021-10-03 18:33 | 2021-10-03 19:49 | 76 | 11kV | 206641 | 3010 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.35600 Kingsford - Pnl.9 tripped on Earth Fault (9L) UG cable fault in front line section of feeder See 1879069 1879071 | October | 2021 | 2022Q2 | 2022 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2021-10-03 | N | 68.6515 | N | 3 | N | N | 1.1101 | 39.4971 | 151007.1479
[7 empty] | 535 | 6380 | 1878873 | 2021-10-03 21:50 | 2021-10-03 22:30 | 40 | 11kV | 240 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 211516 A & B Phase DOLF : 16 Amp Blown L/A Excluded OMS 1878873 | October | 2021 | 2022Q2 | 2022 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2021-10-03 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 353 | 4822 | 1878868 | 2021-10-03 19:37 | 2021-10-04 07:00 | 683 | 11kV | 3415 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211515 DOLF : 10 Amp Tree down at JP-76554. Resulted in a TX fault. 100KVA Tx needs replacing excluded OMS 1878868 | October | 2021 | 2022Q2 | 2022 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2021-10-03 | N | 683 | N | 3 | N | N | 1.1101 | 39.4971 | 2495.5813
[7 empty] | 135 | 1649 | 1878899 | 2021-10-04 11:48 | 2021-10-04 12:40 | 52 | 11kV | 156 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211518 A Phase DOLF : 10 Amp | October | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-10-04 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 758 | 9510 | 1878923 | 2021-10-04 13:59 | 2021-10-04 16:36 | 157 | 11kV | 191777 | 1237 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | At Zn15014 Monda Vale Panel 7 Tripped on Relays: A Protection: Fault Flag IOC A B and C phase B Protection: Fault Flag IOC A B and C phase Abnormal Switching: SW/B Closed at S16893 - AB25751 Open Cause: Pole has fallen at 6 Cabbage Tree Rd - LV parallels found in - LV mains down in Barrenjoey Rd See OMS: 1879074 1879078 1879064 1879050 1878923 1878940 1878946 | October | 2021 | 2022Q2 | 2022 | ZN15014:PA7 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Not Veg | 2021-10-04 | N | 155.034 | N | 4 | N | N | 1.1101 | 39.4971 | 140144.9751
[7 empty] | 1070 | 13768 | 1878971 | 2021-10-04 22:46 | 2021-10-05 01:27 | 161 | 11kV | 483 | 3 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1285 Green Acre Park 11HV tripped under fault Protection relay operations at ZN1285 Pa34: Translay Trip, Intertrip recive, efi, Fault Check Pa28: EFI, Fault Check Protection Operations at S7215Muir Hume: SW/C: Translay trip, IT Send UG 11kV Cable fault betwen ZN1285 Green Avre Park Panel 34 abd S8297 Liverp[ools Brunker SW/A See OMS 1879009 1878971 | October | 2021 | 2022Q2 | 2022 | ZN1285:PA34 | ZN1285:PA34 | ZN01285/000034 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-10-04 | N | 161 | N | 4 | N | N | 1.1101 | 39.4971 | 352.9622
[7 empty] | 601 | 7619 | 1878978 | 2021-10-05 04:35 | 2021-10-05 07:50 | 195 | 11kV | 206583 | 1164 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | AT Zn4545 Meadowbank Tripped under fault Cause: Protection Flag @ Zn4545 A phase timed OC, EFI, Fault Check, TX2 Group Earth, Zone Earth, 11kV Trip Cause: UGOH fault short circuit 11kV UGOH before recloser CP46116 Lancaster Andrew defective. DOp found porcelin on ground under UGOH See OMS 1879170 1879171 1879172 1878978 | October | 2021 | 2022Q2 | 2022 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | Unknown | Unknown | 2021-10-05 | N | 177.4768 | N | 3 | N | N | 1.1101 | 39.4971 | 150964.7632
[7 empty] | 574 | 7150 | 1879123 | 2021-10-05 12:38 | 2021-10-05 13:39 | 61.5 | 11kV | 4920 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn35370 Galston Panel 12 CP3280 Hunt Ave Tripped and Locked out Cause: Tree branch on OH mains at pole DU36970 | October | 2021 | 2022Q2 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2021-10-05 | N | 61.5 | N | 3 | N | N | 1.1101 | 39.4971 | 3595.3909
[7 empty] | 1346 | 16397 | 1878966 | 2021-10-04 20:52 | 2021-10-05 18:25 | 1293 | 11kV | 9512 | 33 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 211520 A & B Phase DOLF : 40 Amp Faulty TX. Note 11kV frd 8691 and 33kV Fdr 3423 tripped and reclosed at same time. See LID 211521 and 211522. Excluded OMS 1878966/67 | October | 2021 | 2022Q2 | 2022 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2021-10-04 | N | 288.2424 | N | 4 | N | N | 1.1101 | 39.4971 | 6951.089
[7 empty] | 1565 | 19137 | 1879225 | 2021-10-05 23:44 | 2021-10-06 00:22 | 38 | 11kV | 17252 | 454 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1673 Turramurra Panel 9 tripped Signals: 11kV trip Relays: C phase IOC, EFI and Fault Check Field EFI's @ S31785, S4241 Cause: Deceased possum outside 82 Ada Ave | October | 2021 | 2022Q2 | 2022 | ZN1673:PA9 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | OH | Not Veg | 2021-10-05 | N | 38 | N | 3 | N | N | 1.1101 | 39.4971 | 12607.2528
[7 empty] | 1662 | 20187 | 1879403 | 2021-10-06 16:51 | 2021-10-06 17:44 | 53 | 11kV | 2438 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211529 A Phase DOLF : 31 Amp Excluded OMS 1879403 | October | 2021 | 2022Q2 | 2022 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2021-10-06 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 1781.6185
[7 empty] | 1593 | 19452 | 1879405 | 2021-10-06 16:55 | 2021-10-06 19:15 | 140 | 11kV | 9660 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | 11kV Interrupted beyond LB48850 for remove of dead tree on Glenworth Valley Rd, Wendoree Park | October | 2021 | 2022Q2 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2021-10-06 | N | 140 | N | 4 | N | N | 1.1101 | 39.4971 | 7059.2431
[7 empty] | 564 | 6991 | 1879436 | 2021-10-06 22:25 | 2021-10-06 23:59 | 94 | 11kV | 3196 | 34 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | LID 211532 Possum at ABS 40592 | October | 2021 | 2022Q2 | 2022 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2021-10-06 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 2335.5425
[7 empty] | 1297 | 15780 | 1879446 | 2021-10-07 05:57 | 2021-10-07 08:45 | 168 | 11kV | 155622 | 1794 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn12570 Avoca Panel 24 "S.12664 Woodfield Waldron" feeder, tripped, reclosed and tripped on: Relays: B phase IOC, Reclose timing, LO, EFI Signals: see log Field EFIs: Nil Note: EFI at S.12664 initially found flagged, however, on a re-attempt to energise from panel 24, it was found the EFI was not down, indicating a fault before the EFI Remarks: UG fault. Ex ZN 12570 Avoca, ex panel 24 "S.12664 Woodfield Waldron", 11kv feeder form Zn12570 panel 24 to S.12664 Woodfield Waldron Sw A has suspect UG cable fault. See DMA | October | 2021 | 2022Q2 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | UG | Not Veg | 2021-10-07 | N | 86.7458 | N | 7 | N | N | 1.1101 | 39.4971 | 113723.9675
[7 empty] | 465 | 5712 | 1879445 | 2021-10-07 05:45 | 2021-10-07 09:40 | 235 | 11kV | 1880 | 8 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 211534 Phase B Refer to oms 1879445 sub isolated to repair broken LL LEAD all 3 LLC replaced" SOP De VRIES M DOP NORTON D | October | 2021 | 2022Q2 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2021-10-07 | N | 235 | N | 7 | N | N | 1.1101 | 39.4971 | 1373.8485
[7 empty] | 603 | 7641 | 1879545 | 2021-10-07 12:40 | 2021-10-07 13:31 | 51 | 11kV | 2703 | 53 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211535 Refer to OMS 1879545 LV and HV Earthing system partly stolen. No protection operation," SOP DOOLAN P DOP RIDING M | October | 2021 | 2022Q2 | 2022 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Not Veg | 2021-10-07 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 1975.2727
[7 empty] | 341 | 4755 | 1879547 | 2021-10-07 12:42 | 2021-10-07 13:31 | 49 | 11kV | 31945 | 697 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN630 Mascot 11kv Pa.31 CB 'O'Riordan Coward No.2' feeder tripped: Signals: Zone Earth, Tx.4 Group Earth, 11kv Trip Relays: B phase OC, EFI Remarks: UG cable damaged by contractor. Piling rig hit cable at 38 Baxter Rd, Mascot | October | 2021 | 2022Q2 | 2022 | ZN630:PA31 | ZN630:PA31 | ZN00630/000031 | BAYSIDE | UG | Not Veg | 2021-10-07 | N | 45.8321 | N | 7 | N | N | 1.1101 | 39.4971 | 23344.4638
[7 empty] | 1129 | 14278 | 1879613 | 2021-10-07 17:08 | 2021-10-07 18:29 | 81 | 11kV | 106221 | 1361 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.14 tripped on: A Phase OC Abnormal: S35376 Sw/A closed with Sw/B Open UG cable fault between S1203 Sw/B and S65526 Sw/A EFI incorrectly operated twice at S65526 See 1880402 1880403 | October | 2021 | 2022Q2 | 2022 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2021-10-07 | N | 78.0463 | N | 7 | N | N | 1.1101 | 39.4971 | 77623.1738
[7 empty] | 1671 | 20346 | 1879608 | 2021-10-07 16:39 | 2021-10-07 18:45 | 126 | 11kV | 145128 | 1746 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12600 Lisarow - Pnl.3 tripped, reclosed and locked out on: Earth Fault UG cable fault See 1880394 1880395 1880396 1880397 | October | 2021 | 2022Q2 | 2022 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | UG | Not Veg | 2021-10-07 | N | 83.1203 | N | 7 | N | N | 1.1101 | 39.4971 | 106055.2618
[7 empty] | 1319 | 16121 | 1879680 | 2021-10-07 18:31 | 2021-10-07 20:00 | 89 | 11kV | 51264 | 576 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Pnl.24 Avoca - HV Bond burnt off LB42022 towards PT11831 Abnormal: LB45097 closed for feeder fault between Pnl.24 and S12664 Sw/A | October | 2021 | 2022Q2 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2021-10-07 | N | 89 | N | 7 | N | N | 1.1101 | 39.4971 | 37462.2192
[7 empty] | 205 | 2598 | 1879769 | 2021-10-08 03:15 | 2021-10-08 03:55 | 40 | 11kV | 320 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At PT15672 Tumbledown Dick 11kv C phase 16 Amp HDO blown Remarks: cause not ascertained | October | 2021 | 2022Q2 | 2022 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2021-10-08 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 1210 | 14990 | 1879832 | 2021-10-08 10:47 | 2021-10-08 13:03 | 136 | 11kV | 19388 | 171 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211538 No Cause Found (Not Storm Condition) Overcurrent also refer to OMS oms 1879832 SOP DOOLAN P DOP McINTOSH G DOP SWAN P | October | 2021 | 2022Q2 | 2022 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2021-10-08 | N | 113.3801 | N | 4 | N | N | 1.1101 | 39.4971 | 14168.1786
[7 empty] | 667 | 8613 | 1879318 | 2021-10-06 11:15 | 2021-10-08 16:20 | 3185 | 11kV | 340632 | 172 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At S15014 Mona Vale ex panel NO10, At CP24702 Western Forshores 11kv Tee off has tripped. Relays- HV fuse blown - C phase, EFI Second trip at CP24702 Western Foreshores - 11kv tee off has tripped. Relalys - HV fuse blown - A phase, EFI Field EFIs: All down to and including S16529, except S16468, CP24701, CO24702 Sw5995 Remarks: UG fault. 11kv UG fault from S16528 Elvina Bay South Sw/B to S16529 Elvina Bay North Sw A | October | 2021 | 2022Q2 | 2022 | ZN15014:PA10 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | OH | Not Veg | 2021-10-06 | N | 1980.4186 | N | 4 | N | N | 1.1101 | 39.4971 | 248923.8187
[7 empty] | 691 | 8828 | 1879906 | 2021-10-08 14:52 | 2021-10-08 19:05 | 253 | 11kV | 82786 | 1046 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN14144 Wamberal 11kv Panel '7', labelled AB 44978, tripped on: Relays: SEL, EFI Signals: 11kv trip, Tx1 G/E Field efis: Nil Remarks: tree trimming in area. Tree trimming O/S 39 John St Forresters Beach, branch fell on 11kv OH. Feeder tripped when tied back. Dop found wire down at AB 44381. HV repaired by L/Wkr | October | 2021 | 2022Q2 | 2022 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2021-10-08 | N | 79.1453 | N | 4 | N | N | 1.1101 | 39.4971 | 60497.567
[7 empty] | 1411 | 17381 | 1879972 | 2021-10-09 02:31 | 2021-10-09 05:48 | 197 | 11kV | 75168 | 1668 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Ex ZN4545 Meadowbank, ex panel 40 "S.47010 Anthony Betts" feeder, the Recloser 1437 Shaftsbury Morvan tripped and reclosed on: Relays: OC Abnormal: Recloser 46116 Lancaster Andrew is open (isolation point) LB1751 closed Remarks: cause not ascertained. Dop found middle phase bond at LB479 open. See DMA | October | 2021 | 2022Q2 | 2022 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Veg | 2021-10-09 | N | 45.0647 | N | 6 | N | N | 1.1101 | 39.4971 | 54930.5573
[7 empty] | 1332 | 16226 | 1879978 | 2021-10-09 04:32 | 2021-10-09 07:04 | 152 | 11kV | 281904 | 1905 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN10999 Kogarah panel 32 "S.10658 Bent Willison" feeder, tripped reclosed and tripped on: Relays: B and C phase IOC, EFI, Rec Lo Signals: 11kv reclose lockout, protection trip, earth fault indication Field EFIs: S.10658, S10122, S.10546 Remarks: Animals/Birds. There is a large bat entangled in the bottom UGOH between S.10546 Caledonia Vivian and S.65804 Forest Preddys and LB31107 | October | 2021 | 2022Q2 | 2022 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | OH | Not Veg | 2021-10-09 | N | 147.9811 | N | 6 | N | N | 1.1101 | 39.4971 | 206007.1284
[7 empty] | 383 | 5050 | 1879965 | 2021-10-08 22:50 | 2021-10-09 11:45 | 775 | 11kV | 313098 | 1584 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211540 2 fault operations C Phase Overcurrent, Earth Fault broken 11kV xarm at pole JU-30749 HV into LV Excluded oms 1879965 | October | 2021 | 2022Q2 | 2022 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2021-10-08 | N | 197.6629 | N | 4 | N | N | 1.1101 | 39.4971 | 228802.7836
[7 empty] | 1397 | 17104 | 1880023 | 2021-10-09 11:00 | 2021-10-09 12:37 | 97 | 11kV | 145058 | 1714 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN342 Paddington, 11kv Panel NO.35 "S-4371 Celment Waratah, etc" tripped under fault. Proftection Relay Operations at Zone Sub: OC/EF Trip, Tx4 Group Earth Field EFI Operations: Nil Abnormal: Sw/F closed at S-1681 New South Rushcutters, Sw/B Open at S-8395 Boundary Dillon Remarks: UG fault. 11kv Underground cable fault between Zn-342 Paddington Panel 35, S-4371 Clement Waratah Sw/A and S-1681 New South Rushcutters Sw/F | October | 2021 | 2022Q2 | 2022 | ZN342:PA28 | ZN342:PA28 | ZN00342/000028 | SYDNEY | UG | Not Veg | 2021-10-09 | N | 84.6313 | N | 6 | N | N | 1.1101 | 39.4971 | 106004.1079
[7 empty] | 1032 | 13056 | 1880085 | 2021-10-09 16:49 | 2021-10-09 21:57 | 308 | 11kV | 72688 | 236 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Interupted from ABS 3605 due to glowing/arcing contact at ABS 5550 No LID DQ trial see ## Found A phase contacts on ABS switch 5550 arcing and sparking. Opened off LB switch 3605 to de energise section of 11KV feeder and warning tag applied to switch. | October | 2021 | 2022Q2 | 2022 | 216:10722 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2021-10-09 | N | 308 | N | 6 | N | N | 1.1101 | 39.4971 | 53118.2465
[7 empty] | 930 | 11295 | 1880107 | 2021-10-09 22:06 | 2021-10-09 23:33 | 87 | 11kV | 90633 | 1048 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN36100 Rose Bay, panel 20 "S.36182 Rose Bay Aux No 2" feeder tripped on: Relays: 51N, EFI Signals (From local HMI): Panel 20 Left EF trip, Panel 20 Left earth fault indication. Field efis: S.36182, S47334, S.5099, S.48350, S.2716 Remarks: UG fault. At ZN36100 Rose Bay, panel 20 "S.36182 Rose Bay Aux No 2" feeder, section of feeder from S.2716 Military Myuna to S.1672 Eastern Mil has a suspect UG cable fault | October | 2021 | 2022Q2 | 2022 | ZN36100:PA20 | ZN36100:PA20 | ZN36100/000020 | WAVERLEY | UG | Not Veg | 2021-10-09 | N | 86.4819 | N | 6 | N | N | 1.1101 | 39.4971 | 66231.9232
[7 empty] | 1331 | 16213 | 1880114 | 2021-10-10 03:00 | 2021-10-10 04:04 | 64 | 11kV | 74560 | 1165 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1673 Turramurra panel 6 "AB 3326 etc" feeder, reclosed and tripped on: Relays: B and C Phase IOC, Reclose, LO Remarks: tree/branch on OH mains. Branch found on HV OH on Maxwell near Eden. Dop removed branch and power restored | October | 2021 | 2022Q2 | 2022 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2021-10-10 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 54486.2489
[7 empty] | 1562 | 19120 | 1880109 | 2021-10-09 22:40 | 2021-10-10 09:40 | 660 | 11kV | 2640 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211543 A & B Phase DOLF : 16 Amp Excluded oms 1880131, 1880123, 1880109 | October | 2021 | 2022Q2 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-10-09 | N | 660 | N | 6 | N | N | 1.1101 | 39.4971 | 1929.2341
[7 empty] | 889 | 10915 | 1880195 | 2021-10-10 16:47 | 2021-10-10 19:51 | 184 | 11kV | 200283 | 1781 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 211552 2 fault operations A & C Phase Overcurrent feeder patrolled nothing found Excluded OMS 1880195 | October | 2021 | 2022Q2 | 2022 | 216:10722 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Veg | 2021-10-10 | N | 112.4554 | N | 2 | N | N | 1.1101 | 39.4971 | 146360.9091
[7 empty] | 1405 | 17256 | 1880257 | 2021-10-11 02:37 | 2021-10-11 03:20 | 43 | 11kV | 29885 | 695 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN14144 Wamberal 11kv Panel 10 "Wamberal Aux No.2" feeder tripped Relays: A & B phase IOC, L/O, efi Signals: 11kv trip FIeld efis: S.18824, S.18802, S.18826 Remarks: tree/branch on OH mains. Tree branch on OH at PT14484 | October | 2021 | 2022Q2 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-10-11 | N | 43 | N | 7 | N | N | 1.1101 | 39.4971 | 21839.0765
[7 empty] | 378 | 5018 | 1880263 | 2021-10-11 05:06 | 2021-10-11 06:18 | 72 | 11kV | 7850 | 110 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | 11kv Rec 50096 Tonkiss Pacific tripped and locked out Section of 11kv feeder panel NO:26R "Wyong Rd" fdr Relays: O/C trip, lockout Remarks: cause not ascertained. Feeder patrolled by D.ops | October | 2021 | 2022Q2 | 2022 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2021-10-11 | N | 71.3636 | N | 7 | N | N | 1.1101 | 39.4971 | 5736.5485
[7 empty] | 774 | 9698 | 1880404 | 2021-10-11 12:23 | 2021-10-11 14:51 | 148 | 11kV | 50542 | 373 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | The 11kv Panel 23 "Christie Oxley etc" cb at ZN187 Crows Nest tripped on: Signals: 11kv trip, Tx11 Group Earth Note: EFI @ S6594 Mitchell Pacific operated several times when it shouldn't have. (Operated on original fault, when energising from S7254 with Sw/A open @ S6594 Mitchell Pacific and with Sw/D open at S6594 Mitchell Pacific) Remarks: UG fault. 11kv UG cable fault from S7254 Pacific Friedlander to S8592 Clarke Pole Sw/A to S6594 Mitchell Pacific Sw/D | October | 2021 | 2022Q2 | 2022 | ZN187:PA23 | ZN187:PA23 | ZN00187/000023 | LANE COVE | UG | Not Veg | 2021-10-11 | N | 135.5013 | N | 7 | N | N | 1.1101 | 39.4971 | 36934.6029
[7 empty] | 1148 | 14424 | 1880272 | 2021-10-11 06:43 | 2021-10-11 15:40 | 537 | 11kV | 17430 | 98 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | @ZN12630 Peats Ridge exiting Panel 8 labelled "Kulnura" 11kv rec.44995 Kulnura tripped: Relays: SEF, lockout Signals: CP44995 open, CP44995 lockout Remarks: tree/branch on OH mains. 55 Collins Ave, Kulnura CTW issued to Authorised Person @ 1130. AP issued to Authorised Person @ 1130 | October | 2021 | 2022Q2 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-10-11 | N | 177.8571 | N | 7 | N | N | 1.1101 | 39.4971 | 12737.3299
[7 empty] | 143 | 1720 | 1880417 | 2021-10-11 12:46 | 2021-10-11 16:40 | 234 | 11kV | 3510 | 15 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Electrical Storm | N | LID Replace insulator pole IV-41267 interupted to make emergency repairs to 33kV ohm damaged insulator at pole IU-41267 Excluded OMS 1880417 | October | 2021 | 2022Q2 | 2022 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2021-10-11 | N | 234 | N | 7 | N | N | 1.1101 | 39.4971 | 2565.0045
[7 empty] | 1151 | 14428 | 1880519 | 2021-10-11 20:23 | 2021-10-11 21:45 | 81.9 | 11kV | 7125.3 | 87 | HV | Animal Possum | Animal | O/H Conductor Insulated | Unplanned | Rain Heavy | N | PT12604 Centre Phase HDO 31.5k Remarks: Animals/Birds. Possum found electrocuted OS 21 Sorrento Rd | October | 2021 | 2022Q2 | 2022 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Not Veg | 2021-10-11 | N | 81.9 | N | 7 | N | N | 1.1101 | 39.4971 | 5206.9591
[7 empty] | 441 | 5447 | 1880664 | 2021-10-12 12:19 | 2021-10-12 13:15 | 56 | 11kV | 112 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 211927 A Phase DOLF : 10 Amp Excluded OMS 1880664 | October | 2021 | 2022Q2 | 2022 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2021-10-12 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 502 | 6015 | 1880617 | 2021-10-12 10:39 | 2021-10-12 14:25 | 226 | 11kV | 226 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 211928 Single phase DOLF Short cicuit found in cabling between TX 20621 LV tank bushing and LVF20621. S01 notified, LVF 20621 opened removed and warning tagged, 11 KV Dolf 20621, opened removed and warning tagged. Please have OH crew attend to replace cabling and restore supply. Please also have a DOP attend if crew not trained to switch Excluded OMS 1880617 | October | 2021 | 2022Q2 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2021-10-12 | N | 226 | N | 4 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 1359 | 16635 | 1880526 | 2021-10-11 21:00 | 2021-10-12 14:50 | 1070 | 11kV | 258370 | 1174 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 211924 2 Fault operations A & B Phase Overcurrent broken 33kV xarm at pole JV-70603 prot = 50TAB see report # 211923 Excluded oms 1880526 | October | 2021 | 2022Q2 | 2022 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2021-10-11 | N | 220.0767 | N | 7 | N | N | 1.1101 | 39.4971 | 188809.1754
[7 empty] | 422 | 5310 | 1880579 | 2021-10-12 09:16 | 2021-10-12 16:15 | 419 | 11kV | 838 | 2 | HV | 3rd Party Action | 3rd Party Impact | 3rd Party Asset | Unplanned | Rain Heavy | N | At S10904 West Botany DMR - 11kv C phase Haz fuse operated Remarks: customers installation. Customers repaired own equipment | October | 2021 | 2022Q2 | 2022 |  |  |  | BAYSIDE | Unknown | Not Veg | 2021-10-12 | N | 419 | N | 4 | N | N | 1.1101 | 39.4971 | 612.3857
[7 empty] | 1333 | 16234 | 1880730 | 2021-10-12 17:44 | 2021-10-12 17:59 | 15 | 11kV | 12900 | 860 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 211930 2 fault operations A & B Phase A prot Hiset O/C A and B phase. B prot Hiset O/C A and B phase and MR User alarm 23. Palm Frong cnr Croudace Rd and Mitchell Ave. Excluded OMS 1880734/35/37 | October | 2021 | 2022Q2 | 2022 | 210:83466 | 210:83466 | ZN00210/083466 | NEWCASTLE | OH | Veg | 2021-10-12 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 9426.9395
[7 empty] | 1436 | 17712 | 1880759 | 2021-10-13 03:10 | 2021-10-13 10:51 | 461 | 11kV | 37039 | 119 | HV | Vegetation Blow/Fall In | Vegetation | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | At ZN12630 Peats Ridge, ex Panel 1, Rec 610987 Wise Ferry Lavender 10.2 has tripped Relays: OC trip and L/O Remarks: tree/branch on OH mains. tree near PT13629 | October | 2021 | 2022Q2 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-10-13 | N | 311.2521 | N | 6 | N | N | 1.1101 | 39.4971 | 27067.0087
[7 empty] | 955 | 11566 | 1880772 | 2021-10-13 07:41 | 2021-10-13 13:50 | 369 | 11kV | 1107 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At PT18621 The Ridgeway Awabakil 0.5, 'B & C' phase 10Amp HDO's operated Section of 11kv Panel 2 'Holgate' feeder at Zn12600 Lisarow Remarks: tree/branch on OH mains. B and C phase 11kv HDO's operated at PT18621. . Tiny stick across insulated 11kv bushings | October | 2021 | 2022Q2 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-10-13 | N | 369 | N | 6 | N | N | 1.1101 | 39.4971 | 808.9629
[7 empty] | 104 | 1350 | 1880893 | 2021-10-13 12:56 | 2021-10-13 15:46 | 170 | 11kV | 43138 | 266 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn116 Leichhardt - Pnl.1 -tripped on Earth Fault UG cable fault between S35867 Sw/B , S63942 Sw/A, S63706 Sw/A and S5437 Sw/A See 1881543 1881545 | October | 2021 | 2022Q2 | 2022 | ZN116:PA1 | ZN116:PA1 | ZN00116/000001 | INNER WEST | UG | Not Veg | 2021-10-13 | N | 162.1729 | N | 6 | N | N | 1.1101 | 39.4971 | 31523.978
[7 empty] | 1309 | 15930 | 1880779 | 2021-10-13 08:17 | 2021-10-13 18:50 | 633 | 11kV | 25287 | 99 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | 11kv iR.41066 Macdonalds Rd tripped Relays: OC trip, L/O Section of 11kv Panel 2 'Holgate' feeder at ZN12600 Lisarow Remarks: vehicle hit pole. Truck has hit and snapped pole. HV into LV at PT.18790 The Ridgeway Tapley Dist #2. Isolated from LB.44275 to LK.41374 tee to PT.18790, PT.14866, PT.13986, PT.14479. AP and CTW to L/W issued at PT.18790 | October | 2021 | 2022Q2 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2021-10-13 | N | 255.4242 | N | 6 | N | N | 1.1101 | 39.4971 | 18478.9938
[7 empty] | 1612 | 19605 | 1880989 | 2021-10-13 20:21 | 2021-10-13 21:42 | 81 | 11kV | 9696 | 121 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | At ZN12630 Peats Ridge, ex panel 11 Rec 46803 Wise Ferry Dog Trap 0.1 has tripped Relays: SEF, lock out Remarks: transformer failure. At ZN12630 Peats Ridge, ex Panel 11. At PT13778 Wise Ferry Expressway Left hand side HDO blown switching tag left region required to organise repairs ASAP | October | 2021 | 2022Q2 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2021-10-13 | N | 80.1322 | N | 6 | N | N | 1.1101 | 39.4971 | 7085.5508
[7 empty] | 1126 | 14260 | 1880961 | 2021-10-13 17:39 | 2021-10-14 00:01 | 382 | 11kV | 13600 | 54 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 211933 After trip and reclose. lock out. wire off pin at 4G-40013. Caused a pole fire. Excluded OMS 1880961, 1880974 | October | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-10-13 | N | 251.8519 | N | 6 | N | N | 1.1101 | 39.4971 | 9938.4789
[7 empty] | 1160 | 14569 | 1881093 | 2021-10-14 12:42 | 2021-10-14 13:55 | 73 | 11kV | 3285 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211934 B Phase DOLF : 40 Amp Excluded OMS 1881093 | October | 2021 | 2022Q2 | 2022 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Veg | 2021-10-14 | N | 73 | N | 10 | N | N | 1.1101 | 39.4971 | 2400.5811
[7 empty] | 493 | 5966 | 1881106 | 2021-10-14 13:52 | 2021-10-14 18:30 | 278 | 11kV | 277642 | 1483 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn1850 Bass Hill - pnl.32 tripped on: A,B & C phase OC Abnormal: S4343 Sw/A Closed with AB3297 Open Suspected UG cable fault between LB2986 and S47485 Sw/B tee PT1815 Universal Ave See 1881514 1881515 1881517 1881518 1881519 1881520 | October | 2021 | 2022Q2 | 2022 | ZN1850:PA32 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-10-14 | N | 187.2165 | N | 10 | N | N | 1.1101 | 39.4971 | 202892.5845
[7 empty] | 1276 | 15569 | 1881130 | 2021-10-14 15:38 | 2021-10-14 18:35 | 177 | 11kV | 14458 | 906 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | Zn3154 St Ives - Pnl.17 tripped & reclosed on: A phase IOC @ PT39 Waterhouse Torrens - 2 x HDOs blown (Roadside and footpath side) Customer reported PT was hit by lightning See 1881535 1881536 | October | 2021 | 2022Q2 | 2022 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Not Veg | 2021-10-14 | N | 15.9581 | N | 10 | N | N | 1.1101 | 39.4971 | 10565.48
[7 empty] | 1180 | 14735 | 1881221 | 2021-10-14 18:24 | 2021-10-14 18:57 | 33 | 11kV | 7986 | 242 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Kogarah Zn - Pnl.17 - LB64130 Opened for safety 11kV Mains at pole KO19568 hanging by a few strands | October | 2021 | 2022Q2 | 2022 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2021-10-14 | N | 33 | N | 10 | N | N | 1.1101 | 39.4971 | 5835.9333
[7 empty] | 1633 | 19760 | 1881158 | 2021-10-14 16:54 | 2021-10-14 19:07 | 132.6167 | 11kV | 79570 | 600 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Rain Wind Storm | N | HR HV bond. Switched around it. Put in as a DMA. Referred to Maintenance Oatley. Note: unable to find a control room report, however 16 calls were received of NS, LV or PS | October | 2021 | 2022Q2 | 2022 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2021-10-14 | N | 132.6167 | N | 10 | N | N | 1.1101 | 39.4971 | 58147.4091
[7 empty] | 387 | 5111 | 1881225 | 2021-10-14 17:38 | 2021-10-14 19:30 | 112 | 11kV | 11273 | 617 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Lightning | N | At S15011 Beacon Hill ex panel No4, Recloser 21685 Warringah Cornish tripped and reclosed on Relays: Overcurrent, IOC trip At S15011 Beacon Hill panel No.4 Relays: EFI, fault check, fram leakage At PT15463 Beacon Kalianna Road side HDO blown, 50A Field EFI - S17063 Tristram Danes Remarks: storm. Lightning | October | 2021 | 2022Q2 | 2022 | ZN15011:PA4 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | OH | Not Veg | 2021-10-14 | N | 18.2707 | N | 10 | N | N | 1.1101 | 39.4971 | 8237.9759
[7 empty] | 1294 | 15711 | 1881246 | 2021-10-14 19:27 | 2021-10-14 22:00 | 153 | 11kV | 81332 | 800 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | Zn14143 Somersby - Pnl.17 tripped, reclosed & locked out on: C phase OC Possible Lightning Strike See 1881527 1881528 1881529 1881530 | October | 2021 | 2022Q2 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2021-10-14 | N | 101.665 | N | 10 | N | N | 1.1101 | 39.4971 | 59435.0267
[7 empty] | 386 | 5077 | 1881268 | 2021-10-14 21:46 | 2021-10-14 23:21 | 95 | 11kV | 118984 | 1264 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | The 11kv Panel 3 'Oxford gorokan' CB at Zn.14892 Charmhaven tripped, reclosed and locked out on: Signals: 11kv trip Relays: A & B phase O/C, EFI, fault check lock out and timer Field EFIs: S.14575, S.12298 Remarks; weather related. Weather related storm | October | 2021 | 2022Q2 | 2022 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Veg | 2021-10-14 | N | 94.1329 | N | 10 | N | N | 1.1101 | 39.4971 | 86949.9978
[7 empty] | 305 | 3974 | 1881273 | 2021-10-14 23:25 | 2021-10-15 00:50 | 85 | 11kV | 5355 | 63 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | PT13655 Danbury Malvina - Footpath phase HDO fuse blown Transformer failure. See further outage CC1: 22-"Refer to SOp" FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | October | 2021 | 2022Q2 | 2022 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2021-10-14 | N | 85 | N | 10 | N | N | 1.1101 | 39.4971 | 3913.2761
[7 empty] | 536 | 6383 | 1881278 | 2021-10-15 01:02 | 2021-10-15 01:30 | 28 | 11kV | 2965 | 1264 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | ZN14892 Charmhaven Panel 3 'Oxford Gorokan' tripped and reclosed Relays: E/F, EFI, fault check, time and lock out Signals: 11kv trip EFI's: S14575, S.12298 Remarks: transformer failure. PT13655 Danbury Mavina HDO has operated twice within a few hours. Possible tank or surge arrestor issue. HDO's pulled and in LV//. | October | 2021 | 2022Q2 | 2022 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2021-10-15 | N | 2.3457 | N | 10 | N | N | 1.1101 | 39.4971 | 2166.7345
[7 empty] | 700 | 9048 | 1881380 | 2021-10-15 11:15 | 2021-10-15 12:20 | 65 | 11kV | 65 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211941 B Phase DOLF : 16 Amp Excluded OMS 1881380 | October | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-10-15 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 635 | 8237 | 1881397 | 2021-10-15 11:57 | 2021-10-15 13:27 | 90 | 11kV | 88950 | 1045 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN14144 Wamberal Zn, 11kv Panel 7 has tripped on: Relays: SEF Signals: 11kv trip Field EFIs: nil 11kV burnt off bond (road side phase) found on LB 44486 See 1883319, 1883320, 1881397 (record withdrawn) | October | 2021 | 2022Q2 | 2022 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2021-10-15 | N | 85.1196 | N | 10 | N | N | 1.1101 | 39.4971 | 65002.0364
[7 empty] | 30 | 316 | 1881425 | 2021-10-15 12:32 | 2021-10-15 13:51 | 79 | 11kV | 28045 | 355 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | ZN14892 Charmhaven Panel 9 'Advance Crowe' feeder tripped on: Relays: A & B phase OC and EF, reclose and lockout Signals: 11kV trip, AR lockout Field EFIs: nil Branch on 11kV mains adjacent S14678 Heritage Eden. | October | 2021 | 2022Q2 | 2022 | ZN14892:PA9 | ZN14892:PA9 | ZN14892/000009 | CENTRAL COAST | OH | Veg | 2021-10-15 | N | 79 | N | 10 | N | N | 1.1101 | 39.4971 | 20494.4588
[7 empty] | 1335 | 16318 | 1883426 | 2021-10-15 13:08 | 2021-10-15 15:25 | 137 | 11kV | 6302 | 46 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Wind Strong | N | PT 14196 Watanobbi Cuttler Was found with the centre phase 11kV dropper burnt off (Ex ZN14891 Wyong Panel 5). | October | 2021 | 2022Q2 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2021-10-15 | N | 137 | N | 10 | N | N | 1.1101 | 39.4971 | 4605.3157
[7 empty] | 869 | 10797 | 1881456 | 2021-10-15 13:01 | 2021-10-15 16:11 | 190 | 11kV | 239324 | 1589 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN4545 Meadowbank 11kv VCB panel 44 "S-1575" feeder tripped on - Relays: micom P122 Relay -O/C, E/fault Signals: 11kv trip Field EFIs: Nil Abnormal: Sw/B closed @ S4667 John Winborne, LB479 open and defective Remarks: cause not ascertained. No fault found again on this feeder which has tripped multiple times in last few months | October | 2021 | 2022Q2 | 2022 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Veg | 2021-10-15 | N | 150.613 | N | 10 | N | N | 1.1101 | 39.4971 | 174890.9203
[7 empty] | 1069 | 13764 | 1881604 | 2021-10-15 16:30 | 2021-10-15 18:00 | 90 | 11kV | 180 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 211945 Faulty Crossarm @ GS-83319 Excluded OMS 1881604 | October | 2021 | 2022Q2 | 2022 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2021-10-15 | N | 90 | N | 10 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 842 | 10405 | 1881418 | 2021-10-15 12:20 | 2021-10-15 21:15 | 535 | 11kV | 12905 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 211948 tree on mains at CV-53681 Excluded OMS 1881418 | October | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-10-15 | N | 280.5435 | N | 10 | N | N | 1.1101 | 39.4971 | 9430.5934
[7 empty] | 445 | 5491 | 1881417 | 2021-10-15 12:19 | 2021-10-15 21:25 | 546 | 11kV | 21573 | 221 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S14891 Wyong, Ex Panel 5, R62705 Jilliby Durren has tripped on OC trip Remarks: OH down. 11kv OH down adjacent to PT13266 Smiths Durren 1.9 | October | 2021 | 2022Q2 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2021-10-15 | N | 97.6154 | N | 10 | N | N | 1.1101 | 39.4971 | 15764.9121
[7 empty] | 401 | 5174 | 1881595 | 2021-10-15 17:35 | 2021-10-15 22:40 | 305 | 11kV | 38728 | 180 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 211946 2 fault operations Wire down from pole 4I-40039 towards Sw 33238 Excluded OMS 1881595 | October | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-10-15 | N | 215.1556 | N | 10 | N | N | 1.1101 | 39.4971 | 28301.2801
[7 empty] | 13 | 185 | 1881700 | 2021-10-16 12:33 | 2021-10-16 14:40 | 127 | 11kV | 127 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211950 A phase tapping open at pole DP-10101. Excluded OMS 1881700 | October | 2021 | 2022Q2 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2021-10-16 | N | 127 | N | 7 | N | N | 1.1101 | 39.4971 | 92.8079
[7 empty] | 845 | 10439 | 1881739 | 2021-10-16 15:23 | 2021-10-16 18:02 | 159 | 11kV | 44038 | 947 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn9245 Engadine - Pnl.15 tripped on: A & B phase IOC Cause not ascertained See 1882206 1882207 | October | 2021 | 2022Q2 | 2022 | ZN9245:PA15 | ZN9245:PA15 | ZN09245/000015 | SUTHERLAND | OH | Veg | 2021-10-16 | N | 46.5026 | N | 7 | N | N | 1.1101 | 39.4971 | 32181.6715
[7 empty] | 449 | 5519 | 1883506 | 2021-10-16 16:04 | 2021-10-16 18:05 | 121 | 11kV | 92900 | 1589 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn4545 Meadowbank - Pnl.44 tripped on IOC Abnormal: S4667 Sw/B closed with LB479 Open (DMA) 11kV Mains clashing outside 14 Emu St West Ryde LB61774 is defective and was unable to be used as an isolation point to return feeder back to service earlier. Lineworker required to open and repair. PT2491 restored via LV // See 1883506 1883508 1883509 | October | 2021 | 2022Q2 | 2022 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Not Veg | 2021-10-16 | N | 58.4644 | N | 7 | N | N | 1.1101 | 39.4971 | 67888.5799
[7 empty] | 1012 | 12739 | 1881783 | 2021-10-16 16:52 | 2021-10-16 19:00 | 127.8 | 11kV | 127.8 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 211953 Live Line Clamp detached | October | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-10-16 | N | 127.8 | N | 7 | N | N | 1.1101 | 39.4971 | 93.3925
[7 empty] | 1649 | 20060 | 1881760 | 2021-10-16 15:59 | 2021-10-16 19:15 | 196 | 11kV | 392 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 211951 Live Line Lead detached Excluded OMS 1881760 | October | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2021-10-16 | N | 196 | N | 7 | N | N | 1.1101 | 39.4971 | 286.462
[7 empty] | 1366 | 16739 | 1881742 | 2021-10-16 15:24 | 2021-10-16 19:45 | 261 | 11kV | 5562 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC45083 SMITHS RD - opened for safety after EMSO reported 11kV down near AL44783 See 1882200 1882201 | October | 2021 | 2022Q2 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2021-10-16 | N | 92.7 | N | 7 | N | N | 1.1101 | 39.4971 | 4064.5455
[7 empty] | 4 | 62 | 1881804 | 2021-10-16 21:15 | 2021-10-16 23:35 | 140 | 11kV | 1820 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | Broken HV xarm Allens sub 15496 dq | October | 2021 | 2022Q2 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2021-10-16 | N | 140 | N | 7 | N | N | 1.1101 | 39.4971 | 1330.0023
[7 empty] | 914 | 11240 | 1881862 | 2021-10-17 12:29 | 2021-10-17 14:30 | 121 | 11kV | 21901 | 181 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Kogarah Zn Pnl.17 - Bond burnt off (found arcing) on tee off pole to S10660 Middle phase on LB30762 side | October | 2021 | 2022Q2 | 2022 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2021-10-17 | N | 121 | N | 1 | N | N | 1.1101 | 39.4971 | 16004.6048
[7 empty] | 1249 | 15219 | 1882039 | 2021-10-18 12:47 | 2021-10-18 13:53 | 66 | 11kV | 46284 | 731 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills Pnl.38 tripped on O/C & E/F Field EFIs:S5613, S5929, S6109, S5927, S8661, S8569, S6886, S49065, S6125, S5711 & S6290 UG cable fault between S6290 Sw/B and S5616 Sw/A See 1883165 1883167 | October | 2021 | 2022Q2 | 2022 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | UG | Not Veg | 2021-10-18 | N | 63.316 | N | 3 | N | N | 1.1101 | 39.4971 | 33822.9821
[7 empty] | 1661 | 20178 | 1882097 | 2021-10-18 16:23 | 2021-10-18 16:31 | 8 | 11kV | 3976 | 497 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Previous Storm | N | Section of 11kV feeder ex Matraville Zn Pnl.44 interrupted from S4084 Sw/B after Dop found 11kV fuse switch at CP.2552 Rifle Range Abnormal: PT1993 & PT1238 already interrupted due to ongoing fault from 14/10. | October | 2021 | 2022Q2 | 2022 | ZN1788:PA44 | ZN1788:PA44 | ZN01788/000044 | RANDWICK | OH | Not Veg | 2021-10-18 | N | 8 | N | 3 | N | N | 1.1101 | 39.4971 | 2905.5435
[7 empty] | 249 | 3068 | 1882113 | 2021-10-18 20:37 | 2021-10-18 22:55 | 138 | 11kV | 40848 | 296 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 211963 Broken Xarm IU-20218. Interrupted to repair. Excluded OMS 1882113 | October | 2021 | 2022Q2 | 2022 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2021-10-18 | N | 138 | N | 3 | N | N | 1.1101 | 39.4971 | 29850.5136
[7 empty] | 134 | 1638 | 1882250 | 2021-10-19 13:31 | 2021-10-19 14:50 | 79 | 11kV | 1817 | 23 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211965 Conductor off pin pole 4K-90001 | October | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-10-19 | N | 79 | N | 2 | N | N | 1.1101 | 39.4971 | 1327.81
[7 empty] | 1477 | 18250 | 1882293 | 2021-10-19 17:15 | 2021-10-19 18:35 | 80 | 11kV | 57280 | 716 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kv Panel 3 "Oxford Gorokan" supplied from ZN 14892 CHARMHAVEN Report of dim lights beyond AB 42481. Footpath side phase 11kV bond found burnt on load side of AB 42481 (left open DMA recorded) 1882293 - record withdrawn. | October | 2021 | 2022Q2 | 2022 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2021-10-19 | N | 80 | N | 2 | N | N | 1.1101 | 39.4971 | 41858.5345
[7 empty] | 162 | 2006 | 1882342 | 2021-10-20 05:17 | 2021-10-20 08:50 | 213 | 11kV | 639 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 211971 DOLF : 10 Amp Excluded OMS 1882342 | October | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-10-20 | N | 213 | N | 3 | N | N | 1.1101 | 39.4971 | 466.9624
[7 empty] | 991 | 12109 | 1882344 | 2021-10-20 06:46 | 2021-10-20 09:20 | 154 | 11kV | 154 | 1 | HV | Vegetation Grow In | Vegetation | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 211972 Single phase DOLF : 10 Amp Excluded OMS 1882344 | October | 2021 | 2022Q2 | 2022 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Veg | 2021-10-20 | N | 154 | N | 3 | N | N | 1.1101 | 39.4971 | 112.5387
[7 empty] | 264 | 3390 | 1882498 | 2021-10-20 17:50 | 2021-10-20 19:45 | 115 | 11kV | 11270 | 98 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 211975 Hazemeyer Insulating tubes slipped of Tx terminals. Exposing metal terminals. Minimal Clearance. Excluded OMS 1882498 | October | 2021 | 2022Q2 | 2022 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2021-10-20 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 8235.7836
[7 empty] | 937 | 11341 | 1882652 | 2021-10-21 15:07 | 2021-10-21 16:55 | 108 | 11kV | 324 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 211977 No Cause Found (Not Storm Condition) 16Amp, Phase A,Line DOLF Line fuse 41271 blown also refer to OMS 1882652 SOP FITZPATRICK S DOP KEEN A | October | 2021 | 2022Q2 | 2022 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2021-10-21 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 1008 | 12637 | 1882693 | 2021-10-21 20:06 | 2021-10-21 21:08 | 62 | 11kV | 63674 | 1027 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | At Mortdale Zn 11kV Panel 21L feeder tripped and reclosed to lockout Relays: A,B and C phase IOC and timed, lockout, timing Field EFIs: Nil Suspected bat caused flashover on river crossing, mains inspected clear, further inspection requested for daylight hours. Please see 1883205 from previous evening trip and reclose. | October | 2021 | 2022Q2 | 2022 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Not Veg | 2021-10-21 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 46531.0811
[7 empty] | 1541 | 18876 | 1882691 | 2021-10-21 20:05 | 2021-10-21 21:59 | 114 | 11kV | 97821 | 1094 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At Zn9550 Gwawley Bay 11kV feeder panel 42 tripped on Relays: E/F and EFI Cause not ascertained for outage Note: 33kV Feeder No725 Tripped at the same time in vicinity of 11KV feeder by no related cause See OMS 1882691 1883224 1883225 | October | 2021 | 2022Q2 | 2022 | ZN9550:PA42 | ZN9550:PA42 | ZN09550/000042 | SUTHERLAND | OH | Veg | 2021-10-21 | N | 89.4159 | N | 3 | N | N | 1.1101 | 39.4971 | 71484.7016
[7 empty] | 602 | 7639 | 1882720 | 2021-10-22 00:10 | 2021-10-22 05:25 | 315 | 11kV | 20295 | 67 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211978 also refer to oms 1882720 open tapping 11kV links 74313 system abnormal 64944 open & 75204 closed section isolated for repairs DOP AUSTIN G SOP WATSON J | October | 2021 | 2022Q2 | 2022 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2021-10-22 | N | 302.9104 | N | 2 | N | N | 1.1101 | 39.4971 | 14830.9874
[7 empty] | 1342 | 16361 | 1882806 | 2021-10-22 13:51 | 2021-10-22 16:02 | 131 | 11kV | 296816 | 2482 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn690 Campsie - Pnl.25 tripped on Earth Fault UG cable hit in Rail corridor "22 Loftus Street Campsie" Front line section of feeder between Pnl.25, S3773 Sw/A, S1976 Sw/A and S3834 Sw/B | October | 2021 | 2022Q2 | 2022 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-10-22 | N | 119.5874 | N | 2 | N | N | 1.1101 | 39.4971 | 216904.3782
[7 empty] | 919 | 11258 | 1881222 | 2021-10-14 18:01 | 2021-10-22 18:00 | 11519 | 11kV | 115190 | 10 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Previous Storm | N | CP.2552 Rifle Range - 11kV fuse switch tripped Earth blown off UGOH, possibly caused by earlier lightning. Delay due to multiple investigations to diagnose and fix the issues - 19/10/2021 08:43 t43340: HV repairs done on PT 1238 but 11kV Control Point failed when line was re.energised. See further outage 1883161 | October | 2021 | 2022Q2 | 2022 | ZN1788:PA44 | ZN1788:PA44 | ZN01788/000044 | RANDWICK | OH | Not Veg | 2021-10-14 | N | 11519 | N | 10 | N | N | 1.1101 | 39.4971 | 84177.4545
[7 empty] | 1513 | 18586 | 1882946 | 2021-10-23 17:44 | 2021-10-23 20:50 | 186 | 11kV | 7384 | 40 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 211983 Pole EF40045 tree branch on line Excluded OMS 1882946 | October | 2021 | 2022Q2 | 2022 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2021-10-23 | N | 184.6 | N | 8 | N | N | 1.1101 | 39.4971 | 5396.0094
[7 empty] | 1384 | 16997 | 1882968 | 2021-10-23 20:33 | 2021-10-23 22:42 | 129 | 11kV | 129 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212000 DOLF : 10 Amp | October | 2021 | 2022Q2 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2021-10-23 | N | 129 | N | 8 | N | N | 1.1101 | 39.4971 | 94.2694
[7 empty] | 74 | 906 | 1882918 | 2021-10-23 14:29 | 2021-10-24 01:05 | 636 | 11kV | 1272 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 211982 B Phase Blown tapping on UG/OH pole AH 61402 ( this pole no. is shown on DNMS as AH 61482) Excluded OMS 1882918 | October | 2021 | 2022Q2 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-10-23 | N | 636 | N | 8 | N | N | 1.1101 | 39.4971 | 929.5401
[7 empty] | 1370 | 16767 | 1882954 | 2021-10-23 18:34 | 2021-10-24 01:54 | 440 | 11kV | 2200 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212003 A Phase DOLF : 10 Amp Excluded OMS 1882954 | October | 2021 | 2022Q2 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2021-10-23 | N | 440 | N | 8 | N | N | 1.1101 | 39.4971 | 1607.6951
[7 empty] | 302 | 3839 | 1882966 | 2021-10-23 20:31 | 2021-10-24 02:45 | 374 | 11kV | 23562 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212004 A Phase DOLF : 31 Amp Excluded OMS 1882966 | October | 2021 | 2022Q2 | 2022 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2021-10-23 | N | 374 | N | 8 | N | N | 1.1101 | 39.4971 | 17218.4146
[7 empty] | 1573 | 19231 | 1882956 | 2021-10-23 18:40 | 2021-10-24 03:05 | 505 | 11kV | 49783 | 192 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 211986 3 fault operations Branch found on OHM beyond LF 74689 remove branch & replaced blown LF, Sw 74434 closed and tripped again. Feeder patroled again and no fault found Excluded OMS 1882956 | October | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-10-23 | N | 259.2865 | N | 8 | N | N | 1.1101 | 39.4971 | 36379.9481
[7 empty] | 256 | 3237 | 1882975 | 2021-10-23 21:34 | 2021-10-24 03:30 | 356 | 11kV | 12104 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212005 A & C Phase DOLF : 16 Amp Excluded OMS 1882975 | October | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-10-23 | N | 356 | N | 8 | N | N | 1.1101 | 39.4971 | 8845.2462
[7 empty] | 1320 | 16133 | 1882991 | 2021-10-24 06:22 | 2021-10-24 09:20 | 177.95 | 11kV | 2847.2 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212008 A Phase LINE DOLF : 10 Amp also replaced Sub 51243:11kV B Phase DOLF : 10 Amp refer to LID 212006 CC1: 22-"Refer to SOp" | October | 2021 | 2022Q2 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2021-10-24 | N | 177.95 | N | 4 | N | N | 1.1101 | 39.4971 | 2080.6498
[7 empty] | 589 | 7442 | 1883005 | 2021-10-24 07:41 | 2021-10-24 10:45 | 184 | 11kV | 552 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212010 A Phase DOLF : 10 Amp Excluded OMS 1883005 | October | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-10-24 | N | 184 | N | 4 | N | N | 1.1101 | 39.4971 | 403.3853
[7 empty] | 252 | 3128 | 1882955 | 2021-10-23 18:37 | 2021-10-24 11:47 | 1030 | 11kV | 21388 | 106 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 211987 2 fault operations A & C phases Overcurrent 4 bays 11kV OHM down from pole 8L-80402 Excluded OMS 1882955 | October | 2021 | 2022Q2 | 2022 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2021-10-23 | N | 201.7736 | N | 8 | N | N | 1.1101 | 39.4971 | 15629.7196
[7 empty] | 1159 | 14546 | 1883009 | 2021-10-24 08:52 | 2021-10-24 15:25 | 393 | 11kV | 786 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212015 A Phase DOLF : 10 Amp Excluded OMS 1883009 | October | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-10-24 | N | 393 | N | 4 | N | N | 1.1101 | 39.4971 | 574.3856
[7 empty] | 427 | 5351 | 1883082 | 2021-10-24 22:31 | 2021-10-25 03:15 | 284 | 11kV | 95661 | 1370 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN9037 Miranda 11kV Panel 16 tripped on: Relays: timed overcurent A + C phase, earth fault, EFI, timing relay, lockout relay Signals: 11kV trip, tx3 group each, zone earth EFIs: 79727, 77621, 9780, 79392, 47294, 77093 11kV UG cable fault from S77621 University Kingsway No.3 SW/B to S9133 Karimbla Wandella to S9404 Westfield Miranda No.2 see 1883330, 1883331, 18833332, withdrawn- 1883082, 1883084, 1883085 | October | 2021 | 2022Q2 | 2022 | ZN9037:PA16 | ZN9037:PA16 | ZN09037/000016 | SUTHERLAND | UG | Not Veg | 2021-10-24 | N | 69.8255 | N | 4 | N | N | 1.1101 | 39.4971 | 69906.2373
[7 empty] | 271 | 3505 | 1882761 | 2021-10-25 13:05 | 2021-10-25 14:55 | 110 | 11kV | 990 | 9 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 212023 section isolated to repair broken x-arm during storm 23/10/2021 Excluded OMS 1882761 | October | 2021 | 2022Q2 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2021-10-25 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 723.4628
[7 empty] | 475 | 5788 | 1883308 | 2021-10-25 23:29 | 2021-10-26 00:31 | 61.9333 | 11kV | 36788.4 | 594 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At ZN 965 Pennant Hills 11kV feeder panel 22 "Warne Rosemount, etc" feeder tripped on: Relays: EF and EFI At PT1667 Centre and roadside HDO operted 63amp MGK type Field EFIs: S5847 Possum caused flashover at PT 1667, no apparent damage, supply restored. | October | 2021 | 2022Q2 | 2022 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | OH | Not Veg | 2021-10-25 | N | 61.9333 | N | 2 | N | N | 1.1101 | 39.4971 | 26883.8776
[7 empty] | 1594 | 19454 | 1883318 | 2021-10-26 07:32 | 2021-10-26 09:00 | 88 | 11kV | 264 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212025 10 Amp, Phase C, Substation DOLF also refer to OMS 1883318 SOP McGUIRE L DOP BROWN M | October | 2021 | 2022Q2 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2021-10-26 | N | 88 | N | 5 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 301 | 3833 | 1883311 | 2021-10-26 06:34 | 2021-10-26 10:02 | 208 | 11kV | 256998 | 1572 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 1788 Matraville, 11kV Panel 17 "S4631 Barown Gwydir" tripped under fault B protection relays: Earth fault, C phase OC, EFI 11kV trip signal Field EFIs: S4631 to S62425, S49663, S2306 See 1883552, 1883557, 1883558, 1883559, 1883560, 1883562, 1883564, RECORDS WITHDRAWN 1883563, 1883311, 1883317 | October | 2021 | 2022Q2 | 2022 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2021-10-26 | N | 163.4847 | N | 5 | N | N | 1.1101 | 39.4971 | 187806.5582
[7 empty] | 747 | 9421 | 1883371 | 2021-10-26 10:52 | 2021-10-26 14:00 | 188 | 11kV | 752 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 212026 10Amp Substation DOLF also refer to "OMS 1883371 Replace arrestor" SOP McGUIRE L DOP THOMPSON D | October | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-10-26 | N | 188 | N | 5 | N | N | 1.1101 | 39.4971 | 549.5394
[7 empty] | 689 | 8768 | 1883433 | 2021-10-26 14:36 | 2021-10-26 15:40 | 64.3333 | 11kV | 257.3333 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 212027 M Brown assigned section isolated for repairs to x-arm pole BI-70126, power restored 1540.MdV SOP De VRIES M DOP BROWN M | October | 2021 | 2022Q2 | 2022 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2021-10-26 | N | 64.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 188.0516
[7 empty] | 1660 | 20173 | 1883466 | 2021-10-26 17:05 | 2021-10-26 17:50 | 45 | 11kV | 45 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | LID 212028 10 Amp, Single Phase, Substation DOLF also refer to OMS 1883466 SOP De VRIES M DOP AUSTIN G | October | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-10-26 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 136 | 1661 | 1883527 | 2021-10-27 10:58 | 2021-10-27 12:29 | 91 | 11kV | 213413 | 2594 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S15006 Dee Why West Panel 9 Tripped on Siganls: 11kV Trip, Zone Earth, Fault Check TX1 Relays: IOC B phase, Fault Check, EFI Cause: Suspect cable maybe damaged by civil works @ 20 Westminster Avenue See OMS 1883734 1883735 1883527 | October | 2021 | 2022Q2 | 2022 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2021-10-27 | N | 82.2718 | N | 3 | N | N | 1.1101 | 39.4971 | 155955.9258
[7 empty] | 1244 | 15180 | 1883574 | 2021-10-27 14:18 | 2021-10-27 15:30 | 72 | 11kV | 78840 | 1095 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36800 Waverley - Pnl.46L tripped on Earth Fault UG cable fault between S.62998 Sw/B and S76970 Sw/A See 1883699 1883700 | October | 2021 | 2022Q2 | 2022 | ZN36800:PA46 | ZN36800:PA46 | ZN36800/000046 | WAVERLEY | UG | Not Veg | 2021-10-27 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 57613.9466
[7 empty] | 736 | 9369 | 1883601 | 2021-10-27 16:35 | 2021-10-27 18:22 | 107 | 11kV | 642 | 6 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 212029 Broken stay wire on pole IQ-41707. Crews isolated to carry out repairs SOP S Fitzpatrick DOP R Mansini | October | 2021 | 2022Q2 | 2022 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2021-10-27 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 469.1547
[7 empty] | 466 | 5721 | 1883636 | 2021-10-28 03:17 | 2021-10-28 04:05 | 48 | 11kV | 3264 | 68 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT11009 Plane Blackwall - Roadside HDO operated Possum found at base of PT | October | 2021 | 2022Q2 | 2022 | ZN12660:PA11 | ZN12660:PA11 | ZN12660/000011 | CENTRAL COAST | OH | Not Veg | 2021-10-28 | N | 48 | N | 2 | N | N | 1.1101 | 39.4971 | 2385.2349
[7 empty] | 1610 | 19582 | 1884329 | 2021-10-28 12:58 | 2021-10-28 13:40 | 42 | 11kV | 3822 | 91 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 212030 Rusted x-arm brace at PT 8040 Harry. isolated to replace under AP. | October | 2021 | 2022Q2 | 2022 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2021-10-28 | N | 42 | N | 2 | N | N | 1.1101 | 39.4971 | 2793.0049
[7 empty] | 682 | 8696 | 1883810 | 2021-10-29 02:01 | 2021-10-29 03:30 | 89 | 11kV | 110312 | 1264 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.6 tripped on O/C & E/F UG cable fault between S.6946 Sw/D and S3494 Sw/B See 1884325 1884326 | October | 2021 | 2022Q2 | 2022 | ZN35600:PA6 | ZN35600:PA6 | ZN35600/000006 | RANDWICK | UG | Not Veg | 2021-10-29 | N | 87.2722 | N | 5 | N | N | 1.1101 | 39.4971 | 80612.7559
[7 empty] | 1329 | 16205 | 1883832 | 2021-10-29 08:08 | 2021-10-29 12:15 | 247 | 11kV | 494 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212033 broken tapping to LLC @sub 46550 JMH Excluded OMS 1883832 | October | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2021-10-29 | N | 247 | N | 5 | N | N | 1.1101 | 39.4971 | 361.0006
[7 empty] | 1317 | 16056 | 1883906 | 2021-10-29 13:15 | 2021-10-29 16:35 | 200 | 11kV | 800 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 212037 This Line fuse blows all the time when windy. Redesign required. Email sent to J.Oswald | October | 2021 | 2022Q2 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2021-10-29 | N | 200 | N | 5 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 1378 | 16894 | 1883899 | 2021-10-29 12:54 | 2021-10-29 16:51 | 237 | 11kV | 18244 | 112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212039 1 faulty operation SEF trip Tree on mains pole NG-77011 | October | 2021 | 2022Q2 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2021-10-29 | N | 162.8929 | N | 5 | N | N | 1.1101 | 39.4971 | 13332.1771
[7 empty] | 1098 | 13978 | 1884052 | 2021-10-29 18:25 | 2021-10-29 21:48 | 203 | 11kV | 70441 | 347 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Ex Balgowlah North Pnl.8 - AB20332 has an open bond Abnormal: S48811 Sw/B Closed with S17020 Sw/B Open | October | 2021 | 2022Q2 | 2022 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Not Veg | 2021-10-29 | N | 203 | N | 5 | N | N | 1.1101 | 39.4971 | 51476.2051
[7 empty] | 697 | 8953 | 1884093 | 2021-10-30 02:22 | 2021-10-30 05:16 | 174 | 11kV | 121004 | 858 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn12600 Lisarow - Pnl.13 tripped on: C phase O/C Cause not ascertained See 1884423 1884424 1884425 1884426 | October | 2021 | 2022Q2 | 2022 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2021-10-30 | N | 141.0303 | N | 4 | N | N | 1.1101 | 39.4971 | 88426.1542
[7 empty] | 237 | 2938 | 1884102 | 2021-10-30 08:40 | 2021-10-30 15:00 | 380 | 11kV | 8406 | 45 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212043 interrupt to replace dead end that broke | October | 2021 | 2022Q2 | 2022 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2021-10-30 | N | 186.8 | N | 4 | N | N | 1.1101 | 39.4971 | 6142.8569
[7 empty] | 1523 | 18682 | 1884173 | 2021-10-30 13:52 | 2021-10-30 15:08 | 76 | 11kV | 8232 | 250 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.51 tripped on C Phase IOC and Earth Fault UG cable fault between S.65942 Sw/B, S35643 Sw/B and S78729 Sw/F See 1884315 1884316 1884317 | October | 2021 | 2022Q2 | 2022 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | UG | Not Veg | 2021-10-30 | N | 32.928 | N | 4 | N | N | 1.1101 | 39.4971 | 6015.7028
[7 empty] | 1501 | 18467 | 1884200 | 2021-10-30 17:38 | 2021-10-30 18:52 | 74 | 11kV | 74 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 212048 B Phase DOLF : 31 Amp B Phase DOLF fuse carrier Burnt in half Replaced and supply restored Excluded OMS 1884200 | October | 2021 | 2022Q2 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2021-10-30 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 1495 | 18398 | 1884229 | 2021-10-31 09:17 | 2021-10-31 11:00 | 103 | 11kV | 7416 | 72 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT48458 Heath Como - Middle phase HDO operated Fuse fatigue | October | 2021 | 2022Q2 | 2022 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2021-10-31 | N | 103 | N | 1 | N | N | 1.1101 | 39.4971 | 5419.3941
[7 empty] | 1381 | 16926 | 1884470 | 2021-11-01 16:48 | 2021-11-01 17:45 | 57 | 11kV | 171 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212050 Single phase DOLF : 10 Amp Excluded OMS 1884470 | November | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-11-01 | N | 57 | N | 2 | N | N | 1.1101 | 39.4971 | 124.9618
[7 empty] | 54 | 655 | 1884490 | 2021-11-01 19:35 | 2021-11-01 22:50 | 195 | 11kV | 20475 | 105 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212053 Sub 27088 Faulty DOLF dropper & defective LV assembly Excluded OMS 1884490 | November | 2021 | 2022Q2 | 2022 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2021-11-01 | N | 195 | N | 2 | N | N | 1.1101 | 39.4971 | 14962.5261
[7 empty] | 1268 | 15486 | 1884558 | 2021-11-02 09:00 | 2021-11-02 09:41 | 41 | 11kV | 50348 | 1228 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 12690 BERKELEY VALE - 11kV Panel 19 "Corella Enterprise, etc" feeder tripped on: Relays: A and B phase IOC Signals: 11kV trip Field EFIs: nil Tree trimmer at 25 Kilkenny Parade, Berkeley Vale. Dop advised and check okay. | November | 2021 | 2022Q2 | 2022 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2021-11-02 | N | 41 | N | 4 | N | N | 1.1101 | 39.4971 | 36792.8334
[7 empty] | 1372 | 16810 | 1884732 | 2021-11-02 15:39 | 2021-11-02 17:13 | 94 | 11kV | 94 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of 11kV Panel 33 'MacMasters Beach' at Zn 12570 Avoca 11kV Recloser 45098 Kincumber Tip tripped: Relays: L/O Patrolled no cause found. Customer contact spoken to Simon Wood 0417 746 605. | November | 2021 | 2022Q2 | 2022 |  |  |  | CENTRAL COAST | OH | Veg | 2021-11-02 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 527 | 6249 | 1884678 | 2021-11-02 18:32 | 2021-11-02 21:01 | 149 | 11kV | 446 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex ZN 7900 Kirrawee Panel 20 - 11kV RECLOSER CO.35006 National Park, tripped, reclosed and locked out on: Relays: lockout, OC Cause not ascertained. See 1885103, 1885104, 1884678 (record withdrawn) | November | 2021 | 2022Q2 | 2022 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2021-11-02 | N | 148.6667 | N | 4 | N | N | 1.1101 | 39.4971 | 325.9236
[7 empty] | 455 | 5639 | 1884699 | 2021-11-02 21:40 | 2021-11-02 23:01 | 81 | 11kV | 123885 | 1670 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN35550 TOP RYDE 11kV Panel 21 'S47334' tripped on: Relays: E Fault, EFI Field EFIs: 8310 only Signalds: 11kV trip UG Fault from S48849 SW/A to S8310 SW/B to S79425 SW/B NETWORK WAS SWITCHED ABNORMALLY SW/A CLOSED @ 8310 SW/A OPEN @ 65683 See 1884893, 1884894, 1884898, 1884701 (withdrawn), 1884699 (withdrawn) | November | 2021 | 2022Q2 | 2022 | ZN35500:PA31 | ZN35500:PA31 | ZN35500/000031 | RYDE | UG | Not Veg | 2021-11-02 | N | 74.1826 | N | 4 | N | N | 1.1101 | 39.4971 | 90531.504
[7 empty] | 343 | 4760 | 1885180 | 2021-11-03 02:57 | 2021-11-03 05:22 | 145 | 11kV | 221413 | 2151 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2602 Clovellt Zone 11kV Panel30 Tripped on Signals: 11kV Trip, Zone Earth, No2 Group Earth Relays: Earth Fault, Fault Check, Group Earth Relays: Earth Fault, Fault CHeck, EFI Field EFI's Nil Cause: UG fault between S3229 Farnham Ave SW/B and S4107 Carr Byron Sw/A to S1183 Glebe St SW/D See OMS 1887352 1887353 1887354 1887355 1887357 1887358 | November | 2021 | 2022Q2 | 2022 | ZN2602:PA30 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | UG | Not Veg | 2021-11-03 | N | 102.9349 | N | 3 | N | N | 1.1101 | 39.4971 | 161802.0898
[7 empty] | 1046 | 13427 | 1884711 | 2021-11-03 00:13 | 2021-11-03 06:09 | 355.6833 | 11kV | 14938.7 | 42 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 212057 open 11kV bond at links 74755 | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2021-11-03 | N | 355.6833 | N | 3 | N | N | 1.1101 | 39.4971 | 10916.7613
[7 empty] | 326 | 4424 | 1884876 | 2021-11-03 22:43 | 2021-11-04 00:25 | 102 | 11kV | 4080 | 40 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | At PT14063 Stephenson Kipling 31.5A HDO blown on Roadsite phase Signals: Zone and Group Earth with EFI Cause: Suspect Possum at PT14063 | November | 2021 | 2022Q2 | 2022 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2021-11-03 | N | 102 | N | 3 | N | N | 1.1101 | 39.4971 | 2981.5437
[7 empty] | 234 | 2837 | 1884880 | 2021-11-04 03:41 | 2021-11-04 07:40 | 239 | 11kV | 1673 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212061 A Phase DOLF : 10 Amp Excluded OMS 1884887 | November | 2021 | 2022Q2 | 2022 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2021-11-04 | N | 239 | N | 4 | N | N | 1.1101 | 39.4971 | 1222.5791
[7 empty] | 192 | 2468 | 1885051 | 2021-11-04 17:20 | 2021-11-04 18:40 | 80 | 11kV | 11120 | 139 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | AT ZN2466 Flemington Panel 2 on: Earth Fault, EFI, Fault Check Field Operations: NIL Cause: 11kV Cable fault between ZN24666 Flemington Pa2 and S6019 Day Derby No2 and S7661 Aquatic Temp | November | 2021 | 2022Q2 | 2022 | ZN2466:PA2 | ZN2466:PA2 | ZN02466/000002 | PARRAMATTA | UG | Not Veg | 2021-11-04 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 8126.168
[7 empty] | 1678 | 20392 | 1885079 | 2021-11-04 21:10 | 2021-11-04 22:20 | 70 | 11kV | 5180 | 74 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn3154 St Ives - Panel 25 Relays: Zone Earth, Group Earth PT1753 Hayle Woodury 11kV HDO 31.5A fuse blown Cause: Possum found on HDO and TX See OMS 1885080 1885081 1885079 | November | 2021 | 2022Q2 | 2022 | ZN3154:PA25 | ZN3154:PA25 | ZN03154/000025 | KU-RING-GAI | OH | Not Veg | 2021-11-04 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 3785.3912
[7 empty] | 65 | 824 | 1884996 | 2021-11-04 13:00 | 2021-11-04 22:25 | 565 | 11kV | 141585 | 1773 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 212063 3 fault operations 3 phase Earth Fault UG fault beyond UGOH OR-30086 Excluded OMS 1884996 | November | 2021 | 2022Q2 | 2022 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | UG | Not Veg | 2021-11-04 | N | 79.8562 | N | 4 | N | N | 1.1101 | 39.4971 | 103466.1419
[7 empty] | 588 | 7418 | 1885191 | 2021-11-05 15:00 | 2021-11-05 16:50 | 110 | 11kV | 220 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212067 A & B Phase DOLF : 10 Amp Crow at base of pole Excluded OMS 1885191 | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2021-11-05 | N | 110 | N | 1 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 309 | 4056 | 1886243 | 2021-11-06 20:27 | 2021-11-06 20:38 | 11 | 11kV | 14047 | 1277 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn15005 Belrose - Pnl.6 tripped & reclosed on OC & EF Dop found possum at REC24831 | November | 2021 | 2022Q2 | 2022 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2021-11-06 | N | 11 | N | 1 | N | N | 1.1101 | 39.4971 | 10265.1333
[7 empty] | 1575 | 19269 | 1885327 | 2021-11-07 04:49 | 2021-11-07 05:54 | 65 | 11kV | 162451 | 2645 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S342 Paddington - 11kV Panel 26 L "McLachlan Boundary" tripped on: Relays Panel 26L: Alstom KCG - G140 Relay - FN, G1, B Star, C, N-Star-N Signals: 11kV trip Field EFIs: nil 11kV UG fault from S 342 Paddington Panel 26 to S8252 McLachlan Boundary Sw/A to S6899 Brougham Lane to S778 Glenmore Rd Sw/B. See 1885952, 1885954, 1885956, 1885327 (record withdrawn) | November | 2021 | 2022Q2 | 2022 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2021-11-07 | N | 61.4181 | N | 9 | N | N | 1.1101 | 39.4971 | 118714.3993
[7 empty] | 1283 | 15619 | 1885416 | 2021-11-07 17:19 | 2021-11-07 18:28 | 69 | 11kV | 125649 | 1821 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | ZN 12610 LONG JETTY PANEL 6 'RHODIN DRIVE' FEEDER TRIPPED ON: RELAYS: OC, IOC, EF, Rec, LO Field EFIs: nil Dop patrolled and inspected lightening strike location and no damage noticed. | November | 2021 | 2022Q2 | 2022 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2021-11-07 | N | 69 | N | 9 | N | N | 1.1101 | 39.4971 | 91820.5832
[7 empty] | 563 | 6964 | 1885423 | 2021-11-07 17:47 | 2021-11-07 19:15 | 88 | 11kV | 264 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | PT18621 The Ridgeway Awabakil 0.5 - HDO found blown No cause ascertained - customers restored via LV// | November | 2021 | 2022Q2 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-11-07 | N | 88 | N | 9 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 1001 | 12370 | 1885432 | 2021-11-07 18:13 | 2021-11-07 19:25 | 72 | 11kV | 648 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212079 B Phase DOLF : 16 Amp Excluded OMS 1885432 | November | 2021 | 2022Q2 | 2022 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2021-11-07 | N | 72 | N | 9 | N | N | 1.1101 | 39.4971 | 473.5393
[7 empty] | 918 | 11254 | 1885430 | 2021-11-07 18:06 | 2021-11-07 19:48 | 102 | 11kV | 92208 | 904 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212080 1 fault operation Sw 12213 no protection targets found SCADA indicated 1 trip without a reclose. All 3 line fault indicators flashing pole JU-54710. EF indicator at Sw 67639 did not operate, DOPs patrolled feeder & no fault found. Please check protection relays on Sw 12213 Excluded OMS 1885433 | November | 2021 | 2022Q2 | 2022 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Veg | 2021-11-07 | N | 102 | N | 9 | N | N | 1.1101 | 39.4971 | 67382.8867
[7 empty] | 809 | 10057 | 1885421 | 2021-11-07 17:42 | 2021-11-07 19:57 | 135 | 11kV | 340710 | 2912 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At ZN12620 Noraville, Panel 1'Hutton Rd' feeder, tripped on: Relays: 1R B & C phase PC, EFI and trip flag Signals: 11kv trip Fields EFIs: nil Dop patrolled - no cause ascertained Abnormal switching DMA- SW/B closed at S11215, SW/A closed at 18142. Section of feeder out defective SW/B 14875 to SW/A 14951 to S11902. See 1886231, 1886232, 1886233 | November | 2021 | 2022Q2 | 2022 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Veg | 2021-11-07 | N | 117.0021 | N | 9 | N | N | 1.1101 | 39.4971 | 248980.8188
[7 empty] | 640 | 8273 | 1885384 | 2021-11-07 15:25 | 2021-11-07 21:10 | 345 | 11kV | 198561 | 1807 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | ZN15002 Narrabeen Panel 6 Relays: C phase time OC, EF, lock and time delay FC and EFI. Signals: 11kV trip and zone earth Field EFIs: nil Storm related fault, 11kV mains struck by lightning in Arnott Cres. HV into LV and 11kV down. PT15955 was in LV// at the time of fault which back feed into feeder fault causing PT15399 11kV to come down. Abnormal switching: PT15955 (Mona Vale Panel 22) was being supplied from Narrabeen Panel 6,8 and Mona Vale 22 via LV//s. AB21756 to LB62890 tee PT15955 out for existing DMA. See 1886167, 1886168, 1886169, 1886170, 1886171, 1886172 | November | 2021 | 2022Q2 | 2022 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2021-11-07 | N | 109.8843 | N | 9 | N | N | 1.1101 | 39.4971 | 145102.5222
[7 empty] | 1279 | 15602 | 1885462 | 2021-11-07 21:11 | 2021-11-07 22:15 | 64 | 11kV | 1856 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | PT12464 Chamberlain Pangari - Foot path side 40A HDO found blown Customers restored for via LV//. No cause found. | November | 2021 | 2022Q2 | 2022 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Veg | 2021-11-07 | N | 64 | N | 9 | N | N | 1.1101 | 39.4971 | 1356.3101
[7 empty] | 1078 | 13822 | 1885431 | 2021-11-07 23:10 | 2021-11-08 00:18 | 68 | 11kV | 952 | 14 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 212082 No protection operation. Open 11kV bond pole AI-80155. repairs completed Excluded OMS 1885431 | November | 2021 | 2022Q2 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-11-07 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 695.6935
[7 empty] | 555 | 6790 | 1885489 | 2021-11-08 04:39 | 2021-11-08 05:54 | 75 | 11kV | 22050 | 294 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 212083 2 fault operations Overcurrent Removed tree branch from 11kV OHM pole KR-60222 | November | 2021 | 2022Q2 | 2022 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2021-11-08 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 16113.4896
[7 empty] | 560 | 6906 | 1885492 | 2021-11-08 05:15 | 2021-11-08 10:05 | 290 | 11kV | 870 | 3 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212084 Single phase DOLF : 10 Amp Possum on transformer Excluded OMS 1885492 | November | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-11-08 | N | 290 | N | 3 | N | N | 1.1101 | 39.4971 | 635.7703
[7 empty] | 1445 | 17801 | 1885610 | 2021-11-08 12:35 | 2021-11-08 14:35 | 120 | 11kV | 240 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | PT13283 Springs Greta 0.2 interrupted to remove tree from 11kV mains LB65879 to AB42005 tee PT 13283 Springs Greta 0.2. Tree on mains. customers restored via LV// | November | 2021 | 2022Q2 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-11-08 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 58 | 693 | 1885799 | 2021-11-09 11:30 | 2021-11-09 12:13 | 42.9 | 11kV | 58815.9 | 1371 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn4545 Epping - Pnl.52 tripped on A & B phase OC Tree trimmers on site unaware anything happened (ANA Arbor Tree Service) Feeder tried back and held | November | 2021 | 2022Q2 | 2022 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Veg | 2021-11-09 | N | 42.9 | N | 2 | N | N | 1.1101 | 39.4971 | 42980.9249
[7 empty] | 1344 | 16364 | 1885832 | 2021-11-09 13:05 | 2021-11-09 16:05 | 180 | 11kV | 900 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | LID 212091 A Phase DOLF : 10 Amp sub isolated for LA replacement Excluded oms 1885832 | November | 2021 | 2022Q2 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2021-11-09 | N | 180 | N | 2 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 1618 | 19666 | 1885948 | 2021-11-10 07:51 | 2021-11-10 11:20 | 209 | 11kV | 169941 | 2774 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn129 Hunters Hill - Pnl.52 tripped on: A & C phase OC & EF Field EFIs: S6209 S47499 (did not operate), S8287 S5268 S78102 (did not operate) 5 EFIs did not operate - SCADA defects raised Ug cable fault between S78102 Sw/B, S61562 Sw/A tee S4671. (Possibly outside 16 Linley Pl) During restoration - Pnl.57 tripped on B Phase O/C due to faulty EFIs See 1886507 1886509 1886510 1886513 1886514 1886515 1886517 | November | 2021 | 2022Q2 | 2022 | ZN129:PA52 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2021-11-10 | N | 61.2621 | N | 6 | N | N | 1.1101 | 39.4971 | 124187.8704
[7 empty] | 1002 | 12425 | 1886073 | 2021-11-10 17:15 | 2021-11-10 20:35 | 200 | 11kV | 2000 | 10 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | 11kV Feeder isolated between LB42549 to USL42139 tee PT11916 Basford Pacific Car hit pole - Stay wire broken | November | 2021 | 2022Q2 | 2022 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2021-11-10 | N | 200 | N | 6 | N | N | 1.1101 | 39.4971 | 1461.541
[7 empty] | 1524 | 18694 | 1886052 | 2021-11-10 17:00 | 2021-11-10 20:45 | 225 | 11kV | 1800 | 8 | HV | 3rd Party Vehicle | 3rd Party Impact | Stay Wire | Unplanned | Rain Heavy | N | PT13391 Pacific Basford - PT isolated for fallen distributor mains on Dist #2 Car hit stay wire causing it to snap and make contact with two LV distributor wires, bringing them to ground. Earthed and shorted hv/lv network, repaired stay and restrung LV mains. Damage form and before and after photos submitted | November | 2021 | 2022Q2 | 2022 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2021-11-10 | N | 225 | N | 6 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 702 | 9069 | 1886105 | 2021-11-10 19:49 | 2021-11-10 21:47 | 118 | 11kV | 354 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212108 C Phase DOLF : 10 Amp Excluded OMS 1886105 | November | 2021 | 2022Q2 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2021-11-10 | N | 118 | N | 6 | N | N | 1.1101 | 39.4971 | 258.6928
[7 empty] | 469 | 5757 | 1886112 | 2021-11-10 20:12 | 2021-11-10 22:02 | 110 | 11kV | 330 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212109 C Phase DOLF : 10 Amp Excluded OMS 1886112 | November | 2021 | 2022Q2 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2021-11-10 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 189 | 2452 | 1886127 | 2021-11-10 23:44 | 2021-11-11 07:20 | 456 | 11kV | 4104 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212111 DOLF : 10 Amp Excluded OMS 1886127 | November | 2021 | 2022Q2 | 2022 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2021-11-10 | N | 456 | N | 6 | N | N | 1.1101 | 39.4971 | 2999.0822
[7 empty] | 1553 | 19033 | 1886155 | 2021-11-11 07:14 | 2021-11-11 10:20 | 186 | 11kV | 186 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 212119 DOLF : 6 Amp blown arrester at sub 53575. Replaced 1 x Dolf Excluded oms 1886155. | November | 2021 | 2022Q2 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-11-11 | N | 186 | N | 5 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 19 | 238 | 1886195 | 2021-11-11 08:38 | 2021-11-11 11:10 | 152 | 11kV | 608 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212113 C Phase DOLF : 16 Amp Excluded OMS 1886195 | November | 2021 | 2022Q2 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2021-11-11 | N | 152 | N | 5 | N | N | 1.1101 | 39.4971 | 444.3085
[7 empty] | 491 | 5960 | 1886304 | 2021-11-11 13:59 | 2021-11-11 15:48 | 109 | 11kV | 55814 | 522 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.9 tripped on OC and EF Contractor drilled into cable adjacent to S7525 Brisbane Goulburn See 1886557 1886558 1886560 | November | 2021 | 2022Q2 | 2022 | ZN7900:PA9 | ZN7900:PA9 | ZN07900/000009 | SYDNEY | UG | Not Veg | 2021-11-11 | N | 106.9234 | N | 5 | N | N | 1.1101 | 39.4971 | 40787.225
[7 empty] | 356 | 4837 | 1886327 | 2021-11-11 15:44 | 2021-11-11 16:55 | 71 | 11kV | 27927 | 426 | HV | 3rd Party Vehicle | 3rd Party Impact | Insulator | Unplanned | Rain Light | N | LID 212117 MVA. 11kV mains of pin & LV service on road at pole DV21611 T/R on Lid 212114 at 1243hrs | November | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-11-11 | N | 65.5563 | N | 5 | N | N | 1.1101 | 39.4971 | 20408.2279
[7 empty] | 437 | 5429 | 1886412 | 2021-11-12 00:55 | 2021-11-12 02:30 | 95 | 11kV | 42590 | 542 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn36100 Rose Bay - Pnl.20 tripped on OC & EF Abnormal: 11kV DMA between S2716 and S1672 - S78659 Sw/B closed UG cable fault between S48350 and S2716. S2716 restored via LV // due to existing DMA See 1886549 1886550 1886551 | November | 2021 | 2022Q2 | 2022 | ZN36100:PA20 | ZN36100:PA20 | ZN36100/000020 | WAVERLEY | UG | Not Veg | 2021-11-12 | N | 78.5793 | N | 6 | N | N | 1.1101 | 39.4971 | 31123.5158
[7 empty] | 606 | 7707 | 1886425 | 2021-11-12 05:50 | 2021-11-12 06:20 | 30 | 11kV | 17610 | 587 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 212126 Merriwa River running very high. Caused willow tree to touch 11kV on spur to sub 71542 | November | 2021 | 2022Q2 | 2022 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2021-11-12 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 12868.8686
[7 empty] | 106 | 1363 | 1886375 | 2021-11-11 19:18 | 2021-11-12 09:38 | 860 | 11kV | 26330 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 212123 1 fault operation 3 phase Earth Fault | November | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-11-11 | N | 572.3913 | N | 5 | N | N | 1.1101 | 39.4971 | 19241.1874
[7 empty] | 734 | 9359 | 1886417 | 2021-11-12 03:24 | 2021-11-12 11:35 | 491.0833 | 11kV | 6384.0833 | 13 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 212127 1 fault operation Tree on mains between 3F50024 & 3F50133. Removed with insulated stick. 4 ops since 24/09/2019 | November | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2021-11-12 | N | 491.0833 | N | 6 | N | N | 1.1101 | 39.4971 | 4665.2998
[7 empty] | 711 | 9159 | 1886603 | 2021-11-12 14:27 | 2021-11-12 17:00 | 153 | 11kV | 41446 | 471 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 212128 BI-70072 pole down Excluded OMS 1886603 | November | 2021 | 2022Q2 | 2022 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2021-11-12 | N | 87.9958 | N | 6 | N | N | 1.1101 | 39.4971 | 30287.5143
[7 empty] | 176 | 2289 | 1886626 | 2021-11-12 15:52 | 2021-11-12 20:05 | 253 | 11kV | 9533 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Peats Ridge Zn Pnl.3 - REC45035 Mangrove Mountain tripped on Earth Fault OH mains down See 1887524 1887525 | November | 2021 | 2022Q2 | 2022 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2021-11-12 | N | 146.6615 | N | 6 | N | N | 1.1101 | 39.4971 | 6966.4352
[7 empty] | 236 | 2906 | 1886673 | 2021-11-12 20:36 | 2021-11-12 21:51 | 75 | 11kV | 3399 | 50 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 212132 2 fault operation Pole fire at pole 8M60032 Excluded OMS 1886673 | November | 2021 | 2022Q2 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2021-11-12 | N | 67.98 | N | 6 | N | N | 1.1101 | 39.4971 | 2483.8889
[7 empty] | 1361 | 16676 | 1886686 | 2021-11-13 01:14 | 2021-11-13 02:31 | 77 | 11kV | 24932 | 328 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn874 Concord - Pnl.25 tripped on: IOC UG cable fault between S7014 Sw/B, S8761 Sw/A & S4369 Sw/B See 1887522 1887523 | November | 2021 | 2022Q2 | 2022 | ZN874:PA25 | ZN874:PA25 | ZN00874/000025 | CANADA BAY | UG | Not Veg | 2021-11-13 | N | 76.0122 | N | 15 | N | N | 1.1101 | 39.4971 | 18219.5702
[7 empty] | 1288 | 15666 | 1886701 | 2021-11-13 07:46 | 2021-11-13 08:50 | 64 | 11kV | 128 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212134 A Phase DOLF : 10 Amp Excluded OMS 1886701 | November | 2021 | 2022Q2 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2021-11-13 | N | 64 | N | 15 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 1525 | 18701 | 1886760 | 2021-11-13 10:43 | 2021-11-13 11:51 | 68 | 11kV | 56304 | 828 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 212137 2 fault operations A & C Phase Overcurrent Branch on 11kV OHM adj ABS 40013 | November | 2021 | 2022Q2 | 2022 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2021-11-13 | N | 68 | N | 15 | N | N | 1.1101 | 39.4971 | 41145.3025
[7 empty] | 151 | 1818 | 1886778 | 2021-11-13 11:30 | 2021-11-13 13:19 | 109 | 11kV | 35561 | 737 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212138 2 fault operations 3 phase Tree on mains between poles HW-70717 & HW-71006. Removed by DOp Excluded OMS 1886778. | November | 2021 | 2022Q2 | 2022 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2021-11-13 | N | 48.251 | N | 15 | N | N | 1.1101 | 39.4971 | 25986.9299
[7 empty] | 5 | 95 | 1886762 | 2021-11-13 10:55 | 2021-11-13 13:31 | 156 | 11kV | 7420 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC41020 tripped, reclosed and tripped on OC Tree on mains adj PT12703 See 1887583 1887585 | November | 2021 | 2022Q2 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-11-13 | N | 65.6637 | N | 15 | N | N | 1.1101 | 39.4971 | 5422.3171
[7 empty] | 287 | 3650 | 1886728 | 2021-11-13 09:25 | 2021-11-13 14:05 | 280 | 11kV | 280 | 1 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 212139 Conductor off pin pole GP-43033 Excluded OMS 1886728 | November | 2021 | 2022Q2 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-11-13 | N | 280 | N | 15 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 977 | 11962 | 1886786 | 2021-11-13 11:45 | 2021-11-13 15:15 | 210 | 11kV | 210 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212144 Excluded OMS 1886786 | November | 2021 | 2022Q2 | 2022 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2021-11-13 | N | 210 | N | 15 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 1651 | 20076 | 1887580 | 2021-11-13 13:55 | 2021-11-13 15:25 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | REC45098 Kimkumber Tip tripped on OC Cause not ascertained | November | 2021 | 2022Q2 | 2022 |  |  |  | CENTRAL COAST | OH | Veg | 2021-11-13 | N | 90 | N | 15 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 1619 | 19670 | 1886829 | 2021-11-13 13:10 | 2021-11-13 15:57 | 167 | 11kV | 10688 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 212141 2 fault operations B & C Phase Overcurrent | November | 2021 | 2022Q2 | 2022 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Veg | 2021-11-13 | N | 167 | N | 15 | N | N | 1.1101 | 39.4971 | 7810.4752
[7 empty] | 1025 | 12978 | 1886794 | 2021-11-13 12:01 | 2021-11-13 17:40 | 339 | 11kV | 57020 | 489 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 212143 2 fault operation 3 phase Overcurrent Tree on mains IU-70225 Excluded OMS 1886794. | November | 2021 | 2022Q2 | 2022 | 224:80329 | 224:80329 | ZN00224/080329 | LAKE MACQUARIE | OH | Veg | 2021-11-13 | N | 116.6053 | N | 15 | N | N | 1.1101 | 39.4971 | 41668.5342
[7 empty] | 506 | 6029 | 1886892 | 2021-11-13 16:35 | 2021-11-13 18:06 | 91 | 11kV | 273 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212146 HV lead broken on TX 51983. repaired by john Butelr Excluded OMS 1886892 | November | 2021 | 2022Q2 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-11-13 | N | 91 | N | 15 | N | N | 1.1101 | 39.4971 | 199.5003
[7 empty] | 1569 | 19195 | 1886814 | 2021-11-13 12:45 | 2021-11-13 19:15 | 390.2833 | 11kV | 32783.8 | 84 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 212153 LLC had become detached Excluded OMS 1886914 | November | 2021 | 2022Q2 | 2022 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2021-11-13 | N | 390.2833 | N | 15 | N | N | 1.1101 | 39.4971 | 23957.4341
[7 empty] | 1065 | 13664 | 1886899 | 2021-11-13 16:57 | 2021-11-13 21:35 | 278 | 11kV | 9826 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC44853 Ourimbah Bumble - tripped on OC and EF Tree brought down HV and LV mains from USL42816 to LB44051 See 1887704 1887705 | November | 2021 | 2022Q2 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2021-11-13 | N | 228.5116 | N | 15 | N | N | 1.1101 | 39.4971 | 7180.551
[7 empty] | 45 | 600 | 1886940 | 2021-11-13 22:00 | 2021-11-13 23:10 | 70 | 11kV | 1606 | 433 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | REC40178 Elizabeth Bay Anthony - tripped & reclosed on OC & IOC @ PT12987 Elizabeth Greenacre - Middle phase HDO found blown Cause not ascertained See 1887708 188709 | November | 2021 | 2022Q2 | 2022 | ZN13000:PA10 | ZN13000:PA10 | ZN13000/000010 | CENTRAL COAST | OH | Veg | 2021-11-13 | N | 3.709 | N | 15 | N | N | 1.1101 | 39.4971 | 1173.6174
[7 empty] | 202 | 2582 | 1886922 | 2021-11-13 18:45 | 2021-11-14 05:15 | 630 | 11kV | 161384 | 1074 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 212152 Bph 11kV UGOH pole JU-30315 PG clamp burnt up. Excluded OMS 1886922 | November | 2021 | 2022Q2 | 2022 | 204:82689 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Not Veg | 2021-11-13 | N | 150.2644 | N | 15 | N | N | 1.1101 | 39.4971 | 117934.6672
[7 empty] | 1134 | 14324 | 1886992 | 2021-11-14 13:35 | 2021-11-14 17:10 | 215 | 11kV | 1075 | 5 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 212157 A Phase Broken LLC Excluded OMS 1886992 | November | 2021 | 2022Q2 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-11-14 | N | 215 | N | 9 | N | N | 1.1101 | 39.4971 | 785.5783
[7 empty] | 1119 | 14092 | 1887030 | 2021-11-14 17:34 | 2021-11-14 19:38 | 124 | 11kV | 34720 | 280 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212158 1 fault operation Overcurrent Tree on ohm's at sub 16789. 50A trip O/C. Excluded OMS 1887060 | November | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-11-14 | N | 124 | N | 9 | N | N | 1.1101 | 39.4971 | 25372.3519
[7 empty] | 281 | 3614 | 1887061 | 2021-11-14 18:45 | 2021-11-14 20:13 | 88 | 11kV | 10472 | 119 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge Pnl.1 - REC61097 Wise Ferry Lavender 10.2 tripped on OC Tree on OH mains at 5902 Wisemans Ferry Rd (adj Pole BF13) | November | 2021 | 2022Q2 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-11-14 | N | 88 | N | 9 | N | N | 1.1101 | 39.4971 | 7652.6287
[7 empty] | 90 | 1175 | 1887065 | 2021-11-14 19:06 | 2021-11-14 21:30 | 144 | 11kV | 720 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 212160 B & C Phase DOLF : 20 Amp | November | 2021 | 2022Q2 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2021-11-14 | N | 144 | N | 9 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 1465 | 18096 | 1887074 | 2021-11-14 19:44 | 2021-11-14 23:17 | 213 | 11kV | 639 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212163 DOLF : 10 Amp Excluded OMS 1887074 | November | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-11-14 | N | 213 | N | 9 | N | N | 1.1101 | 39.4971 | 466.9624
[7 empty] | 1266 | 15476 | 1887081 | 2021-11-14 21:58 | 2021-11-14 23:20 | 81.6333 | 11kV | 3265.3333 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 212162 A & B Phase DOLF : 20 Amp Excluded OMS 1887082 | November | 2021 | 2022Q2 | 2022 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2021-11-14 | N | 81.6333 | N | 9 | N | N | 1.1101 | 39.4971 | 2386.2093
[7 empty] | 1363 | 16688 | 1887045 | 2021-11-14 22:37 | 2021-11-14 23:45 | 68 | 11kV | 4352 | 64 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212159 REmove tree from 11kV OHM between poles GW-501117 & GW-50122. excluded OMS 1887069 | November | 2021 | 2022Q2 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2021-11-14 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 3180.3132
[7 empty] | 59 | 697 | 1887095 | 2021-11-15 01:44 | 2021-11-15 03:33 | 109 | 11kV | 107933 | 1017 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Previous Storm | N | Zn10994 Mortdale - Pnl.19L tripped on ABC phase OC Tree branch on 11kV UGOH adj S10731 Frenway Valentia See 1887717 1887718 | November | 2021 | 2022Q2 | 2022 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2021-11-15 | N | 106.1288 | N | 9 | N | N | 1.1101 | 39.4971 | 78874.2529
[7 empty] | 1422 | 17498 | 1887099 | 2021-11-15 06:00 | 2021-11-15 07:45 | 105 | 11kV | 10080 | 96 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | S10994 Mortdale Ex Panel 19L Roberts Fairway No.1 11kV burnt off bond on tee off to PT64515 Linden Valentia Suspect bond burnt off during previous fault (panel 19 trip see 1887095). | November | 2021 | 2022Q2 | 2022 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2021-11-15 | N | 105 | N | 9 | N | N | 1.1101 | 39.4971 | 7366.1667
[7 empty] | 1412 | 17400 | 1887138 | 2021-11-15 09:00 | 2021-11-15 09:20 | 20 | 11kV | 720 | 36 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S4940 GOLF LINKS FIDDENS - TX AND LV DE-ENERGISED TO MAKE REPAIRS Fallen streetlight mains. | November | 2021 | 2022Q2 | 2022 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2021-11-15 | N | 20 | N | 9 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 1093 | 13954 | 1886993 | 2021-11-14 13:43 | 2021-11-15 12:00 | 1337 | 11kV | 5348 | 4 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind Strong | N | LID 212161 Tree broke pole DV-61752. Sub isolated to fix pole Technician had to do safety check before connecting some services last person reported on at 1200 hours 15 Nov 2021. | November | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-11-14 | N | 1337 | N | 9 | N | N | 1.1101 | 39.4971 | 3908.1607
[7 empty] | 969 | 11799 | 1887028 | 2021-11-14 17:24 | 2021-11-15 13:00 | 1176 | 11kV | 10886 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN2400 BEROWRA EX PANEL 18 - RECLOSER 3281 BAY COOPER TRIPPED ON: Relays: OC trip, lockout Tree branch on mains beyond LLC (supplies PT2132) on pole AR22252 on cnr of Chilcott and McCallums Rd, conductors off pin. See 1887577, 1887578, 1887579 | November | 2021 | 2022Q2 | 2022 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2021-11-14 | N | 194.3929 | N | 9 | N | N | 1.1101 | 39.4971 | 7955.1677
[7 empty] | 997 | 12247 | 1887194 | 2021-11-15 11:39 | 2021-11-15 14:50 | 191 | 11kV | 33882 | 1103 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Wind Strong | N | ZN 2635 EPPING - PANEL 46 'VIMERA RD' TRIPPED ON: Relays: Basler BE1 Relay (OC & EF Relay) - 150TN (no.2 definite timed OC and EF) - 51N (EF & OC) REC Lockout, EFI Signals: 11kV trip Field EFIs: 65866, 78267 Crane has come into contact with 11kV OH. Section of 11kV feeder from SW/B S78267 to SW/B S80033 tee PT2208 Reeves Crandon. NOTE: UNKNOWN LV// IN AT THE TIME OF FAULT. see 1887564, 1887566, 1887568, 1887569, 1887570 | November | 2021 | 2022Q2 | 2022 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | PARRAMATTA | OH | Not Veg | 2021-11-15 | N | 30.718 | N | 9 | N | N | 1.1101 | 39.4971 | 24759.9663
[7 empty] | 160 | 1967 | 1887184 | 2021-11-15 10:43 | 2021-11-15 15:30 | 287 | 11kV | 574 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212164 Burnt off LL lead Excluded OMS 1887184 | November | 2021 | 2022Q2 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2021-11-15 | N | 287 | N | 9 | N | N | 1.1101 | 39.4971 | 419.4623
[7 empty] | 146 | 1756 | 1887267 | 2021-11-15 13:24 | 2021-11-15 17:50 | 266 | 11kV | 266 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212165 Single phase Live Line Lead broken Excluded OMS 1887267 | November | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-11-15 | N | 266 | N | 9 | N | N | 1.1101 | 39.4971 | 194.385
[7 empty] | 517 | 6166 | 1887297 | 2021-11-15 18:25 | 2021-11-15 19:34 | 69 | 11kV | 5865 | 85 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind Strong | N | LID 212166 Replace broken 33kV crossarm brace at pole IV-11990. 11kV Fdr isolated for clearance. Excluded OMS 1887297 | November | 2021 | 2022Q2 | 2022 | 270:83584 | 270:83584 | ZN00270/083584 | LAKE MACQUARIE | OH | Not Veg | 2021-11-15 | N | 69 | N | 9 | N | N | 1.1101 | 39.4971 | 4285.969
[7 empty] | 1637 | 19808 | 1887365 | 2021-11-15 17:50 | 2021-11-15 21:10 | 200 | 11kV | 2600 | 13 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212167 Treeon side of dam fell into tree ar pole IQ10021 Excluded OMS 1887365 | November | 2021 | 2022Q2 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2021-11-15 | N | 200 | N | 9 | N | N | 1.1101 | 39.4971 | 1900.0033
[7 empty] | 525 | 6208 | 1887402 | 2021-11-15 22:36 | 2021-11-16 08:24 | 588 | 11kV | 232412 | 946 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212168 2 fault operations Overcurrent; Earth Fault 11kV OHM down from ABS 19329 towards pole JU-20949. Excluded OMS No. 1887402, 1887403 | November | 2021 | 2022Q2 | 2022 | 257:81999 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2021-11-15 | N | 245.6786 | N | 9 | N | N | 1.1101 | 39.4971 | 169839.8346
[7 empty] | 976 | 11936 | 1887406 | 2021-11-16 01:44 | 2021-11-16 12:20 | 636 | 11kV | 159527 | 1043 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212169 1 fault operation Sensitive Earth Fault cable stolen at pole MG-60264/MG-60439 Excluded OMS No. 1887406 | November | 2021 | 2022Q2 | 2022 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2021-11-16 | N | 152.9501 | N | 3 | N | N | 1.1101 | 39.4971 | 116577.6264
[7 empty] | 669 | 8616 | 1887560 | 2021-11-16 13:49 | 2021-11-16 15:02 | 73 | 11kV | 18980 | 260 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212172 11kV off insulator at pole IS31961 Excluded OMS 1887552 | November | 2021 | 2022Q2 | 2022 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2021-11-16 | N | 73 | N | 3 | N | N | 1.1101 | 39.4971 | 13870.0242
[7 empty] | 315 | 4189 | 1887667 | 2021-11-16 23:35 | 2021-11-17 02:05 | 150 | 11kV | 109432 | 735 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn35370 Galston - Pnl.8 tripped on: B & C phase OC Possum on top of REC427 See 1887725 1887726 1887727 | November | 2021 | 2022Q2 | 2022 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2021-11-16 | N | 148.8871 | N | 3 | N | N | 1.1101 | 39.4971 | 79969.6779
[7 empty] | 232 | 2808 | 1887797 | 2021-11-17 14:00 | 2021-11-17 14:32 | 32 | 11kV | 30848 | 964 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC1437 Shaftsbury Morven - tripped, reclosed & locked out on OC Tree branch on 11kV OH mains outside 12 Sidel St West Ryde | November | 2021 | 2022Q2 | 2022 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Veg | 2021-11-17 | N | 32 | N | 3 | N | N | 1.1101 | 39.4971 | 22542.8085
[7 empty] | 1438 | 17716 | 1887699 | 2021-11-17 11:55 | 2021-11-17 14:40 | 165 | 11kV | 1815 | 11 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Section of 11kV feeder Ex Peats Ridge Pnl.3 between LB46215 to USL42797 tee PT13151 Miclins Wise Feery 1.4 interrupted for safety Tree about to fall on 11kV OH outside 150 Niclins Rd | November | 2021 | 2022Q2 | 2022 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2021-11-17 | N | 165 | N | 3 | N | N | 1.1101 | 39.4971 | 1326.3485
[7 empty] | 547 | 6697 | 1887848 | 2021-11-17 20:53 | 2021-11-18 00:20 | 207 | 11kV | 12817.7333 | 62 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212181 Phase B HV lead burnt off Bph Tx bushing." Refer to OMS No. 1887848, 1887850, 1887856 SOP WILKINSON T DOP POPLE A CC1: 22-"Refer to SOp" | November | 2021 | 2022Q2 | 2022 | 523:33503 | 523:33503 | ZN00523/033503 | SINGLETON | OH | Not Veg | 2021-11-17 | N | 206.7376 | N | 3 | N | N | 1.1101 | 39.4971 | 9366.8215
[7 empty] | 931 | 11309 | 1887945 | 2021-11-18 11:19 | 2021-11-18 12:29 | 70 | 11kV | 7808 | 112 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212183 Bph Links 40504 Insulator failure. Aph Insulator cracked also. All 3 Phases Replaced. Excluded OMS 1887945 | November | 2021 | 2022Q2 | 2022 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2021-11-18 | N | 69.7143 | N | 2 | N | N | 1.1101 | 39.4971 | 5705.8561
[7 empty] | 760 | 9524 | 1888025 | 2021-11-18 16:21 | 2021-11-18 18:50 | 149.0833 | 11kV | 2385.3333 | 16 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212184 A Car hit sub 27982 11kV mains at pole GQ71118 disconnected. Sub 27982, pole GQ72633 and all associated HV and LV mains removed. B fault detector on CB 83733 also operated Excluded oms 1888027, 1888032 | November | 2021 | 2022Q2 | 2022 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2021-11-18 | N | 149.0833 | N | 2 | N | N | 1.1101 | 39.4971 | 1743.1312
[7 empty] | 1223 | 15040 | 1888092 | 2021-11-19 08:49 | 2021-11-19 09:42 | 53 | 11kV | 8215 | 155 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12650 West Gosford - Pnl.16 tripped on: Earth Fault UG cable fault in frontline section of feeder between Pnl.16 to S50231 tee S18232 West Gosford Aux No.2 | November | 2021 | 2022Q2 | 2022 | ZN12650:PA16 | ZN12650:PA16 | ZN12650/000016 | CENTRAL COAST | UG | Not Veg | 2021-11-19 | N | 53 | N | 3 | N | N | 1.1101 | 39.4971 | 6003.2797
[7 empty] | 857 | 10622 | 1888124 | 2021-11-19 10:51 | 2021-11-19 14:55 | 244 | 11kV | 3904 | 16 | HV | 3rd Party Vehicle | 3rd Party Impact | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 212188 No protection operation today, isolated for safety to allow repairs. Had to re build sub 27982 knocked down by truck LID 212184. PD | November | 2021 | 2022Q2 | 2022 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2021-11-19 | N | 244 | N | 3 | N | N | 1.1101 | 39.4971 | 2852.9281
[7 empty] | 459 | 5666 | 1888202 | 2021-11-19 21:23 | 2021-11-19 22:16 | 52.75 | 11kV | 1318.75 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212191 A & C Phase DOLF : 10 Amp A & C ph LF 74742 & B ph DOLF 78284 replaced | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-11-19 | N | 52.75 | N | 3 | N | N | 1.1101 | 39.4971 | 963.7036
[7 empty] | 587 | 7414 | 1888226 | 2021-11-20 07:20 | 2021-11-20 08:00 | 40 | 11kV | 40 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212192 A Phase DOLF : 10 Amp Excluded OMS 1888226 | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-11-20 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 29.2308
[7 empty] | 213 | 2622 | 1888214 | 2021-11-20 00:25 | 2021-11-20 13:00 | 755 | 11kV | 92955 | 1475 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn10998 Rockdale - Pnl.32 - Opened by AOP for safety after vehicle hit pole KO-18458 S10612 Dist #3 - Also interrupted on the same pole See 1889177 1889178 | November | 2021 | 2022Q2 | 2022 | ZN10998:PA32 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Not Veg | 2021-11-20 | N | 63.0203 | N | 4 | N | N | 1.1101 | 39.4971 | 67928.7723
[7 empty] | 777 | 9787 | 1888231 | 2021-11-20 08:25 | 2021-11-20 15:15 | 410 | 11kV | 410 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212199 Single phase DOLF : 10 Amp Excluded OMS 1888247 | November | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-11-20 | N | 410 | N | 4 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 531 | 6329 | 1888240 | 2021-11-20 12:50 | 2021-11-20 15:50 | 180 | 11kV | 12960 | 72 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT.12114 Ocean View Clairvoux - Interrupted for safety due to OH mains down | November | 2021 | 2022Q2 | 2022 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Not Veg | 2021-11-20 | N | 180 | N | 4 | N | N | 1.1101 | 39.4971 | 9470.7857
[7 empty] | 875 | 10828 | 1888302 | 2021-11-21 03:08 | 2021-11-21 04:13 | 64.85 | 11kV | 52398.8 | 808 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | ZN1673 Turramurra 11kV Panel 2 "Forbes Higgs", tripped on: Relays: B and C phase OC Field EFIs: Nil Feeder patrolled clear and supply restored - cause not ascertained | November | 2021 | 2022Q2 | 2022 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2021-11-21 | N | 64.85 | N | 4 | N | N | 1.1101 | 39.4971 | 38291.4975
[7 empty] | 279 | 3588 | 1888367 | 2021-11-21 15:19 | 2021-11-21 17:13 | 114 | 11kV | 36480 | 320 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn12630 Peats Ridge - Pnl.10 tripped on B & C phase OC Burnt stick on HV near USL44814 | November | 2021 | 2022Q2 | 2022 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2021-11-21 | N | 114 | N | 4 | N | N | 1.1101 | 39.4971 | 26658.508
[7 empty] | 561 | 6936 | 1888393 | 2021-11-21 18:23 | 2021-11-21 19:15 | 52 | 11kV | 2340 | 45 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 212209 A Phase DOLF : 40 Amp Magpie | November | 2021 | 2022Q2 | 2022 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2021-11-21 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 1710.003
[7 empty] | 209 | 2609 | 1888410 | 2021-11-21 23:06 | 2021-11-22 00:45 | 99 | 11kV | 9306 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 212211 2 fault operations 3 phase No cause found | November | 2021 | 2022Q2 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2021-11-21 | N | 99 | N | 4 | N | N | 1.1101 | 39.4971 | 6800.5503
[7 empty] | 788 | 9885 | 1888516 | 2021-11-22 12:13 | 2021-11-22 15:14 | 181 | 11kV | 8977 | 117 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212213 Tree fell onto mains at P. GV-90331 Excluded OMS 1888516 | November | 2021 | 2022Q2 | 2022 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2021-11-22 | N | 76.7265 | N | 2 | N | N | 1.1101 | 39.4971 | 6560.1268
[7 empty] | 9 | 134 | 1888557 | 2021-11-22 16:05 | 2021-11-22 18:57 | 172 | 11kV | 15308 | 89 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | PT916 Raleigh Rd - Interrupted due to cat 1 emergency cross arm replacement | November | 2021 | 2022Q2 | 2022 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-11-22 | N | 172 | N | 2 | N | N | 1.1101 | 39.4971 | 11186.6349
[7 empty] | 708 | 9133 | 1888642 | 2021-11-23 03:59 | 2021-11-23 11:00 | 421 | 11kV | 195872 | 1685 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 212219 2 fault operations 3 phase Earth Fault A ph HV main down between CH-20109 & CH-20017 Excluded OMS 1888642 | November | 2021 | 2022Q2 | 2022 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2021-11-23 | N | 116.2445 | N | 1 | N | N | 1.1101 | 39.4971 | 143137.4804
[7 empty] | 216 | 2678 | 1888837 | 2021-11-24 02:12 | 2021-11-24 04:30 | 138 | 11kV | 8694 | 63 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT11144 Donnison Hely - Footpath phase HDO blown Possum found at base of PT | November | 2021 | 2022Q2 | 2022 | ZN12650:PA10 | ZN12650:PA10 | ZN12650/000010 | CENTRAL COAST | OH | Not Veg | 2021-11-24 | N | 138 | N | 3 | N | N | 1.1101 | 39.4971 | 6353.3188
[7 empty] | 225 | 2747 | 1888840 | 2021-11-24 05:33 | 2021-11-24 19:50 | 857 | 11kV | 87299 | 538 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.45 tripped on IOC & EF Abnormal: LB62109 closed with LB2920 open + LB745 Closed with AB2438 Open UG cable fault in frontline section of feeder | November | 2021 | 2022Q2 | 2022 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | UG | Not Veg | 2021-11-24 | N | 162.2658 | N | 3 | N | N | 1.1101 | 39.4971 | 63795.5343
[7 empty] | 1226 | 15049 | 1889021 | 2021-11-24 22:44 | 2021-11-25 00:26 | 102 | 11kV | 67476 | 668 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn384 Camperdown - Pnl.81 tripped UG cable fault between S8970 Sw/D and S2389 Sw/A See 1889126 | November | 2021 | 2022Q2 | 2022 | ZN384:PA81 | ZN384:PA81 | ZN00384/000081 | SYDNEY | UG | Not Veg | 2021-11-24 | N | 101.012 | N | 3 | N | N | 1.1101 | 39.4971 | 49309.4706
[7 empty] | 1386 | 17007 | 1889030 | 2021-11-25 02:05 | 2021-11-25 06:12 | 247 | 11kV | 24521 | 195 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2606 ex Panel 10 Galston Recloser CP50015 Quarry Old Norther has tripped RelaysL OC trip and Lockout Cause: Tree branch on OH mains in vicinity of 97 Quarry Rd See OMS 1890365 1890366 1890367 1890369 1889036 188903218 | November | 2021 | 2022Q2 | 2022 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2021-11-25 | N | 125.7487 | N | 10 | N | N | 1.1101 | 39.4971 | 17919.2236
[7 empty] | 68 | 837 | 1889395 | 2021-11-25 14:05 | 2021-11-25 14:40 | 35 | 11kV | 350 | 10 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Rain Light | N | LID 212228 stay wire retensioned pole 8L-70119 | November | 2021 | 2022Q2 | 2022 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2021-11-25 | N | 35 | N | 10 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 1488 | 18368 | 1889168 | 2021-11-25 13:25 | 2021-11-25 15:10 | 105 | 11kV | 1890 | 18 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 212229 Failed 11kV x-arm at sub 51734 Excluded oms 1889168 | November | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-11-25 | N | 105 | N | 10 | N | N | 1.1101 | 39.4971 | 1381.1563
[7 empty] | 816 | 10113 | 1889234 | 2021-11-25 17:53 | 2021-11-25 17:58 | 5 | 11kV | 1175 | 235 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn3425 Castle Cove Existing Panel 33 CP64824 Deepwater Holly Tripped and reclosed @ 1753 @1756 and @1758 Relays: OC Trip Cause: Burnt Metallic Balloon found at the base of IR64824 Deep Water Holly | November | 2021 | 2022Q2 | 2022 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Veg | 2021-11-25 | N | 5 | N | 10 | N | N | 1.1101 | 39.4971 | 858.6553
[7 empty] | 986 | 12064 | 1889239 | 2021-11-25 18:13 | 2021-11-25 19:14 | 61 | 11kV | 124989 | 2049 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 212234 HV tapping blown at pole JU-70043 & broken insulator at pole JU-70091. Excluded OMS No. 1889239, 1889259 | November | 2021 | 2022Q2 | 2022 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2021-11-25 | N | 61 | N | 10 | N | N | 1.1101 | 39.4971 | 91338.2746
[7 empty] | 1547 | 18938 | 1889271 | 2021-11-25 19:40 | 2021-11-26 | 260 | 11kV | 1300 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 212237 C Phase DOLF : 10 Amp Blown surge arrestor Excluded OMS 1889271 | November | 2021 | 2022Q2 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2021-11-25 | N | 260 | N | 10 | N | N | 1.1101 | 39.4971 | 950.0017
[7 empty] | 649 | 8414 | 1889278 | 2021-11-25 20:07 | 2021-11-26 00:40 | 273 | 11kV | 273 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212238 C Phase DOLF : 10 Amp Excluded OMS 1889278 | November | 2021 | 2022Q2 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2021-11-25 | N | 273 | N | 10 | N | N | 1.1101 | 39.4971 | 199.5003
[7 empty] | 1379 | 16909 | 1889236 | 2021-11-25 18:05 | 2021-11-26 04:20 | 615 | 11kV | 178301 | 1783 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Electrical Storm | N | LID 212232 3 fault operations Earth Fault HV endbox flashover at Binet Close sub 35618. Excluded OMS No. 1889236, 1889237, 1889287. | November | 2021 | 2022Q2 | 2022 | 238:34136 | 238:34136 | ZN00238/034136 | MAITLAND | UG | Not Veg | 2021-11-25 | N | 100.0006 | N | 10 | N | N | 1.1101 | 39.4971 | 130297.1118
[7 empty] | 1274 | 15543 | 1889324 | 2021-11-26 05:23 | 2021-11-26 06:24 | 61 | 11kV | 427 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212245 A & B phase DOLF : 20 Amp No cause found | November | 2021 | 2022Q2 | 2022 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2021-11-26 | N | 61 | N | 17 | N | N | 1.1101 | 39.4971 | 312.039
[7 empty] | 1043 | 13346 | 1889342 | 2021-11-26 06:45 | 2021-11-26 08:54 | 129 | 11kV | 48588 | 587 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212246 Tree on mains between LLC at pole 5I-40095 and sub 71461. Excluded OMS 1889342 | November | 2021 | 2022Q2 | 2022 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2021-11-26 | N | 82.7734 | N | 17 | N | N | 1.1101 | 39.4971 | 35506.6773
[7 empty] | 646 | 8396 | 1889363 | 2021-11-26 07:39 | 2021-11-26 09:38 | 118.9667 | 11kV | 2855.2 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212248 & 212249 Line DOLF : 20 Amp Fault was at line fuse 74395 not sub 72295. Excluded OMS 1889363 | November | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-11-26 | N | 118.9667 | N | 17 | N | N | 1.1101 | 39.4971 | 2086.4959
[7 empty] | 933 | 11317 | 1889341 | 2021-11-26 06:42 | 2021-11-26 09:44 | 182 | 11kV | 15288 | 84 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | 11kV surge arrestor cut away A phase 40A A phase dolf blown No LID No Switching DQ | November | 2021 | 2022Q2 | 2022 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Not Veg | 2021-11-26 | N | 182 | N | 17 | N | N | 1.1101 | 39.4971 | 11172.0195
[7 empty] | 1590 | 19407 | 1889356 | 2021-11-26 08:53 | 2021-11-26 10:50 | 117 | 11kV | 8042 | 389 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 212247 NO PROTECTION OPERATION 11KV mains down pole KS-93308, section isolated for repairs. Excluded OMS 1889394 | November | 2021 | 2022Q2 | 2022 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2021-11-26 | N | 20.6735 | N | 17 | N | N | 1.1101 | 39.4971 | 5876.8564
[7 empty] | 743 | 9393 | 1889434 | 2021-11-26 10:15 | 2021-11-26 12:01 | 106 | 11kV | 14098 | 133 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | ## 19360 trip and LO on OC branch removed from OHM adj Rocky Pnt Rd sub 21846 No LID DQ Note this OMS job is not related to OMS 1889479 | November | 2021 | 2022Q2 | 2022 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2021-11-26 | N | 106 | N | 17 | N | N | 1.1101 | 39.4971 | 10302.4026
[7 empty] | 707 | 9129 | 1889459 | 2021-11-26 11:29 | 2021-11-26 16:10 | 281 | 11kV | 281 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212252 DOLF : 10 Amp Excluded OMS 1889459 | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-11-26 | N | 281 | N | 17 | N | N | 1.1101 | 39.4971 | 205.3465
[7 empty] | 1653 | 20091 | 1889620 | 2021-11-26 17:32 | 2021-11-26 17:50 | 18 | 11kV | 774 | 43 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212253 SEE REPORT 212232 Section isolated for repair and removal of generator. | November | 2021 | 2022Q2 | 2022 | 238:34136 | 238:34136 | ZN00238/034136 | MAITLAND | OH | Not Veg | 2021-11-26 | N | 18 | N | 17 | N | N | 1.1101 | 39.4971 | 565.6164
[7 empty] | 147 | 1775 | 1889554 | 2021-11-26 15:50 | 2021-11-26 18:06 | 136 | 11kV | 10608 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC45117 Glenning Valley tripped on: Earth Fault Abnormal: REC in scan fail Tree on OH mains adj pole BV3192 | November | 2021 | 2022Q2 | 2022 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2021-11-26 | N | 136 | N | 17 | N | N | 1.1101 | 39.4971 | 7752.0135
[7 empty] | 379 | 5032 | 1889580 | 2021-11-26 16:46 | 2021-11-26 18:54 | 128 | 11kV | 369781 | 3440 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn12570 Avoca - Pnl.33 tripped, reclosed & tripped o: Earth Fault OH mains down near 190 Cullens Rd near Melville St Kincumber See 1890471 1890474 1890475 | November | 2021 | 2022Q2 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2021-11-26 | N | 107.4945 | N | 17 | N | N | 1.1101 | 39.4971 | 270225.0481
[7 empty] | 221 | 2722 | 1889613 | 2021-11-26 17:08 | 2021-11-26 19:07 | 119 | 11kV | 9520 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | REC3280 Hunt Ave tripped on OC Tree on OH mains near LB1548 | November | 2021 | 2022Q2 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2021-11-26 | N | 119 | N | 17 | N | N | 1.1101 | 39.4971 | 6956.9352
[7 empty] | 320 | 4274 | 1889442 | 2021-11-26 10:29 | 2021-11-26 22:10 | 701 | 11kV | 73798 | 238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC527 Catherine Paul tripped on OC and IOC Tree brought down OH adj Pole PY37005 See 1890416 1890417 1890418 | November | 2021 | 2022Q2 | 2022 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2021-11-26 | N | 310.0756 | N | 17 | N | N | 1.1101 | 39.4971 | 53929.4017
[7 empty] | 144 | 1725 | 1889683 | 2021-11-26 21:01 | 2021-11-26 22:55 | 114 | 11kV | 73530 | 645 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | REC46673 Terrigal Penrose tripped & locked out on OC Tree on OH mains adj LB45076 | November | 2021 | 2022Q2 | 2022 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2021-11-26 | N | 114 | N | 17 | N | N | 1.1101 | 39.4971 | 53733.5552
[7 empty] | 532 | 6362 | 1889654 | 2021-11-26 19:38 | 2021-11-27 00:11 | 273 | 11kV | 23478 | 86 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex Long Jetty Pnl.18 - HV bond burnt off adj PT12881 North Scenic Forresters | November | 2021 | 2022Q2 | 2022 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2021-11-26 | N | 273 | N | 17 | N | N | 1.1101 | 39.4971 | 17157.0299
[7 empty] | 1265 | 15474 | 1889698 | 2021-11-26 22:32 | 2021-11-27 04:00 | 328 | 11kV | 107734 | 748 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn35370 Glaston Pnl.8 tripped on Earth Fault & B Phase OC 11kV and 415V OH mains clashed together between USL2892 and PT2216 See 1890426 1890427 | November | 2021 | 2022Q2 | 2022 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2021-11-26 | N | 144.0294 | N | 17 | N | N | 1.1101 | 39.4971 | 78728.8296
[7 empty] | 573 | 7120 | 1889253 | 2021-11-25 18:29 | 2021-11-27 08:50 | 2301 | 11kV | 6903 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Flood | N | LID 212256 Single phase DOLF : 10 Amp Replaced blown lightning Arrestor and fuse Delay in restoration due to flood water Excluded OMS 1889253 | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2021-11-25 | N | 2301 | N | 10 | N | N | 1.1101 | 39.4971 | 5044.5088
[7 empty] | 1081 | 13860 | 1889724 | 2021-11-27 02:58 | 2021-11-27 08:50 | 352 | 11kV | 57966 | 494 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 212255 1 fault operation B & C Phase - Overcurrent Fault Current: Bph - 2563A, Cph - 2586A tree on OHM at pole IV-21846 HV into LV repairs complete all ok | November | 2021 | 2022Q2 | 2022 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2021-11-27 | N | 117.3401 | N | 3 | N | N | 1.1101 | 39.4971 | 42359.8431
[7 empty] | 1403 | 17173 | 1889679 | 2021-11-26 20:57 | 2021-11-27 09:25 | 748 | 11kV | 2244 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 212257 Single phase DOLF : 10 Amp | November | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-11-26 | N | 748 | N | 17 | N | N | 1.1101 | 39.4971 | 1639.849
[7 empty] | 962 | 11693 | 1889606 | 2021-11-26 16:53 | 2021-11-27 15:55 | 1382 | 11kV | 240477 | 1585 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn36200 Empire Bay - Pnl.11 tripped, relcosed and tripped on: Earth Fault Abnormal: S65112 Sw/A Open with LB62074 Closed 11kV OH down outside 68 Fishermans Pde, Daleys Point See 1890461 1890462 1890463 1890464 1890465 | November | 2021 | 2022Q2 | 2022 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Not Veg | 2021-11-26 | N | 151.7205 | N | 17 | N | N | 1.1101 | 39.4971 | 175733.4987
[7 empty] | 1071 | 13777 | 1889756 | 2021-11-27 12:05 | 2021-11-27 18:30 | 385 | 11kV | 4620 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | ex Zn12690 Berkeley Vale Panel 24R burns rd feeder, Section of 11kV feeder beyond 11kV link 43859 was isolated for safety Cause: Link 43859 was isolated for safety due to tree on mains See OMS 1889756 1889838 | November | 2021 | 2022Q2 | 2022 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2021-11-27 | N | 385 | N | 3 | N | N | 1.1101 | 39.4971 | 3376.1597
[7 empty] | 684 | 8707 | 1889883 | 2021-11-27 15:56 | 2021-11-27 20:35 | 279 | 11kV | 8370 | 30 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 212262 Conductor off pin FR-74805, broken x-arm FR-74789 Excluded OMS 1889883 | November | 2021 | 2022Q2 | 2022 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2021-11-27 | N | 279 | N | 3 | N | N | 1.1101 | 39.4971 | 6116.5491
[7 empty] | 1182 | 14748 | 1889949 | 2021-11-28 02:42 | 2021-11-28 06:55 | 253 | 11kV | 155874 | 2238 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn2835 Burwood - Pnl.10 tripped on: Earth Fault EFIs did not operate at: S3484, S46519 & S46978 During restoration switching @ 0448 - Pnl.31 tripped on:C phase IOC and OC @ 0546 - Pnl.10 tripped on 3 phase OC UG cable fault between S3484 Sw/B, S2398 Sw/A and 48553 Sw/A See 1890596 1890597 1890598 1890599 1890601 | November | 2021 | 2022Q2 | 2022 | ZN2835:PA10 | ZN2835:PA10 | ZN02835/000010 | STRATHFIELD | UG | Not Veg | 2021-11-28 | N | 69.6488 | N | 6 | N | N | 1.1101 | 39.4971 | 113908.1217
[7 empty] | 906 | 11143 | 1889222 | 2021-11-25 17:37 | 2021-11-28 12:25 | 4008 | 11kV | 115389 | 54 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Flood | N | LID 212236 3 fault operations Defective transformer at Sub 70298 - replaced 28th 12:25. Delay due to flooding, access was blocked until the 28th Nov Excluded OMS 1889222 | November | 2021 | 2022Q2 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2021-11-25 | N | 2136.8333 | N | 10 | N | N | 1.1101 | 39.4971 | 84322.8778
[7 empty] | 1552 | 19003 | 1890001 | 2021-11-28 12:00 | 2021-11-28 12:40 | 40 | 11kV | 3160 | 79 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | LID 212264 high volts on A phase 300V, sub isolated interconnected & replaced Excluded oms 1890001 1889972 1889999 | November | 2021 | 2022Q2 | 2022 | 257:82006 | 257:82006 | ZN00257/082006 | NEWCASTLE | OH | Not Veg | 2021-11-28 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 2309.2348
[7 empty] | 259 | 3326 | 1889964 | 2021-11-28 08:40 | 2021-11-28 13:50 | 310 | 11kV | 46500 | 150 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 212263 Faulty ABS 25587 & Faulty ABS 40044 repaired so network could be restored for NAR 76000 Excluded OMS 1889964 | November | 2021 | 2022Q2 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-11-28 | N | 310 | N | 6 | N | N | 1.1101 | 39.4971 | 33980.8285
[7 empty] | 1666 | 20275 | 1890025 | 2021-11-28 12:54 | 2021-11-28 17:27 | 272.6333 | 11kV | 161174.7333 | 1417 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Zn10991 Blakehurst - pnl.12 tripped on A phase IOC & OC HAZ RMI @ S10133 Mooney Terry has flashed over and damaged. Section of feeder isolated from AB1161 to S10795 Sw/A tee S10133 Mortdale Pnl.7 isolated between S10133 to AB30094 tee S10133 & S10802 See 1890441 1890442 1890045 1890031 | November | 2021 | 2022Q2 | 2022 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | OH | Not Veg | 2021-11-28 | N | 113.7436 | N | 6 | N | N | 1.1101 | 39.4971 | 117781.7413
[7 empty] | 727 | 9289 | 1890054 | 2021-11-28 15:00 | 2021-11-28 19:00 | 240 | 11kV | 18960 | 79 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | LID 212266 Initially customers restored via LV// isolated to change faulty trans Excluded oms 1890054 | November | 2021 | 2022Q2 | 2022 | 257:82006 | 257:82006 | ZN00257/082006 | NEWCASTLE | OH | Not Veg | 2021-11-28 | N | 240 | N | 6 | N | N | 1.1101 | 39.4971 | 13855.4088
[7 empty] | 111 | 1417 | 1890272 | 2021-11-29 15:02 | 2021-11-29 16:35 | 93 | 11kV | 279 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212274 B Phase DOLF : 10 Amp B ph Dolf carrier burnt up. JMH Excluded OMS 1890272 | November | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-11-29 | N | 93 | N | 2 | N | N | 1.1101 | 39.4971 | 203.885
[7 empty] | 901 | 11095 | 1890305 | 2021-11-29 18:13 | 2021-11-29 20:49 | 156 | 11kV | 3276 | 21 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Lake Munmorah pnl.5 - 11kV Feeder interrupted between IS.41987. LB40109 and AB40158 tee PT11811 & PT 14474 MVA into pole BU739. Insulator broken away from cross arm and 11kV OH 5 meters from the ground | November | 2021 | 2022Q2 | 2022 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2021-11-29 | N | 156 | N | 2 | N | N | 1.1101 | 39.4971 | 2394.0042
[7 empty] | 1358 | 16627 | 1890385 | 2021-11-30 09:51 | 2021-11-30 10:28 | 37 | 11kV | 481 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212278 replaced HV pin pole 9N20115. JMH | November | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2021-11-30 | N | 37 | N | 3 | N | N | 1.1101 | 39.4971 | 351.5006
[7 empty] | 1460 | 18015 | 1890481 | 2021-11-30 13:54 | 2021-11-30 14:45 | 51 | 11kV | 204 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212280 A & C Phase DOLF : 16 Amp Excluded OMS 1890481 | November | 2021 | 2022Q2 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-11-30 | N | 51 | N | 3 | N | N | 1.1101 | 39.4971 | 149.0772
[7 empty] | 1538 | 18868 | 1890511 | 2021-11-30 15:43 | 2021-11-30 16:57 | 74 | 11kV | 126730 | 2009 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.21 tripped, reclosed & tripped on: Earth Fault Abnormal: S65613 Sw/B Closed with S77361 Sw/A Open. LB321 Closed with AB694 Open (DMA) Crane hit section of OH mains between S79600, CP694 & S64281 See 1890604 1890605 | November | 2021 | 2022Q2 | 2022 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2021-11-30 | N | 63.0811 | N | 3 | N | N | 1.1101 | 39.4971 | 92610.5461
[7 empty] | 951 | 11521 | 1890582 | 2021-12-01 03:09 | 2021-12-01 05:00 | 111 | 11kV | 7738 | 1028 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.21 tripped & reclosed on: B Phase OC @ PT10513 Boronia Woodlands - Possum caused flashover resulting in open circuit dropper to PT. Restored via LV // See 1890588 1890607 | December | 2021 | 2022Q2 | 2022 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Not Veg | 2021-12-01 | N | 7.5272 | N | 4 | N | N | 1.1101 | 39.4971 | 5654.7022
[7 empty] | 526 | 6217 | 1890632 | 2021-12-01 08:55 | 2021-12-01 11:23 | 148 | 11kV | 332000 | 2360 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.16 tripped on: Earth Fault UG cable fault between S1900 Sw/b, S482 Sw/B and S77202 Sw/A See 1891158 1891159 | December | 2021 | 2022Q2 | 2022 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2021-12-01 | N | 140.678 | N | 4 | N | N | 1.1101 | 39.4971 | 242615.8077
[7 empty] | 336 | 4705 | 1890710 | 2021-12-01 12:13 | 2021-12-01 13:07 | 54 | 11kV | 4328 | 512 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn12620 Noraville - Pnl.2 tripped & reclosed on: OC @ PT11022 Boomerang Ourringo - Roadside and middle phase HDOs blown Bird on PT See 1891156 1891157 | December | 2021 | 2022Q2 | 2022 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2021-12-01 | N | 8.4531 | N | 4 | N | N | 1.1101 | 39.4971 | 3162.7747
[7 empty] | 1212 | 15016 | 1891000 | 2021-12-01 21:02 | 2021-12-01 22:15 | 73 | 11kV | 119364 | 1688 | HV | Animal Possum | Animal | Pole | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.14 tripped on: A & B phase IOC Abnormal: S8428 Sw/B closed with AB1593 Open (DMA) Possum found on corner pole between LB173 and LB685 See 1891153 1891154 | December | 2021 | 2022Q2 | 2022 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2021-12-01 | N | 70.7133 | N | 4 | N | N | 1.1101 | 39.4971 | 87227.6906
[7 empty] | 519 | 6175 | 1891100 | 2021-12-02 11:36 | 2021-12-02 13:05 | 89 | 11kV | 135174 | 1742 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.29 tripped on; Earth Fault UG cable fault in front line section of feeder | December | 2021 | 2022Q2 | 2022 | ZN3155:PA29 | ZN3155:PA29 | ZN03155/000029 | WOOLLAHRA | UG | Not Veg | 2021-12-02 | N | 77.597 | N | 2 | N | N | 1.1101 | 39.4971 | 98781.1722
[7 empty] | 713 | 9191 | 1891113 | 2021-12-02 12:24 | 2021-12-02 14:15 | 111 | 11kV | 111 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212288 DOLF : 10 Amp WAS NOT THE SUB REPORTED AS FAULTY IN oms Excluded OMS 1891113 | December | 2021 | 2022Q2 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2021-12-02 | N | 111 | N | 2 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 773 | 9688 | 1891330 | 2021-12-03 11:33 | 2021-12-03 12:39 | 66 | 11kV | 80784 | 1224 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn1290 Leightonfield - Pnl.2 tripped on B & C phase IOC Balloon found across phases. CB would then not electrically spring charge | December | 2021 | 2022Q2 | 2022 | ZN1290:PA2 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-12-03 | N | 66 | N | 9 | N | N | 1.1101 | 39.4971 | 59034.5645
[7 empty] | 150 | 1800 | 1891329 | 2021-12-03 11:22 | 2021-12-03 12:43 | 81 | 11kV | 73467 | 907 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Berkeley Vale Pnl.6 - B phase bond burnt off USL43325 (Line side) | December | 2021 | 2022Q2 | 2022 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2021-12-03 | N | 81 | N | 9 | N | N | 1.1101 | 39.4971 | 53687.5167
[7 empty] | 1296 | 15772 | 1890080 | 2021-11-28 18:27 | 2021-12-03 13:20 | 6893 | 11kV | 62279 | 13 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 212267 3 fault operations 11kV UGOH failed at pole 4M-80046. Note: Unable to access UGOH as it is on the railway coridor and rail shut down will be required. A regan has advised that planning is underway to arrange a suitable time to repair.JMH 11kV UGOH blown up at pole 4M-80046. Repairs will be made during daylight hrs when safe, per ERC (Dean Davies). Excluded OMS No. 1890080, 1890100 | November | 2021 | 2022Q2 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | Unknown | Unknown | 2021-11-28 | N | 4790.6923 | N | 6 | N | N | 1.1101 | 39.4971 | 45511.6563
[7 empty] | 1298 | 15781 | 1891307 | 2021-12-03 09:27 | 2021-12-03 17:26 | 479 | 11kV | 4693 | 13 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 212289 tripped on Earth failt E-Cph found Blown S/A on sub 70795 Excluded OMS 1891307 | December | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2021-12-03 | N | 361 | N | 9 | N | N | 1.1101 | 39.4971 | 3429.506
[7 empty] | 728 | 9301 | 1891407 | 2021-12-03 14:39 | 2021-12-03 18:30 | 231 | 11kV | 6599 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 212306 A phase DOLF No fault found Excluded OMS 1891407 | December | 2021 | 2022Q2 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2021-12-03 | N | 227.5517 | N | 9 | N | N | 1.1101 | 39.4971 | 4822.3546
[7 empty] | 306 | 3980 | 1891441 | 2021-12-03 16:21 | 2021-12-03 18:30 | 129 | 11kV | 3354 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 212304 A & C Phase DOLF : 20 Amp A Pople LF 40534 A C phase 20A LF Excluded OMS 1891441 | December | 2021 | 2022Q2 | 2022 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2021-12-03 | N | 129 | N | 9 | N | N | 1.1101 | 39.4971 | 2451.0043
[7 empty] | 276 | 3550 | 1891404 | 2021-12-03 14:32 | 2021-12-03 18:35 | 243 | 11kV | 4860 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 212305 Found wire down at pole HR91883 Excluded 1891404 | December | 2021 | 2022Q2 | 2022 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2021-12-03 | N | 243 | N | 9 | N | N | 1.1101 | 39.4971 | 3551.5447
[7 empty] | 242 | 2960 | 1891487 | 2021-12-03 20:56 | 2021-12-03 22:30 | 94 | 11kV | 77186 | 981 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.22 tripped on C phase OC Cause not ascertained See 1892490 1892491 1892492 | December | 2021 | 2022Q2 | 2022 | ZN1287:PA22 | ZN1287:PA22 | ZN01287/000022 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-12-03 | N | 78.6809 | N | 9 | N | N | 1.1101 | 39.4971 | 56405.2522
[7 empty] | 1642 | 19881 | 1891502 | 2021-12-03 22:58 | 2021-12-04 08:44 | 586 | 11kV | 1172 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212311 Single phase DOLF : 10 Amp Excluded OMS 1891502 | December | 2021 | 2022Q2 | 2022 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2021-12-03 | N | 586 | N | 9 | N | N | 1.1101 | 39.4971 | 856.463
[7 empty] | 767 | 9555 | 1891535 | 2021-12-04 08:49 | 2021-12-04 10:38 | 109 | 11kV | 109 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212312 C Phase DOLF : 10 Amp Excluded OMS 1891535 | December | 2021 | 2022Q2 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-12-04 | N | 109 | N | 5 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 1367 | 16743 | 1891525 | 2021-12-04 08:03 | 2021-12-04 11:45 | 222 | 11kV | 2664 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212313 A Phase DOLF : 20 Amp Excluded OMS 1891525 | December | 2021 | 2022Q2 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2021-12-04 | N | 222 | N | 5 | N | N | 1.1101 | 39.4971 | 1946.7726
[7 empty] | 1044 | 13368 | 1891598 | 2021-12-04 14:49 | 2021-12-04 16:00 | 71 | 11kV | 66413 | 1168 | HV | Wind Blown Debris | Adverse Weather/Environment | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn15004 Newport - Pnl.9 tripped on IOC A phase Abnormal: Open bonds near PT15467 with CP24703 Sw/A closed (DMA) Explosive fault at PT16016 Howell Cl. Witness said there was a silver helium baloon on top of Tx. See 1892480 1892481 | December | 2021 | 2022Q2 | 2022 | ZN15004:PA9 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | OH | Veg | 2021-12-04 | N | 56.8604 | N | 5 | N | N | 1.1101 | 39.4971 | 48532.6615
[7 empty] | 972 | 11874 | 1891574 | 2021-12-04 11:34 | 2021-12-04 16:40 | 306 | 11kV | 1224 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212315 Broken Live Line Lead Excluded OMS 1891574 | December | 2021 | 2022Q2 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2021-12-04 | N | 306 | N | 5 | N | N | 1.1101 | 39.4971 | 894.4631
[7 empty] | 862 | 10670 | 1891475 | 2021-12-03 18:54 | 2021-12-04 17:33 | 1359 | 11kV | 22704 | 17 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212309 Single phase Tree on mains at P. ED-30003 Excluded OMS 1891475 | December | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2021-12-03 | N | 1335.5294 | N | 9 | N | N | 1.1101 | 39.4971 | 16591.4135
[7 empty] | 599 | 7597 | 1891648 | 2021-12-04 22:33 | 2021-12-05 00:25 | 112 | 11kV | 23585 | 235 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | REC64824 Deepwater Holly - tripped on OC 11kV insulators broken on pole MO-72977 See 1892476 1892477 1892478 | December | 2021 | 2022Q2 | 2022 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2021-12-04 | N | 100.3617 | N | 5 | N | N | 1.1101 | 39.4971 | 17235.2224
[7 empty] | 655 | 8482 | 1891671 | 2021-12-05 08:01 | 2021-12-05 10:15 | 134 | 11kV | 268 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212317 C Phase DOLF : 10 Amp Excluded OMS 1891671 | December | 2021 | 2022Q2 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2021-12-05 | N | 134 | N | 3 | N | N | 1.1101 | 39.4971 | 195.8465
[7 empty] | 21 | 246 | 1891722 | 2021-12-05 14:06 | 2021-12-05 16:15 | 129 | 11kV | 8385 | 65 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | PT13907 Yhelma Grandview - Roadside HDO blown Cause not ascertained | December | 2021 | 2022Q2 | 2022 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Veg | 2021-12-05 | N | 129 | N | 3 | N | N | 1.1101 | 39.4971 | 6127.5107
[7 empty] | 610 | 7764 | 1891712 | 2021-12-05 12:23 | 2021-12-05 20:40 | 497 | 11kV | 81868.3333 | 165 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Section of Pnl.10 Harbord Zn interrupted from LB20547 to AB20745 to repair broken cross arm at pole FF58683 CC1: 22-"Refer to SOp" CC2: 23-"Mains Required" CC3: 22-"Refer to SOp" FRC1: 363-"Damaged/Defective Cross-Arm - Requires repair/replacement" FRC2: 363-"Damaged/Defective Cross-Arm - Requires repair/replacement" FRC3: 300-"Specify details by voice" | December | 2021 | 2022Q2 | 2022 | ZN15008:PA10 | ZN15008:PA10 | ZN15008/000010 | NORTHERN BEACHES | OH | Not Veg | 2021-12-05 | N | 496.1717 | N | 3 | N | N | 1.1101 | 39.4971 | 59826.9633
[7 empty] | 73 | 905 | 1891892 | 2021-12-06 10:20 | 2021-12-06 13:05 | 165 | 11kV | 330 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212320 B Phase DOLF : 10 Amp Excluded OMS 1891892 | December | 2021 | 2022Q2 | 2022 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2021-12-06 | N | 165 | N | 2 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 273 | 3509 | 1891990 | 2021-12-06 14:00 | 2021-12-06 14:50 | 50 | 11kV | 50 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212322 3 Phase DOLF : 10 Amp Excluded OMS 1891990 | December | 2021 | 2022Q2 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2021-12-06 | N | 50 | N | 2 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 402 | 5176 | 1892140 | 2021-12-07 11:48 | 2021-12-07 12:57 | 69 | 11kV | 24357 | 353 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212323 No protection operations. 11kV insulator replaced pole IU-61825 | December | 2021 | 2022Q2 | 2022 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2021-12-07 | N | 69 | N | 11 | N | N | 1.1101 | 39.4971 | 17799.3772
[7 empty] | 1039 | 13210 | 1892203 | 2021-12-07 14:08 | 2021-12-07 15:33 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212325 A Phase DOLF : 10 Amp | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-07 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 1173 | 14699 | 1892536 | 2021-12-07 16:09 | 2021-12-07 16:43 | 34 | 11kV | 3910 | 115 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | REC44961 Morgan Pacific 0.4 tripped on OC Lightning Storm | December | 2021 | 2022Q2 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2021-12-07 | N | 34 | N | 11 | N | N | 1.1101 | 39.4971 | 2857.3127
[7 empty] | 149 | 1797 | 1892168 | 2021-12-07 14:22 | 2021-12-07 17:30 | 187.6667 | 11kV | 2627.3333 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212326 A & C Phase DOLFs : 10 Amp | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-07 | N | 187.6667 | N | 11 | N | N | 1.1101 | 39.4971 | 1919.9777
[7 empty] | 752 | 9478 | 1892229 | 2021-12-07 15:15 | 2021-12-07 19:00 | 225 | 11kV | 225 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212327 A & C Phase DOLF's : 20 Amp excluded OMD 1892229 | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-07 | N | 225 | N | 11 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 398 | 5150 | 1892211 | 2021-12-07 16:43 | 2021-12-07 21:21 | 278 | 11kV | 35430 | 210 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC44995 Kulnura tripped on IOC & OC Abnormal: LB42005 Open DMA with LB45195 Closed Tree on 11kV OH adj USL41566 See 1892538 1892539 | December | 2021 | 2022Q2 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-12-07 | N | 168.7143 | N | 11 | N | N | 1.1101 | 39.4971 | 25891.199
[7 empty] | 837 | 10282 | 1892230 | 2021-12-07 17:54 | 2021-12-07 21:55 | 241 | 11kV | 1205 | 5 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | PT13362 Ironbarks Kirks 1.7 - Footpath phase HDO blown Lightning | December | 2021 | 2022Q2 | 2022 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2021-12-07 | N | 241 | N | 11 | N | N | 1.1101 | 39.4971 | 880.5785
[7 empty] | 1643 | 19891 | 1892331 | 2021-12-07 19:55 | 2021-12-07 22:50 | 175 | 11kV | 2450 | 14 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | PT12139 Mimosa Elizabeth Bay - Middle and Footpath phase HDOs blown Lightning Customers also impacted by wider area previous outage that began at 17:37 refer to OMS 1892547 | December | 2021 | 2022Q2 | 2022 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2021-12-07 | N | 175 | N | 11 | N | N | 1.1101 | 39.4971 | 1790.3877
[7 empty] | 442 | 5449 | 1892318 | 2021-12-07 22:06 | 2021-12-08 02:37 | 271 | 11kV | 10298 | 38 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 212333 B Phase DOLF : 63 Amp Lightening Arrestor on fire. Excluded OMS 1892318 CC1: 22-"Refer to SOp" | December | 2021 | 2022Q2 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-12-07 | N | 271 | N | 11 | N | N | 1.1101 | 39.4971 | 7525.4747
[7 empty] | 212 | 2615 | 1892349 | 2021-12-08 03:34 | 2021-12-08 04:43 | 69 | 11kV | 40089 | 581 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Pnl.13 Rockdale - 11kV Bond burnt off above S10349 Moate Gordon | December | 2021 | 2022Q2 | 2022 | ZN10998:PA13 | ZN10998:PA13 | ZN10998/000013 | BAYSIDE | OH | Not Veg | 2021-12-08 | N | 69 | N | 24 | Y | Y | 1.1101 | 39.4971 | 29295.8588
[7 empty] | 329 | 4493 | 1892363 | 2021-12-08 06:54 | 2021-12-08 09:05 | 131 | 11kV | 262 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212342 Single phase DOLF : 10 Amp Excluded OMS 1892363 | December | 2021 | 2022Q2 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 131 | N | 24 | Y | Y | 1.1101 | 39.4971 | 191.4619
[7 empty] | 333 | 4566 | 1892337 | 2021-12-07 22:30 | 2021-12-08 10:15 | 705 | 11kV | 6876 | 22 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 212344 Line DOLFs blew as did ceveral sub fuses. Excluded OMS 1892337 | December | 2021 | 2022Q2 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2021-12-07 | N | 312.5455 | N | 11 | N | N | 1.1101 | 39.4971 | 5024.778
[7 empty] | 1037 | 13118 | 1892372 | 2021-12-08 07:53 | 2021-12-08 10:30 | 157 | 11kV | 192084 | 1520 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.31 tripped on: Earth Fault Abnormal: S1127 Sw/B Closed with S2398 Sw/A Open. S1980 Sw/B Closed with S48553 Sw/A Open UG cable damaged by contractor outside 31 Boden Ave See1892803 1892804 | December | 2021 | 2022Q2 | 2022 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2021-12-08 | N | 126.3711 | N | 24 | Y | Y | 1.1101 | 39.4971 | 140369.3217
[7 empty] | 1161 | 14574 | 1892347 | 2021-12-08 02:55 | 2021-12-08 11:34 | 519 | 11kV | 4403 | 12 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Ex Pnl.4 Lake Munmorah - LB46170 had a burnt off bond. 11kV feeder isolated between AB41889 and LB40170 for repairs at 0900 See 1894461 1894462 | December | 2021 | 2022Q2 | 2022 | ZN13000:PA4 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2021-12-08 | N | 366.9167 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3217.5825
[7 empty] | 673 | 8634 | 1892487 | 2021-12-08 13:05 | 2021-12-08 14:20 | 75 | 11kV | 225 | 3 | HV | Animal Goanna | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212347 B Phase DOLF : 10 Amp Goanna contacted 11kVcausing fault. Excluded OMS 1892487 | December | 2021 | 2022Q2 | 2022 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2021-12-08 | N | 75 | N | 24 | Y | Y | 1.1101 | 39.4971 | 164.4234
[7 empty] | 1568 | 19182 | 1892447 | 2021-12-08 10:42 | 2021-12-08 15:18 | 276.3667 | 11kV | 276.3667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212348 3 phase DOLF's : 10 Amp Excluded OMS 1892509 | December | 2021 | 2022Q2 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 276.3667 | N | 24 | Y | Y | 1.1101 | 39.4971 | 201.9606
[7 empty] | 1462 | 18031 | 1893035 | 2021-12-08 16:03 | 2021-12-08 16:07 | 4 | 11kV | 616 | 154 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212350 Trip & Reclose 3 fault operations Overcurrent B phase 366A C pjhase 372A 2 trip and recloses in 2 minutes. | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 4 | N | 24 | Y | Y | 1.1101 | 39.4971 | 450.1546
[7 empty] | 185 | 2417 | 1892541 | 2021-12-08 15:54 | 2021-12-08 18:50 | 175.7333 | 11kV | 3866.1333 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212402 B & C Phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | December | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-12-08 | N | 175.7333 | N | 24 | Y | Y | 1.1101 | 39.4971 | 2825.2562
[7 empty] | 373 | 4957 | 1892564 | 2021-12-08 16:25 | 2021-12-08 19:18 | 172.85 | 11kV | 36644.2 | 212 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212360 Earth Fault Sensitive Earth fault | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 172.85 | N | 24 | Y | Y | 1.1101 | 39.4971 | 26778.5005
[7 empty] | 371 | 4951 | 1892233 | 2021-12-07 23:45 | 2021-12-08 20:25 | 1240 | 11kV | 1240 | 1 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Lightning | N | PT11802 Keighley Grants 1.4 - Interruted due to pole fire Restored via Generator | December | 2021 | 2022Q2 | 2022 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2021-12-07 | N | 1240 | N | 11 | N | N | 1.1101 | 39.4971 | 906.1554
[7 empty] | 476 | 5800 | 1892634 | 2021-12-08 19:22 | 2021-12-08 20:40 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212394 Single phase DOLF : 10 Amp Excluded OMS 1892634 | December | 2021 | 2022Q2 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2021-12-08 | N | 78 | N | 24 | Y | Y | 1.1101 | 39.4971 | 114.0002
[7 empty] | 978 | 11986 | 1892533 | 2021-12-08 15:34 | 2021-12-08 20:45 | 310.5833 | 11kV | 5901.0833 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212392 A & B Phase DOLF's : 16 Amp | December | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2021-12-08 | N | 310.5833 | N | 24 | Y | Y | 1.1101 | 39.4971 | 4312.3376
[7 empty] | 1371 | 16807 | 1892614 | 2021-12-08 18:12 | 2021-12-08 20:55 | 163 | 11kV | 652 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212395 A Phase DOLF : 10 Amp Excluded OMS 1892614 | December | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-12-08 | N | 163 | N | 24 | Y | Y | 1.1101 | 39.4971 | 476.4624
[7 empty] | 1579 | 19309 | 1892606 | 2021-12-08 18:02 | 2021-12-08 21:09 | 186.7833 | 11kV | 747.1333 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212397 A Phase DOLF : 10 Amp Excluded OMS 1892606 CC1: 22-"Refer to SOp" | December | 2021 | 2022Q2 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2021-12-08 | N | 186.7833 | N | 24 | Y | Y | 1.1101 | 39.4971 | 545.983
[7 empty] | 1056 | 13514 | 1892531 | 2021-12-08 15:22 | 2021-12-08 21:24 | 362 | 11kV | 362 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | No LID No supply call see OMS 1892531 T&R captured jobs | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-08 | N | 362 | N | 24 | Y | Y | 1.1101 | 39.4971 | 264.5389
[7 empty] | 1036 | 13099 | 1892642 | 2021-12-08 19:53 | 2021-12-08 22:45 | 172 | 11kV | 5848 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212401 C Phase DOLF : 20 Amp | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 172 | N | 24 | Y | Y | 1.1101 | 39.4971 | 4273.5459
[7 empty] | 696 | 8952 | 1892620 | 2021-12-08 21:53 | 2021-12-08 23:39 | 106 | 11kV | 5016 | 48 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 212375 blown tapping at 9L-40811. Excluded OMS 1892620 | December | 2021 | 2022Q2 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2021-12-08 | N | 104.5 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3665.5449
[7 empty] | 468 | 5751 | 1892560 | 2021-12-08 16:13 | 2021-12-08 23:59 | 466 | 11kV | 4194 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212372 and also LID 212403 Replace Lightning Arrestor Excluded OMS 1892560 | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 466 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3064.8515
[7 empty] | 78 | 969 | 1892681 | 2021-12-09 05:34 | 2021-12-09 06:48 | 74 | 11kV | 95830 | 1295 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn3472 Secton 11kV Panel 28 tripped, reclosed and locked out on RelaysL A and B phase IOC, Reclose, Timer and lockout Signals: 11kV Trip Field EFI's NIL Cause: Near PT2197 Australia Hum - No visable damage to mains. Tree branch on OH mains | December | 2021 | 2022Q2 | 2022 | ZN3472:PA28 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-12-09 | N | 74 | N | 12 | N | N | 1.1101 | 39.4971 | 70029.7375
[7 empty] | 24 | 261 | 1892690 | 2021-12-09 06:41 | 2021-12-09 08:25 | 104 | 11kV | 208 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212388 Single Phase DOLF : 10 Amp Excluded OMS 1892690 | December | 2021 | 2022Q2 | 2022 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Veg | 2021-12-09 | N | 104 | N | 12 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 155 | 1851 | 1892657 | 2021-12-08 20:34 | 2021-12-09 09:05 | 751 | 11kV | 1502 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212390 Single phase DOLF : 10 Amp Excluded OMS 1892657 | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 751 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1097.6173
[7 empty] | 596 | 7584 | 1892646 | 2021-12-08 19:55 | 2021-12-09 09:25 | 810 | 11kV | 2430 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 212389 Single phase sub isolated to repair burnt off LL Clamp Excluded oms 1892646 | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-12-08 | N | 810 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1775.7723
[7 empty] | 83 | 997 | 1892628 | 2021-12-08 18:39 | 2021-12-09 10:20 | 941 | 11kV | 3764 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 212400 3 phase DOLF : 16 Amp Excluded OMS 1892628 | December | 2021 | 2022Q2 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2021-12-08 | N | 941 | N | 24 | Y | Y | 1.1101 | 39.4971 | 2750.6202
[7 empty] | 1084 | 13887 | 1892587 | 2021-12-08 17:06 | 2021-12-09 11:15 | 1089 | 11kV | 5445 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 212376 Blown Live Line Clamp Lead Excluded OMS 1892587 | December | 2021 | 2022Q2 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-12-08 | N | 1089 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3979.0454
[7 empty] | 1657 | 20128 | 1892734 | 2021-12-09 08:45 | 2021-12-09 12:16 | 211 | 11kV | 633 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Replaced blown dolf 10amp | December | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-12-09 | N | 211 | N | 12 | N | N | 1.1101 | 39.4971 | 462.5777
[7 empty] | 1480 | 18306 | 1892661 | 2021-12-08 21:10 | 2021-12-09 16:45 | 1175 | 11kV | 7050 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212417 A Phase DOLF : 10 Amp Excluded OMS 1892661 | December | 2021 | 2022Q2 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2021-12-08 | N | 1175 | N | 24 | Y | Y | 1.1101 | 39.4971 | 5151.9321
[7 empty] | 864 | 10701 | 1892571 | 2021-12-09 11:35 | 2021-12-09 18:00 | 384.65 | 11kV | 3461.85 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 212415 SWER Isolating Transformer failed in service | December | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-12-09 | N | 384.65 | N | 12 | N | N | 1.1101 | 39.4971 | 2529.8179
[7 empty] | 923 | 11272 | 1892866 | 2021-12-09 15:26 | 2021-12-09 18:43 | 197 | 11kV | 21670 | 110 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212420 Sensitive Earth Fault Faulty Transformer sub 65420 Excluded OMS 1892866 | December | 2021 | 2022Q2 | 2022 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2021-12-09 | N | 197 | N | 12 | N | N | 1.1101 | 39.4971 | 15835.7968
[7 empty] | 709 | 9136 | 1892915 | 2021-12-08 19:00 | 2021-12-09 18:45 | 1425 | 11kV | 2013 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212416 Single phase DOLF : 10 Amp | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-08 | N | 33 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1471.041
[7 empty] | 1130 | 14306 | 1893158 | 2021-12-09 16:13 | 2021-12-09 19:15 | 182 | 11kV | 1638 | 9 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 212404 Isolated for repairs Broken xarm 7M-70056 | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2021-12-09 | N | 182 | N | 12 | N | N | 1.1101 | 39.4971 | 1197.0021
[7 empty] | 839 | 10313 | 1892891 | 2021-12-09 16:43 | 2021-12-09 22:10 | 327 | 11kV | 327 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 212427 Replaced blown lightning arrestor Excluded OMS 1892891 | December | 2021 | 2022Q2 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-12-09 | N | 327 | N | 12 | N | N | 1.1101 | 39.4971 | 238.962
[7 empty] | 61 | 707 | 1892845 | 2021-12-09 14:05 | 2021-12-09 23:05 | 540 | 11kV | 540 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 212428 C Phase DOLF : 10 Amp Excluded OMS 1892845 | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2021-12-09 | N | 540 | N | 12 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 171 | 2192 | 1892939 | 2021-12-09 19:59 | 2021-12-09 23:25 | 206 | 11kV | 130904 | 1646 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | iR49612 Barinya Wells tripped on: OC and SEF Tree on the mains between AB43779 to AB40759 to LB42654 See 1894451 1894452 | December | 2021 | 2022Q2 | 2022 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2021-12-09 | N | 79.5286 | N | 12 | N | N | 1.1101 | 39.4971 | 95660.7822
[7 empty] | 662 | 8528 | 1892930 | 2021-12-09 19:51 | 2021-12-10 00:50 | 299 | 11kV | 305234 | 1262 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn12660 Woy Woy - Pnl.14 tripped on: C phase IOC Abnormal: USL32897 Open with CP64362 Closed Weather related. Patrolled Ok See 189447 189448 189449 | December | 2021 | 2022Q2 | 2022 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2021-12-09 | N | 241.8653 | N | 12 | N | N | 1.1101 | 39.4971 | 223056.0043
[7 empty] | 926 | 11291 | 1893066 | 2021-12-10 09:36 | 2021-12-10 10:17 | 41 | 11kV | 17784 | 994 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S342 Paddington Zone Panel 24 Tripped on Signals: 11kV Trip Relays: B phase to Neutral trip Cause: UG fault between S35426 Mary Floods SW/B to S35852 SW/A to S65389 See OMS 1894383 1894384 1894385 1893066 | December | 2021 | 2022Q2 | 2022 | ZN342:PA24 | ZN342:PA24 | ZN00342/000024 | SYDNEY | UG | Not Veg | 2021-12-10 | N | 17.8913 | N | 10 | N | N | 1.1101 | 39.4971 | 12996.0227
[7 empty] | 417 | 5293 | 1893084 | 2021-12-10 10:05 | 2021-12-10 11:10 | 65 | 11kV | 910 | 14 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 212431 ISOLATED FOR REPAIRS AT abs 47269 Excluded 1893084 | December | 2021 | 2022Q2 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2021-12-10 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 686 | 8760 | 1893852 | 2021-12-09 15:26 | 2021-12-10 11:15 | 1189 | 11kV | 2378 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 212453 A & B Phase DOLF :10 Amp NO OMS job found TX failure, times derived from note on DNMS | December | 2021 | 2022Q2 | 2022 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2021-12-09 | N | 1189 | N | 12 | N | N | 1.1101 | 39.4971 | 1737.7723
[7 empty] | 915 | 11243 | 1893093 | 2021-12-10 10:10 | 2021-12-10 11:15 | 65 | 11kV | 715 | 11 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 212430 ISOLATED FOR REPAIRS AT abs 47269 Excluded OMS 1893093 | December | 2021 | 2022Q2 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2021-12-10 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 522.5009
[7 empty] | 138 | 1677 | 1893633 | 2021-12-10 12:25 | 2021-12-10 13:40 | 75 | 11kV | 825 | 11 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 212437 Section isolated for repairs to burnt off tapping at pole AJ90096 | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-12-10 | N | 75 | N | 10 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 328 | 4447 | 1892562 | 2021-12-08 16:16 | 2021-12-10 14:05 | 2749 | 11kV | 8247 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Flood | N | LID 212436 Transformer failed in service. Note: delay in restoration due to excessive rain causing localised flooding, which took several days to withdraw Excluded OMS 1892562 Note: customers also affected by wider area outage at same time refer to OMS 1892564 | December | 2021 | 2022Q2 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2021-12-08 | N | 2749 | N | 24 | Y | Y | 1.1101 | 39.4971 | 6026.6644
[7 empty] | 1147 | 14420 | 1892927 | 2021-12-09 19:19 | 2021-12-10 15:50 | 1231 | 11kV | 156384 | 429 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | 11kV Recloser CP45189 Cooks Peats Ridge 0.5 Tripped on Relays: OC Trip Cause: Multiple tree on mains beyond recloser CP44945 Lower Mangrove Cause: Weather Related See OMS 1894030 1894031 189 4032 1894033 1894034 1894035 1894038 1892961 1892927 | December | 2021 | 2022Q2 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2021-12-09 | N | 364.5315 | N | 12 | N | N | 1.1101 | 39.4971 | 114280.8147
[7 empty] | 1295 | 15748 | 1893181 | 2021-12-10 16:00 | 2021-12-10 19:00 | 180 | 11kV | 900 | 5 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 212441 Pole on fire WT-20219 Excluded OMS 1893181 | December | 2021 | 2022Q2 | 2022 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2021-12-10 | N | 180 | N | 10 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 850 | 10540 | 1893160 | 2021-12-10 13:13 | 2021-12-10 20:25 | 432 | 11kV | 432 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212443 A Phase broken LLC Dropper lead sub 27925 Excluded OMS 1893160 | December | 2021 | 2022Q2 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2021-12-10 | N | 432 | N | 10 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 1258 | 15319 | 1893185 | 2021-12-10 19:00 | 2021-12-10 20:30 | 90 | 11kV | 9180 | 102 | HV | Arcing | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 212442 PG Clamp Arcing pole HR-61861 Excluded OMS.1893185 | December | 2021 | 2022Q2 | 2022 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2021-12-10 | N | 90 | N | 10 | N | N | 1.1101 | 39.4971 | 6708.4732
[7 empty] | 1554 | 19051 | 1893150 | 2021-12-10 12:48 | 2021-12-11 00:35 | 707 | 11kV | 16901 | 46 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212440 Sensitive Earth Fault Trees grown into mains excluded OMS 1893150 | December | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-12-10 | N | 367.413 | N | 10 | N | N | 1.1101 | 39.4971 | 12350.7523
[7 empty] | 1364 | 16693 | 1893277 | 2021-12-11 00:40 | 2021-12-11 02:28 | 108 | 11kV | 29784 | 300 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35400 North Sydney the 11kV Panel 83 tripped on Relays: Protection A - Trip, B phase, Neutral, EF Protection B - Trip, B Phase, EFI, EFI Cause UG Fault 11kV UG fault from S2899 Little Walker Pacific SW?B to S35547 Lavender Cliff SW/A to S6306 Arthur Pacific SwA | December | 2021 | 2022Q2 | 2022 | ZN35400:PA83 | ZN35400:PA83 | ZN35400/000083 | NORTH SYDNEY | UG | Not Veg | 2021-12-11 | N | 99.28 | N | 2 | N | N | 1.1101 | 39.4971 | 21765.2687
[7 empty] | 704 | 9079 | 1893376 | 2021-12-11 15:18 | 2021-12-11 19:10 | 232 | 11kV | 75834 | 1317 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV Bond off (Pole WW-50) with 11kV Mains making contact with SL mains adjacent LB45205 on HV at pole WW72 Cause: Balloon on HV mains @ pole WW72 - 11kV mains into LV adjacent to LB45205 At Zn12660 Woy Woy Panel 8 interrupted for safety - 11kV Mains into LV reported by EMSO 93 Aaron Wagstraf See OMS 1893832 1893831 1893402 1893398 1893383 1893376 1893370 1893367 | December | 2021 | 2022Q2 | 2022 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Veg | 2021-12-11 | N | 57.5809 | N | 2 | N | N | 1.1101 | 39.4971 | 55417.2505
[7 empty] | 721 | 9243 | 1893448 | 2021-12-12 07:59 | 2021-12-12 08:52 | 53 | 11kV | 85471 | 1717 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl.2 tripped on OC & EF UG cable fault between S64392 to S6213 to S47274 See 1894463 1894464 | December | 2021 | 2022Q2 | 2022 | ZN7900:PA2 | ZN7900:PA2 | ZN07900/000002 | SYDNEY | UG | Not Veg | 2021-12-12 | N | 49.7793 | N | 3 | N | N | 1.1101 | 39.4971 | 62459.6858
[7 empty] | 1432 | 17645 | 1893455 | 2021-12-12 08:23 | 2021-12-12 09:55 | 92 | 11kV | 154122 | 1694 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn10994 Mortdale - Pnl.19 tripped on SEL Abnormal: AB31265 Closed with AB31153 Open (DMA) Bond durnt off AB30063 PT10222 in LV // since 21/12/2019 for pT10442 which is not on any diagram - caused mains to burn down See 1894482 1894483 1894484 | December | 2021 | 2022Q2 | 2022 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2021-12-12 | N | 90.9811 | N | 3 | N | N | 1.1101 | 39.4971 | 112627.8118
[7 empty] | 732 | 9336 | 1893475 | 2021-12-12 10:24 | 2021-12-12 13:15 | 171 | 11kV | 342 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212448 A Phase DOLF : 16 Amp Excluded OMS 1893475 | December | 2021 | 2022Q2 | 2022 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2021-12-12 | N | 171 | N | 3 | N | N | 1.1101 | 39.4971 | 249.9235
[7 empty] | 753 | 9481 | 1893526 | 2021-12-13 05:02 | 2021-12-13 08:01 | 179 | 11kV | 113675 | 858 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S12600 Lisarow No12 CB tripped, reclosed, tripped and locked out on Relays: A and B phase OC, Reclose, Lockout, timing Cause not ascertained for outage see OMS 1893815 1893816 1893817 1893526 | December | 2021 | 2022Q2 | 2022 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2021-12-13 | N | 132.4883 | N | 3 | N | N | 1.1101 | 39.4971 | 83070.3372
[7 empty] | 139 | 1709 | 1893624 | 2021-12-13 12:12 | 2021-12-13 13:08 | 56.3833 | 11kV | 107974.0833 | 1915 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Blown11kV C phase tapping at UGOH no cause found area back feed at 1308hrs | December | 2021 | 2022Q2 | 2022 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2021-12-13 | N | 56.3833 | N | 3 | N | N | 1.1101 | 39.4971 | 78904.2754
[7 empty] | 847 | 10504 | 1892979 | 2021-12-10 02:04 | 2021-12-13 13:30 | 5006 | 11kV | 56138 | 98 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Flood | N | LID 212434 and 212435 Broken xarm and mains down beyond links 43521 no access due to water levels. Luke Watters to organise repairs. MdV TARGETS B ph 58amp, Cph 26amp, EF 51amp Excluded OMS 1892979 | December | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2021-12-10 | N | 572.8367 | N | 10 | N | N | 1.1101 | 39.4971 | 41023.9946
[7 empty] | 222 | 2724 | 1893005 | 2021-12-10 06:53 | 2021-12-13 14:20 | 4767 | 11kV | 27777 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Flood | N | LID 212454 Looking through recoprds looks like depot staff identified flooding beyond LF 40875. 53504 had damage to private pillar restored at 14:20 13/12/21 | December | 2021 | 2022Q2 | 2022 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2021-12-10 | N | 4629.5 | N | 10 | N | N | 1.1101 | 39.4971 | 20298.6123
[7 empty] | 1664 | 20209 | 1893663 | 2021-12-13 15:01 | 2021-12-13 16:23 | 82 | 11kV | 1148 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 212457 It appears 11kV mains detached from pole at 9K-90237 in recent storms. Excluded OMS 1893663 & 1893679 | December | 2021 | 2022Q2 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2021-12-13 | N | 82 | N | 3 | N | N | 1.1101 | 39.4971 | 838.9245
[7 empty] | 429 | 5384 | 1893766 | 2021-12-14 02:57 | 2021-12-14 05:30 | 153 | 11kV | 251772 | 2185 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Zn10995 Riverwood - Pnl.7 tripped on: A Phase IOC @ PT10856 Melvin Broad Arrow - Roadside HDOs defective See 1894491 1894492 | December | 2021 | 2022Q2 | 2022 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2021-12-14 | N | 115.2275 | N | 6 | N | N | 1.1101 | 39.4971 | 183987.5516
[7 empty] | 204 | 2586 | 1893769 | 2021-12-14 04:33 | 2021-12-14 05:38 | 65 | 11kV | 86970 | 1338 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ## CB 11899 trip and LO on C ph OC. Patrolled nothing found. DQ Note No LID report. | December | 2021 | 2022Q2 | 2022 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2021-12-14 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 63555.1108
[7 empty] | 43 | 572 | 1893770 | 2021-12-14 04:37 | 2021-12-14 05:38 | 61 | 11kV | 3599 | 59 | HV | Animal Possum | Animal | O/H Conductor Insulated | Unplanned | No Weather Impact | N | At PT12831 Narcooma Narambu - Footpath blown HDO 31amp Cause: Possum found at PT see OMS 1839805 1893770 | December | 2021 | 2022Q2 | 2022 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2021-12-14 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 2630.043
[7 empty] | 1217 | 15031 | 1893779 | 2021-12-14 09:25 | 2021-12-14 11:37 | 132 | 11kV | 924 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 212465 BLOWN TAPPING AT POLE HR-52022 No protection operation to repair, there wasa trip and reclose earlier today on a seperate report. | December | 2021 | 2022Q2 | 2022 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2021-12-14 | N | 132 | N | 6 | N | N | 1.1101 | 39.4971 | 675.2319
[7 empty] | 170 | 2170 | 1893858 | 2021-12-14 12:03 | 2021-12-14 13:50 | 107 | 11kV | 214 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212464 C Phase DOLF : 10 Amp Excluded OMS 1893858 | December | 2021 | 2022Q2 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2021-12-14 | N | 107 | N | 6 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 1051 | 13469 | 1893938 | 2021-12-14 16:11 | 2021-12-14 20:00 | 229 | 11kV | 229 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212466 A & C Phases Broken strands on 11kV mains at pole 6J30244 Excluded OMS 1893938 | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2021-12-14 | N | 229 | N | 6 | N | N | 1.1101 | 39.4971 | 167.3464
[7 empty] | 966 | 11759 | 1893992 | 2021-12-15 08:19 | 2021-12-15 11:27 | 188 | 11kV | 18077 | 109 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212469 2 fault operations Overcurrent, Earth Fault Tipper truck contacted OHM at sub 22994 Excluded OMS 1893992 | December | 2021 | 2022Q2 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2021-12-15 | N | 165.844 | N | 3 | N | N | 1.1101 | 39.4971 | 13210.1384
[7 empty] | 39 | 442 | 1894122 | 2021-12-15 16:23 | 2021-12-15 17:25 | 62 | 11kV | 186 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212471 A Phase DOLF : 10 Amp Excluded OMS 1894122 | December | 2021 | 2022Q2 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2021-12-15 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 575 | 7174 | 1894166 | 2021-12-15 20:14 | 2021-12-15 21:48 | 94 | 11kV | 54596 | 586 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC554 Arcadia Rossscommon tripped on OC Abnormal: LB62159 Closed with LB3210 open = LB1236 Closed with LB8961 Closed (NAR87276) Tree on mains near PT77568. Dop made safe See 1894436 1894437 | December | 2021 | 2022Q2 | 2022 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2021-12-15 | N | 93.1672 | N | 3 | N | N | 1.1101 | 39.4971 | 39897.1465
[7 empty] | 1009 | 12707 | 1894196 | 2021-12-16 01:30 | 2021-12-16 03:45 | 135 | 11kV | 244714 | 2603 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn10999 Kogarah -panel 12 Feeeder Tripped on Signals 11kV Tripped on Signals: 11kV Trip and lockout Relays: Earth Fault and EFI Cause: 11kV feeder has been isolated from S10253 to S10811 to PT10367 Cause not ascertained suspect UG fault See OMS 1894512 1894514 1894515 1894196 | December | 2021 | 2022Q2 | 2022 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | UG | Not Veg | 2021-12-16 | N | 94.0123 | N | 3 | N | N | 1.1101 | 39.4971 | 178829.7734
[7 empty] | 1622 | 19681 | 1894216 | 2021-12-16 07:34 | 2021-12-16 09:53 | 139 | 11kV | 192124 | 1596 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | The 11kV Panel 10 CB at ZN15011 Beacon Hill Tripped on Signals: 11kV Tip, Zone Earth Relays: OC and Eath Fault Trip A B and E, Fault Check, EFI Cause: 11kV UG feeder between S16710 Frenchs Forest Hurdis and S16376 and S16389 See OMS 1894507 1894508 1894216 11kV Feeder cable and LV dist (see 1895656) hit by contractor drilling adjacent to S16710. | December | 2021 | 2022Q2 | 2022 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | UG | Not Veg | 2021-12-16 | N | 120.3784 | N | 3 | N | N | 1.1101 | 39.4971 | 140398.5525
[7 empty] | 1409 | 17354 | 1894390 | 2021-12-16 17:25 | 2021-12-16 19:00 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212477 DOLF : 10 Amp Excluded OMS 1894390 | December | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-12-16 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 248 | 3026 | 1895722 | 2021-12-17 12:10 | 2021-12-17 14:20 | 130 | 11kV | 1430 | 11 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212482 11kV mains low adj pole CV-53681 | December | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2021-12-17 | N | 130 | N | 2 | N | N | 1.1101 | 39.4971 | 1045.0018
[7 empty] | 1107 | 14017 | 1894546 | 2021-12-17 15:35 | 2021-12-17 19:15 | 219.55 | 11kV | 27443.75 | 125 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | At Zn15008 Harbord Panel 5 Feeder beyond CP63715 was interrupted to repair broken HV cross arm | December | 2021 | 2022Q2 | 2022 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2021-12-17 | N | 219.55 | N | 2 | N | N | 1.1101 | 39.4971 | 20055.083
[7 empty] | 240 | 2950 | 1894594 | 2021-12-18 06:58 | 2021-12-18 07:46 | 48 | 11kV | 107313 | 2376 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.3 tripped on Earth Fault Bird made contact with 11kV mains at PT1156 See 1895801 1895802 | December | 2021 | 2022Q2 | 2022 | ZN398:PA3 | ZN398:PA3 | ZN00398/000003 | INNER WEST | OH | Not Veg | 2021-12-18 | N | 45.1654 | N | 10 | N | N | 1.1101 | 39.4971 | 78421.1752
[7 empty] | 1644 | 19942 | 1894645 | 2021-12-18 13:21 | 2021-12-18 14:11 | 50 | 11kV | 52976 | 1148 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 212486 Protection details required Faulty UGOH IT95075 | December | 2021 | 2022Q2 | 2022 | 213:33775 | 213:33775 | ZN00213/033775 | NEWCASTLE | Unknown | Unknown | 2021-12-18 | N | 46.1463 | N | 10 | N | N | 1.1101 | 39.4971 | 38713.2983
[7 empty] | 651 | 8430 | 1894666 | 2021-12-18 14:29 | 2021-12-18 15:40 | 71 | 11kV | 38273 | 712 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn800 Macquarie Park - Pnl.6 tripped on Earth Fault UG cable fault See 1895791 1895792 | December | 2021 | 2022Q2 | 2022 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2021-12-18 | N | 53.7542 | N | 10 | N | N | 1.1101 | 39.4971 | 27968.7795
[7 empty] | 414 | 5273 | 1894679 | 2021-12-18 15:07 | 2021-12-18 16:15 | 68 | 11kV | 66377 | 1390 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | Zn15006 Dee Why - Pnl.9 tripped on: B phase OC Footpath side lightning arrestor blown at PT15755 See 1897112 1897113 1897114 | December | 2021 | 2022Q2 | 2022 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | OH | Not Veg | 2021-12-18 | N | 47.7532 | N | 10 | N | N | 1.1101 | 39.4971 | 48506.3538
[7 empty] | 1407 | 17283 | 1894672 | 2021-12-18 14:47 | 2021-12-18 17:10 | 143 | 11kV | 184739 | 1413 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | iR61133 Minamurra Tosca tripped on: OC EFI: no EFI @ S14725 UG cable fault between S14725 Sw/A amd S147896 Sw/B See 1895776 1895778 1895779 1895780 1895784 1895783 | December | 2021 | 2022Q2 | 2022 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | UG | Not Veg | 2021-12-18 | N | 130.7424 | N | 10 | N | N | 1.1101 | 39.4971 | 135001.8123
[7 empty] | 128 | 1591 | 1894705 | 2021-12-18 18:05 | 2021-12-18 18:59 | 54 | 11kV | 91323 | 1720 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn14892 Charmhaven - Pnl.6 tripped on Earth Fault UG cable fault in frontline section of feeder | December | 2021 | 2022Q2 | 2022 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2021-12-18 | N | 53.0948 | N | 10 | N | N | 1.1101 | 39.4971 | 66736.1548
[7 empty] | 412 | 5255 | 1894723 | 2021-12-18 20:15 | 2021-12-18 21:45 | 90 | 11kV | 8460 | 94 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | LID 212488 Faulty Tx, Supply restored via LV interconnections, Tx will be replaced next day 19/12/21 Trans replaced 19/12/21 LV interruption between links 76875 and 8660 start 0950hrs supply back on 1215hrs Excluded OMS 1894723 | December | 2021 | 2022Q2 | 2022 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | OH | Not Veg | 2021-12-18 | N | 90 | N | 10 | N | N | 1.1101 | 39.4971 | 6182.3185
[7 empty] | 572 | 7109 | 1894761 | 2021-12-18 23:30 | 2021-12-19 00:22 | 52 | 11kV | 48360 | 930 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At Zn965 Pennant Hills Panel 26 Tripped and locked out on C phase IOC, Reclose Timer and Lockout Cause: Tree branch on 11kV OH Larool Cres Thornleigh - Removed by DOp Sigansl 11kV trip | December | 2021 | 2022Q2 | 2022 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2021-12-18 | N | 52 | N | 10 | N | N | 1.1101 | 39.4971 | 35340.0616
[7 empty] | 1617 | 19658 | 1894801 | 2021-12-19 00:59 | 2021-12-19 01:57 | 58 | 11kV | 4524 | 78 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At ZN 12690 Berkeley Vale - 11kV Panel 6 tripped, reclosed, tripped and locked out on: Relays: Earth Fault, EFI, reclose timer, lock out Sigs: 11kV trip, zone earth, No.12 Group earth Field EFI: S18124 Krone Enterprise Possum on UGOH below S18124 Krone Enterprise See 1895907 , 1894801 | December | 2021 | 2022Q2 | 2022 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2021-12-19 | Y | 58 | N | 6 | N | Y | 1.1101 | 39.4971 | 3306.0058
[7 empty] | 1006 | 12580 | 1894790 | 2021-12-19 00:47 | 2021-12-19 03:16 | 149.2333 | 11kV | 182866.1667 | 1690 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | At ZN847 Hornsby - 11kV Panel 14 tripped on: Relays: OC trip Signals: 11kV trip NETWORK ABNORMALLY SWITCHED: AB 1953 OPEN defective, SwB closed at S8428 Hornsby Hospital No.3 Cause of CB trip not ascertained. see 1894791, 1895890, 1895891, 1894790 | December | 2021 | 2022Q2 | 2022 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Veg | 2021-12-19 | Y | 108.2048 | N | 6 | N | Y | 1.1101 | 39.4971 | 133633.201
[7 empty] | 488 | 5943 | 1894776 | 2021-12-18 23:48 | 2021-12-19 03:22 | 214 | 11kV | 188106 | 879 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | ZN 9252 Jannali 11kV Panel 25, labelled LV35248 tripped and locked out on: Relays: OC A phase Signals: 11kV trip Field EFIs: nil 11kV mains down Sumner St Jannali. Section of 11kV feeder isolated from ZN9252 Jannali to LB 35248 to 35362. | December | 2021 | 2022Q2 | 2022 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Not Veg | 2021-12-18 | N | 214 | N | 10 | N | N | 1.1101 | 39.4971 | 137462.3166
[7 empty] | 566 | 7005 | 1894756 | 2021-12-18 23:17 | 2021-12-19 08:34 | 557 | 11kV | 94689 | 725 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | At ZN 9900 Menai - 11kV Panel 19 tripped and reclosed on: Relays: E Fault, Lock out, timer, EFI Signals: 11kV trip, G/E Field EFIs: nil Bond off at UGOH below S9698 Menai Sewage Pump See 1896025, 1896027 | December | 2021 | 2022Q2 | 2022 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | OH | Not Veg | 2021-12-18 | N | 130.6055 | N | 10 | N | N | 1.1101 | 39.4971 | 69195.9283
[7 empty] | 393 | 5140 | 1894828 | 2021-12-19 09:38 | 2021-12-19 11:40 | 122.45 | 11kV | 9918.45 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | 11kV feeder ex Revesby Pnl.4 from LB186 to PT390 interrupted to remove tree from mains outside 14 Carinya Rd | December | 2021 | 2022Q2 | 2022 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | CANTERBURY-BANKSTOWN | OH | Veg | 2021-12-19 | N | 122.45 | N | 6 | N | N | 1.1101 | 39.4971 | 7248.1107
[7 empty] | 820 | 10120 | 1895495 | 2021-12-19 20:31 | 2021-12-19 20:37 | 6 | 11kV | 9606 | 1601 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | Y | LID 212502 De energised Fdr for fire brigade to extinguish pole fire on 33kV & 11kV pole KT-40828 also refer OMS 1895818 and 1895822 Excluded OMS 1895394 | December | 2021 | 2022Q2 | 2022 | 228:85413 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2021-12-19 | Y | 6 | N | 6 | N | Y | 1.1101 | 39.4971 | 7019.7815
[7 empty] | 1057 | 13533 | 1895379 | 2021-12-19 19:11 | 2021-12-19 21:10 | 119 | 11kV | 10589 | 91 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 212493 1 fault operation 3 phase Overcurrent No fault found Excluded OMS 1895379 | December | 2021 | 2022Q2 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2021-12-19 | N | 116.3626 | N | 6 | N | N | 1.1101 | 39.4971 | 7738.1289
[7 empty] | 1385 | 16998 | 1895328 | 2021-12-19 18:46 | 2021-12-19 22:11 | 205 | 11kV | 243730 | 1298 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn1193 Lindfield - Pnl.12 tripped on A phase O/C Branch on 11kV outside 57 Stanhope See 1859949 1895950 | December | 2021 | 2022Q2 | 2022 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Veg | 2021-12-19 | N | 187.7735 | N | 6 | N | N | 1.1101 | 39.4971 | 178110.6952
[7 empty] | 220 | 2720 | 1895524 | 2021-12-19 20:56 | 2021-12-19 23:25 | 149 | 11kV | 2809 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 212495 A & C Phase Blown line fuses - no fault found Excluded OMS 1895524 | December | 2021 | 2022Q2 | 2022 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2021-12-19 | N | 133.7619 | N | 6 | N | N | 1.1101 | 39.4971 | 2052.7343
[7 empty] | 1323 | 16157 | 1894935 | 2021-12-19 15:25 | 2021-12-19 23:55 | 510 | 11kV | 510 | 1 | HV | Vegetation Blow/Fall In | Vegetation | 3rd Party Asset | Unplanned | Rain Wind Storm | Y | F.1352 MWS & DB Victoria Rd - HDO fuse operated (80A) Bark on Customer's transformer | December | 2021 | 2022Q2 | 2022 |  |  |  | HORNSBY | OH | Veg | 2021-12-19 | Y | 510 | N | 6 | N | Y | 1.1101 | 39.4971 | 372.693
[7 empty] | 28 | 295 | 1895316 | 2021-12-19 18:46 | 2021-12-20 00:27 | 341 | 11kV | 460691 | 1351 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn847 Hornsby - Pnl.22 tripped on C phase O/C & IOC Weather related | December | 2021 | 2022Q2 | 2022 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2021-12-19 | Y | 341 | N | 6 | N | Y | 1.1101 | 39.4971 | 336659.3947
[7 empty] | 720 | 9236 | 1895340 | 2021-12-19 18:34 | 2021-12-20 00:50 | 376 | 11kV | 203496 | 2028 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN3472 Secton - Panel 30 Tripped, reclosed, tripped and locked out on RelaysL OC, EF, EFI, Fault Check, Timing and Lockout Cause: OH down in Wren St See OMS 1895952 1895954 1895955 1895533 1895525 1895311 | December | 2021 | 2022Q2 | 2022 | ZN3472:PA30 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2021-12-19 | N | 100.3432 | N | 6 | N | N | 1.1101 | 39.4971 | 148708.8747
[7 empty] | 1603 | 19542 | 1895577 | 2021-12-19 23:55 | 2021-12-20 01:20 | 85 | 11kV | 11730 | 138 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | Y | LID 212504 pole KT-40828 insulator failed, main on xarm started pole fire. De energised & isolated for repairs, also see OMS 1895818 Excluded OMS 1895394 | December | 2021 | 2022Q2 | 2022 | 228:85413 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2021-12-19 | Y | 85 | N | 6 | N | Y | 1.1101 | 39.4971 | 8571.938
[7 empty] | 957 | 11606 | 1895446 | 2021-12-19 19:51 | 2021-12-20 03:20 | 449 | 11kV | 130655 | 1109 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 212496 1 fault operation B &C Phase Overcurrent tree on 11kV OHM pole IR-92470 Excluded OMS 1895446 | December | 2021 | 2022Q2 | 2022 | 238:34151 | 238:34151 | ZN00238/034151 | MAITLAND | OH | Veg | 2021-12-19 | N | 117.8133 | N | 6 | N | N | 1.1101 | 39.4971 | 95478.8203
[7 empty] | 826 | 10179 | 1895465 | 2021-12-19 20:05 | 2021-12-20 05:00 | 535 | 11kV | 189405 | 1345 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 212497 2 fault operations B & C Phase Instantaneous Overcurrent; Instantaneous Earth Fault Tree on N/O ABS 63933 pole MW-70059. HV into LV Also see report 212499. Sw 85815 Targets = 50T BC, 50TN Excluded OMS 1895465 | December | 2021 | 2022Q2 | 2022 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2021-12-19 | Y | 140.8216 | N | 6 | N | Y | 1.1101 | 39.4971 | 138411.5875
[7 empty] | 1464 | 18053 | 1895652 | 2021-12-20 07:00 | 2021-12-20 07:35 | 35 | 11kV | 700 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | PT13796 Pacific Morgan - Interrupted due to tree through 11kV mains. See also DMA for mains down from LB43657 | December | 2021 | 2022Q2 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2021-12-20 | N | 35 | N | 8 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 658 | 8507 | 1895612 | 2021-12-20 04:16 | 2021-12-20 08:21 | 244.8 | 11kV | 16891.2 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | @ PT 722 VAUGHAN LAURENCE, 11kV centre phase 31.5A HDO Operated Section of 11kV Panel 44 'Leith Malahide' feeder @ Zn 965 Pennant Hill Note: restoration time amended as per notepad, which correlates with customer call times | December | 2021 | 2022Q2 | 2022 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Veg | 2021-12-20 | N | 244.8 | N | 8 | N | N | 1.1101 | 39.4971 | 12343.5908
[7 empty] | 1635 | 19790 | 1895480 | 2021-12-19 20:07 | 2021-12-20 08:35 | 748 | 11kV | 95009 | 268 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 212499 2 fault operations B & C Phase Instantaneous Overcurrent; Instantaneous Earth Fault Tree on N/O ABS 63933 pole MW-70059. HV into LV See report 212497. LVF 14930 close on at 0835 sc. Excluded OMS 1895480 | December | 2021 | 2022Q2 | 2022 | 233:82821 | 233:82821 | ZN00233/082821 | PORT STEPHENS | OH | Veg | 2021-12-19 | Y | 354.5112 | N | 6 | N | Y | 1.1101 | 39.4971 | 69429.7749
[7 empty] | 683 | 8697 | 1894933 | 2021-12-19 15:30 | 2021-12-20 09:05 | 1055 | 11kV | 1063954 | 1177 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn3154 St Ives - Pnl.5 tripped on A Phase OC & IOC, SEF Weather related. See 1895960 1895961 1895962 | December | 2021 | 2022Q2 | 2022 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Not Veg | 2021-12-19 | Y | 903.9541 | N | 6 | N | Y | 1.1101 | 39.4971 | 777506.2019
[7 empty] | 892 | 11005 | 1895685 | 2021-12-20 08:07 | 2021-12-20 12:06 | 239 | 11kV | 19235 | 139 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212510 Fdr patrolled no problem found power restored. Excluded oms 1895685 | December | 2021 | 2022Q2 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2021-12-20 | N | 138.3813 | N | 8 | N | N | 1.1101 | 39.4971 | 14056.3707
[7 empty] | 11 | 159 | 1895398 | 2021-12-19 19:23 | 2021-12-20 12:45 | 1042 | 11kV | 1763064 | 1692 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn13000 Lake Munmorah - Pnl.5 tripped. Tree brought down OH adj USL44685 See 1895398 1895571 | December | 2021 | 2022Q2 | 2022 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Veg | 2021-12-19 | Y | 1042 | N | 6 | N | Y | 1.1101 | 39.4971 | 1288395.1696
[7 empty] | 408 | 5205 | 1894936 | 2021-12-19 15:26 | 2021-12-20 13:30 | 1324 | 11kV | 1161626 | 1177 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 15012 KILLARNEY - 11KV PANEL 8 'FORESTVILL' TRIPPED ON: Relays: A and C phase IOC, LO, EFI Signals: 11kV trip Field EFIs: 16789 Tree branch across 11kV at pole FF-84666 cnr of Nicholas Av and Cook St. See 1896529, 1896528, 1896527, 1896526, 1896525, 1895957 (LV separate event Panel 8), 1895883(withdrawn), 1895618(withdrawn), 1894936 (withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2021-12-19 | Y | 986.938 | N | 6 | N | Y | 1.1101 | 39.4971 | 848882.0186
[7 empty] | 618 | 7943 | 1895388 | 2021-12-19 19:16 | 2021-12-20 15:05 | 1189 | 11kV | 149968 | 425 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC62381 Jenson Pollock tripped on O/C Large tree on mains near LB45153. Tree also on pole WY2478 See 1895388 1895518 | December | 2021 | 2022Q2 | 2022 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2021-12-19 | Y | 352.8659 | N | 6 | N | Y | 1.1101 | 39.4971 | 109592.1911
[7 empty] | 990 | 12106 | 1895346 | 2021-12-19 18:59 | 2021-12-20 15:06 | 1207 | 11kV | 499698 | 414 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC50001 Pacific Morgan 0.46 tripped "in scan fail - protection not known" Bays of 11kV mains down from LB43657 to AB43362 REC50001 Pacific Morgan and TCAT50001 have been cut away | December | 2021 | 2022Q2 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2021-12-19 | Y | 1207 | N | 6 | N | Y | 1.1101 | 39.4971 | 365164.5598
[7 empty] | 776 | 9766 | 1895647 | 2021-12-19 15:35 | 2021-12-20 16:00 | 1465 | 11kV | 57135 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At PT15538 Yallumba Close HDO's isolated for safe removal of tree / branch on OH mains. | December | 2021 | 2022Q2 | 2022 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Veg | 2021-12-19 | Y | 1465 | N | 6 | N | Y | 1.1101 | 39.4971 | 41752.5728
[7 empty] | 1437 | 17714 | 1895342 | 2021-12-19 18:56 | 2021-12-20 16:18 | 1282 | 11kV | 54682 | 73 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN12630 PEATS RIDGE PANEL 3 'MANGROVE MOUNTAIN' - 11KV RECLOSER 49206 MANGROVE MOUNTAIN WEST TRIPPED ON OVERCURRENT STORM - 11kV 2 bays down near PT 13708 Bell Waratah 0.7. see 1896577, 1896578, 1896579, 1895342 (withdrawn), 1895564 (withdrawn), 1895644 (withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2021-12-19 | Y | 749.0685 | N | 6 | N | Y | 1.1101 | 39.4971 | 39959.9928
[7 empty] | 1273 | 15541 | 1895396 | 2021-12-19 21:00 | 2021-12-20 17:48 | 1248 | 11kV | 14976 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Section of lisarow Zn Pnl.2 interrupted between LB41933 to USL40247 Tree brought down OH mains & HDOs damaged at PT11714 See 1896658 1896657 1896656 | December | 2021 | 2022Q2 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2021-12-19 | Y | 1248 | N | 6 | N | Y | 1.1101 | 39.4971 | 10944.0191
[7 empty] | 303 | 3843 | 1896231 | 2021-12-20 17:15 | 2021-12-20 19:58 | 163 | 11kV | 85116 | 547 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35800 BANKSTOWN - 11KV Panel 19 Tripped under fault Relays: A and B phase IOC, Fault Check, EFI, TX12 Group Earth Field EFI Operations: S3050 Panel 21 tripped upon restoration see 1896602. See 1896617, 1896618, 1896621, 1896245, 1896602, (1896231 withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN35800:PA19 | ZN35800:PA19 | ZN35800/000019 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2021-12-20 | N | 155.6051 | N | 8 | N | N | 1.1101 | 39.4971 | 62200.2623
[7 empty] | 974 | 11918 | 1894953 | 2021-12-19 15:38 | 2021-12-20 20:52 | 1754 | 11kV | 1905154 | 1740 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Section of 11kV Feeder Panel 7 Harbord ZN - INTELLIRUPTOR 63175 GRIFFIN ADAM - tripped and locked out: OC trip 11kV Conductors clashed at corner of Molong St & Soniver Rd. STORM See 1897286, 89, 90, 91, 92, 93, 94, 95, 96 - records withdrawn 1894953, 1894989, 1896554, 1895875, 1896252, 1896254, 1896256 | December | 2021 | 2022Q2 | 2022 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2021-12-19 | Y | 1094.9161 | N | 6 | N | Y | 1.1101 | 39.4971 | 1392230.3507
[7 empty] | 1131 | 14309 | 1896108 | 2021-12-20 19:15 | 2021-12-20 22:00 | 165 | 11kV | 1320 | 8 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 212516 11kV isolated at LF3970 to allow repairs on 66kV abandoned fdr at pole GQ-71121 Excluded OMS 1896108 | December | 2021 | 2022Q2 | 2022 | 512:83733 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2021-12-20 | N | 165 | N | 8 | N | N | 1.1101 | 39.4971 | 964.6171
[7 empty] | 591 | 7477 | 1896337 | 2021-12-20 19:15 | 2021-12-20 22:00 | 165 | 11kV | 585 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 212517 B Phase DOLF : 31 Amp LF 74721 fuse replaced 2040hrs 11kV LA replaced PT 70466 also 10A DOLF Excluded OMS 1896337 | December | 2021 | 2022Q2 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2021-12-20 | N | 117 | N | 8 | N | N | 1.1101 | 39.4971 | 427.5007
[7 empty] | 20 | 241 | 1895974 | 2021-12-20 13:08 | 2021-12-20 22:10 | 542 | 11kV | 2710 | 5 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 212513 Emergency switching to replace faulty pole HW-20206. | December | 2021 | 2022Q2 | 2022 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2021-12-20 | N | 542 | N | 8 | N | N | 1.1101 | 39.4971 | 1980.3881
[7 empty] | 1353 | 16507 | 1896379 | 2021-12-19 19:00 | 2021-12-20 23:45 | 1725 | 11kV | 1725 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Previous Storm | Y | At PT11347 HUNTS GRETA 0.4 - ex Panel 8 ZN 12630 Peats Ridge Dop found centre phase HDO had fallen open. Check and re-inserted. Note: customer reported no power since 7pm 19.12. Others hav had power restored. clr access, no isolation See 1896586, 1896379 (withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2021-12-19 | Y | 1725 | N | 6 | N | Y | 1.1101 | 39.4971 | 1260.5791
[7 empty] | 1544 | 18910 | 1896491 | 2021-12-21 05:15 | 2021-12-21 06:57 | 102 | 11kV | 97966 | 974 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN15014 Mona Vale - 11kV Panel 22 tripped on: Relays: A & C phase OC Sigs: 11kV CB22 Open Field EFIs: S65962 Branch found on HV beyond S79180 - removed by Dop See 1897369, 1897371, 1896491 (withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Veg | 2021-12-21 | N | 100.5811 | N | 14 | N | N | 1.1101 | 39.4971 | 71590.6633
[7 empty] | 1321 | 16147 | 1896504 | 2021-12-21 06:35 | 2021-12-21 07:58 | 83 | 11kV | 83 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212534 A Phase DOLF : 16 Amp same property has 2 subs, wrong sub in oms Excluded oms 1896504 | December | 2021 | 2022Q2 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2021-12-21 | N | 83 | N | 14 | N | N | 1.1101 | 39.4971 | 60.654
[7 empty] | 1482 | 18319 | 1896626 | 2021-12-21 10:17 | 2021-12-21 11:28 | 71 | 11kV | 26519 | 376 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN80 chatswood - 11kV Panel 36 Burra Pyrl feeder tripped: Relays: Basler - 51N(E/F), 150TN (EFI), F/C Signals: 11kV trip Field EFIs: 47513, 4059 11kV UG cable fault - feeder isolated from S4059 to S32327 to S47852. See 1897418, 1897419, (1896626 withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN80:PA36 | ZN80:PA36 | ZN00080/000036 | WILLOUGHBY | UG | Not Veg | 2021-12-21 | N | 70.5293 | N | 14 | N | N | 1.1101 | 39.4971 | 19379.303
[7 empty] | 1030 | 13026 | 1895205 | 2021-12-21 09:45 | 2021-12-21 13:20 | 215 | 11kV | 24725 | 115 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Previous Storm | N | Section of 11kV Panel 2 NARRABEEN - 11kV isolated from LB 20399 to LB 24357 tee S74807 ILUKA AVE ELANORA Large tree branch on 11kV CCt and LV ABC between TH15615 and TH 15616. Isolated by Dop and repairs carried out by Ausgrid staff. | December | 2021 | 2022Q2 | 2022 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2021-12-21 | N | 215 | N | 14 | N | N | 1.1101 | 39.4971 | 18068.3007
[7 empty] | 960 | 11662 | 1896760 | 2021-12-21 14:00 | 2021-12-21 16:10 | 130 | 11kV | 2470 | 19 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 212525 Mains off insulators at pole FD-60120 Excluded OMS 1896760 | December | 2021 | 2022Q2 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2021-12-21 | N | 130 | N | 14 | N | N | 1.1101 | 39.4971 | 1805.0031
[7 empty] | 1668 | 20291 | 1894934 | 2021-12-19 15:20 | 2021-12-21 16:52 | 2972 | 11kV | 535775.9833 | 229 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | At ZN15013 Terrehy Hills - 11kV Panel 6 'Cooyong Rd' feeder tripped: Relays: A & C phase OC and IOC, L/O, F/L, EFI Signals: 11kV trip STORM See 1897204, 1897214, 1897215, 1894947 | December | 2021 | 2022Q2 | 2022 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2021-12-19 | Y | 2339.6331 | N | 6 | N | Y | 1.1101 | 39.4971 | 391529.2859
[7 empty] | 274 | 3522 | 1896939 | 2021-12-21 15:48 | 2021-12-21 16:55 | 67 | 11kV | 5226 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | pt15306 elanora lumeah STORM DAMAGE ISOLATED BY 5P OPERATOR TO MAKE REPAIRS / REMOVE FALLEN TREES | December | 2021 | 2022Q2 | 2022 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2021-12-21 | N | 67 | N | 14 | N | N | 1.1101 | 39.4971 | 3819.0067
[7 empty] | 694 | 8915 | 1896823 | 2021-12-21 15:48 | 2021-12-21 16:55 | 67 | 11kV | 4087 | 61 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | PT 15485 COOLANGATTA AV ISOLATED BY 5P OPERATOR TO MAKE REPAIRS / REMOVE FALLEN TREES | December | 2021 | 2022Q2 | 2022 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2021-12-21 | N | 67 | N | 14 | N | N | 1.1101 | 39.4971 | 2986.6591
[7 empty] | 528 | 6270 | 1896829 | 2021-12-21 15:50 | 2021-12-21 17:08 | 78 | 11kV | 102058 | 1661 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2835 Burwood - Pnl.21 - tripped on Earth Fault UG cable fault between S3303 Sw/B, S2238 Sw/A and S77080 Sw/A See 1897698 1897698 1897699 | December | 2021 | 2022Q2 | 2022 | ZN2835:PA21 | ZN2835:PA21 | ZN02835/000021 | CANADA BAY | UG | Not Veg | 2021-12-21 | N | 61.4437 | N | 14 | N | N | 1.1101 | 39.4971 | 74580.9762
[7 empty] | 1433 | 17667 | 1896871 | 2021-12-21 15:13 | 2021-12-21 17:45 | 152 | 11kV | 19304 | 127 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 212527 No Fuses Blew LLC came loose | December | 2021 | 2022Q2 | 2022 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2021-12-21 | N | 152 | N | 14 | N | N | 1.1101 | 39.4971 | 14106.7938
[7 empty] | 676 | 8664 | 1896767 | 2021-12-21 13:41 | 2021-12-21 18:30 | 289 | 11kV | 7800 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | EX ZN 14891 WYONG, 11KV PANEL 12 - RECLOSER 45015 BRUSH CREEK tripped on: Relays: SEF, lockout Tree on OH mains just beyond PT 1355 Brush Creek Yarra 5.9 see 1897416, 17 , (1896767, 1896876 withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2021-12-21 | N | 136.8421 | N | 14 | N | N | 1.1101 | 39.4971 | 5700.0099
[7 empty] | 477 | 5805 | 1896877 | 2021-12-21 17:45 | 2021-12-21 19:11 | 86 | 11kV | 860 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 212526 3 phase No protection operations. Stranded conductors at pole GW-40236 repaired under A/P | December | 2021 | 2022Q2 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2021-12-21 | N | 86 | N | 14 | N | N | 1.1101 | 39.4971 | 628.4626
[7 empty] | 693 | 8891 | 1894944 | 2021-12-19 15:35 | 2021-12-21 20:19 | 3164.3167 | 11kV | 237323.75 | 75 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | S46588 Ferguson Woodlands - Dist.1 and Dist.2 Supply interrupted due to tree / branches on OH - report of multiple bays of OH down - STORM 1894944 (withdrawn) - rolled up to panel in error | December | 2021 | 2022Q2 | 2022 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Veg | 2021-12-19 | Y | 3164.3167 | N | 6 | N | Y | 1.1101 | 39.4971 | 173429.1966
[7 empty] | 1171 | 14675 | 1895139 | 2021-12-19 15:35 | 2021-12-21 21:00 | 3205 | 11kV | 1694975 | 575 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | ZN 15002 Narrabeen - 11kV Panel 4 'Collaroy Feeder' tripped on: Relays: E/F, C phase OC, L/O timer, F/L, EFI, Tx2 FC flag Signals: 11kV trip, ZE STORM - 11kV feeder trip and major damage to all low voltage. Entered into OMS as individual substations with individual outage durations. See PANEL 4 - 1897654, 1897658, 1897660, 1897661, 1897662, 1897663, 1897664 | December | 2021 | 2022Q2 | 2022 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Veg | 2021-12-19 | Y | 2947.7826 | N | 6 | N | Y | 1.1101 | 39.4971 | 1238637.7367
[7 empty] | 439 | 5440 | 1896927 | 2021-12-21 21:09 | 2021-12-21 22:15 | 66 | 11kV | 396 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212531 A & B Phase DOLF : 10 Amp excluded OMS 1896927; 1896928 | December | 2021 | 2022Q2 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-12-21 | N | 66 | N | 14 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 32 | 412 | 1896795 | 2021-12-21 15:11 | 2021-12-21 22:28 | 436.9 | 11kV | 18786.7 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212528 C Phase DOLF : 31 Amp Excluded OMS 1896799 | December | 2021 | 2022Q2 | 2022 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Veg | 2021-12-21 | N | 436.9 | N | 14 | N | N | 1.1101 | 39.4971 | 13728.7662
[7 empty] | 815 | 10111 | 1896964 | 2021-12-21 22:41 | 2021-12-22 00:12 | 91 | 11kV | 110697 | 1314 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 14892 Charmhaven - 11kV Panel 14 feeder tripped on: Relays: Earth Fault, Fault check, prohibition relay. On TX 2 Prot Pnl: Earth Fault check relay Signals: Field EFIs: 18599, 18600 ABNORMAL SWITCHING: Sw/B closed at S63909 Colorado Menindee. Panel 6 open at Charmhaven. Sw/A Open at S14807 Colorado Timbara. 11kV UG fault from Sw/B at S18600 Northlakes Pacific to Sw/B at S14932 Marsden Nelmes to Sw/B at S14548 Callan Kirrajong. see 1897552, 1897553, 1897554, 1896956 | December | 2021 | 2022Q2 | 2022 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | UG | Not Veg | 2021-12-21 | N | 84.2443 | N | 14 | N | N | 1.1101 | 39.4971 | 80894.1026
[7 empty] | 367 | 4920 | 1897055 | 2021-12-22 09:02 | 2021-12-22 09:49 | 47.5833 | 11kV | 47.5833 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S64756 Botany High No.2 - 11kV CB tripped on Earth Fault Possible UG cable fault or fault on customer's MSB | December | 2021 | 2022Q2 | 2022 |  |  |  | RANDWICK | UG | Not Veg | 2021-12-22 | N | 47.5833 | N | 12 | N | N | 1.1101 | 39.4971 | 34.7725
[7 empty] | 804 | 10017 | 1895360 | 2021-12-19 19:02 | 2021-12-22 11:00 | 3838 | 11kV | 58088 | 63 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | EX ZN 12630 Peats Ridge Panel 8 'Kulnura' - Recloser 44994 Mangrove Creek tripped: on O/C 4 bays of 11kV down beyond LB 44211, PT 14121 restored via generator. See 1897530, 1897533, (withdrawn 1895360, 1895874) | December | 2021 | 2022Q2 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2021-12-19 | Y | 922.0317 | N | 6 | N | Y | 1.1101 | 39.4971 | 42448.9971
[7 empty] | 1648 | 20054 | 1897166 | 2021-12-22 11:58 | 2021-12-22 12:29 | 31 | 11kV | 31 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 212535 B Phase DOLF : 40 Amp Fuse Fatigue Excluded OMS 1897166 | December | 2021 | 2022Q2 | 2022 | 224:80332 | 224:80332 | ZN00224/080332 | LAKE MACQUARIE | OH | Not Veg | 2021-12-22 | N | 31 | N | 12 | N | N | 1.1101 | 39.4971 | 22.6539
[7 empty] | 1326 | 16184 | 1897012 | 2021-12-22 06:56 | 2021-12-22 13:10 | 374 | 11kV | 23112 | 139 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212533 1 fault operation A & B Phases Overcurrent A-B Phase O/C 850A Wire off pin at pole AJ-20543. Excluded OMS 1897012 | December | 2021 | 2022Q2 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2021-12-22 | N | 166.2734 | N | 12 | N | N | 1.1101 | 39.4971 | 16889.5679
[7 empty] | 49 | 627 | 1897355 | 2021-12-22 14:52 | 2021-12-22 16:33 | 101 | 11kV | 101 | 1 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT1974 NP & WS MT COLAH - 11kV Middle and East side HDOs blown Bird on mains | December | 2021 | 2022Q2 | 2022 |  |  |  | HORNSBY | OH | Not Veg | 2021-12-22 | N | 101 | N | 12 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 360 | 4906 | 1897272 | 2021-12-22 13:20 | 2021-12-22 16:45 | 205 | 11kV | 28621 | 242 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2466 Flemington - Pnl.1 tripped on: IOC UG cable fault See 1897687 1897688 | December | 2021 | 2022Q2 | 2022 | ZN2466:PA1 | ZN2466:PA1 | ZN02466/000001 | PARRAMATTA | UG | Not Veg | 2021-12-22 | N | 118.2686 | N | 12 | N | N | 1.1101 | 39.4971 | 20915.3826
[7 empty] | 744 | 9396 | 1895042 | 2021-12-20 16:07 | 2021-12-22 16:48 | 2921.3833 | 11kV | 245396.2 | 84 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | S46739 Woorarra Elanora - Dist.1 and Dist.2 Interrupted by restricted operator to repair damaged LV OH and remove fallen trees. CC1: 23-"Mains Required" CC2: 22-"Refer to SOp" FRC1: 371-"Tree across Service Lines or Distributors - Unable to remove tree" FRC2: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | December | 2021 | 2022Q2 | 2022 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2021-12-20 | N | 2921.3833 | N | 8 | N | N | 1.1101 | 39.4971 | 179328.305
[7 empty] | 1650 | 20068 | 1897531 | 2021-12-22 17:02 | 2021-12-22 17:28 | 26 | 11kV | 182 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212547 A & B Phase DOLF : 20 Amp | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-12-22 | N | 26 | N | 12 | N | N | 1.1101 | 39.4971 | 133.0002
[7 empty] | 755 | 9503 | 1897421 | 2021-12-22 16:01 | 2021-12-22 17:45 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212548 A Phase DOLF : 10 Amp Excluded OMS 1897421 Note: customers also impacted by concurrent wider area outage refer to 1897531 | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-12-22 | N | 104 | N | 12 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 798 | 9970 | 1897422 | 2021-12-22 16:02 | 2021-12-22 17:55 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212549 A Phase DOLF : 10 Amp Note: customer also affected by Trip and Reclose refer to OMS 1897531 Excluded OMS 1897422 | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-12-22 | N | 113 | N | 12 | N | N | 1.1101 | 39.4971 | 82.5771
[7 empty] | 1113 | 14077 | 1897547 | 2021-12-22 17:35 | 2021-12-22 18:57 | 82 | 11kV | 3362 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212544 2 quick fault operations of SW 32514 seem to have initiated this trip see LID 212543 Excluded OMS 1897456 | December | 2021 | 2022Q2 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2021-12-22 | N | 82 | N | 12 | N | N | 1.1101 | 39.4971 | 2456.8504
[7 empty] | 224 | 2736 | 1897563 | 2021-12-22 19:45 | 2021-12-22 20:40 | 55 | 11kV | 495 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212550 low 11kV OHM - 4.4m. | December | 2021 | 2022Q2 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2021-12-22 | N | 55 | N | 12 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 1186 | 14773 | 1897472 | 2021-12-22 20:28 | 2021-12-22 23:33 | 185 | 11kV | 370 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | ## 1ph 10A dolf defective surge arrestor. Nil LID DQ excluded OMS 1897472 | December | 2021 | 2022Q2 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2021-12-22 | N | 185 | N | 12 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 1277 | 15578 | 1897479 | 2021-12-23 00:04 | 2021-12-23 02:00 | 116 | 11kV | 696 | 6 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | PT14507 Arundel Melina - Roadside and Middle phase HDOs blown Bark found across 11kV bushings at PT | December | 2021 | 2022Q2 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-12-23 | N | 116 | N | 14 | N | N | 1.1101 | 39.4971 | 508.6163
[7 empty] | 64 | 813 | 1897560 | 2021-12-23 08:53 | 2021-12-23 10:05 | 72 | 11kV | 140436 | 2013 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn398 Dulwich Hill - Pnl.30 tripped on: B phase OC and Earth Fault UG cable fault in front line section of feeder | December | 2021 | 2022Q2 | 2022 | ZN398:PA30 | ZN398:PA30 | ZN00398/000030 | INNER WEST | UG | Not Veg | 2021-12-23 | N | 69.7645 | N | 14 | N | N | 1.1101 | 39.4971 | 102626.4866
[7 empty] | 270 | 3488 | 1897487 | 2021-12-23 05:39 | 2021-12-23 11:35 | 356 | 11kV | 2848 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | PT12077 Chittaway Peach 0.6 - Middle phase HDO blown Fuse fatigue | December | 2021 | 2022Q2 | 2022 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2021-12-23 | N | 356 | N | 14 | N | N | 1.1101 | 39.4971 | 2081.2344
[7 empty] | 841 | 10377 | 1897696 | 2021-12-23 11:15 | 2021-12-23 13:43 | 148 | 11kV | 296 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212562 A Phase DOLF : 10 Amp Excluded OMS 189769600 | December | 2021 | 2022Q2 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2021-12-23 | N | 148 | N | 14 | N | N | 1.1101 | 39.4971 | 216.3081
[7 empty] | 1600 | 19497 | 1898039 | 2021-12-23 13:25 | 2021-12-23 15:33 | 128 | 11kV | 21243 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Rec44946 Kumarra Rd tripped on OC Multiple tree branches on OH mains See 1899451 1899452 | December | 2021 | 2022Q2 | 2022 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2021-12-23 | N | 127.9699 | N | 14 | N | N | 1.1101 | 39.4971 | 15523.7578
[7 empty] | 210 | 2611 | 1898017 | 2021-12-23 13:02 | 2021-12-23 16:05 | 183 | 11kV | 1281 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 212565 B Phase DOLF : 10 Amp Exclided OMS 1898017 | December | 2021 | 2022Q2 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2021-12-23 | N | 183 | N | 14 | N | N | 1.1101 | 39.4971 | 936.117
[7 empty] | 118 | 1479 | 1898260 | 2021-12-23 14:08 | 2021-12-23 16:17 | 129 | 11kV | 134676 | 1044 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn14144 Wamberal - Pnl.7 tripped on B & C phase IOC Tree on OH mains adj AB44979 | December | 2021 | 2022Q2 | 2022 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2021-12-23 | N | 129 | N | 14 | N | N | 1.1101 | 39.4971 | 98417.2485
[7 empty] | 627 | 8057 | 1897439 | 2021-12-22 16:24 | 2021-12-23 16:55 | 1471 | 11kV | 87769 | 293 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 212539 and LID 212564 1 fault operation PT 53359 failed in service Transformer replaced Excluded OMS 1897439 | December | 2021 | 2022Q2 | 2022 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2021-12-22 | N | 299.5529 | N | 12 | N | N | 1.1101 | 39.4971 | 64138.9965
[7 empty] | 1450 | 17872 | 1898030 | 2021-12-23 17:10 | 2021-12-23 18:15 | 65 | 11kV | 15600 | 240 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 212567 Tree branch on HV & LV mains pole GS-61318 Excluded OMS 1898030 | December | 2021 | 2022Q2 | 2022 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2021-12-23 | N | 65 | N | 14 | N | N | 1.1101 | 39.4971 | 11400.0199
[7 empty] | 1196 | 14818 | 1898038 | 2021-12-23 13:20 | 2021-12-23 20:05 | 405 | 11kV | 10530 | 38 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 212568 A Phase burnt off 11kV tapping pole IQ-11596 Excluded oms 1898038 | December | 2021 | 2022Q2 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2021-12-23 | N | 277.1053 | N | 14 | N | N | 1.1101 | 39.4971 | 7695.0134
[7 empty] | 1429 | 17615 | 1898560 | 2021-12-23 17:56 | 2021-12-23 21:07 | 191.4667 | 11kV | 2680.5333 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 212572 Single phase DOLF : 10 Amp Operator said feeder patrolled as well as possible could not find cause. | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-23 | N | 191.4667 | N | 14 | N | N | 1.1101 | 39.4971 | 1958.8547
[7 empty] | 1165 | 14631 | 1898516 | 2021-12-23 15:31 | 2021-12-23 21:18 | 347 | 11kV | 184996 | 1184 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 212569 1 fault operation 3 phase Instantaneous overcurrent 11kV ohm down between poles FT-33309 & FT-33321 HV into LV, EMSO CHECKS DONE Excluded OMS 1898516 | December | 2021 | 2022Q2 | 2022 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2021-12-23 | N | 156.2466 | N | 14 | N | N | 1.1101 | 39.4971 | 135189.6203
[7 empty] | 867 | 10781 | 1898502 | 2021-12-23 14:52 | 2021-12-24 03:35 | 763 | 11kV | 5656 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 212571 Earth Fault 11kV not 33kV as reported off pole at 11kV links 6L823. Also tx failed at sub 71931. Excluded OMS 1898502 | December | 2021 | 2022Q2 | 2022 | 514:18141 | 514:18141 | ZN00514/018141 | SINGLETON | OH | Not Veg | 2021-12-23 | N | 628.4444 | N | 14 | N | N | 1.1101 | 39.4971 | 4133.238
[7 empty] | 724 | 9263 | 1898005 | 2021-12-23 12:56 | 2021-12-24 09:40 | 1244 | 11kV | 5706 | 47 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 212563 A & C Phase DOLF : 16 Amp LF 40617 A-C DOLF 16A Sub 53172 TX Replaced Excluded OMS 1898005 | December | 2021 | 2022Q2 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2021-12-23 | N | 121.4043 | N | 14 | N | N | 1.1101 | 39.4971 | 4169.7765
[7 empty] | 1410 | 17357 | 1898545 | 2021-12-23 20:05 | 2021-12-24 15:50 | 1185 | 11kV | 5925 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | PT18473 Yarramalong Stinson 0.7 - Interupted from LB41096 to USL43925 to repair broken cross arm | December | 2021 | 2022Q2 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2021-12-23 | N | 1185 | N | 14 | N | N | 1.1101 | 39.4971 | 4329.8152
[7 empty] | 1680 | 20417 | 1898656 | 2021-12-24 09:31 | 2021-12-24 17:15 | 464 | 11kV | 928 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212578 B & C Phase found LF 64390 dropped. B & C phase. Should have fuses links in it. It had 10A fuses in. No fuses Links, replaced with 20A A phase DOLF Sub 51126 out. 10A | December | 2021 | 2022Q2 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2021-12-24 | N | 464 | N | 6 | N | N | 1.1101 | 39.4971 | 678.155
[7 empty] | 1626 | 19700 | 1898765 | 2021-12-24 19:16 | 2021-12-24 20:24 | 68 | 11kV | 93137 | 1573 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville - Pnl.17 tripped on C phase OC UG cable fault between S49663 Sw/B and S2306 Sw/A See 1899545 1899546 | December | 2021 | 2022Q2 | 2022 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2021-12-24 | N | 59.2098 | N | 6 | N | N | 1.1101 | 39.4971 | 68061.7725
[7 empty] | 886 | 10899 | 1898718 | 2021-12-24 14:39 | 2021-12-24 21:20 | 401 | 11kV | 41148.4833 | 575 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.36 tripped on: Earth Fault UG cable fault between S5391 Sw/B and S3770 Sw/D See 1899542 1899543 | December | 2021 | 2022Q2 | 2022 | ZN2835:PA36 | ZN2835:PA36 | ZN02835/000036 | STRATHFIELD | UG | Not Veg | 2021-12-24 | N | 71.5626 | N | 6 | N | N | 1.1101 | 39.4971 | 30070.0979
[7 empty] | 706 | 9124 | 1898770 | 2021-12-24 19:39 | 2021-12-24 21:35 | 116 | 11kV | 232 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212579 C Phase DOLF : 10 Amp Excluded OMS 1898770 been out for a week from previous storm. | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-12-24 | N | 116 | N | 6 | N | N | 1.1101 | 39.4971 | 169.5388
[7 empty] | 576 | 7247 | 1898779 | 2021-12-24 22:15 | 2021-12-25 00:10 | 115 | 11kV | 233697 | 2242 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.3 tripped on: ABC Phase IOC Possum caused flashover on LB61276 Abnormal: S17132 Sw/B Closed with USL22338 open See 1899539 1899540 | December | 2021 | 2022Q2 | 2022 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2021-12-24 | N | 104.236 | N | 6 | N | N | 1.1101 | 39.4971 | 170778.8747
[7 empty] | 899 | 11075 | 1898791 | 2021-12-24 23:48 | 2021-12-25 01:00 | 72.2833 | 11kV | 3975.5833 | 55 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212581 C Phase DOLF : 31 Amp Possum across A phase arrestor removed A phase 31a DOLF sub 8378 | December | 2021 | 2022Q2 | 2022 | 261:81886 | 261:81886 | ZN00261/081886 | NEWCASTLE | OH | Not Veg | 2021-12-24 | N | 72.2833 | N | 6 | N | N | 1.1101 | 39.4971 | 2905.239
[7 empty] | 781 | 9841 | 1898801 | 2021-12-25 01:15 | 2021-12-25 01:45 | 30 | 11kV | 27960 | 932 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212583 2 fault operations A & C Phases Overcurrent Possum at pole SW30141 | December | 2021 | 2022Q2 | 2022 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2021-12-25 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 20432.3433
[7 empty] | 278 | 3583 | 1898821 | 2021-12-25 07:01 | 2021-12-25 11:30 | 269 | 11kV | 269 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212586 A Phase DOLF : 10 Amp Excluded OMS 1898821 | December | 2021 | 2022Q2 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2021-12-25 | N | 269 | N | 4 | N | N | 1.1101 | 39.4971 | 196.5773
[7 empty] | 250 | 3074 | 1898870 | 2021-12-25 17:12 | 2021-12-25 18:25 | 73.2 | 11kV | 32854.2 | 1262 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC46117 Blaclava Vimiera - tripped on: OC Branch on 11kV outside 26 Vimiera Rd | December | 2021 | 2022Q2 | 2022 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | PARRAMATTA | OH | Veg | 2021-12-25 | N | 26.0334 | N | 4 | N | N | 1.1101 | 39.4971 | 24008.8803
[7 empty] | 1166 | 14634 | 1898896 | 2021-12-25 21:39 | 2021-12-25 22:50 | 70.5833 | 11kV | 105451.5 | 1494 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | 11kV Bond burnt off UGOH below S.18775 | December | 2021 | 2022Q2 | 2022 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2021-12-25 | N | 70.5833 | N | 4 | N | N | 1.1101 | 39.4971 | 77060.8459
[7 empty] | 375 | 4970 | 1898987 | 2021-12-26 18:04 | 2021-12-26 18:43 | 39 | 11kV | 27963 | 717 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 212592 C Phase Appears 2 birds contacted the 11kV Excluded OMS 1898987 | December | 2021 | 2022Q2 | 2022 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2021-12-26 | N | 39 | N | 2 | N | N | 1.1101 | 39.4971 | 20434.5356
[7 empty] | 12 | 168 | 1899510 | 2021-12-26 22:23 | 2021-12-26 22:34 | 11 | 11kV | 4290 | 390 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Rain Light | N | Zn9245 Engadine - Pnl.9 tripped & reclosed Possum found at base of UGOH to S64804 | December | 2021 | 2022Q2 | 2022 | ZN9245:PA9 | ZN9245:PA9 | ZN09245/000009 | SUTHERLAND | OH | Not Veg | 2021-12-26 | N | 11 | N | 2 | N | N | 1.1101 | 39.4971 | 3135.0055
[7 empty] | 156 | 1861 | 1899026 | 2021-12-27 02:44 | 2021-12-27 04:08 | 84 | 11kV | 504 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | PT14507 Arundel Milina - Middle phase HDO blown Bark across surge arrestors and HV bushings | December | 2021 | 2022Q2 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2021-12-27 | N | 84 | N | 12 | N | N | 1.1101 | 39.4971 | 368.3083
[7 empty] | 999 | 12313 | 1899033 | 2021-12-27 06:20 | 2021-12-27 08:26 | 126 | 11kV | 172498 | 1436 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | REC45061 Chain Valley Bay Mulloway - tripped on earth fault UG cable fault between S18063 Sw/A and S18111 Sw/A See 1899496 1899498 1899499 | December | 2021 | 2022Q2 | 2022 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | UG | Not Veg | 2021-12-27 | N | 120.124 | N | 12 | N | N | 1.1101 | 39.4971 | 126056.4506
[7 empty] | 896 | 11034 | 1899037 | 2021-12-27 06:59 | 2021-12-27 08:30 | 91 | 11kV | 91 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212602 Single phase DOLF : 10 Amp Excluded OMS 1899037 | December | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-12-27 | N | 91 | N | 12 | N | N | 1.1101 | 39.4971 | 66.5001
[7 empty] | 509 | 6113 | 1899014 | 2021-12-27 00:12 | 2021-12-27 11:00 | 648 | 11kV | 138392 | 2051 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven - pnl.5 tripped, reclosed & locked out on: ABC O/C Abnormal: LB44170 Closed with S14807 Sw/A Open LB44111 Closed with S14932 and S14796 Open 11kV UGOH fault to S.18122 Olney Popran See 1899493 1899494 1899495 | December | 2021 | 2022Q2 | 2022 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2021-12-27 | N | 67.4754 | N | 12 | N | N | 1.1101 | 39.4971 | 101132.7917
[7 empty] | 1388 | 17025 | 1899084 | 2021-12-27 09:27 | 2021-12-27 11:50 | 143.15 | 11kV | 858.9 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LF 75178 C ph Blown 20A fuse replaced and supply restored 11:50AM. JMH | December | 2021 | 2022Q2 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2021-12-27 | N | 143.15 | N | 12 | N | N | 1.1101 | 39.4971 | 627.6588
[7 empty] | 110 | 1415 | 1899056 | 2021-12-27 09:44 | 2021-12-27 12:48 | 184 | 11kV | 552 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Blown C ph DOLF 10A supply restored.JMH | December | 2021 | 2022Q2 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2021-12-27 | N | 184 | N | 12 | N | N | 1.1101 | 39.4971 | 403.3853
[7 empty] | 41 | 453 | 1899055 | 2021-12-27 09:42 | 2021-12-27 13:00 | 198.3167 | 11kV | 991.5833 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LF 75167 replaced 20A supply restored. JMH | December | 2021 | 2022Q2 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2021-12-27 | N | 198.3167 | N | 12 | N | N | 1.1101 | 39.4971 | 724.6199
[7 empty] | 1262 | 15418 | 1899078 | 2021-12-27 11:51 | 2021-12-27 13:02 | 71 | 11kV | 60492 | 852 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn14144 Wamberal - Pnl.4 tripped, reclosed & locked out on B & C phase IOC Bark fell onto 11kV feeder @ PT12362 hastings Aspen | December | 2021 | 2022Q2 | 2022 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2021-12-27 | N | 71 | N | 12 | N | N | 1.1101 | 39.4971 | 44205.7694
[7 empty] | 1476 | 18226 | 1899100 | 2021-12-27 13:25 | 2021-12-27 14:15 | 50 | 11kV | 73848 | 1484 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn9700 Kirrawee - Pnl.24 tripped on: SEL Bond burnt off on C phase corner Waratah & Oak Rd See 1899485 1899486 | December | 2021 | 2022Q2 | 2022 | ZN9700:PA24 | ZN9700:PA24 | ZN09700/000024 | SUTHERLAND | OH | Not Veg | 2021-12-27 | N | 49.7628 | N | 12 | N | N | 1.1101 | 39.4971 | 53965.9403
[7 empty] | 759 | 9516 | 1899141 | 2021-12-27 16:16 | 2021-12-27 17:15 | 59 | 11kV | 19588 | 332 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 212604 2 fault operations Small tree branch across 11kV OHM adjacent pole GW-57036. | December | 2021 | 2022Q2 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2021-12-27 | N | 59 | N | 12 | N | N | 1.1101 | 39.4971 | 14314.3327
[7 empty] | 729 | 9307 | 1899168 | 2021-12-27 18:21 | 2021-12-27 20:00 | 99 | 11kV | 594 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 212606 B Phase DOLF : 10 Amp | December | 2021 | 2022Q2 | 2022 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2021-12-27 | N | 99 | N | 12 | N | N | 1.1101 | 39.4971 | 434.0777
[7 empty] | 1570 | 19200 | 1899071 | 2021-12-27 11:10 | 2021-12-27 21:05 | 595 | 11kV | 208076 | 1126 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - pnl.4 tripped, reclosed, tripped on: A & C phase IOC OH mains down outside 212 New Line Rd near Hastings Rd, Dural. HV into LV mains - EMSO checked customer installations See 1899464 1899465 1899466 1899467 1899468 | December | 2021 | 2022Q2 | 2022 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Veg | 2021-12-27 | N | 184.7922 | N | 12 | N | N | 1.1101 | 39.4971 | 152055.8036
[7 empty] | 244 | 2990 | 1899213 | 2021-12-28 03:15 | 2021-12-28 04:38 | 83 | 11kV | 33283 | 401 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 212608 2 fault operations B & C Phases Overcurrent Branch on Fdr near ABS 22080 | December | 2021 | 2022Q2 | 2022 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2021-12-28 | N | 83 | N | 5 | N | N | 1.1101 | 39.4971 | 24322.2347
[7 empty] | 1675 | 20375 | 1899216 | 2021-12-28 04:41 | 2021-12-28 06:10 | 89 | 11kV | 163127 | 2727 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn80 Chatswood - Pnl.40 tripped on: Earth Fault UG cable fault between S.3268 Sw/B and S2935 Sw/A See 1899431 1899432 1899433 | December | 2021 | 2022Q2 | 2022 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | UG | Not Veg | 2021-12-28 | N | 59.8192 | N | 5 | N | N | 1.1101 | 39.4971 | 119208.4002
[7 empty] | 1574 | 19263 | 1899234 | 2021-12-28 08:23 | 2021-12-28 12:05 | 222 | 11kV | 444 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212610 A Phase DOLF : 10 Amp Excluded OMS 1899234 | December | 2021 | 2022Q2 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2021-12-28 | N | 222 | N | 5 | N | N | 1.1101 | 39.4971 | 324.4621
[7 empty] | 31 | 394 | 1899310 | 2021-12-28 20:06 | 2021-12-28 21:35 | 88.8333 | 11kV | 355.3333 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 212611 Overhead Mains off pin insulator Excluded OMS 1899310 | December | 2021 | 2022Q2 | 2022 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2021-12-28 | N | 88.8333 | N | 5 | N | N | 1.1101 | 39.4971 | 259.6671
[7 empty] | 178 | 2344 | 1899361 | 2021-12-28 21:17 | 2021-12-29 00:35 | 198 | 11kV | 198 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 212612 Single phase DOLF : 10 Amp excluded OMS 1899361 | December | 2021 | 2022Q2 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2021-12-28 | N | 198 | N | 5 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 893 | 11006 | 1899371 | 2021-12-29 04:14 | 2021-12-29 05:29 | 75 | 11kV | 90000 | 1200 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Pnl.1 Empire Bay - AB44614 11kV bond burnt off | December | 2021 | 2022Q2 | 2022 | ZN36200:PA1 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2021-12-29 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 65769.3454
[7 empty] | 186 | 2419 | 1899449 | 2021-12-29 11:25 | 2021-12-29 13:10 | 105 | 11kV | 1260 | 12 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 212614 LV fuses burning up at sub 73110 excluded OMS 1899449 | December | 2021 | 2022Q2 | 2022 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2021-12-29 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 182 | 2401 | 1899447 | 2021-12-29 11:21 | 2021-12-29 13:20 | 119 | 11kV | 238 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 212615 C Phase DOLF : 3 Amp Excluded OMS 1899447 | December | 2021 | 2022Q2 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2021-12-29 | N | 119 | N | 4 | N | N | 1.1101 | 39.4971 | 173.9234
[7 empty] | 1237 | 15133 | 1899570 | 2021-12-29 20:05 | 2021-12-29 22:46 | 161 | 11kV | 36968 | 265 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Ex North Sydney Pnl.72 - @ S3187 Angelo Berry - 11kV CB, Tx No.1 & Tx No.2 ACB tripped UG cable fault between S3187 tee Tx No.1, to S65945 to S3691 See 1899635 1899636 | December | 2021 | 2022Q2 | 2022 | ZN35400:PA72 | ZN35400:PA72 | ZN35400/000072 | NORTH SYDNEY | UG | Not Veg | 2021-12-29 | N | 139.5019 | N | 4 | N | N | 1.1101 | 39.4971 | 27015.124
[7 empty] | 392 | 5129 | 1899597 | 2021-12-30 08:18 | 2021-12-30 11:33 | 195 | 11kV | 195 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 212616 B Phase Broken Live Line Clamp Excluded OMS 1899597 | December | 2021 | 2022Q2 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2021-12-30 | N | 195 | N | 3 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 346 | 4782 | 1899719 | 2021-12-30 17:14 | 2021-12-30 18:19 | 65 | 11kV | 115501 | 1792 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 8100 GREEN SQUARE - 11KV PANEL 38 'S252 GARDENERS RD NO 1' tripped on: Signals: 11kV trip, No 3 tx group earth Relays: A,B,C phase OC, EFI Field EFIs: 252, 779, 50420, 5800 UG Fault between S5800 Primrose Tweedmouth SW/A to S50429 SW/A to S2387 SW/D See 1900261, 1900262, (1899719 withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN8100:PA38 | ZN8100:PA38 | ZN08100/000038 | BAYSIDE | UG | Not Veg | 2021-12-30 | N | 64.4537 | N | 3 | N | N | 1.1101 | 39.4971 | 84404.7241
[7 empty] | 1376 | 16877 | 1899734 | 2021-12-30 19:19 | 2021-12-30 21:09 | 110 | 11kV | 96670 | 923 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 965 Pennant Hills Zn - 11kV Panel 26 'Victoria Wilson' feeder tripped on: Relays: 'B' phase OV timed, LO, EFI Signals: 11kV trip, Tx3 GE Field EFIs: S6153 11kV feeder fault from ZN965 Pennant Hills Panel 26 to S 6153 Victoria Wilson. See 1900249, 51, 52, 53, (1899734 withdrawn) | December | 2021 | 2022Q2 | 2022 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2021-12-30 | N | 104.7346 | N | 3 | N | N | 1.1101 | 39.4971 | 70643.5847
[7 empty] | 1589 | 19387 | 1899763 | 2021-12-31 06:54 | 2021-12-31 07:22 | 28 | 11kV | 18849 | 705 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC62731 Narara Creek Manns - tripped on OC Cockatoo on 11kV adj PT49023 See 1900277 1900278 | December | 2021 | 2022Q2 | 2022 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2021-12-31 | N | 26.7362 | N | 2 | N | N | 1.1101 | 39.4971 | 13774.2932
[7 empty] | 813 | 10082 | 1899874 | 2021-12-31 17:54 | 2021-12-31 21:50 | 236 | 11kV | 14455 | 139 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 212620 HV wires down at pole AJ-20529 Excluded 1899874 | December | 2021 | 2022Q2 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2021-12-31 | N | 103.9928 | N | 2 | N | N | 1.1101 | 39.4971 | 10563.2876
[7 empty] | 659 | 8508 | 1900016 | 2022-01-01 16:45 | 2022-01-01 17:42 | 57 | 11kV | 63555 | 1115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn9550 Gwawley Bay - Pnl.43 tripped on: A & B phase OC Cause not ascertained | January | 2022 | 2022Q3 | 2022 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Veg | 2022-01-01 | N | 57 | N | 1 | N | N | 1.1101 | 39.4971 | 46444.1194
[7 empty] | 1586 | 19368 | 1900043 | 2022-01-02 07:10 | 2022-01-02 08:00 | 50 | 11kV | 50 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 220005 B Phase DOLF : 10 Amp excluded OMS 1900043 | January | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2022-01-02 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 554 | 6789 | 1900056 | 2022-01-02 08:45 | 2022-01-02 09:34 | 49 | 11kV | 36946 | 754 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca - Pnl.24 - REC77908 Copacabana Korrabel tripped on: OC 11kV UGOH fault on pole AV00879 | January | 2022 | 2022Q3 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | Unknown | Unknown | 2022-01-02 | N | 49 | N | 5 | N | N | 1.1101 | 39.4971 | 26999.0471
[7 empty] | 583 | 7358 | 1900038 | 2022-01-02 06:45 | 2022-01-02 12:05 | 320 | 11kV | 11320 | 41 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 220006 no protection operations. ABS 41337 burning up. Customer voltage fluctuations reported beyond ABS 41425. Excluded OMS 1900042. | January | 2022 | 2022Q3 | 2022 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2022-01-02 | N | 276.0976 | N | 5 | N | N | 1.1101 | 39.4971 | 8272.3221
[7 empty] | 971 | 11847 | 1900134 | 2022-01-02 22:11 | 2022-01-02 22:34 | 23 | 11kV | 19977 | 1277 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn15005 Belrose - Pnl.6 tripped & reclosed on A & C phase OC @ REC24831 Lockwood Peakcock - CB tripped on IOC Possum on mains at REC24831 See 1900256 1900257 | January | 2022 | 2022Q3 | 2022 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2022-01-02 | N | 15.6437 | N | 5 | N | N | 1.1101 | 39.4971 | 14598.6024
[7 empty] | 1566 | 19168 | 1900151 | 2022-01-03 07:56 | 2022-01-03 08:39 | 43 | 11kV | 5934 | 138 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3425 Castle Cove - Pnl.32 tripped on Earth Fault UG cable fault in front line section of feeder | January | 2022 | 2022Q3 | 2022 | ZN3425:PA32 | ZN3425:PA32 | ZN03425/000032 | WILLOUGHBY | UG | Not Veg | 2022-01-03 | N | 43 | N | 1 | N | N | 1.1101 | 39.4971 | 4336.3922
[7 empty] | 648 | 8407 | 1900133 | 2022-01-02 21:57 | 2022-01-03 12:00 | 843 | 11kV | 10453 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220007 3 phase Sensitive Earth Fault Excluded OMS 1900138 | January | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2022-01-02 | N | 193.5741 | N | 5 | N | N | 1.1101 | 39.4971 | 7638.7441
[7 empty] | 52 | 639 | 1900250 | 2022-01-04 08:27 | 2022-01-04 11:15 | 168 | 11kV | 1680 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT13883 Peats Ridge Karee 0.4 - Centre phase HDO blown Possible fuse fatigue | January | 2022 | 2022Q3 | 2022 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2022-01-04 | N | 168 | N | 4 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 1572 | 19228 | 1900302 | 2022-01-04 11:02 | 2022-01-04 12:30 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220013 Single phase DOLF : 10 Amp Excluded OMS 1900302 | January | 2022 | 2022Q3 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2022-01-04 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 507 | 6031 | 1900326 | 2022-01-04 12:08 | 2022-01-04 13:15 | 67 | 11kV | 79569 | 1305 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.23 tripped on: Earth Fault UG cable fault between S5064 Sw/B, S5651 Sw/A and S4488 Sw/A See 1900716 1900717 | January | 2022 | 2022Q3 | 2022 | ZN847:PA23 | ZN847:PA23 | ZN00847/000023 | HORNSBY | UG | Not Veg | 2022-01-04 | N | 60.9724 | N | 4 | N | N | 1.1101 | 39.4971 | 58146.6783
[7 empty] | 585 | 7382 | 1900397 | 2022-01-05 06:09 | 2022-01-05 07:13 | 63.5833 | 11kV | 44571.9167 | 701 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.21 tripped on: Earth Fault Tree bark on PT1887 Chapman Cardinal | January | 2022 | 2022Q3 | 2022 | ZN965:PA21 | ZN965:PA21 | ZN00965/000021 | HORNSBY | OH | Veg | 2022-01-05 | N | 63.5833 | N | 10 | N | N | 1.1101 | 39.4971 | 32571.8421
[7 empty] | 241 | 2958 | 1900402 | 2022-01-05 06:36 | 2022-01-05 08:15 | 99 | 11kV | 198 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220017 Single phase DOLF : 10 Amp Excluded OMS 1900402 | January | 2022 | 2022Q3 | 2022 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2022-01-05 | N | 99 | N | 10 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 277 | 3553 | 1900510 | 2022-01-05 13:46 | 2022-01-05 15:10 | 84 | 11kV | 84 | 1 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220023 C Phase DOLF : 10 Amp dead possum found at sub Excluded OMS1900510 | January | 2022 | 2022Q3 | 2022 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2022-01-05 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 61.3847
[7 empty] | 968 | 11791 | 1900233 | 2022-01-04 00:18 | 2022-01-05 16:15 | 2397 | 11kV | 185287 | 205 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC349 Berowra Waters tripped on SEF Abnormal: REC3227 Open DMA with bypass closed Tree brough down 3 bays of OH mains beyond AB2013 See 1900761 1900762 1900763 1900765 | January | 2022 | 2022Q3 | 2022 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2022-01-04 | N | 903.839 | N | 4 | N | N | 1.1101 | 39.4971 | 135402.2746
[7 empty] | 490 | 5957 | 1900528 | 2022-01-05 16:18 | 2022-01-05 17:50 | 92 | 11kV | 920 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220025 Single phase DOLF : 6 Amp TREE FELL THROUGH MAINS THEN FELL CLEAR. | January | 2022 | 2022Q3 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2022-01-05 | N | 92 | N | 10 | N | N | 1.1101 | 39.4971 | 672.3089
[7 empty] | 1146 | 14418 | 1900413 | 2022-01-05 07:55 | 2022-01-05 20:40 | 765 | 11kV | 197064 | 382 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 220021 pole fire OS-27018 Section isolated to replace pole. see reports 220019, 220020 Excluded oms 1900413 | January | 2022 | 2022Q3 | 2022 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2022-01-05 | N | 515.8743 | N | 10 | N | N | 1.1101 | 39.4971 | 144008.5588
[7 empty] | 499 | 5986 | 1900578 | 2022-01-05 20:23 | 2022-01-05 21:53 | 90 | 11kV | 256368 | 3012 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35600 Kingsford - Pnl.9 tripped on : Earth Fault UG cable fault between S2276 and S4743 See 1900745 1900746 | January | 2022 | 2022Q3 | 2022 | ZN35600:PA9 | ZN35600:PA9 | ZN35600/000009 | RANDWICK | UG | Not Veg | 2022-01-05 | N | 85.1155 | N | 10 | N | N | 1.1101 | 39.4971 | 187346.1728
[7 empty] | 403 | 5182 | 1900595 | 2022-01-05 22:45 | 2022-01-05 23:15 | 30 | 11kV | 61050 | 2035 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn262 Marrickville - Pnl.31 tripped on Earth Fault UG cable fault in frontline section of feeder See 1900750 1900751 | January | 2022 | 2022Q3 | 2022 | ZN262:PA31 | ZN262:PA31 | ZN00262/000031 | INNER WEST | UG | Not Veg | 2022-01-05 | N | 30 | N | 10 | N | N | 1.1101 | 39.4971 | 44613.5393
[7 empty] | 1299 | 15808 | 1900599 | 2022-01-05 23:05 | 2022-01-06 00:15 | 70 | 11kV | 560 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Light | N | Zn8700 City North - 61/62J tripped on : 61/62J Buchholz @ S1911 IBM Kent St: Signal received - Misc Protection Dop coldn't access S1911 (Confined Space) to check Misc Protection Possible Tx fault based on Bz signal at Zone. See 1900599 1900600 | January | 2022 | 2022Q3 | 2022 | ZN8700:PA61 62GHJ | ZN8700:PA61 62GHJ | ZN08700/61 62GHJ | SYDNEY | UG | Not Veg | 2022-01-05 | N | 70 | N | 10 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 1172 | 14697 | 1900589 | 2022-01-05 21:20 | 2022-01-06 01:02 | 222 | 11kV | 2664 | 12 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220026 Section isolate to replace 33kV crosarm | January | 2022 | 2022Q3 | 2022 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2022-01-05 | N | 222 | N | 10 | N | N | 1.1101 | 39.4971 | 1946.7726
[7 empty] | 1383 | 16963 | 1900603 | 2022-01-05 23:40 | 2022-01-06 02:21 | 161 | 11kV | 56644 | 370 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn35370 Galston - Pnl.2 tripped on: A & C phase OC Tree on OH mains near LB3092 See 1900993, 1900994 | January | 2022 | 2022Q3 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2022-01-05 | N | 153.0919 | N | 10 | N | N | 1.1101 | 39.4971 | 41393.7645
[7 empty] | 843 | 10414 | 1900611 | 2022-01-06 01:08 | 2022-01-06 08:09 | 421 | 11kV | 421 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 220029 Single phase DOLF : 10 Amp Excluded OMS 1900611 | January | 2022 | 2022Q3 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2022-01-06 | N | 421 | N | 8 | N | N | 1.1101 | 39.4971 | 307.6544
[7 empty] | 404 | 5186 | 1900700 | 2022-01-06 10:54 | 2022-01-06 12:07 | 73 | 11kV | 43438 | 616 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.6 tripped on B & C phase OC UG cable fault between S5723 Sw/B and S7865 Sw/A See 1900952 1900953 | January | 2022 | 2022Q3 | 2022 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-01-06 | N | 70.5162 | N | 8 | N | N | 1.1101 | 39.4971 | 31743.2092
[7 empty] | 770 | 9662 | 1900727 | 2022-01-06 12:27 | 2022-01-06 14:00 | 93 | 11kV | 54285 | 1495 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn80 Chatswood - Pnl.25 tripped on: A & B phase IOC Tree branch on OH mains, fault current has caused bond to burn off at pole GL36844 See 1900941 1900942 1900943 | January | 2022 | 2022Q3 | 2022 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2022-01-06 | N | 36.311 | N | 8 | N | N | 1.1101 | 39.4971 | 39669.8769
[7 empty] | 1052 | 13482 | 1900623 | 2022-01-06 05:49 | 2022-01-06 15:55 | 606 | 11kV | 114297 | 1262 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn12660 Woy Woy - Pnl.14 tripped on: C phase IOC & OC Abnormal: CP64362 Sw/B Open with USL32987 Open Vehicle hit pole See 1900935 19900936 | January | 2022 | 2022Q3 | 2022 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2022-01-06 | N | 90.5681 | N | 8 | N | N | 1.1101 | 39.4971 | 83524.8764
[7 empty] | 177 | 2315 | 1900838 | 2022-01-06 17:58 | 2022-01-06 19:40 | 102 | 11kV | 8766 | 1191 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind Strong | N | Zn1673 Turramurra - Pnl.18 tripped & reclosed on: B & C phase OC UGOH bond burnt off near LB238 See 1901000 1901001 | January | 2022 | 2022Q3 | 2022 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | Unknown | Unknown | 2022-01-06 | N | 7.3602 | N | 8 | N | N | 1.1101 | 39.4971 | 6405.9342
[7 empty] | 1457 | 17960 | 1900796 | 2022-01-06 16:04 | 2022-01-06 20:13 | 249 | 11kV | 498 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220032 Single phase DOLF : 10 Amp Note: customers also affected by wider area outage refer to OMS 1902029 Excluded OMS 1900796 | January | 2022 | 2022Q3 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2022-01-06 | N | 249 | N | 8 | N | N | 1.1101 | 39.4971 | 363.9237
[7 empty] | 77 | 961 | 1900867 | 2022-01-06 19:16 | 2022-01-06 22:25 | 189 | 11kV | 4347 | 23 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 220034 interrupt to repair broken tapping at ABS 61474 Excluded oms 1900867 | January | 2022 | 2022Q3 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2022-01-06 | N | 189 | N | 8 | N | N | 1.1101 | 39.4971 | 3176.6594
[7 empty] | 1021 | 12902 | 1900665 | 2022-01-06 17:15 | 2022-01-07 01:25 | 490 | 11kV | 15943 | 139 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220031 feeder tripped from wires down pole AJ-20532 to AJ-20530 | January | 2022 | 2022Q3 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2022-01-06 | N | 114.6978 | N | 8 | N | N | 1.1101 | 39.4971 | 11650.6742
[7 empty] | 964 | 11713 | 1900895 | 2022-01-07 00:45 | 2022-01-07 02:08 | 83 | 11kV | 2324 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220035 A Phase DOLF : 31 Amp | January | 2022 | 2022Q3 | 2022 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Veg | 2022-01-07 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 1698.3107
[7 empty] | 1503 | 18479 | 1900992 | 2022-01-07 09:30 | 2022-01-07 17:30 | 480 | 11kV | 480 | 1 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220037 No protection operation, 11kV OHM on ground at pole MG-37025, suspected thieves trying to steal OHM, repairs completed Excluded OMS 1900992 | January | 2022 | 2022Q3 | 2022 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2022-01-07 | N | 480 | N | 4 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 1034 | 13080 | 1901111 | 2022-01-07 17:51 | 2022-01-07 20:35 | 164 | 11kV | 64794 | 1181 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn80 Chatswood - Pnl.31 tripped on: A & C phase OC & IOC Abnormal: S750 Sw/D Closed with S31787 Sw/B Open (DMA open bond) Tree damaged OH mains outside 57 Coolaroo See 1902330 1902331 | January | 2022 | 2022Q3 | 2022 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2022-01-07 | N | 54.8637 | N | 4 | N | N | 1.1101 | 39.4971 | 47349.5441
[7 empty] | 956 | 11591 | 1901077 | 2022-01-07 16:09 | 2022-01-07 22:20 | 371 | 11kV | 148723 | 992 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn1193 Lindfield - Pnl.16 tripped on: Earth Fault Tree brought down OH mains near PT2037. HV into LV mains See 1902337 1902338 1902343 1920344 | January | 2022 | 2022Q3 | 2022 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Veg | 2022-01-07 | N | 149.9224 | N | 4 | N | N | 1.1101 | 39.4971 | 108682.3818
[7 empty] | 1064 | 13653 | 1901213 | 2022-01-08 00:40 | 2022-01-08 01:54 | 74 | 11kV | 56707 | 883 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn12690 Berkeley Vale - Pnl.7 tripped on B & C phase OC Weather related See 1902326 1902327 | January | 2022 | 2022Q3 | 2022 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2022-01-08 | N | 64.2208 | N | 7 | N | N | 1.1101 | 39.4971 | 41439.803
[7 empty] | 1115 | 14079 | 1901221 | 2022-01-08 01:12 | 2022-01-08 05:00 | 228 | 11kV | 15471 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220043 1 fault operation Bph DOLF blown at sub 51701 Taylor sub. Excluded OMS 1901221 | January | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-01-08 | N | 195.8354 | N | 7 | N | N | 1.1101 | 39.4971 | 11305.7505
[7 empty] | 272 | 3506 | 1901269 | 2022-01-08 09:01 | 2022-01-08 10:21 | 80 | 11kV | 32000 | 409 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | Zn3155 Double Bay - Pnl.39 tripped on Earth Fault UG cable fault between S35880 Sw/A and S8946 Sw/A and S35420 Sw/B See 1901789 1901790 | January | 2022 | 2022Q3 | 2022 | ZN3155:PA39 | ZN3155:PA39 | ZN03155/000039 | WOOLLAHRA | UG | Not Veg | 2022-01-08 | N | 78.2396 | N | 7 | N | N | 1.1101 | 39.4971 | 23384.6562
[7 empty] | 112 | 1432 | 1901274 | 2022-01-08 09:10 | 2022-01-08 12:15 | 185 | 11kV | 185 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 220048 B Phase DOLF : 10 Amp Faulty Lightning arrestor Excluded OMS 1901274 | January | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2022-01-08 | N | 185 | N | 7 | N | N | 1.1101 | 39.4971 | 135.1925
[7 empty] | 1118 | 14091 | 1901314 | 2022-01-08 11:40 | 2022-01-08 12:32 | 52 | 11kV | 17888 | 344 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220049 No protection operations. Loose cross arm brace strap pole SW-60261. Excluded OMS 1901314 | January | 2022 | 2022Q3 | 2022 | 222:33601 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2022-01-08 | N | 52 | N | 7 | N | N | 1.1101 | 39.4971 | 13072.0228
[7 empty] | 1075 | 13811 | 1901333 | 2022-01-08 13:27 | 2022-01-08 16:00 | 153 | 11kV | 612 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | S9618 Cawarra Namco - Tx 2 - B phase HV fuse blown Fuse failure | January | 2022 | 2022Q3 | 2022 | ZN9550:PA27 | ZN9550:PA27 | ZN09550/000027 | SUTHERLAND | OH | Not Veg | 2022-01-08 | N | 153 | N | 7 | N | N | 1.1101 | 39.4971 | 447.2315
[7 empty] | 806 | 10030 | 1901388 | 2022-01-08 17:37 | 2022-01-08 23:00 | 323 | 11kV | 73967 | 229 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 220051 tree damaged 11kV mains adjacent sub 65276 Excluded OMS 1901388 | January | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2022-01-08 | N | 323 | N | 7 | N | N | 1.1101 | 39.4971 | 54052.9019
[7 empty] | 970 | 11845 | 1901488 | 2022-01-09 05:58 | 2022-01-09 07:15 | 77 | 11kV | 20482 | 266 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC41845 North Erina tripped on O/C Tree on OH mains outside 181 Wattle Tree Rd | January | 2022 | 2022Q3 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2022-01-09 | N | 77 | N | 8 | N | N | 1.1101 | 39.4971 | 14967.6415
[7 empty] | 1280 | 15616 | 1901495 | 2022-01-09 07:15 | 2022-01-09 08:14 | 59 | 11kV | 83935 | 1549 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.29 tripped on Earth Fault UG cable fault between S48581 and S3364 See 1902219 1902220 | January | 2022 | 2022Q3 | 2022 | ZN2602:PA29 | ZN2602:PA29 | ZN02602/000029 | RANDWICK | UG | Not Veg | 2022-01-09 | N | 54.1866 | N | 8 | N | N | 1.1101 | 39.4971 | 61337.2223
[7 empty] | 218 | 2686 | 1901492 | 2022-01-09 06:41 | 2022-01-09 09:43 | 182 | 11kV | 5534 | 31 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 220061 2 fault operation A & C Phase Overcurrent Dead gallah removed from 11kv links 75064. | January | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2022-01-09 | N | 178.5161 | N | 8 | N | N | 1.1101 | 39.4971 | 4044.084
[7 empty] | 1303 | 15866 | 1901481 | 2022-01-09 02:28 | 2022-01-09 10:55 | 507 | 11kV | 2772 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 220060 2 X LF 78340 replaced section isloated for repair to network after tree on mains, x-arms repaired @ 9v-50031 & 9v-50033 power restored 1055. Excluded OMS No. 1901481 | January | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2022-01-09 | N | 462 | N | 8 | N | N | 1.1101 | 39.4971 | 2025.6958
[7 empty] | 1528 | 18750 | 1901477 | 2022-01-09 03:06 | 2022-01-09 12:15 | 549 | 11kV | 142725 | 265 | HV | 3rd Party Action | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 220056 MVA @ pole HW-77017. Excluded OMS No. 1901477 | January | 2022 | 2022Q3 | 2022 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2022-01-09 | N | 538.5849 | N | 8 | N | N | 1.1101 | 39.4971 | 104299.2203
[7 empty] | 1301 | 15838 | 1901504 | 2022-01-09 08:23 | 2022-01-09 12:30 | 247 | 11kV | 988 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220063 A & B Phase DOLF : 16 Amp Excluded OMS 1901504 | January | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-01-09 | N | 247 | N | 8 | N | N | 1.1101 | 39.4971 | 722.0013
[7 empty] | 1241 | 15155 | 1901527 | 2022-01-09 11:15 | 2022-01-09 12:45 | 89.55 | 11kV | 4208.85 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220062 B Phase DOLF : 31 Amp Excluded OMS 1901528 CC1: 22-"Refer to SOp" | January | 2022 | 2022Q3 | 2022 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Veg | 2022-01-09 | N | 89.55 | N | 8 | N | N | 1.1101 | 39.4971 | 3075.7034
[7 empty] | 822 | 10152 | 1901559 | 2022-01-09 15:25 | 2022-01-09 16:50 | 85 | 11kV | 34043 | 463 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Previous Storm | N | Zn7900 Campbell St - Pnl.15 tripped on Earth Fault UG cable fault in front line section of feeder | January | 2022 | 2022Q3 | 2022 | ZN7900:PA15 | ZN7900:PA15 | ZN07900/000015 | SYDNEY | UG | Not Veg | 2022-01-09 | N | 73.527 | N | 8 | N | N | 1.1101 | 39.4971 | 24877.6203
[7 empty] | 939 | 11351 | 1901602 | 2022-01-10 03:09 | 2022-01-10 05:49 | 160 | 11kV | 20596 | 132 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220069 1 fault operation 3 phase Overcurrent Excludedm OMS 1901602 | January | 2022 | 2022Q3 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2022-01-10 | N | 156.0303 | N | 3 | N | N | 1.1101 | 39.4971 | 15050.9493
[7 empty] | 324 | 4353 | 1901722 | 2022-01-10 11:08 | 2022-01-10 13:00 | 112 | 11kV | 69697 | 911 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.6 tripped, reclosed & tripped on: Earth Fault UGOH exploded at 173 Davies Rd on pole PE-16257 See 1902350 1902351 1902352 | January | 2022 | 2022Q3 | 2022 | ZN1287:PA6 | ZN1287:PA6 | ZN01287/000006 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2022-01-10 | N | 76.506 | N | 3 | N | N | 1.1101 | 39.4971 | 50932.5119
[7 empty] | 460 | 5675 | 1901802 | 2022-01-10 14:36 | 2022-01-10 19:10 | 274 | 11kV | 135216 | 1216 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220071 11kV fdr 33596 opened for safety, faulty section then isolated for repairs at pole SW-31419 Excluded OMS 1901783 | January | 2022 | 2022Q3 | 2022 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2022-01-10 | N | 111.1974 | N | 3 | N | N | 1.1101 | 39.4971 | 98811.8646
[7 empty] | 1667 | 20288 | 1901939 | 2022-01-11 10:04 | 2022-01-11 11:20 | 76 | 11kV | 228 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220077 Single phase DOLF : 10 Amp Excluded OMS 1901939 | January | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2022-01-11 | N | 76 | N | 11 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 580 | 7293 | 1901921 | 2022-01-11 09:21 | 2022-01-11 11:42 | 141 | 11kV | 90789 | 3559 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | At S15001 Beacon Hill Panel 10L tripped on RelaysL Earth Fault, EFI, Fault Check and SEF Cause: Surveyor Hammered Nail into 11kV Feeder between S16710 Frenchs Forest Hurdis SW/A to S16376 Skyline Place No.4 tee to S16389 Warringah Wakehurst SW/A See OMS 1902248 1902250 1902253 1901921 | January | 2022 | 2022Q3 | 2022 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | UG | Not Veg | 2022-01-11 | N | 25.5097 | N | 11 | N | N | 1.1101 | 39.4971 | 66345.9234
[7 empty] | 616 | 7926 | 1901906 | 2022-01-11 08:52 | 2022-01-11 16:20 | 448 | 11kV | 1344 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Hot >35C | N | LID 220078 Single phase DOLF : 10 Amp Blown L/A Excluded OMS 1901906 | January | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-01-11 | N | 448 | N | 11 | N | N | 1.1101 | 39.4971 | 982.1556
[7 empty] | 737 | 9370 | 1902017 | 2022-01-11 13:43 | 2022-01-11 17:50 | 247 | 11kV | 172165 | 1228 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn1290 Leightonfield 11kV Panel 3 tripped reclosed and loced out on Signals: 11kV Trip, earth fault, overcurrentr, SEL, EFI, Timing and Lockout Cause: HV mains down Cnr of Gurney and Campbell Hill Rd Chester Hill. Tree branch on HV. DOp reports HV may have fallen on house 3 Gurney Rd EMSO to check for damage See OMS 1902239 1902240 1902242 1902017 1902063 | January | 2022 | 2022Q3 | 2022 | ZN1290:PA3 | ZN1290:PA3 | ZN01290/000003 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-01-11 | N | 140.1995 | N | 11 | N | N | 1.1101 | 39.4971 | 125813.104
[7 empty] | 623 | 8015 | 1902073 | 2022-01-11 17:21 | 2022-01-11 18:17 | 56 | 11kV | 25979 | 845 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220085 A Phase Instantaneous Overcurrent Excluded OMS 1902073 | January | 2022 | 2022Q3 | 2022 | 801:74119 | 801:74119 | ZN00801/074119 | MUSWELLBROOK | OH | Veg | 2022-01-11 | N | 30.7444 | N | 11 | N | N | 1.1101 | 39.4971 | 18984.6869
[7 empty] | 861 | 10666 | 1902070 | 2022-01-11 17:14 | 2022-01-11 18:45 | 91 | 11kV | 2184 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220086 A & B Phase DOLF : 16 Amp excluded OMS 1902070 | January | 2022 | 2022Q3 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2022-01-11 | N | 91 | N | 11 | N | N | 1.1101 | 39.4971 | 1596.0028
[7 empty] | 431 | 5397 | 1902091 | 2022-01-11 18:32 | 2022-01-11 19:39 | 67 | 11kV | 64052 | 956 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP62730 Manns Narra Creek Tripped on Relay: O/C and Lockout Cause: Tree branch removed from 11kV Mains O/S 95 Deane St | January | 2022 | 2022Q3 | 2022 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2022-01-11 | N | 67 | N | 11 | N | N | 1.1101 | 39.4971 | 46807.3124
[7 empty] | 117 | 1453 | 1902074 | 2022-01-11 17:24 | 2022-01-11 20:45 | 201.2167 | 11kV | 3420.6833 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220088 A & C Phase DOLF | January | 2022 | 2022Q3 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2022-01-11 | N | 201.2167 | N | 11 | N | N | 1.1101 | 39.4971 | 2499.7345
[7 empty] | 317 | 4243 | 1902109 | 2022-01-11 20:08 | 2022-01-11 20:51 | 43 | 11kV | 86 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220087 A Phase DOLF : 10 Amp Excluded OMS 1902109 | January | 2022 | 2022Q3 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2022-01-11 | N | 43 | N | 11 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 716 | 9215 | 1902068 | 2022-01-11 17:09 | 2022-01-11 22:35 | 326 | 11kV | 1304 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220091 A Phase DOLF : 10 Amp Excluded OMS 1902068 | January | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-01-11 | N | 326 | N | 11 | N | N | 1.1101 | 39.4971 | 952.9247
[7 empty] | 1077 | 13819 | 1902096 | 2022-01-11 18:54 | 2022-01-11 23:55 | 301 | 11kV | 301 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220092 Single phase DOLF : 10 Amp Excluded OMS 1902096 | January | 2022 | 2022Q3 | 2022 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2022-01-11 | N | 301 | N | 11 | N | N | 1.1101 | 39.4971 | 219.9619
[7 empty] | 1019 | 12875 | 1902141 | 2022-01-12 07:20 | 2022-01-12 08:15 | 55 | 11kV | 110 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220098 single phase DOLF : 10 Amp Excluded OMS 1902141 | January | 2022 | 2022Q3 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2022-01-12 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 141 | 1714 | 1902270 | 2022-01-12 11:51 | 2022-01-12 13:01 | 70 | 11kV | 106600 | 2120 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220100 1 fault operation A & B Phase Overcurrent tree branch on OHM at sub 50865. Excluded OMS 1902270 | January | 2022 | 2022Q3 | 2022 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Veg | 2022-01-12 | N | 50.283 | N | 4 | N | N | 1.1101 | 39.4971 | 77900.1358
[7 empty] | 723 | 9258 | 1902419 | 2022-01-12 16:28 | 2022-01-12 19:00 | 152 | 11kV | 152 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | No LID Report Broken Live Line Lead to top of DOLF 77925. Operator John Frazer. AP issued for repairs. JMH Excluded OMS 1902419 | January | 2022 | 2022Q3 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2022-01-12 | N | 152 | N | 4 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 1290 | 15701 | 1902433 | 2022-01-12 19:56 | 2022-01-12 20:35 | 39 | 11kV | 39 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | Blown A phase DOLF replaced 10 amp fuse no cause found but previous storm night before Operator John Morris. JMH See related OMS 1902433 for original customer report | January | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-01-12 | N | 39 | N | 4 | N | N | 1.1101 | 39.4971 | 28.5
[7 empty] | 1338 | 16330 | 1902460 | 2022-01-13 02:20 | 2022-01-13 02:59 | 39 | 11kV | 12246 | 314 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S384 Camperdown Panel 4 tripped on Relays: A phase OC, EFI Field EFI's: NIl Cause: Section of front line feeder from ZN384 Camperdown Panel 4 to S5759 Mitchel Glebe has a suspected cable fault | January | 2022 | 2022Q3 | 2022 | ZN384:PA4 | ZN384:PA4 | ZN00384/000004 | SYDNEY | UG | Not Veg | 2022-01-13 | N | 39 | N | 8 | N | N | 1.1101 | 39.4971 | 8949.0156
[7 empty] | 925 | 11283 | 1902464 | 2022-01-13 05:40 | 2022-01-13 06:45 | 65 | 11kV | 1365 | 21 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Ex Caringbah Pnl.4R - AB35434 Centre phase open circuit and arcing | January | 2022 | 2022Q3 | 2022 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | OH | Not Veg | 2022-01-13 | N | 65 | N | 8 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 913 | 11238 | 1902552 | 2022-01-13 17:20 | 2022-01-13 17:42 | 22 | 11kV | 22 | 1 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 220103 Refer to OMS 1902552 Isolated PT 13449 to remove broken stay wire" SOP KEEGAN T DOP CLULOW G PETER FITZGERALD Pole SW 31550 has a pole top on it the stabalising wire has come loose and is hanging down over infrastructure concerned for safety no sign of arcing sparking or smoke - no animals will need to access the pole via the fairway - no covid isolation | January | 2022 | 2022Q3 | 2022 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2022-01-13 | N | 22 | N | 8 | N | N | 1.1101 | 39.4971 | 16.077
[7 empty] | 411 | 5225 | 1902596 | 2022-01-13 16:30 | 2022-01-13 18:05 | 95 | 11kV | 95 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220105 low 11kv OHM due to leaning pole 9M-90026. Excluded OMS 1902596 | January | 2022 | 2022Q3 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2022-01-13 | N | 95 | N | 8 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 1540 | 18874 | 1902668 | 2022-01-13 17:47 | 2022-01-13 18:29 | 42 | 11kV | 22890 | 545 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant Hill panel 2 tripped on Relays: Earth fault, EFI Signals: TX1 Group Earth Zone Earth, 11kV Trip | January | 2022 | 2022Q3 | 2022 | ZN965:PA2 | ZN965:PA2 | ZN00965/000002 | HORNSBY | OH | Not Veg | 2022-01-13 | N | 42 | N | 8 | N | N | 1.1101 | 39.4971 | 16727.3369
[7 empty] | 1506 | 18498 | 1902663 | 2022-01-13 17:11 | 2022-01-13 18:53 | 102 | 11kV | 76970 | 755 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn2196 Milperra Panel 2 Tripped on Relays: 11kV Trip, Zone Earth, TX3 Group Earth Cause: UG fault See OMSA1903587 1903588 1902663 | January | 2022 | 2022Q3 | 2022 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-01-13 | N | 101.947 | N | 8 | N | N | 1.1101 | 39.4971 | 56247.4058
[7 empty] | 1255 | 15274 | 1902658 | 2022-01-13 17:20 | 2022-01-13 21:25 | 245 | 11kV | 58115 | 271 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Insulator | Unplanned | No Weather Impact | N | LID 220102 Shocks job. Then Anthony Dallaway found Touch voltages on pole OR-30117. 11kV & LV isolated to check insulators on pole. | January | 2022 | 2022Q3 | 2022 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2022-01-13 | N | 214.4465 | N | 8 | N | N | 1.1101 | 39.4971 | 42468.7279
[7 empty] | 1013 | 12772 | 1902691 | 2022-01-13 20:29 | 2022-01-13 23:55 | 206 | 11kV | 206 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 220107 Single Phase Large tree branch brought down LV service - ABC conductor replaced and restrung - J.Lumley Refer to OMS No. 1902691 Sub isolated to restore service after falling tree branch brough service main down." SOP WILKINSON T DOP LUMLEY J | January | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2022-01-13 | N | 206 | N | 8 | N | N | 1.1101 | 39.4971 | 150.5387
[7 empty] | 546 | 6648 | 1902795 | 2022-01-14 11:59 | 2022-01-14 14:00 | 121 | 11kV | 110383 | 1389 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN 9118 CRONULLA - 11KV PANEL 8 'WOODWARD SAUNDERS' TRIPPED ON: Relays: C phase overcurrent, earth fault Signals: Group 1 and zone earth with EFI Field EFIs: Pnl18 to sub 9872 Defective 11kV UGOH at PT 9469 Mookara Pl - SHORT CIRCUIT See 1903580, 81, 82 (1902793, 95, 96, 97, 98, 1802805 records withdrawn) | January | 2022 | 2022Q3 | 2022 | ZN9118:PA8 | ZN9118:PA8 | ZN09118/000008 | SUTHERLAND | Unknown | Unknown | 2022-01-14 | N | 79.4694 | N | 3 | N | N | 1.1101 | 39.4971 | 80664.6407
[7 empty] | 196 | 2497 | 1902809 | 2022-01-14 12:47 | 2022-01-14 15:04 | 137 | 11kV | 36440 | 270 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC61084 Bushells Peats 0.1 tripped, reclosed & locked out on OC Cause not ascertained See 1905263 1905264 | January | 2022 | 2022Q3 | 2022 | ZN12630:PA6 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2022-01-14 | N | 134.963 | N | 3 | N | N | 1.1101 | 39.4971 | 26629.2772
[7 empty] | 948 | 11483 | 1902904 | 2022-01-14 21:55 | 2022-01-14 22:03 | 8 | 11kV | 21432 | 2679 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn15006 Dee Why West 11kV Panel 8 Narraweena feeder tripped on Relays: SEL Signals: 11kV Trip[ Cause: SW/B closed at S50262 with USL 21622 Open Staff error: Protection left auto on Panel 8 while switching See OMS 1903516 1902906 1902904 | January | 2022 | 2022Q3 | 2022 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | Unknown | Not Veg | 2022-01-14 | N | 8 | N | 3 | N | N | 1.1101 | 39.4971 | 15661.8735
[7 empty] | 598 | 7591 | 1902994 | 2022-01-15 10:47 | 2022-01-15 12:55 | 128 | 11kV | 896 | 7 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220112 A Phase DOLF : 10 Amp EExcluded OMS 1902994 | January | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2022-01-15 | N | 128 | N | 25 | Y | Y | 1.1101 | 39.4971 | 654.7704
[7 empty] | 500 | 6002 | 1903078 | 2022-01-15 17:50 | 2022-01-15 19:02 | 72 | 11kV | 73633 | 1309 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220128 2 fault operations A & C Phases Overcurrent excluded OMS 1903078 | January | 2022 | 2022Q3 | 2022 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Veg | 2022-01-15 | N | 56.2513 | N | 25 | Y | Y | 1.1101 | 39.4971 | 53808.8246
[7 empty] | 814 | 10094 | 1903063 | 2022-01-15 17:24 | 2022-01-15 19:44 | 140 | 11kV | 107940 | 771 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220139 Thunderstorm Overcurrent SOP DOOLAN P DOP POPLE A | January | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2022-01-15 | N | 140 | N | 25 | Y | Y | 1.1101 | 39.4971 | 78879.3683
[7 empty] | 456 | 5653 | 1903189 | 2022-01-15 19:20 | 2022-01-15 20:00 | 40 | 11kV | 40 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220129 Thunderstorm 10 Amp, Phase A, Substation DOLF Refer to OMS 1903189 DOP HOLLAND P SOP WADWELL D | January | 2022 | 2022Q3 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2022-01-15 | N | 40 | N | 25 | Y | Y | 1.1101 | 39.4971 | 29.2308
[7 empty] | 1558 | 19078 | 1903073 | 2022-01-15 17:48 | 2022-01-15 20:05 | 137 | 11kV | 37627 | 284 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Rain Wind Storm | N | At Zn12600 11 Kv Pa12 CB tripped, reclosed and tripped on Signals: 11KV Trip Relays: IOC, O/C A+C phase EFI 11kV DOwn on Pacific Hwy near Prings Rd (Between S18078 and S18011) See OMS 1803451 1803453 1903233 1903232 1903073 | January | 2022 | 2022Q3 | 2022 | ZN12600:PA12 | ZN12600:PA12 | ZN12600/000012 | CENTRAL COAST | OH | Not Veg | 2022-01-15 | N | 132.4894 | N | 25 | Y | Y | 1.1101 | 39.4971 | 27496.7018
[7 empty] | 617 | 7936 | 1903094 | 2022-01-15 17:58 | 2022-01-15 20:28 | 150 | 11kV | 219244 | 1741 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220134 Blown 11kV Lightning Arrestor pole HQ-81140 | January | 2022 | 2022Q3 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2022-01-15 | N | 125.9299 | N | 25 | Y | Y | 1.1101 | 39.4971 | 160217.0486
[7 empty] | 1300 | 15816 | 1903133 | 2022-01-15 18:34 | 2022-01-15 20:40 | 126 | 11kV | 252 | 2 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220131 Thunderstorm 10Amp, Phase B, Substation DOLF Refer to OMS 1903133 SOP HOLLAND P DOP AUSTIN G | January | 2022 | 2022Q3 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2022-01-15 | N | 126 | N | 25 | Y | Y | 1.1101 | 39.4971 | 184.1542
[7 empty] | 1137 | 14332 | 1903072 | 2022-01-15 17:44 | 2022-01-15 22:00 | 256 | 11kV | 58880 | 230 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220135 Thunderstorm 20 Amp, Phases A & C Phase, Line DOLF Refer to OMS 1903072 SOP HOLLAND P DOP POPLE A | January | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2022-01-15 | N | 256 | N | 25 | Y | Y | 1.1101 | 39.4971 | 43027.7673
[7 empty] | 289 | 3666 | 1903158 | 2022-01-15 18:56 | 2022-01-15 22:00 | 184.4833 | 11kV | 25089.7333 | 136 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220141 3 phase DOLF's : 40 Amp | January | 2022 | 2022Q3 | 2022 | 532:83314 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Veg | 2022-01-15 | N | 184.4833 | N | 25 | Y | Y | 1.1101 | 39.4971 | 18334.8371
[7 empty] | 6 | 104 | 1903074 | 2022-01-15 17:50 | 2022-01-15 22:47 | 297 | 11kV | 515041 | 1745 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At S12600 Lisarow Panel 3 Lisarow High Taylor CB tripped on Signals: 11kV Trip Relays: IOC, OC, EFI DOp Patrolled feeder and found no cause: Previous lightning storm. See OMS 1903455 1903457 1903459 1903074 | January | 2022 | 2022Q3 | 2022 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2022-01-15 | N | 295.1524 | N | 25 | Y | Y | 1.1101 | 39.4971 | 376376.7717
[7 empty] | 1474 | 18200 | 1903091 | 2022-01-15 17:57 | 2022-01-15 23:35 | 338 | 11kV | 362468 | 1243 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220142 and LID 220195 2 fault operations B & C Phases Overcurrent No Cause Found | January | 2022 | 2022Q3 | 2022 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2022-01-15 | N | 291.6074 | N | 25 | Y | Y | 1.1101 | 39.4971 | 264880.9234
[7 empty] | 1682 | 20421 | 1903118 | 2022-01-15 18:14 | 2022-01-16 00:25 | 371 | 11kV | 126107 | 1236 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220137 and LID 220185 1 fault operation C Phase Overcuurent 11kV mains down from pole IU-61188 Excluded OMS 1903118, 1903215. | January | 2022 | 2022Q3 | 2022 | 214:8669 | 214:8669 | ZN00214/008669 | LAKE MACQUARIE | OH | Not Veg | 2022-01-15 | N | 102.0283 | N | 25 | Y | Y | 1.1101 | 39.4971 | 92155.2761
[7 empty] | 1204 | 14943 | 1903124 | 2022-01-15 18:16 | 2022-01-16 00:28 | 372 | 11kV | 494760 | 1330 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220147 and LID 220189 Earth Fault Blown lightning arrestor at ELB 78314 + blown arrestor at UGOH pole IR-50348 Excluded OMS 1903124 AND 1903239 | January | 2022 | 2022Q3 | 2022 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2022-01-15 | N | 372 | N | 25 | Y | Y | 1.1101 | 39.4971 | 361556.0151
[7 empty] | 1005 | 12538 | 1903120 | 2022-01-15 18:14 | 2022-01-16 02:10 | 476 | 11kV | 149548 | 1869 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220133 and 220186 2 fault operations A & B Phase Overcurrent Tree on 11kV mains sub 15568 | January | 2022 | 2022Q3 | 2022 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | OH | Veg | 2022-01-15 | N | 80.015 | N | 25 | Y | Y | 1.1101 | 39.4971 | 109285.2675
[7 empty] | 66 | 830 | 1903168 | 2022-01-15 19:48 | 2022-01-16 07:40 | 712 | 11kV | 17800 | 25 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 220151 C Phase Burnt off LLC. Left in LV//. Excluded OMS 1903214 | January | 2022 | 2022Q3 | 2022 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2022-01-15 | N | 712 | N | 25 | Y | Y | 1.1101 | 39.4971 | 13007.715
[7 empty] | 194 | 2485 | 1903100 | 2022-01-15 18:08 | 2022-01-16 08:45 | 877 | 11kV | 4385 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220156 10 Amp, Phase A, Substation DOLF Refer to OMS 1903100 SOP McGUIRE L DOP POPLE A | January | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-01-15 | N | 877 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3204.4287
[7 empty] | 203 | 2583 | 1903102 | 2022-01-15 18:56 | 2022-01-16 09:13 | 857 | 11kV | 261076 | 322 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220144 Overcurrent Excluded OMS 1903102 | January | 2022 | 2022Q3 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-01-15 | N | 810.795 | N | 25 | Y | Y | 1.1101 | 39.4971 | 190786.6404
[7 empty] | 1063 | 13638 | 1903227 | 2022-01-15 20:31 | 2022-01-16 09:58 | 807 | 11kV | 1614 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220158 C Phase DOLF : 10 Amp Excluded OMS 1903227 | January | 2022 | 2022Q3 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2022-01-15 | N | 807 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1179.4636
[7 empty] | 1516 | 18609 | 1903196 | 2022-01-15 19:28 | 2022-01-16 11:20 | 952 | 11kV | 4760 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 220159 Substation DOLF Customer reported, Pole IQ-81932 struck by lightning SOP McGUIRE L DOP McFADYEN T NOTE: incorrect sub and times in LID, job recreated from information in OMS 1903196 | January | 2022 | 2022Q3 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2022-01-15 | N | 952 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3478.4676
[7 empty] | 941 | 11376 | 1903322 | 2022-01-16 11:45 | 2022-01-16 11:49 | 4 | 11kV | 10048 | 2512 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220147 - Part 2 Blown lightning arrestor at ELB 78314 + blown arrestor at UGOH pole IR-50348 also refer to 1903818 | January | 2022 | 2022Q3 | 2022 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2022-01-16 | N | 4 | N | 6 | N | N | 1.1101 | 39.4971 | 7342.782
[7 empty] | 1076 | 13812 | 1903060 | 2022-01-15 17:19 | 2022-01-16 12:38 | 1158.9667 | 11kV | 43342.3333 | 73 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | 11kV Recloser 45035 'Mangrove Mountain' (ex ZN 12630 Peats Ridge Panel 6L) tripped and reclosed on: RElays: OC trip, EF trip, lockout Wires down beyond USL 40940 - tree/branch brought down OH See 1903771, 72, 1903175 | January | 2022 | 2022Q3 | 2022 | ZN12630:PA6 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2022-01-15 | N | 593.7306 | N | 25 | Y | Y | 1.1101 | 39.4971 | 31673.2988
[7 empty] | 1458 | 17988 | 1903114 | 2022-01-15 18:13 | 2022-01-16 13:50 | 1177 | 11kV | 416987 | 924 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220138 and LID 220187 2 fault operations 3 phase DOLF : 31 Amp Intellirupter; Overcurrent; Substation DOLF Excluded OMS 1903114 | January | 2022 | 2022Q3 | 2022 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2022-01-15 | N | 451.2846 | N | 25 | Y | Y | 1.1101 | 39.4971 | 304721.8006
[7 empty] | 644 | 8378 | 1903128 | 2022-01-15 18:26 | 2022-01-16 14:15 | 1189 | 11kV | 15457 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220163 DOLF : 20 Amp Excluded OMS 1903128 | January | 2022 | 2022Q3 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2022-01-15 | N | 1189 | N | 25 | Y | Y | 1.1101 | 39.4971 | 11295.5197
[7 empty] | 900 | 11083 | 1903105 | 2022-01-15 18:06 | 2022-01-16 15:00 | 1254 | 11kV | 179154 | 504 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN35370 Galston, ex Panel 10L Recloser 3280 Hunt Ave has tripped on overcurrent and SEF trip. Recloser 50015 Quarry Old Northern has also tripped on overcurrent and SEF trip. Section of 11kV feeder interrupted from LB 914 to repair HR bonds at LB 3092 @ 1115 hrs. Tree / branch reported on OH mains. See 1903830, 1903829, 1903827, 1903825, 1903824, (1903310, 1903307, 1903306, 1903355, 1903354, 1903117, 1903105 records withdrawn) | January | 2022 | 2022Q3 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2022-01-15 | N | 355.4643 | N | 25 | Y | Y | 1.1101 | 39.4971 | 130920.4591
[7 empty] | 72 | 895 | 1903070 | 2022-01-15 17:44 | 2022-01-16 15:00 | 1276.1167 | 11kV | 26798.45 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220165 A & C phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | January | 2022 | 2022Q3 | 2022 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2022-01-15 | N | 1276.1167 | N | 25 | Y | Y | 1.1101 | 39.4971 | 19583.5168
[7 empty] | 698 | 9000 | 1903076 | 2022-01-15 17:47 | 2022-01-16 16:20 | 1353 | 11kV | 123047 | 339 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220130 3 fault operations 3 phase Overcurrent, Earth Fault 11kV mains down pole GW-20160 Excluded OMS 1903076 | January | 2022 | 2022Q3 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2022-01-15 | N | 362.9705 | N | 25 | Y | Y | 1.1101 | 39.4971 | 89919.1183
[7 empty] | 1673 | 20359 | 1903282 | 2022-01-16 08:14 | 2022-01-16 17:50 | 575.5667 | 11kV | 3453.4 | 6 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Previous Storm | N | At PT 13338 Dooralong Yambo 0.8 - EX ZN14891 Wyong Panel 5 'wyong' 11kV middle and footpath 16 amp HDOs blown PT TX defective after suspected lightning strike supply restored via MG, TX to be replaced. CC1: 22-"Refer to SOp" FRC1: 329-"High Voltage Fuse - Requires replacement" | January | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2022-01-16 | N | 575.5667 | N | 6 | N | N | 1.1101 | 39.4971 | 2523.6429
[7 empty] | 1327 | 16191 | 1903375 | 2022-01-16 17:01 | 2022-01-16 19:25 | 144 | 11kV | 288 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220170 B & C Phase DOLF : 10 Amp Excluded OMS 1903375 | January | 2022 | 2022Q3 | 2022 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2022-01-16 | N | 144 | N | 6 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 935 | 11330 | 1903336 | 2022-01-16 12:26 | 2022-01-16 21:30 | 544 | 11kV | 1088 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220174 A Phase DOLF : 16 Amp Excluded OMS 1903336 | January | 2022 | 2022Q3 | 2022 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Veg | 2022-01-16 | N | 544 | N | 6 | N | N | 1.1101 | 39.4971 | 795.0783
[7 empty] | 349 | 4802 | 1903400 | 2022-01-16 21:02 | 2022-01-16 22:28 | 86 | 11kV | 85140 | 990 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ZN 847 Hornsby 11kV VCB Panel 14 '8506; feeder tripped on: Relays: B phase IOC, A and C Phase overcurrent, EFI, Fault check Field EFIs: 8506, 7292 Sigs: 11kV trip OH section of feeder patrolled after report of explosion head with nil defects found - no cause ascertained. ABNORMAL SWITCHING: SW/B CLOSED @ S8428 SW/B CLOSED @ S65858 AB 1593 OPENED See 1903846, 1903850 | January | 2022 | 2022Q3 | 2022 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Veg | 2022-01-16 | N | 86 | N | 6 | N | N | 1.1101 | 39.4971 | 62217.8008
[7 empty] | 1260 | 15355 | 1903411 | 2022-01-16 22:57 | 2022-01-17 11:25 | 748 | 11kV | 748 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220207 Single phase DOLF : 10 Amp Excluded OMS 1903411 | January | 2022 | 2022Q3 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-01-16 | N | 748 | N | 6 | N | N | 1.1101 | 39.4971 | 546.6163
[7 empty] | 1399 | 17133 | 1903524 | 2022-01-17 10:57 | 2022-01-17 12:50 | 113 | 11kV | 141540 | 1258 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35800 Bankstwon Panel 7 Tripped on Relays:L 51N(EF), 50TN(Fault Check), EFI Cause: UG or UGoH fault between S3579 to S74332 to S4527 See OMS1903804 1903805 1903524 | January | 2022 | 2022Q3 | 2022 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-01-17 | N | 112.5119 | N | 7 | N | N | 1.1101 | 39.4971 | 103433.2573
[7 empty] | 881 | 10853 | 1903597 | 2022-01-17 13:29 | 2022-01-17 14:45 | 76 | 11kV | 152 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Previous Storm | N | LID 220214 Single phase DOLF : 10 Amp Replaced both Dolf carriers. Excluded OMS 1903597 | January | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2022-01-17 | N | 76 | N | 7 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 835 | 10271 | 1903596 | 2022-01-17 13:25 | 2022-01-17 17:48 | 263 | 11kV | 39187 | 149 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 220213 sub isolated for emergency transformer change excluded oms 1903596 | January | 2022 | 2022Q3 | 2022 | 257:81987 | 257:81987 | ZN00257/081987 | NEWCASTLE | OH | Not Veg | 2022-01-17 | N | 263 | N | 7 | N | N | 1.1101 | 39.4971 | 28636.7038
[7 empty] | 938 | 11348 | 1903684 | 2022-01-17 17:36 | 2022-01-17 18:45 | 69 | 11kV | 48921 | 709 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 129 Hunters Hill - Panel 63 tripped on: Relays: On Pro 1 & 2 A & B phase O/C Signals: A& B phase O/C Field EFIs: nil Section of OH 11kV feeder patrolled and Dop advised trees above and below the mains. No tree branch found on the mains at time of patrol. | January | 2022 | 2022Q3 | 2022 | ZN129:PA63 | ZN129:PA63 | ZN00129/000063 | LANE COVE | OH | Not Veg | 2022-01-17 | N | 69 | N | 7 | N | N | 1.1101 | 39.4971 | 35750.0239
[7 empty] | 1014 | 12784 | 1903710 | 2022-01-17 19:27 | 2022-01-17 23:15 | 228 | 11kV | 228 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220219 A & C Phase DOLF's : 5 Amp Excluded OMS 1903710 | January | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-01-17 | N | 228 | N | 7 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 831 | 10221 | 1903677 | 2022-01-17 18:40 | 2022-01-18 | 320 | 11kV | 140452 | 1079 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 220221 No protection operations. Section isolated for pole fire Excluded OMS 1903707 & 1903677 | January | 2022 | 2022Q3 | 2022 | 532:83298 | 532:83298 | ZN00532/083298 | MAITLAND | OH | Not Veg | 2022-01-17 | N | 130.1687 | N | 7 | N | N | 1.1101 | 39.4971 | 102638.179
[7 empty] | 391 | 5128 | 1903726 | 2022-01-18 00:23 | 2022-01-18 01:24 | 61 | 11kV | 18374 | 2286 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35800 Bankstown - Pnl.15 tripped, reclosed & locked out on: A & B phase IOC Abnormal: LB2110 Closed with S7432 Sw/A Open (DMA) UG cable fault between S77854 Sw/B & S79611 Sw/A See 1903721 1903845 CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | January | 2022 | 2022Q3 | 2022 | ZN35800:PA7 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-01-18 | N | 8.0376 | N | 7 | N | N | 1.1101 | 39.4971 | 13427.1773
[7 empty] | 650 | 8421 | 1903717 | 2022-01-17 20:21 | 2022-01-18 01:36 | 315 | 11kV | 172199 | 1073 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.12 tripped on: Earth Fault UG cable fault between S18576 Sw/B to S14910 Sw/A See 1903907 1903908 1903912 1903913 1903914 1903915 | January | 2022 | 2022Q3 | 2022 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | UG | Not Veg | 2022-01-17 | N | 160.4837 | N | 7 | N | N | 1.1101 | 39.4971 | 125837.9502
[7 empty] | 1518 | 18650 | 1903753 | 2022-01-18 07:26 | 2022-01-18 09:32 | 126 | 11kV | 9684 | 79 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.20 tripped on: C phase to Neutral OC UG cable fault between S8145 Vore griffard to S823 Fariola St See 1903838 1903838 | January | 2022 | 2022Q3 | 2022 | ZN1610:PA20 | ZN1610:PA20 | ZN01610/000020 | PARRAMATTA | UG | Not Veg | 2022-01-18 | N | 122.5823 | N | 7 | N | N | 1.1101 | 39.4971 | 7076.7816
[7 empty] | 126 | 1572 | 1903768 | 2022-01-18 08:39 | 2022-01-18 11:05 | 146 | 11kV | 292 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220222 B Phase DOLF : 10 Amp Excluded OMS 1903768 | January | 2022 | 2022Q3 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2022-01-18 | N | 146 | N | 7 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 1351 | 16502 | 1903868 | 2022-01-18 12:48 | 2022-01-18 15:30 | 162 | 11kV | 175044 | 1750 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 220236 2 fault operations B Phase Overcurrent; Earth Fault Possible LA's or UG cable fault. - restored via LV// Excluded OMS 1903868 | January | 2022 | 2022Q3 | 2022 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | UG | Not Veg | 2022-01-18 | N | 100.0251 | N | 7 | N | N | 1.1101 | 39.4971 | 127916.9923
[7 empty] | 963 | 11707 | 1903905 | 2022-01-18 14:24 | 2022-01-18 17:42 | 198 | 11kV | 212147 | 1783 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 220231 3 phase Earth Fault Fdr 34136 tripped due to cable fault between sw 29706 & 11kv links 28819. Section isolated for future repairs. Excluded OMS 1903905. | January | 2022 | 2022Q3 | 2022 | 238:34136 | 238:34136 | ZN00238/034136 | MAITLAND | UG | Not Veg | 2022-01-18 | N | 118.9832 | N | 7 | N | N | 1.1101 | 39.4971 | 155030.7703
[7 empty] | 1154 | 14507 | 1904012 | 2022-01-18 20:35 | 2022-01-18 22:05 | 90 | 11kV | 25725 | 297 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn2466 Flemington - Pnl.7 tripped on: B Phase OC & EF UG cable fault between S7725 and S8205 See 1905223 1905224 1905225 | January | 2022 | 2022Q3 | 2022 | ZN2466:PA7 | ZN2466:PA7 | ZN02466/000007 | PARRAMATTA | UG | Not Veg | 2022-01-18 | N | 86.6162 | N | 7 | N | N | 1.1101 | 39.4971 | 18799.0712
[7 empty] | 522 | 6204 | 1904027 | 2022-01-19 01:47 | 2022-01-19 02:34 | 47 | 11kV | 47940 | 1020 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220237 2 fault operations Instantaneous Overcurrent branch on mains pole JU-31309 Excluded OMS 1904029/030 | January | 2022 | 2022Q3 | 2022 | 257:81985 | 257:81985 | ZN00257/081985 | NEWCASTLE | OH | Veg | 2022-01-19 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 35033.138
[7 empty] | 594 | 7505 | 1904112 | 2022-01-19 10:48 | 2022-01-19 12:10 | 82 | 11kV | 82 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 220240 A Phase DOLF : 10 Amp Excluded OMS 1904112 | January | 2022 | 2022Q3 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2022-01-19 | N | 82 | N | 5 | N | N | 1.1101 | 39.4971 | 59.9232
[7 empty] | 877 | 10836 | 1903864 | 2022-01-18 12:38 | 2022-01-19 14:15 | 1537 | 11kV | 705903 | 2274 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn36800 Waverley - Pnl.58 tripped on Earth Fault Contractor underboring in Carrington Rd Near Darley See 1905239 1905240 1905241 | January | 2022 | 2022Q3 | 2022 | ZN36800:PA58 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2022-01-18 | N | 310.4235 | N | 7 | N | N | 1.1101 | 39.4971 | 515853.0918
[7 empty] | 1219 | 15036 | 1904153 | 2022-01-19 12:27 | 2022-01-19 17:04 | 277 | 11kV | 11024 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | No LID Report B phase main down near HC5839 Halls Road B Phase broken away from Halls creek RAGCB 5839. B and C phase terminations repaired. Operator Mulvaney Protection SEF operation. Excluded OMS 1904153 | January | 2022 | 2022Q3 | 2022 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2022-01-19 | N | 268.878 | N | 5 | N | N | 1.1101 | 39.4971 | 8056.014
[7 empty] | 1490 | 18373 | 1904280 | 2022-01-20 00:59 | 2022-01-20 02:35 | 96 | 11kV | 85472 | 1045 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S14144 Wamberal Panel 7 tripped, reclosed, tripped and locked Relays: A and B phase OC Field EFI's Nil Cause: Branch Near CP42620 1904655 1904657 1904280 | January | 2022 | 2022Q3 | 2022 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2022-01-20 | N | 81.7914 | N | 4 | N | N | 1.1101 | 39.4971 | 62460.4166
[7 empty] | 668 | 8614 | 1905233 | 2022-01-19 12:33 | 2022-01-20 03:00 | 867 | 11kV | 37281 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn35370 Galston - 11kV Bonds broken beyond USL1556 No Protection operation as mains broken clear and de-energised on ground in Laurie Rd Galston | January | 2022 | 2022Q3 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2022-01-19 | N | 867 | N | 5 | N | N | 1.1101 | 39.4971 | 27243.8552
[7 empty] | 105 | 1359 | 1904265 | 2022-01-19 20:15 | 2022-01-20 13:00 | 1005 | 11kV | 1005 | 1 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 220244 C Phase DOLF : 10 Amp SEE REPORT 220245 Ugoh pole IQ-41146 open cct on one phase section isolated for repairs. Excluded oms 1904265 | January | 2022 | 2022Q3 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | Unknown | Unknown | 2022-01-19 | N | 1005 | N | 5 | N | N | 1.1101 | 39.4971 | 734.4244
[7 empty] | 1325 | 16182 | 1904387 | 2022-01-20 11:45 | 2022-01-20 13:00 | 75 | 11kV | 75 | 1 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 220245 Repairs required to ugoh pole IQ-41146 requires llc pole IQ-41146 WHICH ALSO ISOLATES sub 52844. Excluded OMS 1904265 | January | 2022 | 2022Q3 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | Unknown | Unknown | 2022-01-20 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 511 | 6133 | 1904361 | 2022-01-20 09:50 | 2022-01-20 14:00 | 250 | 11kV | 2830 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | ## FDR abnormally switched from NAR 89962 Blown Dolfs : 10Amp Restored and no cause found. OMS 1904361, 1904392, 1904394 related | January | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2022-01-20 | N | 217.6923 | N | 4 | N | N | 1.1101 | 39.4971 | 2068.0805
[7 empty] | 562 | 6943 | 1904470 | 2022-01-20 16:03 | 2022-01-20 17:20 | 77 | 11kV | 539 | 7 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | Broken C phase LLC at Sub 51064. Permits issued and repairs completed Operator J Frazer. JMH Excluded OMS 1904470 | January | 2022 | 2022Q3 | 2022 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2022-01-20 | N | 77 | N | 4 | N | N | 1.1101 | 39.4971 | 393.8853
[7 empty] | 1239 | 15147 | 1904578 | 2022-01-21 09:52 | 2022-01-21 13:17 | 205 | 11kV | 78169 | 1309 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 220247 2 fault operations Earth Fault, Overcurrent Explosion on UGOH Blown L/A at P. JS-20741 Excluded OMS 1904578 1904601 | January | 2022 | 2022Q3 | 2022 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | Unknown | Unknown | 2022-01-21 | N | 59.7166 | N | 3 | N | N | 1.1101 | 39.4971 | 57123.5996
[7 empty] | 849 | 10534 | 1904705 | 2022-01-21 19:49 | 2022-01-21 22:10 | 141 | 11kV | 141 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220252 C Phase DOLF : 10 Amp Excluded OMS 1904705 | January | 2022 | 2022Q3 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2022-01-21 | N | 141 | N | 3 | N | N | 1.1101 | 39.4971 | 103.0386
[7 empty] | 79 | 970 | 1904661 | 2022-01-21 21:25 | 2022-01-22 00:20 | 175 | 11kV | 29750 | 170 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 220251 3 phase Transformer Unit Protection Sub 50834 leaking oil 11kV section isolated by DOPs Excluded OMS#1904661 | January | 2022 | 2022Q3 | 2022 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2022-01-21 | N | 175 | N | 3 | N | N | 1.1101 | 39.4971 | 21740.4225
[7 empty] | 1416 | 17420 | 1904869 | 2022-01-22 23:28 | 2022-01-23 00:40 | 72 | 11kV | 288 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220255 A & B Phase DOLF : 16 Amp Excluded OMS 1904869 | January | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2022-01-22 | N | 72 | N | 2 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 920 | 11259 | 1904737 | 2022-01-22 07:06 | 2022-01-23 01:00 | 1074 | 11kV | 69630 | 789 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn80 Chatswood Panel 27 Feeder tripped on Relays: 27L OC A and B pohase Earth fault, EFI, A phase OC timed earth fault check Cause: 11kV UG Fault - Trunk section See OMS 1905261 1905262 1904737 1904758 | January | 2022 | 2022Q3 | 2022 | ZN80:PA27 | ZN80:PA27 | ZN00080/000027 | WILLOUGHBY | UG | Not Veg | 2022-01-22 | N | 88.251 | N | 2 | N | N | 1.1101 | 39.4971 | 50883.5503
[7 empty] | 494 | 5967 | 1904960 | 2022-01-23 21:18 | 2022-01-23 23:02 | 104 | 11kV | 17784 | 171 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of 11kV Feeder @ ZN12660 Woy Woy 11kV Bond off roadside @ C64363 Abnormal Swithcing: CP64363 SW/A Open CP64362 Closed see OMS 1905200 1904960 | January | 2022 | 2022Q3 | 2022 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2022-01-23 | N | 104 | N | 2 | N | N | 1.1101 | 39.4971 | 12996.0227
[7 empty] | 1608 | 19566 | 1904967 | 2022-01-23 23:54 | 2022-01-24 01:28 | 94 | 11kV | 165706 | 1807 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN14892 Charmhaven 11kV Feeder panel 6 tripped, reclosed tripped and loced out on Cause: UG cable faullt on front line feeder from ZN14892 Charmhaven Panel 6 to S14980 Parkside pacific Abnormal Switching: S18122 SW/B Open, SW/A closed Cause: UG cable fault frontline feeder fault See OMS 1905187 1905189 1904968 1904967 | January | 2022 | 2022Q3 | 2022 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | UG | Not Veg | 2022-01-23 | N | 91.7023 | N | 2 | N | N | 1.1101 | 39.4971 | 121093.0573
[7 empty] | 1442 | 17797 | 1905128 | 2022-01-24 17:53 | 2022-01-24 19:30 | 97 | 11kV | 37349 | 390 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35490 North Sydney Panel 97 Tripped on Relays: A Protn - B phase Earth Fault B Protction - B phase Earth Fault and Neutral Fault Signals: 11kV Trip Cause: UG cable fault - S6910 and S6644 NO EFI's sections of feeder had to be proved one at a time section defective from S6644 to S219 See OMS1905278 1905280 1905128 | January | 2022 | 2022Q3 | 2022 | ZN35400:PA97 | ZN35400:PA97 | ZN35400/000097 | NORTH SYDNEY | UG | Not Veg | 2022-01-24 | N | 95.7667 | N | 1 | N | N | 1.1101 | 39.4971 | 27293.5476
[7 empty] | 1278 | 15581 | 1905166 | 2022-01-25 06:51 | 2022-01-25 08:40 | 109 | 11kV | 34487 | 964 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 220263 Earth Fault Refer to oms 1905166 Auto open due to bird at SI-90941 SOP CARSON S DOP OLIVER S | January | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2022-01-25 | N | 35.7749 | N | 4 | N | N | 1.1101 | 39.4971 | 25202.0824
[7 empty] | 1144 | 14405 | 1905476 | 2022-01-25 11:00 | 2022-01-25 13:53 | 173 | 11kV | 173 | 1 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 220264 "#oms 1905156 continue from lid 220261. To fix ABS 41016" SOP CARSON S DOP WATTERS L | January | 2022 | 2022Q3 | 2022 |  |  |  | SINGLETON | OH | Not Veg | 2022-01-25 | N | 173 | N | 4 | N | N | 1.1101 | 39.4971 | 126.4233
[7 empty] | 685 | 8754 | 1905284 | 2022-01-25 14:39 | 2022-01-25 18:25 | 226 | 11kV | 5910 | 42 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 220265 Earth Fault Sensitive Earth Fault Blown Lightning Arrestor at Sub 72901, DOLF didn't fall Refer to oms 1905284 EF, SEF" SOP CARSON S DOP AUSTIN G | January | 2022 | 2022Q3 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2022-01-25 | N | 140.7143 | N | 4 | N | N | 1.1101 | 39.4971 | 4318.8537
[7 empty] | 840 | 10356 | 1905332 | 2022-01-25 20:15 | 2022-01-25 20:58 | 43 | 11kV | 4988 | 116 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn1193 Lindfield Panel 28L From Recloser CP2749 Delhi River Tripped on OC and Locked open Cause: DOp Patrolled feeder upto S5068 Fairy Land River DOp found tree branch on Mains neqar N/O LB 1817 | January | 2022 | 2022Q3 | 2022 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | RYDE | OH | Veg | 2022-01-25 | N | 43 | N | 4 | N | N | 1.1101 | 39.4971 | 3645.0833
[7 empty] | 796 | 9931 | 1905415 | 2022-01-26 17:08 | 2022-01-26 18:50 | 102 | 11kV | 3689 | 41 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn9534 Panel 18 Tripped and reclosed on Signals: 11kV Trip Relays: B Phase OC trip, and EFI Cause: Truck took down 3 services aand launched one into the 11kV causing the road and middle phases of AB35375 to go HR and Catch fire See Second outage @ 17:08 See OMS 1905447 1905448 1905415 | January | 2022 | 2022Q3 | 2022 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2022-01-26 | N | 89.9756 | N | 2 | N | N | 1.1101 | 39.4971 | 2695.8124
[7 empty] | 60 | 704 | 1905432 | 2022-01-26 20:05 | 2022-01-27 10:20 | 855 | 11kV | 855 | 1 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220272 Replace faulty service | January | 2022 | 2022Q3 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2022-01-26 | N | 855 | N | 2 | N | N | 1.1101 | 39.4971 | 624.8088
[7 empty] | 183 | 2408 | 1905451 | 2022-01-27 10:40 | 2022-01-27 16:55 | 375 | 11kV | 1875 | 5 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Section of 11kV feeder panel No18 'Kurnell aux no 1' at ZN9534 Kurnell Due to abnormal switching Radial from LB35962, section of feeder interrupted to allow emergency repairs on DMA link @ REC 35971 Captain Cook 1905451 Withdrawn | January | 2022 | 2022Q3 | 2022 | ZN9534:PA18 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2022-01-27 | N | 375 | N | 5 | N | N | 1.1101 | 39.4971 | 1370.1947
[7 empty] | 153 | 1828 | 1905559 | 2022-01-27 17:33 | 2022-01-27 18:20 | 47.15 | 11kV | 3159.05 | 67 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV OH (Ex ZN 12630 Peats Ridge Panel 8) from LB 49853 interrupted for safety reasons. Emergency repair for significant de-stranding of HV OH. | January | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2022-01-27 | N | 47.15 | N | 5 | N | N | 1.1101 | 39.4971 | 2308.5406
[7 empty] | 907 | 11196 | 1905596 | 2022-01-27 16:07 | 2022-01-27 21:00 | 293 | 33kV Distribution | 673 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220278 No protection operations. Broken PG clamps pole JT-62429 Aslo refer to ## OMS 1905596. | January | 2022 | 2022Q3 | 2022 | 417:80491 | 417:80491 | ZN00417/080491 | NEWCASTLE | OH | Not Veg | 2022-01-27 | N | 134.6 | N | 5 | N | N | 1.1101 | 39.4971 | 491.8085
[7 empty] | 715 | 9211 | 1905648 | 2022-01-27 22:16 | 2022-01-27 22:52 | 36 | 11kV | 43776 | 1216 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 220279 Cable fault UGOH Pole IV-97076 SOP HODDA J DOP JOHNS G | January | 2022 | 2022Q3 | 2022 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | Unknown | Unknown | 2022-01-27 | N | 36 | N | 5 | N | N | 1.1101 | 39.4971 | 31990.2096
[7 empty] | 860 | 10654 | 1905641 | 2022-01-27 20:15 | 2022-01-27 23:40 | 205 | 11kV | 52070 | 254 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 220276 MVA pole HW-77013. SOP HODDA J DOP ROBERTSON D | January | 2022 | 2022Q3 | 2022 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2022-01-27 | N | 205 | N | 5 | N | N | 1.1101 | 39.4971 | 38051.2202
[7 empty] | 1263 | 15422 | 1905665 | 2022-01-28 03:09 | 2022-01-28 06:50 | 221 | 11kV | 71835 | 486 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3472 Sefton -Pnl.11 tripped on: B phase OC UG cable fault between S6081, LB3067 tee PT1467 See 1907215 1907216 | January | 2022 | 2022Q3 | 2022 | ZN3472:PA11 | ZN3472:PA11 | ZN03472/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-01-28 | N | 147.8086 | N | 7 | N | N | 1.1101 | 39.4971 | 52494.8992
[7 empty] | 895 | 11026 | 1905691 | 2022-01-28 09:04 | 2022-01-28 11:08 | 124 | 11kV | 124 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220285 Also see OMS 1905691 80A C Phase FUSE BLEW IN RMI , NO OBVIOUS CAUSE." SOP DOOLAN P DOP MULVANEY G | January | 2022 | 2022Q3 | 2022 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2022-01-28 | N | 124 | N | 7 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 879 | 10845 | 1905779 | 2022-01-28 14:04 | 2022-01-28 16:02 | 118 | 11kV | 118 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220287 No Cause Found (Not Storm Condition) 10 Amp, Phase A, Substation DOLF Refer to "OMS 1905779 Job incorrectly ID'd sub as 50497" SOP FITZPATRICK S DOP APPS D | January | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-01-28 | N | 118 | N | 7 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 1188 | 14775 | 1906166 | 2022-01-28 15:48 | 2022-01-28 16:25 | 37 | 11kV | 740 | 20 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220291 Single phase Fuse saver During SI 88621 after closing 11kv links 41293 to restore supply fuse saver 41292 tripped. Fuse saver reinstated power restored. | January | 2022 | 2022Q3 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2022-01-28 | N | 37 | N | 7 | N | N | 1.1101 | 39.4971 | 540.7702
[7 empty] | 690 | 8826 | 1905831 | 2022-01-28 15:14 | 2022-01-28 16:55 | 101 | 11kV | 101 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220290 No Cause Found (Not Storm Condition) 10 Amp, C phase, Substation DOLF Note: refer to OMS 1905807 incorrectly IDs sub as 77698 SOP FITZPATRICK S DOP APPS D | January | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2022-01-28 | N | 101 | N | 7 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 586 | 7386 | 1905836 | 2022-01-28 17:50 | 2022-01-28 19:28 | 98 | 11kV | 85554 | 873 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | REC35756 Bundeena - Tripped on SEL Cause not ascertained. DOp patrolled and found nothing. | January | 2022 | 2022Q3 | 2022 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2022-01-28 | N | 98 | N | 7 | N | N | 1.1101 | 39.4971 | 62520.3398
[7 empty] | 405 | 5188 | 1905872 | 2022-01-28 21:10 | 2022-01-28 22:35 | 85 | 11kV | 228255 | 3039 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn4545 Meadowbank Panel 31 Tripped on Relays: F/C, O/C, EF and EFI Signals: TX3 Group Earth, 11KV trip, Zone Earth Cause: UG cable fault between S1561 and S2968 See OMS 1906260 1906261 1906263 1905875 1905872 | January | 2022 | 2022Q3 | 2022 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | RYDE | UG | Not Veg | 2022-01-28 | N | 75.1086 | N | 7 | N | N | 1.1101 | 39.4971 | 166802.0216
[7 empty] | 407 | 5194 | 1905882 | 2022-01-29 00:15 | 2022-01-29 02:20 | 125 | 11kV | 3375 | 27 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 220293 section isolated to repair abs 40147 Excluded oms 1905882 | January | 2022 | 2022Q3 | 2022 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2022-01-29 | N | 125 | N | 4 | N | N | 1.1101 | 39.4971 | 2466.3505
[7 empty] | 1510 | 18567 | 1905913 | 2022-01-29 10:24 | 2022-01-29 13:06 | 162 | 11kV | 231007 | 2181 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12620 Noraville - Pnl.11 tripped on: B & C phase OC 1. Centre phase bond off pole TO22992 (above LB40203) 2. Centre phase bond off ex Pnl.2 below LB47933 - tee off to Pnl.11) Note: When DOp closed AB45015 @ 1130, 11kV bond burnt off below LB47933 @1132 - REC45050 & REC45053 tripped See 1907229 1907230 1905935 | January | 2022 | 2022Q3 | 2022 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2022-01-29 | N | 105.9179 | N | 4 | N | N | 1.1101 | 39.4971 | 168813.102
[7 empty] | 607 | 7752 | 1905980 | 2022-01-29 15:39 | 2022-01-29 18:45 | 186 | 11kV | 99033 | 1723 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN15004 Newport Zone 11kV Panel 1 Feeder tripped on Signals : CB1 Sw3014 Open 11kV Trip,Zone Earth Relays B & C phase IOC, Fault Check,EFI Field EFI's S15792,S16755, (S48427 EFI electronic did not work) Ex S16841 UGOH Defective UGOH Fault Short Circuit See OMS 1906284 in relation OMS 1905892,1905980,1905981,1905984 1905999 Withdrawn | January | 2022 | 2022Q3 | 2022 | ZN15004:PA1 | ZN15004:PA1 | ZN15004/000001 | NORTHERN BEACHES | Unknown | Unknown | 2022-01-29 | N | 57.4771 | N | 4 | N | N | 1.1101 | 39.4971 | 72370.3954
[7 empty] | 1679 | 20403 | 1906006 | 2022-01-29 18:20 | 2022-01-29 22:55 | 275 | 11kV | 47605 | 860 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 1260 Lisarow 11kV Feeder Panel #13 'Brush Rd' feeder tripped and locked out. Relays - C phase O/C, reclosing, timer, lockout. Field EFI's Nil 11kV failure into LV near PT11064, section of 11kV feeder from AB44898 to LK42861 to S14735 Ourimbah Campus South tee PT11064 Brush ourimbah 0.5 tee PT 11460 Brush Ourimbah 0.9. Emso checked cust premises and LV fuses checked. See 1906719,1906723,1906724 Withdrawn 1906006,1906027,1906028,1906029 | January | 2022 | 2022Q3 | 2022 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2022-01-29 | N | 55.3547 | N | 4 | N | N | 1.1101 | 39.4971 | 34788.3299
[7 empty] | 1121 | 14214 | 1906064 | 2022-01-30 09:23 | 2022-01-30 12:39 | 196 | 11kV | 6042 | 62 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220299 3 fault operations Earth Fault Tree cut down bringing down OHM between poles 6K-60034 & 6K-60035 Excluded OMS 1906064 | January | 2022 | 2022Q3 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2022-01-30 | N | 97.4516 | N | 3 | N | N | 1.1101 | 39.4971 | 4415.3154
[7 empty] | 1066 | 13665 | 1906104 | 2022-01-30 14:42 | 2022-01-30 18:00 | 198 | 11kV | 140439 | 1202 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn116 leichhardt Zone - Pnl.20 tripped on A & B phase IOC UG cable fault in frontline section of feeder See 1907232 1907233 1906114 | January | 2022 | 2022Q3 | 2022 | ZN116:PA20 | ZN116:PA20 | ZN00116/000020 | INNER WEST | UG | Not Veg | 2022-01-30 | N | 116.8378 | N | 3 | N | N | 1.1101 | 39.4971 | 102628.679
[7 empty] | 569 | 7056 | 1906150 | 2022-01-30 22:33 | 2022-01-30 23:26 | 53 | 11kV | 134596 | 2590 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN 15006 Dee Why West Panel 9 'Feeder has tripped' Signals 11kV Trip Relays: O/C IOC C Phase EFI Fault Check Field EFI's S16792, S17031 Cause of Interrruption - U/G Fault 11kV feeder from Sw/B at S17031 SW/B to SW/A S16733 See 1906776 & 1906778 1906150 withdrawn | January | 2022 | 2022Q3 | 2022 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2022-01-30 | N | 51.9676 | N | 3 | N | N | 1.1101 | 39.4971 | 98358.7869
[7 empty] | 516 | 6165 | 1907241 | 2022-01-31 16:32 | 2022-01-31 18:20 | 108 | 11kV | 43956 | 407 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15014 Mona Vale - Pnl.10 tripped on A & B phase IOC UG cable fault between CP21620 Sw/B to S16467 Sw/A See 1907241 1907242 1907243 | January | 2022 | 2022Q3 | 2022 | ZN15014:PA10 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2022-01-31 | N | 108 | N | 4 | N | N | 1.1101 | 39.4971 | 32121.7483
[7 empty] | 458 | 5657 | 1906348 | 2022-01-31 19:32 | 2022-01-31 21:28 | 116 | 11kV | 48217 | 1014 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn1099 Kogarah - Pnl.7 tripped & reclosed on: A & B phase OC @ S10925 Forest Water Board - Sw/A & Sw/B tripped on A phase OC OH mains twisted adj S10920 + 11kV Bond burnt off adj UGOH to S62206 Sw/A See 1907247 1907248 | January | 2022 | 2022Q3 | 2022 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | GEORGES RIVER | OH | Not Veg | 2022-01-31 | N | 47.5513 | N | 4 | N | N | 1.1101 | 39.4971 | 35235.5614
[7 empty] | 1645 | 19961 | 1906328 | 2022-01-31 17:41 | 2022-01-31 21:50 | 249 | 11kV | 158014 | 952 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn116 Leichhardt - Pnl.14 tripped on OC UG cable fault in frontline section of feeder See 1907245 1906332 | January | 2022 | 2022Q3 | 2022 | ZN116:PA14 | ZN116:PA14 | ZN00116/000014 | INNER WEST | UG | Not Veg | 2022-01-31 | N | 165.9811 | N | 4 | N | N | 1.1101 | 39.4971 | 115471.9706
[7 empty] | 137 | 1669 | 1906370 | 2022-01-31 23:20 | 2022-02-01 01:09 | 109 | 11kV | 5559 | 51 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 220306 section isolated to repair faulty LL Clamp "D" at sub 51175. Excluded oms 1906370 | January | 2022 | 2022Q3 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2022-01-31 | N | 109 | N | 4 | N | N | 1.1101 | 39.4971 | 4062.3532
[7 empty] | 425 | 5338 | 1906384 | 2022-02-01 03:24 | 2022-02-01 04:51 | 87 | 11kV | 157259 | 2017 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn 690 Campsie 11kV feeder panel #12 Woolcott St feeder tripped on: Relays: C phase timed O/C, EFI,fault check, #2 TX fault check Field EFI's S266,S8108,S35958,S7679,s2344,S1399,S4277,S4278 UG fault in section of 11kV feeder from S4278 (Sw/B) to S4049 (SW/A) to S8076 (SW/A) See 1907393,1907397 1906384 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN690:PA12 | ZN690:PA12 | ZN00690/000012 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-02-01 | N | 77.9668 | N | 11 | N | N | 1.1101 | 39.4971 | 114920.2388
[7 empty] | 1313 | 15956 | 1906406 | 2022-02-01 08:26 | 2022-02-01 09:15 | 49 | 11kV | 11996 | 1486 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn 36800 Waverly Panel 54 'S3348, S347' feeder tripped on: Relays:EF,EFI Field EFI's: 3348,8786,8526,48367 Scada EFIs :S77073 Section of feeder from S77073 Bronte Murray to S46848 Bronte Lugar has a suspect cbale fault. DMA created See 1907352 and 1907354 906406 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN36800:PA54 | ZN36800:PA54 | ZN36800/000054 | WAVERLEY | UG | Not Veg | 2022-02-01 | N | 8.0727 | N | 11 | N | N | 1.1101 | 39.4971 | 8766.323
[7 empty] | 484 | 5881 | 1906455 | 2022-02-01 10:28 | 2022-02-01 11:49 | 81 | 11kV | 73871 | 967 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9900 Menai Panel 8 'S9626 Hall Trumper' feeder tripped, reclosed and tripped on: Relays EF,IOC,EFI Signals 11kV Trip, GE,ZE Field EFI's S9626,S9398,S9708,S9551,S9341 Section of feeder between S9341 Sw/B to S9174 S/B has a suspect cable fault See1907176,1907180 1906455 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN9900:PA8 | ZN9900:PA8 | ZN09900/000008 | SUTHERLAND | UG | Not Veg | 2022-02-01 | N | 76.3919 | N | 11 | N | N | 1.1101 | 39.4971 | 53982.748
[7 empty] | 385 | 5056 | 1906481 | 2022-02-01 11:37 | 2022-02-01 13:02 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220311 C Phase DOLF : 10 Amp Excluded OMS 1906481 | February | 2022 | 2022Q3 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2022-02-01 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 80 | 971 | 1906393 | 2022-02-01 07:22 | 2022-02-01 15:00 | 457.8667 | 11kV | 25640.5333 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 220312 3 phase Mains down at pole 5O50061 | February | 2022 | 2022Q3 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2022-02-01 | N | 457.8667 | N | 11 | N | N | 1.1101 | 39.4971 | 18737.3455
[7 empty] | 436 | 5428 | 1906553 | 2022-02-01 15:53 | 2022-02-01 16:48 | 55 | 11kV | 104833 | 1926 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn7481 Darling Harbour - Pnl.14 tripped on: Earth Fault UG cable fault between S8986 Sw/B and S7946 Sw/A See 1907163 1907164 | February | 2022 | 2022Q3 | 2022 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2022-02-01 | N | 54.4304 | N | 11 | N | N | 1.1101 | 39.4971 | 76608.8643
[7 empty] | 313 | 4138 | 1906518 | 2022-02-01 14:20 | 2022-02-01 18:40 | 260 | 11kV | 1040 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | S9618 Cawarra Naco - 11kV/415V Tx tripped on Centre phase HV Fuse Cause not ascertained. Previous trip on same device 8/1/22 | February | 2022 | 2022Q3 | 2022 | ZN9550:PA27 | ZN9550:PA27 | ZN09550/000027 | SUTHERLAND | UG | Not Veg | 2022-02-01 | N | 260 | N | 11 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 286 | 3647 | 1906621 | 2022-02-01 18:17 | 2022-02-01 19:37 | 80 | 11kV | 97694 | 1235 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn129 Hunters Hill - Pnl.38 tripped on: A Phase IOC and Earth Fault UG cable fault between S7579 to S4078 See 1907140 1907141 | February | 2022 | 2022Q3 | 2022 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | UG | Not Veg | 2022-02-01 | N | 79.1045 | N | 11 | N | N | 1.1101 | 39.4971 | 71391.8937
[7 empty] | 1038 | 13185 | 1906626 | 2022-02-01 18:25 | 2022-02-01 20:23 | 118 | 11kV | 108149 | 974 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | Zn12660 Woy Woy - Pnl.16 tripped, reclosed & locked out on: A Phase OC Suspected UG cable fault between S18242 Sw/B and S18156 Sw/A See 1907131 1907132 | February | 2022 | 2022Q3 | 2022 | ZN12660:PA16 | ZN12660:PA16 | ZN12660/000016 | CENTRAL COAST | UG | Not Veg | 2022-02-01 | N | 111.0359 | N | 11 | N | N | 1.1101 | 39.4971 | 79032.0993
[7 empty] | 1104 | 13985 | 1906502 | 2022-02-01 12:58 | 2022-02-01 22:25 | 567 | 11kV | 18727 | 228 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn14891 Wyong - Pnl.6 tripped on: OC & EF Sw/B endbox fault at S.14209 Lucca bayer - repaired and returned to service See 1907125 1907126 | February | 2022 | 2022Q3 | 2022 | ZN14891:PA6 | ZN14891:PA6 | ZN14891/000006 | CENTRAL COAST | UG | Not Veg | 2022-02-01 | N | 82.136 | N | 11 | N | N | 1.1101 | 39.4971 | 13685.1392
[7 empty] | 1425 | 17543 | 1906639 | 2022-02-01 18:55 | 2022-02-02 01:10 | 375 | 11kV | 115694 | 880 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | Zn1673 Turramurra - Pnl.2 - tripped on B & C phase IOC Abnormal: LB2209 Closed with LB238 Open (DMA - HR Bond) UGOH between CP373 Sw/C and AB3019 tee PT1917 has cracked insulators and defective surge arrestors Delayed resoration to 3 PTs due to exisitng DMA See 1907118 1907121 | February | 2022 | 2022Q3 | 2022 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | Unknown | Unknown | 2022-02-01 | N | 131.4705 | N | 11 | N | N | 1.1101 | 39.4971 | 84545.7628
[7 empty] | 416 | 5288 | 1906693 | 2022-02-02 06:25 | 2022-02-02 07:39 | 74 | 11kV | 12429 | 1122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn10998 Rockdale - Pnl.28 tripped, reclosed and locked out on: Earth Fault (B-N) UG cable fault between S63452 Sw/A and S10854 Sw/A See 1907111 1907112 1907113 | February | 2022 | 2022Q3 | 2022 | ZN10998:PA28 | ZN10998:PA28 | ZN10998/000028 | BAYSIDE | UG | Not Veg | 2022-02-02 | N | 11.0775 | N | 11 | N | N | 1.1101 | 39.4971 | 9082.7466
[7 empty] | 297 | 3775 | 1906694 | 2022-02-02 06:28 | 2022-02-02 09:30 | 182 | 11kV | 364 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220321 A Phase DOLF : 10 Amp | February | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-02-02 | N | 182 | N | 11 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 157 | 1912 | 1906764 | 2022-02-02 09:51 | 2022-02-02 12:30 | 158.8167 | 11kV | 952.9 | 6 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | PT14507 Arundel Milina - Centre phase HDO blown Wet bark found on Tx tank and found no covering on Tx Bushings | February | 2022 | 2022Q3 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2022-02-02 | N | 158.8167 | N | 11 | N | N | 1.1101 | 39.4971 | 696.3512
[7 empty] | 498 | 5982 | 1906821 | 2022-02-02 12:16 | 2022-02-02 13:16 | 60 | 11kV | 1657 | 30 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn8000 Macquarie Park - Pnl.34 tripped on: Earth Fault S.35235 & S8849 EFIs found down on first attempt, Second attempt only S35235 UG cable fault between S35235 Sw/B and S8849 Sw/A See 1907104 1907105 | February | 2022 | 2022Q3 | 2022 | ZN8000:PA34 | ZN8000:PA34 | ZN08000/000034 | RYDE | UG | Not Veg | 2022-02-02 | N | 55.2333 | N | 11 | N | N | 1.1101 | 39.4971 | 1210.8867
[7 empty] | 479 | 5824 | 1906817 | 2022-02-02 11:50 | 2022-02-02 13:45 | 115 | 11kV | 19205 | 167 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Light | N | LID 220324 2 fault operations A & C Phase Overcurrent tree branch arcing across 2 phases of vertical CCT. | February | 2022 | 2022Q3 | 2022 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2022-02-02 | N | 115 | N | 11 | N | N | 1.1101 | 39.4971 | 14034.4475
[7 empty] | 108 | 1409 | 1906840 | 2022-02-02 13:04 | 2022-02-02 15:27 | 143 | 11kV | 2145 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | PT13268 Kiliby Durren 4.1 - Roadside HDO operated Fuse Fatigue | February | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2022-02-02 | N | 143 | N | 11 | N | N | 1.1101 | 39.4971 | 1567.5027
[7 empty] | 342 | 4756 | 1906860 | 2022-02-02 13:39 | 2022-02-02 16:51 | 192 | 11kV | 19165 | 171 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 220325 2 fault operations Earth Fault; Overcurrent Excluded OMS 1906860 | February | 2022 | 2022Q3 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2022-02-02 | N | 112.076 | N | 11 | N | N | 1.1101 | 39.4971 | 14005.2167
[7 empty] | 94 | 1206 | 1906913 | 2022-02-02 16:19 | 2022-02-02 17:30 | 71 | 11kV | 8905 | 995 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Zn12570 Avoca - Pnl.25 tripped & reclosed on A & B phase OC Roadside phase bond burnt off USL43253 See 1907191 1907192 | February | 2022 | 2022Q3 | 2022 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Not Veg | 2022-02-02 | N | 8.9497 | N | 11 | N | N | 1.1101 | 39.4971 | 6507.5113
[7 empty] | 567 | 7029 | 1906890 | 2022-02-02 15:21 | 2022-02-02 19:37 | 256 | 11kV | 8239 | 61 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC44604 Dog Trap Rd tripped, reclosed & locked out on: IOC & OC Tree brought down OH mains outside 716 Dog Trap Rd See 1907187 1907189 | February | 2022 | 2022Q3 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2022-02-02 | N | 135.0656 | N | 11 | N | N | 1.1101 | 39.4971 | 6020.8182
[7 empty] | 1663 | 20204 | 1906956 | 2022-02-02 19:28 | 2022-02-02 20:32 | 64 | 11kV | 62112 | 1884 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn12650 West Gosford - Pnl.13 tripped & reclosed on A & B phase IOC and Earth Fault iR62730 Manns Narra Creek tripped on OC Tree branch on OH mains near PT12886 See 1907185 1907186 | February | 2022 | 2022Q3 | 2022 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2022-02-02 | N | 32.9682 | N | 11 | N | N | 1.1101 | 39.4971 | 45389.6176
[7 empty] | 1101 | 13981 | 1906972 | 2022-02-02 22:39 | 2022-02-02 23:33 | 54 | 11kV | 25110 | 465 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.15 tripped on Earth Fault UG cable fault in front line section of feeder | February | 2022 | 2022Q3 | 2022 | ZN188:PA15 | ZN188:PA15 | ZN00188/000015 | SYDNEY | UG | Not Veg | 2022-02-02 | N | 54 | N | 11 | N | N | 1.1101 | 39.4971 | 18349.6474
[7 empty] | 129 | 1592 | 1906978 | 2022-02-03 03:12 | 2022-02-03 04:46 | 94 | 11kV | 12972 | 138 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 220330 B Phase DOLF : 40 Amp Blown Bph arrestor, sub interconnected. Excluded OMS 1906978 CC1: 22-"Refer to SOp" | February | 2022 | 2022Q3 | 2022 | 228:85410 | 228:85410 | ZN00228/085410 | NEWCASTLE | OH | Not Veg | 2022-02-03 | N | 94 | N | 6 | N | N | 1.1101 | 39.4971 | 9479.555
[7 empty] | 1105 | 13986 | 1907063 | 2022-02-03 11:17 | 2022-02-03 11:56 | 39 | 11kV | 32370 | 830 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12570 Avoca 11kV Panel No14 Tripped and locked out. Protection relay operations at Zone Sub B&C phase OC EFI,Recloser timer, Reclose lockout Field EFI operations S49887 Palm Branch on O/H mains adj to PT 14162 Terrigal Drive Junction. Branch removed and feeder restored | February | 2022 | 2022Q3 | 2022 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Veg | 2022-02-03 | N | 39 | N | 6 | N | N | 1.1101 | 39.4971 | 23655.0412
[7 empty] | 834 | 10268 | 1907170 | 2022-02-03 14:47 | 2022-02-03 16:08 | 81 | 11kV | 68346 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN12570 Avoca 11kV panel no34 tripped on Relays - Basler relay 50T BC, IOC B+C phase Trip LED, Rec lockout Tree Branch contact See 1908249,1908250 1907170,1907184 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2022-02-03 | N | 80.3126 | N | 6 | N | N | 1.1101 | 39.4971 | 49945.2409
[7 empty] | 664 | 8559 | 1907228 | 2022-02-03 16:13 | 2022-02-03 19:00 | 167 | 11kV | 167 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 220334 Single phase Broken Live Line Lead Excluded OMS 1907228 | February | 2022 | 2022Q3 | 2022 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2022-02-03 | N | 167 | N | 6 | N | N | 1.1101 | 39.4971 | 122.0387
[7 empty] | 1514 | 18587 | 1907153 | 2022-02-03 16:31 | 2022-02-03 19:46 | 195 | 11kV | 10140 | 52 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220333 BROKEN 33KV INSULATOR AT POLE DP80055 LEFT 33KV ON X ARM. 11kV had to be interrupted to allow access. No protection operation. Excluded OMS 1907153, 1907294 | February | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2022-02-03 | N | 195 | N | 6 | N | N | 1.1101 | 39.4971 | 7410.0129
[7 empty] | 100 | 1257 | 1907301 | 2022-02-03 21:08 | 2022-02-03 23:33 | 145 | 11kV | 86271 | 2090 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Zn12610 Long Jetty - Pnl.10 tripped on SEF Bond burnt off 3 poles from LB61730 (pole WL-1881) See 1910411 1910414 1910415 | February | 2022 | 2022Q3 | 2022 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2022-02-03 | N | 41.278 | N | 6 | N | N | 1.1101 | 39.4971 | 63044.3022
[7 empty] | 166 | 2146 | 1907341 | 2022-02-04 07:45 | 2022-02-04 10:46 | 181 | 11kV | 543 | 3 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Rain Light | N | LID 220337 Broken stay at sub 50134 | February | 2022 | 2022Q3 | 2022 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2022-02-04 | N | 181 | N | 4 | N | N | 1.1101 | 39.4971 | 396.8084
[7 empty] | 1091 | 13928 | 1907439 | 2022-02-04 11:27 | 2022-02-04 13:55 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220338 Single phase DOLF : 10 Amp Excluded OMS 1907439 | February | 2022 | 2022Q3 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2022-02-04 | N | 148 | N | 4 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 120 | 1502 | 1907499 | 2022-02-04 14:28 | 2022-02-04 16:45 | 137.0833 | 11kV | 80742.0833 | 589 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 35370 Galston - 11kV CB No10 'Galston Aux No2' tripped, reclosed & locked out Relays: IOC ABC Phase OC ABC Phase EFI Signals:11kV Trip Field EFI's Nil Tree Branch on OH mains near PT 1983 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2022-02-04 | N | 137.0833 | N | 4 | N | N | 1.1101 | 39.4971 | 59003.933
[7 empty] | 979 | 12012 | 1907586 | 2022-02-04 21:50 | 2022-02-04 22:25 | 35 | 11kV | 175 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220340 Wire off pin insulator pole 6N-80066 | February | 2022 | 2022Q3 | 2022 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2022-02-04 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 1216 | 15030 | 1907611 | 2022-02-05 05:45 | 2022-02-05 13:37 | 472 | 11kV | 12314 | 47 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 220345 2 fault operations Single phase Excluded OMS 1907611 | February | 2022 | 2022Q3 | 2022 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2022-02-05 | N | 262 | N | 8 | N | N | 1.1101 | 39.4971 | 8998.708
[7 empty] | 457 | 5656 | 1907700 | 2022-02-05 14:36 | 2022-02-05 16:20 | 104 | 11kV | 23611 | 237 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN10999 Kogarah 11kV panel 2 'English Railway No2' feeder tripped on: Relays EF,EFI, Field EFI's S77890, S10116 11kV UG fault from S10116 O'Keefes Kensington SW/B to S10316 Wicks Kensington No1 SW/A to S10557 Post Office Lane Sw/A See 1908686 1907700 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN10999:PA2 | ZN10999:PA2 | ZN10999/000002 | GEORGES RIVER | UG | Not Veg | 2022-02-05 | N | 99.6245 | N | 8 | N | N | 1.1101 | 39.4971 | 17254.2224
[7 empty] | 1026 | 12984 | 1907601 | 2022-02-05 03:19 | 2022-02-05 16:30 | 791 | 11kV | 188192 | 576 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | At ZN 35800 Bankstown 11kV Panel No19 Feeder tripped on Relays:A & B phase IOC Trip Field EFI's S6696, S79481,S3690,S7104,S1336 Vehicle hit pole section of 11kV feeder from LB3293 to Sw/B S5519 Banks Davies tee PT2274 Jayelem Davies Multiple DMA'S 1/S3514 to S6413, closed SW/B @ S2468 2/S5723 to S7865 SW/B @S5611 closed See 1908999,1909002,1909003,1907608 Withdrawn 1907601,1907602,1907612,1907609, | February | 2022 | 2022Q3 | 2022 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-02-05 | N | 326.7222 | N | 8 | N | N | 1.1101 | 39.4971 | 137525.1629
[7 empty] | 1195 | 14800 | 1907708 | 2022-02-05 15:09 | 2022-02-05 17:30 | 141 | 11kV | 130812 | 1053 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 220351 Isolated 11kV UG cable fault in Railway St Cooks Hill Excluded OMS 1907708, 1907717 | February | 2022 | 2022Q3 | 2022 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | UG | Not Veg | 2022-02-05 | N | 124.2279 | N | 8 | N | N | 1.1101 | 39.4971 | 95593.5513
[7 empty] | 541 | 6502 | 1907697 | 2022-02-05 16:53 | 2022-02-05 17:42 | 49 | 11kV | 784 | 16 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220350 Broken tie on SWER line on pole FD30127 Excluded OMS 1907697 1907723. | February | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2022-02-05 | N | 49 | N | 8 | N | N | 1.1101 | 39.4971 | 572.9241
[7 empty] | 1658 | 20153 | 1907726 | 2022-02-05 17:26 | 2022-02-05 19:45 | 139 | 11kV | 278 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220352 A Phase DOLF : 20 Amp Excluded OMS 1907729 | February | 2022 | 2022Q3 | 2022 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2022-02-05 | N | 139 | N | 8 | N | N | 1.1101 | 39.4971 | 203.1542
[7 empty] | 967 | 11782 | 1907757 | 2022-02-05 22:20 | 2022-02-05 23:55 | 95 | 11kV | 40840 | 660 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Fdr 74119 tripped on IOC EF and Aph IOC on tryback (maloperation email sent to L Archer) UG cable fault between Sw B Chablis Close sub 78139 and Sw 69226 Lexia St sub. DQ Excluded OMS 1907757 | February | 2022 | 2022Q3 | 2022 | 801:74119 | 801:74119 | ZN00801/074119 | MUSWELLBROOK | UG | Not Veg | 2022-02-05 | N | 61.8788 | N | 8 | N | N | 1.1101 | 39.4971 | 29844.6674
[7 empty] | 1267 | 15477 | 1907742 | 2022-02-05 19:03 | 2022-02-06 00:55 | 351.7667 | 11kV | 4929.6667 | 20 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | No Weather Impact | N | ## Tree fell through 11kV and broke LV xarm at pole KR-30085. Rec 42360 tripped on EF. Checked for possible HV into LV DQ No LID report | February | 2022 | 2022Q3 | 2022 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2022-02-05 | N | 246.4833 | N | 8 | N | N | 1.1101 | 39.4971 | 3602.455
[7 empty] | 381 | 5043 | 1907771 | 2022-02-06 06:57 | 2022-02-06 08:42 | 105 | 11kV | 98198 | 1172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN129 Hunters Hill 11kV feeder Panel No52 'Pittwater Thompson etc' tripped on: Relays IOC trip B phase O/C E/F, EFI Field EFI's S26209,S47499,S8287,S5268 UG cable fault in section of 11kV feeder from S5268 Boronia Park (SW/A) to S78102 Burton Linley (SW/A) to S4372 Barons Montefiore No1 (SW/A) See 1908719,1908722, 190771,1907781 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN129:PA52 | ZN129:PA52 | ZN00129/000052 | LANE COVE | UG | Not Veg | 2022-02-06 | N | 83.7867 | N | 3 | N | N | 1.1101 | 39.4971 | 71760.202
[7 empty] | 75 | 927 | 1907877 | 2022-02-06 17:11 | 2022-02-06 19:35 | 144 | 11kV | 720 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220356 A & B Phase DOLF : 20 Amp Tree on mains at SM-40120. excluded oms 1907877 | February | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2022-02-06 | N | 144 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 571 | 7103 | 1907905 | 2022-02-06 22:06 | 2022-02-06 23:35 | 88.65 | 11kV | 354.6 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | A and B phase dolf 16A no cause found. Daniel Thompson to refer to depot for detailed patrol in daylight as this has happened a number of times according to customer. DQ No LID | February | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2022-02-06 | N | 88.65 | N | 3 | N | N | 1.1101 | 39.4971 | 259.1312
[7 empty] | 874 | 10825 | 1907912 | 2022-02-07 01:25 | 2022-02-07 03:22 | 117 | 11kV | 11877 | 113 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At ZN14143 Somersby panel 12 CP 44633 Phillips Gingurra' feeder tripped on Relays (Initial) A Protection : A phase, Trip, Neutral, EF B Protection: OC, EF,EFI Field EFI's CP 44633 Relays (After first close attempt) A Protection: Nil B Protection: A & B phase IOC,EF,IOC,EFI Filed EFI's : CP 44633 11kV UGOH section of feeder from CP44633 Phillips Gindurra to AB 44598 has blown surge arrestors. 1907912 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN14143:PA12 | ZN14143:PA12 | ZN14143/000012 | CENTRAL COAST | OH | Not Veg | 2022-02-07 | N | 105.1062 | N | 8 | N | N | 1.1101 | 39.4971 | 8679.3613
[7 empty] | 611 | 7800 | 1907913 | 2022-02-07 02:59 | 2022-02-07 04:59 | 120 | 11kV | 57840 | 482 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 9550 Gwawley Bay panel 33 'S9177 Bellgrave Bellinger' tripped on: Relays: Earth fault trip Field EFI's: S9177, S9145,S9470,S9202,S9476,S9486 Delay in restoration due to only 1 Dop in South area. Dop was sent from North. Wet tree branch removed from PT.9451 Woodlands Rd | February | 2022 | 2022Q3 | 2022 | ZN9550:PA33 | ZN9550:PA33 | ZN09550/000033 | SUTHERLAND | OH | Veg | 2022-02-07 | N | 120 | N | 8 | N | N | 1.1101 | 39.4971 | 42267.766
[7 empty] | 1072 | 13778 | 1907914 | 2022-02-07 03:47 | 2022-02-07 05:22 | 95 | 11kV | 24415 | 257 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At Zn 14891 Wyong, panel 19 "S.12636 Pacific Howarth" feeder tripped, reclosed and tripped on: Relays: 51ABC (ABC phase Timed OC), Fault Check, EFI, Reclose Timing, Lockout Field EFIs: S.12636 Ex Zn 14891 Wyong, ex panel 19 "S.12636 Pacific Howarth" feeder, section of feeder from S.12636 Pacific Howarth to AB 40001 tee PT 14979 Lou Gardiner pacific has suspect damage. Dop to patrol in golf course during daylight hours. | February | 2022 | 2022Q3 | 2022 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | OH | Veg | 2022-02-07 | N | 95 | N | 8 | N | N | 1.1101 | 39.4971 | 17841.7619
[7 empty] | 1440 | 17741 | 1907915 | 2022-02-07 03:47 | 2022-02-07 09:01 | 314 | 11kV | 160286 | 553 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At ZN 14891 Wyong Panel 20 'Warnervale West Railway' fedder tripped reclosed and tripped on Relays:51A (A phase timed OC) Fault Check, EFI, Reclose timing, lockout Field EFI's Nil HDO operated at PT13927 Cause not ascertained See 1908510,1908513,19085111908512,1908508 1907915,1907914 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2022-02-07 | N | 289.8481 | N | 8 | N | N | 1.1101 | 39.4971 | 117132.2812
[7 empty] | 448 | 5513 | 1907927 | 2022-02-07 06:36 | 2022-02-07 11:30 | 294 | 11kV | 294 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | At PT14591 George Down Nanuandi No1 Centre and Roadside amp HDO operated Section of 11kV feeder Panel No8 Kulnura @ ZN12630 Peats Ridge Cause not ascertained 1907927 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-02-07 | N | 294 | N | 8 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 1205 | 14953 | 1908103 | 2022-02-07 15:41 | 2022-02-07 18:30 | 169 | 11kV | 507 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Wind Strong | N | LID 220358 A Phase Broken LL clamp Excluded OMS 1908103 | February | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-02-07 | N | 169 | N | 8 | N | N | 1.1101 | 39.4971 | 370.5006
[7 empty] | 44 | 581 | 1908028 | 2022-02-07 11:38 | 2022-02-07 19:00 | 442 | 11kV | 17486 | 98 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | REC44995 Kulnura tripped & reclosed on IOC OH mains down between USL42325, PT13323 & PT12029 See 1910417 1910418 | February | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2022-02-07 | N | 178.4286 | N | 8 | N | N | 1.1101 | 39.4971 | 12778.2531
[7 empty] | 1350 | 16484 | 1908153 | 2022-02-07 19:42 | 2022-02-07 21:21 | 99 | 11kV | 105003 | 1126 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn965 Pennant Hills - Pnl.4 tripped on Earth Fault and A Phase OC UG cable fault in front line section of feeder | February | 2022 | 2022Q3 | 2022 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2022-02-07 | N | 93.2531 | N | 8 | N | N | 1.1101 | 39.4971 | 76733.0953
[7 empty] | 33 | 417 | 1908168 | 2022-02-08 00:37 | 2022-02-08 03:00 | 143.15 | 11kV | 2433.55 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | A & B ph 31A no cause found. No LID DQ | February | 2022 | 2022Q3 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2022-02-08 | N | 143.15 | N | 3 | N | N | 1.1101 | 39.4971 | 1778.3666
[7 empty] | 1116 | 14083 | 1908274 | 2022-02-08 12:39 | 2022-02-08 14:37 | 118 | 11kV | 2006 | 17 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220360 Bat across mains pole FS 73506 Excluded OMS 1908287 | February | 2022 | 2022Q3 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2022-02-08 | N | 118 | N | 3 | N | N | 1.1101 | 39.4971 | 1465.9256
[7 empty] | 1599 | 19496 | 1907947 | 2022-02-08 19:43 | 2022-02-08 21:20 | 96.5333 | 11kV | 7336.5333 | 76 | HV | Animal Bird | Animal | Fuse | Unplanned | No Weather Impact | N | Ex Zn 9550 Gwawley Bay, ex panel 33 "S.9177 Belgrave Bellinger" feeder, PT 9451 Woodlands Rd tripped on: HDO: Road side | February | 2022 | 2022Q3 | 2022 | ZN9550:PA33 | ZN9550:PA33 | ZN09550/000033 | SUTHERLAND | OH | Not Veg | 2022-02-08 | N | 96.5333 | N | 3 | N | N | 1.1101 | 39.4971 | 5361.3222
[7 empty] | 1345 | 16367 | 1908469 | 2022-02-09 11:36 | 2022-02-09 12:45 | 69 | 11kV | 138 | 2 | HV | Animal Goanna | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220364 Single phase DOLF : 10 Amp GOANNA CONTACTED MAINS Excluded OMS 1908469 | February | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2022-02-09 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 983 | 12036 | 1909486 | 2022-02-09 22:34 | 2022-02-09 23:40 | 66 | 11kV | 266 | 215 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | NOTE - Abnormal switching for NAR #88519 Closed LB2063 Opened LB 46975 11 kV Rec 555 Acadia park tripped and reclosed Section of 11kV feeder panel no4 Galston Aux No1 feeder Relays E/f Field F/D @ LB62108 Interrupted from LB 62108 to allow Dop safe removal @2339 Possum caused flashover at LB62108 on outgoing side See 1909486,1909488 | February | 2022 | 2022Q3 | 2022 |  |  |  | HORNSBY | OH | Not Veg | 2022-02-09 | N | 1.2372 | N | 2 | N | N | 1.1101 | 39.4971 | 194.385
[7 empty] | 908 | 11199 | 1908642 | 2022-02-10 08:28 | 2022-02-10 12:20 | 232 | 11kV | 13456 | 58 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 220367 A Phase LLC lead fell off. excluded oms 1908642 | February | 2022 | 2022Q3 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2022-02-10 | N | 232 | N | 9 | N | N | 1.1101 | 39.4971 | 9833.2479
[7 empty] | 870 | 10812 | 1908684 | 2022-02-10 10:56 | 2022-02-10 13:50 | 174 | 11kV | 174 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 220368 LLC lead fell off Excluded oms 1908684 | February | 2022 | 2022Q3 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2022-02-10 | N | 174 | N | 9 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 99 | 1256 | 1908733 | 2022-02-10 15:30 | 2022-02-10 16:00 | 30 | 11kV | 90 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220370 isolated to fix OHM off pin at 9J-30001 Excluded oms 1908733, 1908753 | February | 2022 | 2022Q3 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | MUSWELLBROOK | OH | Not Veg | 2022-02-10 | N | 30 | N | 9 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 1114 | 14078 | 1908773 | 2022-02-10 16:02 | 2022-02-10 18:01 | 119 | 11kV | 263245 | 2226 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At Zn 35800 Bankstown Panel 14 tripped on: Relays A-B-C phase IOC, EFI Field EFIs S47454, S5762 Cause not ascertained See 1910365,1910369 1908773 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-02-10 | N | 118.2592 | N | 9 | N | N | 1.1101 | 39.4971 | 192371.6816
[7 empty] | 656 | 8485 | 1908817 | 2022-02-10 17:49 | 2022-02-10 19:17 | 88 | 11kV | 5368 | 61 | HV | Vegetation Grow In | Vegetation | UGOH | Unplanned | No Weather Impact | N | LID 220371 No protection operations. A vine has grown up the pole and is now around the 11kV UGOH terminations. Excluded OMS 1908817. | February | 2022 | 2022Q3 | 2022 | 258:80790 | 258:80790 | ZN00258/080790 | NEWCASTLE | OH | Veg | 2022-02-10 | N | 88 | N | 9 | N | N | 1.1101 | 39.4971 | 3922.7761
[7 empty] | 1152 | 14483 | 1908865 | 2022-02-10 23:13 | 2022-02-11 00:20 | 67 | 11kV | 50534 | 995 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | At ZN12570 Avoca 11kV feeder Panel No25 'Hillcrest St' feeder tripped and reclosed and locked out on: Relays: E/F, EFI, auto-close, lockout Field EFI's:NIL 11kV UGOH fail on pole WL917 on section of 11kV feeder from LB40475 tee PT12842 Havenview Hillcrest to SWB @ S48510 Havenview Junction. See 1909534,1909535 1908872,1908865 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | Unknown | Unknown | 2022-02-10 | N | 50.7879 | N | 9 | N | N | 1.1101 | 39.4971 | 36928.7567
[7 empty] | 1415 | 17411 | 1908796 | 2022-02-10 16:59 | 2022-02-11 01:11 | 491.8 | 11kV | 38966.8 | 2299 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At ZN 15002 Narrabeen Panel 2L tripped and reclosed Relay A&B O/C reclose lockout, frame leakage fault check and EFI. Signals 11kV Trip Field EFI's S16499 At ZN 15002 Narrabeen Panel 8 Relays C phase timed O/C, fault check and EFI Field EFI's CP24276,S47436,S15366 Electrical storm common AB26122 between panel 8 and 2 both feeders tripped at the same tim but Panel 2 has reclose function on the panel protection. Also LV//'s failed at PT15306 Cause of Interruption - Weather related See 1908808,1908837,1908796 | February | 2022 | 2022Q3 | 2022 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2022-02-10 | N | 16.9495 | N | 9 | N | N | 1.1101 | 39.4971 | 28475.7881
[7 empty] | 998 | 12276 | 1908845 | 2022-02-10 22:35 | 2022-02-11 02:59 | 264 | 11kV | 312623 | 1468 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At ZN847 Hornsby Panel 47 tripped, reclosed, tripped and locked out on A B and C phase OC Cause: unknown/weather related Abnormal Switching: Hornbsy Pa45 Open Bonds, CP1972 Closed, CP62109 Closed, CP2920 Open See OMS 1910928/930/931/932/933/934 1908845 1908846 | February | 2022 | 2022Q3 | 2022 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2022-02-10 | N | 212.9584 | N | 9 | N | N | 1.1101 | 39.4971 | 228455.6676
[7 empty] | 1555 | 19065 | 1909552 | 2022-02-11 01:21 | 2022-02-11 03:15 | 114 | 11kV | 3413 | 2313 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN9700 Kirrawee 11kV feeder panel No17 'Hotman Badto feeder tripped and reclosed Relays: A phase timed and Instataneous, lockout timer, fault check, EFI Field EFI's: NIL On patrol of feeder DOp found a coat hanger adjacent to PT 9543 on pole SU12772, switched section of feeder and interrupted PT 9543 from 0255 to 0315 to allow safe removal.' See 1909552,1909567 | February | 2022 | 2022Q3 | 2022 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Not Veg | 2022-02-11 | N | 1.4756 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2494.1197
[7 empty] | 122 | 1521 | 1908891 | 2022-02-11 03:57 | 2022-02-11 08:37 | 280.1 | 11kV | 4761.7 | 17 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220376 31 Amp, Phases A & B. Line DOLF Flying Fox across 2 phases SOP APPS S DOP RIDING M | February | 2022 | 2022Q3 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2022-02-11 | N | 280.1 | N | 27 | Y | Y | 1.1101 | 39.4971 | 3479.7099
[7 empty] | 227 | 2761 | 1908862 | 2022-02-10 22:56 | 2022-02-11 09:40 | 644 | 11kV | 45080 | 70 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Unknown | Unplanned | Lightning | N | Ex Zn 15013 Terrey Hills Ex Panel 10 Recloser 20852 Sectionalizer 49122 locked open Relays ABC phase O/C Unable to find cause | February | 2022 | 2022Q3 | 2022 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2022-02-10 | N | 644 | N | 9 | N | N | 1.1101 | 39.4971 | 32943.1344
[7 empty] | 1396 | 17093 | 1908889 | 2022-02-11 03:27 | 2022-02-11 10:40 | 433 | 11kV | 12608 | 42 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 220374 Sub 71468 pole fire has been cut away no customers currently takign supply from this sub depot staff to arrange repairs. Excluded OMS 1908889 | February | 2022 | 2022Q3 | 2022 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2022-02-11 | N | 300.1905 | N | 27 | Y | Y | 1.1101 | 39.4971 | 9213.5545
[7 empty] | 859 | 10629 | 1909010 | 2022-02-11 12:09 | 2022-02-11 12:25 | 16 | 11kV | 80 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220379 Replaced C phase 10 amp HV DOF at sub 8185. Supply restored at 1225 hrs. A phase 242v, B phase 242v, C phase 242 v. 420 volts between phases. Storm related. Thunderstorm SOP APPS S DOP McINTOSH G | February | 2022 | 2022Q3 | 2022 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2022-02-11 | N | 16 | N | 27 | Y | Y | 1.1101 | 39.4971 | 58.4616
[7 empty] | 1614 | 19631 | 1909660 | 2022-02-11 14:09 | 2022-02-11 14:19 | 10 | 11kV | 500 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220386 Thunderstorm Overcurrent SOP DOOLAN P | February | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2022-02-11 | N | 10 | N | 27 | Y | Y | 1.1101 | 39.4971 | 365.3853
[7 empty] | 1546 | 18925 | 1909073 | 2022-02-11 14:18 | 2022-02-11 14:58 | 40 | 11kV | 12280 | 307 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | At ZN 14144 Wamberal 11kV Panel 5 tripped Relays AR L/O IOC 'A&B' phase Siganls 11kV trip Tree/branch on OH mains | February | 2022 | 2022Q3 | 2022 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2022-02-11 | N | 40 | N | 27 | Y | Y | 1.1101 | 39.4971 | 8973.8618
[7 empty] | 624 | 8033 | 1909222 | 2022-02-11 14:20 | 2022-02-11 16:16 | 116 | 11kV | 7888 | 68 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 220448 Replace damage insulator at DG-40022. Excluded oms 1909222, 315, 328 & 315. | February | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2022-02-11 | N | 116 | N | 27 | Y | Y | 1.1101 | 39.4971 | 5764.3177
[7 empty] | 856 | 10597 | 1909075 | 2022-02-11 14:44 | 2022-02-11 16:50 | 126 | 11kV | 126 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220411 Replaced blown 10 amp Single Phase, H.V fuse on Pt sub 25389. Supply restored at 1650. Single phase sub. Cause of fuse to blow, storms in the area. SOP APPS S DOP ANDRUSCHTHAK M | February | 2022 | 2022Q3 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-02-11 | N | 126 | N | 27 | Y | Y | 1.1101 | 39.4971 | 92.0771
[7 empty] | 1597 | 19489 | 1909107 | 2022-02-11 15:41 | 2022-02-11 17:48 | 127 | 11kV | 76327 | 601 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220417 Phase B & C Overcurrent Thunderstorm Patrolled, No Fault Found SOP TOMLINSON M DOP BUDDEN J | February | 2022 | 2022Q3 | 2022 | 202:34253 | 202:34253 | ZN00202/034253 | NEWCASTLE | OH | Veg | 2022-02-11 | N | 127 | N | 27 | Y | Y | 1.1101 | 39.4971 | 55777.5203
[7 empty] | 125 | 1553 | 1909110 | 2022-02-11 15:56 | 2022-02-11 17:50 | 114 | 11kV | 228 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220418 Found A phase H.V fuse blown at PT sub 77905. Replaced 16 amp fuse. Supply restored at 1750. Cause for fuse to blow was storms in the area. SOP APPS S DOP ANDRUSCHTHAK M | February | 2022 | 2022Q3 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-02-11 | N | 114 | N | 27 | Y | Y | 1.1101 | 39.4971 | 166.6157
[7 empty] | 1582 | 19324 | 1909116 | 2022-02-11 16:00 | 2022-02-11 18:07 | 127 | 11kV | 155702 | 1226 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220419 Phase C Overcurrent Thunderstorm No fault found SOP KEEGAN T DOP KEEN A | February | 2022 | 2022Q3 | 2022 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Veg | 2022-02-11 | N | 127 | N | 27 | Y | Y | 1.1101 | 39.4971 | 113782.4292
[7 empty] | 1192 | 14786 | 1909130 | 2022-02-11 16:29 | 2022-02-11 18:45 | 135.5667 | 11kV | 7862.8667 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220421 Thunderstorm 50 Amp, Phase A, Substation DOLF SOP KEEGAN T DOP KEEN A | February | 2022 | 2022Q3 | 2022 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Veg | 2022-02-11 | N | 135.5667 | N | 27 | Y | Y | 1.1101 | 39.4971 | 5745.951
[7 empty] | 1136 | 14326 | 1909126 | 2022-02-11 16:21 | 2022-02-11 19:10 | 169 | 11kV | 507 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220422 Thunderstorm 10 Amp, Phase C, Substation DOLF SOP ARLITSCH E DOP BAXTER M | February | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-02-11 | N | 169 | N | 27 | Y | Y | 1.1101 | 39.4971 | 370.5006
[7 empty] | 1211 | 15007 | 1909125 | 2022-02-11 16:20 | 2022-02-11 19:35 | 195 | 11kV | 390 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220423 Thunderstorm 10 Amp, Phase A, Substation DOLF SOP ARLITSCH E DOP BAXTER M | February | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-02-11 | N | 195 | N | 27 | Y | Y | 1.1101 | 39.4971 | 285.0005
[7 empty] | 1472 | 18191 | 1909175 | 2022-02-11 18:25 | 2022-02-11 20:05 | 100.3833 | 11kV | 100.3833 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220426 Thunderstorm 10 Amp, Single Phase, Substation DOLF SOP ARLITSCH E DOP BAXTER M | February | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2022-02-11 | N | 100.3833 | N | 27 | Y | Y | 1.1101 | 39.4971 | 73.3572
[7 empty] | 905 | 11139 | 1909141 | 2022-02-11 16:38 | 2022-02-11 20:20 | 222 | 11kV | 222 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220424 Thunderstorm 10 Amp, Single Phase Substation DOLF Refer to oms 1909141 Blown LAs SOP ARLITSCH E DOP NORTON D | February | 2022 | 2022Q3 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2022-02-11 | N | 222 | N | 27 | Y | Y | 1.1101 | 39.4971 | 162.2311
[7 empty] | 450 | 5527 | 1909193 | 2022-02-11 19:23 | 2022-02-11 20:45 | 82 | 11kV | 39517 | 483 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | IR 48838 Yarramalong Maitland 1.2 tripped Relays: L/O, OC trip Section of 11kV Panel 12 'Yarramalong' feeder at ZN 14891 Wyong Burnt tree branch found at 313 Yarramalong Rd See1909822,190824 1909193 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2022-02-11 | N | 81.8157 | N | 27 | Y | Y | 1.1101 | 39.4971 | 28877.858
[7 empty] | 350 | 4812 | 1909091 | 2022-02-11 13:30 | 2022-02-11 21:30 | 480 | 11kV | 1440 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220428 Found with blown dolfs 10A cut away HVSA. requires replacement HVSA.JMH Thunderstorm 10 Amp, Substation DOLFs SOP HUBY J DOP WILLIAMS S | February | 2022 | 2022Q3 | 2022 | 229:34983 | 229:34983 | ZN00229/034983 | PORT STEPHENS | OH | Not Veg | 2022-02-11 | N | 480 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 323 | 4338 | 1909128 | 2022-02-11 16:23 | 2022-02-11 22:36 | 373 | 11kV | 24275 | 101 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220429 3 phase SEF Trip Sensitive Earth Fault Excluded OMS 1909128 | February | 2022 | 2022Q3 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2022-02-11 | N | 240.3465 | N | 27 | Y | Y | 1.1101 | 39.4971 | 17739.454
[7 empty] | 372 | 4956 | 1909056 | 2022-02-11 22:26 | 2022-02-11 22:56 | 30 | 11kV | 10320 | 344 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220431 Thunderstorm OMS 1909056, 1909225 Tree branch on 11kv Mains JR84304.JMH deenergised fdr to remove" SOP HUBY J DOP MILLS A | February | 2022 | 2022Q3 | 2022 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2022-02-11 | N | 30 | N | 27 | Y | Y | 1.1101 | 39.4971 | 7541.5516
[7 empty] | 175 | 2284 | 1909188 | 2022-02-11 19:05 | 2022-02-12 00:15 | 310 | 11kV | 23611 | 181 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | No Weather Impact | N | LID 220434 Lightning hit poles JV-91752 & JV-91664 Excluded OMS 1909151 | February | 2022 | 2022Q3 | 2022 | 204:82689 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Not Veg | 2022-02-11 | N | 130.4475 | N | 27 | Y | Y | 1.1101 | 39.4971 | 17254.2224
[7 empty] | 1308 | 15926 | 1909121 | 2022-02-11 16:14 | 2022-02-12 01:05 | 531 | 11kV | 59472 | 112 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220433 Blown B Phase DOLF : 63 Amp Blown B phase 11kV LA Excluded OMS 1909121 | February | 2022 | 2022Q3 | 2022 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2022-02-11 | N | 531 | N | 27 | Y | Y | 1.1101 | 39.4971 | 43460.3835
[7 empty] | 1322 | 16151 | 1909221 | 2022-02-11 21:07 | 2022-02-12 01:05 | 238 | 11kV | 51597 | 1422 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 220432 1 fault operation Blown insulators 11kV pole JV-40011 Reclose was off on feeder due to isolating another PT. DOP unable to reset targets Sw 8689 please investigate Excluded OMS 1909221 | February | 2022 | 2022Q3 | 2022 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | OH | Not Veg | 2022-02-11 | N | 36.2848 | N | 27 | Y | Y | 1.1101 | 39.4971 | 37705.5657
[7 empty] | 1189 | 14777 | 1908968 | 2022-02-11 10:24 | 2022-02-12 03:00 | 996 | 11kV | 203563.9 | 1381 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | At ZN9037 Miranda Zone 11kV panel 16 'S9780 Sylvania Dwyer' reclosed and tripped on Signal: Zone Earth, Group Eart No3 TX, 11 kV Trip Relays: Earth Fault time, Timing, Loclout, Sealing Contactor Field EFIs S9780, S79727,S79392,S47294,S77093,S77621,S9133,S9378,S9436 Pole Defective/Failure See 1909799,1909801 Withdrawn 1908949,1908968 | February | 2022 | 2022Q3 | 2022 | ZN9037:PA16 | ZN9037:PA16 | ZN09037/000016 | SUTHERLAND | OH | Not Veg | 2022-02-11 | N | 147.4033 | N | 27 | Y | Y | 1.1101 | 39.4971 | 148758.494
[7 empty] | 1095 | 13967 | 1909241 | 2022-02-12 03:42 | 2022-02-12 05:47 | 125 | 11kV | 12561 | 173 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220442 B Fault detector indicated at Sw 83495 Excluded OMS 1909241 | February | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2022-02-12 | N | 72.6069 | N | 8 | N | N | 1.1101 | 39.4971 | 9179.2083
[7 empty] | 1311 | 15948 | 1909249 | 2022-02-12 07:12 | 2022-02-12 10:10 | 178 | 11kV | 356 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220443 supply back on 5A, A Phase, dolf replaced Previous Storm SOP CARSON S DOP BAXTER M | February | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-02-12 | N | 178 | N | 8 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 1390 | 17043 | 1909263 | 2022-02-12 08:34 | 2022-02-12 10:25 | 111 | 11kV | 111 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220444 Previous Storm 10 Amp, Phase A. Substation DOLF SOP CARSON S DOP MORRIS J | February | 2022 | 2022Q3 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2022-02-12 | N | 111 | N | 8 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 1284 | 15624 | 1909257 | 2022-02-12 08:13 | 2022-02-12 11:00 | 167 | 11kV | 334 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220445 Replaced 10 Amp, A & B Phase Dolf's on Sub 51380, supply restored at 11.00am Previous Storm SOP CARSON S DOP JORDAN M | February | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-02-12 | N | 167 | N | 8 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 1028 | 13013 | 1909228 | 2022-02-11 16:23 | 2022-02-12 11:35 | 1152 | 11kV | 8064 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220435 Thunderstorm BLOWN A phase dolf tried back and failed agian, JMH Found blown dolf when patroling 11kv feeder. JMH 10 Amp, A Phase, Substation DOLF SOP HUBY J DOPHICKEY V | February | 2022 | 2022Q3 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2022-02-11 | N | 1152 | N | 27 | Y | Y | 1.1101 | 39.4971 | 5892.9334
[7 empty] | 1624 | 19690 | 1909270 | 2022-02-12 09:25 | 2022-02-12 12:07 | 162 | 11kV | 1296 | 8 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Transformer | Unplanned | No Weather Impact | N | At Ex 12630 Peats Ridge ex panel 13 11kV USL 47842 opened to allow emergency repairs to PT 13885 Lutana Wiseferry 0.4 Interrupted for safety reasons to allow emergency repairs to PT 13885 Lutana Wiseferry 0.4 | February | 2022 | 2022Q3 | 2022 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2022-02-12 | N | 162 | N | 8 | N | N | 1.1101 | 39.4971 | 947.0786
[7 empty] | 705 | 9091 | 1909281 | 2022-02-11 16:34 | 2022-02-12 17:00 | 1466 | 11kV | 33718 | 23 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 220441 Thunderstorm Phases A & B. Substation DOLF Faulty TX" SOP KEEGAN T DOP MILLS A | February | 2022 | 2022Q3 | 2022 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2022-02-11 | N | 1466 | N | 27 | Y | Y | 1.1101 | 39.4971 | 24640.1199
[7 empty] | 608 | 7755 | 1909230 | 2022-02-11 16:23 | 2022-02-12 17:07 | 1484 | 11kV | 1484 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220436 Phases A,B & C (Three Phase) Blown DOLF a b c 10 Amp tried back once.JMH Found with blown dolf when patroling 11kv feeder. JMH Thunderstorm SOP HUBY J DOP HICKEY V | February | 2022 | 2022Q3 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2022-02-11 | N | 1484 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1084.4634
[7 empty] | 1047 | 13445 | 1909334 | 2022-02-12 14:30 | 2022-02-12 18:30 | 240 | 11kV | 1680 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 220449 Replace defective transformer Found ont the 11th, refer to 1909013 | February | 2022 | 2022Q3 | 2022 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2022-02-12 | N | 240 | N | 8 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 81 | 972 | 1909351 | 2022-02-12 18:45 | 2022-02-12 20:30 | 105 | 11kV | 6195 | 59 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 220452 Interrupt to replace Transformer Excluded OMS 1909351 | February | 2022 | 2022Q3 | 2022 | 228:85413 | 228:85413 | ZN00228/085413 | NEWCASTLE | OH | Not Veg | 2022-02-12 | N | 105 | N | 8 | N | N | 1.1101 | 39.4971 | 4527.1233
[7 empty] | 480 | 5836 | 1909368 | 2022-02-12 23:31 | 2022-02-13 01:30 | 119.4833 | 11kV | 2031.2167 | 17 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220453 31 Amp, Phases A & B., Line DOLF Removed flying fox pole FS-73506" SOP KEEGAN T DOP QUIST M | February | 2022 | 2022Q3 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2022-02-12 | N | 119.4833 | N | 8 | N | N | 1.1101 | 39.4971 | 1484.3532
[7 empty] | 787 | 9877 | 1909375 | 2022-02-13 01:28 | 2022-02-13 03:21 | 113 | 11kV | 192165 | 1701 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | AT ZN35*900 Potts Hill Panel 24 trippe don O/C, E/F, EFI, E/F check Cause: Vehicle hit pole near the corner of Weeroona and Joseph St. 11kV pol and cross arm damaged See OMS 1910384 1910387 1909375 | February | 2022 | 2022Q3 | 2022 | ZN35900:PA24 | ZN35900:PA24 | ZN35900/000024 | CUMBERLAND | OH | Not Veg | 2022-02-13 | N | 112.9718 | N | 1 | N | N | 1.1101 | 39.4971 | 140428.5141
[7 empty] | 570 | 7077 | 1909665 | 2022-02-14 20:20 | 2022-02-14 21:20 | 60 | 11kV | 120 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | ## Isolate sub 72535 to repair broken 11kV X-arm at pole FD-80184. JMH Related to Hazard OMS1909665. Repairs complete | February | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2022-02-14 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 1421 | 17485 | 1909728 | 2022-02-14 22:20 | 2022-02-14 23:07 | 46.8833 | 11kV | 2766.1167 | 59 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220459 C Phase DOLF : 31 Amp Possum found at sub pole | February | 2022 | 2022Q3 | 2022 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Not Veg | 2022-02-14 | N | 46.8833 | N | 5 | N | N | 1.1101 | 39.4971 | 2021.3965
[7 empty] | 1355 | 16564 | 1909715 | 2022-02-14 20:32 | 2022-02-15 00:05 | 213 | 11kV | 295550 | 1744 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.39 tripped, reclosed & locked out on: A & C phase OC Cause not ascertained. Delayed restoration due to multiple electronic EFIs not working - defective tags raised See 1910370 1910371 1910372 1910373 1910374 1910375 | February | 2022 | 2022Q3 | 2022 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Veg | 2022-02-14 | N | 169.4667 | N | 5 | N | N | 1.1101 | 39.4971 | 215979.2228
[7 empty] | 551 | 6744 | 1909721 | 2022-02-14 21:53 | 2022-02-15 00:55 | 182.2833 | 11kV | 2916.5333 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220460 No cause found replaced C phase LF 40607 10A supply on 0055hrs CC1: 22-"Refer to SOp" | February | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2022-02-14 | N | 182.2833 | N | 5 | N | N | 1.1101 | 39.4971 | 2131.3165
[7 empty] | 198 | 2547 | 1909736 | 2022-02-14 23:41 | 2022-02-15 01:15 | 94 | 11kV | 470 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220461 B & C Phase DOLF : 20 Amp Excluded OMS 1909726 | February | 2022 | 2022Q3 | 2022 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2022-02-14 | N | 94 | N | 5 | N | N | 1.1101 | 39.4971 | 343.4621
[7 empty] | 8 | 133 | 1909739 | 2022-02-15 02:31 | 2022-02-15 03:51 | 80 | 11kV | 320 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220462 A & B Phase DOLF : 16 Amp Excluded OMS 1909739 | February | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2022-02-15 | N | 80 | N | 2 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 2 | 51 | 1909950 | 2022-02-15 18:13 | 2022-02-15 21:30 | 197 | 11kV | 168234 | 1607 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | No Weather Impact | N | Zn1068 Lidcombe - Pnl.27 tripped on: A & B phase IOC Car hit kiosk S64916 | February | 2022 | 2022Q3 | 2022 | ZN1068:PA27 | ZN1068:PA27 | ZN01068/000027 | CUMBERLAND | Unknown | Not Veg | 2022-02-15 | N | 104.6882 | N | 2 | N | N | 1.1101 | 39.4971 | 122940.4451
[7 empty] | 254 | 3172 | 1910035 | 2022-02-16 10:19 | 2022-02-16 11:32 | 73 | 11kV | 19962 | 330 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1068 Lidcombe - Pnl.21 tripped on: No flags found by DOp on main protection only EFI flag. UG cable fault between S77991 Sw/B and S7849 Sw/A See 1910312 1910314 | February | 2022 | 2022Q3 | 2022 | ZN1068:PA21 | ZN1068:PA21 | ZN01068/000021 | CUMBERLAND | UG | Not Veg | 2022-02-16 | N | 60.4909 | N | 3 | N | N | 1.1101 | 39.4971 | 14587.6408
[7 empty] | 265 | 3428 | 1910153 | 2022-02-16 17:20 | 2022-02-16 18:45 | 85 | 11kV | 325 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220466 Broken Pin at SM-30024 Excluded oms 1910153, 1910183. | February | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2022-02-16 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 237.5004
[7 empty] | 319 | 4251 | 1910140 | 2022-02-16 15:11 | 2022-02-16 20:25 | 314 | 11kV | 221336 | 2254 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn14143 Somersby - Pnl16 tripped on B & C phase OC 11kV cross arm broken away between LB41707 and AB4222 tee PT49696 PT1104 Dist #2 isolated for cross arm replacement See 1910339 1910340 | February | 2022 | 2022Q3 | 2022 | ZN14143:PA16 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2022-02-16 | N | 98.197 | N | 3 | N | N | 1.1101 | 39.4971 | 161745.8205
[7 empty] | 57 | 688 | 1910226 | 2022-02-17 04:06 | 2022-02-17 05:15 | 68.7833 | 11kV | 6947.1167 | 101 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220469 A & B Phase DOLF : 31 Amp Possum Excluded OMS 1910228 | February | 2022 | 2022Q3 | 2022 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2022-02-17 | N | 68.7833 | N | 19 | N | N | 1.1101 | 39.4971 | 5076.748
[7 empty] | 1238 | 15140 | 1910245 | 2022-02-17 08:05 | 2022-02-17 10:16 | 131 | 11kV | 230961 | 1914 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn5868 Gore Hill Panel 14 tripped on Relays: Lockout, EF, ABC OC with efi Signals: 11kV Trup, Zone Earth, TX3 Group Earth Cause: 11kV feeder from S804 to S7064 to S4087 tio S3864 See OMS 1914414 1914416 1910250 1910245 | February | 2022 | 2022Q3 | 2022 | ZN5868:PA14 | ZN5868:PA14 | ZN05868/000014 | WILLOUGHBY | UG | Not Veg | 2022-02-17 | N | 120.6693 | N | 19 | N | N | 1.1101 | 39.4971 | 168779.4866
[7 empty] | 878 | 10842 | 1910889 | 2022-02-17 16:35 | 2022-02-17 16:45 | 10 | 11kV | 10 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220472 Single phase DOLF : 10 Amp No OMS Called in by Meter Reader. | February | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-02-17 | N | 10 | N | 19 | N | N | 1.1101 | 39.4971 | 7.3077
[7 empty] | 1029 | 13025 | 1910457 | 2022-02-17 18:29 | 2022-02-17 20:55 | 146 | 11kV | 199814 | 1925 | HV | Animal Bird | Animal | DC-PT Transformer | Unplanned | Rain Heavy | N | At ZN116 Leichardt 11 kV panel 12 ' Balmain Derby' feeder tripped on 50TBC, EFI PT1862 Lilyfield Trev blew centre and roadside HDO Birds across HV droppers at PT1862 Lilyfield Trev See1912811,1912810 1910457 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN116:PA12 | ZN116:PA12 | ZN00116/000012 | INNER WEST | OH | Not Veg | 2022-02-17 | N | 103.7995 | N | 19 | N | N | 1.1101 | 39.4971 | 146018.1777
[7 empty] | 805 | 10025 | 1910545 | 2022-02-17 20:02 | 2022-02-17 22:06 | 124 | 11kV | 49848 | 405 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220478 A & C Phase Overcurrent Fault was a branch across 11kV at ABS 43973. Excluded OMS 1910545 | February | 2022 | 2022Q3 | 2022 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2022-02-17 | N | 123.0815 | N | 19 | N | N | 1.1101 | 39.4971 | 36427.4481
[7 empty] | 1174 | 14705 | 1910512 | 2022-02-17 19:32 | 2022-02-17 22:10 | 158 | 11kV | 155283 | 1671 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Electrical Storm | N | At ZN 12580 Erina Panel 10 'S13682 Erina High Ernest' feeder tripped on Relays IOC C phase, timed OC, phase, EFI Field EFI's S14189, S12866, S77675, S14024, S13682 Section of feeder from LB45420 to PT14132 to S18013 isolated due to enbox failure at S18013 See 1912838,1912839,1912840,1912841 1910512 | February | 2022 | 2022Q3 | 2022 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | UG | Not Veg | 2022-02-17 | N | 92.9282 | N | 19 | N | N | 1.1101 | 39.4971 | 113476.2363
[7 empty] | 1473 | 18199 | 1910524 | 2022-02-17 19:46 | 2022-02-17 22:31 | 165 | 11kV | 184414 | 1118 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | At ZN12600 ex panel 9, Recloser 47607 Toomeys Rd has tripped and reclosed Relays: LO earth fault At PT14152 Toomey Madens blown HDO foot path side 10A 2nd attempt Recloser 47607 Toomeys Rd has tripped and reclosed Relays LO Earth Fault Section of feeder from LK44339 to AB44074 has suspect fault. Possible faulty ABC or surge arrestor. Additionally HDO found blown at PT14152 Toomey Madens See 1912788,1912789 1910524 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2022-02-17 | N | 164.9499 | N | 19 | N | N | 1.1101 | 39.4971 | 134764.3119
[7 empty] | 645 | 8379 | 1910546 | 2022-02-17 20:05 | 2022-02-17 23:09 | 184 | 11kV | 3864 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220492 A Phase DOLF : 10 Amp Excluded OMS 1910546 | February | 2022 | 2022Q3 | 2022 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2022-02-17 | N | 184 | N | 19 | N | N | 1.1101 | 39.4971 | 2823.6972
[7 empty] | 1665 | 20230 | 1910582 | 2022-02-17 21:03 | 2022-02-17 23:12 | 129 | 11kV | 199228 | 1748 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 220497 2 fault operations A & B Phase Overcurrent LA's at pole JT-71334 blown clear. note Wallsend Admin No.2 sub transfered over to 80776 for CR power security. Excluded OMS 1910582 | February | 2022 | 2022Q3 | 2022 | 258:80784 | 258:80784 | ZN00258/080784 | NEWCASTLE | OH | Not Veg | 2022-02-17 | N | 113.9748 | N | 19 | N | N | 1.1101 | 39.4971 | 145589.9462
[7 empty] | 42 | 494 | 1910573 | 2022-02-17 20:52 | 2022-02-18 00:20 | 208 | 11kV | 13520 | 65 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | PT12115 Lake View Minell HDO 16A Roadside fuse blew low volts in area. PT 12115 looks as if road side HV fuse has blown. Fuse is still in position but can see fuse wire hanging out the bottom of the fuse. DOP required to replace. Cause not ascertained | February | 2022 | 2022Q3 | 2022 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Veg | 2022-02-17 | N | 208 | N | 19 | N | N | 1.1101 | 39.4971 | 9880.0172
[7 empty] | 639 | 8266 | 1910608 | 2022-02-17 21:36 | 2022-02-18 00:55 | 199 | 11kV | 16716 | 84 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 220495 Suspect faulty TX. HV f/Sw tripped after lightening strike and tripped again with a replacement fuse. Left in LV// to restore customers. Excluded OMS 1910608 | February | 2022 | 2022Q3 | 2022 | 256:80641 | 256:80641 | ZN00256/080641 | NEWCASTLE | UG | Not Veg | 2022-02-17 | N | 199 | N | 19 | N | N | 1.1101 | 39.4971 | 12215.5598
[7 empty] | 321 | 4306 | 1910556 | 2022-02-17 20:26 | 2022-02-18 01:50 | 324 | 11kV | 15140 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220491 A & B Phase DOLF's : 40 Amp Excluded OMS 1910556 | February | 2022 | 2022Q3 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2022-02-17 | N | 302.8 | N | 19 | N | N | 1.1101 | 39.4971 | 11063.8654
[7 empty] | 1534 | 18846 | 1910513 | 2022-02-17 19:36 | 2022-02-18 02:20 | 404 | 11kV | 6868 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220496 3 phase DOLF's : 31 Amp No cause found | February | 2022 | 2022Q3 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2022-02-17 | N | 404 | N | 19 | N | N | 1.1101 | 39.4971 | 5018.9318
[7 empty] | 866 | 10723 | 1910578 | 2022-02-17 21:01 | 2022-02-18 03:09 | 368 | 11kV | 4416 | 12 | HV | Vegetation Blow/Fall In | Vegetation | Fuse Assembly | Unplanned | Electrical Storm | N | LID 220500 C Phase Tree struck fuse carrier. Excluded OMS 1910578 | February | 2022 | 2022Q3 | 2022 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2022-02-17 | N | 368 | N | 19 | N | N | 1.1101 | 39.4971 | 3227.0826
[7 empty] | 1007 | 12595 | 1910551 | 2022-02-17 21:03 | 2022-02-18 03:35 | 392 | 11kV | 8320 | 69 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220490 Wires on Ground beyond LF 62318 Excluded OMS 1910551 | February | 2022 | 2022Q3 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2022-02-17 | N | 120.5797 | N | 19 | N | N | 1.1101 | 39.4971 | 6080.0106
[7 empty] | 653 | 8453 | 1910599 | 2022-02-17 21:27 | 2022-02-18 04:46 | 438.5 | 11kV | 5262 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220502 Single phase DOLF : 20 Amp | February | 2022 | 2022Q3 | 2022 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2022-02-17 | N | 438.5 | N | 19 | N | N | 1.1101 | 39.4971 | 3845.3144
[7 empty] | 423 | 5319 | 1910626 | 2022-02-17 22:11 | 2022-02-18 05:15 | 424.1 | 11kV | 8482 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 220503 Broken tap pole HR-91893. Excluded OMS 1910646 | February | 2022 | 2022Q3 | 2022 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2022-02-17 | N | 424.1 | N | 19 | N | N | 1.1101 | 39.4971 | 6198.3954
[7 empty] | 811 | 10069 | 1910597 | 2022-02-17 21:26 | 2022-02-18 06:55 | 569 | 11kV | 2276 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220504 DOLF : 10 Amp Excluded OMS 1910597 | February | 2022 | 2022Q3 | 2022 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2022-02-17 | N | 569 | N | 19 | N | N | 1.1101 | 39.4971 | 1663.2337
[7 empty] | 1641 | 19879 | 1910671 | 2022-02-18 02:41 | 2022-02-18 08:36 | 355 | 11kV | 1065 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220508 A Phase DOLF : 16 Amp Excluded OMS 1910671 | February | 2022 | 2022Q3 | 2022 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2022-02-18 | N | 355 | N | 19 | N | N | 1.1101 | 39.4971 | 778.2706
[7 empty] | 783 | 9858 | 1910690 | 2022-02-18 06:17 | 2022-02-18 08:54 | 157 | 11kV | 157 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220518 Single phase DOLF : 10 Amp Excluded OMS 1910690 | February | 2022 | 2022Q3 | 2022 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2022-02-18 | N | 157 | N | 19 | N | N | 1.1101 | 39.4971 | 114.731
[7 empty] | 1027 | 13007 | 1910673 | 2022-02-18 02:57 | 2022-02-18 08:57 | 360 | 11kV | 128746 | 746 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn 2196 Milperra panel 26 tripped on Relays A and B phase OC Filed EFI's S63412 Tree on HV found between S48646 Yanderra Simmat and S62316 Sizth Yanderra Open bonfd found below tee off to S47074 Harris St See 1912404,1912406,1912410 1910673,1910681,1910685 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-02-18 | N | 172.5818 | N | 19 | N | N | 1.1101 | 39.4971 | 94083.7794
[7 empty] | 1435 | 17707 | 1910628 | 2022-02-18 06:55 | 2022-02-18 09:28 | 152.7667 | 11kV | 611.0667 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | No further information is available, assume calls and OMS prediction is correct. Major electrical storm the night before | February | 2022 | 2022Q3 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-02-18 | N | 152.7667 | N | 19 | N | N | 1.1101 | 39.4971 | 446.5495
[7 empty] | 487 | 5940 | 1910741 | 2022-02-18 08:28 | 2022-02-18 09:47 | 79 | 11kV | 474 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220509 B Phase DOLF : 40 Amp Excluded OMS 1910741 | February | 2022 | 2022Q3 | 2022 | 256:80652 | 256:80652 | ZN00256/080652 | NEWCASTLE | OH | Veg | 2022-02-18 | N | 79 | N | 19 | N | N | 1.1101 | 39.4971 | 346.3852
[7 empty] | 1656 | 20119 | 1910707 | 2022-02-18 07:08 | 2022-02-18 09:50 | 162 | 11kV | 486 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220521 B & C Phase DOLF : 10 Amp B and C phase HV fuses blown due to electrical storm. Replaced 10A fuses and B phase carrier. Excluded OMS 1910707 | February | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-02-18 | N | 162 | N | 19 | N | N | 1.1101 | 39.4971 | 355.1545
[7 empty] | 1080 | 13850 | 1910718 | 2022-02-18 07:29 | 2022-02-18 09:50 | 141 | 11kV | 282 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220520 Single phase DOLF : 10 Amp Excluded OMS 1910718 | February | 2022 | 2022Q3 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2022-02-18 | N | 141 | N | 19 | N | N | 1.1101 | 39.4971 | 206.0773
[7 empty] | 1187 | 14774 | 1910667 | 2022-02-18 01:35 | 2022-02-18 10:35 | 540 | 11kV | 3240 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220511 C Phase DOLF : 10 Amp Excluded OMS 1910667 | February | 2022 | 2022Q3 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2022-02-18 | N | 540 | N | 19 | N | N | 1.1101 | 39.4971 | 2367.6964
[7 empty] | 17 | 214 | 1910713 | 2022-02-18 07:21 | 2022-02-18 11:30 | 249 | 11kV | 4980 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 220512 Burnt off tapping at pole HR-91889 Excluded 1910713 | February | 2022 | 2022Q3 | 2022 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2022-02-18 | N | 249 | N | 19 | N | N | 1.1101 | 39.4971 | 3639.2371
[7 empty] | 1234 | 15122 | 1910463 | 2022-02-17 18:50 | 2022-02-18 13:00 | 1090 | 11kV | 348009 | 1128 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Lightning | N | At ZN1193 Lindfield 11kV Panel 27 'S77133 Havilah Nelson' tripped, reclosed and locked out on: Relays O/C, E/F, EFI, lock out Signals 11kV trip Field efi's S47362 Large tree branch on HV mains with broken HV cross arm | February | 2022 | 2022Q3 | 2022 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Veg | 2022-02-17 | N | 308.5186 | N | 19 | N | N | 1.1101 | 39.4971 | 254314.7127
[7 empty] | 761 | 9526 | 1910867 | 2022-02-18 12:30 | 2022-02-18 13:11 | 41 | 11kV | 29766 | 726 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 3155 Double Bay, 11kV Panel 21 has tripped on Relays - A phase and Earth fault, EFI and Fault check Signals 11 kV trip, TX1 Group Earth, Zone Earth Filed EFI's NIL 11 kV UG fault from S3155 Double Bay Panel 21 to S1696 Redleaf. Increased STIPUS cost as Pnl 39 is abnormal due to feeder fault. Fault repaired but not notified ready for service. Abnormal switching - Sw/A closed at S35725 Wolsely Rd No.2, Sw/A is open at S8946 Wentworth Kilmory East. 1910867,1910868 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN3155:PA21 | ZN3155:PA21 | ZN03155/000021 | WOOLLAHRA | UG | Not Veg | 2022-02-18 | N | 41 | N | 19 | N | N | 1.1101 | 39.4971 | 21752.1149
[7 empty] | 559 | 6903 | 1910860 | 2022-02-18 11:56 | 2022-02-18 13:35 | 99 | 11kV | 13365 | 135 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220517 Broken down earth stapling, Earth contacted LV OHM, Sub Isolated for safety & repairs. Excluded OMS 19108606 | February | 2022 | 2022Q3 | 2022 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2022-02-18 | N | 99 | N | 19 | N | N | 1.1101 | 39.4971 | 9766.7478
[7 empty] | 208 | 2606 | 1910879 | 2022-02-18 17:10 | 2022-02-18 18:25 | 75 | 11kV | 1500 | 20 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220527 Replace crossarm at sub72833 Excluded OMS 1910879 | February | 2022 | 2022Q3 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2022-02-18 | N | 75 | N | 19 | N | N | 1.1101 | 39.4971 | 1096.1558
[7 empty] | 481 | 5853 | 1910877 | 2022-02-18 17:25 | 2022-02-18 18:45 | 80 | 11kV | 1040 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 220528 Ausgird helicopter patrol found b phase 11kV insulator broken at pole DI-80039. Excluded OMS 1910877 | February | 2022 | 2022Q3 | 2022 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2022-02-18 | N | 80 | N | 19 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 800 | 9988 | 1910957 | 2022-02-18 19:19 | 2022-02-18 19:52 | 33 | 11kV | 3404 | 106 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 220529 Helicopter patrol 11kV on x arm pole 41-70113 Excluded OMS 1910957 | February | 2022 | 2022Q3 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2022-02-18 | N | 32.1132 | N | 19 | N | N | 1.1101 | 39.4971 | 2487.5428
[7 empty] | 92 | 1196 | 1910795 | 2022-02-18 10:09 | 2022-02-18 20:00 | 591 | 11kV | 1773 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 220535 Faulty Transformer 50950 Excluded OMS 1910795 | February | 2022 | 2022Q3 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2022-02-18 | N | 591 | N | 19 | N | N | 1.1101 | 39.4971 | 1295.6561
[7 empty] | 1606 | 19554 | 1910893 | 2022-02-18 13:16 | 2022-02-18 20:45 | 449 | 11kV | 898 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220542 Single phase DOLF : 10 Amp Excluded OMS 1910893 | February | 2022 | 2022Q3 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2022-02-18 | N | 449 | N | 19 | N | N | 1.1101 | 39.4971 | 656.2319
[7 empty] | 1354 | 16545 | 1910709 | 2022-02-18 07:14 | 2022-02-18 21:10 | 836 | 11kV | 1672 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 220532 Faulty transformer 50298 Excluded OMS 1910709 | February | 2022 | 2022Q3 | 2022 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2022-02-18 | N | 836 | N | 19 | N | N | 1.1101 | 39.4971 | 1221.8483
[7 empty] | 40 | 444 | 1911013 | 2022-02-18 21:26 | 2022-02-19 00:29 | 183.1667 | 11kV | 3846.5 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220546 A Phase DOLF : 10 Amp | February | 2022 | 2022Q3 | 2022 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2022-02-18 | N | 183.1667 | N | 19 | N | N | 1.1101 | 39.4971 | 2810.9087
[7 empty] | 981 | 12019 | 1910647 | 2022-02-18 23:50 | 2022-02-19 05:40 | 350 | 11kV | 146424 | 1040 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 220548 Faulty ugoh sw 31019 Excluded 1911033 | February | 2022 | 2022Q3 | 2022 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | Unknown | Unknown | 2022-02-18 | N | 140.7923 | N | 19 | N | N | 1.1101 | 39.4971 | 107002.3404
[7 empty] | 1247 | 15209 | 1911043 | 2022-02-19 07:54 | 2022-02-19 11:35 | 221 | 11kV | 221 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 220551 B Phase DOLF : 10 Amp Excluded OMS 1911043 | February | 2022 | 2022Q3 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2022-02-19 | N | 221 | N | 7 | N | N | 1.1101 | 39.4971 | 161.5003
[7 empty] | 565 | 6999 | 1911057 | 2022-02-19 09:30 | 2022-02-19 12:25 | 175 | 11kV | 317145 | 3174 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn15015 North Head panel 15 tripped on Earth Fault with EFI. Network abnormally switched: S16690 SwB closed with S16194 Sw A open, S15193 Sw B closed with S15095 Sw A open, S16374 Sw B closed with S16374 Sw F open. UG fault from S16721 Fairy Bower Vivian to 11kv USL 22305 to tee S15525 Osbourne Rd. 1912436, 1912438 1911058, 1911057 | February | 2022 | 2022Q3 | 2022 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | UG | Not Veg | 2022-02-19 | N | 99.9197 | N | 7 | N | N | 1.1101 | 39.4971 | 231760.2118
[7 empty] | 1062 | 13593 | 1911105 | 2022-02-19 12:33 | 2022-02-19 13:40 | 67 | 11kV | 5312.6 | 80 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Replaced C phase DOLF : 40Amps No Cause Found Operator T Cameron | February | 2022 | 2022Q3 | 2022 | 239:82136 | 239:82136 | ZN00239/082136 | LAKE MACQUARIE | OH | Veg | 2022-02-19 | N | 66.4075 | N | 7 | N | N | 1.1101 | 39.4971 | 3882.2914
[7 empty] | 1348 | 16449 | 1911099 | 2022-02-19 14:25 | 2022-02-19 17:15 | 170 | 11kV | 2890 | 17 | HV | 3rd Party Vehicle | 3rd Party Impact | Insulator | Unplanned | No Weather Impact | N | LID 220577 car hit pole last night. car not at scene. wires knocked off pins etc. Replaced broken 11kv ties on poles SI90970, SI90972, SI90973 queen st singleton after vehicle impact, repaired ABC 95mm service connection on pole SI90972. Excluded oms 1911099 | February | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2022-02-19 | N | 170 | N | 7 | N | N | 1.1101 | 39.4971 | 2111.9268
[7 empty] | 434 | 5413 | 1911140 | 2022-02-19 17:27 | 2022-02-19 18:49 | 82 | 11kV | 51168 | 624 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN3425 Castle Cove 11kV panel No18 tripped on- Relays B+C phase over current, EFI, fault check. Signals - 11kV trip, TX 4 group E, EFI's - NIL U/G Fault 11kV front line feeder fault from ZN3425 Castle Cove to S1854 Victor Victoria SW/B | February | 2022 | 2022Q3 | 2022 | ZN3425:PA18 | ZN3425:PA18 | ZN03425/000018 | WILLOUGHBY | UG | Not Veg | 2022-02-19 | N | 82 | N | 7 | N | N | 1.1101 | 39.4971 | 37392.0652
[7 empty] | 14 | 192 | 1911152 | 2022-02-19 18:36 | 2022-02-19 19:23 | 47 | 11kV | 188 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV 'Killarney West' feeder Panel 6L at ZN15012 Killarney At Recloser 26228 Valley Road tripped on Relays O/C trip, IOC trip Tree branch clashed mains near USL 22297 | February | 2022 | 2022Q3 | 2022 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2022-02-19 | N | 47 | N | 7 | N | N | 1.1101 | 39.4971 | 137.3849
[7 empty] | 38 | 440 | 1911146 | 2022-02-19 18:16 | 2022-02-19 20:05 | 108.8667 | 11kV | 10668.9333 | 98 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 220580 A Phase DOLF : 40 Amp Faulty transformer. Backfed on LV. Tx to be replaced 20/2/22. See Matt Hobbs MAitland ERC. | February | 2022 | 2022Q3 | 2022 | 522:83129 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Not Veg | 2022-02-19 | N | 108.8667 | N | 7 | N | N | 1.1101 | 39.4971 | 7796.5418
[7 empty] | 53 | 642 | 1911230 | 2022-02-20 16:38 | 2022-02-20 17:40 | 62 | 11kV | 186 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220582 A Phase DOLF : 10 Amp Excluded OMS 1911230 | February | 2022 | 2022Q3 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-02-20 | N | 62 | N | 1 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 337 | 4723 | 1911270 | 2022-02-21 06:34 | 2022-02-21 10:57 | 263 | 11kV | 165896 | 1050 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1290 Leightonfield Panel 12 tripped on Relays: C phase IOC, timed overcurrent, Reclose timing relay, Lockout Relay Cause: Bird found burnt and stuck on 11kV Mains outside 134 Alcoomie Rd Villawood Between S35969 to AB995 to AB1699 See OMS1912484 1812488 1812487 1812489 1912510 1912486 1911270 1911898 | February | 2022 | 2022Q3 | 2022 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-02-21 | N | 157.9962 | N | 11 | N | N | 1.1101 | 39.4971 | 121231.9037
[7 empty] | 91 | 1187 | 1911339 | 2022-02-21 09:55 | 2022-02-21 11:34 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220589 C Phase DOLF : 20 Amp Excluded OMS 1911339 | February | 2022 | 2022Q3 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2022-02-21 | N | 99 | N | 11 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 1139 | 14351 | 1911401 | 2022-02-21 11:54 | 2022-02-21 13:54 | 120 | 11kV | 174844 | 1728 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn3425 Castle Cove Panel 22 tripped on Relays: A and C phase OC, EFI and Fault Check Abnormal Switching: Pa18 Trunk OOS, SW/B Closed @ S4742 Anderson Ferguson Cause: UG cable fault from S2493 to S5409 See OMS 1912338 1912340 1911408 1911401 | February | 2022 | 2022Q3 | 2022 | ZN3425:PA22 | ZN3425:PA22 | ZN03425/000022 | WILLOUGHBY | UG | Not Veg | 2022-02-21 | N | 101.1829 | N | 11 | N | N | 1.1101 | 39.4971 | 127770.8382
[7 empty] | 952 | 11535 | 1911470 | 2022-02-21 14:41 | 2022-02-21 17:45 | 184 | 11kV | 22960 | 140 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 220590 Wire off pin at pole 5H-70067 Excluded OMS 1911470 | February | 2022 | 2022Q3 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2022-02-21 | N | 164 | N | 11 | N | N | 1.1101 | 39.4971 | 16778.4908
[7 empty] | 48 | 624 | 1911490 | 2022-02-21 19:27 | 2022-02-21 20:00 | 33.2833 | 11kV | 1264.7667 | 38 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 220592 C Phase Broken insulator pole 7G40042 Excluded OMS 1911490 | February | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2022-02-21 | N | 33.2833 | N | 11 | N | N | 1.1101 | 39.4971 | 924.2542
[7 empty] | 470 | 5759 | 1911518 | 2022-02-21 17:27 | 2022-02-21 20:35 | 188 | 11kV | 6392 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220594 B & C Phases : 16 Amp Excluded OMS 1911518 | February | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2022-02-21 | N | 188 | N | 11 | N | N | 1.1101 | 39.4971 | 4671.0851
[7 empty] | 1669 | 20304 | 1911267 | 2022-02-21 05:57 | 2022-02-21 21:00 | 903.1 | 11kV | 903.1 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | LID 220591 Blown B phase Dolf : 20A sub DOLFs operated twice Sub faulty and replaced. no cause found. JMH Excluded OMS 1911316 | February | 2022 | 2022Q3 | 2022 | 507:80926 | 507:80926 | ZN00507/080926 | CESSNOCK | OH | Not Veg | 2022-02-21 | N | 903.1 | N | 11 | N | N | 1.1101 | 39.4971 | 659.9588
[7 empty] | 1505 | 18484 | 1911537 | 2022-02-21 18:48 | 2022-02-22 01:30 | 402 | 11kV | 42288 | 140 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | Section of Panel 4 Galston Recloser CP555 Arcadia Park Tripped on No indication Lightning arrestor cap found blown off at PT1486 Bay Keighran Farm (Smelt Burning) RecloserCP555 Arcadia Park Keeps Shooting thorugh See OMS 1912039 1912040 1912042 1911594 1912041 1911553 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2022-02-21 | N | 302.0571 | N | 11 | N | N | 1.1101 | 39.4971 | 30902.8231
[7 empty] | 1031 | 13033 | 1911539 | 2022-02-21 19:15 | 2022-02-22 02:15 | 420 | 11kV | 840 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 220609 Single phase DOLF : 10 Amp Excluded OMS 1911539 | February | 2022 | 2022Q3 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2022-02-21 | N | 420 | N | 11 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 345 | 4777 | 1911545 | 2022-02-21 19:20 | 2022-02-22 06:15 | 655 | 11kV | 71288 | 135 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220600 5 fault operations Overcurrent; Earth Fault Broken conductor under PG Clamp pole HQ-51459 Faulty PG clamp ABS 40036. Tree on 11kV OHM adjacent PT 50271. Excluded OMS 1911545 | February | 2022 | 2022Q3 | 2022 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2022-02-21 | N | 528.0593 | N | 11 | N | N | 1.1101 | 39.4971 | 52095.1678
[7 empty] | 255 | 3193 | 1911616 | 2022-02-22 06:57 | 2022-02-22 07:45 | 48 | 11kV | 48 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220613 C Phase DOLF : 10 Amp Excluded OMS 1911616 | February | 2022 | 2022Q3 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2022-02-22 | N | 48 | N | 26 | Y | Y | 1.1101 | 39.4971 | 35.077
[7 empty] | 1394 | 17086 | 1911637 | 2022-02-22 07:12 | 2022-02-22 08:27 | 75 | 11kV | 832 | 92 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN12560 West Gosford Panel 1 Recloser 44937 Alan St tripped and reclosed PT 12166 Glen Boorawa HDO operated fott path phase. Dop patrolled feeder, tree branch on PT bushings See1914156, 1914158 1911637 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2022-02-22 | N | 9.0435 | N | 26 | Y | Y | 1.1101 | 39.4971 | 608.0011
[7 empty] | 894 | 11020 | 1911603 | 2022-02-22 07:35 | 2022-02-22 08:37 | 62 | 11kV | 37950 | 631 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN35370 Galston 11kV feeder panel No 4L 'Galston Aux No1' tripped and reclosed to lockout on Relays:A and C phase O/C, EFI, lockout Field EFI's: S47361, S65844 Tree/branch on OH mains near PT1616 Abnormal Switching - Recloser 555 Open AB 2063 closed See 1914192,1914194,1914196 1911603 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2022-02-22 | N | 60.1426 | N | 26 | Y | Y | 1.1101 | 39.4971 | 27732.7407
[7 empty] | 86 | 1083 | 1911644 | 2022-02-22 08:20 | 2022-02-22 09:30 | 70 | 11kV | 140 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220615 C Phase DOLF : 10 Amp excluded OMS 1911644 | February | 2022 | 2022Q3 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2022-02-22 | N | 70 | N | 26 | Y | Y | 1.1101 | 39.4971 | 102.3079
[7 empty] | 1202 | 14877 | 1911707 | 2022-02-22 10:16 | 2022-02-22 11:36 | 80 | 11kV | 97704 | 1406 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | At ZN14891 Wyong 11kV feeder panel No5. "Wyong" feeder tripped and reclosed to lockout on: Relays: SEL and EFI Signals: 11kV trip Field EFI's: NIL At IR62705 Jilliby Durren operated Relays: O/C trip At ZN 14891 Panel 5 'Wyong' AB 43811 Road side bond off. See 1914334,1914335,1914337,191349 1911707 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2022-02-22 | N | 69.4908 | N | 26 | Y | Y | 1.1101 | 39.4971 | 71399.2014
[7 empty] | 903 | 11136 | 1911737 | 2022-02-22 11:15 | 2022-02-22 12:50 | 95 | 11kV | 285 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Ex ZN 12630 Peats Ridge , Panel 8 ' Kulnura' A & B fault indication PT 11986 Forest Bumble Hill 0.5 16 Amp HDO road side operated Electrical storm | February | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-02-22 | N | 95 | N | 26 | Y | Y | 1.1101 | 39.4971 | 208.2696
[7 empty] | 782 | 9842 | 1911667 | 2022-02-22 09:15 | 2022-02-22 13:40 | 265 | 11kV | 2120 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At PT2185 Charltons Creek Rd HDO operated Cause: Weather related electrical storm at the time of interruption See OMS1912955 1911704 1911686 1911667 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2022-02-22 | N | 265 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1549.2335
[7 empty] | 428 | 5362 | 1911765 | 2022-02-22 11:41 | 2022-02-22 13:50 | 129 | 11kV | 2193 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220624 C Phase DOLF : 31 Amp Excluded OMS 1911765 | February | 2022 | 2022Q3 | 2022 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2022-02-22 | N | 129 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1602.5797
[7 empty] | 725 | 9268 | 1911739 | 2022-02-22 11:17 | 2022-02-22 14:04 | 167 | 11kV | 5561 | 405 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220621 Trip & Reclose 1 fault operation 3 phase Earth Fault | February | 2022 | 2022Q3 | 2022 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2022-02-22 | N | 13.7309 | N | 26 | Y | Y | 1.1101 | 39.4971 | 4063.8148
[7 empty] | 593 | 7492 | 1911823 | 2022-02-22 12:54 | 2022-02-22 14:15 | 80.6333 | 11kV | 2096.4667 | 26 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | Operator J Frazer 3 x Blown dolfs ABC :20A Lightning >JMH OMS 1911823 related CC1: 22-"Refer to SOp" | February | 2022 | 2022Q3 | 2022 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2022-02-22 | N | 80.6333 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1532.036
[7 empty] | 243 | 2962 | 1911830 | 2022-02-22 12:52 | 2022-02-22 14:20 | 88 | 11kV | 61776 | 702 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At Zn965 Pennant Hills Panel 21 tripped on Relays: A phase overcurrent Signals: 11kV Trip With EFI FCause: Electric Storm at the time - Branch on PT1887 | February | 2022 | 2022Q3 | 2022 | ZN965:PA21 | ZN965:PA21 | ZN00965/000021 | HORNSBY | OH | Veg | 2022-02-22 | N | 88 | N | 26 | Y | Y | 1.1101 | 39.4971 | 45144.0787
[7 empty] | 485 | 5887 | 1911708 | 2022-02-22 10:16 | 2022-02-22 14:27 | 251 | 11kV | 10689 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Recloser CP44853 Ourimbah Bumble Tripped and locked out on Earth Fault Cause: 11kV on the ground afyer stiorm - Near PT13618 Ourimbah Bumble 0.9 See OMS 1912948 1912949 1911708 | February | 2022 | 2022Q3 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2022-02-22 | N | 248.5814 | N | 26 | Y | Y | 1.1101 | 39.4971 | 7811.2059
[7 empty] | 1638 | 19850 | 1911832 | 2022-02-22 12:54 | 2022-02-22 14:59 | 125 | 11kV | 72610 | 590 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Wind Storm | N | At ZN35370 Galston Panel 10 Tripped, Reclosed Tripped and locked out on RelaysL A and C phase overcurrent with lockout Signals; 11kV Trup with Fault indicator Cause: Electric Storm at the time of failure - broken insulator on pole 762077 (Endeavour joint use pole) See OMS 1912958 1912960 1911832 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2022-02-22 | N | 123.0678 | N | 26 | Y | Y | 1.1101 | 39.4971 | 53061.2464
[7 empty] | 1463 | 18051 | 1911595 | 2022-02-21 19:20 | 2022-02-22 15:10 | 1190 | 11kV | 3035 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 220606 Overcurrent; Earth Fault faulty Tx 70801 replaced with 16KVA Excluded OMS 1911544 | February | 2022 | 2022Q3 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2022-02-21 | N | 337.2222 | N | 11 | N | N | 1.1101 | 39.4971 | 2217.8885
[7 empty] | 1337 | 16329 | 1911888 | 2022-02-22 14:07 | 2022-02-22 15:29 | 82 | 11kV | 75540 | 931 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | IR79642 Herring Lucinda Tripped on Relays: OC Trip, Lockout Cause: Weather related: Feeder patrolled, no cause found See OMS 1912646 1912947 19118888 | February | 2022 | 2022Q3 | 2022 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2022-02-22 | N | 81.1386 | N | 26 | Y | Y | 1.1101 | 39.4971 | 55202.4039
[7 empty] | 1387 | 17010 | 1911947 | 2022-02-22 14:38 | 2022-02-22 15:30 | 52 | 11kV | 2132 | 41 | HV | Lightning Strike | Adverse Weather/Environment | Cable End Box | Unplanned | Rain Heavy | N | At PT2179 Currawong Wymah Interrupted for safety Cause: NAR92743 - Interrupted for safety S6666 Hit by Lightning | February | 2022 | 2022Q3 | 2022 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | UG | Not Veg | 2022-02-22 | N | 52 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1558.0027
[7 empty] | 55 | 665 | 1911874 | 2022-02-22 13:48 | 2022-02-22 16:12 | 144 | 11kV | 1584 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At PT13266 Smiths Durren 1.9 HDO footpath phase blown Weather related, Part of panel 5 interruption | February | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2022-02-22 | N | 144 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1157.5405
[7 empty] | 295 | 3748 | 1912002 | 2022-02-22 14:15 | 2022-02-22 17:05 | 170 | 11kV | 465 | 296 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | Recloser CP48813 Yarramalong Boyds 3.7 tripped and reloced on O/C PT12894 Bumble Hill HDO Operated 10A footpath side Cause: PT12894 Bumble Hill Yarra hit by lightning | February | 2022 | 2022Q3 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2022-02-22 | N | 1.5709 | N | 26 | Y | Y | 1.1101 | 39.4971 | 339.8083
[7 empty] | 1092 | 13953 | 1911968 | 2022-02-22 17:07 | 2022-02-22 18:00 | 53 | 11kV | 6466 | 122 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 220634 No protection operation. Helicopter patrol found damgeed 11kV pin and 11kV on x arm at pole 8H-20052. Excluded OMS 1911968 | February | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2022-02-22 | N | 53 | N | 26 | Y | Y | 1.1101 | 39.4971 | 4725.1621
[7 empty] | 579 | 7285 | 1911894 | 2022-02-22 14:11 | 2022-02-22 18:21 | 250 | 11kV | 550421 | 2598 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN15001 Brookvale 11kV Panel 8 Labelled Harbord Rd Tripped Relays: IOC, EFI, (Code 50T B+C) phase Signals: 11kV Trip[, CB8 Open S50262 Safety In Trip Cause: Closed SW B @ S16894, Open SwA at S16829, Closed SW/A @ S46569, Open Panel 16 @ Brookvale, Closed SW/B @ S46596, Open LB24568 See 1914159 1914163 1914164 1914167 1911872 1911894 1911896 1911918 1912063 1912067 | February | 2022 | 2022Q3 | 2022 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2022-02-22 | N | 211.8634 | N | 26 | Y | Y | 1.1101 | 39.4971 | 402231.4321
[7 empty] | 687 | 8762 | 1912065 | 2022-02-22 17:06 | 2022-02-22 18:28 | 82 | 11kV | 656 | 8 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | AT Zn14144 Wamberal Panel 5 Beaufort PT14618 Beaufird Wycombe 0.5 HDO Centre Phase 16AMP Cause: Weather related - Electrical storm See OMS 1912919 1912068 1912065 | February | 2022 | 2022Q3 | 2022 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2022-02-22 | N | 82 | N | 26 | Y | Y | 1.1101 | 39.4971 | 479.3855
[7 empty] | 314 | 4141 | 1911738 | 2022-02-22 11:14 | 2022-02-22 19:00 | 466 | 11kV | 13980 | 30 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Wind Storm | N | At ZN12630 Peats Ridge 11kV Intellirupter tripped, reclosed tripped on Relays: OC trip Field EFI's NIL Cause: Tree branch on OH mains and broken cross arm beyond CP44318 Wisemans Ferry | February | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2022-02-22 | N | 466 | N | 26 | Y | Y | 1.1101 | 39.4971 | 10216.1717
[7 empty] | 1302 | 15842 | 1911820 | 2022-02-22 12:38 | 2022-02-22 19:05 | 387 | 11kV | 70857 | 371 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | At Zn35370 Galston Panel 2 Tripped, reclosed and locked out on Relays: B and C phase OC, EFI and Lockout Cause: 11kV Mains down beyond USL 58 See OMS 1914020 1914021 1914023 1914024 1914025 1911820 1911999 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2022-02-22 | N | 190.9892 | N | 26 | Y | Y | 1.1101 | 39.4971 | 51780.2057
[7 empty] | 292 | 3708 | 1912021 | 2022-02-22 16:42 | 2022-02-22 19:15 | 153 | 11kV | 306 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220636 B & C Phase DOLF : 10 Amp Excluded OMS 1912021 | February | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2022-02-22 | N | 153 | N | 26 | Y | Y | 1.1101 | 39.4971 | 223.6158
[7 empty] | 152 | 1819 | 1912046 | 2022-02-22 17:30 | 2022-02-22 19:20 | 110.3833 | 11kV | 14659.8667 | 157 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | EX ZN14891 Wyong Panel Section between CP40067 and CP43322 interrupted for safety repairs to Bonda on AB43811 | February | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2022-02-22 | N | 93.3749 | N | 26 | Y | Y | 1.1101 | 39.4971 | 10712.9982
[7 empty] | 1163 | 14600 | 1912050 | 2022-02-22 17:32 | 2022-02-22 19:54 | 142 | 11kV | 38961 | 339 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220633 2 fault operation 3 phase Overcurrent Removed tree branch pole GW-10001 | February | 2022 | 2022Q3 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2022-02-22 | N | 114.9292 | N | 26 | Y | Y | 1.1101 | 39.4971 | 28471.5496
[7 empty] | 1423 | 17504 | 1912058 | 2022-02-22 15:46 | 2022-02-22 21:01 | 315 | 11kV | 132875 | 931 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | N | IR79642 Herring Lucinda Tripped Relays: OC trip, Lockout Cause: Lightning arrestor at UGOH to S7045 + AB3048 fell apart See OMS 1914188 1914193 1912058 1912057 1911989 | February | 2022 | 2022Q3 | 2022 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2022-02-22 | N | 142.7229 | N | 26 | Y | Y | 1.1101 | 39.4971 | 97101.1309
[7 empty] | 133 | 1630 | 1912231 | 2022-02-23 08:33 | 2022-02-23 11:13 | 160 | 11kV | 320 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220641 A Phase DOLF : 10 Amp Excluded OMS 1912531 | February | 2022 | 2022Q3 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2022-02-23 | N | 160 | N | 9 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 1102 | 13982 | 1912386 | 2022-02-23 13:02 | 2022-02-23 14:23 | 81 | 11kV | 90396 | 1116 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S9550 Gwawley Bay Panel 11 tripped on Relays: 51AB (A and B phase Overcurrent Signals: 11kV Trip EFI's NIL Cause: Customers in street say branch fell from tree that is located in construction site opposite no.30. | February | 2022 | 2022Q3 | 2022 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Veg | 2022-02-23 | N | 81 | N | 9 | N | N | 1.1101 | 39.4971 | 66058.7306
[7 empty] | 984 | 12051 | 1912417 | 2022-02-23 14:00 | 2022-02-23 15:07 | 67 | 11kV | 43148 | 644 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At IR46673 Terrigal Penrose Tripped on Overcurrent with lockout Cause: Branch on 11kV between AB42543 and PT48338 | February | 2022 | 2022Q3 | 2022 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2022-02-23 | N | 67 | N | 9 | N | N | 1.1101 | 39.4971 | 31531.2857
[7 empty] | 1190 | 14780 | 1912474 | 2022-02-23 15:57 | 2022-02-23 16:05 | 8 | 11kV | 5768 | 721 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S10999 Kogarah 11kV Panel 7 Tripped on Earth Fault Trip with EFI Cause: Whilst restoring NAR90660 - DOp left earth on at S62206 Forest Roberts SW/A Cause: 11kV Bond Off drom Fault Current | February | 2022 | 2022Q3 | 2022 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | BAYSIDE | Unknown | Not Veg | 2022-02-23 | N | 8 | N | 9 | N | N | 1.1101 | 39.4971 | 4215.0843
[7 empty] | 113 | 1435 | 1912260 | 2022-02-23 09:12 | 2022-02-23 16:25 | 433 | 11kV | 866 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220644 A Phase DOLF : 10 Amp Excluded OMS 1912260 | February | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-02-23 | N | 433 | N | 9 | N | N | 1.1101 | 39.4971 | 632.8473
[7 empty] | 604 | 7652 | 1912478 | 2022-02-23 16:05 | 2022-02-23 17:54 | 109 | 11kV | 19509 | 297 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2568 St Peters 11kV Panel 7 Tripped on Relays: Earthb Fault, EFI, Fault Check Signals: 11kV Trip, TX4 Group Eargb, Zone Earth Cause: UG cable fault from S61715 to S35459 Note: EFI was found down at S7654 RPA Missended No 2 - Incorrect EFI Flag triggered DOp to close ondo fault duing restoration See OMS 1914120 1914124 1914123 1912512 1912478 | February | 2022 | 2022Q3 | 2022 | ZN2568:PA7 | ZN2568:PA7 | ZN02568/000007 | SYDNEY | UG | Not Veg | 2022-02-23 | N | 65.6869 | N | 9 | N | N | 1.1101 | 39.4971 | 14256.6018
[7 empty] | 76 | 933 | 1912524 | 2022-02-23 19:20 | 2022-02-23 20:00 | 40 | 11kV | 960 | 24 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220647 1 pin insulator & 3 sets ties replaced Excluded oms 1912524 | February | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2022-02-23 | N | 40 | N | 9 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 478 | 5809 | 1912566 | 2022-02-23 21:15 | 2022-02-24 00:30 | 195 | 11kV | 138307 | 1116 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN9550 Gwawley Bay Panel 43 tripped on RelaysL 150TN (Timed overcurrent with Earth Fault), 51 (B phase overcurrent), EFI, Earth Fault Check Cause: UG fault ro Faulty UGOH loacated between SW/B @ S49698 Corea Str North To LB35923 to S9948 Tara Corea See OMS 1914033 1914036 1914038 1914035 1914039 | February | 2022 | 2022Q3 | 2022 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | UG | Not Veg | 2022-02-23 | N | 123.931 | N | 9 | N | N | 1.1101 | 39.4971 | 101070.6762
[7 empty] | 193 | 2484 | 1913816 | 2022-02-24 08:26 | 2022-02-24 08:30 | 4 | 11kV | 6228 | 1557 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Rain Heavy | N | At Wyong panel 16 opened incorrectly by operator The correct panel that should have been opened was panel 14 NAR 90961 | February | 2022 | 2022Q3 | 2022 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | Unknown | Not Veg | 2022-02-24 | N | 4 | N | 11 | N | N | 1.1101 | 39.4971 | 4551.2387
[7 empty] | 515 | 6161 | 1912549 | 2022-02-23 19:47 | 2022-02-24 09:25 | 818 | 11kV | 286308 | 1057 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 220648 2 fault operations Tree onto Mains p FT-71324 ( sub 54554 ) possible HV into LV-EMSO attending Targets Sw 33399 = O/C trip Excluded OMS 1912549 | February | 2022 | 2022Q3 | 2022 | 509:33399 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2022-02-23 | N | 270.8685 | N | 9 | N | N | 1.1101 | 39.4971 | 209225.4417
[7 empty] | 523 | 6205 | 1912615 | 2022-02-24 07:40 | 2022-02-24 09:30 | 110 | 11kV | 33277 | 485 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 220652 Earth Fault Refer OMS 1912615 1912619 faulty Hazemeyer switchgear at sub 11274" SOP WATSON J DOP McPHAIL D | February | 2022 | 2022Q3 | 2022 | 257:81991 | 257:81991 | ZN00257/081991 | NEWCASTLE | OH | Not Veg | 2022-02-24 | N | 68.6124 | N | 11 | N | N | 1.1101 | 39.4971 | 24317.8501
[7 empty] | 409 | 5219 | 1912668 | 2022-02-24 09:14 | 2022-02-24 10:18 | 64 | 11kV | 60759 | 958 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN 9550 Gwawley Bay, 11kV panel No.1 tripped Protection relay flags/signal at Zone Sub: EF Trip, EFI Field EFI operations S48721, S48723, S9083 11kV UG cable fault between S9083 Port Hacking Box No.2 SW/B and S9816 Miranda Windermere SW/A See 1913883,1913884 1912668 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2022-02-24 | N | 63.4228 | N | 11 | N | N | 1.1101 | 39.4971 | 44400.8851
[7 empty] | 260 | 3356 | 1913094 | 2022-02-24 11:27 | 2022-02-24 12:55 | 88 | 11kV | 264 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220653 Thunderstorm 10 Amp, Phase A, Substation DOLF, Line DOLF "LF 74750 Blown A phase dolf : 10A Sub 70459 Blown A phase dolf : 10A OMS 1912745" SOP HUBY J DOP BYFIELD J | February | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-02-24 | N | 88 | N | 11 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 1254 | 15251 | 1912760 | 2022-02-24 11:48 | 2022-02-24 13:48 | 119.7167 | 11kV | 478.8667 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 220655 Emergency repairs on 11kv & 33kV pole BI-70140. JMH 33kv Xarm broken BI 70140 11kv isolated for clearance. JMH" SOP HUBY J | February | 2022 | 2022Q3 | 2022 | 814:82291 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2022-02-24 | N | 119.7167 | N | 11 | N | N | 1.1101 | 39.4971 | 349.9416
[7 empty] | 1640 | 19876 | 1912778 | 2022-02-24 12:36 | 2022-02-24 14:55 | 139 | 11kV | 2363 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 220658 Refer to OMS 1912816 & 1912778 11kv main of pin pole 8N-30594" Reported by Heli-Patrol - 8N30594 Centre conductor broken tie wire, conductor is resting on the x-arm and there are visible scorch marks SOP HUBY J DOP NICHOL L | February | 2022 | 2022Q3 | 2022 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2022-02-24 | N | 139 | N | 11 | N | N | 1.1101 | 39.4971 | 1726.8107
[7 empty] | 1461 | 18025 | 1912765 | 2022-02-24 12:04 | 2022-02-24 15:05 | 181 | 11kV | 543 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 220660 Blown A Phase HV Fuse on Sub 47582 and Fuse blew when re-tried. Customer stated nearby Lightning strike 2 nights ago. De-energised Sub 47582 (HV & LV) and Warning Tag applied on Pole. Please send crew and Dops to check HV arrestors Etc. LV not able to be interconnected. Faulty la cut away & supply restored 1505hrs SOP WATSON J DOP WILLIAMS L | February | 2022 | 2022Q3 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2022-02-24 | N | 181 | N | 11 | N | N | 1.1101 | 39.4971 | 396.8084
[7 empty] | 838 | 10285 | 1912767 | 2022-02-24 13:50 | 2022-02-24 15:06 | 76 | 11kV | 2204 | 29 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 220656 Refer to OMS 1912767 & 1912817 broken 11kv pin insulator 5G30124" Warren Weatherhead (Mondo Aerial Patrol) 0421619552 . Reporting defect on our pole, closest supply point used - 5G30124 The B phase 11KV bridge wire pin insulator is broken on this pole. SOP HUBY J DOP PASCOE D | February | 2022 | 2022Q3 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2022-02-24 | N | 76 | N | 11 | N | N | 1.1101 | 39.4971 | 1610.6182
[7 empty] | 1519 | 18663 | 1912823 | 2022-02-24 11:07 | 2022-02-24 16:00 | 293 | 11kV | 1172 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 220659 Broken 11Kv tie at pole AI10050 Also refer to OMS 1912737 & 1912823 DOP HUBY J SOP NORTON D | February | 2022 | 2022Q3 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2022-02-24 | N | 293 | N | 11 | N | N | 1.1101 | 39.4971 | 856.463
[7 empty] | 692 | 8871 | 1912871 | 2022-02-24 20:11 | 2022-02-24 20:22 | 11 | 11kV | 1903 | 173 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 220662 Heavy Rain Earth Fault refer to OMS 1912941 Multiple Trips already this week. PATROL REQUIRED !!" SOP ARLITSCH E | February | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2022-02-24 | N | 11 | N | 11 | N | N | 1.1101 | 39.4971 | 1390.6563
[7 empty] | 622 | 8000 | 1912982 | 2022-02-24 22:30 | 2022-02-25 01:13 | 163 | 11kV | 267577 | 2342 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN12570 Avoca 11kV feeder panel 21 "LB49826" tripped and reclosed to lock out on: Relays:A,B,C, Phase IOC, EFI Field EFI's S77326 UG fault section of 11kV feeder from AB41357 to S64802 Reginald Bridges (SW/A) See 1913952,1913955 1912982 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | UG | Not Veg | 2022-02-24 | N | 114.2515 | N | 11 | N | N | 1.1101 | 39.4971 | 195537.3794
[7 empty] | 497 | 5978 | 1912996 | 2022-02-25 01:21 | 2022-02-25 03:17 | 116 | 11kV | 86844 | 1181 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN4545 Meadowbank 11kV feeder panel 41 'LB570' feeder tripped, reclosed to lock out on: Relays: E/F, EFI, F/C, no 3 TX F/C Field EFI's S77186,S8853,S4606,S35110 UG Fault Section of 11kV feeder from S35110 Sybil Darvall (SW/B) to S8530 Marist Hillview (SW/A) to S7890 Warrawong Reserve (SW/B) 11kV feeder CB panel 41 at ZN4545 Meadowbank unable to close via DNMS or locally by DOP See 1913901,1913905 1912996 withdrawn | February | 2022 | 2022Q3 | 2022 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | UG | Not Veg | 2022-02-25 | N | 73.5343 | N | 7 | N | N | 1.1101 | 39.4971 | 63463.0337
[7 empty] | 1591 | 19420 | 1913003 | 2022-02-25 02:07 | 2022-02-25 03:25 | 78 | 11kV | 156 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 220665 Replaced 10A DOLF and fuse carrier complete as burnt in half at Sub 47188. Supply restored 0325hrs. SOP KEEGAN T DOP AUBIN R | February | 2022 | 2022Q3 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2022-02-25 | N | 78 | N | 7 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 454 | 5633 | 1912997 | 2022-02-25 01:33 | 2022-02-25 12:00 | 627 | 11kV | 129487 | 780 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S35370 Galston 11kV Panel 8 Tripped, Reclosed, Tripped and locked out Cause: Large Traa resting on 11kV Mains near PT2112 (Section from LB66058 to AB52 tee PT21112 Hansen Johnson Abnormal Switching: CP2422 and CP64783 Open, CP62158 Closed, Recloser CP555 Open, AB2063 Close, CP427 Open, CP62109 Closed See P<S 1914283 1914284, 1913013 1913012 1912997 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2022-02-25 | N | 166.009 | N | 7 | N | N | 1.1101 | 39.4971 | 94625.2804
[7 empty] | 415 | 5287 | 1913072 | 2022-02-25 09:15 | 2022-02-25 12:11 | 176 | 11kV | 26576 | 151 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 220667 ABS 42779 glowing red. Replaced under access permit. No trip. Excluded OMS 1913072 | February | 2022 | 2022Q3 | 2022 | 217:33605 | 217:33605 | ZN00217/033605 | LAKE MACQUARIE | OH | Not Veg | 2022-02-25 | N | 176 | N | 7 | N | N | 1.1101 | 39.4971 | 19420.9569
[7 empty] | 1011 | 12728 | 1913184 | 2022-02-25 17:29 | 2022-02-25 17:52 | 23 | 11kV | 1863 | 81 | HV | Vegetation Grow In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220669 Helipatrol HAZARD POLE AL10382 - VINE GROWING UP POLE THROUGH WIRES AND TOUCHING 11 KV NETWORK Excluded OMS 1913184 | February | 2022 | 2022Q3 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2022-02-25 | N | 23 | N | 7 | N | N | 1.1101 | 39.4971 | 1361.4255
[7 empty] | 508 | 6043 | 1913245 | 2022-02-25 19:10 | 2022-02-25 19:44 | 34 | 11kV | 340 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220670 Urgent defect - Pole AH11827 Bphase bridge wire pin insulator is broken Excluded OMS 1913245 | February | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2022-02-25 | N | 34 | N | 7 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 1316 | 16023 | 1913228 | 2022-02-25 15:54 | 2022-02-25 23:20 | 446 | 11kV | 446 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220671 A Phase DOLF : 16 Amp Excluded OMS 1913228 | February | 2022 | 2022Q3 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2022-02-25 | N | 446 | N | 7 | N | N | 1.1101 | 39.4971 | 325.9236
[7 empty] | 1150 | 14426 | 1913478 | 2022-02-26 13:25 | 2022-02-26 16:00 | 155 | 11kV | 7150 | 63 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12630 Peats Ridge Panel 8 Recloser CP44994 Mangrove Creek Tripped, Reclosed and Tripped and locked out on Relays: OC trip Cayuse: Burnt Tree branch found on OH mains adjacent to LK44006 See OMS 1914392 1914393 1914394 1913478 | February | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-02-26 | N | 113.4921 | N | 5 | N | N | 1.1101 | 39.4971 | 5225.0091
[7 empty] | 823 | 10155 | 1913501 | 2022-02-26 15:11 | 2022-02-26 16:25 | 74 | 11kV | 63122 | 853 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn 12570 Avoca, ex Panel 40, iR 41778 Amy Kincumber 0.1 tripped, reclosed and tripped on: Relays: OC No concrete cause ascertained - Storm | February | 2022 | 2022Q3 | 2022 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2022-02-26 | N | 74 | N | 5 | N | N | 1.1101 | 39.4971 | 46127.6958
[7 empty] | 1431 | 17630 | 1913369 | 2022-02-26 07:53 | 2022-02-26 18:15 | 622 | 11kV | 16410 | 195 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Section of Panel 10 Galsto CP50015 Quarry Old Northern interrupted Causel 11kV OH CCT down See OMS 1914420 1914421 1913369 1913405 | February | 2022 | 2022Q3 | 2022 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2022-02-26 | N | 84.1538 | N | 5 | N | N | 1.1101 | 39.4971 | 11991.944
[7 empty] | 472 | 5764 | 1913527 | 2022-02-26 18:25 | 2022-02-26 21:25 | 180 | 11kV | 1620 | 9 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | Ex Zn 14891 Wyong, ex panel 5, Section of feeder beyond 11kV LK 42328 was interruped for safety. To repair broken HV Cross Arm at Pole WK300. CC1: 22-"Refer to SOp" | February | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2022-02-26 | N | 180 | N | 5 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 1559 | 19107 | 1913454 | 2022-02-26 12:12 | 2022-02-27 02:15 | 843 | 11kV | 342960 | 1962 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | At Zn1287 Revesby 11kV Panel 15 tripped , reclosed, tripped and locked out on Relays: C phase IOC, C phase OC, Recloser Timing, Recloser Lockout Signals: 11kV Trip Field EFI's NIL Cause: Truck hot pole 53 Price Street.Section of 11kV defective from LB1869 to LB147 tee PT2071 Blue Gum Prince tee PT2004 River Henry Lawson See OMS 1914381 1913569 1913449 1913568 1913500 | February | 2022 | 2022Q3 | 2022 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-02-26 | N | 174.8012 | N | 5 | N | N | 1.1101 | 39.4971 | 250625.0524
[7 empty] | 1369 | 16765 | 1913609 | 2022-02-27 07:31 | 2022-02-27 10:11 | 160 | 11kV | 75898 | 6343 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | "132kv '261' feeder from BS.18005 Beaconsfield to S.188 Zetland including 132kv/11kv Tx 3 & 132kv/11kv Tx 4 and 11kv Panel 45 tripped on: BS.18005 Beaconsfield - A Protection - I/T Rec S.188 Zetland - 261 Fdr - A Protection - I/T Send, Multitrip 11kv Tx 4A Panel - TR-3, TR-4, TR-6 11kv Tx 3A Panel - TR-6 11kv Tx 2A Panel - Autoclosing timing relay, Lockout 11kv Tx 1A Panel - Autoclosing timing relay, Lockout11kv Panel 45 - Earth Fault, EFI, Fault Check Primary Fault - 11kV UG fault from S35077 - S2539 - S35036 (TX4 tripped - Protection Malfunction) See OMS 1914371 1914370 1913609 | February | 2022 | 2022Q3 | 2022 | ZN188:PA45 | ZN188:PA45 | ZN00188/000045 | SYDNEY | UG | Not Veg | 2022-02-27 | N | 11.9656 | N | 1 | N | N | 1.1101 | 39.4971 | 55464.0198
[7 empty] | 1365 | 16728 | 1913812 | 2022-02-28 08:20 | 2022-02-28 12:42 | 262 | 11kV | 6550 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Heavy | N | Ex14891 Pa8 Wyong Recloser CP43856 Failed During Swithcing Cause: Emergency Interruption - During swithcing CP43856 broke apart and was ind danger of making contact with live mains. See OMS 1914424 1913812 1913813 1913815 | February | 2022 | 2022Q3 | 2022 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2022-02-28 | N | 262 | N | 3 | N | N | 1.1101 | 39.4971 | 4786.5468
[7 empty] | 253 | 3151 | 1913945 | 2022-02-28 13:20 | 2022-02-28 15:25 | 125 | 11kV | 1625 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220682 11kV mains on crossarm pole BJ-40009 Excluded OMS 1913945 | February | 2022 | 2022Q3 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2022-02-28 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 1187.5021
[7 empty] | 853 | 10562 | 1913866 | 2022-02-28 09:39 | 2022-02-28 20:15 | 636 | 11kV | 1271.8667 | 2 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Rain Heavy | N | At S-62215 Muir Dasea No.2, 11kV RMCB has tripped. Protection Relay Flags at Sub: Nil Suspect faulty protection relay | February | 2022 | 2022Q3 | 2022 | ZN35900:PA10 | ZN35900:PA10 | ZN35900/000010 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2022-02-28 | N | 635.9333 | N | 3 | N | N | 1.1101 | 39.4971 | 929.4426
[7 empty] | 1670 | 20345 | 1914077 | 2022-03-01 04:52 | 2022-03-01 05:31 | 39 | 11kV | 33267 | 853 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Not Transformer | Unplanned | Rain Light | N | Section of 11kv Pnl 40 "Daviston" feeder at ZN 12570 AVOCA 11kv Recloser 41778 Amy Kinkumber tripped on overcurrent Flashover / Arcing - Bark on 11kv at PT 12100 | March | 2022 | 2022Q3 | 2022 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2022-03-01 | N | 39 | N | 7 | N | N | 1.1101 | 39.4971 | 24310.5424
[7 empty] | 1143 | 14404 | 1914136 | 2022-03-01 08:43 | 2022-03-01 12:30 | 227 | 11kV | 63050 | 1245 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Wind Storm | N | LID Trial 11KV link 13563 burning on pole feeder de energised for safety. Operator P Swan No protection operated - JMH | March | 2022 | 2022Q3 | 2022 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2022-03-01 | N | 50.6426 | N | 7 | N | N | 1.1101 | 39.4971 | 46075.0803
[7 empty] | 510 | 6122 | 1914228 | 2022-03-01 11:00 | 2022-03-01 12:38 | 98 | 11kV | 980 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Wind Storm | N | LID Trial 11KV main on pole HR 52302 Operator P wilkinson Supply restored 1238 JMH | March | 2022 | 2022Q3 | 2022 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2022-03-01 | N | 98 | N | 7 | N | N | 1.1101 | 39.4971 | 716.1551
[7 empty] | 1517 | 18623 | 1914409 | 2022-03-01 18:02 | 2022-03-01 20:10 | 128 | 11kV | 247902 | 2444 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | At ZN9700 11kV feeder panel 18 'President Kirawee' tripped on: Relays: A phase IOC, A phase timed O/C, EFI L/O, fault check Field EFI's :S48939,S9318,S9544,S9359,S9109,S9148 NOTE - 3 DMC in total fail, delayed restoration Separate interrruption @1615 Panel 18 tripped and reclosed DMA - Surge arrestor centre phase at PT9595 on section of 11kV feeder from LB35929 to S78940 Duneba Hunter tee PT9595 Tulong Pl PT9595 restored via LV// See 1915018,1915019,1915020 1914409 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN9700:PA18 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | OH | Not Veg | 2022-03-01 | N | 101.4329 | N | 7 | N | N | 1.1101 | 39.4971 | 181159.4697
[7 empty] | 1588 | 19386 | 1914429 | 2022-03-01 18:56 | 2022-03-01 20:50 | 114 | 11kV | 10219 | 149 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35600 Kingsford Panel 20 Tripped on Signals: 11lV Protection Trip, EFI Panels 15/17/20/23 Relays: Translay Flag, Frame leakage, Fault Check At S1074 Unitec SW/F tripped on Relays: Translay Flag Cause: @ S3351 Wales Hospital No3, NO 2 RMI Fuse area failed explosively See OMS 1915141 1915147 1915148 1914429 | March | 2022 | 2022Q3 | 2022 | ZN35600:PA20 | ZN35600:PA20 | ZN35600/000020 | RANDWICK | UG | Not Veg | 2022-03-01 | N | 68.5839 | N | 7 | N | N | 1.1101 | 39.4971 | 7467.7438
[7 empty] | 675 | 8655 | 1914336 | 2022-03-01 14:42 | 2022-03-02 00:41 | 599 | 11kV | 196967 | 1708 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 220688 11kV OHM down between poles CH-20024 & CH-20025. Excluded OMS 1914336 | March | 2022 | 2022Q3 | 2022 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2022-03-01 | N | 115.3203 | N | 7 | N | N | 1.1101 | 39.4971 | 143937.6741
[7 empty] | 745 | 9411 | 1914451 | 2022-03-01 20:07 | 2022-03-02 04:02 | 475 | 11kV | 82364 | 200 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12630 Peats Ridge Panel 1 CP45013 Gunderman Tripped on Relays: Overcurrent with Lockout Cause: Tree branch brough down 11kV from AB43179 to CP42515 (Tee PT14580, PT13624, PT12893) See OMS1920804 1920805 1914451 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2022-03-01 | N | 411.82 | N | 7 | N | N | 1.1101 | 39.4971 | 60189.1819
[7 empty] | 88 | 1159 | 1914671 | 2022-03-02 13:26 | 2022-03-02 14:30 | 64 | 11kV | 64 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220694 B Phase DOLF : 10 Amp Excluded OMS 1914671 | March | 2022 | 2022Q3 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2022-03-02 | N | 64 | N | 8 | N | N | 1.1101 | 39.4971 | 46.7693
[7 empty] | 1281 | 15617 | 1914696 | 2022-03-02 14:03 | 2022-03-02 16:10 | 127 | 11kV | 296152 | 2488 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN690 Campsie Zone 11kV Panel 25 "S3773 Seventh First Etc' tripped on Signals : Zone Earth #4 TX Group Earth, 11kV trip Relays: C phase time, IOC, Earth Fault, Fault check, EFI Field EFI's NIL UG fault from S690 panel 25 to S976 Sw/A to S3773 Sw/A to S3834 Sw/B 1914696 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-03-02 | N | 119.0322 | N | 8 | N | N | 1.1101 | 39.4971 | 216419.1466
[7 empty] | 1470 | 18167 | 1914727 | 2022-03-02 15:07 | 2022-03-02 16:15 | 68 | 11kV | 3944 | 58 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 220695 A Phase replaced faulty LAs Supply restored 1615hrs via LV interconnection, arrestor has been replaced & LV restored to normal Excluded oms 1914735 | March | 2022 | 2022Q3 | 2022 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2022-03-02 | N | 68 | N | 8 | N | N | 1.1101 | 39.4971 | 2882.1589
[7 empty] | 799 | 9975 | 1914687 | 2022-03-02 13:21 | 2022-03-02 16:30 | 189 | 11kV | 1354 | 98 | HV | Lightning Strike | Adverse Weather/Environment | OTHER - REFER COMMENTS | Unplanned | Rain Wind Storm | N | At Zn12630 Peats Rodge CP44995 Kulnura Triped and Reclosed Cause Lightning See OM<S 1918505 1918506 1918507 1914687 1914699 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | Unknown | Not Veg | 2022-03-02 | N | 13.8163 | N | 8 | N | N | 1.1101 | 39.4971 | 989.4633
[7 empty] | 609 | 7760 | 1914759 | 2022-03-02 16:40 | 2022-03-03 00:22 | 462 | 11kV | 107489 | 641 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Heavy | N | At S9900 Menai Zone 11kV Panel 2 Trippe don Signals: Zone Earth, No 1 TX group Earth 11kV trip Relays: A and C phase IOC with EFI Cause: RMI railure @ S9139 Yala Menai Due to water in substation See OMS 1915131 1915132 1915133 1914759 1914798 | March | 2022 | 2022Q3 | 2022 | ZN9900:PA2 | ZN9900:PA2 | ZN09900/000002 | SUTHERLAND | UG | Not Veg | 2022-03-02 | N | 167.6895 | N | 8 | N | N | 1.1101 | 39.4971 | 78549.7908
[7 empty] | 1293 | 15709 | 1914958 | 2022-03-03 10:30 | 2022-03-03 12:20 | 110 | 11kV | 2090 | 19 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Rain Heavy | N | LID 220700 Stay wire of pole JR-42405 to JR-47944 Resting on LV off sub 10838 Excluded OMS 1914958, 1915006. | March | 2022 | 2022Q3 | 2022 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2022-03-03 | N | 110 | N | 11 | N | N | 1.1101 | 39.4971 | 1527.3104
[7 empty] | 1054 | 13507 | 1914882 | 2022-03-02 23:34 | 2022-03-03 12:32 | 778 | 11kV | 10465 | 63 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 11kV recloser CP44994 Mangrove Creek Tripoped and Reclosed on Overcurrent Cause: Large Tree Brought down 4 Bays of HV in Kyola Ave See OMS 1920798 1902797 1920795 1914888 19148825 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-03-02 | N | 166.1111 | N | 8 | N | N | 1.1101 | 39.4971 | 7647.5133
[7 empty] | 530 | 6317 | 1915092 | 2022-03-03 13:32 | 2022-03-03 14:40 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 220702 B Phase DOLF : 10 Amp Excluded OMS 1915092 | March | 2022 | 2022Q3 | 2022 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2022-03-03 | N | 68 | N | 11 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 226 | 2760 | 1915025 | 2022-03-03 11:07 | 2022-03-03 17:05 | 358 | 11kV | 21334 | 73 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge Panel 6 CP49206 MTN West tripped on Overcurrent Cause: Tree on maisn adjacent to 11kV link CP41734 - Feeder isolated from AB43968 to AB44878 tee PT65652, PT11882, PT18044 See OMS1920820 1920821 1915025 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA6 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2022-03-03 | N | 292.2466 | N | 11 | N | N | 1.1101 | 39.4971 | 15590.258
[7 empty] | 1248 | 15211 | 1915129 | 2022-03-03 16:50 | 2022-03-03 17:40 | 50 | 11kV | 3550 | 71 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 220703 C Phase Main on Xarm pole 7M60121 Excluded OMS 1915129 & 1915200 | March | 2022 | 2022Q3 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2022-03-03 | N | 50 | N | 11 | N | N | 1.1101 | 39.4971 | 2594.2353
[7 empty] | 1177 | 14726 | 1915076 | 2022-03-03 17:00 | 2022-03-03 17:45 | 45 | 11kV | 1485 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 11kV Feeder innterrupted by DOp for lineworker to to get access to remove a tree branch on mains outside 129 Wattle Tree Rd Holgate Cause: Interrupted between LB44993 to AP42920 to LB43440 See OMS 1917247 1917249 1917250 1915218 1915119 | March | 2022 | 2022Q3 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2022-03-03 | N | 45 | N | 11 | N | N | 1.1101 | 39.4971 | 1085.1942
[7 empty] | 1634 | 19770 | 1915269 | 2022-03-03 19:00 | 2022-03-03 21:17 | 137 | 11kV | 28793 | 307 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN12690 Berkeley Vale 11kV Panel 26 tripped on RelaysL RHS A and B phase overcurrent IR50096 Tonliss Pacific tripped at 1900 on Relays: Overcurrent trip, Lockout Cause: Tree branch on OH mains near PT12862, removed by DOp See OMS 1917270 1917272 1915269 1915275 1915277 1915278 | March | 2022 | 2022Q3 | 2022 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2022-03-03 | N | 93.7883 | N | 11 | N | N | 1.1101 | 39.4971 | 21041.0752
[7 empty] | 1049 | 13464 | 1914724 | 2022-03-02 19:21 | 2022-03-03 23:42 | 1701 | 11kV | 371420 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12650 Peats Ridge CP61375 Wise Ferry Niara 1.3 tripped on relays: Overcurrent, SEF, Lockout See OMS1920826 1920827 1920828 1914724 Cause: Tree branch brought down 11kV mainn. 1 Bay before AB40598. Feeder is isolated between LK43962 to Recloser CP45013 Gunderman Note: Confirmed on DNMS that CP61375 Tripped @ 1921 on 02/03/2022 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2022-03-02 | N | 1139.3252 | N | 8 | N | N | 1.1101 | 39.4971 | 271422.781
[7 empty] | 1511 | 18576 | 1915327 | 2022-03-04 00:22 | 2022-03-04 02:30 | 128 | 11kV | 87544 | 879 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | At Zn9252 Jannali Panel 25 tripped and reclosed to lockoiut on Relays: B and C phase OC trip, reclose and lockout Cause: 11kV AB35478 damaged insulators (Zone side) See OMS 1917210 1917213 1917214 1915327 1915328 | March | 2022 | 2022Q3 | 2022 | ZN9252:PA25 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Not Veg | 2022-03-04 | N | 99.595 | N | 19 | N | N | 1.1101 | 39.4971 | 63974.5731
[7 empty] | 988 | 12084 | 1915338 | 2022-03-04 03:36 | 2022-03-04 05:40 | 124 | 11kV | 49107 | 992 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | AT ZN1183 Lindfield 11kV Panel 16 tripped on Relays: B and C phase Overcurrent with reclose lockout Signals: 11kV trip with efi Cause: Load side contact burnt off at AB3233 and mains annealled between AB3233 and S61523 See OMS 1918533 1918536 1918537 1915338 | March | 2022 | 2022Q3 | 2022 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Not Veg | 2022-03-04 | N | 49.503 | N | 19 | N | N | 1.1101 | 39.4971 | 35885.9472
[7 empty] | 1362 | 16686 | 1915354 | 2022-03-04 05:22 | 2022-03-04 07:07 | 105 | 11kV | 23940 | 228 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Art Zn15013 Terrey Hill 11kV feeder No6 tripped and reclosed Tripped and locked out on Relays: C p[hase IOC, C phase TImed OC, Time delay, Lockout Signals: 11kV Trip Field EFIs: Nil DOp found branch on HV mains tnear LB23602 - Removed and feeder restored | March | 2022 | 2022Q3 | 2022 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2022-03-04 | N | 105 | N | 19 | N | N | 1.1101 | 39.4971 | 17494.6459
[7 empty] | 1401 | 17136 | 1915355 | 2022-03-04 05:24 | 2022-03-04 07:53 | 149 | 11kV | 221265 | 1485 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn35500 Top Ryde Panel 18 tripped and reclosed, tripped and locked out on Relays: EF, EFI Signals: TX2 Group Earth, 11kV Trip Field EFI's Nil Cause: DMA S8849 SW/A Open, SW/F @ S64810 Closed UG Cable fault See OMS 1917143 1917144 1915747 1915719 1915355 | March | 2022 | 2022Q3 | 2022 | ZN35500:PA18 | ZN35500:PA18 | ZN35500/000018 | RYDE | UG | Not Veg | 2022-03-04 | N | 149 | N | 19 | N | N | 1.1101 | 39.4971 | 161693.9358
[7 empty] | 50 | 635 | 1915416 | 2022-03-04 08:46 | 2022-03-04 10:00 | 74 | 11kV | 71410 | 965 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN2653 Epping 11kV Panel 31 Tripped on Relays: B phase OC, IOC, EFI, EFI Signals: 11kV Trip Field EFI's NIl | March | 2022 | 2022Q3 | 2022 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | UG | Not Veg | 2022-03-04 | N | 74 | N | 19 | N | N | 1.1101 | 39.4971 | 52184.3218
[7 empty] | 1235 | 15127 | 1915423 | 2022-03-04 08:57 | 2022-03-04 10:30 | 93 | 11kV | 465 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220711 A Phase DOLF : 10 Amp Excluded OMS 1915423 | March | 2022 | 2022Q3 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-03-04 | N | 93 | N | 19 | N | N | 1.1101 | 39.4971 | 339.8083
[7 empty] | 852 | 10561 | 1915499 | 2022-03-04 11:10 | 2022-03-04 11:22 | 12 | 11kV | 1212 | 101 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Section of 11kV Feeder ex Panle 8 @ ZN10995 Rockdale from LB31334 to LB31335 Interrupted to remove bat Cause: LB30217 Defective (Will Not Open) Cause: Bat on UGOH to S10125 | March | 2022 | 2022Q3 | 2022 | ZN10998:PA8 | ZN10998:PA8 | ZN10998/000008 | BAYSIDE | OH | Not Veg | 2022-03-04 | N | 12 | N | 19 | N | N | 1.1101 | 39.4971 | 885.6939
[7 empty] | 1264 | 15436 | 1915418 | 2022-03-04 08:51 | 2022-03-04 11:25 | 154 | 11kV | 415269 | 3507 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | At ZN15006 Dee Why 11kV Panel 13 labelled S79533 Tripped on Relays: OC B and C phase EFI Signals: 11kV Trip Group Eatth Abnormal Switching: SW/B @ S47635 Closed, SW/A S16989 Open, SW/B Closed @ S16559 SW/A Open @ S16733 Cause: USL24253 Burnt off Bond and links burnt - requires replacement See OMS 1917118 1917121 1917124 1917118 1915427 1915427 1915424 1915419 1915418 | March | 2022 | 2022Q3 | 2022 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | OH | Not Veg | 2022-03-04 | N | 118.4115 | N | 19 | N | N | 1.1101 | 39.4971 | 303466.3368
[7 empty] | 1512 | 18583 | 1915398 | 2022-03-04 10:09 | 2022-03-04 12:50 | 161 | 11kV | 10143 | 63 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN14144 Wamberal Panel 10 Feeder isolated for safety from LB40248 Tree on 11kV OH mains 236 Matcham Rd. 1917001 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2022-03-04 | N | 161 | N | 19 | N | N | 1.1101 | 39.4971 | 7412.2052
[7 empty] | 1577 | 19278 | 1915516 | 2022-03-04 12:00 | 2022-03-04 13:25 | 85 | 11kV | 595 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN12630 Peats Ridge Panel 10 11kV Isolated between LB45002 to LB14514 Tree branch on OH mains See OMS1915516 1915517 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA10 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2022-03-04 | N | 85 | N | 19 | N | N | 1.1101 | 39.4971 | 434.8085
[7 empty] | 533 | 6364 | 1915368 | 2022-03-04 08:10 | 2022-03-04 16:14 | 484 | 11kV | 30976 | 64 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 220713 OHM down beyond GW20327 11KV main broken at pole GW20327. Two spans of HV down along Alton rd. EmSO standing by. Advised S.O by phone. Appears from customer phone calls customers had low volts from 06:32am, when the main broke, then at 04/03/22 08:10 the feeder was isolated at ABS10841 to enact repairs | March | 2022 | 2022Q3 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2022-03-04 | N | 484 | N | 19 | N | N | 1.1101 | 39.4971 | 22636.3472
[7 empty] | 735 | 9366 | 1915384 | 2022-03-04 07:46 | 2022-03-04 16:30 | 524 | 11kV | 188304 | 1344 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 220712 3 phase Tree on ohm at pole MW-70466. Sw 82815 tripped 50T ABC O/C Reclose relay 11kv into LV at pole. LV Sub fuse 25093 blown on B & C phase 200amps replaced. | March | 2022 | 2022Q3 | 2022 | 233:82815 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Veg | 2022-03-04 | N | 140.1071 | N | 19 | N | N | 1.1101 | 39.4971 | 137607.0092
[7 empty] | 1406 | 17279 | 1915665 | 2022-03-04 16:01 | 2022-03-04 20:50 | 289 | 11kV | 85701 | 980 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | CP79940 Kincumber Bungoona Tripped on Relays: SEF, OC, and Lockout Field EDI's Nil Cause: Tree branch on 11kV mains 431 Avoca Dribve See OMS 1918550 1918551 1915665 1915669 | March | 2022 | 2022Q3 | 2022 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2022-03-04 | N | 87.45 | N | 19 | N | N | 1.1101 | 39.4971 | 62627.763
[7 empty] | 1089 | 13913 | 1915726 | 2022-03-04 19:03 | 2022-03-04 20:50 | 107 | 11kV | 321 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID Trial Blown Dolf C phase : 10 Amp No cause found Excluded OMS 1915726 | March | 2022 | 2022Q3 | 2022 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2022-03-04 | N | 107 | N | 19 | N | N | 1.1101 | 39.4971 | 234.5773
[7 empty] | 424 | 5325 | 1915752 | 2022-03-04 20:51 | 2022-03-04 21:37 | 45.9833 | 11kV | 1287.5333 | 28 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID Trial Dead Possum at base of pole blown dolfs B and C Phase : 40Amp Operator John Morris OMS 1915760 & OMS 1915754 related | March | 2022 | 2022Q3 | 2022 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2022-03-04 | N | 45.9833 | N | 19 | N | N | 1.1101 | 39.4971 | 940.8914
[7 empty] | 1494 | 18397 | 1915756 | 2022-03-04 20:59 | 2022-03-04 22:51 | 112 | 11kV | 2352 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Section of 11kV Panel 6 Recloser CP24722 Forest Crozier tripped on Overcurrent Cause not ascertained for outage CP79807 Open CP20632 Closed See OMS1917413 1915756 | March | 2022 | 2022Q3 | 2022 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2022-03-04 | N | 112 | N | 19 | N | N | 1.1101 | 39.4971 | 1718.7722
[7 empty] | 739 | 9372 | 1915743 | 2022-03-04 23:15 | 2022-03-05 01:26 | 131 | 11kV | 13594 | 106 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | No Weather Impact | N | LID 220716 3 phase MVA pole 4I-40007 broken HV X-Arm. JMH Excluded OMS 1915743 & 1915765 | March | 2022 | 2022Q3 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2022-03-04 | N | 128.2453 | N | 19 | N | N | 1.1101 | 39.4971 | 9934.0942
[7 empty] | 1023 | 12970 | 1915774 | 2022-03-05 00:55 | 2022-03-05 01:57 | 62 | 11kV | 99262 | 1601 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn15005 Belrose 11kV Panel 8 Tripped, reclosed and locked out on Relays: A and C phase IOC, Reclose time delay, lockout Signals: 11kVC trip Field EFI's nil Cause: 11kV Mains twisted together Near LB 64765 Fixed by Dop | March | 2022 | 2022Q3 | 2022 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Veg | 2022-03-05 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 72537.7419
[7 empty] | 791 | 9909 | 1915738 | 2022-03-04 19:47 | 2022-03-05 02:42 | 415 | 11kV | 80925 | 195 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | No LID Report Broken 11kV Insulator at pole IV-93558 Excluded OMS 1915738 | March | 2022 | 2022Q3 | 2022 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | OH | Not Veg | 2022-03-04 | N | 415 | N | 19 | N | N | 1.1101 | 39.4971 | 59137.6031
[7 empty] | 584 | 7374 | 1915851 | 2022-03-05 10:45 | 2022-03-05 12:47 | 122 | 11kV | 50477 | 659 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN 9550 Gwawley Bay, 11kV Panel 9 has tripped on Relays - EF & EFI Signals TX3 GE, 11 kV trip Field EFI's S9370,S9278,S9947,S9395 11kV UG Fault from S9395 Sw/B to S9899 Sw/A to S9123 Sw/A tee to PT9745 See1917303,1917306,1917310 1915851 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN9550:PA9 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | UG | Not Veg | 2022-03-05 | N | 76.5964 | N | 4 | N | N | 1.1101 | 39.4971 | 36887.1028
[7 empty] | 1496 | 18411 | 1915813 | 2022-03-05 08:45 | 2022-03-05 13:00 | 255 | 11kV | 10710 | 42 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN 14891 Wyong ex panel 20 'Warnervale West Railway' 11kV feeder from AB44518 to Link 44810 interrupted to carry out repairs. 11kV bond burnt off near PT14451 1915813 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2022-03-05 | N | 255 | N | 4 | N | N | 1.1101 | 39.4971 | 7826.5521
[7 empty] | 245 | 2992 | 1915780 | 2022-03-05 02:41 | 2022-03-05 15:50 | 789 | 11kV | 6312 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex ZN12660 Woy Woy Panel 14 labelled 'LB 14814' etc 11kV Recloser 45093 Wondabyne has tripped on Relays:SEF trip Filed EFI's: NIL Tree/branch bought down OH Located adjacent to USL 40638 | March | 2022 | 2022Q3 | 2022 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2022-03-05 | N | 789 | N | 4 | N | N | 1.1101 | 39.4971 | 4612.6234
[7 empty] | 1616 | 19637 | 1916005 | 2022-03-06 02:21 | 2022-03-06 03:50 | 89 | 11kV | 81969 | 921 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN10998 Rockdale Panel 26 tripped on Signals: 11kV trip A protection Relays: A and B phase IOC B protection relays: Phase IOC, reclose Cause: Branch on 11kV near AB31208 | March | 2022 | 2022Q3 | 2022 | ZN10998:PA26 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | OH | Veg | 2022-03-06 | N | 89 | N | 6 | N | N | 1.1101 | 39.4971 | 59900.5275
[7 empty] | 1003 | 12502 | 1916006 | 2022-03-06 03:06 | 2022-03-06 10:55 | 469 | 11kV | 2790 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 220729 DOLF : 10 Amp HV CABLE AT SUB 70436 TOUCHED X ARM Excluded OMS 1916006 | March | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-03-06 | N | 465 | N | 6 | N | N | 1.1101 | 39.4971 | 2038.8497
[7 empty] | 730 | 9311 | 1916052 | 2022-03-06 09:04 | 2022-03-06 11:30 | 146 | 11kV | 876 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 220730 Single phase DOLF : 16 Amp Excluded OMS 1916052 | March | 2022 | 2022Q3 | 2022 | 509:33397 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2022-03-06 | N | 146 | N | 6 | N | N | 1.1101 | 39.4971 | 640.155
[7 empty] | 389 | 5121 | 1916084 | 2022-03-06 10:45 | 2022-03-06 12:30 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 220732 Single phase DOLF : 10 Amp Excluded OMS 1916084 | March | 2022 | 2022Q3 | 2022 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2022-03-06 | N | 105 | N | 6 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 890 | 10918 | 1915234 | 2022-03-03 15:12 | 2022-03-06 14:40 | 4288 | 11kV | 45690 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S14891 Wyong ex Panel 12 CP45015 Brush Creek Tripped on Relays: Overcurrent Auto link at CP44776 Brush ctreek tripped on Roadside Cause: 11kV Mains down adjacent to PT14888 MG connected to PT13354 Brush Creek Yarra7.0 by Do OSullivan See OMS 1920847 1920849 1920848 1915234 1915986 | March | 2022 | 2022Q3 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2022-03-03 | N | 801.5789 | N | 11 | N | N | 1.1101 | 39.4971 | 33388.9044
[7 empty] | 1111 | 14056 | 1915605 | 2022-03-03 14:04 | 2022-03-06 16:22 | 4458 | 11kV | 1174859 | 281 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Flood | N | LID 220701 RAGCB 42064 Auto Open. Extensive Flooding has caused delays to restoration due to access issues etc refer to related records Excluded OMS 1915105 | March | 2022 | 2022Q3 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2022-03-03 | N | 4180.9929 | N | 11 | N | N | 1.1101 | 39.4971 | 858552.3047
[7 empty] | 396 | 5145 | 1915051 | 2022-03-03 13:21 | 2022-03-06 18:15 | 4614 | 11kV | 910033 | 296 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge ex Panel 1 Recloser CP61375 Wise Ferry Biara 1.3 was Opened Manually due to Reports of wires down Abnormal: Network isolated beyond CP 44316 (Wires down) See OMS1920754 1920756 1920757 1920759 1920760 1920761 see excluded OMS1914724 1915086 1915473 1915977 1915978 1916136 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2022-03-03 | N | 3074.4358 | N | 11 | N | N | 1.1101 | 39.4971 | 665025.275
[7 empty] | 613 | 7819 | 1916211 | 2022-03-06 18:46 | 2022-03-06 19:30 | 44 | 11kV | 352 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220740 C Phase DOLF : 10 Amp Excluded OMS 1916211 | March | 2022 | 2022Q3 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2022-03-06 | N | 44 | N | 6 | N | N | 1.1101 | 39.4971 | 257.2312
[7 empty] | 654 | 8478 | 1916245 | 2022-03-06 23:11 | 2022-03-07 01:15 | 124 | 11kV | 120946 | 1216 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | At Zn4545 Meadowbank Panel 44 Tripped on Relays: EFI, Fault Check, SEL, Trip Alarm, OC alarm Fignals: TX3 Group Earh, Zone Earth, CB 44 Open Cause: @ PT2230 Reserve St 415 Transformer Busing Failure - See OMS 1918598 1918599 1918600 1916245 | March | 2022 | 2022Q3 | 2022 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Not Veg | 2022-03-06 | N | 99.4622 | N | 6 | N | N | 1.1101 | 39.4971 | 88383.7695
[7 empty] | 1209 | 14989 | 1916253 | 2022-03-07 00:11 | 2022-03-07 02:01 | 110 | 11kV | 128623 | 1175 | HV | Animal Possum | Animal | UGOH | Unplanned | Rain Heavy | N | At ZN129 Hunters Hill 11kV Panel 36L "LB2382' tripped Relays - Inst O/C A and B phase Field EFI's - NIL Flashover caused by possum at UGOH near PT2421 Philip Stanley, no apparent damage See 1918945,1918948,1916253 | March | 2022 | 2022Q3 | 2022 | ZN129:PA36 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Not Veg | 2022-03-07 | N | 109.4664 | N | 10 | N | N | 1.1101 | 39.4971 | 93993.8947
[7 empty] | 443 | 5469 | 1916277 | 2022-03-07 04:54 | 2022-03-07 09:42 | 288 | 11kV | 13536 | 47 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Rain Heavy | N | At Zn1230 Peats Ridge Recloser CP44945 Opened BY AOP due to reported of wires down CauseL OH down 4015 Wisemans Ferry Rd Lower Mangrove DOp patrolled and coupldnt fine any problem. DOp spoke to cuistomer and confirmed that site was already isolated Abnormal Swithcing: CP40607 to CP44079 isolated See OMS 1918371 1916285 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | Unknown | Unknown | 2022-03-07 | N | 288 | N | 10 | N | N | 1.1101 | 39.4971 | 9891.7096
[7 empty] | 550 | 6720 | 1916265 | 2022-03-07 02:29 | 2022-03-07 19:30 | 1021 | 11kV | 64475 | 66 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 220742 Mains Down pole CT-63985 Excluded OMS 1916265 | March | 2022 | 2022Q3 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2022-03-07 | N | 976.8939 | N | 10 | N | N | 1.1101 | 39.4971 | 47116.4283
[7 empty] | 980 | 12016 | 1916695 | 2022-03-07 19:49 | 2022-03-07 21:05 | 76 | 11kV | 228 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 220751 3 phase DOLF : 10 Amp Excluded OMS 1916695 | March | 2022 | 2022Q3 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2022-03-07 | N | 76 | N | 10 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 283 | 3634 | 1916654 | 2022-03-07 18:39 | 2022-03-07 21:15 | 156.3333 | 11kV | 2657.6667 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 11kV Recloser 45010 Palm Grove isolated for removal of tree off 11kV | March | 2022 | 2022Q3 | 2022 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2022-03-07 | N | 156.3333 | N | 10 | N | N | 1.1101 | 39.4971 | 1942.1444
[7 empty] | 331 | 4542 | 1916781 | 2022-03-07 22:57 | 2022-03-08 01:30 | 153 | 11kV | 216256 | 1746 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | ZN 12600 Lisarow Pnl 3 - tripped and locked out on: Relays: EF, EFI Suspected UG fault in UGOH cable to S14378, section of 11kV between AB 44327 and LK 44430 tee 14378. see 1918907, 1918909, 1918910, 1918911 | March | 2022 | 2022Q3 | 2022 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | UG | Not Veg | 2022-03-07 | N | 123.858 | N | 10 | N | N | 1.1101 | 39.4971 | 158033.5063
[7 empty] | 268 | 3475 | 1916822 | 2022-03-08 00:47 | 2022-03-08 02:15 | 88 | 11kV | 3256 | 37 | HV | Animal Other | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Section of 11kV feeder panel 10 "Chitaway" feeder Zn Berkeley Vale PT11658 Wombat Lakedge - roadside and middle HDOs 16 amp operatred Animal caused flashover at PT11658. | March | 2022 | 2022Q3 | 2022 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2022-03-08 | N | 88 | N | 18 | N | N | 1.1101 | 39.4971 | 2379.3888
[7 empty] | 206 | 2602 | 1916935 | 2022-03-08 08:28 | 2022-03-08 09:34 | 66 | 11kV | 117546 | 1781 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 342 Paddington 11kv Panel 17 has tripped on: Relays: OC + EF - C phase EF Front line feeder cable fault. | March | 2022 | 2022Q3 | 2022 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2022-03-08 | N | 66 | N | 18 | N | N | 1.1101 | 39.4971 | 85899.1498
[7 empty] | 334 | 4619 | 1916931 | 2022-03-08 08:29 | 2022-03-08 10:30 | 120.7833 | 11kV | 8575.6167 | 71 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | At PT11114 Warrawilla Turpentine - HDO centre phase blown See OMS 1916931 1916934 | March | 2022 | 2022Q3 | 2022 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2022-03-08 | N | 120.7833 | N | 18 | N | N | 1.1101 | 39.4971 | 6266.8077
[7 empty] | 89 | 1171 | 1916904 | 2022-03-08 07:51 | 2022-03-08 10:40 | 169 | 11kV | 1014 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220754 C Phase DOLF : 10 Amp Excluded OMS 1916904 | March | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-03-08 | N | 169 | N | 18 | N | N | 1.1101 | 39.4971 | 741.0013
[7 empty] | 778 | 9799 | 1916747 | 2022-03-07 21:41 | 2022-03-08 13:18 | 937 | 11kV | 64653 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Heavy | N | section of 11kV feeder Panel 17 Somersby zn Clearance given by Aop to interrupt from LB48850 onwards due to tree resting on CCT. AP issued and repairs made. | March | 2022 | 2022Q3 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2022-03-07 | N | 937 | N | 10 | N | N | 1.1101 | 39.4971 | 47246.5055
[7 empty] | 1430 | 17623 | 1917329 | 2022-03-08 14:33 | 2022-03-08 17:10 | 157 | 11kV | 37670 | 307 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN 14144 Wamberal - 11kV Panel 5 Beaufort feeder tripped: Relays A & B phase IOC Signals: 11kV trip UGOH short circuit fault - front line feeder fault see 1918629, 30, 31, 32 | March | 2022 | 2022Q3 | 2022 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | UG | Not Veg | 2022-03-08 | N | 122.7036 | N | 18 | N | N | 1.1101 | 39.4971 | 27528.1249
[7 empty] | 1097 | 13976 | 1917400 | 2022-03-08 15:25 | 2022-03-08 17:37 | 132 | 11kV | 210565 | 1748 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN 180 Mosman - 11kV Panel 30 feeder tripped on: Relays: A prot e/fault, B prot e/fault with fault check Signals: 11kV trip with EFI Field EFIs: S 507 11kV cable fault from S507 to S 36190 to s2415 to S8094. see 1918636, 38, 39 | March | 2022 | 2022Q3 | 2022 | ZN180:PA30 | ZN180:PA30 | ZN00180/000030 | MOSMAN | UG | Not Veg | 2022-03-08 | N | 120.4605 | N | 18 | N | N | 1.1101 | 39.4971 | 153874.6914
[7 empty] | 858 | 10624 | 1917333 | 2022-03-08 17:33 | 2022-03-08 18:54 | 81 | 11kV | 53371 | 884 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Insulated | Unplanned | Rain Heavy | N | At ZN 12690 Berkeley Vale 11kV Panel 7 'Jeager Sandpiper' tripped on Relays : Overcurrent Signals : 11kV trip Field EFI's: nil Cause not ascertained Weather related | March | 2022 | 2022Q3 | 2022 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2022-03-08 | N | 60.3744 | N | 18 | N | N | 1.1101 | 39.4971 | 39001.9526
[7 empty] | 285 | 3640 | 1917662 | 2022-03-08 18:43 | 2022-03-08 19:12 | 29 | 11kV | 24592 | 848 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn12570 Avoca Panel 34 tripped on Relays: Earth Fault, EFI Signals: 11kV trip Cause: Tree branch on OH | March | 2022 | 2022Q3 | 2022 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2022-03-08 | N | 29 | N | 18 | N | N | 1.1101 | 39.4971 | 17971.1083
[7 empty] | 307 | 4026 | 1917577 | 2022-03-08 17:20 | 2022-03-08 19:16 | 116 | 11kV | 22040 | 190 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | ## OMS 1917589 related Tree clashed with 11kv mains. tree fell clear and OH checked OK. supply restored 1916 | March | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-03-08 | N | 116 | N | 18 | N | N | 1.1101 | 39.4971 | 16106.1819
[7 empty] | 145 | 1734 | 1917056 | 2022-03-08 10:11 | 2022-03-08 20:20 | 609 | 11kV | 158949 | 261 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12580 Erina DOp OpenedLB42564 for safety Cause: Large Tree on mains at AB42150 | March | 2022 | 2022Q3 | 2022 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2022-03-08 | N | 609 | N | 18 | N | N | 1.1101 | 39.4971 | 116155.241
[7 empty] | 848 | 10515 | 1917462 | 2022-03-08 16:18 | 2022-03-08 20:20 | 242 | 11kV | 96014 | 1377 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12570 Avoca Panel 22 CP79940 Kincumber Bungo has tripped Abnormal switching:LS65223 SW closed, CP40382 Open RelaysL OC trip and Lockout Cause:Tree branch near AB 4330 See nOMS 1918464 1917468 1917462 | March | 2022 | 2022Q3 | 2022 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2022-03-08 | N | 69.7269 | N | 18 | N | N | 1.1101 | 39.4971 | 70164.1993
[7 empty] | 215 | 2674 | 1917137 | 2022-03-08 11:38 | 2022-03-08 21:50 | 612 | 11kV | 54720 | 340 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 220757 2 fault operation tree down at pole GW-50021 HV into LV Excluded oms 1917137 | March | 2022 | 2022Q3 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2022-03-08 | N | 160.9412 | N | 18 | N | N | 1.1101 | 39.4971 | 39987.762
[7 empty] | 164 | 2079 | 1917772 | 2022-03-08 20:38 | 2022-03-08 23:59 | 201 | 11kV | 207834 | 1034 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | Rain Heavy | N | At Zn 15002 NARRABEEN - 11kV Panel 8 'Nareen Narroy, etc' feeder tripped: Relays: O/C signals: 11kV trip field EFIs: nil Possum found on PT 15224 Irrawong Rd | March | 2022 | 2022Q3 | 2022 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2022-03-08 | N | 201 | N | 18 | N | N | 1.1101 | 39.4971 | 151878.9571
[7 empty] | 1492 | 18388 | 1917983 | 2022-03-09 00:05 | 2022-03-09 01:43 | 98 | 11kV | 85537 | 1031 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn 874 Concord Panel 3 '2031 etc' feeder tripped signals: 11kV trip Relays: EF, EFI Field EFIs: s 35569 UG Fault located between SW/B 35569, SW/A 7107 tee SW/A 8380 see 1918541, 1918543, 1918542, (withdrawn 1917983) | March | 2022 | 2022Q3 | 2022 | ZN874:PA3 | ZN874:PA3 | ZN00874/000003 | CANADA BAY | UG | Not Veg | 2022-03-09 | N | 82.9651 | N | 8 | N | N | 1.1101 | 39.4971 | 62507.9167
[7 empty] | 1360 | 16653 | 1917527 | 2022-03-08 16:59 | 2022-03-09 02:00 | 541 | 11kV | 54985 | 671 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | LID 220762 Vehicle hit pole IR-21162 pole requires replacement Excluded OMS 1917527 | March | 2022 | 2022Q3 | 2022 | 508:82576 | 508:82576 | ZN00508/082576 | PORT STEPHENS | OH | Not Veg | 2022-03-08 | N | 81.9449 | N | 18 | N | N | 1.1101 | 39.4971 | 40181.4162
[7 empty] | 1018 | 12858 | 1918022 | 2022-03-09 04:29 | 2022-03-09 05:40 | 71 | 11kV | 47325 | 825 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | ZN 3154 St Ives - 11kv Panel 22 'Roma Rd' tripped, reclosed and locked out: Relays: IOC, timed OC C phase, lock out, timer Signals: 11kV trip Field EFIs: Broken HV cross arm on pole MC-13830 See 1918621, 1918623, 1918624 | March | 2022 | 2022Q3 | 2022 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Not Veg | 2022-03-09 | N | 57.3636 | N | 8 | N | N | 1.1101 | 39.4971 | 34583.7141
[7 empty] | 1201 | 14871 | 1918176 | 2022-03-09 08:43 | 2022-03-09 09:44 | 61 | 11kV | 31811 | 557 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Heavy | N | At ZN 1285 GREENACRE PARK Panel 22 tripped on: Relays: A & C phase overcurrent, Fault check, EFI Signals: 11kV trip Field EFIs: S5443, S5468, S6052 S5992 Rickard Jacobs, SW/B end box failure See 1918978, 79 (withdrawn 1918388, 1918201, 1918176) | March | 2022 | 2022Q3 | 2022 | ZN1285:PA22 | ZN1285:PA22 | ZN01285/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-03-09 | N | 57.1113 | N | 8 | N | N | 1.1101 | 39.4971 | 23246.5405
[7 empty] | 1096 | 13968 | 1918047 | 2022-03-09 06:06 | 2022-03-09 10:06 | 240 | 11kV | 7770 | 45 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 220764 3 fault operations Single phase Overcurrent Pin Insulator broken pole EO-10420 Excluded OMS 1918047 | March | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2022-03-09 | N | 172.6667 | N | 8 | N | N | 1.1101 | 39.4971 | 5678.0868
[7 empty] | 492 | 5965 | 1917741 | 2022-03-08 20:20 | 2022-03-09 11:26 | 906 | 11kV | 2718 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser 65006 national park tripped on: Unkown as RTU had failed sect. of ZN9700 Kirrawee ex Panel 20 cause not ascertained | March | 2022 | 2022Q3 | 2022 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2022-03-08 | N | 906 | N | 18 | N | N | 1.1101 | 39.4971 | 1986.2342
[7 empty] | 558 | 6878 | 1916706 | 2022-03-07 20:10 | 2022-03-09 16:00 | 2630 | 11kV | 2630 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Flood | N | LID 220765 Single phase DOLF : 10 Amp Note: Mark Baxter assigned no access due to creek crossing being flooded, this has caused an extensive delay in restoration Customer also affected by multiple feeder trip and recloses during outage event refer to 1918197 and 1918299 Excluded OMS 1916706 | March | 2022 | 2022Q3 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2022-03-07 | N | 2630 | N | 10 | N | N | 1.1101 | 39.4971 | 1921.9264
[7 empty] | 1058 | 13538 | 1917825 | 2022-03-09 03:57 | 2022-03-09 16:25 | 748 | 11kV | 132261 | 1432 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind Strong | N | At ZN15001 Brookvale - 11kV Panel 6, tripped on: Relays: 50T A phase, EFI, FC Signals: 11kV trip Field EFIs: 16892, 15189, 16948, 61988, 16636, 16816, 50675, 78498, 16933 Top of HV pole FF-56219 burnt pole needing replacement - POLE FIRE 11kV feeder from S16933 to S 17046 tee S16278 See 1917825, 1918017, 1918184 CC1: 22-"Refer to SOp" | March | 2022 | 2022Q3 | 2022 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Not Veg | 2022-03-09 | N | 92.361 | N | 8 | N | N | 1.1101 | 39.4971 | 96652.4378
[7 empty] | 359 | 4903 | 1916896 | 2022-03-08 06:30 | 2022-03-09 17:15 | 2085 | 11kV | 62236 | 154 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12630 Peats Ridge Recloser CP46935 Tripped on A and B phase IOC Note: IR46935 Ironbark Kirks 0.8 was in Scan fail - Controlroom only aware of No supply via OMS Abnormal Switching: CP44077 Close CP44079 Open Cause: Large Tree on 11kV Mains on Link 43090 11kV Feeder Isolated from LB42326 to LK40558 tee PT13225 PT18791 PT18739 See OMS 1920810 1920811 1916869 1917015 1917018 19170191916912 1917020 1917021 1917083 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2022-03-08 | N | 404.1299 | N | 18 | N | N | 1.1101 | 39.4971 | 45480.2331
[7 empty] | 1636 | 19795 | 1918211 | 2022-03-09 09:12 | 2022-03-09 18:05 | 533 | 11kV | 122220 | 1773 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220767 Broken crossarm pole HV-30017 Excluded OMS 1918211 | March | 2022 | 2022Q3 | 2022 | 216:10722 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2022-03-09 | N | 68.934 | N | 8 | N | N | 1.1101 | 39.4971 | 89314.7711
[7 empty] | 1184 | 14764 | 1918683 | 2022-03-09 20:12 | 2022-03-09 23:45 | 213 | 11kV | 47547 | 687 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220769 interrupt to repair tree on OHM pole LS20102 Excluded OMS 1918681 | March | 2022 | 2022Q3 | 2022 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2022-03-09 | N | 69.2096 | N | 8 | N | N | 1.1101 | 39.4971 | 34745.9452
[7 empty] | 87 | 1085 | 1918181 | 2022-03-09 08:54 | 2022-03-10 03:10 | 1096 | 11kV | 4166 | 31 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Heavy | N | S5992 Rickard Jacbos Sw/B endbox failure. See 1919024, 1919025, 1919026 | March | 2022 | 2022Q3 | 2022 | ZN1285:PA33 | ZN1285:PA33 | ZN01285/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-03-09 | N | 134.3871 | N | 8 | N | N | 1.1101 | 39.4971 | 3044.3899
[7 empty] | 1549 | 18964 | 1918714 | 2022-03-10 02:55 | 2022-03-10 07:10 | 255 | 11kV | 3060 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 220771 A Phase DOLF : 10 Amp Excluded OMS 1918714 | March | 2022 | 2022Q3 | 2022 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Veg | 2022-03-10 | N | 255 | N | 6 | N | N | 1.1101 | 39.4971 | 2236.1577
[7 empty] | 1408 | 17325 | 1917718 | 2022-03-08 19:56 | 2022-03-10 10:31 | 2315 | 11kV | 122695 | 53 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Flood | N | 11kV recloser CP45015 Brush Creek Tripped, reclosed and Tripped on IOC Trip, OC Trip Cause: Awaiting Flood Waters to Subside to enable patrol of feeder Open Bonds before PT14888 MG connected to PT's See OMS1920834 1917718 | March | 2022 | 2022Q3 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2022-03-08 | N | 2315 | N | 18 | N | N | 1.1101 | 39.4971 | 89661.8871
[7 empty] | 807 | 10042 | 1916279 | 2022-03-07 04:44 | 2022-03-10 11:19 | 4715 | 11kV | 1321557 | 281 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Flood | N | LID 220743 Broken mains at pole MN-45440 Note: Area was affected by extensive flooding and was not accessible refer to related records Heli patrol completed on 10/3 and control room advised ok Excluded OMS 1916279 | March | 2022 | 2022Q3 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2022-03-07 | N | 4703.0498 | N | 10 | N | N | 1.1101 | 39.4971 | 965754.8763
[7 empty] | 825 | 10159 | 1918806 | 2022-03-10 09:28 | 2022-03-10 11:40 | 132 | 11kV | 178065 | 1745 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | At ZN14891 Wyong Panel 10 tripped and reclosed tripped and locked out on Relays: A and B phase OC, EF EFI, Lockout and timing 'Field EFI's NiL Mains have knocked of pins on section of 11kV feeder from ZN14891 Pa10 to SW/A @ S14897 Pacific Masonic to SW/A @ S14810 Lucca Pacific see OMS 1918989 1918806 | March | 2022 | 2022Q3 | 2022 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2022-03-10 | N | 102.043 | N | 6 | N | N | 1.1101 | 39.4971 | 130124.65
[7 empty] | 1441 | 17764 | 1918725 | 2022-03-10 07:07 | 2022-03-10 14:00 | 413 | 11kV | 983433 | 4132 | HV | 3rd Party Vehicle | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At ZN 36300 Balgowlah North - 11kV Pnl 11 "Condamine Sydney, etc" tripped on: Relays: earth fault with fault check Signals: 11kv trip Field EFIs: S16980 ABNORMAL SWITCHING: SW/A 16993 OPEN WITH SW/B 16724 CLOSED, SW/A 17102 CLOSED WITH SW/A 17119 OPEN, SW/A16962 OPEN AND SW/B CLOSED, SW/B 17132 CLOSED AND LINK 22338 OPEN. Failure caused by 3rd party error Crane into mains at 60 Perrone St. See 1919040, 43, 44, 47, 48, 51, 52, 53 for restoration steps | March | 2022 | 2022Q3 | 2022 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | Unknown | Not Veg | 2022-03-10 | N | 238.0041 | N | 6 | N | N | 1.1101 | 39.4971 | 718663.83
[7 empty] | 625 | 8046 | 1918932 | 2022-03-10 13:21 | 2022-03-10 14:15 | 54 | 11kV | 648 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220775 A Phase DOLF : 20 Amp Excluded OMS 1918932 | March | 2022 | 2022Q3 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-03-10 | N | 54 | N | 6 | N | N | 1.1101 | 39.4971 | 473.5393
[7 empty] | 1623 | 19688 | 1917180 | 2022-03-08 12:18 | 2022-03-10 14:40 | 3022 | 11kV | 89870 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At S12630 Peats Ridge Pane13 Recloser CP46763 Grants Keighley 0.3W tripped on Relays: Overcurrent, Trip and Earth Fault Cause: Tree branch brought down on OH. Large tree on 33KV feeder no 794 as well as section of 11kV mains adjacent to LB62288 AB40514 to LB61387. Tee to PT's 13375, PT 14931, PT 11620 ( interrupted) PT's 12356, PT 13693, PT13869 also interrupted. See OMS 1919796 1919797 1917180 1917735 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA13 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2022-03-08 | N | 1497.8333 | N | 18 | N | N | 1.1101 | 39.4971 | 65674.3453
[7 empty] | 674 | 8637 | 1918974 | 2022-03-10 14:35 | 2022-03-10 16:10 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220776 C Phase DOLF : 10 Amp Excluded OMS 1918974 | March | 2022 | 2022Q3 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2022-03-10 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 1285 | 15652 | 1919084 | 2022-03-10 19:11 | 2022-03-10 23:15 | 244.2667 | 11kV | 2198.4 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 220778 broken tapping at pole AG 80505 | March | 2022 | 2022Q3 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2022-03-10 | N | 244.2667 | N | 6 | N | N | 1.1101 | 39.4971 | 1606.5259
[7 empty] | 636 | 8240 | 1919100 | 2022-03-11 00:32 | 2022-03-11 07:35 | 423 | 11kV | 1692 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220780 A & C Phase DOLF : 16 Amp Excluded OMS 1919100 | March | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2022-03-11 | N | 423 | N | 6 | N | N | 1.1101 | 39.4971 | 1236.4637
[7 empty] | 1560 | 19118 | 1919133 | 2022-03-11 08:43 | 2022-03-11 10:35 | 112 | 11kV | 448 | 4 | HV | Animal Other | Animal | Stay Wire | Unplanned | No Weather Impact | N | LID 220782 A & B Phase DOLF : 16 Amp Bull rubbing in ground stay at pole DP-20214. Farmer to erect electric fence until proper stay guard can be built. Excluded OMS 1919133 | March | 2022 | 2022Q3 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2022-03-11 | N | 112 | N | 6 | N | N | 1.1101 | 39.4971 | 327.3852
[7 empty] | 1508 | 18524 | 1919154 | 2022-03-11 09:27 | 2022-03-11 12:55 | 208 | 11kV | 112181 | 1389 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | The 11kV Panel 4 CB tripped, reclosed and locked out on Signals: 11kV Trup Relays: EF, EFI, Fault Check, Reclose timing + Lockout Field EFI's Cause: UG cable fault. There is an 11kV UG fault in one of the section of feeder from AB31104 to CO31001 to S10066 See OMS 1919822 1919827 1919828 1919829 1919831 1919832 1919154 | March | 2022 | 2022Q3 | 2022 | ZN10999:PA4 | ZN10999:PA4 | ZN10999/000004 | GEORGES RIVER | UG | Not Veg | 2022-03-11 | N | 80.7639 | N | 6 | N | N | 1.1101 | 39.4971 | 81978.566
[7 empty] | 1179 | 14734 | 1919156 | 2022-03-11 11:30 | 2022-03-11 13:00 | 90 | 11kV | 630 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 220785 X-arm broken at P. 7I-30019 Excluded OMS 1919156 | March | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2022-03-11 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 1292 | 15707 | 1915697 | 2022-03-04 17:20 | 2022-03-11 13:55 | 9875 | 11kV | 533250 | 54 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | U/G Cable | Unplanned | Flood | N | Section of 11kV feeder from LB41846 to PT 18872 Geoffrey Royle 0.7 to PT 14055 Geoffrey Vesta interrupted for safety. Multiple LV UG services underwater due to flooding. EX ZN12690 Berkeley Vale panel 6 "S18124 Krone Enterprise" 09/03/2022 09:26: Current status awaiting flood water to subside 06/03/2022 11:17: Dop attended but area is not safe to energise. Houses are still under water and access was through flood water. | March | 2022 | 2022Q3 | 2022 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | UG | Not Veg | 2022-03-04 | N | 9875 | N | 19 | N | N | 1.1101 | 39.4971 | 389683.3718
[7 empty] | 581 | 7309 | 1919272 | 2022-03-11 14:15 | 2022-03-11 14:56 | 41 | 11kV | 36212 | 907 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At ZN14892 Charmhaven 11kV Panel 8 "S18058' tripped on Relays:SEF Signals 11kV trip Field EFI'S: nil Cause of interruption - Burnt off bond @ AB44857 See 1919717, 1919718 1919272 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN14892:PA8 | ZN14892:PA8 | ZN14892/000008 | CENTRAL COAST | OH | Not Veg | 2022-03-11 | N | 39.925 | N | 6 | N | N | 1.1101 | 39.4971 | 26462.6615
[7 empty] | 3 | 61 | 1919346 | 2022-03-11 18:45 | 2022-03-11 19:50 | 65 | 11kV | 455 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220788 Heli patrol Split X arm pole 7M90218. | March | 2022 | 2022Q3 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2022-03-11 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 332.5006
[7 empty] | 247 | 3025 | 1919443 | 2022-03-12 14:44 | 2022-03-12 16:00 | 76 | 11kV | 380 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220790 A Phase DOLF : 10 Amp Excluded OMS 1919443 | March | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-03-12 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 223 | 2729 | 1919777 | 2022-03-12 15:17 | 2022-03-12 18:18 | 181 | 11kV | 12670 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | IR - CP63686 Blundaleer Empire Bay 0.2 DOp patrolled feeder - Unable to find cause | March | 2022 | 2022Q3 | 2022 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2022-03-12 | N | 181 | N | 3 | N | N | 1.1101 | 39.4971 | 9258.8623
[7 empty] | 1141 | 14396 | 1919504 | 2022-03-13 08:45 | 2022-03-13 09:40 | 55 | 11kV | 7040 | 128 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At PT78849 Wales Pelham DC interrupted Vehcile hit pole in roberts rd - Interrupted for safety and repair | March | 2022 | 2022Q3 | 2022 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-03-13 | N | 55 | N | 1 | N | N | 1.1101 | 39.4971 | 5144.6244
[7 empty] | 1050 | 13467 | 1914721 | 2022-03-02 15:01 | 2022-03-13 18:00 | 16019 | 11kV | 167946 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Flood | N | At S12650 Peats Ridge Panel 1 CP44945 Lower Mangrove Tripped on Overcurrent Cause: Tree branch Brought down OH Note: PT13729, PT12514, PT12571 and PT11983 OOS for >10 Days. Major Flooding See OMS1920726 1920728 1914721 1914805 1914806 1914807 1914808 1915324 1915686 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2022-03-02 | N | 2846.5424 | N | 8 | N | N | 1.1101 | 39.4971 | 122729.9832
[7 empty] | 975 | 11932 | 1919460 | 2022-03-12 17:05 | 2022-03-13 22:45 | 1780.2833 | 11kV | 67650.7667 | 38 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | S1673 Turramurra, Ex Panel 2, S4702 Campbell Clyde has a blown HV Fuse. Cause: Tree on OH Mains causing Distributor wires on ground. broken cross arm and poles have moved in ground. Fuse was being replaced and the Dop noticed an unusual noise inside the RMI. The 11kV Feeder From S4701 Roland Campbell Sw B to CP 373 Bogan Campbell tee to PT 64728 Campbell cooper and S4702 Campbell Clyde has been isolated to allow repairs. | March | 2022 | 2022Q3 | 2022 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2022-03-12 | N | 1780.2833 | N | 3 | N | N | 1.1101 | 39.4971 | 49437.1849
[7 empty] | 1215 | 15028 | 1919599 | 2022-03-14 04:07 | 2022-03-14 12:00 | 473 | 11kV | 2838 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn14891 Wyong Panel 5 labelled 'Wyong' 11kV Autolink 44783 'Smiths Rd' found operated Cause not ascertained 1919599,1919649 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2022-03-14 | N | 473 | N | 3 | N | N | 1.1101 | 39.4971 | 2073.9267
[7 empty] | 214 | 2664 | 1919731 | 2022-03-14 11:51 | 2022-03-14 14:10 | 138.65 | 11kV | 6100.6 | 44 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220796 split xarm pole LI-81080 | March | 2022 | 2022Q3 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2022-03-14 | N | 138.65 | N | 3 | N | N | 1.1101 | 39.4971 | 4458.1385
[7 empty] | 1170 | 14671 | 1919937 | 2022-03-14 14:15 | 2022-03-14 14:40 | 25 | 11kV | 100 | 4 | HV | Vandalism | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220797 sub isolated to replace stolen earth wires Sub 42232 has had both HV and LV Earths cut approx 2 metres above ground. Excluded oms 1919659 | March | 2022 | 2022Q3 | 2022 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2022-03-14 | N | 25 | N | 3 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 1112 | 14071 | 1919851 | 2022-03-15 09:00 | 2022-03-15 10:00 | 60 | 11kV | 120 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220803 A & B Phase DOLF : 10 Amp Pump Only. Has been out for several days but customer only rang in yesterday due to no access. I will put outage as 1 hour. Excluded OMS 1919851. | March | 2022 | 2022Q3 | 2022 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2022-03-15 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 1142 | 14399 | 1916302 | 2022-03-07 06:35 | 2022-03-15 16:20 | 12105 | 11kV | 1860994 | 189 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Flood | N | Ex Zn12630 Peats Ridge Panel 1 CP43962 Manually Interrupted by DOp due to downstream downstream hazards including flooding Master Event 192076 Abnormal Switching Supply down Stream of 44316 Isolated due to flooding Restoration Step: 1920768/70/72/73/74/75/76/77 Withdrawn: 1916302 1916535 1918416 1919079 191972 1919230 1919294 1919323 1919914 1919915 1920003 1920004 Confirmed on DNMS - Start time of Outage based On Load trent @CP45013 and Oms Job CP43962 Closed @ 1211 on 09/03/2022 CP40598 Closed @ 2023 on 10/03/2022 CP45013 Closed @ 1152 on 11/03/2022 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2022-03-07 | N | 9846.5291 | N | 10 | N | N | 1.1101 | 39.4971 | 1359959.5252
[7 empty] | 1453 | 17911 | 1920042 | 2022-03-15 16:20 | 2022-03-15 18:20 | 120 | 11kV | 1440 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV feeder from auto link CP44776 was interrupte dto enable restoration of HV network damaged by tree | March | 2022 | 2022Q3 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2022-03-15 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 15 | 205 | 1920181 | 2022-03-15 18:35 | 2022-03-15 20:40 | 125 | 11kV | 21500 | 172 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220806 11kV OHM damaged at pole JT-91504. | March | 2022 | 2022Q3 | 2022 | 204:82689 | 204:82689 | ZN00204/082689 | NEWCASTLE | OH | Not Veg | 2022-03-15 | N | 125 | N | 4 | N | N | 1.1101 | 39.4971 | 15711.5659
[7 empty] | 1060 | 13585 | 1920093 | 2022-03-15 19:46 | 2022-03-16 00:25 | 279 | 11kV | 128424 | 1235 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S9245 Engadine Panel 1 Tripped on Relays: SEL, 51B, Lockout, EFI Cause: Large tree down onHV and LV outside 105 Lanata St Engadine. Feeder Isolated from LB35197 to LB35272 tee to PT9006 Trafalga Glenview See OMS1920270 1920271 1920272 | March | 2022 | 2022Q3 | 2022 | ZN9245:PA1 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Veg | 2022-03-15 | N | 103.987 | N | 4 | N | N | 1.1101 | 39.4971 | 93848.4713
[7 empty] | 388 | 5116 | 1920127 | 2022-03-16 05:49 | 2022-03-16 06:57 | 68 | 11kV | 63978 | 1233 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At ZN129 Hunters Hill Panel 38 'S4060' Feeder has tripped Signals:11kV trip Relays A and B phase OC Filed EFI's @ Subs 49203 Animals/Birds outside 67 Huntleys Pt Rd See 1920506,1920508 1920127 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN129:PA38 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2022-03-16 | N | 51.8881 | N | 4 | N | N | 1.1101 | 39.4971 | 46753.2354
[7 empty] | 290 | 3678 | 1920049 | 2022-03-16 09:10 | 2022-03-16 11:10 | 120 | 11kV | 4920 | 41 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220807 Broken pin insualtoir pole EL-40042 Excluded OMS 1920049 | March | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2022-03-16 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 3595.3909
[7 empty] | 447 | 5510 | 1915012 | 2022-03-03 23:42 | 2022-03-16 18:45 | 18423 | 11kV | 503727 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Flood | N | AEx Zn12630 Peats Ridge ex Panel 1. 11kV IR44316 Wisemans Ferry was Manually Opened Due to emergency conditions 11kV Mains brought down by tree towards water. Note: Due to Major Flooding - All customers expericed an outage > 10 Days Note: Customer were continuously out from 02/03/2022 19:21 refer to previous event OMS 1920828 See OMS 1920729 1920733 1920734 1915012 1916203 1916205 19120020 1920024 1920026 1920027 | March | 2022 | 2022Q3 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2022-03-03 | N | 16790.9 | N | 11 | N | N | 1.1101 | 39.4971 | 368108.8342
[7 empty] | 1270 | 15508 | 1920326 | 2022-03-16 18:36 | 2022-03-16 21:20 | 164 | 11kV | 492 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ## LID Trial Broken LL lead Operator M baxter Excluded OMS 1920326 | March | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-03-16 | N | 164 | N | 4 | N | N | 1.1101 | 39.4971 | 359.5391
[7 empty] | 1551 | 18995 | 1920346 | 2022-03-16 20:12 | 2022-03-17 01:25 | 313 | 11kV | 159136 | 1264 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN14892 Charmhaven Panel 3 feeder has tripped Signals 11kV trip, Lock out Relays Lockout A+B phase timed O/C, reclose and timing relays Field EFI's: NIL 11kV OH mains down in tree adjacent LB 42481 Bond burnt off adjacent LB61138 LB42751 defective will not open DMA done 11kV feeder interrupted from LB4272 for safety at 2053 16/3/22 See 1920458, 1920460 1920341 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Veg | 2022-03-16 | N | 125.8987 | N | 4 | N | N | 1.1101 | 39.4971 | 116291.8951
[7 empty] | 504 | 6020 | 1920371 | 2022-03-17 03:22 | 2022-03-17 04:33 | 71 | 11kV | 4899 | 69 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220809 C Phase DOLF : 31 Amp Dead possum at base of sub pole. Excluded OMS No. 1920371 | March | 2022 | 2022Q3 | 2022 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Not Veg | 2022-03-17 | N | 71 | N | 5 | N | N | 1.1101 | 39.4971 | 3580.0447
[7 empty] | 605 | 7657 | 1920373 | 2022-03-17 03:56 | 2022-03-17 07:00 | 183.9 | 11kV | 13424.7 | 73 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | At PT15139 Mirool St EX Narrabeen Panel 4 'Collaroy Feeder' blew center and footpath HDO's TX failure PT restored via LV// 19020379 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Not Veg | 2022-03-17 | N | 183.9 | N | 5 | N | N | 1.1101 | 39.4971 | 9810.3748
[7 empty] | 719 | 9231 | 1920438 | 2022-03-17 10:12 | 2022-03-17 12:05 | 113 | 11kV | 202231 | 2360 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At ZN35500 Top Ryde Panel 27 Tripped Reclosed, Tripped and locked out on Relays: Timed OC, EF, EFI lockout relays Fault check relay Signals: Protection trip, Protection Latch, TX 3 Group Earth Anormal Switching: CP289 Close, SW/A at S5352 Open SW/F Closed at S64810 Sw/A Open at S8849 Cause: UGOH fault between S4341 o LB1918 tee PT1267 See OMS1920633 1920634 1920438 192484 1924839 1920442 1920447 | March | 2022 | 2022Q3 | 2022 | ZN35500:PA18 | ZN35500:PA18 | ZN35500/000018 | RYDE | Unknown | Unknown | 2022-03-17 | N | 85.6911 | N | 5 | N | N | 1.1101 | 39.4971 | 147784.45
[7 empty] | 1199 | 14862 | 1920443 | 2022-03-17 10:12 | 2022-03-17 12:05 | 113 | 11kV | 1469 | 13 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At Zn8000 Macquarie Park Panel 34 Tripped and locked out on Abnormal Switching: LB289 Closed, SW/A Open at S5352, SW/F CLosed at S64810, SW/A Opened at S8849 Unknown cause at the time of Interruption | March | 2022 | 2022Q3 | 2022 | ZN8000:PA34 | ZN8000:PA34 | ZN08000/000034 | RYDE | Unknown | Unknown | 2022-03-17 | N | 113 | N | 5 | N | N | 1.1101 | 39.4971 | 1073.5019
[7 empty] | 540 | 6488 | 1920588 | 2022-03-17 17:09 | 2022-03-17 19:50 | 161 | 11kV | 14329 | 89 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn1193 Lindfield Pannel 15 S5119 HV fuse tblown Cause: Tree branch caused LV mains to twit together which appears to have caused the HV fuse to blow See OMS 1920588 1920590 1920593 | March | 2022 | 2022Q3 | 2022 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2022-03-17 | N | 161 | N | 5 | N | N | 1.1101 | 39.4971 | 10471.2106
[7 empty] | 358 | 4856 | 1920650 | 2022-03-18 01:34 | 2022-03-18 04:35 | 181.35 | 11kV | 4352.4 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220811 A & B Phase DOLF : 31 Amp CC1: 22-"Refer to SOp" | March | 2022 | 2022Q3 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-03-18 | N | 181.35 | N | 9 | N | N | 1.1101 | 39.4971 | 3180.6055
[7 empty] | 299 | 3806 | 1920674 | 2022-03-18 08:42 | 2022-03-18 09:11 | 29 | 11kV | 20445 | 705 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN12560 West Gosford ex Panel 13, IR62731 Narara Creek Manns has tripped and locked out on B and C phase overcurrent. Bird has main contact with 11kV mains at 56 Reeves St Narara 1920676,1920677 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2022-03-18 | N | 29 | N | 9 | N | N | 1.1101 | 39.4971 | 14940.603
[7 empty] | 399 | 5168 | 1920712 | 2022-03-18 10:44 | 2022-03-18 12:35 | 111 | 11kV | 111 | 1 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220812 C Phase DOLF : 10 Amp Bat on mains. Blown Dolf Excluded OMS 1920712 | March | 2022 | 2022Q3 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2022-03-18 | N | 111 | N | 9 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 647 | 8405 | 1920743 | 2022-03-18 11:40 | 2022-03-18 13:01 | 81 | 11kV | 324 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220813 broken insulator at AK-52613 Excluded @oms oms 1920743 | March | 2022 | 2022Q3 | 2022 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2022-03-18 | N | 81 | N | 9 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 1581 | 19321 | 1920657 | 2022-03-18 05:19 | 2022-03-18 13:16 | 477 | 11kV | 146312 | 1451 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 220815 & 220823 3 phase Earth Fault B Phase to Earth Excluded OMS 1920657 | March | 2022 | 2022Q3 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2022-03-18 | N | 100.8353 | N | 9 | N | N | 1.1101 | 39.4971 | 106920.4941
[7 empty] | 294 | 3732 | 1920858 | 2022-03-18 18:26 | 2022-03-18 19:45 | 79 | 11kV | 79 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220816 DOLF : 10 Amp oms SAID SUB 71841, CORRECT SUB 11392. Excluded OMS 1920858 | March | 2022 | 2022Q3 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2022-03-18 | N | 79 | N | 9 | N | N | 1.1101 | 39.4971 | 57.7309
[7 empty] | 660 | 8510 | 1920870 | 2022-03-18 18:45 | 2022-03-18 19:50 | 65 | 11kV | 3055 | 47 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4990 City Central - 55/56H tripped on: Earth Fault (55H) UG cable fault. S5695 lost supply due to being a 2 Tx, split LV bar sub (not triplex) See1922141 1922146 | March | 2022 | 2022Q3 | 2022 | ZN4990:PA55 56GHJ | ZN4990:PA55 56GHJ | ZN04990/55 56GHJ | SYDNEY | UG | Not Veg | 2022-03-18 | N | 65 | N | 9 | N | N | 1.1101 | 39.4971 | 2232.5039
[7 empty] | 872 | 10817 | 1920884 | 2022-03-18 20:29 | 2022-03-18 23:15 | 166 | 11kV | 269103 | 2078 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn35800 bankstown - Pnl.14 tripped on: ABC OC Tree removed from OH near UGOH to S6210 See 1922150 1922152 1922153 1922154 1922158 1922159 1922160 | March | 2022 | 2022Q3 | 2022 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-03-18 | N | 129.501 | N | 9 | N | N | 1.1101 | 39.4971 | 196652.5352
[7 empty] | 1103 | 13983 | 1920929 | 2022-03-18 23:01 | 2022-03-18 23:45 | 44 | 11kV | 20548 | 467 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At ZN 9550 Gwawley Bay 11kV feeder panel No.4 'Bellingra Port' feeder tripped on: Relays: B and C phase O/C Field EFI's: NIL Cause not ascertained Patrolled no cause found | March | 2022 | 2022Q3 | 2022 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | OH | Veg | 2022-03-18 | N | 44 | N | 9 | N | N | 1.1101 | 39.4971 | 15015.8723
[7 empty] | 1053 | 13488 | 1920978 | 2022-03-19 10:50 | 2022-03-19 10:55 | 5 | 11kV | 260 | 52 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT12052 Hillcrest Ave Braith 0.3 - interrupted by DOp to remove possum from OH mains | March | 2022 | 2022Q3 | 2022 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2022-03-19 | N | 5 | N | 2 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 473 | 5765 | 1920999 | 2022-03-19 09:30 | 2022-03-19 14:20 | 290 | 11kV | 9570 | 33 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Section of 11kV feeder from USL43741 to AB41276 interrupted to repair HV cross arm | March | 2022 | 2022Q3 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2022-03-19 | N | 290 | N | 2 | N | N | 1.1101 | 39.4971 | 6993.4737
[7 empty] | 116 | 1447 | 1915305 | 2022-03-03 21:11 | 2022-03-19 15:55 | 22724 | 11kV | 469225 | 98 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Flood | N | LID 220709 Repir crossarm on pole 8U-10079 extended time due to limited access Excluded OMS 1915305 etc. | March | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2022-03-03 | N | 4788.0102 | N | 11 | N | N | 1.1101 | 39.4971 | 342895.7902
[7 empty] | 400 | 5172 | 1921154 | 2022-03-20 08:31 | 2022-03-20 10:53 | 142 | 11kV | 53428 | 499 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.32 tripped, reclosed & locked out on: A & B phase OC 11kV arrestors failed between S2492 Sw/B and LB1408 | March | 2022 | 2022Q3 | 2022 | ZN2635:PA32 | ZN2635:PA32 | ZN02635/000032 | RYDE | OH | Not Veg | 2022-03-20 | N | 107.0701 | N | 4 | N | N | 1.1101 | 39.4971 | 39043.6065
[7 empty] | 1467 | 18140 | 1921159 | 2022-03-20 13:30 | 2022-03-20 15:26 | 116 | 11kV | 1160 | 10 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 220824 Pole DP-10020 leaning due to broken stay, low OHM. Remnant of floods Excluded OMS 1921159 | March | 2022 | 2022Q3 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2022-03-20 | N | 116 | N | 4 | N | N | 1.1101 | 39.4971 | 847.6938
[7 empty] | 18 | 235 | 1921190 | 2022-03-20 12:24 | 2022-03-20 16:55 | 271 | 11kV | 3252 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220825 B & C Phase : 20 Amp A & B phase dolfs replaced at sub 53452 also Excluded OMS 1921190 | March | 2022 | 2022Q3 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-03-20 | N | 271 | N | 4 | N | N | 1.1101 | 39.4971 | 2376.4657
[7 empty] | 954 | 11556 | 1921271 | 2022-03-21 00:36 | 2022-03-21 02:00 | 84 | 11kV | 16401 | 1614 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.46 tripped, reclosed & tripped on: OC and EF Abnormal: LB1408 Open with LB3159 Closed Fire at the 11kV UGOH below PT2208 See 1922218 1922219 1922220 | March | 2022 | 2022Q3 | 2022 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | Unknown | Unknown | 2022-03-21 | N | 10.1617 | N | 2 | N | N | 1.1101 | 39.4971 | 11985.3671
[7 empty] | 47 | 623 | 1921328 | 2022-03-21 09:45 | 2022-03-21 10:10 | 25 | 11kV | 100 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220829 Broken Pin pole BP-60031 | March | 2022 | 2022Q3 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2022-03-21 | N | 25 | N | 2 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 818 | 10116 | 1921234 | 2022-03-20 17:03 | 2022-03-21 10:46 | 1063 | 11kV | 7917 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn14143 Somersby - Pnl.5 tripped on: A & B phase OC Note: Dop could not tell if S64883 or S68684 EFI operated No Access to S18084 - restoration delayed until next morning. Cause not ascertained See 1922196 1922197 1922198 | March | 2022 | 2022Q3 | 2022 | ZN14143:PA5 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Veg | 2022-03-20 | N | 84.2234 | N | 4 | N | N | 1.1101 | 39.4971 | 5785.5101
[7 empty] | 666 | 8593 | 1921518 | 2022-03-22 04:16 | 2022-03-22 04:56 | 40 | 11kV | 47040 | 1176 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn129 Hunters Hill - Pnl.36 tripped on A & C phase IOC Bat caused flashover adj LB2382 | March | 2022 | 2022Q3 | 2022 | ZN129:PA36 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Not Veg | 2022-03-22 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 34375.4446
[7 empty] | 318 | 4250 | 1921555 | 2022-03-22 08:47 | 2022-03-22 09:50 | 63 | 11kV | 63 | 1 | HV | Animal Flying Fox | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220835 B & C Phase DOLF's : 40 Amp sub isolated to remove bat off tx. Excluded oms 1921555 | March | 2022 | 2022Q3 | 2022 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2022-03-22 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 190 | 2456 | 1921633 | 2022-03-22 11:49 | 2022-03-22 13:40 | 111 | 11kV | 555 | 5 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220836 B Phase DOLF : 10 Amp Bird Excluded OMS 1921633 | March | 2022 | 2022Q3 | 2022 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2022-03-22 | N | 111 | N | 5 | N | N | 1.1101 | 39.4971 | 405.5776
[7 empty] | 1200 | 14863 | 1921634 | 2022-03-22 11:51 | 2022-03-22 14:40 | 169 | 11kV | 507 | 3 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | While isolating for NAR91928, DOP incorrectly opened Sw/W @ S.5704 Hickson Pottinger - Interrupting Tx2 | March | 2022 | 2022Q3 | 2022 | ZN8700:PA61 62GHJ | ZN8700:PA61 62GHJ | ZN08700/61 62GHJ | SYDNEY | Unknown | Not Veg | 2022-03-22 | N | 169 | N | 5 | N | N | 1.1101 | 39.4971 | 370.5006
[7 empty] | 167 | 2152 | 1921789 | 2022-03-22 18:57 | 2022-03-22 20:05 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220840 B Phase DOLF : 10 Amp Excluded OMS 1921789 | March | 2022 | 2022Q3 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2022-03-22 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 51 | 638 | 1921827 | 2022-03-23 01:49 | 2022-03-23 07:15 | 326 | 11kV | 2608 | 8 | HV | Animal Flying Fox | Animal | Fuse | Unplanned | No Weather Impact | N | LID 220842 BAT across A phase LF 47341 | March | 2022 | 2022Q3 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2022-03-23 | N | 326 | N | 5 | N | N | 1.1101 | 39.4971 | 1905.8495
[7 empty] | 932 | 11310 | 1921990 | 2022-03-23 15:51 | 2022-03-23 17:55 | 124 | 11kV | 124 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 220851 A Phase arrestor fault Excluded oms 1921990 | March | 2022 | 2022Q3 | 2022 | 513:83500 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2022-03-23 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 179 | 2346 | 1922021 | 2022-03-23 17:54 | 2022-03-23 21:53 | 239.0667 | 11kV | 9801.7333 | 41 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 220858 tree on mains adjacent sub 78784 Excluded oms 1922025 | March | 2022 | 2022Q3 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2022-03-23 | N | 239.0667 | N | 5 | N | N | 1.1101 | 39.4971 | 7162.8176
[7 empty] | 1674 | 20361 | 1922023 | 2022-03-23 18:17 | 2022-03-23 23:35 | 318 | 11kV | 318 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 220857 Single phase DOLF : 10 Amp Sub is faulty and needs to be replaced Excluded oms 1922023 (incorrectly IDs sub as 78927) | March | 2022 | 2022Q3 | 2022 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2022-03-23 | N | 318 | N | 5 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 833 | 10260 | 1922052 | 2022-03-24 00:45 | 2022-03-24 02:41 | 116 | 11kV | 130500 | 1125 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN874 Concord 11kV Panel 17 tripped on Relays: A phase IOC and EFI Signals: 11kV Trip, TX2 Group Earth, Zone Earth Cuase: 11kV Feeder from Zn974 Pa17 to S48393 is defective due to cable fault | March | 2022 | 2022Q3 | 2022 | ZN874:PA17 | ZN874:PA17 | ZN00874/000017 | CANADA BAY | UG | Not Veg | 2022-03-24 | N | 116 | N | 3 | N | N | 1.1101 | 39.4971 | 95365.5509
[7 empty] | 109 | 1410 | 1922064 | 2022-03-24 03:48 | 2022-03-24 04:45 | 57 | 11kV | 3705 | 65 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Rain Light | N | PT12725 Vena Leslie - HV fuse operated Possum on Tx | March | 2022 | 2022Q3 | 2022 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2022-03-24 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 2707.5047
[7 empty] | 1334 | 16264 | 1921998 | 2022-03-24 09:13 | 2022-03-24 10:07 | 54 | 11kV | 4266 | 79 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220861 Phase A wire on x arm, 11kV off pin @ FN-80198, reported from Heli Patrol Refer to OMS 1921998 SOP HOLLAND P DOP BAILEY S | March | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-03-24 | N | 54 | N | 3 | N | N | 1.1101 | 39.4971 | 3117.467
[7 empty] | 553 | 6773 | 1922042 | 2022-03-23 22:22 | 2022-03-24 14:50 | 988 | 11kV | 40642 | 364 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Rain Heavy | N | At ZN12580 Erina 11kV Panel 12 'S65464 Entrance Bonnal 0.1' tripped, reclosed and locked out on: Relays:EF, EFI, SEF, Reclose and L/O Signals 11kV Trip, Group Earth Field EFI's: S65464, S18016, S18172 Tree onto 11kV mains brought down 1 phase of CCT See1922394,1922395 1922042,1922050 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2022-03-23 | N | 111.6538 | N | 5 | N | N | 1.1101 | 39.4971 | 29699.9749
[7 empty] | 413 | 5258 | 1922427 | 2022-03-25 10:58 | 2022-03-25 15:15 | 257 | 11kV | 257 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220870 Substation DOLF Tree into LV services off sub, also refer to OMS 1922427 large tree brought down wires inside tip. No arhcing/sparking. | March | 2022 | 2022Q3 | 2022 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2022-03-25 | N | 257 | N | 3 | N | N | 1.1101 | 39.4971 | 187.808
[7 empty] | 1158 | 14538 | 1922474 | 2022-03-25 13:45 | 2022-03-25 15:24 | 99 | 11kV | 1584 | 16 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | 11kV OHM interupted to break taps at pole IV60710, isolation for clearance for emergency testing of 33kV UGM fdr 3239. DQ Isolated for clearance to test 33kV UG Refer to LID 1922921 and OMS 1922920 | March | 2022 | 2022Q3 | 2022 | 206:34437 | 206:34437 | ZN00206/034437 | LAKE MACQUARIE | UG | Not Veg | 2022-03-25 | N | 99 | N | 3 | N | N | 1.1101 | 39.4971 | 1157.5405
[7 empty] | 1629 | 19734 | 1922510 | 2022-03-25 16:16 | 2022-03-25 19:20 | 184.2167 | 11kV | 33895.8667 | 184 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Section of Pnl.17 Somersby interrupted from CP43257 (radial) to remove tree from OH mains | March | 2022 | 2022Q3 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2022-03-25 | N | 184.2167 | N | 3 | N | N | 1.1101 | 39.4971 | 24770.0996
[7 empty] | 1340 | 16352 | 1922660 | 2022-03-26 12:53 | 2022-03-26 15:01 | 128 | 11kV | 117743 | 1029 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | AT S965 Pennant Hills Panel 43 Tripped on Relays: SEF SIgnals: 11kV Trip Cause: Bond may have burnt off after contact with birda See OMS 1922992 1922994 1922660 | March | 2022 | 2022Q3 | 2022 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2022-03-26 | N | 114.4247 | N | 2 | N | N | 1.1101 | 39.4971 | 86043.1116
[7 empty] | 1140 | 14354 | 1922580 | 2022-03-26 06:03 | 2022-03-26 18:25 | 742 | 11kV | 9604 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | LID 220873 A Phase RAGCB 74815 O/C Trip Wire off pole GE-600037 Excluded OMS 1922580 | March | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2022-03-26 | N | 738.7692 | N | 2 | N | N | 1.1101 | 39.4971 | 7018.3199
[7 empty] | 338 | 4743 | 1922725 | 2022-03-27 05:29 | 2022-03-27 06:55 | 86 | 11kV | 258 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220874 A Phase DOLF : 10 Amp Excluded OMS 1922725 | March | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-03-27 | N | 86 | N | 4 | N | N | 1.1101 | 39.4971 | 188.5388
[7 empty] | 231 | 2789 | 1922735 | 2022-03-27 09:18 | 2022-03-27 10:42 | 84 | 11kV | 168 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220876 C Phase DOLF : 10 Amp Excluded OMS 1922735 | March | 2022 | 2022Q3 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2022-03-27 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 943 | 11402 | 1922739 | 2022-03-27 09:53 | 2022-03-27 13:20 | 207 | 11kV | 414 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220875 Single phase DOLF : 6 Amp Excluded OMS 1922739 | March | 2022 | 2022Q3 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2022-03-27 | N | 207 | N | 4 | N | N | 1.1101 | 39.4971 | 302.539
[7 empty] | 917 | 11253 | 1922852 | 2022-03-28 00:47 | 2022-03-28 02:26 | 99 | 11kV | 134263 | 1612 | HV | Animal Possum | Animal | Bond | Unplanned | Rain Heavy | N | At ZN12650 West Gosford Panel 20 "S32338' Feeder has tripped Signals 11kV trip Relays OC/UFI,EFI Field EFI's @ Subs all down to S77001. Unable to access S18737,S12794 Possum @ UGOH to S61186 caused burnt bond at tee junction above between LB61991, S18104 and S61186 See 1922977,1922978 1922852 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2022-03-28 | N | 83.2897 | N | 4 | N | N | 1.1101 | 39.4971 | 98115.4403
[7 empty] | 93 | 1197 | 1922970 | 2022-03-28 11:04 | 2022-03-28 12:15 | 71 | 11kV | 71 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 220880 Single phase DOLF : 10 Amp Excluded OMS 1922970 | March | 2022 | 2022Q3 | 2022 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2022-03-28 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 51.8847
[7 empty] | 1059 | 13540 | 1922861 | 2022-03-28 03:18 | 2022-03-28 13:48 | 630 | 11kV | 75489 | 863 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 220878 11kV OHM on ground at pole VP-77025. Excluded OMS 1922861 | March | 2022 | 2022Q3 | 2022 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2022-03-28 | N | 87.4728 | N | 4 | N | N | 1.1101 | 39.4971 | 55165.1347
[7 empty] | 1587 | 19375 | 1922811 | 2022-03-27 18:20 | 2022-03-28 19:00 | 1480 | 11kV | 11840 | 8 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Section of 11kV mains defective from AB40526 to LK 42860 tee PT12951 Little Mooney CK Wise tee PT12263 Wise Ferry Hensons 1.5 tee PT 14429 Wise Ferry Meldrum Ex ZN12630 Peats Ridge 11kV Panel 11 'Somersby' Car hit pole PR605 Section of 11kV mains OOS to make emergency repairs 1922814,1922813,1922811 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2022-03-27 | N | 1480 | N | 4 | N | N | 1.1101 | 39.4971 | 8652.3228
[7 empty] | 501 | 6005 | 1923107 | 2022-03-28 19:57 | 2022-03-29 02:10 | 373 | 11kV | 253627 | 2279 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN36800 Waverley 11kV feeder Panel No58 'Tasman Phillip etc tripped on: Relays: E/F, EFI Field EFIs: S8570,S2132,S8981,S46847 11kV UG fault in section from S46847 Darley Carr (Sw/A) to S1183 Glebe St (Sw/A) See 1923195,1923197 1923107,1923134,192315,1923136,1923137,1923138 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN36800:PA58 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2022-03-28 | N | 111.2887 | N | 4 | N | N | 1.1101 | 39.4971 | 185343.1309
[7 empty] | 1377 | 16891 | 1923154 | 2022-03-29 03:38 | 2022-03-29 05:56 | 138 | 11kV | 246700 | 2035 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn14892 Charmhaven Panel 16 'Charmhaven San Remo' feeder has tripped Signals: 11kV trip, TX 2 GE. Relays 5IN, EFI, Reclose timing, Lockout, TX, Fault Chk Field EFI's @ Subs 12884 Suspect UGOH or UG cable fault S12884 to S46911 to S14548 See 1923244,1923246,1923247 1923154 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | UG | Not Veg | 2022-03-29 | N | 121.2285 | N | 1 | N | N | 1.1101 | 39.4971 | 180281.0836
[7 empty] | 1257 | 15314 | 1923512 | 2022-03-30 10:14 | 2022-03-30 12:45 | 151 | 11kV | 3322 | 22 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 220887 Condemed pole MT-30194 interrupted to break taps. Excluded oms1923512 | March | 2022 | 2022Q3 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2022-03-30 | N | 151 | N | 4 | N | N | 1.1101 | 39.4971 | 2427.6196
[7 empty] | 440 | 5446 | 1923748 | 2022-03-30 12:49 | 2022-03-30 17:32 | 283 | 11kV | 980 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220889 Trip & Reclose 1 fault operation Overcurrent | March | 2022 | 2022Q3 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2022-03-30 | N | 7.3134 | N | 4 | N | N | 1.1101 | 39.4971 | 716.1551
[7 empty] | 750 | 9460 | 1923567 | 2022-03-30 12:49 | 2022-03-30 19:00 | 371 | 11kV | 16326 | 172 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220890 Overcurrent Sectionliser opened at 12.49 Reloser back on.12.49 Also found blown surge arresttor at sub 27863 and replaces 16A b phase dolf. T & R on Sw 42004 see LID 220888 & 220889 Excluded oms 1923567, 1923574, 1923650 1923673 and 1923679 | March | 2022 | 2022Q3 | 2022 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2022-03-30 | N | 94.9186 | N | 4 | N | N | 1.1101 | 39.4971 | 11930.5593
[7 empty] | 188 | 2437 | 1923688 | 2022-03-30 21:21 | 2022-03-30 22:26 | 65 | 11kV | 390 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220892 C Phase DOLF : 10 Amp Excluded OMS 1923688 | March | 2022 | 2022Q3 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2022-03-30 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 629 | 8115 | 1923703 | 2022-03-31 03:28 | 2022-03-31 07:30 | 242 | 11kV | 89694 | 1178 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn965 Pennant Hills - Pnl.42 tripped on: B & C phase IOC @ F.1352 Water Board - B & C phase HDOs blown Cause not ascertained See 1924390 1924391 | March | 2022 | 2022Q3 | 2022 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Veg | 2022-03-31 | N | 76.1409 | N | 9 | N | N | 1.1101 | 39.4971 | 65545.7297
[7 empty] | 1022 | 12935 | 1923722 | 2022-03-31 05:46 | 2022-03-31 09:22 | 216 | 11kV | 57303 | 266 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC41845 North Erina tripped, reclosed, tripped, reclosed and locked out on: OC Tree on OH mains adj REC41845 See 1924401 1924402 | March | 2022 | 2022Q3 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2022-03-31 | N | 215.4248 | N | 9 | N | N | 1.1101 | 39.4971 | 41875.3422
[7 empty] | 1083 | 13885 | 1923708 | 2022-03-31 04:02 | 2022-03-31 12:40 | 518 | 11kV | 26418 | 51 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Section of Pnl.2 Galston Zone - Isolated from CP58 to PT2104 to PT2412 to PT2171 to PT1895 Centre phase bond burnt off pole DU-42111 See previous trip and reclose on Pnl.2 | March | 2022 | 2022Q3 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2022-03-31 | N | 518 | N | 9 | N | N | 1.1101 | 39.4971 | 19305.4952
[7 empty] | 363 | 4915 | 1924010 | 2022-03-31 16:16 | 2022-03-31 17:14 | 58 | 11kV | 78068 | 1346 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn847 Hornsby - Pnl.22 tripped on C phase OC Burnt bark over OH mains near tee off to PT1490 | March | 2022 | 2022Q3 | 2022 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Veg | 2022-03-31 | N | 58 | N | 9 | N | N | 1.1101 | 39.4971 | 57049.7918
[7 empty] | 1639 | 19866 | 1924039 | 2022-03-31 16:45 | 2022-03-31 18:35 | 110 | 11kV | 110 | 1 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220898 | March | 2022 | 2022Q3 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-03-31 | N | 110 | N | 9 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 749 | 9432 | 1924053 | 2022-03-31 17:00 | 2022-03-31 18:49 | 109 | 11kV | 75537 | 693 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | No LID Report Tree branch hit OHM at pole NR60460 cleared ok by dop S williams DQ NO LID ## | March | 2022 | 2022Q3 | 2022 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2022-03-31 | N | 109 | N | 9 | N | N | 1.1101 | 39.4971 | 55200.2116
[7 empty] | 638 | 8253 | 1924008 | 2022-03-31 16:11 | 2022-03-31 20:40 | 269 | 11kV | 105043 | 1100 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Rain Heavy | N | Ex Zn 12570 Avoca ex panel 21, Recloser 41397 Karalta Rd tripped,reclosed,tripped, reclosed and tripped on: Relays: EF, Lockout Section of feeder from S78807 Karalta Bronzewing 0.4 to S18017 Karalta Nursing Home has an UG fault caused by contractor using an underborer See 1924411,1924414,1924415 1924041,1924008,1924120 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN12570:PA21 | ZN12580:PA2 | ZN12580/000002 | CENTRAL COAST | UG | Not Veg | 2022-03-31 | N | 95.4936 | N | 9 | N | N | 1.1101 | 39.4971 | 76762.3262
[7 empty] | 505 | 6026 | 1924148 | 2022-03-31 19:27 | 2022-03-31 21:37 | 130.6667 | 11kV | 36841.6 | 627 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | EX ZN 12610 Long Jetty, ex panel 2, IR 62165 was manually opened Interrupted for safety reasons Pole @ PT11541 Rickard Pasadena has HV on Cross Arm, having come off its pin and causing a pole fire See 1924189, 1924213 1924166 withdrawn | March | 2022 | 2022Q3 | 2022 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2022-03-31 | N | 58.7585 | N | 9 | N | N | 1.1101 | 39.4971 | 26922.7546
[7 empty] | 1556 | 19068 | 1923965 | 2022-03-31 15:39 | 2022-04-01 10:50 | 1151 | 11kV | 539409 | 1516 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 220895 2 fault operations 3 phase Earth Fault frame leakage also operated at Cardiff zone and had to be reset, preventing S.O. from remotely restoring unfaulted section. Please investigate. Excluded oms 1923965 | March | 2022 | 2022Q3 | 2022 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Veg | 2022-03-31 | N | 355.8107 | N | 9 | N | N | 1.1101 | 39.4971 | 394184.1873
[7 empty] | 158 | 1919 | 1924389 | 2022-04-01 10:42 | 2022-04-01 14:25 | 223 | 11kV | 11596 | 52 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 220899 11kV Isolation to repair 33kV X arm split. Pole KS-40064 See OMS 1925127 for 33kV details | April | 2022 | 2022Q4 | 2022 | 229:34986 | 229:34986 | ZN00229/034986 | PORT STEPHENS | OH | Not Veg | 2022-04-01 | N | 223 | N | 8 | N | N | 1.1101 | 39.4971 | 8474.0148
[7 empty] | 663 | 8533 | 1924500 | 2022-04-01 13:21 | 2022-04-01 14:51 | 90 | 11kV | 54630 | 607 | HV | Burnt Contacts | Equipment Failure | O/H Link | Unplanned | No Weather Impact | N | Ex ZN12620 Noraville, ex Panel 3 AB40972 became open circuit on the footpath phase due to melted contacts. 1924500,1924502,1924526,1924531 withdrawn | April | 2022 | 2022Q4 | 2022 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2022-04-01 | N | 90 | N | 8 | N | N | 1.1101 | 39.4971 | 39921.9927
[7 empty] | 1016 | 12806 | 1924592 | 2022-04-01 15:25 | 2022-04-01 16:46 | 81 | 11kV | 10611 | 131 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN15013 Terrey Hills, Panel 4 labelled 'S16440 Aumona Mona' 11kV Recloser 21350 Booralia Kulgoa, tripped and locked out on: Relays:Overcurrent Field EFI's:S16440, S77552, UGOH Cnr Echunga and Boorallie, S16981 and S46835 Tree branch found on 11kV adjacent to 11kV link 23634, removed by DOp and restored. | April | 2022 | 2022Q4 | 2022 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2022-04-01 | N | 81 | N | 8 | N | N | 1.1101 | 39.4971 | 7754.2058
[7 empty] | 1236 | 15130 | 1924619 | 2022-04-01 16:13 | 2022-04-01 17:15 | 62 | 11kV | 620 | 10 | HV | Lightning Strike | Adverse Weather/Environment | Cross arm | Unplanned | No Weather Impact | N | LID 220901 11kV x arm struck by lightning at pole 9K-40265. No protection operated. | April | 2022 | 2022Q4 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2022-04-01 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 453.0777
[7 empty] | 98 | 1235 | 1924649 | 2022-04-01 17:07 | 2022-04-01 18:24 | 76.7833 | 11kV | 8369.3833 | 109 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | Removed tree off mains and restring bay of HV cu. work complete | April | 2022 | 2022Q4 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2022-04-01 | N | 76.7833 | N | 8 | N | N | 1.1101 | 39.4971 | 6116.0985
[7 empty] | 1443 | 17799 | 1924694 | 2022-04-01 18:22 | 2022-04-01 21:00 | 158 | 11kV | 178754 | 1502 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | At ZN 9245 Engadine Panel 10 tripped and reclosed, tripped and locked out Relay - 1st (B and C phase IOC) 2nd SEF Field EFI - Nil Tree on Mains in Sladden Rd. On clearance from Dop feeder Panel 10 closed. Tripped on SEF the second time. DOp asked to patrol feeder and local burnt off bonds. DOp located burnt off bonds at Pole EN-00849 See 1925176,1925177,1925179 1924698,1924697,1924694,1924728 withdrawn | April | 2022 | 2022Q4 | 2022 | ZN9245:PA10 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | OH | Not Veg | 2022-04-01 | N | 119.0107 | N | 8 | N | N | 1.1101 | 39.4971 | 130628.1508
[7 empty] | 1178 | 14733 | 1924700 | 2022-04-01 20:30 | 2022-04-02 02:45 | 375 | 11kV | 16125 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At 35370 Galston ex 11kV Panel No2 'Galston High School feeder' USL LK 1556 was opened by DOp for large tree on 11kV and 415V mains near PT667 Laurie Carters Tree Branch on OH mains 1924700 withdrawn | April | 2022 | 2022Q4 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2022-04-01 | N | 375 | N | 8 | N | N | 1.1101 | 39.4971 | 11783.6744
[7 empty] | 1207 | 14971 | 1924747 | 2022-04-02 05:14 | 2022-04-02 07:18 | 124 | 11kV | 6324 | 51 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At ZN 14891 Wyong ex Panel 16, 11kV footpath phase HDO has blown at PT13099 Palmer Wolsely 31.5 A Cause of Interruption: Fuse fatigue 1924749,1924747 withdrawn | April | 2022 | 2022Q4 | 2022 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2022-04-02 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 4621.3927
[7 empty] | 1120 | 14206 | 1924757 | 2022-04-02 07:13 | 2022-04-02 08:16 | 63 | 11kV | 90216 | 1432 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN 15001 Brookvale, 11kV Panel 6 'Winbourne Rd 38' feeder tripped Relays 'A & B' phase IOC Signals 11kV Trip Field EFI's: S16892, S15189 (No operation), S16948 Crow contact with 11kV below AB24223 | April | 2022 | 2022Q4 | 2022 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Not Veg | 2022-04-02 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 65927.1919
[7 empty] | 544 | 6625 | 1924804 | 2022-04-02 10:13 | 2022-04-02 12:10 | 117 | 11kV | 117 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220905 A Phase DOLF : 10 Amp Excluded OMS 1924804 | April | 2022 | 2022Q4 | 2022 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2022-04-02 | N | 117 | N | 5 | N | N | 1.1101 | 39.4971 | 85.5001
[7 empty] | 275 | 3549 | 1924675 | 2022-04-01 17:44 | 2022-04-02 12:45 | 1141 | 11kV | 165786 | 1185 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 220903 Large tree brought down multiple spns of HV & LV adj ABS 40463 & pole GT 13049 B & C ph OC Excluded OMS 1924675 | April | 2022 | 2022Q4 | 2022 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2022-04-01 | N | 139.9038 | N | 8 | N | N | 1.1101 | 39.4971 | 121151.5189
[7 empty] | 795 | 9926 | 1924485 | 2022-04-02 09:50 | 2022-04-02 17:20 | 450 | 11kV | 9000 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220907 Isolated 11kV OHM for emerg removal of tree off house 56 Ridgeway Rd Sub 10194 held in LV parallel Isolated from ABS 1418 sub 8453 interrupted Excluded OMS 1924485 | April | 2022 | 2022Q4 | 2022 | 210:83465 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Veg | 2022-04-02 | N | 450 | N | 5 | N | N | 1.1101 | 39.4971 | 6576.9345
[7 empty] | 1632 | 19759 | 1924981 | 2022-04-03 08:20 | 2022-04-03 11:00 | 160 | 11kV | 94546 | 1030 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Zn3155 Double Bay - Pnl.19 tripped on: Earth Fault UG cable hit by contractor at 138 Bellevue Rd See 1926088 1926089 1926090 | April | 2022 | 2022Q4 | 2022 | ZN3155:PA19 | ZN3155:PA19 | ZN03155/000019 | WOOLLAHRA | UG | Not Veg | 2022-04-03 | N | 91.7922 | N | 5 | N | N | 1.1101 | 39.4971 | 69091.4282
[7 empty] | 438 | 5434 | 1924994 | 2022-04-03 09:38 | 2022-04-03 11:50 | 132 | 11kV | 660 | 5 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Wind Strong | N | LID 220910 B Phase DOLF : 10 Amp Dead bird found at base of pole Excluded OMS 1924994 | April | 2022 | 2022Q4 | 2022 | 513:83502 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2022-04-03 | N | 132 | N | 5 | N | N | 1.1101 | 39.4971 | 482.3085
[7 empty] | 1149 | 14425 | 1924982 | 2022-04-03 11:40 | 2022-04-03 12:39 | 59 | 11kV | 5841 | 99 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | REC.44995 Kulnura - Interrupted at 1140 Branch has come down onto bare 11kV feeder and become stuck in LV bundled distributor near pole KA-449 | April | 2022 | 2022Q4 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-04-03 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 4268.4305
[7 empty] | 463 | 5689 | 1925017 | 2022-04-03 11:27 | 2022-04-03 14:30 | 183 | 11kV | 22122 | 296 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn14891 Wyong IR48813 Yarramalong Boyd has tripped and reclosed Relays: Lockout, OC Trip SEF Cause: Trees down @ 1567 Yarramalong Rd See OMS 1926111 1926113 1925017 1925030 | April | 2022 | 2022Q4 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2022-04-03 | N | 74.7365 | N | 5 | N | N | 1.1101 | 39.4971 | 16166.1051
[7 empty] | 959 | 11638 | 1924947 | 2022-04-02 23:29 | 2022-04-03 16:30 | 1020.6833 | 11kV | 8165.4667 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | CP24720 Cromer Fitness - Sw/C RMI - A & B phase HV fuses blown Cause not ascertained Not group or zone earth at Zone See NAR92914 - Planned customer interruption from 0700 to 1700 - possible factor? | April | 2022 | 2022Q4 | 2022 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Veg | 2022-04-02 | N | 1020.6833 | N | 5 | N | N | 1.1101 | 39.4971 | 5967.0822
[7 empty] | 764 | 9549 | 1925063 | 2022-04-03 17:33 | 2022-04-03 20:34 | 181 | 11kV | 32589 | 396 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn12600 Lisarow Panel 3 Tripped, reclosed tripped and locked out on Relays. Timed Earth Fault and EFI Signals: 11kV trip Field EFI's S12399 Abnormal Switching: CP44024 Closed, CP44327 Open Cause: 11kV Feeder from S12399 Lisarow High Taylor to S18173 Newling Parsons 0.1 is defective due to UG cable fault See OMS 1926092 1926096 1925063 1925080 1925081 | April | 2022 | 2022Q4 | 2022 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | UG | Not Veg | 2022-04-03 | N | 82.2955 | N | 5 | N | N | 1.1101 | 39.4971 | 23815.08
[7 empty] | 1681 | 20419 | 1925093 | 2022-04-04 01:38 | 2022-04-04 03:04 | 86 | 11kV | 113939 | 1543 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1285 Greenacre Park 11kV feeder panel No17 'French Jacobs' feeder tripped on: Relays A,B,C, O/C, EFI, F/C Field EFI's: S64560, S78723 11kV UG Fault in section of feeder from S50 Meredith Parker(Sw/B) to S8618 Meredith Gordon (Sw/A) to S31703 Meredith Gordon No.3 (Sw/B) See 1925471,1925472,1925473,1925475 1925093 withdrawn | April | 2022 | 2022Q4 | 2022 | ZN1285:PA17 | ZN37100:PA6 | ZN37100/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-04-04 | N | 73.8425 | N | 3 | N | N | 1.1101 | 39.4971 | 83263.2606
[7 empty] | 418 | 5298 | 1925243 | 2022-04-04 13:55 | 2022-04-04 14:54 | 58.7667 | 11kV | 43898.7 | 747 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN2196 Milperra panel 26 S63412 feeder tripped on: Relays A and B phase Timed OC, EFI, TX3, 11kV Fault Check Signals 11kV Trip, ZN E, TX 3 GE Filed EFIs: S63412, S35246, S7351, S48646 Tree Branch on OH mains Branch found near S62316 192544,1925245 withdrawn | April | 2022 | 2022Q4 | 2022 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-04-04 | N | 58.7667 | N | 3 | N | N | 1.1101 | 39.4971 | 32079.8752
[7 empty] | 887 | 10910 | 1925280 | 2022-04-04 16:32 | 2022-04-04 17:03 | 31.3333 | 11kV | 4198.6667 | 134 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn36200 Empire Bay, on Panel 8 'S49860 Poole Belrose' LB62075 opened by DOp Interrupted for safety to remove tree branch. Between poles WW2231 & WW2239 a large branch has fallen across all 3, 11Kv CCT conductors. Needs removing urgently putting weight onto wires. | April | 2022 | 2022Q4 | 2022 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2022-04-04 | N | 31.3333 | N | 3 | N | N | 1.1101 | 39.4971 | 3068.2618
[7 empty] | 1426 | 17548 | 1925324 | 2022-04-05 02:51 | 2022-04-05 03:50 | 59 | 11kV | 34633 | 587 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN1287 Revesby 11kV feeder panel No24 'Revesby Workers No2' feeder tripped on: Relays: A phase timed O/C,E/F, fault check Field EFIs: S61162,S49189,S4581,S47465 Possum caused flashover on UGOH to S4755, no damage, supply restored. | April | 2022 | 2022Q4 | 2022 | ZN1287:PA24 | ZN1287:PA24 | ZN01287/000024 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-04-05 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 25308.7749
[7 empty] | 882 | 10879 | 1925419 | 2022-04-05 10:54 | 2022-04-05 12:30 | 96 | 11kV | 81748 | 914 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 220916 O/C E/F Cable fault on Pole OR-67187. Cable isolated and all power restored 12.30 | April | 2022 | 2022Q4 | 2022 | 242:81532 | 242:81532 | ZN00242/081532 | PORT STEPHENS | UG | Not Veg | 2022-04-05 | N | 89.4398 | N | 6 | N | N | 1.1101 | 39.4971 | 59739.0272
[7 empty] | 1048 | 13448 | 1925643 | 2022-04-05 09:03 | 2022-04-05 12:55 | 232 | 11kV | 232 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220915 HV dropperlead burning into Xarm sub70977 Excluded OMS 1925370 | April | 2022 | 2022Q4 | 2022 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Not Veg | 2022-04-05 | N | 232 | N | 6 | N | N | 1.1101 | 39.4971 | 169.5388
[7 empty] | 199 | 2576 | 1925374 | 2022-04-05 09:55 | 2022-04-05 15:19 | 324 | 11kV | 75168 | 232 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 220918 interrupt for repairs at pole IV10932 Excluded oms 1925374 | April | 2022 | 2022Q4 | 2022 | 270:83590 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Not Veg | 2022-04-05 | N | 324 | N | 6 | N | N | 1.1101 | 39.4971 | 54930.5573
[7 empty] | 1527 | 18728 | 1925399 | 2022-04-05 09:49 | 2022-04-05 16:25 | 396.4 | 11kV | 396.4 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN8000 Macquarie Park Zone Substation Panel 30 Tripped on Relays: Basler 50TAC, IOC C phase, Fault CHeck, EFI Signals: Group Earth TX3 Cause: 11kV feeder is defective from ZN8000 Macquarie Park ZN to Panel 30 HVC Next DC | April | 2022 | 2022Q4 | 2022 |  |  |  |  | UG | Not Veg | 2022-04-05 | N | 396.4 | N | 6 | N | N | 1.1101 | 39.4971 | 289.6774
[7 empty] | 1583 | 19334 | 1925544 | 2022-04-05 18:27 | 2022-04-06 02:20 | 473 | 11kV | 137505 | 747 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2196 Milperra Panel 26 tripped on Signals: 11kV Trip Relays: 51N. F/C, efi Cause: 11kV on ground (HV into LV between S48646 and S62316 See OMS 1925694 1925695 1925696 1925544 | April | 2022 | 2022Q4 | 2022 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-04-05 | N | 184.0763 | N | 6 | N | N | 1.1101 | 39.4971 | 100484.5983
[7 empty] | 1484 | 18324 | 1925743 | 2022-04-06 14:28 | 2022-04-06 16:24 | 116 | 11kV | 132768 | 1183 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At Zn847 Hornsby Panel 18 Tripped, reclosed, tripped and locked out on Relays: C phase IOC, Timed OC, C phase EFT, Lockout Signals: 11kV trip, Zone Earth, TX2 Group Earth Abnromal Switching CP1972 Closed, CP420 Open, CP700 Closed, UGOH below Pa45 Open and DMA Cause: Broken tree branch made contact with OH mains See OMS 1926139 1926140 1925743 1925745 | April | 2022 | 2022Q4 | 2022 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2022-04-06 | N | 112.2299 | N | 3 | N | N | 1.1101 | 39.4971 | 97022.9384
[7 empty] | 762 | 9527 | 1925768 | 2022-04-06 15:42 | 2022-04-06 17:05 | 83 | 11kV | 109311 | 1317 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn195 Pymble - Pnl.9 tripped , reclosed & locked out on: B phase Earth Fault and OC UG cable fault in front line section of feeder | April | 2022 | 2022Q4 | 2022 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2022-04-06 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 79881.2547
[7 empty] | 801 | 9998 | 1925818 | 2022-04-06 20:27 | 2022-04-06 22:15 | 108 | 11kV | 121097 | 1406 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | At S35800 Banksown Panel 118 Tripped reclosed tripped and locked out on Signals: 11kV Trip, Auto reclose lockout Relays: 50TN, 51N Minor alarm, Trip Field EFIs S47787 Cause: Vehicle hit UGOH pole (PE20248 ) Ex SW/A @ S50018 Stuart Arab See OMS 1926125 1926128 1926129 1925818 | April | 2022 | 2022Q4 | 2022 | ZN35800:PA18 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-04-06 | N | 86.1287 | N | 3 | N | N | 1.1101 | 39.4971 | 88494.1158
[7 empty] | 1646 | 20009 | 1925893 | 2022-04-07 07:34 | 2022-04-07 08:42 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 220924 A Phase DOLF : 31 Amp Volts = 242. Amps = 180, 190, 180. Excluded OMS 1925893. | April | 2022 | 2022Q4 | 2022 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2022-04-07 | N | 68 | N | 8 | N | N | 1.1101 | 39.4971 | 49.6924
[7 empty] | 1602 | 19541 | 1925972 | 2022-04-07 10:19 | 2022-04-07 11:30 | 71 | 11kV | 142 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Heavy | N | S.6182 Violet St No.5 - Tx No.1 HV fuse blown Transformer No.1 failed Restored via LV // | April | 2022 | 2022Q4 | 2022 | ZN2196:PA6 | ZN2196:PA6 | ZN02196/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-04-07 | N | 71 | N | 8 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 1153 | 14501 | 1925948 | 2022-04-07 09:40 | 2022-04-07 14:30 | 290 | 11kV | 7098 | 63 | HV | Vegetation Cut Down 3rd Party | 3rd Party Impact | O/H Conductor Bare | Unplanned | Rain Heavy | N | At ZN12650 Peats Ridge - Recloser CP44994 Mangrove Creek ex Panel 8 tripped on Relay: O/C trip Tree trimmer dropped branch on 11kV mains near PT11993 Mangrove Ck Dam No.1 See 1925948 1927640 | April | 2022 | 2022Q4 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-04-07 | N | 112.6667 | N | 8 | N | N | 1.1101 | 39.4971 | 5187.009
[7 empty] | 1315 | 16000 | 1926041 | 2022-04-07 13:06 | 2022-04-07 14:45 | 99 | 11kV | 14751 | 149 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At ZN14891 Wyong, CP44753 Bunning Creek (Intellirupter) ex 11kV Panel 12 tripped on Relays: O/C, Lockout Tree Branch on OH mains near CP42675 [LB] | April | 2022 | 2022Q4 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2022-04-07 | N | 99 | N | 8 | N | N | 1.1101 | 39.4971 | 10779.5957
[7 empty] | 1485 | 18327 | 1926040 | 2022-04-07 13:07 | 2022-04-07 15:00 | 113 | 11kV | 152582 | 1489 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S80 Chatswood 11kV Panel 22 tripped on Relays: 11kV Trip, ZN11 Group Earth, Zone Earth Caise: 11kV UG cable fault from S35000 Mowbray Hampden No 1 to S3911 Fehan Pacific SW/A to S2504 Findlason St SW/B to S3026 Lane cove Testing No3 to S46610 Currawond Eloora See OMS 1927649 1927650 1926040 | April | 2022 | 2022Q4 | 2022 | ZN80:PA22 | ZN80:PA22 | ZN00080/000022 | LANE COVE | UG | Not Veg | 2022-04-07 | N | 102.4728 | N | 8 | N | N | 1.1101 | 39.4971 | 111502.4252
[7 empty] | 1521 | 18674 | 1926043 | 2022-04-07 13:30 | 2022-04-07 15:30 | 120 | 11kV | 16320 | 136 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | EX ZN10994 Mortdale Section fo Panel 7 From CPO39358 to PT78744 and PT10312 interrupted for safe remove of tree | April | 2022 | 2022Q4 | 2022 | ZN10994:PA7 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2022-04-07 | N | 120 | N | 8 | N | N | 1.1101 | 39.4971 | 11926.1746
[7 empty] | 529 | 6297 | 1925958 | 2022-04-07 09:59 | 2022-04-07 17:10 | 431 | 11kV | 96327 | 263 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | 11kV recloser CP1126 Mona Vale Rd Tripped and Locked out on Section of 11kV Feeder Panel 10 RelaysIOC trip, OC Trip Cause: Dop reports branch with fres burn marks found adjacent to 11kV Link 21880 See OMS 1927687 1927690 1927691 1927683 1926084 1926154 1925958 | April | 2022 | 2022Q4 | 2022 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2022-04-07 | N | 366.2624 | N | 8 | N | N | 1.1101 | 39.4971 | 70392.9304
[7 empty] | 1133 | 14312 | 1926152 | 2022-04-07 16:24 | 2022-04-07 20:25 | 241 | 11kV | 182857 | 1712 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Rain Heavy | N | At S35500 Top Ryde Panel 36 Tripped on RelaysL 50TABC, EFI, Trip, Reclose Lockout Signals: Protn Trip, TX3 Group Earth Field EFI's S8724, S5334 Cause: At S5334 Quarry Jones Endbox Filled with water and failed explosivelt Se OMS 1927433 1927441 1927442 1927443 1926152 1926178 1926226 | April | 2022 | 2022Q4 | 2022 | ZN35500:PA36 | ZN35500:PA36 | ZN35500/000036 | RYDE | UG | Not Veg | 2022-04-07 | N | 106.809 | N | 8 | N | N | 1.1101 | 39.4971 | 133626.5022
[7 empty] | 763 | 9539 | 1926243 | 2022-04-08 02:40 | 2022-04-08 03:41 | 61 | 11kV | 57092 | 952 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn116 Leichhardt Panel 14 tripped onb Relays: Earth fault Signals: 11kV Trip Field EFI's: S682 Cause: 11kV Cable fault from S682 to S1472 Hearn St See OMS1927415 19274165 1926243 | April | 2022 | 2022Q4 | 2022 | ZN116:PA14 | ZN116:PA14 | ZN00116/000014 | INNER WEST | UG | Not Veg | 2022-04-08 | N | 59.9706 | N | 2 | N | N | 1.1101 | 39.4971 | 41721.1497
[7 empty] | 161 | 1999 | 1926503 | 2022-04-08 22:24 | 2022-04-08 23:30 | 66 | 11kV | 16854 | 266 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn188 Zetland - Pnl.33 tripped on: Earth Fault UG cable fault between S1058 Main Store Sw/A and S.7932 Link Epsom Sw/A See 1927277 1927278 | April | 2022 | 2022Q4 | 2022 | ZN188:PA33 | ZN188:PA33 | ZN00188/000033 | SYDNEY | UG | Not Veg | 2022-04-08 | N | 63.3609 | N | 2 | N | N | 1.1101 | 39.4971 | 12316.4061
[7 empty] | 1225 | 15042 | 1926508 | 2022-04-09 04:01 | 2022-04-09 06:01 | 120 | 11kV | 10440 | 87 | HV | Animal Possum | Animal | Insulator | Unplanned | No Weather Impact | N | 1 x HV drop out fuse blown and another hasn't blown properly and is arcing. Fuse carrier is damaged. Cause is possum stuck on LV bushings on PT12604. Dop required. See OMS 1927717 1926508 1926511 | April | 2022 | 2022Q4 | 2022 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Not Veg | 2022-04-09 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 7629.2441
[7 empty] | 1286 | 15657 | 1926581 | 2022-04-09 13:34 | 2022-04-09 15:10 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220929 Single phase DOLF : 10 Amp Excluded OMS 1926581 | April | 2022 | 2022Q4 | 2022 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2022-04-09 | N | 96 | N | 3 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 200 | 2577 | 1926596 | 2022-04-09 15:20 | 2022-04-09 17:20 | 120 | 11kV | 11520 | 96 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220930 SECTION ISOLATED TO RELACE FAULTY 11Kv CROSS ARM AT POLE IS61437 Excluded OMS 1926596 | April | 2022 | 2022Q4 | 2022 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2022-04-09 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 8418.4762
[7 empty] | 1604 | 19543 | 1926624 | 2022-04-10 03:38 | 2022-04-10 04:38 | 60 | 11kV | 58860 | 981 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | CP79940 Kincumber Bungoona (Intellirupter) Section of Panel 22 feeder - ABC phases tripped to lockout due to Flashover / Arcing Tree branch removed by DOp adjacent to PT12521 Avoca Davistown 0.6 Relay: O/C trip | April | 2022 | 2022Q4 | 2022 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2022-04-10 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 43013.1519
[7 empty] | 557 | 6873 | 1926636 | 2022-04-10 07:39 | 2022-04-10 09:50 | 131 | 11kV | 131 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN8100 Panel 29L to S48417 Bourke Huntley No.3 SW/A - UG Feeder fault Relays: Timed E/F, O/C B phase, O/C E/F, EFI, Fault check Signals Tx.3, G/E, O/C trip, E/F trip, 11kV trip See 1927214 | April | 2022 | 2022Q4 | 2022 |  |  |  | SYDNEY | UG | Not Veg | 2022-04-10 | N | 131 | N | 3 | N | N | 1.1101 | 39.4971 | 95.7309
[7 empty] | 70 | 876 | 1926668 | 2022-04-10 12:08 | 2022-04-10 13:50 | 102 | 11kV | 102681 | 1173 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Panel 8 at ZN15012 Killarney tripped, reclosed then locked out. Tree branch on 11kV mains at 524 Warringah Road. Relays: Instantaneous, A & C phase Signals: 11kV trip, Zone Earth See 1926668, 1927115 | April | 2022 | 2022Q4 | 2022 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2022-04-10 | N | 87.5371 | N | 3 | N | N | 1.1101 | 39.4971 | 75036.2462
[7 empty] | 1197 | 14837 | 1926750 | 2022-04-11 08:54 | 2022-04-11 11:15 | 141 | 11kV | 43984 | 546 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN35500 Top Ryde, Panel 32 reclosed and tripped out UG fault between CP78456 SW/B to S35185 SW/A tee S5572 Relays: 51N (Earth Fault), EFI, Reclose Time, Tx.3 Earth Fault Check B See 1926750 1927540 | April | 2022 | 2022Q4 | 2022 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2022-04-11 | N | 80.5568 | N | 7 | N | N | 1.1101 | 39.4971 | 32142.2099
[7 empty] | 217 | 2679 | 1926853 | 2022-04-11 15:00 | 2022-04-11 17:13 | 133 | 11kV | 7448 | 56 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 220934 Broken LLC sub 53121 Section isolated to allow repairs | April | 2022 | 2022Q4 | 2022 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2022-04-11 | N | 133 | N | 7 | N | N | 1.1101 | 39.4971 | 5442.7787
[7 empty] | 1395 | 17092 | 1926879 | 2022-04-11 15:44 | 2022-04-11 17:22 | 98 | 11kV | 147820 | 1574 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S35555 Croydon Panel 16 Tripped on Relays: 50T A and B phase with efi Cause: UG cable fault from S35720 tio S2405 see OMS 1927030 1927031 1926879 | April | 2022 | 2022Q4 | 2022 | ZN35555:PA16 | ZN35555:PA16 | ZN35555/000016 | INNER WEST | UG | Not Veg | 2022-04-11 | N | 93.9136 | N | 7 | N | N | 1.1101 | 39.4971 | 108022.496
[7 empty] | 197 | 2518 | 1926898 | 2022-04-11 16:26 | 2022-04-11 18:34 | 128 | 11kV | 122508 | 959 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn167 Auburn - Pnl.21 tripped on: IOC UG cable fault between S6245 and S5445 See 1927723 1927724 1927725 | April | 2022 | 2022Q4 | 2022 | ZN167:PA21 | ZN167:PA21 | ZN00167/000021 | CUMBERLAND | UG | Not Veg | 2022-04-11 | N | 127.7456 | N | 7 | N | N | 1.1101 | 39.4971 | 89525.233
[7 empty] | 1079 | 13831 | 1926912 | 2022-04-11 17:09 | 2022-04-11 18:58 | 109 | 11kV | 49759 | 524 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220935 2 fault operation Earth Fault; Overcurrent DOPs patrolled & no fault found. Excluded OMS 1926912 | April | 2022 | 2022Q4 | 2022 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Veg | 2022-04-11 | N | 94.9599 | N | 7 | N | N | 1.1101 | 39.4971 | 36362.4096
[7 empty] | 946 | 11462 | 1926954 | 2022-04-11 20:34 | 2022-04-11 23:46 | 192 | 11kV | 384 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 220936 replaced 11kV LA excluded oms 1926954 | April | 2022 | 2022Q4 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-04-11 | N | 192 | N | 7 | N | N | 1.1101 | 39.4971 | 280.6159
[7 empty] | 1347 | 16415 | 1926950 | 2022-04-11 20:03 | 2022-04-12 00:05 | 242 | 11kV | 2662 | 11 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 220938 Section isolated to replace pole LS-20382 Excluded OMS 1926950 | April | 2022 | 2022Q4 | 2022 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2022-04-11 | N | 242 | N | 7 | N | N | 1.1101 | 39.4971 | 1945.3111
[7 empty] | 637 | 8243 | 1927183 | 2022-04-12 21:23 | 2022-04-12 23:10 | 107 | 11kV | 213366 | 2105 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S187 Crows Nest Panel 20 Tripped on Signals: 11kV Trip Relays : NIl Field EFIs Nil Cause: Suspected defective relays feeder opened with no relay operations. See OM S1927711 1927715 1927183 | April | 2022 | 2022Q4 | 2022 | ZN187:PA20 | ZN187:PA20 | ZN00187/000020 | NORTH SYDNEY | Unknown | Not Veg | 2022-04-12 | N | 101.3615 | N | 3 | N | N | 1.1101 | 39.4971 | 155921.5796
[7 empty] | 102 | 1306 | 1927112 | 2022-04-12 14:08 | 2022-04-12 23:20 | 552 | 11kV | 28348 | 166 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220940 1 fault operation Sensitive Earth Fault B ph SEF & EF Broken X arm pole ER-53051 Excluded OMS 1927112 | April | 2022 | 2022Q4 | 2022 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2022-04-12 | N | 170.7711 | N | 3 | N | N | 1.1101 | 39.4971 | 20715.8823
[7 empty] | 1306 | 15911 | 1927204 | 2022-04-13 05:34 | 2022-04-13 08:25 | 171 | 11kV | 127152 | 939 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36200 Empire Bay - Pnl.4 tripped, reclosed & locked out on: ABC phase OC Suspect UG cable fault between LB43135 to S18061 Sw/B tee PT12835 See 1927697 1927699 1927702 1927701 | April | 2022 | 2022Q4 | 2022 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | UG | Not Veg | 2022-04-13 | N | 135.4121 | N | 4 | N | N | 1.1101 | 39.4971 | 92918.9313
[7 empty] | 251 | 3085 | 1927227 | 2022-04-13 08:16 | 2022-04-13 08:46 | 30 | 11kV | 59850 | 1995 | HV | Animal Bird | Animal | Cross arm | Unplanned | No Weather Impact | N | LID 220942 1 Fault operation B & C Phase Instantaneous Overcurrent Bird on crossarm at sub 11914 excluded OMS 1927272 | April | 2022 | 2022Q4 | 2022 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2022-04-13 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 43736.6147
[7 empty] | 124 | 1525 | 1927191 | 2022-04-12 23:51 | 2022-04-13 14:40 | 889 | 11kV | 21405 | 363 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | No Weather Impact | N | Zn12580 Erina - Pnl.12 - Opened by AOP for safety Tree in Erina Valley Rd has brought down CCT, section of feeder between USL42282 and PT12035 isolated See 1927713 1927714 | April | 2022 | 2022Q4 | 2022 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2022-04-12 | N | 58.9669 | N | 3 | N | N | 1.1101 | 39.4971 | 15642.1427
[7 empty] | 1229 | 15076 | 1927356 | 2022-04-13 12:35 | 2022-04-13 14:42 | 127 | 11kV | 227163 | 2252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 220944 2 fault operations C Phase Overcurrent FDR 10728 tripped and locked out, fdr patrolled and restored. Fdr 10722 has half of its fdr fed from 10728 via ABS 4986 so it was interrupted from ABS 4986 to ABS 10879(DMA) Excluded OMS 1927356 | April | 2022 | 2022Q4 | 2022 | 216:10728 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Veg | 2022-04-13 | N | 100.8717 | N | 4 | N | N | 1.1101 | 39.4971 | 166004.0202
[7 empty] | 1314 | 15961 | 1927366 | 2022-04-13 12:51 | 2022-04-13 20:00 | 429 | 11kV | 657741 | 2976 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn6372 Maroubra - Pnl.13 tripped on: OC & EF On energising from S542 to S35189, Pnl.13 tripped due to closing onto UG cable fault on Pnl.46. On further restoration attempts, S542 Sw/R failed explosivley. See related outage on Pnl.46 (failed to operate) & Tx 3 Group Bar See 1927582 1927596 1927597 1927598 1927602 | April | 2022 | 2022Q4 | 2022 | ZN3672:PA13 | ZN3672:PA13 | ZN03672/000013 | RANDWICK | UG | Not Veg | 2022-04-13 | N | 221.0151 | N | 4 | N | N | 1.1101 | 39.4971 | 480657.7227
[7 empty] | 1400 | 17135 | 1927534 | 2022-04-14 06:19 | 2022-04-14 11:45 | 326 | 11kV | 190994 | 1363 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S340 Botany 11kV Panel 3 tripped on Relays: B phase E?F, efi Signals: Trip Cause: Feeder fault between S7520 Bay St No.96 to S3807 Bay St No.82 tee S2122 Begonia St See OMS 1927732 1927733 1927735 1927534 1927576 | April | 2022 | 2022Q4 | 2022 | ZN340:PA3 | ZN340:PA3 | ZN00340/000003 | BAYSIDE | UG | Not Veg | 2022-04-14 | N | 140.1277 | N | 2 | N | N | 1.1101 | 39.4971 | 139572.7818
[7 empty] | 1550 | 18989 | 1927645 | 2022-04-14 11:09 | 2022-04-14 13:10 | 121 | 11kV | 242 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220948 10 Amp, Phase C, Substation DOLF Refer to oms 1927645 dead bird found at sub SOP De VRIES M DOP WADWELL D | April | 2022 | 2022Q4 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2022-04-14 | N | 121 | N | 2 | N | N | 1.1101 | 39.4971 | 176.8465
[7 empty] | 1647 | 20018 | 1927889 | 2022-04-16 06:07 | 2022-04-16 07:56 | 109 | 11kV | 129383 | 1187 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | CP45140 Pinnaroo Colledina (recloser) - Tripped and locked out Magpie into mains on the corner of Parraweena and Gamban | April | 2022 | 2022Q4 | 2022 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2022-04-16 | N | 109 | N | 6 | N | N | 1.1101 | 39.4971 | 94549.2802
[7 empty] | 928 | 11293 | 1927903 | 2022-04-16 06:45 | 2022-04-16 10:29 | 224 | 11kV | 5600 | 25 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 220955 Single Phase, Earth Fault Tree brought down mains SO-80129 to Sw 63580 SOP ARLITSCH E DOP WEBB Z | April | 2022 | 2022Q4 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2022-04-16 | N | 224 | N | 6 | N | N | 1.1101 | 39.4971 | 4092.3148
[7 empty] | 1672 | 20358 | 1927909 | 2022-04-16 07:46 | 2022-04-16 10:50 | 184 | 11kV | 1840 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT13343 Little Jilliby Jill 2.0 - 11kV fuse blown - middle phase Cause not ascertained - Assumed fatigued fuse - HDO 10A NKG | April | 2022 | 2022Q4 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2022-04-16 | N | 184 | N | 6 | N | N | 1.1101 | 39.4971 | 1344.6177
[7 empty] | 854 | 10578 | 1927938 | 2022-04-16 11:25 | 2022-04-16 13:27 | 122 | 11kV | 366 | 3 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 220954 Vandalism Earths stolen form sub 15396 SOP CARSON S DOP MILLS A | April | 2022 | 2022Q4 | 2022 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2022-04-16 | N | 122 | N | 6 | N | N | 1.1101 | 39.4971 | 267.462
[7 empty] | 1253 | 15240 | 1927921 | 2022-04-16 09:05 | 2022-04-16 13:35 | 270 | 11kV | 270 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 220953 Phase B, Substation DOLF B Phase Live line lead has broken away from LLC and is hanging low near B phase LVF assembly on Sub 52763. Opened DOLF's and LVF's on Sub 52763.Crew beeded, No access with EWP as ground is too soft. SOP CARSON S DOP C.Moore | April | 2022 | 2022Q4 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2022-04-16 | N | 270 | N | 6 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 902 | 11125 | 1927974 | 2022-04-16 17:20 | 2022-04-18 19:00 | 2980 | 11kV | 86228 | 725 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT11769 Crystal Diamond 1.0 damaged and cross arms broken when tree brought down 11kV and LV distributors and crossarms broke, extensive damange Nr 62 Crystal Ave, Pearl Beach CP45090 Pearl Beach (Recloser) interrupted for safety. (section of 11kV Panel 4) Refer 1927982 | April | 2022 | 2022Q4 | 2022 | ZN12640:PA4 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Veg | 2022-04-16 | N | 118.9352 | N | 6 | N | N | 1.1101 | 39.4971 | 63012.8791
[7 empty] | 1493 | 18394 | 1928396 | 2022-04-19 22:02 | 2022-04-19 23:18 | 76 | 11kV | 105564 | 1389 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn36200 Empire bay - Pnl.8 tripped, reclosed & locked out on: B & C phase OC Tree branch on OH mains near PT13952 removed by DOP | April | 2022 | 2022Q4 | 2022 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2022-04-19 | N | 76 | N | 2 | N | N | 1.1101 | 39.4971 | 77143.0576
[7 empty] | 824 | 10158 | 1928400 | 2022-04-19 22:23 | 2022-04-20 00:18 | 115 | 11kV | 122015 | 1061 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | ZN12570 Avoca - Panel 35 "Kincumber" 11kV feeder tripped and reclosed to lockout Tree branch removed by DOp near line side of CP61952 Recloser Relays: A & B phase O/C, EFI, timing, lockout | April | 2022 | 2022Q4 | 2022 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2022-04-19 | N | 115 | N | 2 | N | N | 1.1101 | 39.4971 | 89164.9632
[7 empty] | 961 | 11668 | 1928416 | 2022-04-20 01:44 | 2022-04-20 02:40 | 56 | 11kV | 5992 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | CP44790 Hansens Rd (11kV Recloser) - Section of Panel 7 feeder tripped and reclosed to lockout Tree Branch on OH mains adjacent to CP43317, removed by DOp, supply restored Relays: O/C Trip | April | 2022 | 2022Q4 | 2022 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Veg | 2022-04-20 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 4378.7769
[7 empty] | 1324 | 16158 | 1928419 | 2022-04-20 04:15 | 2022-04-20 14:00 | 585 | 11kV | 87882 | 1178 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.42 tripped on: C phase OC UG cable fault between S4499 (Sw/B), S4513 (Sw/A) tee S5843 See 1928742 1928743 1928745 | April | 2022 | 2022Q4 | 2022 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | UG | Not Veg | 2022-04-20 | N | 74.6027 | N | 5 | N | N | 1.1101 | 39.4971 | 64221.5735
[7 empty] | 827 | 10197 | 1928559 | 2022-04-20 13:52 | 2022-04-20 14:55 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220960 16 Amp, Phase B, Substation DOLF also refer to oms 1928559 replaced B ph 16 amp HVF, power restored 1455. Previous Storm SOP De VRIES M DOP BAXTER M | April | 2022 | 2022Q4 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2022-04-20 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 62 | 787 | 1928568 | 2022-04-20 14:42 | 2022-04-20 19:00 | 258 | 11kV | 25414 | 280 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | CP554 Arcadia Rosscommon tripped, reclosed, tripped & locked out on OC 11kV cross arm broken near PT1572 Fagans End See 1928739 1928740 1928741 | April | 2022 | 2022Q4 | 2022 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2022-04-20 | N | 90.7643 | N | 5 | N | N | 1.1101 | 39.4971 | 18571.8016
[7 empty] | 173 | 2261 | 1928593 | 2022-04-20 16:57 | 2022-04-21 09:20 | 982.8 | 11kV | 94348.8 | 96 | HV | Fire (Non Ausgrid) | UNKNOWN | DC-PT Not Transformer | Unplanned | No Weather Impact | N | PT15463 Beacon Kalianna - Blown HDO and blown LV fuses A vehicle fire at the base of PT15463 damaged HV and LV fuse holders | April | 2022 | 2022Q4 | 2022 | ZN15011:PA4 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | OH | Not Veg | 2022-04-20 | N | 982.8 | N | 5 | N | N | 1.1101 | 39.4971 | 68947.3202
[7 empty] | 1259 | 15330 | 1928709 | 2022-04-21 12:33 | 2022-04-21 17:00 | 267 | 11kV | 534 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 220965 REPLACED 10 Amp, BLOWN DOLF Previous Storm SOP McGUIRE L DOP BAXTER M | April | 2022 | 2022Q4 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-04-21 | N | 267 | N | 4 | N | N | 1.1101 | 39.4971 | 390.2314
[7 empty] | 1269 | 15490 | 1928783 | 2022-04-21 20:20 | 2022-04-21 21:55 | 95 | 11kV | 95 | 1 | HV | Equipment Failed in Service | Equipment Failure | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 220967 Refer to OMS 1928783 Fallen private LV pole of sub 71237 Isolated LV to cut away private pole SOP HOLLAND P DOP APPS D | April | 2022 | 2022Q4 | 2022 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | Unknown | Not Veg | 2022-04-21 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 514 | 6155 | 1928808 | 2022-04-21 21:03 | 2022-04-21 23:00 | 117 | 11kV | 468 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT11924 Oystershell Wise 4.2, 11kV footpath side 16A HDO operated Tree branch on OH mains/Tx lightning arrestors | April | 2022 | 2022Q4 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2022-04-21 | N | 117 | N | 4 | N | N | 1.1101 | 39.4971 | 342.0006
[7 empty] | 538 | 6432 | 1928656 | 2022-04-21 16:30 | 2022-04-21 23:30 | 420 | 11kV | 42000 | 100 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 220964 Refer to oms 1928656 and 1928780 ugoh earth cable & LA faulty at pole JU-21190, isolated for repairs" SOP WATSON J DOP DE GIOVANNI P | April | 2022 | 2022Q4 | 2022 | 205:12210 | 205:12210 | ZN00205/012210 | NEWCASTLE | OH | Not Veg | 2022-04-21 | N | 420 | N | 4 | N | N | 1.1101 | 39.4971 | 30692.3612
[7 empty] | 340 | 4749 | 1928815 | 2022-04-22 02:10 | 2022-04-22 03:14 | 64 | 11kV | 38336 | 599 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | CP45180 Avoca Beach (recloser) tripped section of Panel 37L 11kV feeder Small tree branch on 11kV near PT13522 Relays: OC trip, L/O | April | 2022 | 2022Q4 | 2022 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2022-04-22 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 28014.8181
[7 empty] | 1198 | 14847 | 1928845 | 2022-04-22 09:04 | 2022-04-22 11:01 | 116.7333 | 11kV | 13657.8 | 117 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | Interupted to repair blown surge arrestor see OMS interuption report 1928821. DQ ## no lid | April | 2022 | 2022Q4 | 2022 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2022-04-22 | N | 116.7333 | N | 4 | N | N | 1.1101 | 39.4971 | 9980.7174
[7 empty] | 410 | 5221 | 1928834 | 2022-04-22 10:55 | 2022-04-22 11:25 | 30 | 11kV | 90 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 220969 Refer to OMS 1928834 Reolace burnt LVF assembly SOP McGUIRE L DOP BAXTER M | April | 2022 | 2022Q4 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2022-04-22 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 756 | 9504 | 1928925 | 2022-04-22 14:50 | 2022-04-22 19:31 | 281 | 11kV | 3091 | 11 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 220971 Replaced pole AI-50023. | April | 2022 | 2022Q4 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2022-04-22 | N | 281 | N | 4 | N | N | 1.1101 | 39.4971 | 2258.8116
[7 empty] | 172 | 2216 | 1928973 | 2022-04-23 02:11 | 2022-04-23 03:13 | 62 | 11kV | 70928 | 1144 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn965 Pennant Hills - Pnl.15 tripped on: A phase O/C, A Phase IOC Dop removed tree branch from 11kV OH adj LB1123 | April | 2022 | 2022Q4 | 2022 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2022-04-23 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 51832.0904
[7 empty] | 701 | 9067 | 1929046 | 2022-04-23 16:08 | 2022-04-23 17:50 | 102.05 | 11kV | 918.45 | 9 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | No LID Report - part of trial 2x Blown LF 10382 : 20A 2x Blown DOLF 72423 : 10A Operator D Apps Bird on 11kv at Sub 72423 S baily. all restored at 1750. | April | 2022 | 2022Q4 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2022-04-23 | N | 102.05 | N | 3 | N | N | 1.1101 | 39.4971 | 671.1762
[7 empty] | 996 | 12202 | 1929053 | 2022-04-23 20:07 | 2022-04-23 21:25 | 78 | 11kV | 59262 | 766 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | Zn80 Chatswood - Pnl.22 - Beyond S.2504 interrupted for emergency repairs Abnormal: S48821 Sw/B closed with S2504 Sw/B Open (DMA) S36096 Kariola Gay - Dist #3 - Interrupted for repairs Broken Cross Arm on pole GL37821 between S48821, S3451 and S36096 See 1929853 1929083 | April | 2022 | 2022Q4 | 2022 | ZN80:PA22 | ZN80:PA22 | ZN00080/000022 | LANE COVE | OH | Not Veg | 2022-04-23 | N | 77.3655 | N | 3 | N | N | 1.1101 | 39.4971 | 43306.9217
[7 empty] | 230 | 2780 | 1929127 | 2022-04-24 09:16 | 2022-04-24 13:40 | 264 | 11kV | 71444 | 694 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn14144 Wamberal - Pnl.10 tripped, reclosed, tripped & locked out on: A & B phase OC Abnormal: REC44607 Matcham North bypassed (DMA) Tree branch brought down HV mains between PT14716 and PT11815 See 1929884 1929885 1929887 192886 | April | 2022 | 2022Q4 | 2022 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2022-04-24 | N | 102.9452 | N | 4 | N | N | 1.1101 | 39.4971 | 52209.168
[7 empty] | 316 | 4209 | 1929220 | 2022-04-24 22:52 | 2022-04-25 00:30 | 98 | 11kV | 86646 | 1087 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn1673 turramurra - Pnl.6 tripped, reclosed & locked out on: Earth fault UGOH above AB3326 failed explosivley. See 1929890 1929891 | April | 2022 | 2022Q4 | 2022 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | Unknown | Unknown | 2022-04-24 | N | 79.7111 | N | 4 | N | N | 1.1101 | 39.4971 | 63318.3412
[7 empty] | 1261 | 15401 | 1929138 | 2022-04-24 08:32 | 2022-04-25 05:45 | 1273 | 11kV | 138856 | 1480 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Zn1287 Revesby - Pnl.11 tripped & reclosed on: C phase IOC & OC Car hit pole 755 Henry Lawson Drive See 1929876 1929878 | April | 2022 | 2022Q4 | 2022 | ZN1287:PA11 | ZN1287:PA11 | ZN01287/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-04-24 | N | 93.8216 | N | 4 | N | N | 1.1101 | 39.4971 | 101471.8692
[7 empty] | 1242 | 15170 | 1929241 | 2022-04-25 07:26 | 2022-04-25 08:08 | 42 | 11kV | 47649 | 1277 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN847 Hornsby - Panel 19 - Circuit Breaker - Tripped on: Relays EF, EFI, FC Section of 11kV feeder from S.4185 Hunter Burdett to S.5247 Government Pacific to S.3247 Florence Albert has a suspected cable fault Refer 1929576 | April | 2022 | 2022Q4 | 2022 | ZN847:PA19 | ZN847:PA19 | ZN00847/000019 | HORNSBY | UG | Not Veg | 2022-04-25 | N | 37.3132 | N | 4 | N | N | 1.1101 | 39.4971 | 34820.4838
[7 empty] | 107 | 1375 | 1929231 | 2022-04-25 04:43 | 2022-04-25 09:00 | 257 | 11kV | 31611 | 123 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT116 Eltham Vic - A phase HDO operated Fuse faitgue | April | 2022 | 2022Q4 | 2022 | ZN398:PA3 | ZN398:PA3 | ZN00398/000003 | INNER WEST | OH | Not Veg | 2022-04-25 | N | 257 | N | 4 | N | N | 1.1101 | 39.4971 | 23100.3864
[7 empty] | 444 | 5479 | 1929263 | 2022-04-25 09:43 | 2022-04-25 11:39 | 116 | 11kV | 177076 | 2043 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | No LID Report part of Dan Q trial Protection 50T B C phase. Maggpie on pole JU-10478 also tapping burnt off at pole JU-10196. DQ No LID ## Excluded OMS 1929263 | April | 2022 | 2022Q4 | 2022 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2022-04-25 | N | 86.6745 | N | 4 | N | N | 1.1101 | 39.4971 | 129401.9179
[7 empty] | 924 | 11276 | 1929162 | 2022-04-24 12:35 | 2022-04-25 16:15 | 1660 | 11kV | 112659 | 432 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex Panel 1, CP45189 Cooks Peats Ridge 0.5, tripped, reclosed and locked out Tree branch brought down OH, multiple bays of 11kV mains down between PT12386 and AB 45004 Relays: Earth Fault 11kV feeder from CP45189 (Recloser) to AB45004 tee PT64974 tee PT49032 tee PT12386 is defective | April | 2022 | 2022Q4 | 2022 | ZN12630:PA1 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2022-04-24 | N | 260.7847 | N | 4 | N | N | 1.1101 | 39.4971 | 82327.8743
[7 empty] | 1024 | 12971 | 1929307 | 2022-04-25 18:25 | 2022-04-25 20:00 | 95 | 11kV | 506625 | 5654 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn15006 Dee Why West - Pnl.2 - tripped on SEL Abnormal: USL24253 Open DMA, Closed S16618 Sw/A S17031 to S16733 UG cable DMA - S16559 Sw/B Closed 11kV UGOH bond open at pole LR-61930 See 1930554 1930557 1930558 1930560 | April | 2022 | 2022Q4 | 2022 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | Unknown | Unknown | 2022-04-25 | N | 89.6047 | N | 4 | N | N | 1.1101 | 39.4971 | 370226.6071
[7 empty] | 1627 | 19702 | 1929342 | 2022-04-26 05:37 | 2022-04-26 10:44 | 307 | 11kV | 92170 | 406 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of Milperra Zn2196 11kV Panel 11kV Bond blown at LB133 See OMS 1929649 1929342 | April | 2022 | 2022Q4 | 2022 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-04-26 | N | 227.0197 | N | 1 | N | N | 1.1101 | 39.4971 | 67355.1174
[7 empty] | 1312 | 15955 | 1929563 | 2022-04-27 08:57 | 2022-04-27 16:25 | 448 | 11kV | 329736 | 2281 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn36800 Waverley - Pnl.58 tripped on: earth fault UG cable fault between S46847 and S1183 S1183 restored via generator and LV // See 1930564 1930565 | April | 2022 | 2022Q4 | 2022 | ZN36800:PA58 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2022-04-27 | N | 144.5577 | N | 1 | N | N | 1.1101 | 39.4971 | 240961.3432
[7 empty] | 296 | 3763 | 1929753 | 2022-04-28 01:53 | 2022-04-28 10:30 | 517 | 11kV | 2585 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Light | N | S6916 Reserve Frederick No.1 - Tx No.2 tripped Transformer failure | April | 2022 | 2022Q4 | 2022 | ZN5868:PA30 | ZN5868:PA30 | ZN05868/000030 | WILLOUGHBY | UG | Not Veg | 2022-04-28 | N | 517 | N | 5 | N | N | 1.1101 | 39.4971 | 1889.0418
[7 empty] | 10 | 144 | 1929795 | 2022-04-28 10:07 | 2022-04-28 10:54 | 47 | 11kV | 41548 | 884 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.7 tripped on: OC Large magpie came into contact with N/O LB.62465 See also interruption to CP.61579 | April | 2022 | 2022Q4 | 2022 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2022-04-28 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 30362.0529
[7 empty] | 828 | 10198 | 1929796 | 2022-04-28 10:09 | 2022-04-28 13:00 | 171 | 11kV | 42483 | 466 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn965 Pennant Hills - Pnl.44 tripped and locked out on: B Phase OC Tree branch fell across N/O AB.1022 See also trip & reclosed on Pnl.33 See 1930572 1930573 | April | 2022 | 2022Q4 | 2022 | ZN965:PA44 | ZN965:PA44 | ZN00965/000044 | HORNSBY | OH | Veg | 2022-04-28 | N | 91.1652 | N | 5 | N | N | 1.1101 | 39.4971 | 31045.3234
[7 empty] | 829 | 10219 | 1929850 | 2022-04-28 15:30 | 2022-04-28 17:40 | 130 | 11kV | 390 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | ## No LID Report Operator J Hugg Broken LV x arm at sub 54002 Excluded OMS 1929850 related | April | 2022 | 2022Q4 | 2022 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2022-04-28 | N | 130 | N | 5 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 366 | 4919 | 1929866 | 2022-04-28 14:20 | 2022-04-29 04:33 | 853 | 11kV | 1652261 | 1937 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn80 Chatswood Panel 27 tripped on Relays: 27L: C phase OC, Earth Fault, EFI,Fault Check 27R: A phase OC, Earth Fault.EFI, Fault Check Signals: 11kV Trip, TX1` Group Earth, Zone Earth Field EFIs S24787 Abnormal Switching: S5852 SW/B Closed, S3911 SW/A Open S2268 SW/A Closed, S3864 SW/A Open Cause: Front line feeder fault - Section of 11kV feeder defective from ZN80 Chatswood Panel 27 to S50669 - S2268 to CP77878 See OMS 1930065 192866 192867 1929868 1929917 | April | 2022 | 2022Q4 | 2022 | ZN80:PA27 | ZN80:PA27 | ZN00080/000027 | WILLOUGHBY | UG | Not Veg | 2022-04-28 | N | 853 | N | 5 | N | N | 1.1101 | 39.4971 | 1207423.6054
[7 empty] | 1073 | 13801 | 1930023 | 2022-04-29 11:05 | 2022-04-29 12:30 | 85 | 11kV | 5270 | 62 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220980 11 Kv x arm could not be completed LL because of the X arm condition. Emergency. | April | 2022 | 2022Q4 | 2022 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2022-04-29 | N | 85 | N | 1 | N | N | 1.1101 | 39.4971 | 3851.1606
[7 empty] | 489 | 5944 | 1930169 | 2022-04-30 05:30 | 2022-04-30 10:25 | 295 | 11kV | 29089 | 137 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220983 2 fault operations 3 phase 51N protection flags. Bat on mains @ pole AJ-30525 Excluded OMS No. 1930169 + 1930170 | April | 2022 | 2022Q4 | 2022 | 814:82285 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2022-04-30 | N | 212.3285 | N | 4 | N | N | 1.1101 | 39.4971 | 21257.3832
[7 empty] | 695 | 8923 | 1930216 | 2022-04-30 10:33 | 2022-04-30 11:36 | 63 | 11kV | 2520 | 40 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 220984 B & C Phase DOLF : 20 Amp Branch on mains Excluded OMS 1930216 | April | 2022 | 2022Q4 | 2022 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2022-04-30 | N | 63 | N | 4 | N | N | 1.1101 | 39.4971 | 1841.5417
[7 empty] | 451 | 5529 | 1930202 | 2022-04-30 09:38 | 2022-04-30 11:52 | 134 | 11kV | 54940 | 410 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Empire Bay Pnl.8 - 11kV Bond off AB43265 (Load side) | April | 2022 | 2022Q4 | 2022 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2022-04-30 | N | 134 | N | 4 | N | N | 1.1101 | 39.4971 | 40148.5315
[7 empty] | 26 | 272 | 1930280 | 2022-04-30 21:14 | 2022-04-30 23:20 | 126 | 11kV | 81360 | 784 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn195 pymble - Pnl.25 tripped on: earth fault PT1425 Cultowa Rd - Tx failure See 1930583 1930584 | April | 2022 | 2022Q4 | 2022 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | OH | Not Veg | 2022-04-30 | N | 103.7755 | N | 4 | N | N | 1.1101 | 39.4971 | 59455.4883
[7 empty] | 191 | 2466 | 1930334 | 2022-05-01 15:35 | 2022-05-01 20:23 | 288 | 11kV | 523603 | 1954 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN1287 Revesby 11kV Panel 15 "S47211 Eastern Tomp, etc" tripped, re-closed and tripped Relays: C Phase O/C, Lockout relay, Timing relay Cause not ascertained | May | 2022 | 2022Q4 | 2022 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-05-01 | N | 267.9647 | N | 3 | N | N | 1.1101 | 39.4971 | 382633.6287
[7 empty] | 1564 | 19136 | 1930375 | 2022-05-01 22:05 | 2022-05-01 23:00 | 55 | 11kV | 56980 | 1036 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN1673 Turramurra - Panel 7 - Feeder tripped Possum on 11kV UGOH Derwent Ave Relays: EFI, Earth Fault, A & B IOC | May | 2022 | 2022Q4 | 2022 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2022-05-01 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 41639.3034
[7 empty] | 142 | 1718 | 1930338 | 2022-05-01 16:01 | 2022-05-02 08:08 | 967 | 11kV | 248428 | 420 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN874 Concord - Panel 3 - CB tripped Relays: EFI, Earth Fault Section of 11kV Feeder from S2031 Llewellyn St SW/B to S35569 Gauthorpe Marquet No.2 SW/A tee S6161 Llewellyn Cropley F/Sw Refer 1931085 1931086 1931087 1930338 1930365 | May | 2022 | 2022Q4 | 2022 | ZN874:PA3 | ZN874:PA3 | ZN00874/000003 | CANADA BAY | UG | Not Veg | 2022-05-01 | N | 591.4952 | N | 3 | N | N | 1.1101 | 39.4971 | 181543.855
[7 empty] | 103 | 1332 | 1930396 | 2022-05-02 06:59 | 2022-05-02 10:08 | 189 | 11kV | 210125 | 1159 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.180 Mosman - Pnl.20 tripped on: B Phase OC UG cable fault between S63994 Sw/B & S4282 Sw/A See 1932388 1932391 1932389 1932390 | May | 2022 | 2022Q4 | 2022 | ZN180:PA20 | ZN180:PA20 | ZN00180/000020 | NORTH SYDNEY | UG | Not Veg | 2022-05-02 | N | 181.2985 | N | 1 | N | N | 1.1101 | 39.4971 | 153553.1524
[7 empty] | 1194 | 14799 | 1930678 | 2022-05-03 10:08 | 2022-05-03 11:06 | 58 | 11kV | 116696 | 2012 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN398 Dulwich Hill - 11kV Panel 30 - CB tripped Relays: EF, EFI 11kV UG fault from S7433 Williams Constitution SW/B to S2261 Arlington St SW/A Refer 1930905 1930678 | May | 2022 | 2022Q4 | 2022 | ZN398:PA30 | ZN398:PA30 | ZN00398/000030 | INNER WEST | UG | Not Veg | 2022-05-03 | N | 58 | N | 2 | N | N | 1.1101 | 39.4971 | 85277.9949
[7 empty] | 453 | 5615 | 1930816 | 2022-05-03 21:17 | 2022-05-03 23:20 | 123 | 11kV | 52187 | 669 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN9037 Miranda - Panel 7 - ABC phases - Tripped due to UG fault Relays: EFI, Ceiling Contactor 11kV UG fault from Panel 7 to S9938 Princes Garnet to CP39346 tee PT 9467 Campbell Ruby | May | 2022 | 2022Q4 | 2022 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | UG | Not Veg | 2022-05-03 | N | 78.0075 | N | 2 | N | N | 1.1101 | 39.4971 | 38136.7203
[7 empty] | 1489 | 18369 | 1930819 | 2022-05-04 00:15 | 2022-05-04 00:43 | 28 | 11kV | 23362 | 865 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 220993 1 fault operation C Phase Overcurrent Possum at ABS 61760 Excluded OMS 1930819 | May | 2022 | 2022Q4 | 2022 | 205:12206 | 205:12206 | ZN00205/012206 | NEWCASTLE | OH | Not Veg | 2022-05-04 | N | 27.0081 | N | 6 | N | N | 1.1101 | 39.4971 | 17072.2605
[7 empty] | 1613 | 19622 | 1930855 | 2022-05-04 09:01 | 2022-05-04 11:30 | 149 | 11kV | 208858 | 2146 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN9118 Cronulla - Panel 20 "Burraneer Searl" feeder tripped on Relays: A and C phase o/current SW/B endbox blown at S9282 Allison Clyde (between S9845 Clyde Lewis to S9887 Parramatta Richmount to S9725 Parramatta Allison) Refer 1932100 1930855 | May | 2022 | 2022Q4 | 2022 | ZN9118:PA20 | ZN9118:PA20 | ZN09118/000020 | SUTHERLAND | UG | Not Veg | 2022-05-04 | N | 97.3243 | N | 6 | N | N | 1.1101 | 39.4971 | 152627.2661
[7 empty] | 765 | 9552 | 1930874 | 2022-05-04 10:20 | 2022-05-04 12:48 | 148 | 11kV | 2368 | 16 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 220994 Emergency NAR 97182. Advised By S Hewitt. 11Kv X arm on pole EO 40588 requires emergency replacement. Excluded OMS 1930874 | May | 2022 | 2022Q4 | 2022 | 513:83495 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2022-05-04 | N | 148 | N | 6 | N | N | 1.1101 | 39.4971 | 1730.4646
[7 empty] | 987 | 12076 | 1930820 | 2022-05-04 00:22 | 2022-05-04 15:12 | 890 | 11kV | 29644 | 150 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | Recloser CP44753 Bunning Creek - Tripped, re-closed and locked out on O/C OH down - Section of 11kV mains defective from LK41520 to PT18094 Bunning Ck Yarra 1.0 to PT13441 Bunning Ck Yarra 1.6 to PT18673 Bunning Ck Yarra 2.5 to PT13288 Bunning Ck Yarra 2.4 Ex ZN14891 Wyong - Panel 12 Refer 1932035 1932037 1932038 1932040 1930826 1930820 1931040 1931041 1931042 1931044 | May | 2022 | 2022Q4 | 2022 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2022-05-04 | N | 197.6267 | N | 6 | N | N | 1.1101 | 39.4971 | 21662.9609
[7 empty] | 537 | 6415 | 1930959 | 2022-05-04 15:02 | 2022-05-04 15:55 | 53 | 11kV | 53870 | 1885 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde 11kV panel 28 tripped, reclosed and locked out on Relays: OC A B and C phase, EF, Lockout and EFI Signals: 11kV Trip, Group Earth Field EFI's AB3048 Open, CP1476 Closed Cause: At S4931 Nola Dora 11kV RMI switch B end Box failed. Isolate and Put In LV parallel See OMS 1931029 1931031 1931034 1931035 1930959 1930961 193062 1930965 | May | 2022 | 2022Q4 | 2022 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | UG | Not Veg | 2022-05-04 | N | 28.5782 | N | 6 | N | N | 1.1101 | 39.4971 | 39366.6071
[7 empty] | 1041 | 13280 | 1931014 | 2022-05-04 22:21 | 2022-05-04 23:46 | 85 | 11kV | 95352 | 1122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn690 Campsie 11kV VCB Panel 6 Tripped on Relays: C phase IOC and Timed, EFI, Fault Check, Zone Earth Cause: UG cable fault from Zn690 Campsie Panel 6 to S79440 Canterbury Waverley to S78088 Canterbury Tudor No1 See OMS 1931023 1931024 S1931015 1931014 | May | 2022 | 2022Q4 | 2022 | ZN690:PA6 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-05-04 | N | 84.984 | N | 6 | N | N | 1.1101 | 39.4971 | 69680.4292
[7 empty] | 384 | 5052 | 1931033 | 2022-05-05 08:06 | 2022-05-05 11:55 | 229 | 11kV | 120975 | 1435 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | 11kV Recloser CP45061 Chain Valley Bay Mulloway (ZN13000 Lake Munmorah PA 7) Tripped, reclosed and locked out on Relays: OC trip, Lockout Tree on 11kV mains adjacent to PT11654 Kariola Findlay Refer 1931647 1931071 1931033 | May | 2022 | 2022Q4 | 2022 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Veg | 2022-05-05 | N | 84.3031 | N | 2 | N | N | 1.1101 | 39.4971 | 88404.9618
[7 empty] | 235 | 2868 | 1931106 | 2022-05-05 11:45 | 2022-05-05 14:35 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 220997 Single phase DOLF : 10 Amp Excluded OMS 1931106 | May | 2022 | 2022Q4 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2022-05-05 | N | 170 | N | 2 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 1087 | 13899 | 1931133 | 2022-05-06 09:00 | 2022-05-06 11:37 | 157 | 11kV | 7222 | 46 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | No LID Report Name Comment ADAM-ASSET DEFECTS TEAM helicopter patrol hazard - HV cross arm broken on end with insulator pulling out. Pole HY90146. excluded OMS 1931133 | May | 2022 | 2022Q4 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2022-05-06 | N | 157 | N | 1 | N | N | 1.1101 | 39.4971 | 5277.6246
[7 empty] | 233 | 2811 | 1931468 | 2022-05-08 00:36 | 2022-05-08 03:07 | 151 | 11kV | 137108 | 908 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | CP41389 - 11kV Roadside phase burnt off Ex ZN14144 Wamberal - Panel 7 Refer 1931468 | May | 2022 | 2022Q4 | 2022 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2022-05-08 | N | 151 | N | 3 | N | N | 1.1101 | 39.4971 | 100194.4824
[7 empty] | 772 | 9676 | 1931509 | 2022-05-08 12:30 | 2022-05-08 15:15 | 165 | 11kV | 330 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 221004 Single phase DOLF : 10 Amp Paraglider crashed intio 11kV oms reports was he was free, safe and on the ground, reported that paraglide machine feel through before staff arivved, fuse change only. Excluded oms 1931511 and 1921509 | May | 2022 | 2022Q4 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2022-05-08 | N | 165 | N | 3 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 63 | 798 | 1931541 | 2022-05-08 16:57 | 2022-05-08 20:20 | 203 | 11kV | 406 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221005 A Phase DOLF : 10 Amp Excluded OMS 1931541 | May | 2022 | 2022Q4 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-05-08 | N | 203 | N | 3 | N | N | 1.1101 | 39.4971 | 296.6928
[7 empty] | 1227 | 15050 | 1931664 | 2022-05-09 13:10 | 2022-05-09 15:48 | 158 | 11kV | 6162 | 39 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Air Break Switch | Unplanned | Rain Heavy | N | Section of 11kV feeder from AB45024 to PT47538 Boundary Woodfield to PT43209 Boundary Woodfield 0.5 to PT14485 Boundary Fletcher interrupted to make emergency repairs. Interrupted for safety reasons to repair HR bond at AB45024 Ex ZN12570 Avoca, Panel 24 'Kincumber' | May | 2022 | 2022Q4 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2022-05-09 | N | 158 | N | 2 | N | N | 1.1101 | 39.4971 | 4503.0079
[7 empty] | 1625 | 19693 | 1931641 | 2022-05-09 15:45 | 2022-05-09 17:00 | 75 | 11kV | 5550 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Section of 11kV Feeder interrupted from LB62900 to S14269 Jacana Narara Creek to PT12971 Narara Ck Manns 0.9 to make emergency repairs. Interrupted for safety reasons to remove tree branch off the 11kV mains. Ex ZN12650 West Gosford, Panel 13 | May | 2022 | 2022Q4 | 2022 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2022-05-09 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 4055.7763
[7 empty] | 1571 | 19210 | 1931941 | 2022-05-10 18:36 | 2022-05-10 20:08 | 92 | 11kV | 39560 | 430 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S6391 Glen Dind No.2 - 11kV CB tripped Relay: Short Translay UG fault - Located between S7675 Glen Northcliff (SW/B) to S217 Bligh Humphrey (SW/C) CC1: 22-"Refer to SOp" | May | 2022 | 2022Q4 | 2022 | ZN35400:PA79 | ZN35400:PA79 | ZN35400/000079 | NORTH SYDNEY | UG | Not Veg | 2022-05-10 | N | 92 | N | 1 | N | N | 1.1101 | 39.4971 | 28909.2812
[7 empty] | 1444 | 17800 | 1932012 | 2022-05-11 09:46 | 2022-05-11 11:05 | 79 | 11kV | 7900 | 100 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT9381 Woronora Havelock - Blew 11kV centre phase 50A HDO Fuse Fatigue - Restored via LV network | May | 2022 | 2022Q4 | 2022 | ZN9245:PA13 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Not Veg | 2022-05-11 | N | 79 | N | 1 | N | N | 1.1101 | 39.4971 | 5773.087
[7 empty] | 1446 | 17826 | 1932215 | 2022-05-12 05:38 | 2022-05-12 09:38 | 240 | 11kV | 17880 | 198 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 221017 2 fault operations Earth Fault MVA Pole JS-57003 Sw 81648 Aprot 51N E/F Excluded oms 1932215 | May | 2022 | 2022Q4 | 2022 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Not Veg | 2022-05-12 | N | 90.303 | N | 7 | N | N | 1.1101 | 39.4971 | 13066.1766
[7 empty] | 1447 | 17841 | 1932348 | 2022-05-12 12:30 | 2022-05-12 14:05 | 95 | 11kV | 7505 | 79 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 221019 Isolated for repair Rotten x arm pole IU-91279, isolated to repair. Excluded OMS 1932348 | May | 2022 | 2022Q4 | 2022 | 224:80326 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Not Veg | 2022-05-12 | N | 95 | N | 7 | N | N | 1.1101 | 39.4971 | 5484.4326
[7 empty] | 322 | 4313 | 1932324 | 2022-05-12 10:59 | 2022-05-12 14:20 | 201 | 11kV | 148164 | 2306 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1285 Greenacre Park - Pnl.23 tripped on: Earth Fault and OC Abnormal: S63510 Sw/B closed with S6887 Sw/A Open and S3653 Sw/B Open UG cable fault between S63301 Sw/B, S7626 Sw/A and S1213 Sw/A See 1933365 1933366 | May | 2022 | 2022Q4 | 2022 | ZN1285:PA23 | ZN37100:PA33 | ZN37100/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-05-12 | N | 64.2515 | N | 7 | N | N | 1.1101 | 39.4971 | 108273.8811
[7 empty] | 1595 | 19467 | 1932203 | 2022-05-12 00:50 | 2022-05-12 14:30 | 820 | 11kV | 196490 | 1140 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | Zn12620 Noraville - Pnl.10 tripped on: Earth Fault Car hit pole BU2690 (USL35502 on pole) See 1933354 1933355 1933360 1933361 1933363 | May | 2022 | 2022Q4 | 2022 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2022-05-12 | N | 172.3596 | N | 7 | N | N | 1.1101 | 39.4971 | 143589.0965
[7 empty] | 261 | 3363 | 1932410 | 2022-05-12 17:10 | 2022-05-12 18:50 | 99.5333 | 11kV | 1293.9333 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 221020 Out of service 33kV crossarm failed & fell onto 11kV Fdr @ pole IV-64033. Excluded 1932410 | May | 2022 | 2022Q4 | 2022 | 220:8688 | 220:8688 | ZN00220/008688 | LAKE MACQUARIE | OH | Not Veg | 2022-05-12 | N | 99.5333 | N | 7 | N | N | 1.1101 | 39.4971 | 945.5683
[7 empty] | 1341 | 16355 | 1932444 | 2022-05-13 08:30 | 2022-05-13 09:20 | 50 | 11kV | 250 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 221022 Bail clamp burning up at sub 53000 montrose. Excluded OMS 1932497 | May | 2022 | 2022Q4 | 2022 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2022-05-13 | N | 50 | N | 1 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 793 | 9912 | 1932462 | 2022-05-12 23:12 | 2022-05-13 12:10 | 778 | 11kV | 22503 | 119 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 221021 4 fault operations B & C Phases LL Loops @ sub 71375 resting on crossarm. Excluded OMS No. 1932462 1932475 | May | 2022 | 2022Q4 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2022-05-12 | N | 189.1008 | N | 7 | N | N | 1.1101 | 39.4971 | 16444.5287
[7 empty] | 462 | 5686 | 1932455 | 2022-05-12 21:36 | 2022-05-13 13:50 | 974 | 11kV | 3161 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | REC26228 tripped,, reclosed, tripped & locked out on: Earth fault Tree brought down OH mains at pole FF-00433 See 1933369 1933370 | May | 2022 | 2022Q4 | 2022 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2022-05-12 | N | 790.25 | N | 7 | N | N | 1.1101 | 39.4971 | 2309.9656
[7 empty] | 1287 | 15662 | 1932699 | 2022-05-14 09:27 | 2022-05-14 10:40 | 73 | 11kV | 146 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221028 C Phase DOLF : 16 Amp No Cause Found Excluded OMS 1932699 | May | 2022 | 2022Q4 | 2022 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2022-05-14 | N | 73 | N | 3 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 368 | 4922 | 1932675 | 2022-05-14 07:17 | 2022-05-14 17:15 | 597.7333 | 11kV | 10161.4667 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 221031 Single Phase DOLF : 20 Amp 20 amp LF 31387 replaced tx 47310 replaced | May | 2022 | 2022Q4 | 2022 | 509:33395 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2022-05-14 | N | 597.7333 | N | 3 | N | N | 1.1101 | 39.4971 | 7425.7001
[7 empty] | 746 | 9418 | 1932754 | 2022-05-14 16:00 | 2022-05-14 20:25 | 265 | 11kV | 4045 | 28 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 221032 John Frazer assigned broken x-arm pole WS-90017 Fdr needs to be isolated from ABS 26184 for repairs Excluded OMS 1932754 | May | 2022 | 2022Q4 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-05-14 | N | 144.4643 | N | 3 | N | N | 1.1101 | 39.4971 | 2955.9667
[7 empty] | 680 | 8689 | 1932853 | 2022-05-15 14:32 | 2022-05-15 15:47 | 75 | 11kV | 69730 | 3927 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn847 Hornsby - Pnl.7 tripped on: Earth Fault Pnl.36 tripped on Earth fault during restoration attempt Abnormal: S8497 Sw/B closed with S7732 Sw/A open UG cable fault between S4381 Sw/B and S5157 Sw/A Note: EFIs did not work at S64866 or S4381 See 1933987 1933988 1933989 1933991 1933990 | May | 2022 | 2022Q4 | 2022 | ZN847:PA7 | ZN847:PA7 | ZN00847/000007 | HORNSBY | UG | Not Veg | 2022-05-15 | N | 17.7566 | N | 2 | N | N | 1.1101 | 39.4971 | 50956.6273
[7 empty] | 679 | 8679 | 1932827 | 2022-05-15 09:41 | 2022-05-15 18:00 | 499 | 11kV | 10479 | 21 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | S5644 Dunning Hayes No.1 - 2 x HV fuse blown Fault on customer's equipment - Fuses not grading. | May | 2022 | 2022Q4 | 2022 | ZN188:PA32 | ZN8100:PA30 | ZN08100/000030 | SYDNEY | Unknown | Not Veg | 2022-05-15 | N | 499 | N | 2 | N | N | 1.1101 | 39.4971 | 7657.7441
[7 empty] | 1563 | 19135 | 1932994 | 2022-05-16 10:30 | 2022-05-16 11:20 | 50 | 11kV | 9581 | 737 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S1673 Turramurra Panel 2 Tripped on Relays: IOC A and B phase, OC A and B phase - EFI Abnormal Switching: SW/C Open at CP373, AB3019, LB2209 Closed, PT1917 in LV parallel Cause: NAR96911 Turrmurra submitted for the restoration of DMA section between CP373 and CP3019 - Failed on Energising on supposedly repaired HV UGOH adj CP373 SwC. DOp found branch on OH and tried back faulty section back faulty section at 11:19 causing feeder to trip again, branch evidently not the cause | May | 2022 | 2022Q4 | 2022 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | Unknown | Unknown | 2022-05-16 | N | 13 | N | 1 | N | N | 1.1101 | 39.4971 | 7001.5122
[7 empty] | 612 | 7813 | 1933233 | 2022-05-17 13:55 | 2022-05-18 06:05 | 970 | 11kV | 113769 | 316 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn35500 Top Ryde - Pnl.14 tripped on OC and Earth Fault Abnormal: S1896 Sw/A closed with S35185 Sw/A Open (DMA since 11/4) UG cable fault between S8532 Sw/A, S46817 Sw/A and S1896 Sw/A During proving feeder from S8532 Sw/A, REC2749 tripped on Earth Fault UG cable fault between S8532 Sw/A and S8911 Sw/B See 1934015 1934016 1934017 | May | 2022 | 2022Q4 | 2022 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2022-05-17 | N | 360.0285 | N | 1 | N | N | 1.1101 | 39.4971 | 83139.0296
[7 empty] | 1221 | 15038 | 1933437 | 2022-05-18 12:55 | 2022-05-18 13:28 | 33 | 11kV | 19140 | 580 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn3672 Maroubra - Pnl.42 tripped on: B phase Earth Fault UG cable fault in front line section of feeder | May | 2022 | 2022Q4 | 2022 | ZN3672:PA42 | ZN3672:PA42 | ZN03672/000042 | BAYSIDE | UG | Not Veg | 2022-05-18 | N | 33 | N | 2 | N | N | 1.1101 | 39.4971 | 13986.9475
[7 empty] | 211 | 2613 | 1933469 | 2022-05-18 15:46 | 2022-05-18 16:25 | 39 | 11kV | 195 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 221035 interr to fix 11kv ohm mains at SR-53201. ohm off pin | May | 2022 | 2022Q4 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2022-05-18 | N | 39 | N | 2 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 1243 | 15179 | 1933723 | 2022-05-20 00:37 | 2022-05-20 02:30 | 113 | 11kV | 299753 | 2757 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly - Pnl.42 tripped on: Earth Fault UG cable fault between S36072 Sw/B, S78890 Sw/B and S50120 Sw/A See 1938142 1938143 | May | 2022 | 2022Q4 | 2022 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2022-05-20 | N | 108.7243 | N | 4 | N | N | 1.1101 | 39.4971 | 219050.6512
[7 empty] | 548 | 6703 | 1933728 | 2022-05-20 03:39 | 2022-05-20 04:47 | 68 | 11kV | 3468 | 51 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | No Weather Impact | N | REC705 Knights Chad - tripped on: OC and IOC Possum caused flashover at LB62109 | May | 2022 | 2022Q4 | 2022 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2022-05-20 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 2534.3121
[7 empty] | 229 | 2776 | 1933898 | 2022-05-20 18:10 | 2022-05-20 19:18 | 68 | 11kV | 45220 | 665 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 221042 A & B Phase lockout Overcurrent metalic balloon removed from ohm at pole IV-93451 Excluded oms 1933900 | May | 2022 | 2022Q4 | 2022 | 222:33597 | 222:33597 | ZN00222/033597 | LAKE MACQUARIE | OH | Veg | 2022-05-20 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 33045.4422
[7 empty] | 298 | 3783 | 1933933 | 2022-05-21 06:47 | 2022-05-21 08:40 | 113 | 11kV | 113784 | 1594 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Light | N | No LID Report Bird on 11kV UGOH pole JV-30167 Excluded OMS 1933933 | May | 2022 | 2022Q4 | 2022 | 204:82697 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2022-05-21 | N | 71.3827 | N | 1 | N | N | 1.1101 | 39.4971 | 83149.9911
[7 empty] | 1282 | 15618 | 1933921 | 2022-05-20 22:40 | 2022-05-21 14:50 | 970 | 11kV | 1940 | 2 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Ex Pnl.16 Leichhardt Pnl.12 - section of 11kV feeder from S2449 Sw/A and S1540 Sw/B tee S1436 isolated to replace condemmed poles | May | 2022 | 2022Q4 | 2022 | ZN116:PA12 | ZN116:PA12 | ZN00116/000012 | INNER WEST | OH | Not Veg | 2022-05-20 | N | 970 | N | 4 | N | N | 1.1101 | 39.4971 | 1417.6948
[7 empty] | 1475 | 18208 | 1934268 | 2022-05-23 09:48 | 2022-05-23 12:35 | 167 | 11kV | 334 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 221052 DOLF : 10 Amp blown L/A's Excluded OMS 1934268 | May | 2022 | 2022Q4 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2022-05-23 | N | 167 | N | 2 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 620 | 7991 | 1934362 | 2022-05-23 14:08 | 2022-05-23 18:50 | 281.6 | 11kV | 1126.4 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Operator D Apps Blown LF 74337- 1 phase 10Amp No cause found | May | 2022 | 2022Q4 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2022-05-23 | N | 281.6 | N | 2 | N | N | 1.1101 | 39.4971 | 823.1399
[7 empty] | 82 | 977 | 1934521 | 2022-05-24 08:26 | 2022-05-24 09:25 | 59 | 11kV | 59 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Heavy | N | LID 221055 A Phase DOLF : 10 Amp no cause found Excluded oms 1934521 | May | 2022 | 2022Q4 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2022-05-24 | N | 59 | N | 3 | N | N | 1.1101 | 39.4971 | 43.1155
[7 empty] | 1398 | 17131 | 1934550 | 2022-05-24 10:10 | 2022-05-24 14:00 | 230 | 11kV | 840 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LIS 221054 DOLF : 10 Amp Sub 70440 had a blown arrestor. Sub dolf didnt blow but LF 70440 did. 10amp replcaed. excluded OMS 1934550 | May | 2022 | 2022Q4 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2022-05-24 | N | 210 | N | 3 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 722 | 9251 | 1934530 | 2022-05-24 11:45 | 2022-05-24 14:42 | 177 | 11kV | 8496 | 48 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | No LID Report Interr- 11:45 rest 14:45 to HP 50210 and HP 43578 RHS only replace broken 11kV X arm at ABS 9130 - xarm severly split Excluded OMS 1934530 operator D mcphail & T Cameron | May | 2022 | 2022Q4 | 2022 | 532:83309 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2022-05-24 | N | 177 | N | 3 | N | N | 1.1101 | 39.4971 | 6208.6262
[7 empty] | 1451 | 17886 | 1934760 | 2022-05-25 09:11 | 2022-05-25 11:55 | 164 | 11kV | 1968 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 221056 20 Amp, Phases A & B. Line DOLF Refer to oms 1934760 no cause found SOP CAMERON T DOP WATTERS L | May | 2022 | 2022Q4 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-05-25 | N | 164 | N | 3 | N | N | 1.1101 | 39.4971 | 1438.1564
[7 empty] | 1677 | 20379 | 1934885 | 2022-05-25 15:19 | 2022-05-25 17:22 | 123 | 11kV | 88698 | 1162 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn195 Pymble - Pnl.29 tripped on: Earth Fault Abnormal: S4650 Sw/B closed with Sw/A Open Fault section of UG cable between S46905 and S4643 tee PT15 See 1935351 1935352 1935353 | May | 2022 | 2022Q4 | 2022 | ZN195:PA29 | ZN195:PA29 | ZN00195/000029 | KU-RING-GAI | UG | Not Veg | 2022-05-25 | N | 76.3322 | N | 3 | N | N | 1.1101 | 39.4971 | 64817.8823
[7 empty] | 1167 | 14635 | 1934951 | 2022-05-25 23:46 | 2022-05-26 01:20 | 94 | 11kV | 8554 | 91 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT2156 Beresford Norman - 50A HDO blown on Roadside Cause: Fuse Fatigue See OMS 1934985 1934954 1934953 1934951 | May | 2022 | 2022Q4 | 2022 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | OH | Not Veg | 2022-05-25 | N | 94 | N | 3 | N | N | 1.1101 | 39.4971 | 6251.0109
[7 empty] | 577 | 7253 | 1935022 | 2022-05-26 10:26 | 2022-05-26 11:32 | 66 | 11kV | 54780 | 830 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn15015 North Head - Pnl.15 tripped on: A Phase IOC, C phase OC Abnormal: S16690 Sw/B Closed with S16721 Sw/B Open and Pnl.5 CB Open (Multiple DMAs) S16374 North Head Aux, Sw/F end box failed | May | 2022 | 2022Q4 | 2022 | ZN15015:PA15 | ZN15015:PA15 | ZN15015/000015 | NORTHERN BEACHES | UG | Not Veg | 2022-05-26 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 40031.6083
[7 empty] | 1343 | 16362 | 1935137 | 2022-05-26 17:07 | 2022-05-26 18:37 | 90 | 11kV | 63990 | 711 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.21+23 (ring feeder) tripped on: Pnl.21: Translay & EF Pnl23: B Phase OC @ S.3554 - Sw/B and Tx 2 LV ACB found open 11kV Enbox of Panel 21 failed explosvely at Darlinghurst Zn | May | 2022 | 2022Q4 | 2022 | ZN931:PA23 | ZN931:PA23 | ZN00931/000023 | SYDNEY | UG | Not Veg | 2022-05-26 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 46762.0046
[7 empty] | 1124 | 14252 | 1935310 | 2022-05-27 18:48 | 2022-05-27 20:57 | 129 | 11kV | 127853 | 1041 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1850 Bass Hill - Pnl.40 tripped on: B&C phase IOC UG cable fault See 1935366 1935367 | May | 2022 | 2022Q4 | 2022 | ZN1850:PA40 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-05-27 | N | 122.8175 | N | 1 | N | N | 1.1101 | 39.4971 | 93431.2014
[7 empty] | 1222 | 15039 | 1935327 | 2022-05-28 00:50 | 2022-05-28 01:58 | 68 | 11kV | 45016 | 662 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn711 Blackwattle Bay - Pnl.18 tripped on: Earth Fault UG cable fault between S44 Sw/A, S4362 Sw/B and S7054 Sw/B | May | 2022 | 2022Q4 | 2022 | ZN711:PA18 | ZN711:PA18 | ZN00711/000018 | SYDNEY | UG | Not Veg | 2022-05-28 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 32896.3651
[7 empty] | 633 | 8207 | 1935429 | 2022-05-28 12:38 | 2022-05-28 14:10 | 92 | 11kV | 227864 | 2593 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn342 Paddington - Pnl.22 tripped on (Pnl.22L) OC & EF UG cable fault between S48603 Sw/B and S2332 Sw/A See 1937846 1937847 | May | 2022 | 2022Q4 | 2022 | ZN342:PA22 | ZN342:PA22 | ZN00342/000022 | SYDNEY | UG | Not Veg | 2022-05-28 | N | 87.8766 | N | 4 | N | N | 1.1101 | 39.4971 | 166516.2903
[7 empty] | 1175 | 14716 | 1935463 | 2022-05-28 14:52 | 2022-05-28 16:20 | 88 | 11kV | 92928 | 1056 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Rockdale Zn Pnl.13 - 11kV bond off between S10998 and S65909 | May | 2022 | 2022Q4 | 2022 | ZN10998:PA13 | ZN10998:PA13 | ZN10998/000013 | BAYSIDE | OH | Not Veg | 2022-05-28 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 67909.0415
[7 empty] | 1231 | 15091 | 1935504 | 2022-05-28 19:10 | 2022-05-28 22:30 | 200 | 11kV | 1800 | 9 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | PT12225 Old Maitland Cobbs 0.5 - Middle Phase HDO blown Suspect lightning | May | 2022 | 2022Q4 | 2022 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2022-05-28 | N | 200 | N | 4 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 1481 | 18317 | 1935528 | 2022-05-29 01:22 | 2022-05-29 02:53 | 91 | 11kV | 96170 | 1063 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Zn10997 Sans Souci - Pnl.1 tripped, reclosed, tripped and locked out on IOC Cause not ascertained See 1937860 1937861 | May | 2022 | 2022Q4 | 2022 | ZN10997:PA1 | ZN10997:PA1 | ZN10997/000001 | BAYSIDE | OH | Veg | 2022-05-29 | N | 90.4704 | N | 4 | N | N | 1.1101 | 39.4971 | 70278.1995
[7 empty] | 421 | 5301 | 1935593 | 2022-05-29 14:20 | 2022-05-29 16:07 | 107 | 11kV | 214 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221065 A Phase DOLF : 10 Amp 10A A phase DOLF Bird. Excluded OMS 1935593 | May | 2022 | 2022Q4 | 2022 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2022-05-29 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 1310 | 15939 | 1935604 | 2022-05-29 15:50 | 2022-05-29 17:21 | 91 | 11kV | 151525 | 2021 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn10995 Riverwood - Pnl.6 tripped on: C phase ICO Time over current, EFI Field EFI's: S, 76805, S65982, S65704 UG cable fault between S65704 Sw/B and S10022 EFI did not operate at S79372 this is the reason why we did not utilies the DMC subs in the field to restore supply as we could not be certain of fault location. See 1937865 1937866 1937867 also LV// in and LV// collapsed due to feeder fault see event ID 10809 and OMS 1935609 | May | 2022 | 2022Q4 | 2022 | ZN10995:PA6 | ZN10995:PA6 | ZN10995/000006 | GEORGES RIVER | UG | Not Veg | 2022-05-29 | N | 74.9753 | N | 4 | N | N | 1.1101 | 39.4971 | 110730.0008
[7 empty] | 1466 | 18123 | 1935643 | 2022-05-29 22:41 | 2022-05-30 01:26 | 165 | 11kV | 96303 | 595 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn931 Darlinghurst - Pnl.18 tripped on: Short Translay UG cable fault in front line section between Pnl.18, S35424, S46974 7 S36107 See 1937872 | May | 2022 | 2022Q4 | 2022 | ZN931:PA18 | ZN931:PA18 | ZN00931/000018 | SYDNEY | UG | Not Veg | 2022-05-29 | N | 161.8538 | N | 4 | N | N | 1.1101 | 39.4971 | 70375.3919
[7 empty] | 85 | 1021 | 1935660 | 2022-05-30 06:40 | 2022-05-30 15:40 | 540 | 11kV | 154185 | 1073 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | Y | Zn12690 Berkeley Vale - Pnl.12 tripped, reclosed & tripped on: ABC OC and EF Blown arrestors at 11kV UGOH above LB65005 See 1937902 1937903 1937904 1937905 | May | 2022 | 2022Q4 | 2022 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2022-05-30 | N | 143.6952 | N | 4 | N | N | 1.1101 | 39.4971 | 112673.8503
[7 empty] | 1533 | 18845 | 1935765 | 2022-05-30 14:06 | 2022-05-30 16:03 | 117 | 11kV | 173298 | 1618 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | Zn.187 Crows Nest - Pnl.13 tripped onL Earth Fault UG cable fault between S8545, S4726, S48856 and S3496 See 1937910 1937911 | May | 2022 | 2022Q4 | 2022 | ZN187:PA13 | ZN187:PA13 | ZN00187/000013 | NORTH SYDNEY | UG | Not Veg | 2022-05-30 | N | 107.1063 | N | 4 | N | N | 1.1101 | 39.4971 | 126641.067
[7 empty] | 56 | 684 | 1935655 | 2022-05-30 05:11 | 2022-05-30 17:09 | 718 | 11kV | 718 | 1 | HV | Vandalism | 3rd Party Impact | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | LID 221068 Attempted copper theft and damage to assetts between ABS 7931 & 16506 Excluded OMS 1935655 | May | 2022 | 2022Q4 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 718 | N | 4 | N | Y | 1.1101 | 39.4971 | 524.6932
[7 empty] | 821 | 10121 | 1935814 | 2022-05-30 16:50 | 2022-05-30 18:32 | 102 | 11kV | 8160 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At S35370 Galston Ex 11kV panel Nos, Rec 3280 Hunt ave tripped on Relays O/C trip and Lockout Tree branch on OH Mains removed by DOP | May | 2022 | 2022Q4 | 2022 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2022-05-30 | Y | 102 | N | 4 | N | Y | 1.1101 | 39.4971 | 5963.0873
[7 empty] | 539 | 6456 | 1935843 | 2022-05-30 17:06 | 2022-05-30 18:34 | 88 | 11kV | 2904 | 33 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 221121 1 fault operation 3 phase Overcurrent Tree on 11kV OHM adjacent ABS 40900. Excluded OMS No. 1935843 | May | 2022 | 2022Q4 | 2022 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2022-05-30 | Y | 88 | N | 4 | N | Y | 1.1101 | 39.4971 | 2122.1575
[7 empty] | 300 | 3815 | 1935801 | 2022-05-30 16:25 | 2022-05-30 19:30 | 185 | 11kV | 8731 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221072 1 fault operation Overcurrent | May | 2022 | 2022Q4 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2022-05-30 | Y | 158.7455 | N | 4 | N | Y | 1.1101 | 39.4971 | 6380.3573
[7 empty] | 1305 | 15896 | 1935813 | 2022-05-30 16:50 | 2022-05-30 19:38 | 168 | 11kV | 98952 | 589 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | At S35370 Galston 11kV panel No 10 tripped on Relays A = C phase IOC, EFI, Rec timing relay Signals 11kV trip EFI S47362 Tree brans on OH mains removed by DOP | May | 2022 | 2022Q4 | 2022 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2022-05-30 | Y | 168 | N | 4 | N | Y | 1.1101 | 39.4971 | 72311.203
[7 empty] | 1168 | 14644 | 1936106 | 2022-05-30 18:39 | 2022-05-30 20:15 | 96 | 11kV | 7776 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn 36200 Empire Bay panel 8, S49860 Poole Belrose PT13215 Pomom Wards Hill 11kV road side phase HDO operated Cause not ascertained, bad weather | May | 2022 | 2022Q4 | 2022 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2022-05-30 | N | 96 | N | 4 | N | N | 1.1101 | 39.4971 | 5682.4714
[7 empty] | 1539 | 18869 | 1935967 | 2022-05-30 17:06 | 2022-05-30 20:21 | 195 | 11kV | 13065 | 75 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221099 Tree branch on mains pole BQ-30062 Excluded OMS 1935851 | May | 2022 | 2022Q4 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-05-30 | Y | 174.2 | N | 4 | N | Y | 1.1101 | 39.4971 | 9547.5166
[7 empty] | 1181 | 14738 | 1935893 | 2022-05-30 17:22 | 2022-05-30 20:44 | 202 | 11kV | 261616 | 1453 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 221178 Overcurrent Broken Insulator FS-82905 Excluded OMS 1935893 | May | 2022 | 2022Q4 | 2022 | 522:83124 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 180.0523 | N | 4 | N | Y | 1.1101 | 39.4971 | 191181.2564
[7 empty] | 1654 | 20092 | 1935889 | 2022-05-30 17:13 | 2022-05-30 21:10 | 237 | 11kV | 168285 | 715 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221093 Branch on OHM 13 Satur Rd Trees removed | May | 2022 | 2022Q4 | 2022 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Veg | 2022-05-30 | Y | 235.3636 | N | 4 | N | Y | 1.1101 | 39.4971 | 122977.7144
[7 empty] | 626 | 8056 | 1936269 | 2022-05-30 21:00 | 2022-05-30 21:28 | 28 | 11kV | 840 | 30 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 221075 B & C Phase DOLF : 20 Amp dop D Robertson reported outage and replaced dolfs Excluded OMS 1936269 | May | 2022 | 2022Q4 | 2022 | 258:80793 | 258:80793 | ZN00258/080793 | LAKE MACQUARIE | OH | Veg | 2022-05-30 | Y | 28 | N | 4 | N | Y | 1.1101 | 39.4971 | 613.8472
[7 empty] | 873 | 10824 | 1935868 | 2022-05-30 17:13 | 2022-05-30 21:45 | 272 | 11kV | 635288 | 2679 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | Zn1193 Lindfield - Pnl.28 tripped on: IOC Abnormal: S46817 Sw/B closed with S8532 Sw/A Open Weather related, suspect UGOH or UG cable fault between LB2845 and S4258 See 1937953 1937954 1937959 | May | 2022 | 2022Q4 | 2022 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | KU-RING-GAI | UG | Not Veg | 2022-05-30 | Y | 237.1362 | N | 4 | N | Y | 1.1101 | 39.4971 | 464249.7326
[7 empty] | 238 | 2940 | 1936146 | 2022-05-30 17:15 | 2022-05-30 21:50 | 275 | 11kV | 10171 | 41 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221096 Tree on mains pole EL-10071 Excluded OMS 1936146 | May | 2022 | 2022Q4 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2022-05-30 | Y | 248.0732 | N | 4 | N | Y | 1.1101 | 39.4971 | 7432.6668
[7 empty] | 1 | 45 | 1935960 | 2022-05-30 17:42 | 2022-05-30 22:28 | 286 | 11kV | 180528 | 1305 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221077 A & B Phase Overcurrent Tree on mains pole IV-60526 Excluded OMS 1935960 | May | 2022 | 2022Q4 | 2022 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Veg | 2022-05-30 | Y | 138.3356 | N | 4 | N | Y | 1.1101 | 39.4971 | 131924.5377
[7 empty] | 335 | 4686 | 1935828 | 2022-05-30 17:01 | 2022-05-30 22:55 | 354 | 11kV | 75106 | 525 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221071 2 fault operations Mains down beyond AK-92010 Excluded OMS 1935828 | May | 2022 | 2022Q4 | 2022 | 801:74117 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | OH | Not Veg | 2022-05-30 | Y | 143.059 | N | 4 | N | Y | 1.1101 | 39.4971 | 54885.2495
[7 empty] | 942 | 11385 | 1935805 | 2022-05-30 16:38 | 2022-05-30 23:00 | 382 | 11kV | 19634 | 62 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221074 2 fault operations Overcurrent OHM down near sub 70700 Excluded OMS 1935805 | May | 2022 | 2022Q4 | 2022 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2022-05-30 | Y | 316.6774 | N | 4 | N | Y | 1.1101 | 39.4971 | 14347.9481
[7 empty] | 1391 | 17049 | 1935926 | 2022-05-30 17:32 | 2022-05-30 23:00 | 328 | 11kV | 7544 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | Y | LID 221133 DOLF : 20 Amp Excluded OMS 1936277 | May | 2022 | 2022Q4 | 2022 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2022-05-30 | Y | 328 | N | 4 | N | Y | 1.1101 | 39.4971 | 5512.9327
[7 empty] | 1607 | 19559 | 1936332 | 2022-05-30 23:37 | 2022-05-31 00:30 | 53 | 11kV | 42930 | 810 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221082 A & B Phase Earth Fault large tree on lv mains brushed hv mains while reclose was off for previous outage Excluded OMS 1936332 | May | 2022 | 2022Q4 | 2022 | 270:83591 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2022-05-30 | Y | 53 | N | 4 | N | Y | 1.1101 | 39.4971 | 31371.9778
[7 empty] | 641 | 8279 | 1935981 | 2022-05-30 17:47 | 2022-05-31 00:58 | 431 | 11kV | 79309 | 198 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221084 Tree on mains between JS-57003 & JS-50237 Excluded OMS 1935981 | May | 2022 | 2022Q4 | 2022 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Veg | 2022-05-30 | Y | 400.5505 | N | 4 | N | Y | 1.1101 | 39.4971 | 57956.678
[7 empty] | 121 | 1508 | 1935984 | 2022-05-30 23:21 | 2022-05-31 01:18 | 117 | 11kV | 113824 | 1091 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221087 B & C Phase Overcurrent First 6 calls in excluded job related to LID 221086/ OMS 1936723 Excluded OMS 1935984 | May | 2022 | 2022Q4 | 2022 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2022-05-30 | Y | 104.33 | N | 4 | N | Y | 1.1101 | 39.4971 | 83179.222
[7 empty] | 1020 | 12886 | 1936014 | 2022-05-30 16:52 | 2022-05-31 02:00 | 548 | 11kV | 319184 | 742 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221073 2 fault operation Tree on OHM near sub 70567 Excluded OMS 1935817 | May | 2022 | 2022Q4 | 2022 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2022-05-30 | Y | 430.1671 | N | 4 | N | Y | 1.1101 | 39.4971 | 233250.2529
[7 empty] | 132 | 1624 | 1936070 | 2022-05-30 18:24 | 2022-05-31 02:00 | 456 | 11kV | 912 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Wind Strong | Y | LID 221127 Dolf knocked out by debris Excluded OMS 1936070 | May | 2022 | 2022Q4 | 2022 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2022-05-30 | Y | 456 | N | 4 | N | Y | 1.1101 | 39.4971 | 666.4627
[7 empty] | 940 | 11359 | 1935959 | 2022-05-30 17:41 | 2022-05-31 02:16 | 515 | 11kV | 207669 | 1635 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221095 Tree on mains IT-93309 TREES HAVE BROUGHT POLE TO POLE WIRES DOWN CAD 528228 Excluded OMS 1935959 | May | 2022 | 2022Q4 | 2022 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Veg | 2022-05-30 | N | 127.0147 | N | 4 | N | N | 1.1101 | 39.4971 | 151758.38
[7 empty] | 1452 | 17887 | 1935924 | 2022-05-30 17:21 | 2022-05-31 02:45 | 564 | 11kV | 22880 | 64 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221092 Mains down between ER33031 EQ90237 and ER33144. Excluded OMS 1935924 | May | 2022 | 2022Q4 | 2022 | 512:83743 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2022-05-30 | Y | 357.5 | N | 4 | N | Y | 1.1101 | 39.4971 | 16720.0292
[7 empty] | 748 | 9425 | 1935904 | 2022-05-30 17:23 | 2022-05-31 04:00 | 637 | 11kV | 498671 | 1429 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | At Zn129 Hunters Hill PAnel 41 tripped on Relays: E/F, EFI, Rec Lockout Cause: Tree on 11kV OH Between S5811 Pengilly Sofala to IT63182 =Riverview College to LB259. Note: Permanent Parallel exists due to decommissioned S921 See OMS 1938010 1938018 1938019 1938020 1938022 1935904 1936202 | May | 2022 | 2022Q4 | 2022 | ZN129:PA41 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2022-05-30 | Y | 348.965 | N | 4 | N | Y | 1.1101 | 39.4971 | 364414.0585
[7 empty] | 486 | 5898 | 1935887 | 2022-05-30 17:20 | 2022-05-31 04:08 | 648 | 11kV | 31104 | 48 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221089 2 fault operations Earth Fault TREE DAMAGE NEAR SUB 1899. | May | 2022 | 2022Q4 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-05-30 | Y | 648 | N | 4 | N | Y | 1.1101 | 39.4971 | 22729.8858
[7 empty] | 1652 | 20084 | 1935934 | 2022-05-30 17:33 | 2022-05-31 04:10 | 637 | 11kV | 260226 | 429 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221088 Tree on mains near sub 54570 Excluded OMS 1935934 | May | 2022 | 2022Q4 | 2022 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2022-05-30 | Y | 606.5874 | N | 4 | N | Y | 1.1101 | 39.4971 | 190165.4854
[7 empty] | 1145 | 14412 | 1936080 | 2022-05-31 02:30 | 2022-05-31 10:25 | 475 | 11kV | 2375 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 221102 A Phase DOLF : 16 Amp Tree on mains GS-44584 Excluded OMS 1936080 | May | 2022 | 2022Q4 | 2022 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Veg | 2022-05-31 | N | 475 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1735.5799
[7 empty] | 1090 | 13920 | 1936372 | 2022-05-31 08:14 | 2022-05-31 11:15 | 181 | 11kV | 905 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 221112 C Phase Live Line Dropper broken Excluded OMS 1936372 | May | 2022 | 2022Q4 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-05-31 | N | 181 | N | 27 | Y | Y | 1.1101 | 39.4971 | 661.3473
[7 empty] | 1108 | 14027 | 1936004 | 2022-05-30 17:55 | 2022-05-31 11:20 | 1045 | 11kV | 748406 | 1333 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 221120 2 fault operations B & C Phase Overcurrent 11kV OHM low between poles MW-40187 & MW-40152. Excluded OMS No. 1936004 | May | 2022 | 2022Q4 | 2022 | 233:82819 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2022-05-30 | Y | 561.4449 | N | 4 | N | Y | 1.1101 | 39.4971 | 546913.0306
[7 empty] | 1454 | 17914 | 1935818 | 2022-05-30 16:53 | 2022-05-31 11:22 | 1109 | 11kV | 65034 | 152 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221070 11kV DOWN ADJ 11Kv LINKS 42428 Excluded OMS 1935818 | May | 2022 | 2022Q4 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2022-05-30 | Y | 427.8553 | N | 4 | N | Y | 1.1101 | 39.4971 | 47524.929
[7 empty] | 1246 | 15200 | 1936373 | 2022-05-31 06:51 | 2022-05-31 11:30 | 279 | 11kV | 16265 | 102 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221106 Previous Storm, Trees Blown onto Mains between poles LQ10063 & LQ10064 removed tree, repair/sleeve mains Pole Mounted RAGCB SOP CARSON S DOP MILLS A | May | 2022 | 2022Q4 | 2022 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2022-05-31 | N | 159.4608 | N | 27 | Y | Y | 1.1101 | 39.4971 | 11885.9823
[7 empty] | 1585 | 19338 | 1935822 | 2022-05-30 16:55 | 2022-05-31 11:40 | 1125 | 11kV | 153095 | 329 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | EX Zn12630 Peats Ridge -Pnl.8 - REC44995 Kulnura tripped on: SEF DOP found iR63734 George Downes Blood 2.45 opened - In scan fail and based on trends suspect it tripped at the same time as REC44995 Trees brought down 11kV mains beyond CP45001 See 1937933 1937934 1937935 1937938 1937939 1937941 1937942 1937943 | May | 2022 | 2022Q4 | 2022 | ZN12630:PA8 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2022-05-30 | Y | 465.3343 | N | 4 | N | Y | 1.1101 | 39.4971 | 111877.3105
[7 empty] | 1155 | 14511 | 1936325 | 2022-05-30 23:38 | 2022-05-31 11:40 | 722.45 | 11kV | 47681.7 | 66 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 221104 Replace surge divertor Excluded OMS 1936327 | May | 2022 | 2022Q4 | 2022 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | OH | Not Veg | 2022-05-30 | Y | 722.45 | N | 4 | N | Y | 1.1101 | 39.4971 | 34844.38
[7 empty] | 741 | 9378 | 1936649 | 2022-05-31 12:02 | 2022-05-31 13:02 | 60 | 11kV | 36000 | 600 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex ZN 12570 Avoca, Panel 37, labelled Avoca Beach 11Kv Recloser 45180 Avoca Beach, tripped, reclosed and locked out on: Relays: OC Trip Field efis: Nil Tree branch on HV Mains, 90 Ridgeway Rd. | May | 2022 | 2022Q4 | 2022 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2022-05-31 | N | 60 | N | 27 | Y | Y | 1.1101 | 39.4971 | 26307.7382
[7 empty] | 1304 | 15870 | 1936140 | 2022-05-30 17:21 | 2022-05-31 13:08 | 1187 | 11kV | 62623 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221105 B & C Phase DOLF : 20 Amp Note this might follow outage of Fdr 74123 Excluded OMS OMS 1936140 | May | 2022 | 2022Q4 | 2022 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2022-05-30 | Y | 1181.566 | N | 4 | N | Y | 1.1101 | 39.4971 | 45763.0413
[7 empty] | 672 | 8623 | 1935836 | 2022-05-30 17:06 | 2022-05-31 13:30 | 1224 | 11kV | 70992 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind Strong | Y | PT1039 Cornwall Avenue - Roadside HDO found blown cause unknown 5P operator also made repairs to Dist #2 | May | 2022 | 2022Q4 | 2022 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Not Veg | 2022-05-30 | Y | 1224 | N | 4 | N | Y | 1.1101 | 39.4971 | 51878.8597
[7 empty] | 792 | 9910 | 1936685 | 2022-05-31 12:25 | 2022-05-31 13:36 | 71 | 11kV | 25560 | 360 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn36200 Empire Bay - Pnl.4 tripped, reclosed and locked out on: A & B phase IOC Tree on mains otuside 12 Nerang Rd. | May | 2022 | 2022Q4 | 2022 | ZN36200:PA4 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2022-05-31 | N | 71 | N | 27 | Y | Y | 1.1101 | 39.4971 | 18678.4941
[7 empty] | 863 | 10700 | 1936000 | 2022-05-30 17:54 | 2022-05-31 13:40 | 1186 | 11kV | 181039 | 212 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221069 11kV mains down between Sub 70234 & ABS 75229 Excluded OMS 1936000 | May | 2022 | 2022Q4 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2022-05-30 | Y | 853.9575 | N | 4 | N | Y | 1.1101 | 39.4971 | 132297.9615
[7 empty] | 36 | 422 | 1936027 | 2022-05-30 19:54 | 2022-05-31 13:40 | 1066.5 | 11kV | 1066.5 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | Y | LID 221108 Single phase DOLF : 10 Amp Hv mains on the ground adjacent to L/F 63833 | May | 2022 | 2022Q4 | 2022 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 1066.5 | N | 4 | N | Y | 1.1101 | 39.4971 | 779.3667
[7 empty] | 1033 | 13058 | 1936385 | 2022-05-31 00:49 | 2022-05-31 13:41 | 772 | 11kV | 201526 | 1775 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221109 mains down at pole IV17054 Excluded OMS 1936201 | May | 2022 | 2022Q4 | 2022 | 216:10722 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2022-05-31 | N | 113.5358 | N | 27 | Y | Y | 1.1101 | 39.4971 | 147269.2568
[7 empty] | 992 | 12113 | 1936755 | 2022-05-31 13:25 | 2022-05-31 13:59 | 34 | 11kV | 748 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | Electrical Storm | N | LID 221107 Previous Storm Wire off pin at SM-20024 SOP HOLLAND P DOP WEBB Z | May | 2022 | 2022Q4 | 2022 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2022-05-31 | N | 34 | N | 27 | Y | Y | 1.1101 | 39.4971 | 546.6163
[7 empty] | 433 | 5412 | 1936714 | 2022-05-31 12:46 | 2022-05-31 14:07 | 81 | 11kV | 1458 | 18 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind Strong | N | Zn4853 Strathfield South - Pnl.7 tripped on: C phase IOC UG cable fault in front line section of feeder | May | 2022 | 2022Q4 | 2022 | ZN4853:PA7 | ZN4853:PA7 | ZN04853/000007 | STRATHFIELD | UG | Not Veg | 2022-05-31 | N | 81 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1065.4634
[7 empty] | 808 | 10050 | 1935941 | 2022-05-30 17:34 | 2022-05-31 14:40 | 1266 | 11kV | 309682 | 1309 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221083 3 Phase Earth Fault Tree on mains near sub 6386 Excluded OMS 1935941 | May | 2022 | 2022Q4 | 2022 | 270:83591 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2022-05-30 | Y | 236.5791 | N | 4 | N | Y | 1.1101 | 39.4971 | 226306.4715
[7 empty] | 851 | 10551 | 1935928 | 2022-05-30 17:29 | 2022-05-31 14:40 | 1271 | 11kV | 156530 | 229 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221111 2 fault operations Overcurrent 11kV OHM down between poles GS-71302 & GS-71301. Excluded OMS OMS No. 1935928, 1936484 | May | 2022 | 2022Q4 | 2022 | 522:83131 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 683.5371 | N | 4 | N | Y | 1.1101 | 39.4971 | 114387.5071
[7 empty] | 114 | 1439 | 1935851 | 2022-05-30 17:05 | 2022-05-31 14:55 | 1310 | 11kV | 15180 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221100 2 fault operations 3 phase Earth Fault Tree on mains HY-50360 Excluded OMS 1935856 | May | 2022 | 2022Q4 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2022-05-30 | Y | 506 | N | 4 | N | Y | 1.1101 | 39.4971 | 11093.0963
[7 empty] | 1456 | 17940 | 1936626 | 2022-05-31 11:56 | 2022-05-31 15:50 | 234 | 11kV | 2106 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 221124 wire off pin repaired Pole AH-72306 Had to re tie pin insulator at pole AH-72306. No protection operated isolated to carry our repairs safely. Thunderstorm SOP GARLAND K DOP HOLLAND P | May | 2022 | 2022Q4 | 2022 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2022-05-31 | N | 234 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1539.0027
[7 empty] | 365 | 4918 | 1936791 | 2022-05-31 13:51 | 2022-05-31 16:00 | 129 | 11kV | 237287 | 1923 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | Zn80 Chatswood - Pnl.31 tripped, reclosed and locked out on: A & B phase OC Abnormal: LB1817 Closed with S4258 Sw/A Open Large tree on OH corner Avian/Mowbray See 1938086 1938087 | May | 2022 | 2022Q4 | 2022 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | WILLOUGHBY | OH | Veg | 2022-05-31 | N | 123.3942 | N | 27 | Y | Y | 1.1101 | 39.4971 | 173402.3408
[7 empty] | 615 | 7924 | 1935804 | 2022-05-30 16:39 | 2022-05-31 16:00 | 1401 | 11kV | 25290 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221119 A & B Phase DOLF : 16 Amp Excluded OMS 1935804 | May | 2022 | 2022Q4 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2022-05-30 | Y | 1331.0526 | N | 4 | N | Y | 1.1101 | 39.4971 | 18481.1861
[7 empty] | 718 | 9224 | 1936099 | 2022-05-30 18:37 | 2022-05-31 16:00 | 1283 | 11kV | 3849 | 3 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | Y | LID 221116 A & B Phase DOLF : 10 Amp Tree cleared from 11kV OHM s spans adjacent pole HR-33311. Excluded OMS No. 1936099 | May | 2022 | 2022Q4 | 2022 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2022-05-30 | Y | 1283 | N | 4 | N | Y | 1.1101 | 39.4971 | 2812.7357
[7 empty] | 812 | 10075 | 1935832 | 2022-05-30 17:03 | 2022-05-31 16:05 | 1382 | 11kV | 184517.6 | 184 | HV | Vegetation Blow/Fall In | Vegetation | Pole | Unplanned | Rain Wind Storm | Y | Fallen tree pulled down 3 bays of LV mains and snapped pole BE84371 Replaced pole and re ecrected LV mains and replaced link box Replaced LV bare mains with 4 x 150mm ABC between poles BE84371 and BE84372 (1 span ) eliminating the need to cross bond LV mains Further works required - LV SL UGOH cable was cut off 2 meters above ground at pole BE84371 feeding lights into community centre needs repair cable. referred to wdpcentral Wo 1700261975 not 1300434878 has been created. | May | 2022 | 2022Q4 | 2022 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2022-05-30 | Y | 1002.813 | N | 4 | N | Y | 1.1101 | 39.4971 | 134840.0197
[7 empty] | 965 | 11744 | 1936215 | 2022-05-30 19:54 | 2022-05-31 16:12 | 1218 | 11kV | 169785 | 799 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn14143 Somersby - Pnl.17 tripped, reclosed and locked out on: A & B phase OC Trees down, HV into LV at 11kV USL41695 See 1938014 1938015 | May | 2022 | 2022Q4 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2022-05-30 | Y | 212.4969 | N | 4 | N | Y | 1.1101 | 39.4971 | 124073.8702
[7 empty] | 1368 | 16745 | 1936783 | 2022-05-31 13:45 | 2022-05-31 16:42 | 177 | 11kV | 250386 | 1610 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | Zn2635 Epping - Pnl.46 tripped, reclosed & locked out on: A & B phase IOC Cause not ascertained. Likely Wind See 1938073 1938075 | May | 2022 | 2022Q4 | 2022 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | OH | Veg | 2022-05-31 | N | 155.5193 | N | 27 | Y | Y | 1.1101 | 39.4971 | 182974.7037
[7 empty] | 912 | 11223 | 1936008 | 2022-05-31 09:38 | 2022-05-31 17:05 | 447 | 11kV | 27331 | 91 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 221113 Bph 11kV tapping blown at pole IS-90233. Broken 11kV crossarm at pole KS-40082. Excluded OMS No. 1936008 | May | 2022 | 2022Q4 | 2022 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2022-05-31 | N | 300.3407 | N | 27 | Y | Y | 1.1101 | 39.4971 | 19972.6887
[7 empty] | 201 | 2579 | 1936472 | 2022-05-31 08:51 | 2022-05-31 17:25 | 513.9 | 11kV | 3083.4 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 221128 Phase A, Line DOLF SOP HOLLAND P DOP AUSTIN G | May | 2022 | 2022Q4 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2022-05-31 | N | 513.9 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2253.2578
[7 empty] | 357 | 4849 | 1936593 | 2022-05-31 11:15 | 2022-05-31 17:27 | 372 | 11kV | 13392 | 36 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 221126 Thunderstorm No protection operation, Isolated to replace pole & re tie 11kV mains at pole AF-40109 SOP HOLLAND P DOP HUSSEY N | May | 2022 | 2022Q4 | 2022 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2022-05-31 | N | 372 | N | 27 | Y | Y | 1.1101 | 39.4971 | 9786.4786
[7 empty] | 22 | 248 | 1936282 | 2022-05-30 18:00 | 2022-05-31 17:42 | 1422 | 11kV | 83898 | 59 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 221130 11kV OHM down between poles LQ-80053 & LQ-80054. Excluded OMS No. 1936745 | May | 2022 | 2022Q4 | 2022 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2022-05-30 | Y | 1422 | N | 4 | N | Y | 1.1101 | 39.4971 | 61310.1838
[7 empty] | 1537 | 18867 | 1936918 | 2022-05-31 14:40 | 2022-05-31 19:05 | 265 | 11kV | 80350 | 430 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | Charmhaven Pnl.19 - Interrupted from S14436 Sw/B Wallarah Beryl Pole fire at LB41253 | May | 2022 | 2022Q4 | 2022 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2022-05-31 | N | 186.8605 | N | 27 | Y | Y | 1.1101 | 39.4971 | 58717.4101
[7 empty] | 911 | 11220 | 1936676 | 2022-05-31 12:21 | 2022-05-31 19:05 | 404 | 11kV | 43063 | 222 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind Strong | N | REC62705 Jiliby Durren tripped, reclosed and locked out on: OC Abnormal: REC45016 Dickson - Bypass closed Trees on 11kV mains between USL43590 and USL46395 See 1938048 1938050 1938051 | May | 2022 | 2022Q4 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2022-05-31 | N | 193.9775 | N | 27 | Y | Y | 1.1101 | 39.4971 | 31469.1703
[7 empty] | 344 | 4770 | 1936365 | 2022-05-31 06:23 | 2022-05-31 19:22 | 779.25 | 11kV | 3896.25 | 5 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 221135 Thunderstorm 20 Amp Phases A & B. Substation DOLF Bird attack. SOP CARSON S DOP LEWIS C | May | 2022 | 2022Q4 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2022-05-31 | N | 779.25 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2847.2646
[7 empty] | 945 | 11461 | 1935819 | 2022-05-30 16:56 | 2022-05-31 20:10 | 1634 | 11kV | 453482 | 721 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | Y | Zn3154 St Ives - Pnl.12 tripped, reclosed, tripped & locked out on Earth Fault & C phase IOC Large tree brought down HV and LV mains PT346 Milton Rd - Dist #1 - Also affected See 1937918 1937919 1937926 1937928 | May | 2022 | 2022Q4 | 2022 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2022-05-30 | Y | 628.9626 | N | 4 | N | Y | 1.1101 | 39.4971 | 331391.2701
[7 empty] | 785 | 9873 | 1935979 | 2022-05-30 17:47 | 2022-05-31 20:10 | 1583 | 11kV | 347024 | 1576 | HV | Wind Blown Debris | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 221140 House roof material on 11kV near sub 65625. HV INTO LV AT SUB 65625. Excluded OMS 1935979 | May | 2022 | 2022Q4 | 2022 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2022-05-30 | Y | 220.1929 | N | 4 | N | Y | 1.1101 | 39.4971 | 253594.9037
[7 empty] | 1068 | 13740 | 1936425 | 2022-05-30 18:23 | 2022-05-31 20:30 | 1567 | 11kV | 20371 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221155 CCT on the ground GT-41403 Excluded OMS 1936066/1936174 | May | 2022 | 2022Q4 | 2022 | 522:83126 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 1567 | N | 4 | N | Y | 1.1101 | 39.4971 | 14886.526
[7 empty] | 1469 | 18157 | 1937182 | 2022-05-31 20:25 | 2022-05-31 20:38 | 13 | 11kV | 21320 | 1640 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | Zn9252 Jannali - Pnl.27 tripped on: B & C phase OC Abnormal: LB35517 closed with LB35177, AB35626 Closed with S9938 Sw/A Open Tree contacting bare 11kV mains causing arcing. Due to abnormals and defectives feeder able to be switched. Dop tried to de-erngise from LB35856 for safety but AB flashed over causing feeder trip | May | 2022 | 2022Q4 | 2022 | ZN9252:PA27 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Veg | 2022-05-31 | N | 13 | N | 27 | Y | Y | 1.1101 | 39.4971 | 15580.0272
[7 empty] | 1169 | 14655 | 1936912 | 2022-05-31 15:19 | 2022-05-31 21:48 | 389 | 11kV | 1556 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 221146 sevices on ground . Crews required. LVF isolated service wires to two neighbouring properties from pole on street to metal poles at 27 fletcher and 19 fletcher are down within reach SOP De VRIES M DOP SKINNER A | May | 2022 | 2022Q4 | 2022 | 524:33574 | 524:33574 | ZN00524/033574 | CESSNOCK | OH | Not Veg | 2022-05-31 | N | 389 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1137.0789
[7 empty] | 642 | 8318 | 1936017 | 2022-05-30 18:02 | 2022-05-31 23:25 | 1763 | 11kV | 7052 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | Y | LID 221148 Transformer replaced leaking oil Excluded OMS 1936017 | May | 2022 | 2022Q4 | 2022 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 1763 | N | 4 | N | Y | 1.1101 | 39.4971 | 5153.3936
[7 empty] | 512 | 6134 | 1937009 | 2022-05-31 15:41 | 2022-05-31 23:35 | 474 | 11kV | 1422 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Previous Storm | N | LID 221147 broken live line Clamp Sub 50742 replaced lead Previous Storm DOP De VRIES M SOP MANSINI R | May | 2022 | 2022Q4 | 2022 | 508:82576 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2022-05-31 | N | 474 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1039.1557
[7 empty] | 1601 | 19505 | 1936194 | 2022-05-31 14:06 | 2022-06-01 03:00 | 773.6667 | 11kV | 1547.3333 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221152 Replaced damaged transformer Tree brought down hv main, snapped cross arm and damaged substation 1899. replaced hardware. TX needs replacing tree needs to be removed from road SOP WATSON J DOP B STONE | May | 2022 | 2022Q4 | 2022 | 522:83132 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2022-05-31 | N | 773.6667 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1130.7456
[7 empty] | 1424 | 17525 | 1937170 | 2022-05-31 19:28 | 2022-06-01 03:50 | 502 | 11kV | 27618 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | At ZN15013 Terrey Hill Panel 6 Recloser CP20828 Cooyong Rd was remotely opened Cause: Interrupted due to report of tree on HV CCT at pole MO1093 adjacent to PT117116 Killawarra Weemala. Isolated form LB25242 to LKB48729 tee PT17116 See P<S 1938044 1938045 1938046 197317070 1937213 | May | 2022 | 2022Q4 | 2022 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2022-05-31 | N | 244.4071 | N | 27 | Y | Y | 1.1101 | 39.4971 | 20182.4198
[7 empty] | 677 | 8666 | 1936956 | 2022-05-31 14:47 | 2022-06-01 05:02 | 855 | 11kV | 111800 | 180 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 221150 Gales (40-70k) Phase B & C Overcurrent Refer to oms 1937058 damaged OHM at Iona Lane, Tree on DW on corner of woodville ln and Paterson Road - not within reachable height SOP WATSON J DOP WILLIAMS L | May | 2022 | 2022Q4 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2022-05-31 | N | 621.1111 | N | 27 | Y | Y | 1.1101 | 39.4971 | 81700.1425
[7 empty] | 891 | 10972 | 1936889 | 2022-05-31 14:10 | 2022-06-01 08:50 | 1120 | 11kV | 150101 | 689 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 221157 Tree down on mains pole LS-20374 229:34995 Tripped and locked out Excluded OMS 1936889 | May | 2022 | 2022Q4 | 2022 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2022-05-31 | N | 217.8534 | N | 27 | Y | Y | 1.1101 | 39.4971 | 109689.3836
[7 empty] | 927 | 11292 | 1937278 | 2022-06-01 08:37 | 2022-06-01 09:10 | 33 | 11kV | 3036 | 92 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221159 Tree on mains pole OR90124 Section isolated by DOP to remove Excluded OMS 1937278 | June | 2022 | 2022Q4 | 2022 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2022-06-01 | N | 33 | N | 4 | N | N | 1.1101 | 39.4971 | 2218.6193
[7 empty] | 1659 | 20161 | 1935901 | 2022-05-30 17:26 | 2022-06-01 10:50 | 2484 | 11kV | 7064 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221158 Single phase DOLF : 16 Amp Excluded OMS 1935901 | May | 2022 | 2022Q4 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2022-05-30 | Y | 470.9333 | N | 4 | N | Y | 1.1101 | 39.4971 | 5162.1628
[7 empty] | 115 | 1441 | 1936933 | 2022-06-01 07:20 | 2022-06-01 12:50 | 330.1333 | 11kV | 1320.5333 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind Strong | N | LID 221162 Broken tie wire pole HR95402 | June | 2022 | 2022Q4 | 2022 | 532:83307 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2022-06-01 | N | 330.1333 | N | 4 | N | N | 1.1101 | 39.4971 | 965.0068
[7 empty] | 768 | 9591 | 1937223 | 2022-06-01 10:55 | 2022-06-01 13:38 | 163 | 11kV | 142136 | 872 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | Recloser CP35756 Tripped on Overcurrent Cause: Tree branch contact Eric St Bundeena see OMS 194151 1937223 | June | 2022 | 2022Q4 | 2022 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2022-06-01 | N | 163 | N | 4 | N | N | 1.1101 | 39.4971 | 103868.7965
[7 empty] | 1017 | 12843 | 1936206 | 2022-05-30 17:25 | 2022-06-01 13:50 | 2665 | 11kV | 184870 | 133 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 221168 Mains on ground FS21901 to FS21903 Sub on ground 50972 Excluded OMS 1935905 | May | 2022 | 2022Q4 | 2022 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 1390 | N | 4 | N | Y | 1.1101 | 39.4971 | 135097.5433
[7 empty] | 1218 | 15035 | 1936782 | 2022-05-31 13:46 | 2022-06-01 13:50 | 1444 | 11kV | 4332 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 221170 Gales (40-70k) Phase A Replace LV service- Large tree brought it down Replace Underslung Fuse assembly, damaged from tree. Refer to OMS 1936782 & 1937094 SOP FITZPATRICK S DOP BARTUSH S | May | 2022 | 2022Q4 | 2022 | 526:34633 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2022-05-31 | N | 1444 | N | 27 | Y | Y | 1.1101 | 39.4971 | 3165.6978
[7 empty] | 832 | 10242 | 1936806 | 2022-05-31 14:18 | 2022-06-01 14:50 | 1472 | 11kV | 48576 | 33 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | LID 221167 Gales (40-70k) 16Amp, Phases A & B.Line DOLF Tree brought down OHMS at sub 33090 SOP FITZPATRICK S DOP WILKINSON P | May | 2022 | 2022Q4 | 2022 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2022-05-31 | N | 1472 | N | 27 | Y | Y | 1.1101 | 39.4971 | 35497.9081
[7 empty] | 246 | 3013 | 1935925 | 2022-05-30 17:30 | 2022-06-01 15:00 | 2730 | 11kV | 125491 | 235 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | Y | LID 221169 Mains down at sub 49419 Excluded OMS 1935925 | May | 2022 | 2022Q4 | 2022 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2022-05-30 | Y | 534.0043 | N | 4 | N | Y | 1.1101 | 39.4971 | 91705.1214
[7 empty] | 1088 | 13905 | 1937014 | 2022-05-31 18:35 | 2022-06-01 15:00 | 1225.2667 | 11kV | 20829.5333 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221149 Overcurrent J Byfield assigned mains down beyond sw 74821 section isolated for repair 1/6/22. MdV Excluded OMS 1937014 | May | 2022 | 2022Q4 | 2022 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2022-05-31 | N | 1225.2667 | N | 27 | Y | Y | 1.1101 | 39.4971 | 15221.6086
[7 empty] | 929 | 11294 | 1935896 | 2022-05-30 17:22 | 2022-06-01 16:10 | 2808 | 11kV | 187862 | 166 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 221171 2 fault operations 3 phase Instantaneous Overcurrent Mains down Excluded OMS 1935896 | May | 2022 | 2022Q4 | 2022 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2022-05-30 | Y | 1131.6988 | N | 4 | N | Y | 1.1101 | 39.4971 | 137284.0086
[7 empty] | 883 | 10882 | 1937648 | 2022-06-01 16:43 | 2022-06-01 17:05 | 22 | 11kV | 110 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Wind Storm | N | LID 221166 Faulty Pin Insulatorat pole DJ-10005 Excluded OMS 1937648 | June | 2022 | 2022Q4 | 2022 | 811:74234 | 811:74234 | ZN00811/074234 | MUSWELLBROOK | OH | Not Veg | 2022-06-01 | N | 22 | N | 4 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 953 | 11548 | 1937837 | 2022-06-02 03:57 | 2022-06-02 04:59 | 62 | 11kV | 92380 | 1490 | HV | Animal Possum | Animal | UGOH | Unplanned | Cold <10C | N | At ZN9118 Cronilla Panel 22 Feeder tripped Signals: 11kV Trup, Tx1 Group Earth Relays: Earth Leakge, Timed EFI Cause: Possum found @ UGOH pole CR00641 | June | 2022 | 2022Q4 | 2022 | ZN9118:PA22 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | OH | Not Veg | 2022-06-02 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 67508.5793
[7 empty] | 1094 | 13955 | 1938107 | 2022-06-02 11:37 | 2022-06-02 13:40 | 123 | 11kV | 369 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 221186 A Phase DOLF : 10 Amp Excluded OMS 1938107 | June | 2022 | 2022Q4 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2022-06-02 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 269.6543
[7 empty] | 1106 | 13999 | 1937831 | 2022-06-02 00:21 | 2022-06-02 14:50 | 869 | 11kV | 6083 | 7 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 221179 section isolated to remove tree pole GW-70317 & replace pole GW-77005 Excluded OMS 1937744 | June | 2022 | 2022Q4 | 2022 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2022-06-02 | N | 869 | N | 4 | N | N | 1.1101 | 39.4971 | 4445.277
[7 empty] | 101 | 1302 | 1938100 | 2022-06-02 13:50 | 2022-06-02 17:10 | 200 | 11kV | 2000 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Previous Storm | N | 11kV interrupted from LB43241 due to tree leaning on CCT 11kV cross arm was also replaced | June | 2022 | 2022Q4 | 2022 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2022-06-02 | N | 200 | N | 4 | N | N | 1.1101 | 39.4971 | 1461.541
[7 empty] | 67 | 833 | 1938377 | 2022-06-03 07:35 | 2022-06-03 10:00 | 145 | 11kV | 11320 | 194 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Cold <10C | N | Zn12650 West Gosford - Pnl.8 tripped on OC Faulty Sw/B end box @ S14169 Jusfrute Galstone S14169 interrupted to isolate end box See 1939233 1939234 1938374 | June | 2022 | 2022Q4 | 2022 | ZN12650:PA8 | ZN12650:PA8 | ZN12650/000008 | CENTRAL COAST | UG | Not Veg | 2022-06-03 | N | 58.3505 | N | 5 | N | N | 1.1101 | 39.4971 | 8272.3221
[7 empty] | 1042 | 13304 | 1938387 | 2022-06-03 13:10 | 2022-06-03 13:45 | 35 | 11kV | 595 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 221191 Broken LLC dropper lead & siezed LLC & Broken LLC Loop @ sub 48884 Excluded oms 1938387 | June | 2022 | 2022Q4 | 2022 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2022-06-03 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 434.8085
[7 empty] | 871 | 10814 | 1938501 | 2022-06-03 16:45 | 2022-06-03 18:15 | 90 | 11kV | 2760 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Cold <10C | N | Ex Pnl.2 Lisarow - 11kV tee PT12294 & PT11099 interupted to remove bamboo from the OH mains See 1938501 1938502 | June | 2022 | 2022Q4 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2022-06-03 | N | 89.0323 | N | 5 | N | N | 1.1101 | 39.4971 | 2016.9266
[7 empty] | 37 | 423 | 1938511 | 2022-06-03 20:30 | 2022-06-03 23:20 | 170 | 11kV | 5780 | 34 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Cold <10C | N | 11kV feeder interrupted between LB2603 and LB2604 tee PT1616 and PT2214 to remove tree from OH mains (Pole AR-27460) See 1938560 1938561 | June | 2022 | 2022Q4 | 2022 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2022-06-03 | N | 170 | N | 5 | N | N | 1.1101 | 39.4971 | 4223.8535
[7 empty] | 993 | 12165 | 1938576 | 2022-06-04 00:50 | 2022-06-04 02:00 | 70 | 11kV | 52724 | 946 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Zn12690 Berkeley Vale - Pnl.24 tripped, reclosed and locked out on: B phase OC UGOH failure on pole OU436 in Cambridge Street Note: Multiple supervisory control switches in scan fail delaying restoration See 1939249 1939250 | June | 2022 | 2022Q4 | 2022 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | Unknown | Unknown | 2022-06-04 | N | 55.7336 | N | 3 | N | N | 1.1101 | 39.4971 | 38529.1441
[7 empty] | 1193 | 14787 | 1938564 | 2022-06-03 21:20 | 2022-06-04 03:45 | 385 | 11kV | 57364 | 266 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 221192 2 fault operations Instantaneous Overcurrent Sw 82579 = IOC, Fault detector B operated 11kV OHM on xarm pole IQ-41530 Excluded OMS 1938564 1938578 | June | 2022 | 2022Q4 | 2022 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2022-06-03 | N | 215.6541 | N | 5 | N | N | 1.1101 | 39.4971 | 41919.9192
[7 empty] | 671 | 8618 | 1938584 | 2022-06-04 05:28 | 2022-06-04 15:40 | 612 | 11kV | 80964 | 205 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | REC349 Berowra Waters tripped on OC Tree on OH mains near PT673 See 1940336 1940338 | June | 2022 | 2022Q4 | 2022 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2022-06-04 | N | 394.9463 | N | 3 | N | N | 1.1101 | 39.4971 | 59166.1032
[7 empty] | 1291 | 15704 | 1938707 | 2022-06-04 16:14 | 2022-06-04 18:12 | 118 | 11kV | 276356 | 2342 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn12570 Avoca - Pnl.21 tripped, reclosed & locked out on: B & C phase OC Burnt stick across HV mains OPP 152 KARALTA - CUSTOMER SAW SMALL TREE BRANCH ACROSS D/WIRES - WIRES WERE ARCING & SPARKING BEFORE POWER WENT Out | June | 2022 | 2022Q4 | 2022 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Veg | 2022-06-04 | N | 118 | N | 3 | N | N | 1.1101 | 39.4971 | 201952.8137
[7 empty] | 520 | 6176 | 1938724 | 2022-06-05 11:27 | 2022-06-05 12:20 | 53 | 11kV | 7314 | 138 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | No LID report entered Isolated to repair Hot Joint Pole KT-40685 | June | 2022 | 2022Q4 | 2022 | 228:85413 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2022-06-05 | N | 53 | N | 6 | N | N | 1.1101 | 39.4971 | 5344.8555
[7 empty] | 1500 | 18465 | 1938754 | 2022-06-05 08:16 | 2022-06-05 13:25 | 309 | 11kV | 28692 | 261 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Cold <10C | N | Zn1287 Revesby - Pnl.18 tripped on C phase IOC and EF Tree contact 11kV mains. On call LW had to cut away tree from OH section between CP2319, S7862 to S36045 See 1940286 1940288 1940289 1940290 | June | 2022 | 2022Q4 | 2022 | ZN1287:PA18 | ZN1287:PA18 | ZN01287/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2022-06-05 | N | 109.931 | N | 6 | N | N | 1.1101 | 39.4971 | 20967.2673
[7 empty] | 670 | 8617 | 1938800 | 2022-06-05 12:38 | 2022-06-05 13:50 | 72 | 11kV | 5400 | 75 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind Strong | N | REC44797 Bouddi tripped on OC Weather related - cause not found | June | 2022 | 2022Q4 | 2022 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2022-06-05 | N | 72 | N | 6 | N | N | 1.1101 | 39.4971 | 3946.1607
[7 empty] | 1532 | 18832 | 1938798 | 2022-06-05 12:29 | 2022-06-05 16:58 | 269 | 11kV | 14795 | 55 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 221195 broken x-arm & fire @ pole 4J-60153 | June | 2022 | 2022Q4 | 2022 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2022-06-05 | N | 269 | N | 6 | N | N | 1.1101 | 39.4971 | 10811.7496
[7 empty] | 1418 | 17441 | 1938842 | 2022-06-05 17:01 | 2022-06-05 18:28 | 87 | 11kV | 131793 | 1615 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At Zn 10999 Kogarah 11kV Panel 11 Gladstone Princes tripped on Relays: E/L, Lockout and EFI Signals: 11kV Trip Cause: 11kV fault from S63035 to S10194 See OMS 1940170 1940171 1938842 | June | 2022 | 2022Q4 | 2022 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | UG | Not Veg | 2022-06-05 | N | 81.6056 | N | 6 | N | N | 1.1101 | 39.4971 | 96310.4372
[7 empty] | 1228 | 15071 | 1938888 | 2022-06-06 03:55 | 2022-06-06 06:21 | 146 | 11kV | 217861 | 2964 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12620 Noraville Panel 7 tripped on (Panel 7 and Panel 10 Impacted) A phase OC Field Efi's NIL Abnormal Switching: SW/H Closed @ Zn12620 Panel 10 Open (B-C Bus dection defective and racked out) Cause: Possum on OH at HV USL41644 - Cleared by DOP CP42638 Centre Phase Line and Load bonds blown due to through fault See OMS 1940297 1940301 1940302 1940303 1940304 1938888 1938890 | June | 2022 | 2022Q4 | 2022 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2022-06-06 | N | 73.5024 | N | 18 | N | N | 1.1101 | 39.4971 | 159206.393
[7 empty] | 1615 | 19634 | 1938895 | 2022-06-06 05:23 | 2022-06-06 07:38 | 135 | 11kV | 61830 | 458 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At S1193 Lindfield Panel 10 Tripped Relays: A and B phase OC Trip, EFI, Trip Signal Field EFI's NIl Cause: OH sections of feeder patrolled, No defect found See OMS 1940333 1938898 | June | 2022 | 2022Q4 | 2022 | ZN1193:PA10 | ZN1193:PA10 | ZN01193/000010 | KU-RING-GAI | OH | Veg | 2022-06-06 | N | 135 | N | 18 | N | N | 1.1101 | 39.4971 | 45183.5403
[7 empty] | 165 | 2127 | 1938891 | 2022-06-06 05:10 | 2022-06-06 07:58 | 168 | 11kV | 227136 | 1352 | HV | Animal Possum | Animal | UGOH | Unplanned | Wind Strong | N | Zn10995 Riverwood - Pnl.12 tripped , reclosed & locked out on: A & C phase IOC and OC Possum on 11kV UGOH below S.10897 | June | 2022 | 2022Q4 | 2022 | ZN10995:PA12 | ZN10995:PA12 | ZN10995/000012 | GEORGES RIVER | OH | Not Veg | 2022-06-06 | N | 168 | N | 18 | N | N | 1.1101 | 39.4971 | 165984.2894
[7 empty] | 361 | 4907 | 1938920 | 2022-06-06 06:58 | 2022-06-06 08:55 | 117 | 11kV | 56979 | 487 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | Ex Zn12620 Noraville From LV64867 to PT12766 to USL41875 - 1 pole down from LB64867(Bond Off) See OMS 1940309 1938920 Abnormal switghing CP42638 Open DMA, CP40196 Closed | June | 2022 | 2022Q4 | 2022 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2022-06-06 | N | 117 | N | 18 | N | N | 1.1101 | 39.4971 | 41638.5726
[7 empty] | 293 | 3724 | 1938936 | 2022-06-06 07:21 | 2022-06-06 09:16 | 115 | 11kV | 140875 | 1225 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | Zn15012 Killarney - Pnl.4 tripped on: OC 11kV Bond burnt off pole FF84695 and touching Dist #4 of S16537 Forestville Mall (see related outage 1938942) | June | 2022 | 2022Q4 | 2022 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Not Veg | 2022-06-06 | N | 115 | N | 18 | N | N | 1.1101 | 39.4971 | 102947.2949
[7 empty] | 263 | 3379 | 1938965 | 2022-06-06 08:15 | 2022-06-06 09:25 | 70 | 11kV | 490 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 221198 B Phase DOLF : 31 Amp Excluded OMS 1938965 | June | 2022 | 2022Q4 | 2022 | 814:82289 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2022-06-06 | N | 70 | N | 18 | N | N | 1.1101 | 39.4971 | 358.0775
[7 empty] | 219 | 2714 | 1938998 | 2022-06-06 09:21 | 2022-06-06 10:29 | 68 | 11kV | 126515 | 1867 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Previous Storm | N | Zn187 Crows Nest - Pnl.30 tripped on A & B phase OC 11kV Sw/D Endbox exploded at S6345 Ernest Park See 1940329 1940330 | June | 2022 | 2022Q4 | 2022 | ZN187:PA30 | ZN187:PA30 | ZN00187/000030 | WILLOUGHBY | UG | Not Veg | 2022-06-06 | N | 67.7638 | N | 18 | N | N | 1.1101 | 39.4971 | 92453.4304
[7 empty] | 989 | 12098 | 1938893 | 2022-06-06 05:20 | 2022-06-06 11:00 | 340 | 11kV | 236142 | 1391 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At Zn1673 Turramurra Panel 18 tripped, reclosed tripped and locked out Relays:B and C phase Overcurrent 11kV OH/Mains twisted by tree branch near LB 238. Mains separated and feeder restored Abnormal Switching: section of feeder from CP3019 to CP373 defective LB2209 closed PT78 Monteith Kissing Point in LV parakllel See OMS 1940340 1940341 1940342 1940343 1938916 1938893 1938897 1938918 1938992 | June | 2022 | 2022Q4 | 2022 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2022-06-06 | N | 169.7642 | N | 18 | N | N | 1.1101 | 39.4971 | 172565.6086
[7 empty] | 1183 | 14763 | 1939106 | 2022-06-06 11:30 | 2022-06-06 12:13 | 43 | 11kV | 53793 | 1251 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At ZN12610 Long Jetty 11kV panel 22 tripped, reclosed, tripped and locked out on Relays: B and C phase IOC with lockout relay Cause: EC Zn12610 long yetty Panel 22 Tree branhc on OH mains at AB40268 DOp cleared branch from mains See OMS 139106 139139 | June | 2022 | 2022Q4 | 2022 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Veg | 2022-06-06 | N | 43 | N | 18 | N | N | 1.1101 | 39.4971 | 39310.3378
[7 empty] | 632 | 8189 | 1938914 | 2022-06-06 06:25 | 2022-06-06 12:31 | 366 | 11kV | 151051 | 1092 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 221202 2 fault operations Overcurrent tree on OHM at pole HU-57012 Excluded oms 1938914 | June | 2022 | 2022Q4 | 2022 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2022-06-06 | N | 138.3251 | N | 18 | N | N | 1.1101 | 39.4971 | 110383.6155
[7 empty] | 71 | 885 | 1939148 | 2022-06-06 11:54 | 2022-06-06 14:36 | 162 | 11kV | 164847 | 1174 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 221203 2 fault operation Overcurrent B & C Phase Overcurrent Excluded OMS 1939143 | June | 2022 | 2022Q4 | 2022 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2022-06-06 | N | 140.4148 | N | 18 | N | N | 1.1101 | 39.4971 | 120465.3254
[7 empty] | 1085 | 13895 | 1938883 | 2022-06-05 23:01 | 2022-06-06 15:00 | 959 | 11kV | 162071 | 169 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | 11kV CP45012 Tripped, reclosed, tripped and locked out Relays: DOp reports, earth fault and B phase OC Cause: Tree branch brought down OH near PT13615 | June | 2022 | 2022Q4 | 2022 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2022-06-05 | N | 959 | N | 6 | N | N | 1.1101 | 39.4971 | 118436.7065
[7 empty] | 582 | 7349 | 1939170 | 2022-06-06 12:31 | 2022-06-06 16:15 | 224 | 11kV | 29022 | 1092 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind Strong | N | LID 221206 2 fault operation B Phase Earth Fault tree down on OHM at pole HU-90061 B phase E/F, E/F High set Excluded OMS 1939170 | June | 2022 | 2022Q4 | 2022 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2022-06-06 | N | 26.5769 | N | 18 | N | N | 1.1101 | 39.4971 | 21208.4216
[7 empty] | 790 | 9900 | 1939348 | 2022-06-06 17:11 | 2022-06-06 17:45 | 34 | 11kV | 11740 | 2270 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 221211 deenergise feeder to safely open burnt up ABS 5883 Excluded OMS 1939348 | June | 2022 | 2022Q4 | 2022 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2022-06-06 | N | 5.1718 | N | 18 | N | N | 1.1101 | 39.4971 | 8579.2457
[7 empty] | 154 | 1849 | 1939239 | 2022-06-06 14:04 | 2022-06-06 17:50 | 226 | 11kV | 226 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221205 LLC lead burnt. Replace lead. Excluded OMS 1939271 | June | 2022 | 2022Q4 | 2022 | 512:83741 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2022-06-06 | N | 226 | N | 18 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 406 | 5193 | 1939111 | 2022-06-06 11:33 | 2022-06-06 19:25 | 472 | 11kV | 22368 | 392 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn14891 Wyong Panel 20 11kV Intellirupter CP50560 Hue Hue Sandra tripped, reclosed and locked out on Relays: Overcurrent, lockout Cause: Mains down between CP43633 to link CP44176 tee PT13928 Cause: LB44793 Closed yp restore remaining section of feeder See OMS 1940317 1940318 1939111 1939201 | June | 2022 | 2022Q4 | 2022 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2022-06-06 | N | 57.0612 | N | 18 | N | N | 1.1101 | 39.4971 | 16345.8747
[7 empty] | 288 | 3656 | 1939264 | 2022-06-06 14:43 | 2022-06-06 19:55 | 312.1667 | 11kV | 4994.6667 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221213 Isolated section to repair Live Line Lead at PT 20531. | June | 2022 | 2022Q4 | 2022 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2022-06-06 | N | 312.1667 | N | 18 | N | N | 1.1101 | 39.4971 | 3649.9551
[7 empty] | 1522 | 18678 | 1939387 | 2022-06-06 23:20 | 2022-06-07 01:30 | 130 | 11kV | 20020 | 154 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | PT2364 Wattle Cath - Interrupted to cut away broken streetlight wire and remove cross arm | June | 2022 | 2022Q4 | 2022 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-06-06 | N | 130 | N | 18 | N | N | 1.1101 | 39.4971 | 14630.0255
[7 empty] | 578 | 7282 | 1939421 | 2022-06-07 04:03 | 2022-06-07 05:27 | 84 | 11kV | 183456 | 2184 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Zn10995 Riverwood Pnl.7 tripped on: A phase OC and IOC Possum on ground near UGOH opposite Broadarrow Rd, Opp Yardley Ave. The UGOH between PT77771 an S10161 (Pole PE-398). Pnl.7 VCB will not latch closed | June | 2022 | 2022Q4 | 2022 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2022-06-07 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 134064.2338
[7 empty] | 1156 | 14524 | 1939422 | 2022-06-07 06:43 | 2022-06-07 07:58 | 75 | 11kV | 34009 | 513 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Cold <10C | N | AT ZN12620 Noraville Panel 2 tripped on Relays: A phase timed, C phase IOC Cause: vehicle hit poile TO2849 See OMS 1940210 1940212 1939422 1939427 1939442 | June | 2022 | 2022Q4 | 2022 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2022-06-07 | N | 66.2943 | N | 3 | N | N | 1.1101 | 39.4971 | 24852.7741
[7 empty] | 1256 | 15286 | 1939380 | 2022-06-06 21:56 | 2022-06-07 09:32 | 696 | 11kV | 1392 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 221216 Live Line leade repair. Excluded OMS 1939380 | June | 2022 | 2022Q4 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2022-06-06 | N | 696 | N | 18 | N | N | 1.1101 | 39.4971 | 1017.2325
[7 empty] | 789 | 9892 | 1939449 | 2022-06-07 08:16 | 2022-06-07 12:05 | 229 | 11kV | 1145 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221218 DOLF : 16 Amp Excluded OMS 1939449 | June | 2022 | 2022Q4 | 2022 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2022-06-07 | N | 229 | N | 3 | N | N | 1.1101 | 39.4971 | 836.7322
[7 empty] | 876 | 10829 | 1939757 | 2022-06-08 02:11 | 2022-06-08 05:00 | 169 | 11kV | 90790 | 738 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At Zn1673 Turramurra 11kV Panel 2 tripped on Relays: EFI, A phase IOC, IOC trip, Earth Fault Signals: TC2 Group Earth, 11kV Trip Abnormal Switching: SE/C isolated at CP373 Bpgan Camp[bell - CP2209 Closed Cause: Suspect UG cable fault between S4701 Roland Campbell to S4702 Campbell CLyde tee PT647278 Campbell Cooper See OMS 1940323 1940325 1940326 1940327 1939757 1939978 | June | 2022 | 2022Q4 | 2022 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | UG | Not Veg | 2022-06-08 | N | 123.0217 | N | 3 | N | N | 1.1101 | 39.4971 | 66346.6541
[7 empty] | 1339 | 16338 | 1939796 | 2022-06-08 08:46 | 2022-06-08 10:12 | 86 | 11kV | 64586 | 751 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | iR77908 Copacabana Koorbel - Opened on B phase only - All phases opened by CR @ 0850 Cause not ascertained - T/PE to investigate | June | 2022 | 2022Q4 | 2022 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2022-06-08 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 47197.5438
[7 empty] | 1382 | 16960 | 1939866 | 2022-06-08 11:42 | 2022-06-08 21:20 | 578 | 11kV | 35139 | 396 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | Zn8000 Macquarie Park - Pnl.29 tripped on Earth Fault Cable ID on incorrect cable (cnr Waterloo and Coolinga) for NAR97342 Abnormal: Front line section of Pnl.10 out of service DMA (pnl.10L supplied by Pnl.29R) | June | 2022 | 2022Q4 | 2022 | ZN8000:PA10 | ZN8000:PA10 | ZN08000/000010 | RYDE | UG | Not Veg | 2022-06-08 | N | 88.7348 | N | 3 | N | N | 1.1101 | 39.4971 | 25678.5448
[7 empty] | 1392 | 17064 | 1940045 | 2022-06-09 05:11 | 2022-06-09 10:05 | 294 | 11kV | 3714 | 41 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | LID 221224 Overcurrent Stay wire failed at UGOH pole BJ-70086 contacting 11kV. Excluded OMS 1940045 | June | 2022 | 2022Q4 | 2022 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2022-06-09 | N | 90.5854 | N | 2 | N | N | 1.1101 | 39.4971 | 2714.0817
[7 empty] | 195 | 2487 | 1940129 | 2022-06-09 09:58 | 2022-06-09 11:54 | 116 | 11kV | 33524 | 289 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Cold <10C | N | Ex Zn9245 Engadine - Pnl.9 - 11kV "B" phase bond burnt off UGOH connection below PT9590 Stephen Rd. | June | 2022 | 2022Q4 | 2022 | ZN9245:PA9 | ZN9245:PA9 | ZN09245/000009 | SUTHERLAND | OH | Not Veg | 2022-06-09 | N | 116 | N | 2 | N | N | 1.1101 | 39.4971 | 24498.3504
[7 empty] | 1655 | 20093 | 1940495 | 2022-06-10 11:13 | 2022-06-10 12:33 | 80 | 11kV | 85188 | 1125 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1610 Homebush Bay - Pnl.19 tripped on: Earth Fault UG cable fault between S2071 Sw/A and S4804 Sw/A See 1940761 1940762 | June | 2022 | 2022Q4 | 2022 | ZN1610:PA19 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2022-06-10 | N | 75.7227 | N | 4 | N | N | 1.1101 | 39.4971 | 62252.8778
[7 empty] | 1515 | 18597 | 1940398 | 2022-06-10 03:40 | 2022-06-10 13:15 | 575 | 11kV | 265003 | 1524 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Cold <10C | N | Zn2400 berowra - Pnl.21 tripped, reclosed & tripped on: C phase OC OH mains down between S3500 and AB316 tee PT1166. Also 11kV bond off at AB465 See 1940757 1940758 | June | 2022 | 2022Q4 | 2022 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2022-06-10 | N | 173.8865 | N | 4 | N | N | 1.1101 | 39.4971 | 193656.3761
[7 empty] | 291 | 3694 | 1940604 | 2022-06-10 17:17 | 2022-06-10 19:07 | 109.7167 | 11kV | 21065.6 | 192 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 221227 section isolated to replace pole IU-80033 | June | 2022 | 2022Q4 | 2022 | 214:8667 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Not Veg | 2022-06-10 | N | 109.7167 | N | 4 | N | N | 1.1101 | 39.4971 | 15394.1191
[7 empty] | 1232 | 15092 | 1940628 | 2022-06-10 22:38 | 2022-06-11 00:10 | 92 | 11kV | 13340 | 145 | HV | Overload Operational | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | Cold <10C | N | PT158 Cressy Rd - Middle Phase HDO found blown DOp reports overload | June | 2022 | 2022Q4 | 2022 | ZN35500:PA36 | ZN35500:PA36 | ZN35500/000036 | RYDE | Unknown | Not Veg | 2022-06-10 | N | 92 | N | 4 | N | N | 1.1101 | 39.4971 | 9748.4785
[7 empty] | 703 | 9070 | 1940733 | 2022-06-11 18:17 | 2022-06-11 22:45 | 268 | 11kV | 11979 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn12600 Lisarow CP41020 Wattle Tre Tripped on Relays: OC trip and Lockout Cause: Tree hit Mains between LB45185 and LB45186 See OMS 1940873 1940874 1940733 1940745 1940746 | June | 2022 | 2022Q4 | 2022 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2022-06-11 | N | 106.0088 | N | 1 | N | N | 1.1101 | 39.4971 | 8753.8999
[7 empty] | 868 | 10796 | 1940823 | 2022-06-12 10:08 | 2022-06-12 11:12 | 64 | 11kV | 69248 | 1082 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 32 tripped due to a faulty overcurrent relay Abnormal Swithcing: S2968 SW/B closed, SW/A Open See OMS 1940871 1940823 1940824 | June | 2022 | 2022Q4 | 2022 | ZN4545:PA32 | ZN4545:PA32 | ZN04545/000032 | RYDE | Exclude | Not Veg | 2022-06-12 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 50604.3959
[7 empty] | 1208 | 14972 | 1940771 | 2022-06-12 00:38 | 2022-06-12 12:05 | 687 | 11kV | 7200 | 177 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 221229 S.O. deenergised feeder tree on mains at pole MG90066 Excluded oms 1940771 | June | 2022 | 2022Q4 | 2022 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2022-06-12 | N | 40.678 | N | 2 | N | N | 1.1101 | 39.4971 | 5261.5476
[7 empty] | 1157 | 14525 | 1941039 | 2022-06-13 19:38 | 2022-06-14 01:55 | 377 | 11kV | 559894 | 3167 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Cold <10C | N | At S15011 Beacon Hill Panel 10 tripped under fault Cause: Protection Relays Flags at Zone: Sef Trip, EFI, Fault CHeck Signals: 11kV Trip Zone Earth Cause: 11kV Mains down @ 8 Ellis Rd Beacon Hill See OMS 1941762 1941764 1941765 1941039 1941040 | June | 2022 | 2022Q4 | 2022 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2022-06-13 | N | 176.79 | N | 1 | N | N | 1.1101 | 39.4971 | 409154.0211
[7 empty] | 181 | 2348 | 1941233 | 2022-06-14 14:12 | 2022-06-14 16:20 | 128 | 11kV | 95488 | 746 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 11kV Recloser CP46113 Widdens Whard Coronga tripped, reclosed tripped and locked out on Relaus: Overcurrent and IOC Field EFI's NiL Cause not ascertained | June | 2022 | 2022Q4 | 2022 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2022-06-14 | N | 128 | N | 1 | N | N | 1.1101 | 39.4971 | 69779.814
[7 empty] | 364 | 4917 | 1941384 | 2022-06-15 10:30 | 2022-06-15 13:20 | 170 | 11kV | 3400 | 20 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 221243 SEE programmed NAR 97174, when switchign on this NAR staff measured 220 plus volts at the base of pole AL-70021, this was deemed a safety hazard and resulted in the need to interrupt from FS 74995. | June | 2022 | 2022Q4 | 2022 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2022-06-15 | N | 170 | N | 2 | N | N | 1.1101 | 39.4971 | 2484.6197
[7 empty] | 228 | 2762 | 1941522 | 2022-06-15 17:42 | 2022-06-15 20:20 | 158 | 11kV | 62568 | 396 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Cold <10C | N | 11kV Bond burnt of AB36 EX2196 Milperra Panel 5 See OMS 1941729 1941522 | June | 2022 | 2022Q4 | 2022 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2022-06-15 | N | 158 | N | 2 | N | N | 1.1101 | 39.4971 | 45722.849
[7 empty] | 1502 | 18476 | 1941758 | 2022-06-16 17:46 | 2022-06-16 19:30 | 104 | 11kV | 9373 | 99 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 20 Feeder tripped on Relays: A B and C phase OC, EFI Cause: S5074 Bradfield Booraba HV Endbox Failed Explosively See OMS 1942589 1942590 1941758 | June | 2022 | 2022Q4 | 2022 | ZN1193:PA20 | ZN1193:PA20 | ZN01193/000020 | KU-RING-GAI | UG | Not Veg | 2022-06-16 | N | 94.6768 | N | 3 | N | N | 1.1101 | 39.4971 | 6849.5119
[7 empty] | 1357 | 16624 | 1941769 | 2022-06-16 18:54 | 2022-06-16 21:05 | 131.1833 | 11kV | 131.1833 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At S3535 CSIRO Brsadfield Ex Lindfield - DOp Opened SW/B for safety Cause: Interrupted by DOp to Isolate S5074 after HV Endbox failed. | June | 2022 | 2022Q4 | 2022 |  |  |  | KU-RING-GAI | UG | Not Veg | 2022-06-16 | N | 131.1833 | N | 3 | N | N | 1.1101 | 39.4971 | 95.8649
[7 empty] | 995 | 12176 | 1941752 | 2022-06-16 17:42 | 2022-06-16 23:05 | 323 | 11kV | 93908 | 324 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 221251 11kV OHM into LV & on ground at pole JT-40735 also repaired tapping pole JT-40304. Bird into 11kV OHM Karloo St SEE report 221247 for T&R Sw 80787 Excluded OMS 1941752 | June | 2022 | 2022Q4 | 2022 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2022-06-16 | N | 289.8395 | N | 3 | N | N | 1.1101 | 39.4971 | 68625.1966
[7 empty] | 699 | 9004 | 1941925 | 2022-06-17 17:03 | 2022-06-17 17:53 | 50 | 11kV | 143350 | 2867 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S80 Chatswood Panel 4 tripped on Relays: 40L Leg EF and EFI Cause: 11kV UG fault from S35001 to S6294 to S3602 | June | 2022 | 2022Q4 | 2022 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | UG | Not Veg | 2022-06-17 | N | 50 | N | 1 | N | N | 1.1101 | 39.4971 | 104755.9519
[7 empty] | 1086 | 13898 | 1942092 | 2022-06-18 20:17 | 2022-06-18 21:25 | 68 | 11kV | 2108 | 31 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221256 A Phase DOLF : 16 Amp Possum Excluded OMS 1942092 | June | 2022 | 2022Q4 | 2022 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2022-06-18 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 1540.4642
[7 empty] | 127 | 1590 | 1942102 | 2022-06-18 23:38 | 2022-06-19 00:32 | 54 | 11kV | 44766 | 829 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S12570 Avoca - Panel 41 feederAvoca feeder tripped Relays: B and C phase IOC, Lockout Signals: 11kV Trip Cause: Tree branch on 11kV Mains near PT13984 | June | 2022 | 2022Q4 | 2022 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Veg | 2022-06-18 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 32713.6724
[7 empty] | 740 | 9377 | 1942101 | 2022-06-18 23:36 | 2022-06-19 00:56 | 80 | 11kV | 13520 | 169 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | CP61952 Ballorock Avoca Tripped on Relays: OC trip, Lockout Section of Panel 35 Kincumber Tree branch on 11kV mains near PT12416 | June | 2022 | 2022Q4 | 2022 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2022-06-18 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 9880.0172
[7 empty] | 25 | 262 | 1942106 | 2022-06-19 01:34 | 2022-06-19 02:35 | 61 | 11kV | 6344 | 104 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221257 C Phase DOLF : 40 Amp Excluded OMS 1942106 | June | 2022 | 2022Q4 | 2022 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Veg | 2022-06-19 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 4636.0081
[7 empty] | 1380 | 16924 | 1942395 | 2022-06-19 02:06 | 2022-06-19 03:40 | 94 | 11kV | 1099 | 1006 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At Zn36300 Balgowlan North Panel 8 tripped and reclosed on Relays: B and C pgase IOC, EFI Signals: 11kV Trip TX2 Relay Panel : EFC = - B Cause: Dead Possum ar CP61274 caused the UGOH tails to burn off SW/A side of S65545 Gibbs Sunshine see OMS 1942395 1942396 | June | 2022 | 2022Q4 | 2022 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Not Veg | 2022-06-19 | N | 1.0924 | N | 7 | N | N | 1.1101 | 39.4971 | 803.1168
[7 empty] | 1010 | 12717 | 1942108 | 2022-06-19 06:46 | 2022-06-19 07:25 | 39 | 11kV | 4485 | 115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 221258 B Phase DOLF : 40 Amp excluded OMS 1942108 | June | 2022 | 2022Q4 | 2022 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Veg | 2022-06-19 | N | 39 | N | 7 | N | N | 1.1101 | 39.4971 | 3277.5057
[7 empty] | 180 | 2347 | 1942141 | 2022-06-19 11:03 | 2022-06-19 11:28 | 25 | 11kV | 11600 | 464 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 221260 3 fault operations 3 phase Overcurrent Intelliruptor Branch across mains pole JT-12459 | June | 2022 | 2022Q4 | 2022 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Veg | 2022-06-19 | N | 25 | N | 7 | N | N | 1.1101 | 39.4971 | 8476.9379
[7 empty] | 1349 | 16472 | 1942154 | 2022-06-19 12:35 | 2022-06-19 15:11 | 156 | 11kV | 18702 | 130 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At ZN2196 Milperra Panel 14 tripped on Relays: 50TN, 51N and Minor Alarm (EFI on the Basler Relay + Fault Check Signals: Zone Earth, 11kV Trip Cause: 11kV UG cable fault from SW/B @ S5614 to S5703 to S2688 See OMS 1942388 1942390 1942392 1942154 1942154 | June | 2022 | 2022Q4 | 2022 | ZN2196:PA14 | ZN2196:PA14 | ZN02196/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-06-19 | N | 143.8615 | N | 7 | N | N | 1.1101 | 39.4971 | 13666.87
[7 empty] | 483 | 5871 | 1942156 | 2022-06-19 12:47 | 2022-06-19 15:30 | 163 | 11kV | 63752 | 805 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At ZN36100 Rose Bay Panel 7 tripped on Signals: 11kV TripCause: SW/B End Box failed art S6027 explosively See OPMS 1942356 1942357 1942358 1942359 1942156 1943167 1942166 | June | 2022 | 2022Q4 | 2022 | ZN36100:PA7 | ZN36100:PA7 | ZN36100/000007 | WAVERLEY | UG | Not Veg | 2022-06-19 | N | 79.195 | N | 7 | N | N | 1.1101 | 39.4971 | 46588.0812
[7 empty] | 1557 | 19071 | 1941968 | 2022-06-18 03:27 | 2022-06-19 18:33 | 2346 | 11kV | 39997 | 137 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn690 Campsie Panel 27 Tripped on Relays: Earth Fault, Fault Checik, EFI Signals 11kV Trip, Tx4 Group Earth, Zone Earth. Abnormal Switching: SW/B Closed AR S78089, SW/A Open @ S78088 Cause: UG cable fault, 11kV UG cable from SW/B @ S49897 to SW/A S1301 See 1942410, 1942412 1942413 1941968 1941970 1942003 1942004 1941969 | June | 2022 | 2022Q4 | 2022 | ZN690:PA27 | ZN690:PA27 | ZN00690/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2022-06-18 | N | 291.9489 | N | 4 | N | N | 1.1101 | 39.4971 | 29228.6279
[7 empty] | 794 | 9923 | 1942190 | 2022-06-19 17:28 | 2022-06-19 20:06 | 158.1333 | 11kV | 790.6667 | 5 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | Rain Light | N | Operator V Hickey Blown LF47158 a & B Ph : 20A posible Animal. line patrolled clear | June | 2022 | 2022Q4 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2022-06-19 | N | 158.1333 | N | 7 | N | N | 1.1101 | 39.4971 | 577.7959
[7 empty] | 1567 | 19169 | 1942617 | 2022-06-21 20:53 | 2022-06-21 21:45 | 52 | 11kV | 33635 | 834 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn4853 Strathfield South - Pnl.17 tripped on: B phase OC UG cable fault between S4544 Sw/B and S76918 Sw/A See interrupted to Pnl.8 due to defective EFI @ S4544 See 1942952 1942953 | June | 2022 | 2022Q4 | 2022 | ZN4853:PA17 | ZN4853:PA17 | ZN04853/000017 | STRATHFIELD | UG | Not Veg | 2022-06-21 | N | 40.3297 | N | 2 | N | N | 1.1101 | 39.4971 | 24579.4659
[7 empty] | 1250 | 15221 | 1942620 | 2022-06-21 21:00 | 2022-06-21 22:59 | 119 | 11kV | 80124 | 724 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn14892 Charmhaven -Pnl.9 tripped & reclosed on: OC & EF UG cable fault between S14513 Sw/B and S14237 Sw/A (Haz) Abnormal: S18288 Sw/B closed with S14786 Sw/B open See 1942950 1942951 | June | 2022 | 2022Q4 | 2022 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | UG | Not Veg | 2022-06-21 | N | 110.6685 | N | 2 | N | N | 1.1101 | 39.4971 | 58552.2559
[7 empty] | 123 | 1522 | 1942692 | 2022-06-22 10:35 | 2022-06-22 11:31 | 56 | 11kV | 672 | 12 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | No Weather Impact | N | Emergency NAR 100263 Reinstate broken stay on pole SI30163. | June | 2022 | 2022Q4 | 2022 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2022-06-22 | N | 56 | N | 3 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 184 | 2409 | 1942727 | 2022-06-22 12:34 | 2022-06-22 16:20 | 225.95 | 11kV | 1355.7 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | No LID Report Broken tapping at pole HY-50361 | June | 2022 | 2022Q4 | 2022 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2022-06-22 | N | 225.95 | N | 3 | N | N | 1.1101 | 39.4971 | 990.7056
[7 empty] | 950 | 11515 | 1942819 | 2022-06-22 22:31 | 2022-06-23 00:18 | 107 | 11kV | 146697 | 1371 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2835 Burwood - Pnl.32 tripped on: C phase OC UG cable fault in section between S6376 Sw/B & S2378 Sw/A | June | 2022 | 2022Q4 | 2022 | ZN2835:PA32 | ZN2835:PA32 | ZN02835/000032 | BURWOOD | UG | Not Veg | 2022-06-22 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 107201.8408
[7 empty] | 95 | 1209 | 1942829 | 2022-06-23 03:55 | 2022-06-23 06:44 | 169 | 11kV | 132521 | 1019 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Pnl.8 Noraville - 11kV Bond burnt off UGOH below S14824 Alexandra Natuna | June | 2022 | 2022Q4 | 2022 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2022-06-23 | N | 130.05 | N | 2 | N | N | 1.1101 | 39.4971 | 96842.4381
[7 empty] | 880 | 10847 | 1943000 | 2022-06-23 17:40 | 2022-06-23 19:10 | 90.1333 | 11kV | 450.6667 | 5 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 221273 A & B Phase DOLF : 20 Amp L/F 47158 A & B phase 20A Found dead Swan at pole HS-53203. | June | 2022 | 2022Q4 | 2022 | 507:80914 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2022-06-23 | N | 90.1333 | N | 2 | N | N | 1.1101 | 39.4971 | 329.3339
[7 empty] | 426 | 5349 | 1943034 | 2022-06-24 01:29 | 2022-06-24 03:14 | 105 | 11kV | 38278 | 1096 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn188 Zetland - Pnl.45 tripped on: Earth Fault Note: die to EFI @ S35077 failed to operate, on attempting resotration, Panel 9 tripped on earth fault UG cable fault between S35077 Sw/A and S35036 Sw/A to S2539 Sw/B See 1945041 1945048 | June | 2022 | 2022Q4 | 2022 | ZN188:PA45 | ZN188:PA45 | ZN00188/000045 | SYDNEY | UG | Not Veg | 2022-06-24 | N | 34.9252 | N | 2 | N | N | 1.1101 | 39.4971 | 27972.4334
[7 empty] | 1455 | 17919 | 1943074 | 2022-06-24 09:25 | 2022-06-24 09:40 | 15 | 11kV | 150 | 10 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 221282 DOLF X ARM AT SUB 53084 FOUNF LYING ON TANK Emergency SI indicates interruption was required to perform repars safely. Excluded OMS 1943074 | June | 2022 | 2022Q4 | 2022 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2022-06-24 | N | 15 | N | 2 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 844 | 10435 | 1943209 | 2022-06-25 02:00 | 2022-06-25 03:15 | 75 | 11kV | 102580 | 1610 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2635 Epping - Pnl.46 tripped on: OC & EF Abnormal: LB3159 Closed with LB1408 Open (DMA) UG Cable fault between S78267 and S80033 tee PT2208 See 1945078 1945113 1945115 | June | 2022 | 2022Q4 | 2022 | ZN2635:PA46 | ZN2635:PA46 | ZN02635/000046 | RYDE | UG | Not Veg | 2022-06-25 | N | 63.7143 | N | 3 | N | N | 1.1101 | 39.4971 | 74962.4384
[7 empty] | 819 | 10118 | 1943211 | 2022-06-25 05:28 | 2022-06-25 07:29 | 121 | 11kV | 102124 | 844 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn36300 Balgowlah North - Pnl.17 tripped on: Earth Fault Abnormal: LB61274 Closed with S65545 Sw/A Open Possum found at base of ELB.61274 | June | 2022 | 2022Q4 | 2022 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2022-06-25 | N | 121 | N | 3 | N | N | 1.1101 | 39.4971 | 74629.2071
[7 empty] | 1507 | 18516 | 1943282 | 2022-06-25 21:15 | 2022-06-26 02:40 | 325 | 11kV | 5525 | 17 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 221279 Fallen mains between poles GS80006 & GS80044 Excluded OMS No. 1943282 | June | 2022 | 2022Q4 | 2022 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2022-06-25 | N | 325 | N | 3 | N | N | 1.1101 | 39.4971 | 4037.507
[7 empty] | 802 | 10001 | 1943316 | 2022-06-26 06:07 | 2022-06-26 20:00 | 833 | 11kV | 1397200 | 1745 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn15015 North Head - Pnl.15 tripped on: C phase IOC and OC Abnormal: 1. S16374 Sw/B and S16690 Sw/B Closed with Pnl.5 North Head to S16194 Sw/A and S16374 Sw/D out of service (UG cable fault) 2. S16909 Sw/B closed with S16721 to USL22305 out of service (UG cable fault) - S15525 in LV // 3. S15193 Sw/B Closed with S16427 Sw/A to S15095 Sw/A out of service (UG cable fault) Cause: UG cable fault between Pnl.15 North Head, S15071 Sw/A and S16374 Sw/A LV parallel failure at S.15525 Osborne Rd See 1943442 1943447 | June | 2022 | 2022Q4 | 2022 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | UG | Not Veg | 2022-06-26 | N | 800.6877 | N | 1 | N | N | 1.1101 | 39.4971 | 1021032.5496
[7 empty] | 1356 | 16588 | 1943412 | 2022-06-27 07:10 | 2022-06-27 08:02 | 52 | 11kV | 3432 | 66 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 221284 C Phase DOLF : 32 Amp Blown LA on C phase. Note T&R on this feeder 0420hrs today. Excluded OMS 1943412 | June | 2022 | 2022Q4 | 2022 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2022-06-27 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 2508.0044
[7 empty] | 524 | 6206 | 1943411 | 2022-06-27 07:02 | 2022-06-27 08:54 | 112 | 11kV | 95700 | 1138 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn340 Botany - pnl.35 tripped on: Earth fault with IOC UG cable fault between S3947 and S8637 to S2094 See 1945140 | June | 2022 | 2022Q4 | 2022 | ZN340:PA35 | ZN340:PA35 | ZN00340/000035 | BAYSIDE | UG | Not Veg | 2022-06-27 | N | 84.0949 | N | 5 | N | N | 1.1101 | 39.4971 | 69934.7373
[7 empty] | 159 | 1963 | 1943502 | 2022-06-27 12:21 | 2022-06-27 13:01 | 40 | 11kV | 76560 | 1914 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | No Weather Impact | N | Zn10999 Kogarah - Pnl.10 tripped on: A & B phase OC Balloons on OH mains at 65 Unwin Rd Bexley | June | 2022 | 2022Q4 | 2022 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Veg | 2022-06-27 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 55947.7899
[7 empty] | 1520 | 18666 | 1943585 | 2022-06-27 17:01 | 2022-06-27 21:20 | 259 | 11kV | 2072 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | PT18875 Hensons Hoipos 0.5 - B phase HDO blown Fuse carrier requires replacement | June | 2022 | 2022Q4 | 2022 | ZN12630:PA11 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2022-06-27 | N | 259 | N | 5 | N | N | 1.1101 | 39.4971 | 1514.1565
[7 empty] | 269 | 3476 | 1943624 | 2022-06-27 22:47 | 2022-06-28 12:40 | 833 | 11kV | 9163 | 11 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | At Sub 2179 Gipps Bank - 11KV 80Amp B phase fuse blew due to transformer failure. Related job: 1943624 | June | 2022 | 2022Q4 | 2022 | ZN7481:PA6R | ZN7481:PA6R | ZN07481/000006 | SYDNEY | UG | Not Veg | 2022-06-27 | N | 833 | N | 5 | N | N | 1.1101 | 39.4971 | 6696.0501
[7 empty] | 1389 | 17031 | 1944166 | 2022-06-30 13:44 | 2022-06-30 15:56 | 132 | 11kV | 65288 | 661 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12660 Woy Woy - Pnl.13 tripped on Earth Fault UG cable fault between S12563 Sw/B to S12618 Sw/A Restoration delayed due to S12618 Oval Brickwall due to operating restriction on RMI See 1945166 1945168 | June | 2022 | 2022Q4 | 2022 | ZN12660:PA13 | ZN12660:PA13 | ZN12660/000013 | CENTRAL COAST | UG | Not Veg | 2022-06-30 | N | 98.7716 | N | 1 | N | N | 1.1101 | 39.4971 | 47710.5447
1343382740.9603

## Step 2 AER
Step 2 (AER): Pivot Table based on wind-related weather events
This table shows how the AER filtered disruptive events in making its draft decision.
tmed_exclusion | - all -
Climate Event | - all -
Veg/Non_Veg | Veg
LGA | - all -
event_trigger | - multiple -
Sum of VoUSE | FY
event_weather | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | Total Result
Electrical Storm | 391155.0827 | 490525.9258 | 1379970.8716 | 46360500.6035 | 1229990.846 | 2808714.7308 | 1463842.7787 | 1784304.8036 | 1861594.0152 | 4019925.2864 | 2001012.0077 | 63791536.952
Rain Wind Storm | 710326.8834 | 2468440.592 | 741698.5811 | 159982880.9102 | 10923835.5303 | 1483818.5488 | 318830.7867 | 2713562.6136 | 73525487.4787 | 2732322.5399 | 5798741.1874 | 261399945.6522
Wind | 1195959.6187 | 2629853.242 | 7534021.058 | 766764.2408 | [7 empty] | 12126598.1596
Wind Strong | 107388.918 | 37817.3736 | 112096.5416 | 809480.0422 | 897866.3451 | 713879.8409 | 1326474.8899 | 3382904.075 | 5897335.6965 | 919485.5084 | 2950283.2104 | 17155012.4416
Total Result | 2404830.5029 | 5626637.1334 | 9767787.0523 | 207919625.7968 | 13051692.7213 | 5006413.1206 | 3109148.4553 | 7880771.4921 | 81284417.1904 | 7671733.3347 | 10750036.4054 | 354473093.2053

## Step 2 Ausgrid
Step 2 (Ausgrid): Pivot Table based on wind-related weather events
This table explains how Ausgrid uses the filters to apportion risk to network solutions. (Refer 'Notes' tab, note 2)
We have added an additional summary view starting at cell E7 that is used to determine the proportion of faults CCT can improve
|  |  |  | Summary table | Total | p.a | % of Total | Improved by CCT
|  |  |  | Vegetation Blow/Fall In | 260011860.6019 | 23637441.8729 | 24.7% | Yes
|  |  |  | O/H Conductor Wind Related | 222948275.7045 | 20268025.064 | 21.17% | Yes
|  |  |  | Equipment Failed in Service | 211809072.4896 | 19255370.2263 | 20.12%
|  |  |  | Self Clear (No Cause Found) | 94516133.8255 | 8592375.8023 | 8.977%
|  |  |  | Lightning Strike | 21136169.6477 | 1921469.968 | 2.007%
tmed_exclusion | - all -
Climate Event | Y
Veg/Non_Veg | - all -
LGA | - all -
Sum of VoUSE | FY
event_trigger | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | Total Result
Vegetation Blow/Fall In | 3827390.5333 | 6968402.9698 | 7606270.4135 | 195610367.0553 | 12331203.3413 | 3662277.5781 | 2496679.2085 | 5983807.2588 | 79461005.2276 | 8142468.7286 | 7317098.3862 | 333406970.7011
Equipment Failed in Service | 4182134.8051 | 7574213.996 | 5629566.9873 | 169766445.8337 | 12647035.3869 | 4755578.739 | 7653104.0458 | 10557728.6906 | 34519422.3361 | 7838517.8056 | 7434843.9056 | 272558592.5316
O/H Conductor Wind Related | 36605.7561 | 127766.4536 | 4517.6233 | 193515754.9286 | 1824856.3794 | 415958.2253 | 521309.7551 | 4365237.5154 | 69311236.3208 | 1135418.2298 | 1114165.5966 | 272372826.784
Self Clear (No Cause Found) | 2806058.7941 | 2452021.5063 | 4118728.1559 | 76491744.5772 | 7978854.2305 | 1722099.9374 | 1959979.3169 | 3745178.7541 | 13326714.3765 | 2462277.3223 | 1806949.1283 | 118870606.0994
Lightning Strike | 635738.1854 | 33559.4662 | 459617.4149 | 1585801.4459 | 8548839.6589 | 9924.3385 | 2285257.8867 | 9394495.4963 | 1128845.01 | 364490.0586 | 427057.5088 | 24873626.4702
Wind Blown Debris |  |  |  | 13079135.0782 |  | 55882.0205 | 54343.7486 | 49572.889 | 498032.6075 |  | 253594.9037 | 13990561.2475
OTHER - REFER COMMENTS | 1986.3438 | 32579.5517 | 337.616 | 8823.3231 | 1366158.8341 | 102898.3333 | 425404.8956 | 577258.2758 | 7599772.0977 | 263747.4984 |  | 10378966.7693
3rd Party Vehicle | 190868.4867 | 270897.1743 | 7190.7818 | 566127.1794 |  | 116652.1649 | 109604.6142 | 112926.6969 | 143662.1736 | 42762.4976 |  | 1560691.7694
Animal Bird | 65156.229 | 212018.7998 |  | 110070.8458 | 46713.043 | 91896.5833 | 82233.6049 | 8058.9371 | 89610.0024 |  | 3502.035 | 709260.0803
Animal Possum | 40586.2631 | 62456.032 | 205570.1155 | 2671.697 | 146230.8319 |  | 49625.8942 | 146066.4085 |  | 4912.9701 | 3306.0058 | 661426.2181
Excavation 3rd Party | 1550.695 | 108968.8439 |  |  | 210146.9434 |  |  |  |  | 135493.6209 | 140369.3217 | 596529.4248
Overload |  | 5953.636 |  |  |  | 23329.1176 | 39373.184 | 480.847 | 424430.7785 | 8188.2835 |  | 501755.8467
Bushfire |  |  | 482346.777 | [8 empty] | 482346.777
Arcing |  | 42365.6893 |  | 261630.4562 |  |  | 6547.7037 | 34835.0992 |  |  | 28987.4736 | 374366.422
3rd Party Action |  | 30630.2457 | 252040.7985 | [7 empty] | 2494.1197 | 285165.1639
Vegetation Grow In |  |  |  | 203252.1236 | [7 empty] | 203252.1236
Animal Flying Fox | 32091.056 |  |  | 2185.0038 |  |  | 25117.313 | 57613.9466 | 66966.3475 |  | 3479.7099 | 187453.3769
Excavation Ausgrid Contractor | 168959.2561 | [10 empty] | 168959.2561
Fire (Non Ausgrid) |  |  |  | 9684.1707 |  |  | 153746.8065 |  |  |  |  | 163430.9773
Customer Installation Fault |  | 36872.4874 | 87682.9606 |  |  | 138.8464 | 22990.0401 | 817.0014 | 168.808 | 102.3079 |  | 148772.4517
Overload Operational |  | 67906.8492 |  |  |  |  | 43070.152 |  |  | 25147.2746 |  | 136124.2758
Fire (non-electrical) |  | 53278.2852 | 48797.2005 | [8 empty] | 102075.4857
Vandalism |  | 7510.1285 |  | 35143.4844 | [6 empty] | 524.6932 | 43178.3061
Staff Operation |  |  | 55.5386 | 19153.4949 | 4247.9689 | 684.0012 | 394.6161 | 8044.3217 | 5531.9327 |  |  | 38111.8741
Staff Other |  | 10220.8486 | 22569.847 |  | 2130.9268 |  |  | 176.8465 |  |  |  | 35098.4689
Animal Goanna | [8 empty] | 16399.9517 |  | 164.4234 | 16564.375
Overload LV Parallel |  | 4055.7763 |  |  |  | 8921.2463 | [5 empty] | 12977.0226
Animal Insect | [6 empty] | 5937.5104 |  |  |  |  | 5937.5104
Load Shed - Ausgrid | [10 empty] | 2117.7729 | 2117.7729
Animal Frog |  |  |  | 75.2694 | [7 empty] | 75.2694
Total Result | 11989126.4038 | 18101678.7397 | 18925292.2301 | 651268065.9671 | 45106417.545 | 10966241.1318 | 15934720.2965 | 35042298.985 | 206591797.9706 | 20423526.5978 | 18538654.9843 | 1052887820.8518
[11 empty] | Annual Risk | 76618240.2557

## Step 2-Comparison
Step 2 (Comparison): Comparison of AER and Ausgrid VoUSE based on wind-related weather events
This table shows the differences between the VoUSE from Ausgrid applied filters (Step 2 Ausgrid) to that of those applied by the AER filtered (Step 2 AER) for disruptive events in making its draft decision.
See the Notes tab - Note 2 for further information on the reasoning.
| Summary table | Ausgrid filters |  | Compared to AER filters
|  | Total | p.a | % of Total
| Vegetation Blow/Fall In | 260011860.6019 | 23637441.8729 | 95.51%
| O/H Conductor Wind Related | 222948275.7045 | 20268025.064 | 81.89%
| Equipment Failed in Service | 211809072.4896 | 19255370.2263 | 77.8%
| Self Clear (No Cause Found) | 94516133.8255 | 8592375.8023 | 34.72%
| Lightning Strike | 21136169.6477 | 1921469.968 | 7.764%
| OTHER - REFER COMMENTS | 17754315.5592 | 1614028.6872 | 6.522%
| Wind Blown Debris | 9512862.6116 | 864805.692 | 3.494%
| Total | 837688690.44 | 76153517.3127 | 307.7%

## Step 3 - Analysis
Step 3 Analysis
Parameters/Assumptions | AER's Draft Decision | Ausgrid Revised Proposal (Top Down Model) | Units | Rationale
Probability of Climate scenario (likelihood of the model outcome to occur) | 85% | 85% | % | Ausgrid has accepted with the AER's number for the purpose of this model. However, in our business case and previous submissions, we have explained the advice given to us by climate scientists differs from this.
Probability of encountering wind event at a given investment location p.a. | 50% | 100% | % | The probability of a wind event is already taken into account in the base interruption data and therefore does not need to be discounted a second time.
Percentage of deployment - CCT (extent of CCT coverage to realise avoided risk value) | 20% | 31.86% | % | This represents the proportion of climate risk that requires mitigation to offset the growth in risk.
Percentage of faults CCT can improve |  | 57.3% | % | This is calculated from the tab 'Step 2 Ausgrid' based on historical data.
Effectiveness for CCT (how much risk CCT can avoid) | 25% | 75% | % | The effectiveness of CCT is adjusted for the wind peril, which is the subject of this model. CCT is assumed to be 75% effective for the wind peril. Please see 'Notes' tab (Note 3).
Percentage of deployment - Segmentation (extent of segmentation coverage to realise avoided risk value) | 50% | 31.86% | % | This represents the proportion of climate risk that requires mitigation to offset the growth in risk. Assumed to be the same as row 6.
Percentage of faults Segmentation can improve |  | 100% | % | Segmentation can improve resilience to all climate perils and will be able to impact a percentage of customers for all wind peril events.
Effectiveness for Segmentation (how much risk segmentation can avoid) | 50% | 30% | % | This number has been calculated using a feeder level analysis.
Asset Loss effectiveness | 100% | 100% | % | Ausgrid accepts this number.
Climate modelling rate of change | 1% | 1% | % | Ausgrid accepts this number as a reasonable assessment of wind risk growth (only), which is the peril addressed in this model.
Forecast period | 30 | 28 | Years | Modified due to the program objective to mitigate risk growth to 2050
End of analysis Period | 2052 | 2050 | Year | Modified due to the program objective to mitigate risk growth to 2050
Annual benefit muliplier | 15 | 15 | Times | Ausgrid accepts this number.
Historical asset loss data
2015 cost passthrough total | 43200000 | 43200000 | $ | Sourced from previous cost pass through application/decision
2015 cost passthrough asset replacement component | 5340000 | 5340000 | $ | Sourced from previous cost pass through application/decision
2019 cost passthrough total | 26300000 | 26300000 | $ | Sourced from previous cost pass through application/decision
2019 cost passthrough asset replacement component | 12100000 | 12100000 | $ | Sourced from previous cost pass through application/decision
Total cost pass through | 69500000 | 69500000 | $ | Sourced from previous cost pass through application/decision
Total cost pass through asset replacement | 17440000 | 17440000
Total VoUSE | 272239114 | 842800642.8126 | $ | Ausgrid has selected filters to more accurately reflect the intent. See 'Notes' tab- note 2
Analysis period (historical data) | 11 | 11 | years
Expected VoUSE per annum - average historical over analysis period to 2022 | 24749010.3636 | 76618240.2557 | $ | Formulas are the same
Expected VoUSE per annum at end of forecast period (to 2052) | 33027650.2715 | 100232662.1282 | $ | Formulas are the same
Maximum difference from base to end of Forecast Period VoUSE p.a. | 8278639.9078 | 23614421.8725 | $ | Formulas are the same
CCT Solutions
Maximum avoidable VoUSE risk using CCT p.a. | 413931.9954 | 13723502.2003 | $ | Formula adjusted - Ausgrid has added an additional variable in cell R5
Expected VoUSE benefit p.a. | 175921.098 | 13723502.2003 | $ | Formula adjusted. Probability of climate scenario is not relevant to how much of the risk growth is bought down by this solution.
Segmentation Solutions
Maximum avoidable VoUSE risk using Segmentation p.a. | 2069659.977 | 9579404.6809 | $
Expected Segmentation benefit p.a. | 879605.4902 | 9579404.6809 | $ | Formula adjusted. Probability of climate scenario is not relevant to how much of the risk growth is bought down by this solution.
Asset Loss
Total cost pass through asset replacement | 17440000 | 17440000 | $
Pass through period 2012 to 2022 | 11 | 11 | Years
Expected Asset loss historical average to 2022 (p.a.) | 1585454.5455 | 1585454.5455 | $ | Formulas are the same
Expected Asset loss p.a. at end of Forecast Period | 2115795.237 | 2074105.7122 | $ | Formulas are the same
Difference Asset Loss from Base to end of Forecast Period | 530340.6916 | 488651.1668 | $ | Formulas are the same
Asset Loss difference avoidable using CCT | 132585.1729 | 366488.3751 | $ | Formulas are the same
Expected Asset Loss benefit p.a. | 56348.6985 | 311515.1188
Justifiable Investment
Total expected benefit p.a. | 1111875.2867
Growth in risk |  | 23614422 | $ | The purpose of the program is to mitigate the risk growth. See note 3
Approximate total capex justifiable from the expected annual benefit | 16678129.3009 | 354216330 | $ | Annual benefit multiplier is the same - Ausgrid apply this to the purpose of the program, as described in 'Notes' tab - Note 3.

## Notes
Explanatory Notes
Note 1: Objective of the Program
Ausgrid program objective is 'to maintain current customer and community service outcomes by enhancing the resilience of electricity distribution services in line with the projected growth in risk of disruptive climate events across the period FY25-50'.
Ausgrid have used the model to graph our understanding of the climate risk growth, shown in orange below.
Based on the program objective, we have sought to mitigate the entire risk growth (shown in orange) to maintain current customer and community service levels. This is what drives the required investment.
The model takes the historical annual average outage cost from climate related events ($76.6M year related to storms) and grows the risk at 1% per year to 2050 to give a total risk growth of $23.6M. This is then multiplied by the Annual Benefit Multiplier of 15 to provide a total capex window of $354M.
Growth in risk from Wind Peril at 2050 = $23.6M
Limit of capex available to mitigate the risk = $23.6M x 15 = $354.0M
Note 2. Value of Unserved Energy
Selection Criteria:
1. Scenarios for LGA, RestOfNetwork and WholeOfNetwork Included.
2. Primary mechanism for selecting events is the label Climate Event. Ausgrid uses the strong correlation between number of events per day and adverse weather conditions to label the largest 1% of days. We consider this event population to have the most signficant impact on our customer if the frequency and/or intensity of these events increases.
3. We do not further filter by the event_weather column as the response to all events is impacted by the storm even when the event is not directly related to the storm.
4. We consider the same logic to hold true for the event_trigger column however we concede we must differentiate between risk types because our network solutions can not address all risk types. We include triggers; Vegetation Blow/Fall In, O/H Conductor Wind Related, Equipment Failed in Service, Self Clear (No Cause Found), Lightning Strike, OTHER - REFER COMMENTS and Wind Blown Debris. These event triggers represent 99% of the USE for labelled Climate Events.
Reasoning
To attribute VoEUE to different network solutions we use historical event data to determine what percentage of risk the solution is able to mitigate, however there are some limitations to this method. Ausgrids outage management system (OMS) and reliabilty reporting database (NORD) inhibit how we record and classify events. NORD and OMS record individual events only, neither system records and labels groups of events such as east coast lows. The default method to group individual events together is to group them by date as is done for major event days. This method fails to capture all the events related to disruptive weather conditions. The purpose of the 'climate event' label is to capture all the related events without relying on event labels. Each event record has two fields used to describe the event. An event_trigger field and and asset_at_fault field. These fields can record only one event trigger and one asset_at_fault. During adverse weather conditions the event triggers is often the consequence of both wind and/or rain and/or vegetation. Unfortunately it is not possible to record the combination of contributing causes meaning we we can't rely on the event triggers to classify events as impacted by weather. This limitation means the number of events and VoEUE we can attribute to vegetation and wind is a minimum. There are likely many more events caused by these trigges that are labelled as 'Self Clear' or 'Equipment Failed in Service'. Conservatively we only include VoEUE risk for the CCT solutions where the event is labelled with an appropriate trigger.
Note 3 -Effectiveness of CCT
In our revised proposal, Ausgrid assume CCT to mitigate 75% of faults caused by vegetation blow-in and fall-in. This is a low-end estimate of the percentage of vegetation related faults where a branch causes the conductors to come together and clash, causing an outage, but where the branch can be easily removed by an Ausgrid crew (if it does not clear on its own). In these cases the covered conductor would prevent the clash occurring and the branch would sit on the conductors. The remaining 25% are cases where larger branches cause the conductors to break/fall to the ground, which cannot be mitigated by covering the conductor. CCT also prevents the vast majority of faults caused by conductor clashing in high speed winds, which is not explicitly modelled but is bundled with vegetation caused faults (it is often not possible for inspectors to differentiate between these causes, especially during major events when time to inspect individual faults is limited). For each avoided fault 25% of the conductor repair cost is avoided (as these faults would have required a ground crew inspection only and not a conductor re-stringing) and all of the unserved energy costs
We acknowledge that the application of this number is different to how Ausgrid used the effectiveness number in its draft proposal. In the draft proposal, the effectiveness rate was used to consider its effectiveness against all perils. In this revised proposal, our methodology breaks down the peril that we are focuing on in each of the models, making the 75% the more appropriate number for the wind peril.
In 2022, Pacific Corp published literature stating that CCT was 90% effective against the wind peril. The figure Ausgrid use is conservative, and less than this.
[1] Pacific Corp (2022), 2022 WMP Update Progress Report, pp.11-12.
This assumption is from the literature and is related to CCTs capacity to mitigate events in extreme weather (large branches and falling trees) as opposed to typical fall-in or blow in conditions experienced everyday.The literature gives evidence that CCT is very effective for wind and vegetation related events. The AG end-to-end model seperates the asset damage component of the risk from the general risk. Consequently we beleive the effectiveness of CCT should be increased 75% as it is now being applied only to the vegetation and wind risk component where it is demonstrably very effective.

## Mitigation Effectiveness
| Starting Risk | Total Risk | Risk Growth | CCT Mitigation | Total Benefit | Delta Benefit | CCT Risk Growth only | CCT Total Risk
2023 | 76618240.2557 | 76618240.2557 | 0 | 42.98% | 32929100.2027 | 0 | 76618240.2557 | 43689140.053
2024 | 76618240.2557 | 77384422.6582 | 766182.4026 | 42.98% | 33258391.2047 | 329291.002 | 77055131.6562 | 44126031.4535
2025 | 76618240.2557 | 78158266.8848 | 1540026.6291 | 42.98% | 33590975.1168 | 661874.9141 | 77496391.9708 | 44567291.768
2026 | 76618240.2557 | 78939849.5537 | 2321609.298 | 42.98% | 33926884.868 | 997784.6652 | 77942064.8884 | 45012964.6857
2027 | 76618240.2557 | 79729248.0492 | 3111007.7935 | 42.98% | 34266153.7166 | 1337053.5139 | 78392194.5353 | 45463094.3326
2028 | 76618240.2557 | 80526540.5297 | 3908300.274 | 42.98% | 34608815.2538 | 1679715.0511 | 78846825.4786 | 45917725.2759
2029 | 76618240.2557 | 81331805.935 | 4713565.6793 | 42.98% | 34954903.4063 | 2025803.2036 | 79306002.7314 | 46376902.5287
2030 | 76618240.2557 | 82145123.9944 | 5526883.7387 | 42.98% | 35304452.4404 | 2375352.2377 | 79769771.7567 | 46840671.554
2031 | 76618240.2557 | 82966575.2343 | 6348334.9786 | 42.98% | 35657496.9648 | 2728396.7621 | 80238178.4722 | 47309078.2695
2032 | 76618240.2557 | 83796240.9866 | 7178000.731 | 42.98% | 36014071.9345 | 3084971.7317 | 80711269.2549 | 47782169.0522
2033 | 76618240.2557 | 84634203.3965 | 8015963.1408 | 42.98% | 36374212.6538 | 3445112.4511 | 81189090.9454 | 48259990.7427
2034 | 76618240.2557 | 85480545.4305 | 8862305.1748 | 42.98% | 36737954.7803 | 3808854.5776 | 81671690.8528 | 48742590.6501
2035 | 76618240.2557 | 86335350.8848 | 9717110.6291 | 42.98% | 37105334.3281 | 4176234.1254 | 82159116.7593 | 49230016.5566
2036 | 76618240.2557 | 87198704.3936 | 10580464.1379 | 42.98% | 37476387.6714 | 4547287.4687 | 82651416.9249 | 49722316.7222
2037 | 76618240.2557 | 88070691.4376 | 11452451.1819 | 42.98% | 37851151.5481 | 4922051.3454 | 83148640.0921 | 50219539.8894
2038 | 76618240.2557 | 88951398.3519 | 12333158.0962 | 42.98% | 38229663.0636 | 5300562.8609 | 83650835.491 | 50721735.2883
2039 | 76618240.2557 | 89840912.3355 | 13222672.0798 | 42.98% | 38611959.6943 | 5682859.4915 | 84158052.8439 | 51228952.6412
2040 | 76618240.2557 | 90739321.4588 | 14121081.2031 | 42.98% | 38998079.2912 | 6068979.0885 | 84670342.3703 | 51741242.1676
2041 | 76618240.2557 | 91646714.6734 | 15028474.4177 | 42.98% | 39388060.0841 | 6458959.8814 | 85187754.792 | 52258654.5893
2042 | 76618240.2557 | 92563181.8201 | 15944941.5644 | 42.98% | 39781940.6849 | 6852840.4822 | 85710341.3379 | 52781241.1352
2043 | 76618240.2557 | 93488813.6383 | 16870573.3826 | 42.98% | 40179760.0918 | 7250659.8891 | 86238153.7492 | 53309053.5465
2044 | 76618240.2557 | 94423701.7747 | 17805461.519 | 42.98% | 40581557.6927 | 7652457.49 | 86771244.2847 | 53842144.082
2045 | 76618240.2557 | 95367938.7925 | 18749698.5368 | 42.98% | 40987373.2696 | 8058273.0669 | 87309665.7255 | 54380565.5228
2046 | 76618240.2557 | 96321618.1804 | 19703377.9247 | 42.98% | 41397247.0023 | 8468146.7996 | 87853471.3808 | 54924371.1781
2047 | 76618240.2557 | 97284834.3622 | 20666594.1065 | 42.98% | 41811219.4724 | 8882119.2697 | 88402715.0925 | 55473614.8898
2048 | 76618240.2557 | 98257682.7058 | 21639442.4501 | 42.98% | 42229331.6671 | 9300231.4644 | 88957451.2414 | 56028351.0387
2049 | 76618240.2557 | 99240259.5329 | 22622019.2772 | 42.98% | 42651624.9838 | 9722524.781 | 89517734.7518 | 56588634.5491
2050 | 76618240.2557 | 100232662.1282 | 23614421.8725 | 42.98% | 43078141.2336 | 10149041.0309 | 90083621.0973 | 57154520.8946
2051 | 76618240.2557 | 101234988.7495 | 24616748.4938 | 42.98% | 43508922.6459 | 10579822.4432 | 90655166.3063 | 57726066.1036
2052 | 76618240.2557 | 102247338.637 | 25629098.3813 | 42.98% | 43944011.8724 | 11014911.6697 | 91232426.9673 | 58303326.7646