## Coverpage
2023-11-30
Ausgrid’s 2024-29 Revised Proposal
Attachment 5.5.2: Climate Resilience Model 2 - Network Top Down
Empowering communities for a resilient, affordable and net-zero future.

## Summary
Network Resilience Top Down Model
Background
This model was first developed by the AER to determine its draft decision for Network Resilience.
Ausgrid has adapted the model logic, and provided reasoning where there are differences.
For transparency, Ausgrid has included the AER's calculations and our own side by side, providing an explanation of any differences.
Being clear on the program objective is key to understanding how Ausgrid have used the model
Key to understanding the difference between the AER's draft decision and Ausgrid's proposal is to be clear on the program objective.
Ausgrid program objective is 'to maintain current customer and community service outcomes by enhancing the resilience of electricity distribution services in line with the projected growth in risk of disruptive climate events across the period FY25-50'.
Ausgrid have used the model to graph our understanding of the climate risk growth, shown in orange below.
For more information refer to the 'Notes' tab, note 1

## Steps Taken
Description of steps taken
STEP | DESCRIPTION | ADDITIONAL SUPPORTING INFORMATION on how the AER determined its draft decision | Additional supporting information about how Ausgrid used the top down model for the revised proposal.
STEP 1: | Sourcing Ausgrid's historical outage data | Sourced via 'Ausgrid - IR010 - Climate change resilience - economic model' (i.e. the 'AGD Outages' worksheet) | No change
STEP 2: | Create Pivot Table based on wind-related weather events | Selection criteria: 1. Include all outage data (i.e. all LGAs as well as MED and non-MEDs outages); 2. Select outages from vegetation; 3. Select likely outage triggers related to wind events (i.e. O/H Conductor Wind Related, Vegetation Blow/Fall In, and Wind Blown Debris); 4. Select likely applicable weather events (i.e. storms and wind); 5. Sum the Value of Unserved Energy per annum (VoUSE). | Selection Criteria: (See Notes tab - Note 2) 1. Scenarios for LGA, RestOfNetwork and WholeOfNetwork Included. 2. Primary mechanism for selecting events is the label Climate Event. Ausgrid uses the strong correlation between number of events per day and adverse weather conditions to label the largest 1% of days. We consider this event population to have the most signficant impact on our customer if the frequency and/or intensity of these events increases. 3. We do not further filter by the event_weather column as the response to all events is impacted by the storm even when the event is not directly related to the storm. 4. We consider the same logic to hold true for the event_trigger column however we concede we must differentiate between risk types because our network solutions can not address all risk types. We include triggers; Vegetation Blow/Fall In, O/H Conductor Wind Related, Equipment Failed in Service, Self Clear (No Cause Found), Lightning Strike, OTHER - REFER COMMENTS and Wind Blown Debris. These event triggers represent 99% of the USE for labelled Climate Events.
STEP 3 (PART 1): | Calculate the maximum annual incremental increase in VoUSE from climate risk | Calculate the incremental change of network risk over the forecast period: 1. Calculate the base year using historical average (cell Q26); 2. Grow the base year using the climate/network risk rate of change assumptions (cell Q27); 3. The difference between item 1 & 2 is considered the maximum annual incremental VoUSE in the final years of the forecast period (cell Q28). | No change
STEP 3 (PART 2): | Calculate the maximum VoUSE benefits that Ausgrid can practically achieve through its proposed asset investments | Based on the annual VoUSE derived in STEP 3 (PART 1), apply the following probabilistic multipliers to each asset solution type: 1. Apply the associated effectiveness of solution and its percentage coverage (cell Q32 and Q36); 2. Apply the probability confidence in wind climate scenario and wind event occuring in the same location per annum (cell Q33 and Q37). | See Step 3 - Analysis for more details.
STEP 3 (PART 3): | Calculate the asset loss possibly avoidable | Calculate the likely asset loss avoidable (steps): 1. Source historical asset loss data from previous cost pass through events (cell Q15 to Q20); 2. Calculate the incremental increase in asset loss similar to STEP 3 (PART 1) (cell Q43 to Q45); 3. Apply the effectiveness of CCT and the probability confidence in wind climate scenario and wind event occuring in the same location per annum (cell Q46 and Q47); | See Step 3 - Analysis for more details.
STEP 3 (FINAL): | Calculation the maximum justifiable capex in a given 5 year period | Calculation the maximum justifiable capex (steps): 1. Sum the benefit results in STEP 3 (PART 2) and (PART 3) to determine the annual expected benefits from investments (cell Q49); 2. Multiply item 1 by the annual benefit multiplier (cell Q12) to determine the maximum justifiable capex (cell Q50) | We have used the climate risk growth to determine the maximum justifiable capex. This is based on the program objective which is 'to maintain current customer and community service outcomes by enhancing the resilience of electricity distribution services in line with the projected growth in risk of disruptive climate events across the period FY25-50'. See Notes tab - note 1.

## Key Assumptions
Table of Key Parameters/Assumptions
Assumption | AER's interpretation of Ausgrid's assumptions in the draft proposal | AER assumption used to make draft decision | Comments provided by AER to explain the assumptions made to inform their draft decision. (difference in assumptions between column C and Column B) | Ausgrid Revised Proposal | Ausgrid's reasoning for the assumptions made in the revised proposal (Column D)
Climate/network risk rate of change | 1% | 1% | Applied Ausgrid’s assumption of 1% rate of change in climate risk to 2040 and 2070 from the baseline 2020 level. | 1% | Ausgrid agrees with the AER's assumptions for wind risk growth.
Probability of a wind event occurring in the same location per annum | 100% (every year) | 50% (every other year) | With 100%, Ausgrid assumes the extreme wind event occurs every year in the same investment location. We have applied an upper end assumption of that recurrence every other year. | 100% | The probability of a wind event is already taken into account in the base interruption data and therefore does not need to be discounted a second time.
Probability of climate scenario occurring | 100% (high confidence) | 85% (high-medium confidence) | With 100%, Ausgrid assumes its projection of windstorm intensity/frequency and therefore network impact occurs with 100% certainty. This is contrary to its climate modelling where it classified these risks as ‘Medium Confidence’. We applied an upper end assumption of 85% certainty. | 85% (high-medium confidence) | Ausgrid has accepted the AER's number for the purpose of this model. However, the advice given to us by climate scientists differs from this and this is explained in our business case and other previous submissions.
Effectiveness of CCT | 25% | 25% | Applied Ausgrid’s assumption, although we consider that the effectiveness is likely to diminish if installed in significantly higher volume compared to historical. | 75% | The effectiveness of CCT is adjusted for the wind peril, which is the subject of this model. CCT is assumed to be 75% effective for the wind peril. Please see notes tab (Note 3).
Percentage of faults Segmentation can improve |  | Not used | Not included | 100% | Segmentation can improve resilience to all climate perils.
Effectiveness of segmentation | 100% | 50% | With 100%, Ausgrid assumes its solution will be 100% effective in mitigating wind related risk. We have applied 50% probability, which is higher than the usual industry applied level of one third probability. | 30% | This number has been calculated using a feeder level analysis.
Percentage of CCT coverage | NA | 20% | As our forecast is based on Ausgrid’s total loss of supply associated with wind, we had to make an assumption on the level of deployment that Ausgrid’s can practically deliver from its CCT program within a given 5-year period. Based on existing coverage, this is likely less than 10% for its targeted LGA areas. We have applied 20% as an upper end estimate. | 32% | This represents the proportion of climate risk that requires mitigation to offset the growth in risk
Percentage of segmentation coverage | NA | 50% | As our forecast is based on Ausgrid’s total loss of supply associated with wind, we had to make an assumption on the level of deployment that Ausgrid can practically deliver from its segmentation program within a given 5-year period. Based on existing coverage, this is likely less than 25% for its targeted LGA areas. We have applied 50% as an upper end estimate. | 32% | This represents the proportion of climate risk that requires mitigation to offset the growth in risk. Assumed to be the same as line above.
Forecast period | Up to 30 years | 30 years | We assume the highest value of Ausgrid’s forecast period based on its CBA principles | 28 years | As per the objectives of the business case.
Annual benefit multiplier to approximate the maximum justifiable capex over a 5-year period | NA | 15 times | As our forecast is based on the maximum likely benefits that Ausgrid could reasonably achieve through its investments, it is assumed that the return on and of capital is approximately 8% to 12% of the initial capital cost based on an assumed 40 to 50 years asset life and recent values of the WACC (i.e. such that investment timing is essentially as soon as practical). Depending on economic conditions, this can range between 9 to 15 times of the annual benefits to approximate the maximum justifiable capex over a 5-year period. We have applied 15 times as an upper end estimate in lieu of a suitable time series model. We only consider this figure to be relevant in this case because of the significant uncertainty regarding the application of climate modelling forecast in the context of Ausgrid's network. | 15 times | Ausgrid accepts the AER's assumption as a resonable assumption.
Content relevant to the AER's draft Decision
Content relevant to the Ausgrid's revised proposal

## Step 1 - AGD Outages
Step1 - Outage data used by AER in making its draft decision (provided by Ausgrid as part of IR010) | [19 empty] | is climate and unselected | 13734129.6612 |  | Electrical Storm | 184429217.8494 | 744755180.8226
[20 empty] | is climate and blank | 25503.1599 |  | Rain Wind Storm | 540565451.0421 | [15 empty] | 842800642.8126
[20 empty] | is climate and the selected values | 0 |  | Wind | 9475109.7028 | [7 empty] | is veg and climate | 363024969.4866 |  | 44.29%
|  |  |  | AVG VCR | 39.4971 | [17 empty] | Wind Strong | 10285402.2283 | [7 empty] | is not veg and climate | 456569949.9586 |  | 55.71% | [12 empty] | Hard code paste when this setting is off
|  |  |  | Avg Load | 1.1101 | [21 empty] | 0 | [5 empty] | 819594919.4452
| FEEDER | Customer numbers | Average Power (kW) | vcr ($/kWh) | Avg Power Per Customer | Avg VCR with Filler | Seq |  | event_id | event_begin_time | event_completion_time | event_duration | event_voltage | event_cmi | event_ci | event_voltage_hierarchy | event_trigger | event_trigger_super_group | event_asset_at_fault | event_reporting_category | event_weather | tmed_exclusion | event_comments | month_name | year_calendar | quarter_FY | FY | hist_fdr | current_network_feeder | iams_id | LGA | OH/UG | Veg/Non_Veg | event_begin_date | weather_MED | cmi/ci | weather_MED+ | event_count_for_date | Weather Event | Climate Event | Avg load per customer | Avg VCR | VoUSE |  |  | Weather Event | Climate Event | KPMG 2020 Weather LoS | KPMG 2020 All LoS | Weighted (all climate) | % change from KPMG | $ Change from KPMG
| 814:82283 | 176 | 180.0239 | 42.61 | 1.0229 | 42.61 | 19186 | 5410 | 691163 | 2011-07-01 06:44 | 2011-07-01 07:27 | 43 | 11kV | 30186 | 702 | HV | 3rd Party Vehicle | 3rd Party Impact | Circuit Breaker | Unplanned | Unselected | N | At Sub 12600 Lisarow Panel 2 "Holegate" feeder tripped and locked me out on: Relays: Earth fault and EFI Signals: 11kv trip Rec 41066 Macdonalds Rd tripped, reclosed, tripped and locked out on: Phased Overcurrent ABNORMAL: AB44993 Opened, Rec 40239 Wattle Tree Rd South Closed Remarks: Car hit and snapped pole at 111 Macdonalds Rd Lisarow. 11KV feeder from Lk44031 to LB40866 Tee to PT14486 Macdonalds Tuggerah 1.5 to LK41045 Related jobs: #692122, 691163, 691179, 691164 | July | 2011 | 2012Q1 | 2012 |  |  |  | CENTRAL COAST | Unknown | Not Veg | 2011-07-01 | N | 43 | N | 7 | N | N | 1.1101 | 39.4971 | 22059.0385 |  | BAYSIDE | 196805.3116 | 1017023.0787 | 6647542.0388 | 6945689.1545 | 568072.2872 | -91.82% | -6377616.8673
| 814:82285 | 145 | 154.9699 | 50.62 | 1.0688 | 50.62 | 18596 | 152 | 691486 | 2011-07-01 16:28 | 2011-07-01 17:20 | 52.1167 | 11kV | 4996.4833 | 96 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116724 A Phase DOLF : 40Amp. Load readings: 245V; 300,300,250A. DOLF element fatigue. | July | 2011 | 2012Q1 | 2012 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Not Veg | 2011-07-01 | N | 52.0467 | N | 7 | N | N | 1.1101 | 39.4971 | 3928.736 |  | BURWOOD | 25175.5089 | 26333.0494 | 534796.4157 | 568392.7507 | 21799.1915 | -96.16% | -546593.5592
| 814:82289 | 666 | 651.6166 | 39.5 | 0.9784 | 39.5 | 19934 | 14122 | 691397 | 2011-07-01 14:19 | 2011-07-01 17:26 | 187 | 11kV | 374 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116725 Single phase DOLF : 10Amp. Defective surge arrestor replaced. Excluded OMS 691397 OMS 692304 | July | 2011 | 2012Q1 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2011-07-01 | N | 187 | N | 7 | N | N | 1.1101 | 39.4971 | 273.3082 |  | CANADA BAY | 25295.2224 | 39304.4252 | 1733974.1316 | 1824317.539 | 29744.0636 | -98.37% | -1794573.4754
| 814:82291 | 471 | 404.2199 | 31.72 | 0.85822 | 31.72 | 20426 | 20308 | 691345 | 2011-07-01 12:53 | 2011-07-01 19:01 | 368 | 11kV | 4048 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116728 B Phase DOLF : 31Amp Excluded OMS 691345 OMS 692129 | July | 2011 | 2012Q1 | 2012 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2011-07-01 | N | 368 | N | 7 | N | N | 1.1101 | 39.4971 | 2958.159 |  | CANTERBURY-BANKSTOWN | 392498.6408 | 1280215.6399 | 4027337.8617 | 4761555.6839 | 1063711.3798 | -77.66% | -3697844.3041
| 256:80632 | 861 | 604.025 | 45.64 | 0.70154 | 45.64 | 19167 | 5179 | 691530 | 2011-07-01 18:10 | 2011-07-01 19:36 | 86 | 11kV | 35776 | 416 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Rain Light | N | Section of feeder beyond LK40339 "Hanlan St" fdr ex Panel 13 West Gosford Remarks: At LK 40339 footpath phase bond burnt off Related jobs: #692106, 691530, 691545 | July | 2011 | 2012Q1 | 2012 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2011-07-01 | N | 86 | N | 7 | N | N | 1.1101 | 39.4971 | 26144.0456 |  | CENTRAL COAST | 1860843.2205 | 32209539.7244 | 30944265.8119 | 34485235.5242 | 28029035.7756 | -18.72% | -6456199.7486
| 256:80635 | 530 | 384.9114 | 32.07 | 0.72625 | 32.07 | 18939 | 3417 | 691551 | 2011-07-01 18:44 | 2011-07-01 20:36 | 112 | 11kV | 93861 | 873 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills Panel 26 Tripped on A phase Earthg Fault, EFI, Lockout, 11kV Trip, Field EFI's Cause: Suspect UG fault between S7942 and S1389. See OMS 691551 692375 | July | 2011 | 2012Q1 | 2012 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2011-07-01 | N | 107.5155 | N | 7 | N | N | 1.1101 | 39.4971 | 68590.8504 |  | CESSNOCK | 556432.9894 | 2975551.9446 | 276604.7766 | 2979748.0663 | 2119123.9675 | -28.88% | -860624.0988
| 256:80638 | 1032 | 1052.3863 | 37.8 | 1.0198 | 37.8 | 20313 | 19093 | 691599 | 2011-07-01 23:19 | 2011-07-02 14:00 | 881 | 11kV | 15234 | 99 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | At S355370 Galston Panel 10 Tripped reclosed tripped and locked out on A and C phase IOC Signals: 11kV trip, Lockout with EFI. Cause: Insulator failed on Line side of AB2195 See OMS 692602/607/608/609 691599 691644 | July | 2011 | 2012Q1 | 2012 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2011-07-01 | N | 153.8788 | N | 7 | N | N | 1.1101 | 39.4971 | 11132.5579 | PARRAMATTA | CITY OF PARRAMATTA | 26841.5362 | 26841.5362 | 485936.0326 | 556537.6478 | 26841.5362 | -95.18% | -529696.1116
| 256:80640 | 955 | 591.2042 | 37.1 | 0.61906 | 37.1 | 19139 | 4884 | 691625 | 2011-07-02 07:24 | 2011-07-02 17:07 | 583 | 11kV | 82569 | 1386 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S180 Mosman Panel 30 tripped on Relays: Timed earth fault, EFI, Fault Check Relay. Cause: 11kV feeder fault from S2135 to S372 See OMS 692727 692729 See excluded 691625/629/723 | July | 2011 | 2012Q1 | 2012 | ZN180:PA30 | ZN180:PA30 | ZN00180/000030 | MOSMAN | UG | Not Veg | 2011-07-02 | N | 59.5736 | N | 3 | N | N | 1.1101 | 39.4971 | 60338.9898 |  | CUMBERLAND | 55601.5375 | 110414.5736 | 192638.6574 | 273469.964 | 143561.8537 | -47.5% | -129908.1103
| 256:80641 | 1248 | 704.1309 | 36.45 | 0.56421 | 36.45 | 19073 | 4470 | 691822 | 2011-07-02 19:42 | 2011-07-02 21:00 | 78 | 11kV | 624 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116735 B Phase DOLF : 20Amp DOLF element fatigued Excluded OMS 691822 OMS 692128 | July | 2011 | 2012Q1 | 2012 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2011-07-02 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 456.0008 |  | DUNGOG | 0 | 0 | 0 | 136.8187 | 0 | -100% | -136.8187
| 256:80644 | 1078 | 699.1556 | 36.52 | 0.64857 | 36.52 | 19969 | 14630 | 691601 | 2011-07-02 00:40 | 2011-07-03 10:45 | 2045 | 11kV | 155550 | 594 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Panel 11ex Zn2400 Berowra, 11kV Recloser 1239 Brooklyn Tripped and locked out on Phase Protection. Tree into 11kV mains near AB1188, See OMS 692286 692291 692288, 691601/603/620/676/785 OMS 692288 Two phases are open circuit at distributor pole 93903, customer without supply since outage, ensure clearence of low voltage services from air break shaft as they appear caught up on bolt from ground. OMS 692291 Customer at 3a has bundle clamp come away at pole a, pls re-fit OK-DQ1 | July | 2011 | 2012Q1 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2011-07-02 | N | 261.8687 | N | 3 | N | N | 1.1101 | 39.4971 | 113671.3521 |  | GEORGES RIVER | 245847.0556 | 1485985.5558 | 5173273.9064 | 5275302.0423 | 979405.7887 | -81.43% | -4295896.2536
| 256:80646 | 1712 | 993.9672 | 30.05 | 0.58059 | 30.05 | 18894 | 3057 | 691902 | 2011-07-03 11:55 | 2011-07-03 15:35 | 220 | 11kV | 440 | 2 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 116737 Single phase DOLF : 10Amp bird on tx damaged surge arrestors replaced by field staff Excluded OMS 691902 OMS 692231 | July | 2011 | 2012Q1 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2011-07-03 | N | 220 | N | 2 | N | N | 1.1101 | 39.4971 | 321.539 |  | HORNSBY | 665321.4928 | 6212630.5349 | 1918148.5666 | 2703867.5049 | 5676477.5425 | 109.9% | 2972610.0375
| 256:80647 | 1798 | 1825.9382 | 40.46 | 1.0155 | 40.46 | 18836 | 2386 | 691953 | 2011-07-03 17:44 | 2011-07-03 18:45 | 61 | 11kV | 9455 | 155 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Cold <10C | N | At PT985 Wishart St Roadside 31.5A fuse operated. Cause: Fuse Fatigue See OMS 692686 691953 | July | 2011 | 2012Q1 | 2012 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2011-07-03 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 6909.4351 |  | HUNTERS HILL | 41170.5473 | 80401.0982 | 701916.0459 | 722483.0306 | 104472.2273 | -85.54% | -618010.8034
| 256:80650 | 1221 | 1029.4227 | 37.05 | 0.8431 | 37.05 | 20343 | 19444 | 691991 | 2011-07-04 01:16 | 2011-07-04 02:37 | 81 | 11kV | 60526 | 785 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At ZN.9900 Menai P-12 "Page Sylvan' tripped, reclsoed and tripped on: B phase Earh leakage, timing relay, lockout, EFI 11kv trip FIELD EFIs: S.9049, S.9168 & S.9249 REMARKS: Suspect fault in section 11kV cable between S.9149 Palmer Heritage to S.9937 Phoenix Regent | July | 2011 | 2012Q1 | 2012 | ZN9900:PA12 | ZN9900:PA12 | ZN09900/000012 | SUTHERLAND | UG | Not Veg | 2011-07-04 | N | 77.1032 | N | 3 | N | N | 1.1101 | 39.4971 | 44230.6156 |  | INNER WEST | 74578.279 | 165294.6237 | 10818079.0429 | 11009350.8122 | 174671.3899 | -98.41% | -10834679.4224
| 256:80652 | 171 | 226.1703 | 48.18 | 1.3226 | 48.18 | 19596 | 9821 | 692436 | 2011-07-04 17:12 | 2011-07-04 18:30 | 78 | 11kV | 138017 | 1825 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | At S15008 Harbord Panel 3 tripped reclosed tripped and locked out on A and B phase IOC Timing Relay and Lockout Relay. Cause: USL21137 Roadside Phase High Resistance. See OMS 692554 692553 692436/438/437/442 | July | 2011 | 2012Q1 | 2012 | ZN15008:PA3 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2011-07-04 | N | 75.6258 | N | 3 | N | N | 1.1101 | 39.4971 | 100858.7528 |  | KU-RING-GAI | 362021.9311 | 3202515.6345 | 10988251.6275 | 11234703.482 | 2575478.1732 | -77.08% | -8659225.3088
| 256:80653 | 787 | 491.9161 | 34.62 | 0.62505 | 34.62 | 19792 | 12718 | 692483 | 2011-07-04 17:12 | 2011-07-04 18:30 | 78 | 11kV | 78 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S15008 Harbord Panel 3 tripped reclosed tripped and locked out on A and B phase IOC Timing Relay and Lockout Relay. Cause: USL21137 Roadside Phase High Resistance. See OMS 692554 692553 | July | 2011 | 2012Q1 | 2012 | ZN15003:PA4 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Not Veg | 2011-07-04 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 57.0001 |  | LAKE MACQUARIE | 781131.4447 | 14961984.5069 | 14085495.9708 | 15646397.5381 | 9529260.5217 | -39.1% | -6117137.0164
| 224:80326 | 1156 | 758.1497 | 31.73 | 0.65584 | 31.73 | 18841 | 2477 | 692679 | 2011-07-05 10:34 | 2011-07-05 11:53 | 79 | 11kV | 96645 | 1394 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn12600 Lisarow 11kV panel 3 tripped on A phase O/;C with 11kV protectiion trip alarm Cause not ascertained for outage. See OMS 693336 693338 693329 | July | 2011 | 2012Q1 | 2012 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2011-07-05 | N | 69.3293 | N | 9 | N | N | 1.1101 | 39.4971 | 70625.3155 |  | LANE COVE | 70802.9591 | 103931.5099 | 4827406.5506 | 4878942.2999 | 69145.9409 | -98.58% | -4809796.3591
| 224:80328 | 25 | 416.6122 | 41.86 | 16.6645 | 41.86 | 19152 | 4941 | 692853 | 2011-07-05 13:39 | 2011-07-05 13:55 | 16 | 11kV | 5856 | 366 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 116754 2 fault operations A Phase Overcurrent Tree branch removed. Excluded OMS 692853 OMS 693270 | July | 2011 | 2012Q1 | 2012 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | OH | Veg | 2011-07-05 | N | 16 | N | 9 | N | N | 1.1101 | 39.4971 | 4279.3921 |  | MAITLAND | 455818.4048 | 4202386.7356 | 122171.8115 | 1915511.1129 | 3070110.0192 | 60.28% | 1154598.9064
| 224:80329 | 489 | 464.1378 | 42.06 | 0.94916 | 42.06 | 18898 | 3110 | 692700 | 2011-07-05 10:58 | 2011-07-05 14:00 | 182 | 11kV | 16380 | 90 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 116752 11kV tapping O/C at pole NR-60122. excluded OMS No. s 692697 & 692700. OMS 693190 | July | 2011 | 2012Q1 | 2012 | 230:34047 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2011-07-05 | N | 182 | N | 9 | N | N | 1.1101 | 39.4971 | 11970.0209 |  | MOSMAN | 2584.6733 | 19215.947 | 2325674.3326 | 2424905.3277 | 15344.8759 | -99.37% | -2409560.4518
| 224:80331 | 365 | 907.596 | 59.84 | 2.4866 | 59.84 | 19423 | 8477 | 692778 | 2011-07-05 12:21 | 2011-07-05 14:15 | 114 | 11kV | 5814 | 51 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 116755 A phase DOLF : 40Amp. Tree on LV Mains excluded OMS 692779 OMS 693256 | July | 2011 | 2012Q1 | 2012 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2011-07-05 | N | 114 | N | 9 | N | N | 1.1101 | 39.4971 | 4248.6997 |  | MUSWELLBROOK | 180747.9446 | 272949.0986 | 22496.1184 | 1079934.4504 | 243305.5739 | -77.47% | -836628.8765
| 224:80332 | 1263 | 1035.375 | 38.16 | 0.81977 | 38.16 | 19002 | 4006 | 692863 | 2011-07-05 13:30 | 2011-07-05 15:30 | 120 | 11kV | 3712 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S4558 Chapman Hull 400A fuse blown on A phase of distributor 1. Cause: Tree branch removed from LV mains in Hull Rd Beecroft. See OMS 692842/843 | July | 2011 | 2012Q1 | 2012 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | OH | Veg | 2011-07-05 | N | 119.7419 | N | 9 | N | N | 1.1101 | 39.4971 | 2712.6201 |  | NEWCASTLE | 495526.842 | 7504734.4856 | 16355060.0419 | 19017850.2006 | 5742056.3281 | -69.81% | -13275793.8726
| 224:80335 | 94 | 380.0944 | 57.17 | 4.0436 | 57.17 | 18919 | 3229 | 693063 | 2011-07-05 17:14 | 2011-07-05 18:00 | 46.15 | 11kV | 46.15 | 1 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | CC1: 06-"Urgent - O.H Mains - No others"back fed to be repaired 6/7/11 | July | 2011 | 2012Q1 | 2012 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2011-07-05 | N | 46.15 | N | 9 | N | N | 1.1101 | 39.4971 | 33.7251 |  | NORTH SYDNEY | 27665.6426 | 27665.6426 | 6200482.4688 | 6242622.1345 | 18494.1361 | -99.7% | -6224127.9984
| 224:80337 | 1487 | 1291.8206 | 34.37 | 0.86874 | 34.37 | 20388 | 20035 | 693073 | 2011-07-05 17:52 | 2011-07-05 18:13 | 21 | 11kV | 10780 | 567 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 116759 Dip Fdr for safety to open faulty ABS 74728 excluded oms-693073, 693087 OMS 693393, 693395, 693396, 693397 | July | 2011 | 2012Q1 | 2012 | 813:89058 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2011-07-05 | N | 19.0123 | N | 9 | N | N | 1.1101 | 39.4971 | 7877.706 |  | NORTHERN BEACHES | 487984.4245 | 5536816.4986 | 45360488.8308 | 55228107.551 | 4551665.4305 | -91.76% | -50676442.1205
| 224:80340 | 1099 | 874.3595 | 33.19 | 0.7956 | 33.19 | 18832 | 2368 | 692784 | 2011-07-05 12:17 | 2011-07-05 18:30 | 373 | 11kV | 10544 | 38 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 116753 3 fault operations A Phase Wires down to sub 54050 excluded OMS 693017, 693060 OMS 693238, 693240 | July | 2011 | 2012Q1 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2011-07-05 | N | 277.4737 | N | 9 | N | N | 1.1101 | 39.4971 | 7705.2442 |  | PORT STEPHENS | 681429.9479 | 9839715.7114 | 1516719.0143 | 5376575.5625 | 8243138.214 | 53.32% | 2866562.6515
| 224:80341 | 1303 | 1335.7142 | 37.34 | 1.0251 | 37.34 | 18848 | 2553 | 692871 | 2011-07-05 11:41 | 2011-07-05 19:25 | 464 | 11kV | 5568 | 12 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse | Unplanned | Cold <10C | N | At PT13242 Yarramalong LAUFFS c PHASE HVDO High Resistance Cause:HR connection on HV fuse assembly. See OMS 693392 692871 693066 | July | 2011 | 2012Q1 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2011-07-05 | N | 464 | N | 9 | N | N | 1.1101 | 39.4971 | 4068.9302 |  | RANDWICK | 14749.6061 | 20178.6331 | 5074479.8951 | 5117806.5147 | 17345.5477 | -99.66% | -5100460.967
| 224:80344 | 100 | 1444.3209 | #N/A | 14.4432 | 39.4971 | 19144 | 4894 | 693155 | 2011-07-06 01:46 | 2011-07-06 02:48 | 62 | 11kV | 271722 | 4503 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At ZN.9118 Cronulla P-11 "Ewos Waratah" fdr tripped on: RELAYS: O/C, 1.2.1 Targets 50TAC ABNORMAL: Closed at S.9665 Parramatta St, Open at S.9512 Purley Cordon (e.g. all P-7) REMARKS: Windy, no cause ascertained | July | 2011 | 2012Q1 | 2012 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2011-07-06 | N | 60.3424 | N | 3 | N | N | 1.1101 | 39.4971 | 198566.4232 |  | RYDE | 247161.9243 | 787413.2366 | 1527336.1276 | 1726794.4885 | 488481.791 | -71.71% | -1238312.6975
| 224:80346 | 1739 | 1655.6048 | 38.22 | 0.95204 | 38.22 | 19753 | 12447 | 693210 | 2011-07-06 04:29 | 2011-07-06 04:44 | 15 | 11kV | 6510 | 434 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 116763 Feeders de-energised to remove broken connection at ABS 8384. see LID 116763 : OMS 690209 | July | 2011 | 2012Q1 | 2012 | 225:13444 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Not Veg | 2011-07-06 | N | 15 | N | 3 | N | N | 1.1101 | 39.4971 | 4757.316 |  | SINGLETON | 562740.9993 | 781293.616 | 375156.9669 | 1947859.1442 | 848599.3442 | -56.43% | -1099259.8
| ZN167:PA1 | 181 | 736.6391 | 49.69 | 4.0698 | 49.69 | 18576 | 66 | 693209 | 2011-07-06 04:29 | 2011-07-06 04:45 | 16 | 11kV | 22288 | 1393 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 116763 Feeders de-energised to remove broken connection at ABS 8384. See Report 116764; OMS 693210 | July | 2011 | 2012Q1 | 2012 | 260:33344 | 239:82136 | ZN00239/082136 | LAKE MACQUARIE | OH | Not Veg | 2011-07-06 | N | 16 | N | 3 | N | N | 1.1101 | 39.4971 | 16287.413 |  | STRATHFIELD | 33492.8731 | 76938.774 | 816135.2692 | 864997.0583 | 51562.5878 | -94.04% | -813434.4705
| ZN167:PA10 | 1094 | 747.4888 | 30.64 | 0.68326 | 30.64 | 19201 | 5808 | 693673 | 2011-07-07 02:16 | 2011-07-07 04:19 | 123 | 11kV | 150921 | 1227 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S2400 Berowra Panel 15 tripped on Relays - A and C phase O/C EFI. Signals: 11kV Trip Cause not ascertained for outage DOp unable tpo patrol section near cully crossing. At S2400 Berowra Panel 15 tripped on Relays - A and C phase O/C EFI. Signals: 11kV Trip Cause not ascertained for outage DOp unable tpo patrol section near cully crossing. | July | 2011 | 2012Q1 | 2012 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2011-07-07 | N | 123 | N | 6 | N | N | 1.1101 | 39.4971 | 110288.6154 |  | SUTHERLAND SHIRE | 0 | 0 | 7746856.4776 | 14410127.7858 | 0 | -100% | -14410127.7858
| ZN167:PA11 | 141 | 301.7033 | 45.34 | 2.1397 | 45.34 | 19490 | 9024 | 693681 | 2011-07-07 05:50 | 2011-07-07 08:00 | 130 | 11kV | 130 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116783 single phase DOLF : 10Amp Found DOLF down, replaced OK. As left 243V - 30A. Excluded OMS No. 693681. OMS 695199 | July | 2011 | 2012Q1 | 2012 | 225:33670 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2011-07-07 | N | 130 | N | 6 | N | N | 1.1101 | 39.4971 | 95.0002 |  | SYDNEY | 116557.9686 | 152720.6121 | 9432007.3333 | 9492509.0235 | 250139.8451 | -97.36% | -9242369.1785
| ZN167:PA12 | 150 | 759.6616 | 47.14 | 5.0644 | 47.14 | 19249 | 6513 | 693853 | 2011-07-07 11:14 | 2011-07-07 12:30 | 76 | 11kV | 11488 | 1888 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S12640 Umina Panel 2 tripped and reclosed on A and B phase O/C and Earth Fault. Cause: HV fuse found blown at PT 11374 - Cause not ascertained for outage. See OMS 694516 694517 693853 | July | 2011 | 2012Q1 | 2012 | ZN12640:PA2 | ZN12640:PA2 | ZN12640/000002 | CENTRAL COAST | OH | Veg | 2011-07-07 | N | 6.0847 | N | 6 | N | N | 1.1101 | 39.4971 | 8395.0916 |  | UPPER HUNTER | 182886.5805 | 270473.8267 | 33236.7041 | 565071.6491 | 242624.1099 | -57.06% | -322447.5393
| ZN167:PA13 | 1306 | 707.2366 | 28.05 | 0.54153 | 28.05 | 18690 | 1054 | 693943 | 2011-07-07 13:33 | 2011-07-07 15:10 | 97.3833 | 11kV | 7880.3833 | 81 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 116793 EMERGENCY REPAIRS TO BURNT TAPPINGS POLE JT-82059. | July | 2011 | 2012Q1 | 2012 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2011-07-07 | N | 97.2887 | N | 6 | N | N | 1.1101 | 39.4971 | 5758.7517 |  | WAVERLEY | 0 | 0 | 418693.3738 | 436782.6577 | 0 | -100% | -436782.6577
| ZN167:PA15 | 24 | 257.3715 | 50.53 | 10.7238 | 50.53 | 18814 | 2247 | 693743 | 2011-07-07 09:05 | 2011-07-07 16:40 | 455 | 11kV | 18210 | 145 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Section of Panel 3 Peats Ridge. Recloser CP46935 Iron Bark Kirks 0.8 tripped . Cause: 3 bays Adjacent CP46895 brought down by tree. See OMS 694541 694540 | July | 2011 | 2012Q1 | 2012 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2011-07-07 | N | 125.5862 | N | 6 | N | N | 1.1101 | 39.4971 | 13307.3309 |  | WILLOUGHBY | 136154.4367 | 699649.8957 | 7755309.2079 | 7801734.9044 | 521263.9938 | -93.32% | -7280470.9106
| ZN167:PA17 | 5 | 1101.1854 | 62.86 | 220.2371 | 62.86 | 19108 | 4689 | 694084 | 2011-07-07 17:00 | 2011-07-07 18:40 | 100 | 11kV | 22800 | 228 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 116794 Fdr de-energised for emergency repairs found by Line Inspector. ABS 3605 stranded aluminium conductor, only 1 strand remaining. Damaged discs poles HU-30017, HU-30018 | July | 2011 | 2012Q1 | 2012 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2011-07-07 | N | 100 | N | 6 | N | N | 1.1101 | 39.4971 | 16661.5675 |  | WOOLLAHRA | 10186.7482 | 10186.7482 | 2466846.824 | 2506495.3132 | 10186.7482 | -99.59% | -2496308.565
| ZN167:PA19 | 78 | 661.2648 | 50.83 | 8.4778 | 50.83 | 20052 | 15612 | 694268 | 2011-07-08 05:15 | 2011-07-08 06:07 | 52 | 11kV | 63908 | 1229 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S15005 Bellrose panel 2 tripped on A phase IOC EFI with Fault Check. Cause: Possum on HV UGOH adjacent USL 21194 See OMS 694268 694270 | July | 2011 | 2012Q1 | 2012 | ZN15005:PA2 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2011-07-08 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 46702.0814
| ZN167:PA2 | 127 | 832.2988 | 52.85 | 6.5535 | 52.85 | 19946 | 14231 | 694324 | 2011-07-08 08:33 | 2011-07-08 08:38 | 5 | 11kV | 9000 | 1800 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 116796 Bushing on Reg 10250 Fisherys point rd high resistance smoke from bushing. Emergency interuption from rec 5666 to by pass reg. Note abnormal switching under si 14910 abs 23061 open, abs 3397 closed, abs 23062 open OMS 694324 & 694325 | July | 2011 | 2012Q1 | 2012 | 243:80074 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Not Veg | 2011-07-08 | N | 5 | N | 3 | N | N | 1.1101 | 39.4971 | 6576.9345 |  |  | Actual outage data totals
| ZN167:PA20 | 374 | 767.5813 | 53.05 | 2.0524 | 53.05 | 20035 | 15381 | 694525 | 2011-07-08 13:12 | 2011-07-08 18:35 | 323 | 11kV | 646 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 116799 B Ph dropper to LF 41271 Broken. Excluded OMS# 694525. OMS 695343 | July | 2011 | 2012Q1 | 2012 | 512:48047 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2011-07-08 | N | 323 | N | 3 | N | N | 1.1101 | 39.4971 | 472.0777 |  |  | Weather Event | Climate Event | KPMG 2020 Weather LoS | KPMG 2020 All LoS | Weighted (all climate) | % change from KPMG | $ Change from KPMG
| ZN167:PA21 | 963 | 728.2661 | 34.61 | 0.75625 | 34.61 | 18757 | 1691 | 694726 | 2011-07-09 00:33 | 2011-07-09 02:10 | 97 | 11kV | 11787 | 747 | HV | Animal Possum | Animal | Insulator | Unplanned | Unselected | N | Recloser 45138 tripped and reclosed on IOC and Earth Fault. Possum at base of PT 13690 | July | 2011 | 2012Q1 | 2012 | ZN12590:PA6 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2011-07-09 | N | 15.7791 | N | 3 | N | N | 1.1101 | 39.4971 | 8613.5919 |  | Total | 7707139.621 | 75425120.1846 | 200904818.2348 | 240021814.7383 | 75425120.1846 | -68.58% | -164596694.5537
| ZN167:PA4 | 255 | 493.083 | 43.67 | 1.9337 | 43.67 | 19823 | 12996 | 694729 | 2011-07-09 02:06 | 2011-07-09 03:20 | 74 | 11kV | 5106 | 69 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | Fuse | Unplanned | Unselected | N | PT1281 Farrell Rd Roadside 31.5A HV Fuse Operated Ex Panel 4 "Miller Sir Thomas" feeder @ S1290 Leightonfield Remarks: Optus cable flicked into LV on cnr of hume hwy & Miller Rd Bass Hill Related jobs: #695857, 694729, 694730, 694731, 694732 | July | 2011 | 2012Q1 | 2012 | ZN1290:PA4 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2011-07-09 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 3731.3142
| ZN167:PA7 | 127 | 657.4368 | 60.86 | 5.1767 | 60.86 | 20161 | 16430 | 694875 | 2011-07-09 15:42 | 2011-07-09 16:40 | 58 | 11kV | 58 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116804 Single phase DOLF : 10Amp. Excluded OMS 694875 OMS 695351 | July | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2011-07-09 | N | 58 | N | 3 | N | N | 1.1101 | 39.4971 | 42.3847
| ZN167:PA8 | 13 | 722.5457 | #N/A | 55.5804 | 39.4971 | 19334 | 7558 | 694943 | 2011-07-10 03:13 | 2011-07-10 04:35 | 82 | 11kV | 152438 | 1859 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 116806 2 fault operations Overcurrent Daylight patrol required. Micom Prot relay faulty. OMS 694943. OK'd by Glen Cooper to leave Fdr in service on BU prot. | July | 2011 | 2012Q1 | 2012 | 232:33413 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2011-07-10 | N | 82 | N | 8 | N | N | 1.1101 | 39.4971 | 111397.1942
| ZN12570:PA21 | 2340 | 1328.7881 | 31.29 | 0.56786 | 31.29 | 19124 | 4828 | 695002 | 2011-07-10 10:23 | 2011-07-10 11:05 | 42 | 11kV | 8862 | 211 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S.15013 Terrey Hills, Panel 6 Fdr Cb tripped, reclosed, tripped and locked out on C phase timed COC, timing relay, lockout relay and efi. No field efi's Branch on 11kV OH in Aumuna St | July | 2011 | 2012Q1 | 2012 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2011-07-10 | N | 42 | N | 8 | N | N | 1.1101 | 39.4971 | 6476.0882
| ZN12570:PA22 | 1632 | 1169.1133 | 33.09 | 0.71637 | 33.09 | 18762 | 1773 | 695003 | 2011-07-10 10:27 | 2011-07-10 11:12 | 45.1333 | 11kV | 14803.7333 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Recloser 22381 tripped, reclosed and locked out on IOC - tree on 11kV mains O/S #35 Walter St | July | 2011 | 2012Q1 | 2012 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2011-07-10 | N | 45.1333 | N | 8 | N | N | 1.1101 | 39.4971 | 10818.1317
| ZN12570:PA24 | 1796 | 1295.2425 | 32.01 | 0.72118 | 32.01 | 20209 | 17100 | 695031 | 2011-07-10 11:49 | 2011-07-10 12:20 | 31 | 11kV | 186 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 116814 C Phase DOLF : 10Amp Excluded OMS 695031 OMS 695448 | July | 2011 | 2012Q1 | 2012 | 813:89063 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2011-07-10 | N | 31 | N | 8 | N | N | 1.1101 | 39.4971 | 135.9233
| ZN12570:PA25 | 996 | 604.1789 | 30.34 | 0.60661 | 30.34 | 18622 | 421 | 695010 | 2011-07-10 12:30 | 2011-07-10 15:00 | 150 | 11kV | 2700 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 116816 No protection operation. Fdr isolated to remove tree from OHM @ pole GW-40014. | July | 2011 | 2012Q1 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2011-07-10 | N | 150 | N | 8 | N | N | 1.1101 | 39.4971 | 1973.0804
| ZN12570:PA26 | 1307 | 1648.7578 | 46.21 | 1.2615 | 46.21 | 19219 | 6077 | 695049 | 2011-07-10 13:30 | 2011-07-10 15:55 | 145 | 11kV | 290 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 116815 Single phase Broken LL Clamp droppers. Excluded OMS# 695049. OMS 695428 | July | 2011 | 2012Q1 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2011-07-10 | N | 145 | N | 8 | N | N | 1.1101 | 39.4971 | 211.9234
| ZN12570:PA29 | 611 | 577.0463 | 38.55 | 0.94443 | 38.55 | 19440 | 8568 | 695071 | 2011-07-10 15:16 | 2011-07-10 17:39 | 143 | 11kV | 155656.7333 | 1230 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S.2400 Berowra, Panel 15 Fdr CB tripped on B and C phase OC, earth fault check, miscell alarm, 11kV trip. GIS issue as indicated by A.Op At S.2400 Berowra, Panel 15 Fdr CB tripped on B and C phase OC, earth fault check, miscell alarm, 11kV trip. | July | 2011 | 2012Q1 | 2012 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2011-07-10 | N | 126.5502 | N | 8 | N | N | 1.1101 | 39.4971 | 113749.3496
| ZN12570:PA33 | 1717 | 1032.549 | 35.04 | 0.60137 | 35.04 | 18604 | 267 | 695173 | 2011-07-10 22:43 | 2011-07-11 08:22 | 579 | 11kV | 1158 | 2 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 116817 A Phase DOLF : 10Amp Excluded OMS 695173 OMS 705911 | July | 2011 | 2012Q1 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2011-07-10 | N | 579 | N | 8 | N | N | 1.1101 | 39.4971 | 846.2322
| ZN12570:PA34 | 852 | 725.1807 | 31.02 | 0.85115 | 31.02 | 20293 | 18778 | 695689 | 2011-07-11 18:28 | 2011-07-11 19:15 | 47 | 11kV | 2867 | 61 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 116821 C Phase DOLF : 20Amp. volts 247, 245, 247 load 260, 143, 245 excluded OMS 695689 OMS 695775 | July | 2011 | 2012Q1 | 2012 | 227:13016 | 227:13016 | ZN00227/013016 | LAKE MACQUARIE | OH | Not Veg | 2011-07-11 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 2095.119
| ZN12570:PA35 | 1064 | 1236.6005 | 36.31 | 1.1622 | 36.31 | 19283 | 7237 | 695711 | 2011-07-11 19:19 | 2011-07-11 21:20 | 121 | 11kV | 64086 | 582 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At S.1114 North Ryde, Panel 1 Fdr Cb tripped, reclosed and locked out on A phase IOC and timed OC, lockout, time delay, efi. Field efi's down at S.7545, S.5248, S.4679, S.5250, S.35185, S.8911 and S.8532. The section of cable between S.8532 and S.1896 tee LB.303 failed | July | 2011 | 2012Q1 | 2012 | ZN1114:PA1 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2011-07-11 | N | 110.1134 | N | 3 | N | N | 1.1101 | 39.4971 | 46832.1586
| ZN12570:PA37 | 1529 | 1353.4593 | 30.87 | 0.88519 | 30.87 | 19780 | 12624 | 695719 | 2011-07-11 19:33 | 2011-07-11 23:50 | 257 | 11kV | 257 | 1 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 116822 C Phase DOLF : 16Amp. Service UGOH on private pole caught fire and sub DOLF blew. LV fuse and DOLF did not grade. LV bundle service fuse repaired Excluded OMS 695719 OMS 695838 | July | 2011 | 2012Q1 | 2012 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | Unknown | Unknown | 2011-07-11 | N | 257 | N | 3 | N | N | 1.1101 | 39.4971 | 187.808
| ZN12570:PA39 | 1474 | 1166.0904 | 36.47 | 0.79111 | 36.47 | 19419 | 8426 | 696240 | 2011-07-12 15:29 | 2011-07-12 18:53 | 204.1 | 11kV | 126630.95 | 995 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 1622 tripped, reclosed and locked out {Abnormal switching} OPGW wire off 132kV 9E1 dropped into 11kV OH conductor bwteen LB.3238 and AB.3023 | July | 2011 | 2012Q1 | 2012 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2011-07-12 | N | 127.2673 | N | 1 | N | N | 1.1101 | 39.4971 | 92538.1633
| ZN12570:PA40 | 1189 | 943.3729 | 32.7 | 0.79342 | 32.7 | 19376 | 8010 | 696391 | 2011-07-13 03:02 | 2011-07-13 09:05 | 363 | 11kV | 15002 | 154 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn8100 Green Square: 11kv Pa2 "S3667" Feeder tripped Relays: Earhte Fault, EFI, Fault CHeck on Tx1 Pa Signals: 11kv trip. #1Grp Earth Feild EFI: S3667 Remarks: No access to S5690 Bowden Mandible No2 due to guard dogs@0400. UG Feeder fault from S5690 to S3721 See 698192,3,4 696429 Exclude 696391 From To DC restored? Time Zn8100:Pa2 S3667 1 3:58 S7635 S3721 7 4:03 S3667 S5690 1 9:05 | July | 2011 | 2012Q1 | 2012 | ZN8100:PA2 | ZN8100:PA2 | ZN08100/000002 | SYDNEY | UG | Not Veg | 2011-07-13 | N | 97.4156 | N | 2 | N | N | 1.1101 | 39.4971 | 10963.0191
| ZN12570:PA41 | 833 | 657.0231 | 31.06 | 0.78874 | 31.06 | 18721 | 1286 | 696785 | 2011-07-13 17:58 | 2011-07-13 19:50 | 112 | 11kV | 224 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 116849 A phase DOLF : 3Amp. Suspected fatigued fuse Excluded OMS 696785 OMS 696864 | July | 2011 | 2012Q1 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2011-07-13 | N | 112 | N | 2 | N | N | 1.1101 | 39.4971 | 163.6926
| 227:13014 | 64 | 61.7426 | 40.47 | 0.96473 | 40.47 | 18928 | 3350 | 696834 | 2011-07-14 04:07 | 2011-07-14 05:21 | 74 | 11kV | 77034 | 1041 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Cold <10C | N | At S.15001 Panel 6 Fdr Cb tripped on A phase IOC, efi, fault check. Field efi's down @ S.16892, S.15189 and S.16948. Both UG/OH's on the section of feeder to S.16066 and to S.16027 appear to have experienced damage. | July | 2011 | 2012Q1 | 2012 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | Unknown | Unknown | 2011-07-14 | N | 74 | N | 2 | N | N | 1.1101 | 39.4971 | 56294.1751
| 227:13015 | 1720 | 1169.5531 | 34.21 | 0.67997 | 34.21 | 18760 | 1751 | 697141 | 2011-07-14 15:50 | 2011-07-14 19:38 | 228.0333 | 11kV | 4548.0333 | 1081 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Cold <10C | N | Branch overhanging 11kV at LB.1435. Feeder interrupted to allow removal by Mains | July | 2011 | 2012Q1 | 2012 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2011-07-14 | N | 4.2072 | N | 2 | N | N | 1.1101 | 39.4971 | 3323.5686
| 227:13016 | 164 | 120.8396 | 33.37 | 0.73683 | 33.37 | 19258 | 6622 | 698276 | 2011-07-15 09:20 | 2011-07-15 10:20 | 60 | 11kV | 60 | 1 | HV | Staff Other | Utility Process Issue | Circuit Breaker | Unplanned | Cold <10C | N | At S.1204 Bryant Fair - 11KV HVC "Chloride Batteries Aust Ltd" OCB opened Remarks: Jointer accidently tripped HVC c/b while working adjacent | July | 2011 | 2012Q1 | 2012 |  |  |  |  | Unknown | Not Veg | 2011-07-15 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 43.8462
| 227:13018 | 640 | 633.9271 | 39.52 | 0.99051 | 39.52 | 18766 | 1822 | 697724 | 2011-07-15 18:45 | 2011-07-15 21:34 | 168.7167 | 11kV | 99880.2667 | 592 | HV | Arcing | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | At S2400 Berowra section of Pa11 Brooklyn. Recloser 1239 Tripped Reclosed and locked out on A B OC Cause: Flash over on HR at REC1239. | July | 2011 | 2012Q1 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2011-07-15 | N | 168.7167 | N | 4 | N | N | 1.1101 | 39.4971 | 72989.5529
| 227:13019 | 120 | 250.3684 | 37.02 | 2.0864 | 37.02 | 20419 | 20241 | 697783 | 2011-07-15 22:02 | 2011-07-16 02:05 | 243 | 11kV | 84938 | 665 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 116869 11kv main off disc insulator at ABS 11001 hanging near LV main. Isolation for repairs. Also see report 116870. Excluded OMS 697783, 697786, 697805 OMS 698254 & 698256 | July | 2011 | 2012Q1 | 2012 | 208:53 | 257:81994 | ZN00257/081994 | NEWCASTLE | OH | Not Veg | 2011-07-15 | N | 127.7263 | N | 4 | N | N | 1.1101 | 39.4971 | 62070.1852
| 227:13020 | 844 | 696.3534 | 37.95 | 0.82506 | 37.95 | 19203 | 5838 | 697779 | 2011-07-16 01:05 | 2011-07-16 02:25 | 80 | 11kV | 9040 | 113 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 116870 Isolation for clearance 11kv main off disc insulator at ABS 11001 hanging near LV main. Isolation for repairs. Also see report 116870. Excluded OMS697779, 697804 OMS 698260 | July | 2011 | 2012Q1 | 2012 | 211:33596 | 258:80781 | ZN00258/080781 | NEWCASTLE | OH | Not Veg | 2011-07-16 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 6606.1654
| 802:82215 | 36 | 75.8505 | 54.83 | 2.107 | 54.83 | 19627 | 10477 | 698389 | 2011-07-15 21:45 | 2011-07-16 04:00 | 375 | 11kV | 30281 | 220 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 116868 5 fault operations Earth fault Faulty Arresters at UGOH pole JS-80341. Excluded OMS 697781, 697803 OMS 698389, 698391, 698393, 698395 | July | 2011 | 2012Q1 | 2012 | 234:2006 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2011-07-15 | N | 137.6409 | N | 4 | N | N | 1.1101 | 39.4971 | 22128.4617
| 802:82220 | 64 | 28.5048 | 46.22 | 0.44539 | 46.22 | 20119 | 16105 | 697856 | 2011-07-16 09:55 | 2011-07-16 11:30 | 95 | 11kV | 14884.9333 | 157 | HV | Staff Operation | Utility Process Issue | DC Transformer | Unplanned | No Weather Impact | N | At S2975 Cliff Lavender No1 Tx tripped in IT receive. Cause: common IT relay at S2473 North Sydney. See OMS 698471 697856 697859 Protection Abnormal at the time of interruption | July | 2011 | 2012Q1 | 2012 | ZN2473:PA15 | ZN35400:PA61 | ZN35400/000061 | NORTH SYDNEY | UG | Not Veg | 2011-07-16 | N | 94.8085 | N | 5 | N | N | 1.1101 | 39.4971 | 10877.4702
| 802:82225 | 109 | 137.4759 | 54.53 | 1.2612 | 54.53 | 19634 | 10523 | 698396 | 2011-07-16 12:00 | 2011-07-16 13:50 | 110 | 11kV | 2530 | 23 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 116875 Emergency repairs after fault on Friday evening. See OMS 698389, 698391, 698393, 698395 | July | 2011 | 2012Q1 | 2012 | 234:2006 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2011-07-16 | N | 110 | N | 5 | N | N | 1.1101 | 39.4971 | 1848.8494
| ZN36300:PA1 | 831 | 506.3731 | 36.17 | 0.60935 | 36.17 | 18733 | 1402 | 697923 | 2011-07-16 13:49 | 2011-07-16 14:43 | 54 | 11kV | 28733 | 547 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn340 Botany Pa8 Fdr tripped on Bph Earth Fault EFI Signals" 11kv trip, ZE Remarks: Suspect UG fault btw S35692 & S6803. Sw/B closed @ S8559 Luland Booralee See 698217,8 exclude 697923 From To DC restored? Time Zn340:Pa8 S35692 1 14:36 S8559 S6803 7 14:43 | July | 2011 | 2012Q1 | 2012 | ZN340:PA8 | ZN340:PA8 | ZN00340/000008 | BAYSIDE | UG | Not Veg | 2011-07-16 | N | 52.5283 | N | 5 | N | N | 1.1101 | 39.4971 | 20997.2289
| ZN36300:PA11 | 2969 | 2692.3508 | 35.73 | 0.90682 | 35.73 | 19968 | 14629 | 697978 | 2011-07-16 19:03 | 2011-07-16 22:00 | 177 | 11kV | 101019 | 693 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Cold <10C | N | Section of Panel 21 ex Berowra Zone Recloser 3228 Berowra Pump tripped reclosed tripped and locked out Cause: 11kV ugoh has failed on section of feeder from S7341 to AB2385 tee PT1489. See OMS 699768 699785 699784 | July | 2011 | 2012Q1 | 2012 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | Unknown | Unknown | 2011-07-16 | N | 145.7706 | N | 5 | N | N | 1.1101 | 39.4971 | 73821.7056
| ZN36300:PA13 | 1307 | 742.171 | 34.97 | 0.56784 | 34.97 | 19566 | 9665 | 698335 | 2011-07-18 03:01 | 2011-07-18 04:03 | 62 | 11kV | 129016 | 2234 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn63o:Pa38 tripped Relays: O, Timed O/C, EFault, EFI Signals: 11kv trip, Tx6GE Field EFI: S2286 S7879 Remarks: Fdr fault btw S7879 to S2163 to S46275 See 698335,6,7 From To Restored DC Time Zn630:38 S7879SwB 2 3:49 S4451 S46275SwA 4 3:55 S2387SwD S2163SwA 6 4:03 | July | 2011 | 2012Q1 | 2012 | ZN630:PA38 | ZN630:PA38 | ZN00630/000038 | BAYSIDE | UG | Not Veg | 2011-07-18 | N | 57.7511 | N | 2 | N | N | 1.1101 | 39.4971 | 94281.0875
| ZN36300:PA17 | 841 | 882.8392 | 42.18 | 1.0497 | 42.18 | 20325 | 19291 | 698725 | 2011-07-18 21:51 | 2011-07-19 01:20 | 209 | 11kV | 5615 | 55 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At Recloser 44604 the circuit breaker tripped, reclosed twice, tripped and locked out on B phase OC, IOC, lockout. 11kV wire came off pin insulator and fell off crossarm between LB.44637 and CCT transition connection - 16 bays west of PT.12676 | July | 2011 | 2012Q1 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2011-07-18 | N | 102.0909 | N | 2 | N | N | 1.1101 | 39.4971 | 4103.2764
| ZN36300:PA18 | 328 | 782.4469 | #N/A | 2.3855 | 39.4971 | 19643 | 10674 | 698732 | 2011-07-19 07:42 | 2011-07-19 10:00 | 138 | 11kV | 34500 | 250 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 116906 A Phase No protection operation. Burnt footpath phase tapping line side of ABS 40136. Excluded OMS 698732, 698775, 698915 OMS 699573 | July | 2011 | 2012Q1 | 2012 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2011-07-19 | N | 138 | N | 5 | N | N | 1.1101 | 39.4971 | 25211.5824
| ZN36300:PA19 | 1408 | 1428.0926 | 36.49 | 1.0143 | 36.49 | 19380 | 8047 | 699937 | 2011-07-19 20:42 | 2011-07-19 20:47 | 5 | 11kV | 7845 | 1569 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At ZN.10999 Kogarah P-32 "Bent Willison" fdr tripped REMARKS: Fdr trpped while trying back section of P-12 outage (OMS #699079). Section isolated again and P-32 restored. | July | 2011 | 2012Q1 | 2012 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | OH | Veg | 2011-07-19 | N | 5 | N | 5 | N | N | 1.1101 | 39.4971 | 5732.8946
| ZN36300:PA3 | 2076 | 1829.0668 | 31.03 | 0.88105 | 31.03 | 20192 | 16836 | 699942 | 2011-07-19 21:12 | 2011-07-19 21:17 | 5 | 11kV | 10000 | 2000 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Rain Wind Storm | N | At ZN.10990 Arncliffe P-2 "Dowling Hurst" fdr tripped REMARKS: Fdr tripped while trying back section of P-12 outage (OMS #699079). | July | 2011 | 2012Q1 | 2012 | ZN10990:PA2 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | UG | Not Veg | 2011-07-19 | N | 5 | N | 5 | N | N | 1.1101 | 39.4971 | 7307.705
| ZN36300:PA5 | 1315 | 1359.1756 | 34.08 | 1.0336 | 34.08 | 19747 | 12419 | 699138 | 2011-07-19 18:51 | 2011-07-19 21:40 | 169 | 11kV | 125020 | 822 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | CC1: 22-"Refer to SOp" @Zn9252 Jannali Pa16 "Woronora" fdr tripped & locked out Signals - 11kv trip Relays - SEL Lockout Remarks - bond brunt of Zone side of AB35341 See 700314,8,9 699182 GIS 700321,4 Exclude 699145,1,38 From To DC restored Time Pa16 AB35341 1 20:42 IS35812 S48498 The Crescent Thorp 3 21:10 S9356 Mannikin Willaroo S9987 Warrangarree Wylah 7 21:40 | July | 2011 | 2012Q1 | 2012 | ZN9252:PA16 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Not Veg | 2011-07-19 | N | 152.0925 | N | 5 | N | N | 1.1101 | 39.4971 | 91360.9285
| ZN36300:PA7 | 479 | 314.5243 | 39.38 | 0.65663 | 39.38 | 20159 | 16390 | 699079 | 2011-07-19 17:31 | 2011-07-19 22:48 | 317.15 | 11kV | 529974.6833 | 2974 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | At ZN.10999 Kogarah P-12 "Queen Vic Washington" fdr tripped, closed, tripped & locked out. SIGNALS: 11kV trip. RELAYS: A phase overcurrent, reclose timing, lockout ABNORMAL: LB 49192 closed, Open bonds above AB31147 REMARKS: Lots of reports of causes from different locations. Found what appears to be a cracked insulator on tee off pole near LK30143 with burn marks on crossarm. Also found 11kV beyond AB31147 just touching crossarm. | July | 2011 | 2012Q1 | 2012 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Not Veg | 2011-07-19 | N | 178.2027 | N | 5 | N | N | 1.1101 | 39.4971 | 387289.867
| ZN36300:PA8 | 1567 | 1060.6422 | 33.44 | 0.67686 | 33.44 | 19040 | 4296 | 699220 | 2011-07-20 00:07 | 2011-07-20 00:50 | 43 | 11kV | 37625 | 875 | HV | Overload | Utility Process Issue | Feeder/Distributor U/G | Unplanned | Previous Storm | N | at S.1287 Revesby Panel 22 "Macarthur Revesby" fdr tripped, reclosed, tripped and locked out Signals - 11kv trip, zone earth Relays - A phase IOC and Timed Overcurrent, earth fault, reclose timing, lockout, EFi Remarks: Front line feeder fault from Panel 22 to S3939 Macarthur Revesby Related jobs:# #699372, 699220 | July | 2011 | 2012Q1 | 2012 | ZN1287:PA22 | ZN1287:PA22 | ZN01287/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-07-20 | N | 43 | N | 14 | N | N | 1.1101 | 39.4971 | 27495.2403
| ZN36300:PA9 | 1336 | 1042.2355 | 30.31 | 0.78012 | 30.31 | 19060 | 4405 | 699221 | 2011-07-20 00:10 | 2011-07-20 01:45 | 95 | 11kV | 12545 | 151 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S1673 Turramurra Panel 20 Tripped on Earth Fault and C phase IOC with EFI and 11kV trip Cause: Suspect UG fault in cable from S35245 Turramurra Wonga Wonga Sw B to S811 Pentacost Hwy Sw A to S7264 Karuah Katina SwA to S4724 Kurinhgai Wonga See OMS 699509 699510 699221 | July | 2011 | 2012Q1 | 2012 | ZN1673:PA20 | ZN1673:PA1 | ZN01673/000001 | KU-RING-GAI | UG | Not Veg | 2011-07-20 | N | 83.0795 | N | 14 | N | N | 1.1101 | 39.4971 | 9167.516
| ZN35800:PA1 | 2302 | 1417.2875 | 31.68 | 0.61568 | 31.68 | 18671 | 907 | 699242 | 2011-07-20 03:56 | 2011-07-20 05:59 | 123.0167 | 11kV | 977.4333 | 872 | HV | Arcing | Equipment Failure | Pole | Unplanned | Rain Light | N | pole arcing in front of 42 fairscene | July | 2011 | 2012Q1 | 2012 | ZN12570:PA12 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2011-07-20 | N | 1.1209 | N | 14 | N | N | 1.1101 | 39.4971 | 714.2795
| ZN35800:PA10 | 2350 | 2028.0302 | 43.88 | 0.86299 | 43.88 | 19391 | 8190 | 699256 | 2011-07-20 06:13 | 2011-07-20 11:13 | 300.0167 | 11kV | 140407.8 | 468 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | CC1: 22-"Refer to SOp" Recloser 40075 tripped after wattle tree fell over onto 11kV OH near PT.12890 | July | 2011 | 2012Q1 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2011-07-20 | N | 300.0167 | N | 14 | N | N | 1.1101 | 39.4971 | 102605.8789
| ZN35800:PA11 | 40 | 455.7835 | #N/A | 11.3946 | 39.4971 | 18589 | 120 | 699282 | 2011-07-20 07:15 | 2011-07-20 12:18 | 303 | 11kV | 124910 | 1962 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | At S.15014 Mona Vale, Panel 19L Fdr CB tripped on SEL, fault check, efi, 11kV trip, zone earth. Field efi down at S.16635. 11kV wire on ground O/S #40 Bungan Head Rd, Mona Vale. between UG/OH to S.16635 and PT.15281 | July | 2011 | 2012Q1 | 2012 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | OH | Not Veg | 2011-07-20 | N | 63.6646 | N | 14 | N | N | 1.1101 | 39.4971 | 91280.5438
| ZN35800:PA13 | 497 | 1015.7513 | 49.02 | 2.0438 | 49.02 | 20151 | 16341 | 699539 | 2011-07-20 10:33 | 2011-07-20 12:21 | 108 | 11kV | 120360 | 1120 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Feeder patrolled - nothing found Zn10994 Mortdale Pa31 fdr tripped on ACph IOC with Timed O/L Recloser timer and lockout 11kv trip See 699539 LV// 699549 GIS 701637 Exclude 699569 | July | 2011 | 2012Q1 | 2012 | ZN10994:PA31 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2011-07-20 | N | 107.4643 | N | 14 | N | N | 1.1101 | 39.4971 | 87955.538
| ZN35800:PA14 | 2213 | 1620.1725 | 39.11 | 0.73212 | 39.11 | 20049 | 15585 | 699643 | 2011-07-20 11:47 | 2011-07-20 13:49 | 122 | 11kV | 58714 | 504 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | At S.15009 Manly Panel 11 Fdr Cb tripped, reclosed and tripped , locked out on C phase IOC and timed OC, timing relay, lockout efi, fault check, #3 Tx fault check, 11kV trip, zone earth. Field efi down at S.17051. 11kV UG cable fault between S.17051 to S.15776 to S.46987. | July | 2011 | 2012Q1 | 2012 | ZN15009:PA11 | ZN15009:PA11 | ZN15009/000011 | NORTHERN BEACHES | UG | Not Veg | 2011-07-20 | N | 116.496 | N | 14 | N | N | 1.1101 | 39.4971 | 42906.4594
| ZN35800:PA15 | 1067 | 885.7886 | 40.54 | 0.83017 | 40.54 | 18571 | 50 | 699810 | 2011-07-20 14:35 | 2011-07-20 15:55 | 80 | 11kV | 80 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 116917 ap issued to repair live live dropper Excluded OMS 699810 OMS 700242 | July | 2011 | 2012Q1 | 2012 |  |  |  |  | OH | Not Veg | 2011-07-20 | N | 80 | N | 14 | N | N | 1.1101 | 39.4971 | 58.4616
| ZN35800:PA16 | 1506 | 1436.0743 | 45.07 | 0.95357 | 45.07 | 19015 | 4170 | 699723 | 2011-07-20 12:51 | 2011-07-20 15:59 | 188 | 11kV | 155468 | 894 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S12570 Avoca Section of panel 2 from R44982 tripped reclosed tripped and locked out on A and B phase ZOC. Cause: Suspect UG fault between HV UGOH and S18290 Kallaroo Kildare. See OMS 700408 700405 700403 699723 | July | 2011 | 2012Q1 | 2012 | ZN12570:PA2 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | UG | Not Veg | 2011-07-20 | N | 173.9016 | N | 14 | N | N | 1.1101 | 39.4971 | 113611.4289
| ZN35800:PA18 | 1411 | 1324.0364 | 51.26 | 0.93837 | 51.26 | 20177 | 16700 | 699926 | 2011-07-20 14:09 | 2011-07-20 16:57 | 168 | 11kV | 108192 | 644 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Section Panel 48 "Sub 10774 Mortdale Aux" feeder Remarks: 11kv bond burnt off at AB31311 Related jobs: #700233, 699836, 699926 | July | 2011 | 2012Q1 | 2012 | ZN10994:PA48 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2011-07-20 | N | 168 | N | 14 | N | N | 1.1101 | 39.4971 | 79063.5225
| ZN35800:PA19 | 547 | 484.368 | #N/A | 0.8855 | 39.4971 | 19096 | 4614 | 699811 | 2011-07-20 13:41 | 2011-07-20 17:10 | 209 | 11kV | 7153 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 116916 3 fault operations tree into mains ap issued to repair mains Excluded OMS 699811, 699812 OMS 700310, 700312 | July | 2011 | 2012Q1 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2011-07-20 | N | 125.4912 | N | 14 | N | N | 1.1101 | 39.4971 | 5227.2014
| ZN35800:PA2 | 1882 | 1171.8845 | 36.47 | 0.62268 | 36.47 | 18632 | 527 | 699711 | 2011-07-20 18:06 | 2011-07-20 19:35 | 89 | 11kV | 26522 | 298 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | 11kV bond burnt off UG/OH between L.22539 and S.16416 | July | 2011 | 2012Q1 | 2012 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2011-07-20 | N | 89 | N | 14 | N | N | 1.1101 | 39.4971 | 19381.4953
| ZN35800:PA21 | 327 | 473.098 | 50.61 | 1.4468 | 50.61 | 20248 | 17749 | 700243 | 2011-07-20 08:30 | 2011-07-20 19:40 | 670 | 11kV | 25460 | 38 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" 21/07/11 12:19 T52895: 11KV UG FEEDER FAULT FROM CP2552 RIFLE RANGE TO HV UGOH. Section of ZN1788 Matraville Pa30 from CP2552 to PT1993 & PT1238 DOp replaced HV fuse and tried back. HV fuse blow again Fault on the 11kv UGOH centre ph Switching tag left at CP2552 DOp Pennington advised David Hay Fault was found to be middle phase lightning arrestor on UGOH CE 21/07/11 See 701269 exclude 700243 700834 From To DC restored Time CP2552 PT1238, PT1993 2 19:40 | July | 2011 | 2012Q1 | 2012 | ZN1788:PA30 | ZN1788:PA44 | ZN01788/000044 | RANDWICK | OH | Not Veg | 2011-07-20 | N | 670 | N | 14 | N | N | 1.1101 | 39.4971 | 18605.4171
| ZN35800:PA22 | 1714 | 1159.9769 | 41.34 | 0.67677 | 41.34 | 19978 | 14672 | 700146 | 2011-07-20 23:05 | 2011-07-21 02:20 | 195 | 11kV | 92125 | 492 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Section of Panel 33 at S965 Pennant Hills Recloser 2691 Duneba Drive trippe don B and C phase Overcurrent Cause: Tree branch on 11kV mains near PT2108 Dons Quarry See OMS 700326 700323 700146 | July | 2011 | 2012Q1 | 2012 | ZN965:PA33 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2011-07-20 | N | 187.2459 | N | 14 | N | N | 1.1101 | 39.4971 | 67322.2328
| ZN35800:PA3 | 128 | 623.2591 | 55.61 | 4.8692 | 55.61 | 19883 | 13592 | 700155 | 2011-07-21 01:07 | 2011-07-21 03:25 | 138 | 11kV | 98760 | 844 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S398 Dulwich Hill the "Prospect Cant" fdr Panel 25 tripped. Earth leakage, EFI, 11kv trip, Zone Eth and No.4 Gorup Eth. Field EFIs: S7551, S4028, S2016, S4559 Remarks: 11kv UG cable fault from S4359 Wattle Cant to S35350 Dunkeld Cant to S1097 Hurlston Park RSL Related jobs: #700185, 700213, 700155 | July | 2011 | 2012Q1 | 2012 | ZN398:PA25 | ZN398:PA25 | ZN00398/000025 | INNER WEST | UG | Not Veg | 2011-07-21 | N | 117.0142 | N | 12 | N | N | 1.1101 | 39.4971 | 72170.8951
| ZN35800:PA4 | 950 | 937.6347 | 44.8 | 0.98698 | 44.8 | 20415 | 20231 | 700165 | 2011-07-21 06:25 | 2011-07-21 07:18 | 53 | 11kV | 68900 | 1300 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S965 Pennant Hills Panel 33 tripped on A and C phase O/C with reclose time delay lockout Cause: Tree on 11kV outside 24 Duneba Drive - Removed by DOp See OMS 700165 700166 | July | 2011 | 2012Q1 | 2012 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2011-07-21 | N | 53 | N | 12 | N | N | 1.1101 | 39.4971 | 50350.0878
| ZN35800:PA6 | 618 | 757.1204 | 48.39 | 1.2251 | 48.39 | 19703 | 11712 | 700162 | 2011-07-21 06:49 | 2011-07-21 08:40 | 111 | 11kV | 7548 | 68 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | At S12570 Avoca Section of panel 2 Fromm AB44983 Cause: CB44983 arcing badly and defective Abnormal Switching- CB40459 Closed CP40052 Open See OMS 700570 700168 700162 | July | 2011 | 2012Q1 | 2012 | ZN12570:PA2 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2011-07-21 | N | 111 | N | 12 | N | N | 1.1101 | 39.4971 | 5515.8558
| ZN35800:PA7 | 1262 | 1207.0442 | 40.87 | 0.95645 | 40.87 | 18568 | 11 | 700280 | 2011-07-21 11:12 | 2011-07-21 12:14 | 62 | 11kV | 46128 | 744 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | BOND BURNT OFF AT AB.26297 | July | 2011 | 2012Q1 | 2012 | ZN15011:PA6 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | OH | Not Veg | 2011-07-21 | N | 62 | N | 12 | N | N | 1.1101 | 39.4971 | 33708.9819
| ZN35800:PA9 | 348 | 653.5579 | 41.49 | 1.878 | 41.49 | 20254 | 17863 | 700436 | 2011-07-21 11:39 | 2011-07-21 14:15 | 156 | 11kV | 936 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | Aph HDO was blown. When atempting to restore 2nd ph blew indicating defective transformer. Section of Pa1 from ZN10096 Rockdale Also top tx is badly rusted restored via LV// links closed in turret 417 & IDTs @ PT10050 See 701664 700462 exclude 700436 | July | 2011 | 2012Q1 | 2012 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2011-07-21 | N | 156 | N | 12 | N | N | 1.1101 | 39.4971 | 684.0012
| ZN1850:PA31 | 246 | 211.7097 | 30.06 | 0.86061 | 30.06 | 19302 | 7329 | 700717 | 2011-07-21 15:16 | 2011-07-21 17:35 | 139 | 11kV | 89974 | 736 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14114 Wamberal 11kv VCB Pnl.10 tripped on: Bassler relay EFI, 11kv Trip 50tb IOC Remarks: 11kv Feeder fault from S.18824 to AB41727 to LK41728 tee PT.11665 | July | 2011 | 2012Q1 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | UG | Not Veg | 2011-07-21 | N | 122.2473 | N | 12 | N | N | 1.1101 | 39.4971 | 65750.3454
| ZN1850:PA32 | 740 | 728.3935 | 31.51 | 0.98432 | 31.51 | 19746 | 12416 | 700809 | 2011-07-21 16:33 | 2011-07-21 17:59 | 85.75 | 11kV | 6685 | 78 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 116923 A Phase DOLF : 20Amp. LA replaced | July | 2011 | 2012Q1 | 2012 | 523:33503 | 523:33503 | ZN00523/033503 | SINGLETON | OH | Not Veg | 2011-07-21 | N | 85.7051 | N | 12 | N | N | 1.1101 | 39.4971 | 4885.2008
| ZN1850:PA33 | 399 | 500.3281 | 37.61 | 1.254 | 37.61 | 19059 | 4402 | 700687 | 2011-07-21 14:49 | 2011-07-21 18:50 | 241 | 11kV | 24563 | 271 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Recloser 1126 tripped, reclosed and tripped on OC.11kV OH on ground adj. to PT.15242 | July | 2011 | 2012Q1 | 2012 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2011-07-21 | N | 90.6384 | N | 12 | N | N | 1.1101 | 39.4971 | 17949.9159
| ZN1850:PA40 | 1042 | 1286.7694 | 41.22 | 1.2349 | 41.22 | 20073 | 15800 | 700839 | 2011-07-21 17:13 | 2011-07-21 20:05 | 171.55 | 11kV | 197282.5 | 1150 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1648 Enfield Pa16 fdr tripped on EFault, EFI EFI's nil Suspect UG fault btw Zn1648:Pa16 to S4634 From To Restored DC Time S5217 S4634 & S1840 & S319 9 20:05 | July | 2011 | 2012Q1 | 2012 | ZN1648:PA16 | ZN4853:PA16 | ZN04853/000016 | BURWOOD | UG | Not Veg | 2011-07-21 | N | 171.55 | N | 12 | N | N | 1.1101 | 39.4971 | 144168.2322
| ZN1850:PA41 | 1271 | 984.3348 | 34.93 | 0.77446 | 34.93 | 20299 | 18954 | 700952 | 2011-07-21 19:37 | 2011-07-21 20:05 | 28 | 11kV | 924 | 33 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Suspect LV// btw S3490-2 & S1840-2 based on cust calls Zn1648:Pa16 tripped on EFault, EFI Feild EFI's operated Nil Suspect UG cable fault Zn1648:Pa16 to S4634 See 701703 LV// 700952 From To DC restored Time S5217 S4634 S1840 S319 9 2005 | July | 2011 | 2012Q1 | 2012 | ZN1648:PA15 | ZN4853:PA4 | ZN04853/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-07-21 | N | 28 | N | 12 | N | N | 1.1101 | 39.4971 | 675.2319
| ZN1850:PA42 | 364 | 1438.0765 | 54.39 | 3.9508 | 54.39 | 19612 | 10333 | 700917 | 2011-07-21 18:39 | 2011-07-21 20:25 | 106 | 11kV | 47761 | 513 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn9550:Pa35 tripped on 50 TN EFC Relay, 51 N EFault Relay & EFI EFI's S9370 Suspect UG fdr fault from S9370 to S9278 to PT9159 See 701690 701693 LV// 700923 exclude 700917 From To DC's Restored Time Zn9037:Pa35 S9370 1 2004 S9899 S9370 S9278 8 2009 PT9159 via LV// 1 2025 | July | 2011 | 2012Q1 | 2012 | ZN9550:PA35 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | UG | Not Veg | 2011-07-21 | N | 93.1014 | N | 12 | N | N | 1.1101 | 39.4971 | 34902.3301
| ZN1850:PA44 | 182 | 164.5365 | 29.28 | 0.90405 | 29.28 | 20278 | 18155 | 701006 | 2011-07-21 21:29 | 2011-07-21 22:46 | 77 | 11kV | 97398 | 1314 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7481:Pa9 fdr tripped Relays - Pa9L Cph OC EFault Signals- Pa9L EFI, Tx11 GE EFI - S4199 S8111 Remarks - UG fdr fault btw S8111 & S8012 See 701336 701339 exclude 701006 | July | 2011 | 2012Q1 | 2012 | ZN7481:PA9 | ZN7481:PA9 | ZN07481/000009 | SYDNEY | UG | Not Veg | 2011-07-21 | N | 74.1233 | N | 12 | N | N | 1.1101 | 39.4971 | 71175.5856
| ZN1850:PA45 | 353 | 392.4781 | 42.21 | 1.1118 | 42.21 | 19485 | 8992 | 701203 | 2011-07-22 09:17 | 2011-07-22 10:40 | 83 | 11kV | 71067 | 1008 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @ S116 Leichhardt Panel 42 'S682 North St Etc' feeder tripped on Relays - Earth Fault, EFI Signals - 11KV trip, ZE TX3 GE NO Field EFI's operated Remarks: 11KV UG Feeder fault from S116 Leichhardt (Panel 42) to S682 North Ave to S3491 Norton Marion Related jobs: #704289, 704379, 704287, 701203, 701208, 701221, 701227 | July | 2011 | 2012Q1 | 2012 | ZN116:PA42 | ZN116:PA14 | ZN00116/000014 | INNER WEST | UG | Not Veg | 2011-07-22 | N | 70.503 | N | 7 | N | N | 1.1101 | 39.4971 | 51933.6675
| ZN15011:PA1 | 38 | 1103.7633 | #N/A | 29.0464 | 39.4971 | 19080 | 4512 | 702843 | 2011-07-22 10:20 | 2011-07-22 12:20 | 120 | 11kV | 1680 | 14 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 116930 EMERGENCY ISOLATION TO REPLACE POLE SM-80069 | July | 2011 | 2012Q1 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2011-07-22 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 1227.6944
| ZN15011:PA10 | 1609 | 2060.7452 | 38.04 | 1.2808 | 38.04 | 20162 | 16437 | 701120 | 2011-07-22 08:00 | 2011-07-22 13:40 | 340 | 11kV | 1360 | 4 | HV | Vegetation Blow/Fall In | Vegetation | Fuse | Unplanned | Rain Heavy | N | LID 116932 A & B phase DOLF : 10Amp. Removed tree branch from mains. Excluded OMS 701120 OMS 702623 | July | 2011 | 2012Q1 | 2012 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2011-07-22 | N | 340 | N | 7 | N | N | 1.1101 | 39.4971 | 993.8479
| ZN15011:PA2 | 1722 | 2346.5432 | 39.06 | 1.3627 | 39.06 | 19089 | 4563 | 701493 | 2011-07-22 14:36 | 2011-07-22 15:05 | 29 | 11kV | 1392 | 48 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | UGOH | Unplanned | Unselected | N | Section of Pnl.10 ex Zn.14144 Wamberal interrupted by DOp for testers to break HV UGOH away from AB41727 for clearances. Abnormal Switching: Feeder O/O/S between S.18824 - AB41727 - LK41728. AB41247 Closed - LB40973 Closed Remarks: for testers to test UG fault OH broken away from UGOH. see #703378 for fault at 15:16 21/7/11 | July | 2011 | 2012Q1 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2011-07-22 | N | 29 | N | 7 | N | N | 1.1101 | 39.4971 | 1017.2325
| ZN15011:PA4 | 1239 | 1180.7333 | 34.28 | 0.95297 | 34.28 | 20056 | 15646 | 701438 | 2011-07-22 13:19 | 2011-07-22 15:45 | 146 | 11kV | 154429 | 1532 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @S2196 Milperra Panel 5 'S8696 MArigold Armour No.4' feeder tripped & locked out on - Relays - EF, EFI, fault check, lockout Signals - 11KV trip, ZE, No 3 TX GE Remarks: Suspect UG cable fault S.8696 Marigold Amour No4 to S.5487 Armentieres Av to S.47525 Horsley Beacon tee to PT1679 Sinai Av Related jobs: #703134, 703133, 703135, 703130, 703129, 701438 | July | 2011 | 2012Q1 | 2012 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-07-22 | N | 100.8022 | N | 7 | N | N | 1.1101 | 39.4971 | 112852.1583
| ZN15011:PA6 | 66 | 805.0592 | 46.09 | 12.1979 | 46.09 | 18917 | 3215 | 701506 | 2011-07-22 14:46 | 2011-07-22 16:45 | 119 | 11kV | 7378 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT12100 Morrison Patrick - HV Fuse Centre Phase Blown (31.5 BB Batch #1007) Remarks: Fuse Fatigue | July | 2011 | 2012Q1 | 2012 | ZN12570:PA8 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Not Veg | 2011-07-22 | N | 119 | N | 7 | N | N | 1.1101 | 39.4971 | 5391.6248
| ZN15011:PA8 | 256 | 1445.8514 | 45.19 | 5.6479 | 45.19 | 20174 | 16675 | 702669 | 2011-07-22 23:06 | 2011-07-22 23:36 | 30 | 11kV | 67743 | 2487 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn901 Surry Hills Pa11 tripped Relays-EFI EFault Signals - 11kv trip, ZEarth Tx3GE EFI's S6382 S35657 S34 S2216 UG cable fault btw S2216 & S7466 See 702669 702671 From To Restored DC Time Zn901:Pa11 S2216 & N/O's 6 23:33 S7466 S7466 1 23:36 | July | 2011 | 2012Q1 | 2012 | ZN901:PA11 | ZN901:PA27 | ZN00901/000027 | SYDNEY | UG | Not Veg | 2011-07-22 | N | 27.2388 | N | 7 | N | N | 1.1101 | 39.4971 | 49504.5863
| ZN5959:PA3D | 52 | 693.7323 | #N/A | 13.341 | 39.4971 | 18815 | 2249 | 701827 | 2011-07-23 01:05 | 2011-07-23 02:40 | 95 | 11kV | 124929 | 2109 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn10995:Pa7 tripped, reclosed, tripped and locked out Relays - Aph O/C, reclose timing, lockout Signals - 11kv trip MVA into pole 11kv mains nr PT10439, came off pin insulator and rested together on cross arm. See 702782 702785 702787 exclude 701827 From To Restored DC Time Pa7 S10124 14 0200 AB31012 S10862 2 0214 | July | 2011 | 2012Q1 | 2012 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2011-07-23 | N | 59.2361 | N | 3 | N | N | 1.1101 | 39.4971 | 91294.4284
| ZN15005:PA10 | 741 | 2074.2304 | 37.77 | 2.7992 | 37.77 | 19782 | 12640 | 701866 | 2011-07-23 08:18 | 2011-07-23 11:03 | 165 | 11kV | 330 | 2 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Rain Light | N | S.18540 Pile Pacific 0.3 no.2 - HV Cb operated Remarks: Water ingress into OC relay at kiosk, repaired by Tpe, restored by DOp | July | 2011 | 2012Q1 | 2012 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | Unknown | Not Veg | 2011-07-23 | N | 165 | N | 3 | N | N | 1.1101 | 39.4971 | 241.1543
| ZN15005:PA12 | 1450 | 1411.0071 | 32.27 | 0.97311 | 32.27 | 20008 | 14993 | 702135 | 2011-07-23 19:55 | 2011-07-23 21:20 | 85 | 11kV | 99853 | 1209 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.9 feeder tripped / reclosed / tripped and locked out on: Basler relay -1.2.1, target 51N, Minor alarm, trip, EFI, Fault Check, reclose, lockout, timing. Field EFI's: S.18620, S14753, S14366 Remarks: 11kV fedder failed from S.14366 Sw6375 to S.14551 Sw A to S14547 Sw 6569 | July | 2011 | 2012Q1 | 2012 | ZN14891:PA9 | ZN14891:PA9 | ZN14891/000009 | CENTRAL COAST | UG | Not Veg | 2011-07-23 | N | 82.5914 | N | 3 | N | N | 1.1101 | 39.4971 | 72969.6272
| ZN15005:PA2 | 1976 | 2040.9787 | 35.61 | 1.0329 | 35.61 | 20082 | 15875 | 702229 | 2011-07-24 10:38 | 2011-07-24 11:19 | 41 | 11kV | 49528 | 1208 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | Zn9550:Pa31 triped on electronic O/C relay 50T ABC 50 TN Field EFI S9829 S832 S9006 See 702795 702229 From To Restored DC TIme Pa31 SwBS9500 10 11:19 S9462 SwCS9500 1 11:20 | July | 2011 | 2012Q1 | 2012 | ZN9550:PA31 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | UG | Not Veg | 2011-07-24 | N | 41 | N | 2 | N | N | 1.1101 | 39.4971 | 36193.6016
| ZN15005:PA4 | 1242 | 1169.2308 | 31.36 | 0.94141 | 31.36 | 19082 | 4517 | 702243 | 2011-07-24 11:27 | 2011-07-24 14:35 | 188 | 11kV | 188 | 1 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | S.18165 Donnison Workcover - HV CB opened - No protection relays operated Remarks: 3 Phase OC relay had water ingress. Relays cleaned and dryed out, supply restored | July | 2011 | 2012Q1 | 2012 | ZN12650:PA10 | ZN12650:PA10 | ZN12650/000010 | CENTRAL COAST | Unknown | Not Veg | 2011-07-24 | N | 188 | N | 2 | N | N | 1.1101 | 39.4971 | 137.3849
| ZN15005:PA6 | 1279 | 1192.5381 | 31.66 | 0.9324 | 31.66 | 20062 | 15715 | 702386 | 2011-07-25 05:17 | 2011-07-25 09:20 | 243 | 11kV | 370209 | 1659 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 116951 2 fault operations 3 Phase Instantaneous Overcurrent, Overcurrent. 11kv ugoh to sw 28343 at sub 28345 glendale business park on pole iu-50786 failed explosivley. Excluded OMS 702386, 702387, 702388, 702389 & 702390, 702425, 702421 702429, 703193, 703196 OMS 710097, 710098 | July | 2011 | 2012Q1 | 2012 | 224:80341 | 224:80341 | ZN00224/080341 | LAKE MACQUARIE | Unknown | Unknown | 2011-07-25 | N | 223.1519 | N | 4 | N | N | 1.1101 | 39.4971 | 270537.8179
| ZN15005:PA8 | 1603 | 1837.1505 | 34.01 | 1.1461 | 34.01 | 19544 | 9534 | 702512 | 2011-07-25 09:11 | 2011-07-25 11:05 | 114 | 11kV | 179803.7333 | 1955 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn9700:Pa11 tripped reclosed & locked out Relays: Aph IOC, timed O/C, timing relay, lockout relay, fault check relay, EFI Signals: 11kv trip ZE, Tx3GE EFI's: S9518 S9325 S9448 S9340 S9054 S9359 S9111 Suspect UG fault btw S9394 to S9054 to PT9583 See 703222 703217 703214 LV// 702527 GIS 702542 702579 Exclude 702512 From To Restored DC Time Pa11 S9394 8 10:02 S9394 S9111 -8 Pa11 S9394 8 10:29 S9544 S9054 12 10:50 LV// PT9583 1 11:05 | July | 2011 | 2012Q1 | 2012 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | UG | Not Veg | 2011-07-25 | N | 91.9712 | N | 4 | N | N | 1.1101 | 39.4971 | 131395.265
| ZN12690:PA1 | 3 | 188.6816 | 61.48 | 62.8939 | 61.48 | 18570 | 31 | 702873 | 2011-07-25 15:25 | 2011-07-25 16:25 | 60 | 11kV | 9720 | 162 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | No LID report Interruption to re-tie conductoras per Disconnection Switching: K0540 Excluded OMS 702873 OMS 703246 | July | 2011 | 2012Q1 | 2012 | 222:2014 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2011-07-25 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 7103.0893
| ZN12690:PA10 | 725 | 491.3726 | 32.05 | 0.67776 | 32.05 | 19102 | 4647 | 702955 | 2011-07-25 18:45 | 2011-07-25 21:07 | 142 | 11kV | 9088 | 64 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | Unselected | N | PT.11786 Lurline Bourke - All Dist interrupted Remarks: interrupted for safety by DOp to allow cross arm replacement after car hit pole opposite 18 Lurline St Umina. | July | 2011 | 2012Q1 | 2012 | ZN12640:PA19 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2011-07-25 | N | 142 | N | 4 | N | N | 1.1101 | 39.4971 | 6641.2423
| ZN12690:PA11 | 10 | 903.3856 | 39.91 | 90.3386 | 39.91 | 19702 | 11690 | 703553 | 2011-07-26 22:55 | 2011-07-26 23:50 | 55 | 11kV | 2585 | 47 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 116963 No protection operation. Fdr isolated to replace insulators on 33kV Fdr at pole JT-40108 | July | 2011 | 2012Q1 | 2012 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2011-07-26 | N | 55 | N | 1 | N | N | 1.1101 | 39.4971 | 1889.0418
| ZN12690:PA12 | 1087 | 1226.1376 | 46.4 | 1.128 | 46.4 | 18782 | 1948 | 703629 | 2011-07-27 09:34 | 2011-07-27 10:15 | 41 | 11kV | 82 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 116965 Single phase DOLF : 10Amp. Excluded OMS 703629 OMS 704209 | July | 2011 | 2012Q1 | 2012 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2011-07-27 | N | 41 | N | 8 | N | N | 1.1101 | 39.4971 | 59.9232
| ZN12690:PA14 | 239 | 247.0466 | 36.79 | 1.0337 | 36.79 | 18692 | 1078 | 703675 | 2011-07-27 10:19 | 2011-07-27 12:15 | 116 | 11kV | 232 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 116966 Burnt up live line clamp at sub 51397. Excluded OMS 703675 OMS 704232 | July | 2011 | 2012Q1 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2011-07-27 | N | 116 | N | 8 | N | N | 1.1101 | 39.4971 | 169.5388
| ZN12690:PA16 | 344 | 1079.5437 | 43.3 | 3.1382 | 43.3 | 19458 | 8773 | 703734 | 2011-07-27 11:03 | 2011-07-27 12:15 | 72 | 11kV | 72 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 116968 C Phase DOLF : 16Amp. Excluded OMS 703734 OMS 704217 | July | 2011 | 2012Q1 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2011-07-27 | N | 72 | N | 8 | N | N | 1.1101 | 39.4971 | 52.6155
| ZN12690:PA17 | 145 | 1126.7348 | #N/A | 7.7706 | 39.4971 | 20362 | 19859 | 703857 | 2011-07-27 12:55 | 2011-07-27 20:00 | 425 | 11kV | 38324 | 276 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Section of 11kV interrupted by CB tripping at TCAT 14084 Wise Ferry Ingoola - Ex Pnl.2 Peats Ridge Remarks: 2 bays of 11kV down on Wise Ferry Rd | July | 2011 | 2012Q1 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2011-07-27 | N | 138.8551 | N | 8 | N | N | 1.1101 | 39.4971 | 28006.0488
| ZN12690:PA19 | 1226 | 3318.5579 | 45.27 | 2.7068 | 45.27 | 20363 | 19860 | 704238 | 2011-07-27 20:34 | 2011-07-27 21:00 | 26 | 11kV | 4966 | 191 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Recloser / Sectionaliser | Unplanned | Unselected | N | Section of 11kV from REC 45013 Gunderman was interrupted to restore supply from Ausgrid side. Ex Pnl.2 Peats Ridge See Previous interruption # 704224 | July | 2011 | 2012Q1 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2011-07-27 | N | 26 | N | 8 | N | N | 1.1101 | 39.4971 | 3629.0063
| ZN12690:PA22 | 422 | 1122.0937 | 54.86 | 2.659 | 54.86 | 19548 | 9592 | 704128 | 2011-07-27 19:47 | 2011-07-27 21:37 | 110 | 11kV | 41853 | 1280 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | @Zn9252 Jannali Panel 8 Toronto Buller No.2 fdr tripped and reclosed. Signals:-11kv trip, Zone Earth, TX3 Group earth Relays: A&C instantanious, lockout, timing relay, EFI Remarks: After trip and reclose 11kv bond on AB35115 open circuit. Dop patrolled the rest of the feeder, feeder was closed back in from Sub 9530 Green oyster Sw/A N/O. 11kv UGOH found to have open a bond on to Sub 9204 The Circle of Seventh. Related jobs: #704816, 704815, 704814, 704128, 704136, 704140, 70413 | July | 2011 | 2012Q1 | 2012 | ZN9252:PA8 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2011-07-27 | N | 32.6977 | N | 8 | N | N | 1.1101 | 39.4971 | 30584.9379
| ZN12690:PA24 | 953 | 893.8813 | 34.65 | 0.93797 | 34.65 | 19390 | 8177 | 704021 | 2011-07-27 22:00 | 2011-07-27 23:45 | 105 | 11kV | 6615 | 63 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Section of 11kV feeder from REC 45117 Glenning Valley to LK42212 to LB42219 tee PT11881, PT12121, PT13334, PT12516 was interrupted for repairs after car hit pole. Ex Pnl.24 Berkeley Vale | July | 2011 | 2012Q1 | 2012 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2011-07-27 | N | 105 | N | 8 | N | N | 1.1101 | 39.4971 | 4834.0469
| ZN12690:PA26 | 325 | 1066.8549 | 58.92 | 3.2826 | 58.92 | 19206 | 5877 | 704167 | 2011-07-27 23:28 | 2011-07-28 00:10 | 42 | 11kV | 58758 | 1399 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 116972 Instantaneous Earth fault, Instantaneous Overcurrent Cap bank prot TIE > & TI >. Cap bank left isolated at 34449. Excluded oms 704167 (Times) OMS 704205 | July | 2011 | 2012Q1 | 2012 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | Unknown | Not Veg | 2011-07-27 | N | 42 | N | 8 | N | N | 1.1101 | 39.4971 | 42938.6133
| ZN12690:PA3 | 736 | 503.1867 | 36.54 | 0.68368 | 36.54 | 19559 | 9624 | 704276 | 2011-07-28 09:04 | 2011-07-28 10:15 | 71 | 11kV | 30440 | 660 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S262 Marrickville 11kv trip Zone Earth #3 tx earth. Panel 27 The Coronation Park Fdr tripped on Earth Fault with EFI and fault check Remarks: Suspect UG cable fault Related jobs: #704776, 704786, 704781, 704752, 704753, 704751, 704276, 704281, 704305, 704313 | July | 2011 | 2012Q1 | 2012 | ZN262:PA27 | ZN262:PA27 | ZN00262/000027 | INNER WEST | UG | Not Veg | 2011-07-28 | N | 46.1212 | N | 5 | N | N | 1.1101 | 39.4971 | 22244.6542
| ZN12690:PA4 | 11 | 1039.9546 | 40 | 94.5413 | 40 | 19308 | 7347 | 704197 | 2011-07-28 07:16 | 2011-07-28 11:15 | 239 | 11kV | 104832 | 1067 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 116973 2 fault operations 3 phase Earth fault car hit pole hu-67011 rego silver mazda AQA 56Q (car left scene report from cusyt) the broadway/the trongate killingworth causing 11kv wire down high into low. Excluded OMS 704197, 704204, 704236. OMS 704915, 704918 | July | 2011 | 2012Q1 | 2012 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2011-07-28 | N | 98.2493 | N | 5 | N | N | 1.1101 | 39.4971 | 76608.1336
| ZN12690:PA6 | 988 | 830.9568 | 33.97 | 0.84105 | 33.97 | 19552 | 9599 | 704176 | 2011-07-28 06:15 | 2011-07-28 11:35 | 320 | 11kV | 33635 | 205 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Cold <10C | N | LID 116974 3 fault operations A & B Phase Overcurrent Excluded OMS 704191 OMS 704895, 704900, 704901 | July | 2011 | 2012Q1 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2011-07-28 | N | 164.0732 | N | 5 | N | N | 1.1101 | 39.4971 | 24579.4659
| ZN12690:PA7 | 877 | 918.0089 | 37.86 | 1.0468 | 37.86 | 19103 | 4655 | 704509 | 2011-07-28 13:40 | 2011-07-28 14:30 | 50 | 11kV | 100 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 116980 line fuse 40749 opened for clearance on 66kv fdr 6018. Eccluded OMS No 704509, 704515 OMS 704911 | July | 2011 | 2012Q1 | 2012 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | Unknown | Unknown | 2011-07-28 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
| ZN12690:PA8 | 986 | 670.7785 | 32.95 | 0.6803 | 32.95 | 18638 | 586 | 704713 | 2011-07-28 22:40 | 2011-07-29 00:20 | 100 | 11kV | 800 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 116984 A Phase DOLF : 16Amp. 247 Volts. 3, 45, 25 amps Excluded OMS 704713 OMS 704767 | July | 2011 | 2012Q1 | 2012 | 507:80931 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2011-07-28 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 584.6164
| ZN2400:PA11 | 707 | 694.8039 | 40.69 | 0.98275 | 40.69 | 18968 | 3576 | 705715 | 2011-07-29 11:00 | 2011-07-29 12:00 | 60 | 11kV | 540 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 116991 NO OMS NUMBER FAULT FOUND BY POLE INSPECTOR. NO PROTECTION. Mains fell on crossarm at pole DN-20220. | July | 2011 | 2012Q1 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2011-07-29 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 394.6161
| ZN2400:PA13 | 211 | 550.0822 | 54.01 | 2.607 | 54.01 | 19990 | 14892 | 705048 | 2011-07-29 15:08 | 2011-07-29 15:54 | 46.1333 | 11kV | 17715.2 | 384 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.3154 St Ives, Panel 25 Fdr CB tripped, reclosed, tripped and locked out on C phase IOC and Timed OC, lockout and timing relays. Large tree branch on OH O/S #64 Ayres Rd, St Ives | July | 2011 | 2012Q1 | 2012 | ZN3154:PA25 | ZN3154:PA25 | ZN03154/000025 | KU-RING-GAI | OH | Veg | 2011-07-29 | N | 46.1333 | N | 3 | N | N | 1.1101 | 39.4971 | 12945.7457
| ZN2400:PA15 | 1317 | 1149.6099 | 29.76 | 0.8729 | 29.76 | 20408 | 20195 | 705117 | 2011-07-29 17:55 | 2011-07-29 18:20 | 25 | 11kV | 1075 | 43 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 116996 No protection operations. Fdr isolated to repair insulator at pole EU-94049 under A/P. OMS # 116996 | July | 2011 | 2012Q1 | 2012 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2011-07-29 | N | 25 | N | 3 | N | N | 1.1101 | 39.4971 | 785.5783
| ZN2400:PA18 | 1368 | 1482.5687 | 35.41 | 1.0837 | 35.41 | 19320 | 7463 | 705197 | 2011-07-30 08:40 | 2011-07-30 11:30 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117002 Single phase DOLF : 10Amp. Excluded OMS 705197 OMS705682 | July | 2011 | 2012Q1 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-07-30 | N | 170 | N | 4 | N | N | 1.1101 | 39.4971 | 124.231
| ZN2400:PA21 | 1521 | 1498.4031 | 34.38 | 0.98514 | 34.38 | 19047 | 4360 | 705290 | 2011-07-30 13:43 | 2011-07-30 14:05 | 22 | 11kV | 22 | 1 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117003 A & B Phase DOLF : 10Amp. Excluded OMS 705290 OMS 705728 | July | 2011 | 2012Q1 | 2012 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2011-07-30 | N | 22 | N | 4 | N | N | 1.1101 | 39.4971 | 16.077
| ZN2400:PA22 | 1356 | 1168.9902 | 33.99 | 0.86209 | 33.99 | 19607 | 10277 | 705296 | 2011-07-30 14:33 | 2011-07-30 15:06 | 33 | 11kV | 92070 | 2790 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Unselected | N | @Zn10995 Riverwood 11kv fdr Pa7 tripped on Bph leakage EFI Note Sel and recloser were non auto for reconnect swithcing REF scada log Field EFI" S10236 S10970 Abnormal: S10236SwB closed USL30565 Open See D/R 272612 From To DC restored Time Zn10995:Pa7 USL31565 15:06 See 705660 exclude 705296 705299 | July | 2011 | 2012Q1 | 2012 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Veg | 2011-07-30 | N | 33 | N | 4 | N | N | 1.1101 | 39.4971 | 67282.0404
| ZN2400:PA23 | 333 | 577.5197 | 61.13 | 1.7343 | 61.13 | 19979 | 14712 | 705341 | 2011-07-30 17:58 | 2011-07-30 20:00 | 122 | 11kV | 122 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117004 Single phase No protection operations. Sub isolated to repair broken HV dropper under A/P. Excluded OMS # 705341 OMS 705732 | July | 2011 | 2012Q1 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2011-07-30 | N | 122 | N | 4 | N | N | 1.1101 | 39.4971 | 89.154
| ZN2400:PA26 | 969 | 829.6241 | 29.97 | 0.85617 | 29.97 | 18998 | 3977 | 705494 | 2011-07-31 22:14 | 2011-08-01 00:19 | 125 | 11kV | 221456 | 1795 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | At S10994 Mortdale Panel 49 "Frederick Letitia" fdr tripped, reclosed, tripped and locked out Signals: 11kV trip, Zone earth, Group Earth Relays - A phase IOC, Earth Fault, EFI, Reclose Timer, Lockout Related jobs: #705627, 705624, 705494, 705496 | July | 2011 | 2012Q1 | 2012 | ZN10994:PA49 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | UG | Not Veg | 2011-07-31 | N | 123.3738 | N | 1 | N | N | 1.1101 | 39.4971 | 161833.513
| ZN711:PA11 | 184 | 106.8546 | #N/A | 0.58073 | 39.4971 | 19595 | 9819 | 705503 | 2011-08-01 06:20 | 2011-08-01 09:30 | 190 | 11kV | 1520 | 8 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | Section of Pnl.12 ex Wyong Zone - PT.11507 Yarramalong Bunning 0.3 - A Phase HDO 20A fuse blown - Ringtail possum on HV fuse assembly | August | 2011 | 2012Q1 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2011-08-01 | N | 190 | N | 4 | N | N | 1.1101 | 39.4971 | 1110.7712
| ZN711:PA18 | 669 | 377.804 | #N/A | 0.56473 | 39.4971 | 18947 | 3469 | 705838 | 2011-08-01 14:12 | 2011-08-01 16:10 | 118 | 11kV | 9676 | 82 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1514 Somerset Norfolk 31.5amp Footpath HDO fuse blown Cause: Fuse Fatigue See OMS 706475 705838 705898 705825 705884 | August | 2011 | 2012Q1 | 2012 | ZN2635:PA17 | ZN2635:PA38 | ZN02635/000038 | PARRAMATTA | OH | Not Veg | 2011-08-01 | N | 118 | N | 4 | N | N | 1.1101 | 39.4971 | 7070.9354
| ZN711:PA22 | 202 | 154.6741 | #N/A | 0.76571 | 39.4971 | 20283 | 18271 | 705901 | 2011-08-01 15:50 | 2011-08-01 18:48 | 178 | 11kV | 178 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117016 B Phase DOLF : 10Amp. Excluded OMS 705901 (incorrect premise - same customer) OMS 706039 | August | 2011 | 2012Q1 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2011-08-01 | N | 178 | N | 4 | N | N | 1.1101 | 39.4971 | 130.0771
| ZN711:PA32 | 233 | 157.5399 | #N/A | 0.67614 | 39.4971 | 19530 | 9361 | 705971 | 2011-08-01 18:57 | 2011-08-01 20:03 | 66 | 11kV | 81246 | 1231 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15005 Belrose, Panel 2 Fdr CB tripped on A phase IOC ,efi, frame leakage on #1 and #2 Tx's, Zone earth , 11kV trip. Twp possums found at base of HV UG/OH adjacent to link 21713 - suspect flashover on UG/OH | August | 2011 | 2012Q1 | 2012 | ZN15005:PA2 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2011-08-01 | N | 66 | N | 4 | N | N | 1.1101 | 39.4971 | 59372.1804
| ZN711:PA34 | 408 | 402.8319 | #N/A | 0.98733 | 39.4971 | 19600 | 9852 | 706191 | 2011-08-02 12:38 | 2011-08-02 15:15 | 156.7167 | 11kV | 69680.7167 | 474 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S15001 Brookvale Panel 3 Tripped and reclosed on SEF with 11kV trip signals Cause; Bond burnt off link 22345 See OMS 708290 708288 708287 708296 708310 706249 706191 706246 706258 | August | 2011 | 2012Q1 | 2012 | ZN15001:PA3 | ZN15001:PA3 | ZN15001/000003 | NORTHERN BEACHES | OH | Not Veg | 2011-08-02 | N | 147.0057 | N | 1 | N | N | 1.1101 | 39.4971 | 50920.6125
| ZN10991:PA1 | 1512 | 1402.0318 | 34.89 | 0.92727 | 34.89 | 20316 | 19129 | 706418 | 2011-08-03 06:51 | 2011-08-03 08:17 | 86 | 11kV | 86 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S15070 Darley North Head A and B phase HV fuse blown on SW5709 Cause not ascertained for outage - Problem with trees on OH previously See OMS708873 706418 | August | 2011 | 2012Q1 | 2012 |  |  |  |  | OH | Veg | 2011-08-03 | N | 86 | N | 5 | N | N | 1.1101 | 39.4971 | 62.8463
| ZN10991:PA12 | 1223 | 1157.9859 | 32.21 | 0.94684 | 32.21 | 19486 | 8995 | 706515 | 2011-08-03 10:20 | 2011-08-03 10:40 | 20 | 11kV | 2780 | 139 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Air Break Switch | Unplanned | Unselected | N | LID 117031 Fdr isolated to bridge out ABS 42881 SEE report # 117026 | August | 2011 | 2012Q1 | 2012 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2011-08-03 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 2031.542
| ZN10991:PA13 | 1154 | 1196.6724 | 40.51 | 1.037 | 40.51 | 19642 | 10657 | 706629 | 2011-08-03 12:37 | 2011-08-03 13:45 | 68.4333 | 11kV | 7664.5333 | 112 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CC1: 06-"Urgent - O.H Mains - No others" LID117033 A Phase DOLF : 40Amp. Excluded OMS 706639, 706637, 706629 OMS 706625 | August | 2011 | 2012Q1 | 2012 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2011-08-03 | N | 68.4333 | N | 5 | N | N | 1.1101 | 39.4971 | 5601.0149
| ZN10991:PA2 | 1248 | 633.5644 | #N/A | 0.50766 | 39.4971 | 19710 | 11795 | 706741 | 2011-08-03 15:37 | 2011-08-03 17:47 | 130 | 11kV | 139782 | 1321 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At Zn15008 Harbord panel 4 tripped on C phase IOC and Timed O/C, timer reclose, LO, Tx2 Fault Check and EFI. Signals: 11kV trip Field EFI's S46775 S16797 CP20901 Cause: 11kV UGOH between AB25220 and S16832 Failed, 11kV UGOH outside S16320 Has Blown Surge Arrestors. See OMS 708193 708195 708197 708198 706741 NOTE: On restoration of Panel 4 Panel 6 Tripped See OMS 707385 | August | 2011 | 2012Q1 | 2012 | ZN15008:PA4 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | Unknown | Unknown | 2011-08-03 | N | 105.8153 | N | 5 | N | N | 1.1101 | 39.4971 | 102148.5627
| ZN10991:PA5 | 1517 | 771.7668 | 29.68 | 0.50875 | 29.68 | 19875 | 13537 | 706746 | 2011-08-03 15:37 | 2011-08-03 17:47 | 130 | 11kV | 14487 | 2232 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At Zn15008 Harbord Pa6 feeder tripped on C phase IOC Timed and EF. Signals: 11kV Trip Cause: Pa6 tripped on restoration of panel 4 due to False indication on EFI See OMS 708247 708245 707385 706746 | August | 2011 | 2012Q1 | 2012 | ZN15008:PA6 | ZN15008:PA3 | ZN15008/000003 | NORTHERN BEACHES | Unknown | Unknown | 2011-08-03 | N | 6.4906 | N | 5 | N | N | 1.1101 | 39.4971 | 10586.6723
| ZN10991:PA6 | 1412 | 798.8964 | 35.83 | 0.56579 | 35.83 | 19472 | 8888 | 706869 | 2011-08-04 00:27 | 2011-08-04 01:35 | 68 | 11kV | 20594 | 1535 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | At S.10999 Kogarah 11KV fdr panel No.7 tripped on O/L 1.2.1 50TBC and reclosed to lockout. At S.10925 Forest Water Board SW A tripped on E/L, SW B tripped on E/L and customers CB tripped. Remarks: Defective customers equipment at S.10925 Forest water board. Sydney Water notified Related jobs: #906869, 706905, 706906, 706904, 706870, 706871, 706873 | August | 2011 | 2012Q1 | 2012 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | BAYSIDE | Unknown | Not Veg | 2011-08-04 | N | 13.4163 | N | 6 | N | N | 1.1101 | 39.4971 | 15049.4878
| ZN10991:PA7 | 2008 | 992.3849 | 33.9 | 0.49422 | 33.9 | 20058 | 15654 | 707238 | 2011-08-04 16:29 | 2011-08-04 17:55 | 86 | 11kV | 1978 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117042 B Phase DOLF : 16Amp. Excluded OMS 707238 & 707252 OMS 708307 | August | 2011 | 2012Q1 | 2012 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2011-08-04 | N | 86 | N | 6 | N | N | 1.1101 | 39.4971 | 1445.4641
| ZN10991:PA8 | 2034 | 1677.1106 | 35.74 | 0.82454 | 35.74 | 20290 | 18556 | 707243 | 2011-08-04 19:04 | 2011-08-04 19:19 | 15 | 11kV | 2520 | 168 | HV | Overload Operational | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Unselected | N | Section of Pnl.12 ex Berkeley Vale Zn - REC 44947 Gravenlock Rd tripped on IOC & Timed OC Remarks: tripped when trying to restore feeder fault on section of Pnl.24 (REC47878 Pacific Palmdale) | August | 2011 | 2012Q1 | 2012 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2011-08-04 | N | 15 | N | 6 | N | N | 1.1101 | 39.4971 | 1841.5417
| ZN340:PA10 | 148 | 507.4266 | #N/A | 3.4286 | 39.4971 | 19233 | 6334 | 707244 | 2011-08-04 16:41 | 2011-08-04 19:40 | 179 | 11kV | 38294 | 804 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Ex Zn.12690 Berkeley Vale Pnl.24 feeder tripped on: A + C Phase OC, EFI (Signals: 11kv Trip - No.3 Group Earth) Field EFI's: S.18726 Remarks: 11kV fault on UGOH below S.18726 Pacific Burns - See OMS # 708206 & 708224 for seperate interruption on section of FDR below REC 47878 Pacific Palmdale. | August | 2011 | 2012Q1 | 2012 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | Unknown | Unknown | 2011-08-04 | N | 47.6294 | N | 6 | N | N | 1.1101 | 39.4971 | 27984.1257
| ZN340:PA11 | 346 | 405.9106 | 50.04 | 1.1732 | 50.04 | 19211 | 5968 | 707311 | 2011-08-04 20:11 | 2011-08-04 21:24 | 73 | 11kV | 28417 | 672 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 1610 Homebush Bay 11kv fdr Pnl NO12 "Sub 8703 Bennalong Australia" tripped on Earth fault Fn G1 B/N Overcurrent & EFI Field EFI's S8703 S35652 S5362 S7643 Remarks: Cable failure from Sub 7643 Shirley Australia to Sub 7854 Olympic Sarah Related jobs: #708234, 708235, 708236, 707311 | August | 2011 | 2012Q1 | 2012 | ZN1610:PA12 | ZN1610:PA14 | ZN01610/000014 | PARRAMATTA | UG | Not Veg | 2011-08-04 | N | 42.2872 | N | 6 | N | N | 1.1101 | 39.4971 | 20766.3054
| ZN340:PA3 | 1351 | 934.9716 | 41.24 | 0.69206 | 41.24 | 19751 | 12432 | 717662 | 2011-08-05 02:39 | 2011-08-05 04:55 | 136 | 11kV | 66324 | 549 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S15001 Brookvale Panel 16 tripped on Earth Fault, Fault Check, EFI signals and 11kV trip. Cause; UG feeder fault from S16088 to S16884 to S16894 See OMS 717662 717664 717665 | August | 2011 | 2012Q1 | 2012 | ZN15001:PA16 | ZN15001:PA16 | ZN15001/000016 | NORTHERN BEACHES | UG | Not Veg | 2011-08-05 | N | 120.8087 | N | 5 | N | N | 1.1101 | 39.4971 | 48467.623
| ZN340:PA32 | 355 | 992.6654 | 50.91 | 2.7962 | 50.91 | 19196 | 5609 | 707327 | 2011-08-05 06:58 | 2011-08-05 09:00 | 122 | 11kV | 16348 | 134 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Abmormal switching. 11kV bond burnt off OH in between tee S.16829 and tee S.16310 | August | 2011 | 2012Q1 | 2012 | ZN15001:PA16 | ZN15001:PA16 | ZN15001/000016 | NORTHERN BEACHES | OH | Not Veg | 2011-08-05 | N | 122 | N | 5 | N | N | 1.1101 | 39.4971 | 11946.6362
| ZN340:PA34 | 331 | 389.6565 | 33.46 | 1.1772 | 33.46 | 19788 | 12686 | 707247 | 2011-08-04 16:36 | 2011-08-05 11:37 | 1141 | 11kV | 60817.0833 | 76 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Section of Pnl.24R ex Berkeley Vale Zn - REC 47878 Pacific Palmdale tripped on OC Remarks: Suspect 11kV UG fault in fdr from AB44747 to LB 40054 to LB 44733 Note: @ Zn.12690 Pnl.24 tripped 5 minutes later @ 16:41. See OMS # 708215 | August | 2011 | 2012Q1 | 2012 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | UG | Not Veg | 2011-08-04 | N | 800.2248 | N | 6 | N | N | 1.1101 | 39.4971 | 44443.3307
| ZN340:PA35 | 1143 | 1222.3091 | 41.73 | 1.0694 | 41.73 | 20112 | 16080 | 707420 | 2011-08-05 09:52 | 2011-08-05 12:25 | 153.4 | 11kV | 2761.2 | 18 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | Unselected | N | LID 117046 Trigger: Interruption to replace condemned Pole DD-20101. OMS Job No. 707420. | August | 2011 | 2012Q1 | 2012 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2011-08-05 | N | 153.4 | N | 5 | N | N | 1.1101 | 39.4971 | 2017.8035
| ZN340:PA4 | 289 | 414.0573 | 45.13 | 1.4327 | 45.13 | 20282 | 18249 | 707647 | 2011-08-05 14:31 | 2011-08-05 15:35 | 64 | 11kV | 448 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117049 B Phase burnt off hv lead repaired under ap Excluded OMS 707647 OMS 708478 | August | 2011 | 2012Q1 | 2012 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2011-08-05 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 327.3852
| ZN340:PA40 | 997 | 679.5663 | 38.63 | 0.68161 | 38.63 | 20015 | 15058 | 707770 | 2011-08-05 18:56 | 2011-08-05 20:21 | 85 | 11kV | 73188 | 879 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3922 Drummoyne 11KV feeder panel No 22 labelled "S1593 The Parade etc" tripped on: C phase IOC, Fault check. Electronic relay legend is unreadable Field EFI's: Nil Remarks: 11kv feeder from S3922 Drummoyne "Panel 22" to S2076 Gears Ave "SW A" tp S1593 The Parade "SWA" to S7804 Point Ave "SWB". UG Cable fault Related jobs: #707783, 707778, 70777, 707776, 707774, 707773, 707770, 708907, 708903, 708894, 708889, 708910, 708912 | August | 2011 | 2012Q1 | 2012 | ZN3922:PA22 | ZN3922:PA22 | ZN03922/000022 | CANADA BAY | UG | Not Veg | 2011-08-05 | N | 83.2628 | N | 5 | N | N | 1.1101 | 39.4971 | 53483.6317
| ZN340:PA42 | 14 | 235.3565 | #N/A | 16.8112 | 39.4971 | 20341 | 19428 | 707800 | 2011-08-06 03:19 | 2011-08-06 04:30 | 71 | 11kV | 34666 | 527 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Cold <10C | N | @Sub 2310 Punchbowl Panel #4 labelled S997 tipped on A phase INST IOC Earth Fault EFI 11KV trip ZE #2 GE Field EFI S997, S6243, S6143, S6728 Remarks: Suspected UG cable fault in cable between Sub 35979 Bonds Jindalee SWB to Sub 2320 Methuen Bonds SW A to Sub 3258 Earls Karne SW A Related jobs: #707805, 707803, 707801, 708859, 708858, 708857, 707800 | August | 2011 | 2012Q1 | 2012 | ZN2310:PA4 | ZN35800:PA22 | ZN35800/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-08-06 | N | 65.7799 | N | 2 | N | N | 1.1101 | 39.4971 | 25332.8903
| ZN340:PA44 | 1244 | 1206.9496 | 40.28 | 0.97022 | 40.28 | 19134 | 4861 | 707901 | 2011-08-06 12:29 | 2011-08-06 14:52 | 143 | 11kV | 69172 | 696 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 6 tripped on O/C and EF, EFI, EF and EF check. Signals: 11kV trip, Tx1 Group Earth. Cause: 11kV feeder from S4646 Windsor Kamilaroy to S4647 Patterson Congham tee PT1188 Gillian Yanko. Appears Contractors have hit cable O/S 26 Congham Rd. | August | 2011 | 2012Q1 | 2012 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2011-08-06 | N | 99.3851 | N | 2 | N | N | 1.1101 | 39.4971 | 50548.8574
| ZN340:PA45 | 851 | 1237.3717 | 50.75 | 1.454 | 50.75 | 19460 | 8787 | 708093 | 2011-08-07 12:30 | 2011-08-07 16:50 | 260 | 11kV | 520 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 117059 A & C Phase DOLF : 5Amp. Initially no obvious cause, on attempt to restore supply at sub 51151 transformer got vey hot and fuses blew. SAO required please for details of the new transformer. Excluded OMS 708093 OMS 708563 | August | 2011 | 2012Q1 | 2012 | 516:48066 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Not Veg | 2011-08-07 | N | 260 | N | 3 | N | N | 1.1101 | 39.4971 | 380.0007
| ZN340:PA8 | 621 | 545.9309 | 49.32 | 0.87912 | 49.32 | 19832 | 13019 | 708145 | 2011-08-07 17:56 | 2011-08-07 20:00 | 124 | 11kV | 1334 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | PT.14348 Sandra Hue Hue 0.1 - Footpath phase 20A HDO fuse operated @ Wyong Pnl.20 EFI flagged. Field EFI @ S.18534 & S.18246 Remarks: Lightning Storm | August | 2011 | 2012Q1 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2011-08-07 | N | 121.2727 | N | 3 | N | N | 1.1101 | 39.4971 | 974.8479
| 508:82574 | 220 | 215.9077 | 32.19 | 0.9814 | 32.19 | 19562 | 9640 | 708105 | 2011-08-07 13:57 | 2011-08-07 22:40 | 523 | 11kV | 73808 | 914 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | At Sub 10996 Rockdale Panel 10 "West Botany St North" feeder tripped, reclosed, tripped and locked out on: Relays: A phase timed O/C, timing relay and lock out relay. Signals: 11kv trip Remarks: Car hit pole on corner of Francis and Bestic Sts Kyeemagh. Section of 11KV feeder from AB 30119 to LK 30532 to AB 31266 tee to Sub 10443 Bestic Fishermans Related jobs: #708126, 708114, 708108, 708107, 7008106, 708105, 709010, 709008, 709006 | August | 2011 | 2012Q1 | 2012 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2011-08-07 | N | 80.7527 | N | 3 | N | N | 1.1101 | 39.4971 | 53936.7094
| 508:82575 | 401 | 431.8482 | 32.13 | 1.0769 | 32.13 | 19608 | 10286 | 708293 | 2011-08-08 09:57 | 2011-08-08 11:45 | 108 | 11kV | 108 | 1 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117068 B & C Phase DOLF : 10Amp. birds nest on PT Excluded OMS 708293 ( attached to incorrect premise - see call in info) OMS 708959 | August | 2011 | 2012Q1 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2011-08-08 | N | 108 | N | 8 | N | N | 1.1101 | 39.4971 | 78.9232
| 508:82576 | 676 | 566.0586 | 32.55 | 0.83736 | 32.55 | 19078 | 4492 | 708447 | 2011-08-08 12:12 | 2011-08-08 13:20 | 68 | 11kV | 120975 | 1855 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2602 Clovelly Pa4 "S2963 Carrington Col" tripped on EFI,F/C Signals 11kv trip Tx3 ZE GE EFI S2963 S291 From To Restored DC Time Zn2602:Pa4 S291 2 13:15 S2395 S35473 2 13:16 S300 S2039 3 13:20 Suspect UG fdr from S291SwA to S35473SwA to S300SwE to S3924SwB See 708962 708963 708964 GIS 708451 Exclude 708447 708461 708463 | August | 2011 | 2012Q1 | 2012 | ZN2602:PA4 | ZN2602:PA31 | ZN02602/000031 | RANDWICK | UG | Not Veg | 2011-08-08 | N | 65.2156 | N | 8 | N | N | 1.1101 | 39.4971 | 88404.9618
| 508:82578 | 321 | 272.271 | 33.18 | 0.8482 | 33.18 | 19066 | 4446 | 708630 | 2011-08-08 14:58 | 2011-08-08 16:25 | 87 | 11kV | 87 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117075 B Phase DOLF : 10Amp Excluded OMS 708630 (attached to incorrect premise - see call in info) OMS 708920 | August | 2011 | 2012Q1 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2011-08-08 | N | 87 | N | 8 | N | N | 1.1101 | 39.4971 | 63.577
| 508:82579 | 269 | 316.6146 | 41.51 | 1.177 | 41.51 | 19633 | 10513 | 708738 | 2011-08-08 17:00 | 2011-08-08 17:28 | 28 | 11kV | 16828 | 601 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn12590 Lake Munmorah - Pnl.4 opened by A/OP (Relays: SEF. Signals: CLC Defect, Batt charger AC supply fail, TX1,2,3 no volts) Anbormal Switching: AB43821 Closed Remarks: Pnl.4 Opened by A/OP Vass after reports of 11kV smouldering on ground near Pacific Tall Timers. 11kV feeder found down between LK41929 to S.18291 Sw A to AB40164. - Linesman has repaired - see seperated interruption for Pnl.7 | August | 2011 | 2012Q1 | 2012 | ZN12590:PA4 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Not Veg | 2011-08-08 | N | 28 | N | 8 | N | N | 1.1101 | 39.4971 | 12297.4061
| 508:82580 | 337 | 483.2052 | 41.98 | 1.4338 | 41.98 | 18864 | 2682 | 708690 | 2011-08-08 16:13 | 2011-08-08 17:50 | 97 | 11kV | 1164 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn.14114 Wamberal Pnl.2 - PT18002 Oak McGarrity 0.2 - Middle Phase 16A HDO fuse operated Remarks: Fuse Fatigue | August | 2011 | 2012Q1 | 2012 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Not Veg | 2011-08-08 | N | 97 | N | 8 | N | N | 1.1101 | 39.4971 | 850.6169
| 512:83733 | 1092 | 879.822 | 31.23 | 0.8057 | 31.23 | 20436 | 20395 | 708719 | 2011-08-08 16:54 | 2011-08-08 18:45 | 111 | 11kV | 173538 | 2215 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12590 Lake Munmorah - Pnl.7 tripped on: Earth Fault. Abnormal Switching: AB43821 Closed Remarks: DOp was switching across panels for D/R #272814 when Pnl.7 tripped (S/E & REC were made N/A prior to beginning of switching) 11kV was reported to me smouldering on ground. See seperate interruption for Pnl.4 | August | 2011 | 2012Q1 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2011-08-08 | N | 78.3467 | N | 8 | N | N | 1.1101 | 39.4971 | 126816.4519
| 512:83734 | 1 | 2.5906 | 68.29 | 2.5906 | 68.29 | 19590 | 9754 | 708773 | 2011-08-08 18:00 | 2011-08-08 18:50 | 50 | 11kV | 45700 | 914 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn10996:Pa10 "West Botany St North" Fdr tripped and locked out on: Relays Cph timed OC Signals 11kv trip Note: DOp was resetting relays on Pa10 from a trip on 7/8/11. As he reset the Aph OC relay flag the fdr tripped on Cph O/C. The timing relay and the lockout relay had not being reset at the time. From To restored DC Time ZN10996:Pa10 Whole fdr 18:50 Cause not ascertained | August | 2011 | 2012Q1 | 2012 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Veg | 2011-08-08 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 33396.2121
| 512:83736 | 869 | 713.842 | #N/A | 0.82145 | 39.4971 | 19764 | 12478 | 708808 | 2011-08-08 19:40 | 2011-08-08 20:56 | 75.4 | 11kV | 2186.6 | 29 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14508 Elsinore Scaysbrooke - Centre Phae 31.5 Amp HDO (Batch # 3380) - Failed crimp | August | 2011 | 2012Q1 | 2012 | ZN12590:PA4 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Not Veg | 2011-08-08 | N | 75.4 | N | 8 | N | N | 1.1101 | 39.4971 | 1597.9028
| 512:83741 | 1057 | 1009.101 | 36.55 | 0.95468 | 36.55 | 20424 | 20264 | 709608 | 2011-08-09 04:59 | 2011-08-09 06:05 | 66 | 11kV | 160586 | 2774 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2602 Clovelly Pa15 "Douglas Bishop" 11kv fdr tripped on IOC EFI OC Alarms 11kv trip Tx1 ZE GE EFI's S46310 S60 S1874 ABNORMAL @S300SwD closed, SwE Open Suspect UG cable fault btw S1874SwB to S8254SwB From To Restored DC Time Zn2602:Pa15 S1874SwB 11 5:51 S35196SwB S8524SwB 2 6:05 See 709608 709611 709627 | August | 2011 | 2012Q1 | 2012 | ZN2602:PA15 | ZN36800:PA40 | ZN36800/000040 | RANDWICK | UG | Not Veg | 2011-08-09 | N | 57.8897 | N | 6 | N | N | 1.1101 | 39.4971 | 117351.5123
| 512:83743 | 1014 | 828.5463 | 32.65 | 0.81711 | 32.65 | 20227 | 17361 | 708938 | 2011-08-09 09:44 | 2011-08-09 11:20 | 96.8 | 11kV | 7840.8 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" LID 117086 B Phase DOLF : 40Amp. suspect over tight dolf element OMS 708940, 708938 | August | 2011 | 2012Q1 | 2012 | 512:48046 | 512:83736 | ZN00512/083736 | CESSNOCK | OH | Veg | 2011-08-09 | N | 96.8 | N | 6 | N | N | 1.1101 | 39.4971 | 5729.8254
| 257:81985 | 1025 | 513.7321 | 38.14 | 0.5012 | 38.14 | 19501 | 9089 | 709014 | 2011-08-09 10:54 | 2011-08-09 11:40 | 46 | 11kV | 5290 | 115 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Based on cust calls 709030 & GIS correction 709023 S6534-1 in LV// w/ S589 Zn711 Blackwattle Bay 5kv OCB Pa9 fdr tripped on: Relays:EFI Earth Fault Signals:5kv Trip Tx2 GE ZE Suspect cable fault on 5kv feeder from Zn711:Pa9 to S589 Harris Miller See 709959 LV// 709965 GIS 709023 Exclude 709033 709030 709017 709014 From To Restored DC TIme S589SwD S589SwA 1 11:40 | August | 2011 | 2012Q1 | 2012 | ZN711:PA9 | ZN7481:PA6R | ZN07481/000006 | SYDNEY | UG | Not Veg | 2011-08-09 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 3865.776
| 257:81987 | 2128 | 1804.5233 | 41.71 | 0.84799 | 41.71 | 20156 | 16380 | 708856 | 2011-08-09 07:52 | 2011-08-09 12:45 | 293 | 11kV | 1172 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117089 Single phase DOLF : Cause not ascertained | August | 2011 | 2012Q1 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-08-09 | N | 293 | N | 6 | N | N | 1.1101 | 39.4971 | 856.463
| 257:81988 | 948 | 1010.7814 | 42.2 | 1.0662 | 42.2 | 18607 | 276 | 709079 | 2011-08-09 12:32 | 2011-08-09 13:50 | 78 | 11kV | 45347 | 669 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S1673 Turramurra S4706 tripped on C phase IOC with Earth Fault and EFI. Signals: 11kV Trip Cause: Contractor Hit UG cable to PT1499 O/S 10 Warrawee Ave See OMS 709979 709981 709980 | August | 2011 | 2012Q1 | 2012 | ZN1673:PA21 | ZN1673:PA1 | ZN01673/000001 | KU-RING-GAI | UG | Not Veg | 2011-08-09 | N | 67.7833 | N | 6 | N | N | 1.1101 | 39.4971 | 33138.2501
| 257:81991 | 489 | 699.6677 | 51.52 | 1.4308 | 51.52 | 19831 | 13016 | 709194 | 2011-08-09 15:23 | 2011-08-09 17:09 | 106 | 11kV | 29296 | 280 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | qAt S847 Hornsby Panel 39 tripped on E/L, EFI, Timing, Lockout and F/C Signals; Zone Earth, TX3 Group Earth and 11kV Trip. Cause: Suspect 11kV feeder fault from S847 Hornsby Pa39 and S8317 Sw A. Abnormal Switching: Ab685 is Open and defective. SWB @S8428 is closed See OMS 709576 709194. | August | 2011 | 2012Q1 | 2012 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | UG | Not Veg | 2011-08-09 | N | 104.6286 | N | 6 | N | N | 1.1101 | 39.4971 | 21408.6527
| 257:81994 | 857 | 1406.476 | 40.08 | 1.6412 | 40.08 | 20022 | 15254 | 709337 | 2011-08-10 07:31 | 2011-08-10 08:25 | 54 | 11kV | 88891 | 1849 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At S3425 Castle Cove Panel 24 tripped on C phase O/C, EFI,Fault Check. Signals: 11kV Trip, Tx4 Group Earth Cause: Jointers were pot ending a FDr in Sydney RD Near Laurel St when adjacent feeder tripped See OMS 710061 710063 711908 709338 709343 | August | 2011 | 2012Q1 | 2012 | ZN3425:PA24 | ZN3425:PA24 | ZN03425/000024 | WILLOUGHBY | UG | Not Veg | 2011-08-10 | N | 48.0752 | N | 1 | N | N | 1.1101 | 39.4971 | 64958.921
| 257:81997 | 315 | 291.4046 | 42.68 | 0.92509 | 42.68 | 19188 | 5441 | 709942 | 2011-08-11 10:59 | 2011-08-11 12:14 | 75 | 11kV | 2055 | 33 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa21 tripped Relays Pa21 EF & EFI Signals Tx3 GE ZE & 11kv trip EFI Nil Abnormal S48354SwB Port Botany Aux No1 is closed & ZN35700:Pa12L Port Botany is open under A/P UG fdr fault in front line fdr from Zn1788:Pa21 to S7169SwA to S5180SwB Note: S48354 remains interrupted as Pa12L is under A/P. Port Botany Zone is on standby supply. Excavator dug up HV cables outside Amcor Paper Australia See 711716,8 Exclude 709942 From To Restored DC TIme S3131SwA S5180SwA 3 1200 S6789 S7169SwA 2 1214 | August | 2011 | 2012Q1 | 2012 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | UG | Not Veg | 2011-08-11 | N | 62.2727 | N | 3 | N | N | 1.1101 | 39.4971 | 1501.7334
| 257:81999 | 948 | 1202.812 | 46.22 | 1.2688 | 46.22 | 19665 | 11055 | 710014 | 2011-08-11 12:55 | 2011-08-11 15:35 | 160 | 11kV | 70291 | 483 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Somersby Zone Pnl.17 - REC 45202 Pacific Ashbrooke 2.0 - tripped / closed / tripped / closed / tripped / closed / tripped / locked out on IOC Remarks: Tree branch removed from HV mains @ pole SP692 | August | 2011 | 2012Q1 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2011-08-11 | N | 145.53 | N | 3 | N | N | 1.1101 | 39.4971 | 51366.5896
| 257:82000 | 520 | 569.0287 | 44.01 | 1.0943 | 44.01 | 19389 | 8164 | 710185 | 2011-08-11 18:19 | 2011-08-11 20:57 | 158 | 11kV | 76550 | 489 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 117126 2 fault operations 3 phase Sensitive Earth Fault. BYPASS ABS FAULTY....NOT OPENING FULLY. Excluded OMS 710185, 710187, 710225 OMS 710458, 710459, 710460, 710461 | August | 2011 | 2012Q1 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2011-08-11 | N | 156.544 | N | 3 | N | N | 1.1101 | 39.4971 | 55940.4822
| 257:82003 | 157 | 635.2943 | 48.55 | 4.0465 | 48.55 | 18672 | 908 | 710238 | 2011-08-12 01:13 | 2011-08-12 03:50 | 157 | 11kV | 169510 | 1343 | HV | Overload | Utility Process Issue | Circuit Breaker | Unplanned | Rain Light | N | @Sub 9700 Kirrawee panel #20 labelled Sub 9432 tripped reclosed tripped on B & C phase IOC lockout timing 11KV trip Remarks: Cause unknown Related jobs: #710238, 710297, 710296, 710295 | August | 2011 | 2012Q1 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | Unknown | Not Veg | 2011-08-12 | N | 126.2174 | N | 1 | N | N | 1.1101 | 39.4971 | 123872.9083
| 257:82006 | 256 | 206.8142 | 40.04 | 0.80787 | 40.04 | 20409 | 20198 | 710855 | 2011-08-13 20:04 | 2011-08-13 22:27 | 143 | 11kV | 135593 | 1071 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.10 feeder tripped on: 51A & B OC, EFI - Field EFI: S18584 Remarks: 1: HV Bond burnt off tee to PT13740 Kalani Scenic (Roadside Phase). PT13740 Isolated & In LV// 2: HV Bond Burnt off near LB41073 (O/S 68 scenic Rd) | August | 2011 | 2012Q1 | 2012 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2011-08-13 | N | 126.6041 | N | 1 | N | N | 1.1101 | 39.4971 | 99087.3651
| ZN15001:PA10 | 170 | 1901.8165 | 43.24 | 11.1872 | 43.24 | 19474 | 8898 | 710903 | 2011-08-14 08:49 | 2011-08-14 10:00 | 71 | 11kV | 142 | 2 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117138 B & C Phase DOLF : 10Amp Bird dropped wire across arrestors. 248, 249, 249V. Excluded OMS# 710903. OMS 711268 | August | 2011 | 2012Q1 | 2012 |  |  |  |  | OH | Not Veg | 2011-08-14 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 103.7694
| ZN15001:PA11 | 965 | 1640.2386 | 45.3 | 1.6997 | 45.3 | 20017 | 15080 | 711309 | 2011-08-14 13:15 | 2011-08-14 17:01 | 226 | 11kV | 66090 | 622 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 117146 1 fault operation C Phase Overcurrent, Earth fault, Sensitive Earth fault Main fault appeared to be the C phase 11kV conductor at pole FP-40192 (618 Standen Drive) had broken the tie and fallen onto the crossarm. Summated O/C & Earth fault 66kV Panel. CB 48069 Undervoltage relay. CB 48071 Undervoltage relay. Sensitive Earth Fault Relay at sub. Sw 48049 A & B Phase Overcurrent. Excluded OMS 710956 OMS 711309, 711312 711313, 711316, 711317, 711318, 711319, 711321, 711322 | August | 2011 | 2012Q1 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-08-14 | N | 106.254 | N | 4 | N | N | 1.1101 | 39.4971 | 48296.6227
| ZN15001:PA13 | 83 | 366.6491 | #N/A | 4.4175 | 39.4971 | 20072 | 15797 | 710956 | 2011-08-14 14:27 | 2011-08-14 17:01 | 154.1333 | 11kV | 154.1333 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 117146 1 fault operation C Phase Overcurrent, Earth fault, Sensitive Earth fault Main fault appeared to be the C phase 11kV conductor at pole FP-40192 (618 Standen Drive) had broken the tie and fallen onto the crossarm. Summated O/C & Earth fault 66kV Panel. CB 48069 Undervoltage relay. CB 48071 Undervoltage relay. Sensitive Earth Fault Relay at sub. Sw 48049 A & B Phase Overcurrent. Excluded OMS 710956 OMS 711309, 711312 711313, 711316, 711317, 711318, 711319, 711321, 711322 | August | 2011 | 2012Q1 | 2012 | 513:48059 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-08-14 | N | 154.1333 | N | 4 | N | N | 1.1101 | 39.4971 | 112.6361
| ZN15001:PA15 | 2431 | 1864.5783 | 41.65 | 0.767 | 41.65 | 19778 | 12609 | 711014 | 2011-08-14 19:39 | 2011-08-14 21:34 | 115 | 11kV | 920 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Pnl.20 Wyong zone - PT.13341 Hue Hue Dickson 0.6 - Roadside phase 16Amp HV fuse blown - fuse fatigue (12Amp batch #2587) Remarks: Hv Fuse fatigue | August | 2011 | 2012Q1 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2011-08-14 | N | 115 | N | 4 | N | N | 1.1101 | 39.4971 | 672.3089
| ZN15001:PA16 | 546 | 875.8932 | 56.8 | 1.6042 | 56.8 | 20018 | 15081 | 711205 | 2011-08-15 11:07 | 2011-08-15 12:03 | 56 | 11kV | 16184 | 289 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117157 2 fault operations A & B Phases Instantenous Overcurrent. Excluded OMS 711205 OMS 711610 | August | 2011 | 2012Q1 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2011-08-15 | N | 56 | N | 6 | N | N | 1.1101 | 39.4971 | 11826.7899
| ZN15001:PA17 | 3 | 341.7567 | #N/A | 113.9189 | 39.4971 | 20152 | 16342 | 711106 | 2011-08-15 09:25 | 2011-08-15 13:00 | 215 | 11kV | 3440 | 16 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 117151 Isolation for Trans @ sub 71585 leaking, change req'd. Sub also retrofitted. Excluded OMS 711106 OMS 711585 | August | 2011 | 2012Q1 | 2012 | 813:89058 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2011-08-15 | N | 215 | N | 6 | N | N | 1.1101 | 39.4971 | 2513.8505
| ZN15001:PA18 | 2398 | 2326.9849 | 40.82 | 0.97039 | 40.82 | 19377 | 8012 | 711447 | 2011-08-15 16:32 | 2011-08-15 19:17 | 165 | 11kV | 39705 | 454 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn263 Dalley St 35/37AB CB tripd RELAY Pa35/37A-35A Aph O/C Pa35/37B-37B EF SIGNALS ABC/DEF 11kv trip, VCC Panel Cap step fail, DEF GE fault ABNORMAL 35/37C fdr under A/P to testers from Zn263 to RMI@S6405 Carringbush King st S3988 S5054 S6828 S5488 S6953 on 37C leg While 35/37C fdr was under A/P testers (Disc#272358) 11kv fdr fault on 37B leg 35/37B fdr. 35/37A fdr trip on O/C. See 712306,11,2,4,5,6,7,8,9 MultiSub 711447,51,4,71 Exclude 711448 | August | 2011 | 2012Q1 | 2012 | ZN263:PA35 37ABC | ZN8700:PA65 66KLM | ZN08700/65 66KLM | SYDNEY | UG | Not Veg | 2011-08-15 | N | 87.4559 | N | 6 | N | N | 1.1101 | 39.4971 | 29015.2429
| ZN15001:PA2 | 3101 | 2473.2871 | 38.7 | 0.79758 | 38.7 | 18720 | 1279 | 711353 | 2011-08-15 14:26 | 2011-08-15 21:00 | 393.6333 | 11kV | 5904.5 | 15 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117161 A phase BURNT OFF TAPPING ON 11KV MAINS ABOVE SUB 52514. | August | 2011 | 2012Q1 | 2012 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2011-08-15 | N | 393.6333 | N | 6 | N | N | 1.1101 | 39.4971 | 4314.8344
| ZN15001:PA3 | 407 | 1093.773 | 54.42 | 2.6874 | 54.42 | 20093 | 15908 | 711518 | 2011-08-15 20:10 | 2011-08-16 01:01 | 291 | 11kV | 254491 | 2368 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12610 Long jetty Pnl.11 feeder tripped & locked out on: A & B Phase O/C, E/F, EFI, EF/C (Tx1 - EFC, Zone E) - Field EFI @ S.14377 Remarks: See previous trip & reclose @ 20:01 AB41540 Bond Burnt off - HV ABC come adrift from stand off insulators between AB41224, AB44476 & AB44533 - HV UG cable fault between S.12581 & S.12579 | August | 2011 | 2012Q1 | 2012 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | UG | Not Veg | 2011-08-15 | N | 107.4709 | N | 6 | N | N | 1.1101 | 39.4971 | 185974.5166
| ZN15001:PA4 | 329 | 789.9625 | 52.06 | 2.4011 | 52.06 | 18567 | 10 | 711534 | 2011-08-15 20:58 | 2011-08-16 06:12 | 554.3 | 11kV | 225291.8167 | 1647 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At ZN.9700 Kirrawee 11kv fdr P-23 "Talara Kingsway" Tripped on: 50 TBC, 50 TN, EFI: Zn Eth, Grp Eth REMARKS: Section of 11kV fdr from AB 35882 to AB 35547 to AB 35007 to S.9336 Bunarba Ballar 11kV UGOH near S.9336 shorted and damaged by possum. | August | 2011 | 2012Q1 | 2012 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2011-08-15 | N | 136.7892 | N | 6 | N | N | 1.1101 | 39.4971 | 164636.6146
| ZN15001:PA6 | 1442 | 1331.8527 | 46.7 | 0.92361 | 46.7 | 19833 | 13021 | 712030 | 2011-08-16 19:08 | 2011-08-17 04:14 | 546 | 11kV | 18818 | 159 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Section of Pnl.5 Ex Peats Ridge Zone REC46803 Wise Ferry Dgo trap - tripped / reclosed and locked out on Overcurrent Remarks: Car hit pole wisemans Ferry Rd. Cnst Craig Mcllory Gosford Police | August | 2011 | 2012Q1 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2011-08-16 | N | 118.3522 | N | 1 | N | N | 1.1101 | 39.4971 | 13751.6394
| ZN15001:PA8 | 688 | 889.5343 | 50.32 | 1.2929 | 50.32 | 20221 | 17273 | 712356 | 2011-08-17 15:10 | 2011-08-17 16:45 | 95 | 11kV | 95 | 1 | HV | Overload Operational | Utility Process Issue | Circuit Breaker | Unplanned | Rain Light | N | @S3620 Tooheys Lidcombe 11KV CB 'A', 'B' & 'C' tripped on relays - frequency rate trip Ex Panels 12, 19 & 21 (11kv Ring) @ S2466 Flemington Remarks: Transferring No.4 TX load to No.2 & No.3 TX load to No.1 TX @S2466 Flemington (see Daros #270421) may have caused newly installed protection relays to operate @ S3620 Tooheys Lidcombe. TPE to investigate & advise control room. Related jobs: #714167, 712356 | August | 2011 | 2012Q1 | 2012 |  |  |  | CUMBERLAND | Unknown | Not Veg | 2011-08-17 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 69.4232
| ZN2835:PA10 | 964 | 1103.5274 | 31.75 | 1.1447 | 31.75 | 18660 | 764 | 712538 | 2011-08-17 22:31 | 2011-08-17 23:50 | 79 | 11kV | 8769 | 111 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117188 A Phase DOLF : 40Amp. volts 247 amps 185-120-93 Excluded OMS 712537, 712538, 712540 OMS 712667 | August | 2011 | 2012Q1 | 2012 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2011-08-17 | N | 79 | N | 3 | N | N | 1.1101 | 39.4971 | 6408.1266
| ZN2835:PA15 | 2192 | 1254.505 | 37.45 | 0.57231 | 37.45 | 19646 | 10747 | 712526 | 2011-08-17 20:32 | 2011-08-18 01:30 | 298 | 11kV | 174157 | 1305 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | At Zn 15006 Dee Why, Pnl 13 feeder tripped. Relays: SEL,EF & FC Signals: 11kV trip Field EFI'S:Nil 11kV Stand off insulator in Anzac Ave Collaroy has rusted through and has fallen into the 415V below. As a Result A further section of mains has failed at UGOH bons in the cumberland Ave footway causing the mains to fall to the ground. | August | 2011 | 2012Q1 | 2012 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2011-08-17 | N | 133.4536 | N | 3 | N | N | 1.1101 | 39.4971 | 127268.7988
| ZN2835:PA16 | 1864 | 2179.4727 | 43.55 | 1.1692 | 43.55 | 20003 | 14950 | 712747 | 2011-08-18 13:02 | 2011-08-18 14:44 | 102 | 11kV | 48402 | 563 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.12 feeder tripped / reclosed and locked ot on: 11kV trip, EF, EFI, auto close relay, lock out relay Remarks: DOp patrolled and found B phase bond burnt off on 11kV UGOH near IS44761. Linesman has reapired. | August | 2011 | 2012Q1 | 2012 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2011-08-18 | N | 85.9716 | N | 2 | N | N | 1.1101 | 39.4971 | 35370.754
| ZN2835:PA17 | 339 | 719.4359 | 43.73 | 2.1222 | 43.73 | 19903 | 13761 | 712884 | 2011-08-18 17:35 | 2011-08-18 20:40 | 185 | 11kV | 370 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 1173201 B Phase Live line clamp LIVE LINE LEAD TO DOLF BURNT OFF AT SUB 17046. Excluded OMS No 712884. OMS 714303 | August | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2011-08-18 | N | 185 | N | 2 | N | N | 1.1101 | 39.4971 | 270.3851
| ZN2835:PA18 | 518 | 479.3842 | 36.42 | 0.92545 | 36.42 | 19042 | 4344 | 712954 | 2011-08-19 07:57 | 2011-08-19 10:15 | 138 | 11kV | 294760 | 2615 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S2635 Epping Pa17 tripped reclosed tripped and locked out on A phase IOC and EF, Fault Check, Reclose Timer and lockout relays. Cause: Suspect UG Cable Fault to S4885 to S5602. See OMS 714198 714181 714179 714174 712968 712954/956/969 | August | 2011 | 2012Q1 | 2012 | ZN2635:PA17 | ZN2635:PA35 | ZN02635/000035 | RYDE | UG | Not Veg | 2011-08-19 | N | 112.7189 | N | 7 | N | N | 1.1101 | 39.4971 | 215401.9141
| ZN2835:PA19 | 805 | 1505.2609 | 48.52 | 1.8699 | 48.52 | 19012 | 4156 | 712971 | 2011-08-19 13:38 | 2011-08-19 16:10 | 152 | 11kV | 230949 | 2320 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | S.15001 Brookvale Pnl #18 labelled "Pine Pittwater" tripped on IOC A phase EFI Timing Relay Lockout 11kV Trip Tree on 11kV mains removed by Linesmen | August | 2011 | 2012Q1 | 2012 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Veg | 2011-08-19 | N | 99.547 | N | 7 | N | N | 1.1101 | 39.4971 | 168770.7174
| ZN2835:PA20 | 994 | 1267.9357 | 43.92 | 1.2756 | 43.92 | 19834 | 13023 | 713192 | 2011-08-19 14:03 | 2011-08-19 16:30 | 147 | 11kV | 232071 | 2205 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | N | S.15003 Balgowah Pnl 4 labelled AB 21076 etc tripped on timed OC - Abnormal switching at time of outage 11kV UGOH Urunga St defective | August | 2011 | 2012Q1 | 2012 | ZN15008:PA3 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | Unknown | Unknown | 2011-08-19 | N | 105.2476 | N | 7 | N | N | 1.1101 | 39.4971 | 169590.6419
| ZN2835:PA21 | 1664 | 1385.6705 | 37.25 | 0.83273 | 37.25 | 19136 | 4871 | 713426 | 2011-08-19 16:56 | 2011-08-19 19:05 | 129 | 11kV | 35177 | 312 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14143 Somersby 11kV Pnl.10 feeder tripped / reclosed / tripped & locked out on: A + C Phase timed O/C, SEF Remarks: Fault in section of 11kV OH mains from AB 40488 to AB 44527 to LB 44475. Fault not found. To be patrolled by mains Saturday | August | 2011 | 2012Q1 | 2012 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Not Veg | 2011-08-19 | N | 112.7468 | N | 7 | N | N | 1.1101 | 39.4971 | 25706.3141
| ZN2835:PA22 | 626 | 1650.7617 | 46.38 | 2.637 | 46.38 | 19050 | 4363 | 713502 | 2011-08-19 18:32 | 2011-08-19 20:00 | 88 | 11kV | 122408 | 1391 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Rain Wind Storm | N | At S847 Hornsby Panel 39 tripped on A phase OC, IOC, EFI, Timing and Lockout Cause: Bark on UGOH near LB1748. See OMS 714460 713533 713502 At S8316 Jubilee Collings 400A fuse blown on distributor 1 and 2. Cause: Above sub in LV parallel with Pa39 during fdr trip. See OMS 714465 714466 713517 | August | 2011 | 2012Q1 | 2012 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Veg | 2011-08-19 | N | 88 | N | 7 | N | N | 1.1101 | 39.4971 | 89452.156
| ZN2835:PA23 | 485 | 587.9635 | 45.22 | 1.2123 | 45.22 | 20309 | 19059 | 713262 | 2011-08-19 14:34 | 2011-08-20 00:15 | 581 | 11kV | 220814 | 2163 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At Zn 15005 Belrose Panel 4 "Sorlie Rd" trippef and reclosed on: Relays: A & B Phase IOC, Reclose lockout, Reclose timing, Fault check. Signals: 11kV trip, ZE. D Op reports 11kV mains entagled with tree at sorlie Rd Mains notified to attend ASAP R.21801 Sorlie Merrilee ex Zn 15005 Pnl 4 "Sorlie Rd" opened by D Op at 1559Hrs R.24831 Lockwood Peacock ex Zn 15005 Pnl 6 "Davidson Park" tripped on O/C at 1732 11kV entangled in tree at Sorlie Rd | August | 2011 | 2012Q1 | 2012 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Veg | 2011-08-19 | N | 102.0869 | N | 7 | N | N | 1.1101 | 39.4971 | 161364.3583
| ZN2835:PA24 | 890 | 820.544 | 43.3 | 0.92196 | 43.3 | 19622 | 10426 | 713626 | 2011-08-20 03:18 | 2011-08-20 09:00 | 342 | 11kV | 123899 | 973 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12660 Woy Woy Pnl.6 feeder tripped / reclosed / tripped and locked out on: A phase O/C Signals: EFI, timing, L/O Remarks: Large tree resting on 11kV @ 53 View Rd Saratoga | August | 2011 | 2012Q1 | 2012 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Veg | 2011-08-20 | N | 127.3371 | N | 6 | N | N | 1.1101 | 39.4971 | 90541.7348
| ZN2835:PA27 | 945 | 829.871 | 34.85 | 0.87817 | 34.85 | 19001 | 3999 | 713643 | 2011-08-20 06:58 | 2011-08-20 09:19 | 141 | 11kV | 28764 | 204 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S35370 Galston Panel 2 tripped reclosed tripped and locked out on A and C phase O/C with Lockout flag. Cause: Branch hit OH mains tee PT2104 See OMS 714689 713643/646/649/652/658 | August | 2011 | 2012Q1 | 2012 | ZN965:PA33 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2011-08-20 | N | 141 | N | 6 | N | N | 1.1101 | 39.4971 | 21019.8828
| ZN2835:PA28 | 1457 | 1184.6007 | 36.24 | 0.81304 | 36.24 | 19296 | 7318 | 713624 | 2011-08-20 02:02 | 2011-08-20 10:00 | 478 | 11kV | 2548 | 16 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | Wind | N | At S.10376 Turrella NCR middle & bottom HV fuses blown. WSLD 40 Amp. REMARKS: Hazemeyer fuse switch @ S.10376 NCR has been damaged because of water leaking on it. Dist.1 "127-137 Turrella St" is a direct distributor and is still interrupted. | August | 2011 | 2012Q1 | 2012 | ZN10990:PA8 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | Unknown | Unknown | 2011-08-20 | N | 159.25 | N | 6 | N | N | 1.1101 | 39.4971 | 1862.0032
| ZN2835:PA29 | 845 | 816.5778 | 45.49 | 0.96636 | 45.49 | 19297 | 7320 | 713629 | 2011-08-20 05:07 | 2011-08-20 11:20 | 373 | 11kV | 4103 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.11441 Cromarty Hill North Scenic - 11kV HV Fuse connection - C Phase Remarks: 11kV Connection on botton of C phase DOLF burnt off. Repairs made by Gosford O/H mains | August | 2011 | 2012Q1 | 2012 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2011-08-20 | N | 373 | N | 6 | N | N | 1.1101 | 39.4971 | 2998.3514
| ZN2835:PA30 | 1621 | 1174.0552 | 34.43 | 0.72428 | 34.43 | 20421 | 20253 | 713303 | 2011-08-19 15:08 | 2011-08-20 12:40 | 1292 | 11kV | 12207 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12630 Peats Ridge Pnl.1 feeder tripped / reclosed & locked out on : C Phase timed O/C, timing/lockout relay, EFI Remarks: 2 Phases of 11kV brought down by trees 3 spans from LK44247 | August | 2011 | 2012Q1 | 2012 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2011-08-19 | N | 129.8617 | N | 7 | N | N | 1.1101 | 39.4971 | 8920.5156
| ZN2835:PA31 | 1287 | 1409.1637 | 34.17 | 1.0949 | 34.17 | 19361 | 7790 | 713906 | 2011-08-20 17:16 | 2011-08-20 19:20 | 124 | 11kV | 148348 | 2302 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 117216 2 fault operations 3 phase Overcurrent, Earth fault. UGOH blown at 11kV links 3749. Generator installed at sub 17481. Excluded OMS 713906 OMS 714384, 714387 | August | 2011 | 2012Q1 | 2012 | 232:33409 | 242:81535 | ZN00242/081535 | PORT STEPHENS | Unknown | Unknown | 2011-08-20 | N | 64.4431 | N | 6 | N | N | 1.1101 | 39.4971 | 108408.3429
| ZN2835:PA32 | 1465 | 1040.3958 | 38.02 | 0.71017 | 38.02 | 19744 | 12386 | 713888 | 2011-08-20 16:21 | 2011-08-20 19:59 | 217.5667 | 11kV | 61925.1167 | 306 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | Unselected | N | LID 117215 2 fault operation 3 phase CAR HIT POLE COULD NOT ENTER SW 46641 IN LID AS A DEVICE section isolated to repair broken crossarm and bypass faulty ABS 74367 Excluded OMS 713891, 713888, 713894 OMS 714399, 714400 | August | 2011 | 2012Q1 | 2012 | 813:89058 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2011-08-20 | N | 202.3697 | N | 6 | N | N | 1.1101 | 39.4971 | 45253.0488
| ZN2835:PA33 | 727 | 768.1401 | 45.77 | 1.0566 | 45.77 | 19563 | 9644 | 713985 | 2011-08-21 09:27 | 2011-08-21 11:00 | 93 | 11kV | 149841 | 2073 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Zn.14892 Charmhaven Pnl.16 feeder tripped on: Basler 51B + C Overcurrent, timing relay, lockout. (CB16 auto close defect) Remarks: Roadside insulator disc shattered on AB41807. 11kV feeder from AB41807 to AB43714 tee PT11702 isolated and danger tabbed. PT11702 is in LV// | August | 2011 | 2012Q1 | 2012 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2011-08-21 | N | 72.2822 | N | 2 | N | N | 1.1101 | 39.4971 | 109499.3832
| ZN2835:PA34 | 22 | 563.0557 | 43.47 | 25.5934 | 43.47 | 19004 | 4085 | 714020 | 2011-08-21 12:25 | 2011-08-21 13:20 | 55 | 11kV | 71894 | 1517 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2835 Burwood Panel 10 "russel Wentworth" fdr tripped. Relays - Earth leakage, fault check, EFI. EFI's - S3315, S46519, S8480, S4658 Remarks: Underground feeder fault between S4658 Nichol Strath to S672 Kingsland High to S5109 Agnes St to S294 Angel Rd Related jobs: #714030, 714027, 714022, 714020, 714732, 714738, 714736, 714733, 714731 | August | 2011 | 2012Q1 | 2012 | ZN2835:PA10 | ZN2835:PA10 | ZN02835/000010 | STRATHFIELD | UG | Not Veg | 2011-08-21 | N | 47.3922 | N | 2 | N | N | 1.1101 | 39.4971 | 52538.0147
| ZN2835:PA35 | 1192 | 1407.9722 | 42.51 | 1.1812 | 42.51 | 19140 | 4887 | 714127 | 2011-08-22 08:30 | 2011-08-22 09:56 | 86 | 11kV | 21442 | 251 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At ZN262 Marrickville Zn P28 Marrickville Meeks tripped on, B phase earth leakage, EFI, fault check. EFI's at S8179, S4653 Remarks: Section of UG feeder from S4653 Barkley St to S200 Princess Lymerston to Sw/A at S48230 Princess Forman to S7775 Coward Coggins to S8938 Princes George damaged by contractor in Bellevue St near Princess Hwy Tempe Related jobs: #714205, 714190,, 714162, 714158, 714157, 715143, 715247, 715211, 715205, 715248, 715149, 714127 | August | 2011 | 2012Q1 | 2012 | ZN262:PA28 | ZN262:PA28 | ZN00262/000028 | INNER WEST | UG | Not Veg | 2011-08-22 | N | 85.4263 | N | 8 | N | N | 1.1101 | 39.4971 | 15669.1812
| ZN2835:PA36 | 596 | 1098.4178 | 42.11 | 1.843 | 42.11 | 19673 | 11130 | 714130 | 2011-08-22 07:20 | 2011-08-22 10:30 | 190 | 11kV | 3230 | 17 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 117222 Generator connected at sub 17481 ran out of fuel. see report 117217. Excluded oms 714130 OMS 714905 | August | 2011 | 2012Q1 | 2012 | 232:33409 | 242:81535 | ZN00242/081535 | PORT STEPHENS | Unknown | Not Veg | 2011-08-22 | N | 190 | N | 8 | N | N | 1.1101 | 39.4971 | 2360.3887
| ZN2835:PA41 | 1418 | 1531.8649 | 36.06 | 1.0803 | 36.06 | 19169 | 5209 | 714410 | 2011-08-22 13:04 | 2011-08-22 13:44 | 40 | 11kV | 34676 | 963 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn384 Camperdown 5kv Fdr Pnl 42 Tripped on Bph Leakage Sealing-in contactor EFI EFI Nil REMARKS Cable fault front line SIGNAL GE Pa42 Trip SEE 714761 714763 exclude 714410 From To Restored DC Time S5255 S1954 5 1340 S7372 S7372 1 1344 | August | 2011 | 2012Q1 | 2012 | ZN384:PA42 | ZN384:PA76 | ZN00384/000076 | SYDNEY | UG | Not Veg | 2011-08-22 | N | 36.0083 | N | 8 | N | N | 1.1101 | 39.4971 | 25340.198
| ZN2835:PA42 | 2 | 498.8507 | 39.92 | 249.4253 | 39.92 | 18741 | 1442 | 714365 | 2011-08-22 11:55 | 2011-08-22 18:30 | 395 | 11kV | 207591 | 1948 | HV | Excavation 3rd Party | 3rd Party Impact | UGOH | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.18 feeder tripped and locked out on: EF trip, EFI, lock out Field EFI: S.12682 Remarks: UGOH cable damaged by AGL contractor between AB44655 and AB44856 tee sub 14847 Bungoona Broadwwater (restored to LV via MG) | August | 2011 | 2012Q1 | 2012 | ZN12570:PA18 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | UG | Not Veg | 2011-08-22 | N | 106.5662 | N | 8 | N | N | 1.1101 | 39.4971 | 151701.3799
| ZN2835:PA43 | 4 | 633.2468 | 39.92 | 158.3117 | 39.92 | 19418 | 8424 | 714621 | 2011-08-22 18:19 | 2011-08-22 20:07 | 108 | 11kV | 648 | 6 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | LID 117226 no protection operation feeder isolated to repair ohm at pole FO-70025 see report # 117225 Excluded OMS 714621, 714933 OMS 714939 | August | 2011 | 2012Q1 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-08-22 | N | 108 | N | 8 | N | N | 1.1101 | 39.4971 | 473.5393
| ZN2835:PA8 | 2 | 0 | 39.92 | 0 | 39.92 | 20195 | 16890 | 714614 | 2011-08-22 18:08 | 2011-08-22 20:30 | 142.0167 | 11kV | 22012.5833 | 155 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | At CP.1555 Hood Av 11kV fuse switch had tripped no fuses were blown. REMARKS: At CP.1555 Hood Av no fuses found blown but fues switch was found off. After checking S.1993 Schofield Av fuse switch was closed upon returning to S.1993 loud buzz was heard. Fuse SW at CP.1555 was switched off. No apparent cause was located. | August | 2011 | 2012Q1 | 2012 | ZN690:PA12 | ZN690:PA4 | ZN00690/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-08-22 | N | 142.0167 | N | 8 | N | N | 1.1101 | 39.4971 | 16086.1466
| ZN2835:PA9 | 495 | 844.7758 | 47.35 | 1.7066 | 47.35 | 20040 | 15511 | 714541 | 2011-08-22 15:32 | 2011-08-22 22:00 | 388 | 11kV | 388 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117225 no protection operation oms # 714541 mains down from pole FO-70025 to sub 51601. see report # 117226 | August | 2011 | 2012Q1 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-08-22 | N | 388 | N | 8 | N | N | 1.1101 | 39.4971 | 283.539
| ZN7900:PA1 | 546 | 632.1847 | #N/A | 1.1578 | 39.4971 | 19594 | 9814 | 714657 | 2011-08-22 22:34 | 2011-08-22 23:59 | 85 | 11kV | 60737 | 761 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | Zn342 PAddington Pa23 fdr tripped on RELAY BCph O/C EF, EFI SIGNALS 11kv trip, Tx4GE EFI S7839 S3495 REMARKS 11kV UG fdr fault from S3495 to S292 to S3377. Ausgrid Contractor hit cable in Oxford st nr Elizabeth st Paddington SEE 714771 714769 exclude 714657 From To Restored DC Time Zn342:Pa23 S3495 2 2347 S292 S292 1 2359 | August | 2011 | 2012Q1 | 2012 | ZN342:PA23 | ZN342:PA23 | ZN00342/000023 | WOOLLAHRA | UG | Not Veg | 2011-08-22 | N | 79.8121 | N | 8 | N | N | 1.1101 | 39.4971 | 44384.8082
| ZN7900:PA11 | 888 | 1064.6312 | 42.13 | 1.1989 | 42.13 | 20006 | 14977 | 714737 | 2011-08-23 09:06 | 2011-08-23 09:44 | 38 | 11kV | 6650 | 175 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 Zetland 11kv Pa15 Tripped on short Translay EFI Fault Check Feild EFI's NIL Cable failure from S188 to S5862 to S999 See 715607 exclude 714737 From To Restored DC Time S338 S5862 5 0944 | August | 2011 | 2012Q1 | 2012 | ZN188:PA15 | ZN188:PA33 | ZN00188/000033 | SYDNEY | UG | Not Veg | 2011-08-23 | N | 38 | N | 3 | N | N | 1.1101 | 39.4971 | 4859.6239
| ZN7900:PA12 | 1719 | 1801.9534 | 48.44 | 1.0483 | 48.44 | 19603 | 10147 | 714754 | 2011-08-23 09:23 | 2011-08-23 10:45 | 82 | 11kV | 51300 | 765 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN.9700 Kirrawee, P-16 "Bath Pres" 11kV feeder tripped, reclosed and locked out on: Timed Earth Fault, EFI, Lockout, Timing SIGNALS: 11kv Trip, Zone Earth, Group Earth REMARKS: Suspect UG fdr fault ZN.9700 Kirawee P-16 to S.9013 Bath Pres tee to S.9902 Bath Muttana | August | 2011 | 2012Q1 | 2012 | ZN9700:PA16 | ZN9700:PA16 | ZN09700/000016 | SUTHERLAND | UG | Not Veg | 2011-08-23 | N | 67.0588 | N | 3 | N | N | 1.1101 | 39.4971 | 37488.5269
| ZN7900:PA14 | 406 | 752.2781 | #N/A | 1.8529 | 39.4971 | 19373 | 7988 | 715069 | 2011-08-23 22:47 | 2011-08-24 00:28 | 101 | 11kV | 273843 | 2870 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.10999 Kogarah P-12 "Queen Vic Washington" fdr tripped, reclosed, & locked out on. SIGNALS: Earth fault, reclose lockout, EFI REMARKS: Not ascertain. Mains to patrol. At ZN.10999 Kogarah P-12 "Queen Vic Washington" fdr tripped, reclosed, & locked out on. SIGNALS: Earth fault, reclose lockout, EFI REMARKS: Not ascertain. Mains to patrol. | August | 2011 | 2012Q1 | 2012 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Veg | 2011-08-23 | N | 95.4157 | N | 3 | N | N | 1.1101 | 39.4971 | 200116.3874
| ZN7900:PA15 | 479 | 568.4739 | #N/A | 1.1868 | 39.4971 | 19758 | 12453 | 715503 | 2011-08-24 21:16 | 2011-08-24 22:10 | 54 | 11kV | 91206 | 1689 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 262 Marrickville Panel #15 Harrison Enfield fdr tripped on: Relays: Earth leakage, EFI, Fault check Signals: ZE, Tx4 GE, 11Kv trip Field EFI's: Nil Remarks: Suspect UG fault between panel 15 @ S262 Marrickville and S3058 Harrison Enfield "SWA" Related jobs: #715572, 715503 | August | 2011 | 2012Q1 | 2012 | ZN262:PA15 | ZN262:PA15 | ZN00262/000015 | INNER WEST | UG | Not Veg | 2011-08-24 | N | 54 | N | 1 | N | N | 1.1101 | 39.4971 | 66650.6547
| ZN7900:PA16 | 1047 | 1008.766 | #N/A | 0.96348 | 39.4971 | 19236 | 6345 | 715510 | 2011-08-25 01:26 | 2011-08-25 02:24 | 58 | 11kV | 36952 | 652 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S.3472 Sefton Panel 29 "4410 Joanne Court" feeder tripped on: Relays: B and C phase IOC, B and C phase time, Earth IOC, Fault check, Reclose timing and lockout Signals: 11KV trip, ZE, TX2 GE Fields EFI's: S4410, S8974 Remarks: Suspect UG cable fault from S8974 Carlingford St "SWB" to S4325 PMG Carlingford St "SWA" to S6819 Clapham Yamma "SWB" Related jobs: #715612, 715609, 715510 | August | 2011 | 2012Q1 | 2012 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-08-25 | N | 56.6748 | N | 6 | N | N | 1.1101 | 39.4971 | 27003.4317
| ZN7900:PA17 | 315 | 927.1625 | #N/A | 2.9434 | 39.4971 | 19962 | 14497 | 715526 | 2011-08-25 07:09 | 2011-08-25 12:18 | 309 | 11kV | 23052 | 172 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117249 1 fault operation 3 phase Overcurrent, Earth fault EVENT LOG INDICATES NO RECLOSE PLEASE INVESTIGATE. CABLE FAULT AT SUB 29341 BECKER SUB SECTION ISOLATED TO REPLACE 3 X LA'S. Excluded OMS 715526, 715527 OMS 716197, 716200, 716201 | August | 2011 | 2012Q1 | 2012 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2011-08-25 | N | 134.0233 | N | 6 | N | N | 1.1101 | 39.4971 | 16845.7217
| ZN7900:PA19 | 777 | 1100.1492 | 45.57 | 1.4159 | 45.57 | 19857 | 13365 | 715803 | 2011-08-25 13:40 | 2011-08-25 14:15 | 35 | 11kV | 70 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117255 B phase DOLF : 16Amp. reading 248 volts 0 Amp. Excluded OMS 715803 OMS 716213 | August | 2011 | 2012Q1 | 2012 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2011-08-25 | N | 35 | N | 6 | N | N | 1.1101 | 39.4971 | 51.1539
| ZN7900:PA2 | 1725 | 1091.4758 | 41.39 | 0.63274 | 41.39 | 18868 | 2726 | 715766 | 2011-08-25 12:54 | 2011-08-25 15:20 | 146 | 11kV | 730 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117257 A & B phase DOLF : 16Amp. Excluded OMS 715766 OMS 716208 | August | 2011 | 2012Q1 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2011-08-25 | N | 146 | N | 6 | N | N | 1.1101 | 39.4971 | 533.4625
| ZN7900:PA20 | 94 | 1073.8451 | #N/A | 11.4239 | 39.4971 | 20028 | 15332 | 715922 | 2011-08-25 17:22 | 2011-08-25 18:05 | 42.7833 | 11kV | 14533.5167 | 516 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 117260 ABS 951 did not fully close during S.I. 16064. | August | 2011 | 2012Q1 | 2012 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2011-08-25 | N | 28.1657 | N | 6 | N | N | 1.1101 | 39.4971 | 10620.6653
| ZN7900:PA23 | 415 | 599.6519 | #N/A | 1.4449 | 39.4971 | 19908 | 13834 | 715964 | 2011-08-25 20:22 | 2011-08-25 21:21 | 59 | 11kV | 19566 | 340 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 25 Tripped on B phase EF, FC and EFI. Signals: 11kV Trip Cause: Suspect UG cable fault between S3750 and S5423 and S35025. See OMS716948 716949 715964 | August | 2011 | 2012Q1 | 2012 | ZN8000:PA25 | ZN35500:PA26 | ZN35500/000026 | RYDE | UG | Not Veg | 2011-08-25 | N | 57.5471 | N | 6 | N | N | 1.1101 | 39.4971 | 14298.2557
| ZN7900:PA24 | 878 | 1168.7842 | 46.51 | 1.3312 | 46.51 | 20053 | 15629 | 715989 | 2011-08-26 00:15 | 2011-08-26 04:15 | 240 | 11kV | 97490 | 1349 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117262 1 fault operation A Phase Overcurrent, Sensitive Earth fault OHM down at pole IV-30349. Excluded OMS 715989 OMS 716141 | August | 2011 | 2012Q1 | 2012 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2011-08-26 | N | 72.2683 | N | 2 | N | N | 1.1101 | 39.4971 | 71242.8165
| ZN7900:PA3 | 258 | 245.5987 | 42.26 | 0.95193 | 42.26 | 20090 | 15900 | 716246 | 2011-08-26 14:00 | 2011-08-26 16:55 | 175 | 11kV | 3500 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117267 3 phase interruption Outage for safety clearance to repair 33kV to Mandalong mine on LID outage 117266 - OMS 717216 - Burnt tapping at ABS 16562 Excluded OMS 716246 | August | 2011 | 2012Q1 | 2012 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2011-08-26 | N | 175 | N | 2 | N | N | 1.1101 | 39.4971 | 2557.6968
| ZN7900:PA6 | 954 | 1155.0126 | 42.11 | 1.2107 | 42.11 | 18873 | 2829 | 716401 | 2011-08-27 01:05 | 2011-08-27 07:20 | 375 | 11kV | 40500 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117272 DOLF : 31Amp Excluded OMS 716401, 716409 OMS 717222 | August | 2011 | 2012Q1 | 2012 | 225:13444 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Veg | 2011-08-27 | N | 375 | N | 3 | N | N | 1.1101 | 39.4971 | 29596.2055
| ZN7900:PA7 | 893 | 1726.3611 | 47.66 | 1.9332 | 47.66 | 20027 | 15311 | 716408 | 2011-08-27 06:33 | 2011-08-27 11:10 | 276.6 | 11kV | 84825.95 | 667 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of P-8R "AB 35399 etc" REMARKS: 11kV centre phase bond off at LK 35318 | August | 2011 | 2012Q1 | 2012 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2011-08-27 | N | 127.1753 | N | 3 | N | N | 1.1101 | 39.4971 | 61988.3023
| ZN7900:PA9 | 522 | 590.9448 | #N/A | 1.1321 | 39.4971 | 19685 | 11374 | 716545 | 2011-08-27 16:15 | 2011-08-27 16:25 | 10 | 11kV | 120 | 12 | HV | Vandalism | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 117277 Sub interrupted to replace stolen earth wire. Excluded OMS Job No. 716545. OMS 717236 | August | 2011 | 2012Q1 | 2012 | 228:7490 | 229:34983 | ZN00229/034983 | PORT STEPHENS | Unknown | Not Veg | 2011-08-27 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN384:PA2 | 865 | 800.9535 | 47.6 | 0.92596 | 47.6 | 20406 | 20192 | 716654 | 2011-08-28 12:05 | 2011-08-28 12:50 | 45 | 11kV | 81045 | 1801 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of Pnl.22 ex Zn.12610 Long jetty - Beyond AB 40832 Remarks: Centre phase - zone side bond at AB40832 has burnt off | August | 2011 | 2012Q1 | 2012 | ZN12610:PA22 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2011-08-28 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 59225.2956
| ZN384:PA22 | 317 | 196.3881 | 41.44 | 0.61952 | 41.44 | 18860 | 2650 | 716711 | 2011-08-28 17:50 | 2011-08-28 19:01 | 71 | 11kV | 49911 | 777 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman Pnl 9 "Clifford Spit No 2." feeder tripped on A phase IOC, Earth Fault with Fault check Relay & efi. Field efis operated @ subs 6542, 2724, 6657, 6672 & 35516 UG Cable fault between Sub 25516 Military Albion, Sub 8432 Mandalong Lavoni & Sub 4324 RSL Mosman | August | 2011 | 2012Q1 | 2012 | ZN180:PA9 | ZN180:PA9 | ZN00180/000009 | MOSMAN | UG | Not Veg | 2011-08-28 | N | 64.2355 | N | 3 | N | N | 1.1101 | 39.4971 | 36473.4867
| ZN384:PA32 | 38 | 101.6789 | 49.93 | 2.6758 | 49.93 | 19624 | 10437 | 716724 | 2011-08-28 20:43 | 2011-08-28 21:45 | 62 | 11kV | 27776 | 448 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn1788 Matraville 11kv fdr pa37 tripped on Earth & EFI SIGNALS: 11kv trip, Tx2GE & ZE EFI: Nil 11kv fdr fault from ZN1788:Pa37 to S35450 to S2672 From To Restored DC Time S8627 S35450 6 2145 See 717247, 716724,5,30,32 related w/ 716727,49 | August | 2011 | 2012Q1 | 2012 | ZN1788:PA37 | ZN1788:PA70 | ZN01788/000070 | RANDWICK | UG | Not Veg | 2011-08-28 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 20297.8815
| ZN384:PA4 | 318 | 352.4695 | 45.75 | 1.1084 | 45.75 | 18866 | 2700 | 717085 | 2011-08-29 15:25 | 2011-08-29 16:25 | 60 | 11kV | 3360 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117287 C Phase section isolated to repair mains. dead end broken and hanging by tapping. Excluded OMS 717085 OMS 717393 | August | 2011 | 2012Q1 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-08-29 | N | 60 | N | 1 | N | N | 1.1101 | 39.4971 | 2455.3889
| ZN384:PA62 | 11 | 286.7987 | #N/A | 26.0726 | 39.4971 | 18960 | 3511 | 717188 | 2011-08-30 00:54 | 2011-08-30 04:20 | 206 | 11kV | 104776 | 1182 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Recloser CP46117 Balaclava Vimera tripped and locked out on SEF. Cause; Vehicle Hit pole in West Pde Eastwood. See OMS 717429 717432 717433 | August | 2011 | 2012Q1 | 2012 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | PARRAMATTA | OH | Not Veg | 2011-08-30 | N | 88.643 | N | 4 | N | N | 1.1101 | 39.4971 | 76567.2104
| ZN384:PA63 | 353 | 226.683 | 39.3 | 0.64216 | 39.3 | 19732 | 12056 | 717301 | 2011-08-30 10:52 | 2011-08-30 12:05 | 73 | 11kV | 146 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117296 A & B Phase DOLF : 10Amp Excluded OMS 717301 OMS 717713 | August | 2011 | 2012Q1 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2011-08-30 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 106.6925
| ZN384:PA65 | 324 | 1382.7183 | 39.98 | 4.2676 | 39.98 | 20115 | 16085 | 717388 | 2011-08-30 13:33 | 2011-08-30 14:00 | 27 | 11kV | 270 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Pnl.2 Lisarow Zone - PT.18748 Pollard Wattle Tree - B Phase 31.5 Amp HDO blown (Batch #1004) Remarks: Faulty crimp connections | August | 2011 | 2012Q1 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2011-08-30 | N | 27 | N | 4 | N | N | 1.1101 | 39.4971 | 197.308
| ZN384:PA66 | 9 | 348.2718 | #N/A | 38.6969 | 39.4971 | 19830 | 13014 | 717573 | 2011-08-30 18:35 | 2011-08-30 18:50 | 15 | 11kV | 4380 | 292 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117301 The live line crew on Reconnect SI 15920 found a hazard preventing the live line crew from making taps as planned at pole JU-12221. This required subs 10775, 13618 and 7993 to suffer this short interruption to allow the taps to be re-made. Other subs in the planned outage on SI 15920 also had longer than planned interruptions. Refer control room SI 15920 for details or see planned interruptions 117298 and 117299 for details.. Excluded OMS 717573, 717574, 717578 OMS 717676, 717677 | August | 2011 | 2012Q1 | 2012 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2011-08-30 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 3200.7748
| ZN384:PA69 | 2 | 398.3138 | #N/A | 199.1569 | 39.4971 | 19382 | 8099 | 717616 | 2011-08-31 04:50 | 2011-08-31 05:17 | 27 | 11kV | 6507 | 241 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117304 2 fault operations. Excluded OMS 717616 OMS 717687 | August | 2011 | 2012Q1 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2011-08-31 | N | 27 | N | 4 | N | N | 1.1101 | 39.4971 | 4755.1237
| ZN384:PA70 | 2399 | 1330.4543 | 35.11 | 0.55459 | 35.11 | 19072 | 4469 | 717611 | 2011-08-31 00:47 | 2011-08-31 05:50 | 303 | 11kV | 15450 | 652 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | On 11kV PT.12164 the A and B phase 31.5 amp fuses operated due to possum on PT.12164. Recloser 46529 tripped and reclosed on IOC | August | 2011 | 2012Q1 | 2012 | ZN12580:PA1 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2011-08-31 | N | 23.6963 | N | 4 | N | N | 1.1101 | 39.4971 | 11290.4043
| ZN384:PA71 | 696 | 282.5145 | #N/A | 0.40591 | 39.4971 | 19303 | 7330 | 717802 | 2011-08-31 11:09 | 2011-08-31 12:34 | 85 | 11kV | 62404 | 766 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills. Panel 6 tripped reclosed tripped and locked out on C phase IOC and Timed O/C, Earth Faultr, EFI and Reclose timing and lockout. Cause: UG cable failure between S5840 and S47571 Abnormal Switching AB1414 Closed SW/A at S4490 Open. See OMS 718254 718260 718258 717873/871/825/875/809/802 | August | 2011 | 2012Q1 | 2012 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | UG | Not Veg | 2011-08-31 | N | 81.4674 | N | 4 | N | N | 1.1101 | 39.4971 | 45603.0026
| ZN384:PA73 | 637 | 999.9843 | #N/A | 1.5698 | 39.4971 | 19190 | 5480 | 717728 | 2011-08-31 09:30 | 2011-08-31 13:00 | 210 | 11kV | 84349 | 1294 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12620Noraville Pnl.8 feeder tripped on Overcurrent and Earth Fault, EFI Remarks: Magpie committed suicide on 11kv tee off pole to PT.12751. No damage to mains. See # 718305 for realted outage on PT11022 Dist #1 - dist burnt down adjacent to pnl.8 feeder | August | 2011 | 2012Q1 | 2012 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2011-08-31 | N | 65.1847 | N | 4 | N | N | 1.1101 | 39.4971 | 61639.7613
| ZN384:PA74 | 200 | 118.1918 | 38.91 | 0.59096 | 38.91 | 20181 | 16727 | 718130 | 2011-09-01 01:32 | 2011-09-01 02:40 | 68 | 11kV | 42805 | 1223 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 117319 Trip & reclose Feeder 507:80917 1 fault operation Overcurrent Car hit pole GS-62199 Feeder 507:80917 Isolated at 2:06 for safety reasons. Feeder interrupted to isolate mains on crossarm & low mains. Refer OMS 718226, 718224 Excluded OMS 718130 117319 Trip & reclose 1 fault operation Overcurrent Car hit pole GS-62199 Excluded OMS 718130 | September | 2011 | 2012Q1 | 2012 | 507:80917 | 507:80917 | ZN00507/080917 | CESSNOCK | OH | Not Veg | 2011-09-01 | N | 35 | N | 6 | N | N | 1.1101 | 39.4971 | 31280.6315
| ZN384:PA75 | 2 | 25.3874 | #N/A | 12.6937 | 39.4971 | 19170 | 5212 | 718133 | 2011-09-01 05:02 | 2011-09-01 07:33 | 151 | 11kV | 277173 | 2016 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.10995 Riverwood P-2 "Bonds Rd" fdr tripped, reclosed and locked out on: RELAYS: A phase Inst Overcurrent, with reclose timing relay & lockout SIGNALS: 11kV trip, AC Aux supply fail, TX.1,2,3 no volts, battery defect. FIELD EFIs: S.48648 Riverwood Aux #1 REMARKS: Feeder patrolled & fault not ascertained. Numerous unknown LV//s found in & removed, after feeding into fault causing LV Dist to melt down. | September | 2011 | 2012Q1 | 2012 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Veg | 2011-09-01 | N | 137.4866 | N | 6 | N | N | 1.1101 | 39.4971 | 202549.8532
| ZN384:PA76 | 2396 | 1818.6005 | 39.01 | 0.75902 | 39.01 | 20023 | 15261 | 718793 | 2011-09-01 05:02 | 2011-09-01 07:42 | 160 | 11kV | 13200 | 128 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | At ZN.10995 Riverwood P-2 "Bonds Rd" fdr tripped, reclosed and locked out on: RELAYS: A phase Inst Overcurrent, with reclose timing relay & lockout SIGNALS: 11kV trip, AC Aux supply fail, TX.1,2,3 no volts, battery defect. FIELD EFIs: S.48648 Riverwood Aux #1 REMARKS: Feeder patrolled & fault not ascertained. Numerous unknown LV//s found in & removed, after feeding into fault causing LV Dist to melt down. | September | 2011 | 2012Q1 | 2012 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | UG | Not Veg | 2011-09-01 | N | 103.125 | N | 6 | N | N | 1.1101 | 39.4971 | 9646.1707
| ZN384:PA79 | 33 | 1030.9886 | 42.81 | 31.2421 | 42.81 | 19289 | 7269 | 718328 | 2011-09-01 11:49 | 2011-09-01 12:43 | 54 | 11kV | 3024 | 56 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.11756 Penang Brisbane Water - Centre Phase 31.5A HDO fuse operated Remarks: HR HDO fuse carrier - New carrier replaced by DOp | September | 2011 | 2012Q1 | 2012 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2011-09-01 | N | 54 | N | 6 | N | N | 1.1101 | 39.4971 | 2209.85
| ZN384:PA80 | 485 | 279.8831 | #N/A | 0.57708 | 39.4971 | 19084 | 4533 | 718447 | 2011-09-01 15:37 | 2011-09-01 17:50 | 133 | 11kV | 133 | 1 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117326 B Phase DOLF : 10Amp. Replaced 3 x Fuses Excluded OMS 718447 OMS 718742 | September | 2011 | 2012Q1 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-09-01 | N | 133 | N | 6 | N | N | 1.1101 | 39.4971 | 97.1925
| ZN384:PA81 | 672 | 1109.8485 | 41.28 | 1.6516 | 41.28 | 20277 | 18139 | 718548 | 2011-09-01 22:28 | 2011-09-01 23:30 | 62 | 11kV | 86695 | 1816 | HV | Animal Possum | Animal | Circuit Breaker | Unplanned | Unselected | N | LID 117329 2 fault operations A phase Overcurrent Possum at Pole Sw-20586. Excluded OMS Job Nos. 718548, 718556 & 718542. OMS 718732, 718734 | September | 2011 | 2012Q1 | 2012 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Not Veg | 2011-09-01 | N | 47.7395 | N | 6 | N | N | 1.1101 | 39.4971 | 63354.1489
| ZN690:PA10 | 1228 | 893.0173 | 36.42 | 0.72721 | 36.42 | 19239 | 6413 | 718897 | 2011-09-02 16:30 | 2011-09-02 19:30 | 180 | 11kV | 180 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 117335 Single phase DOLF : 3Amp Defective surge arrestor. replaced Excluded OMS 718897 OMS 719937 | September | 2011 | 2012Q1 | 2012 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2011-09-02 | N | 180 | N | 2 | N | N | 1.1101 | 39.4971 | 131.5387
| ZN690:PA11 | 1823 | 1121.7268 | 31.71 | 0.61532 | 31.71 | 18870 | 2771 | 719250 | 2011-09-03 13:56 | 2011-09-03 15:13 | 77 | 11kV | 43468 | 1592 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At ZN.9037 Miranda P-2 "Sylvania Heights" fdr tripped & reclosed on A phase IOC timing and lockout. FIELD EFIs: S.9531 RELAYS: EFI REMARKS: Roadside bond off at AB.35840 | September | 2011 | 2012Q1 | 2012 | ZN9037:PA2 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | OH | Not Veg | 2011-09-03 | N | 27.304 | N | 3 | N | N | 1.1101 | 39.4971 | 31765.1323
| ZN690:PA12 | 2016 | 1367.2647 | 34.08 | 0.67821 | 34.08 | 19606 | 10275 | 719285 | 2011-09-03 16:12 | 2011-09-03 18:16 | 124 | 11kV | 187550 | 1666 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 2310 Punchbowl Panel No.31 "Roselands No.4" feeder opened on Earth Fault with EFI Zone Earth, No.4 Group Earth, 11KV trip Field EFI's operated @ Subs 4689, 2856, 3435, 2625 Remarks: 11kv UG cable fault located between Sub 2625 Hillard Street & Sub 2867 Edna King Georges Related jobs: #719285, 719525, 719527, 719521 | September | 2011 | 2012Q1 | 2012 | ZN2310:PA31 | ZN35800:PA2 | ZN35800/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-09-03 | N | 112.575 | N | 3 | N | N | 1.1101 | 39.4971 | 137056.0082
| ZN690:PA14 | 2127 | 1377.9426 | 35.8 | 0.64783 | 35.8 | 19988 | 14889 | 718953 | 2011-09-02 22:59 | 2011-09-03 19:40 | 1241 | 11kV | 115451 | 1094 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S129 Hunters Hill Panel 9 Tripped reclosed tripped and locked out on A phase IOC and Timed O/C, Earth fault, Timing relay Suspect UG cable fault from S7636 to LB399 tee S7289 tee PT1837 See OMS 720087 720090 720093 720092 | September | 2011 | 2012Q1 | 2012 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | UG | Not Veg | 2011-09-02 | N | 105.5311 | N | 2 | N | N | 1.1101 | 39.4971 | 84368.1856
| ZN690:PA15 | 1024 | 1259.9157 | 43.86 | 1.2304 | 43.86 | 19392 | 8196 | 719325 | 2011-09-03 22:47 | 2011-09-04 00:05 | 78 | 11kV | 60918 | 781 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | REC.35756 Bundeena tripped, reclosed, tripped, reclosed, tripped and locked out on earth fault. Ex P-11 "S.9755 Ewos Waratah etc" fdr from ZN.9118 Cronulla. REMARKS: # x LA's defective @ UGOH on The Esplande CC1: 22-"Refer to SOp" | September | 2011 | 2012Q1 | 2012 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2011-09-03 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 44517.0776
| ZN690:PA17 | 1291 | 878.2625 | 37.51 | 0.6803 | 37.51 | 19006 | 4099 | 731393 | 2011-09-04 00:59 | 2011-09-04 01:48 | 49 | 11kV | 12053 | 246 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At ZN.10999 Kogarah P-7 "S.10613 Carlton Short" fdr tripped, reclosed on. RELAYS: Earth fault with EFI & reclose timing lockout SIGNALS: 11kV trip at S.10925 Forest Water Board SW A and SW B tripped on earth fault. REMARKS: Car hit pole in Croyden Rd near Forest Rd. | September | 2011 | 2012Q1 | 2012 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | GEORGES RIVER | OH | Not Veg | 2011-09-04 | N | 48.9959 | N | 2 | N | N | 1.1101 | 39.4971 | 8807.9769
| ZN690:PA18 | 1194 | 2210.364 | #N/A | 1.8512 | 39.4971 | 19904 | 13773 | 719342 | 2011-09-04 01:50 | 2011-09-04 02:33 | 43.0667 | 11kV | 20327.4667 | 472 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | ZN.10990 Arncliffe P-5 "S.10407 Eden Burrows" fdr tripped, reclosed, tripped & locked out on RELAYS: EF, Lockout, Reclose, EFI. SIGNALS: 11kV trip FIELD EFIs: S.10407, S.10803, S.10615, S.10742 REMARKS: 11kV fdr from S.10742 Arncliffe Willis No.1 to S.10145 Lusty Bonar via S.46425 Guess Arncliffe. Defective RMI at S.46425. S.46425 found in LV//. | September | 2011 | 2012Q1 | 2012 | ZN10990:PA5 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | Unknown | Not Veg | 2011-09-04 | N | 43.0667 | N | 2 | N | N | 1.1101 | 39.4971 | 14854.7131
| ZN690:PA23 | 623 | 669.0569 | #N/A | 1.0739 | 39.4971 | 20205 | 17042 | 719573 | 2011-09-05 09:40 | 2011-09-05 11:00 | 80 | 11kV | 160 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 117352 Single phase DOLF : 3Amp. Fatigue both elements changed as per instruction. Excluded OMS 719573 OMS 720063 | September | 2011 | 2012Q1 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2011-09-05 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 116.9233
| ZN690:PA24 | 874 | 589.6569 | 42.28 | 0.67466 | 42.28 | 19986 | 14881 | 719553 | 2011-09-05 09:10 | 2011-09-05 12:27 | 197 | 11kV | 7913.9 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117358 B & C Phase DOLF : 16Amp. | September | 2011 | 2012Q1 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2011-09-05 | N | 188.4262 | N | 5 | N | N | 1.1101 | 39.4971 | 5783.2447
| ZN690:PA25 | 2485 | 1374.7975 | 31.41 | 0.55324 | 31.41 | 20317 | 19140 | 719656 | 2011-09-05 11:19 | 2011-09-05 13:15 | 116 | 11kV | 38576 | 441 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 117359 B & C Phase Instantaneous Overcurrent UGOH at pole JV-41483 Harrison St faulty. Repairs arranged. Excluded oms 719656, 719658, 719664, 710671 OMS 720023 | September | 2011 | 2012Q1 | 2012 | 220:8688 | 220:8688 | ZN00220/008688 | LAKE MACQUARIE | Unknown | Unknown | 2011-09-05 | N | 87.4739 | N | 5 | N | N | 1.1101 | 39.4971 | 28190.203
| ZN690:PA26 | 1377 | 821.8672 | 31.46 | 0.59685 | 31.46 | 20045 | 15552 | 719729 | 2011-09-05 12:44 | 2011-09-05 13:53 | 69 | 11kV | 52257 | 767 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @RoseBay Pa26 'Ian Carisle ETC FDR' tripped on Earth Fault Sealing Contactor EFI. 11kv TRIP: Tx4ZE&GE REMARKS: 11kv feeder S2407 Fernleigh Gardens to S1875 Vaucluse Rd to S35070 Gilliver Went, suspected feeder fault See 720012,4 GIS 720008,9 LV// 720007 Exclude 719729,47,62,3,4 created 720017 Cust call outside of outage window 14:21 | September | 2011 | 2012Q1 | 2012 | ZN1164:PA26 | ZN36100:PA16 | ZN36100/000016 | WOOLLAHRA | UG | Not Veg | 2011-09-05 | N | 68.1317 | N | 5 | N | N | 1.1101 | 39.4971 | 38187.8743
| ZN690:PA27 | 136 | 689.5669 | 46.25 | 5.0703 | 46.25 | 20137 | 16203 | 719955 | 2011-09-05 14:52 | 2011-09-05 15:17 | 25 | 11kV | 1950 | 78 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | REC 47746 Patonga Meroo opened by AOp for safety. Ex Pnl.13 patonga feeder from Zn.12640 Umina Remarks:REC 47746 was interrupted for safety due to loud discharge noise coming from s.12325. Discharge was found to be coming from transformer end box. Subs have stopped discharge and will book in M&R. | September | 2011 | 2012Q1 | 2012 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | UG | Not Veg | 2011-09-05 | N | 25 | N | 5 | N | N | 1.1101 | 39.4971 | 1425.0025
| ZN690:PA28 | 1786 | 1577.3062 | 39.4 | 0.88315 | 39.4 | 18842 | 2478 | 719928 | 2011-09-06 01:22 | 2011-09-06 02:15 | 53 | 11kV | 4717 | 89 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12580 Erina Pnl.13 tripped on: No 4 trip LED, EFI Remarks: 11kV UG feeder fault from Pnl.13 @ zn.12580 to S.18192 Erina Fair Coles to No 3 CAP bank to No 3 FIU | September | 2011 | 2012Q1 | 2012 | ZN12580:PA13 | ZN12580:PA13 | ZN12580/000013 | CENTRAL COAST | UG | Not Veg | 2011-09-06 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 3447.0445
| ZN690:PA3 | 531 | 765.0179 | 51.83 | 1.4407 | 51.83 | 18586 | 112 | 720049 | 2011-09-06 10:25 | 2011-09-06 11:20 | 55 | 11kV | 110 | 2 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117366 B Phase DOLF : 10Amp Magpie on bushing Excluded OMS 720049 OMS 720585 | September | 2011 | 2012Q1 | 2012 |  |  |  | MUSWELLBROOK | OH | Not Veg | 2011-09-06 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 80.3848
| ZN690:PA30 | 1847 | 1351.3664 | 37.24 | 0.73165 | 37.24 | 18689 | 1042 | 720599 | 2011-09-06 12:55 | 2011-09-06 13:25 | 30 | 11kV | 450 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117371 B Phase 11KV MAIN ON CROSS-ARM AT POLE 5J-80074. | September | 2011 | 2012Q1 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2011-09-06 | N | 30 | N | 5 | N | N | 1.1101 | 39.4971 | 328.8467
| ZN690:PA33 | 1421 | 1086.7025 | 40.86 | 0.76474 | 40.86 | 18994 | 3946 | 720293 | 2011-09-06 16:26 | 2011-09-06 18:01 | 94.5167 | 11kV | 2740.9833 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117372 Feeder isolated for repair Pin insulator pulled out of crossarm at P. MD-70304 | September | 2011 | 2012Q1 | 2012 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2011-09-06 | N | 94.5167 | N | 5 | N | N | 1.1101 | 39.4971 | 2003.0298
| ZN690:PA34 | 2371 | 1482.8139 | 39.95 | 0.6254 | 39.95 | 18563 | 0 | 720333 | 2011-09-06 18:09 | 2011-09-07 01:00 | 411 | 11kV | 7172 | 38 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Wind | N | LID 117374 2 fault operations Single phase Repaired damaged mains near pole BF-80027. Checked volts 248 on all phases. excluded OMS 720333, 720358 OMS 720631, 720632 & 720633 | September | 2011 | 2012Q1 | 2012 | 806:74076 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2011-09-06 | N | 188.7368 | N | 5 | N | N | 1.1101 | 39.4971 | 1474.4224
| ZN690:PA35 | 3336 | 2154.5709 | 38.3 | 0.64585 | 38.3 | 20021 | 15253 | 720606 | 2011-09-07 13:00 | 2011-09-07 14:50 | 110 | 11kV | 990 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117384 Section isolated to repair stranding at pole EU-61805 Excluded OMS 720606, 720607, 720609, 720610. OMS 720928 | September | 2011 | 2012Q1 | 2012 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2011-09-07 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 723.4628
| ZN690:PA36 | 1313 | 866.1632 | 31.11 | 0.65968 | 31.11 | 19121 | 4741 | 720660 | 2011-09-07 13:44 | 2011-09-07 15:32 | 108 | 11kV | 207796 | 2365 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12610 Pnl.11 tripped on: SEF with EFI EFI's: UGOHs-3 to S.14377 Remarks:11kV bond burnt off LK41198 - roadside phase on zone side | September | 2011 | 2012Q1 | 2012 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2011-09-07 | N | 87.863 | N | 6 | N | N | 1.1101 | 39.4971 | 151851.1879
| ZN690:PA4 | 1398 | 874.3281 | 31.64 | 0.62541 | 31.64 | 20322 | 19242 | 720634 | 2011-09-07 12:55 | 2011-09-07 16:40 | 225 | 11kV | 3600 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Peats Ridge Zone Pnl.4 - PT18834 George Downs Greta 0.1 - Road Side HV fuse operated Remarks: fuse failed due to fuse fatigue | September | 2011 | 2012Q1 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2011-09-07 | N | 225 | N | 6 | N | N | 1.1101 | 39.4971 | 2630.7738
| ZN690:PA5 | 599 | 795.7012 | 50.27 | 1.3284 | 50.27 | 19601 | 10077 | 720695 | 2011-09-07 14:35 | 2011-09-07 22:00 | 445 | 11kV | 13355 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Peats Ridge Pnl.2 - REC44945 lower Mangrove - tripped and locked open Remarks: Large tree cae down onto 11kV. 2 Bays HV down on ground between PT18206 and PT13747 on main line. | September | 2011 | 2012Q1 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2011-09-07 | N | 251.9811 | N | 6 | N | N | 1.1101 | 39.4971 | 9759.4401
| ZN690:PA6 | 1129 | 1123.6987 | 42.15 | 0.9953 | 42.15 | 20442 | 20438 | 720825 | 2011-09-07 21:18 | 2011-09-07 22:55 | 97.4833 | 11kV | 83029.2833 | 1537 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2602 Clovelly Pa23 "S3966 Pauling Av" tripped on RELAYS: Bph Earth Fault, EFI SIGNALS: 11kv trip Tx1 GE ZE EFI: Nil REMARKS: Suspect UG cables fault from S2602 to S2674swA From To Restored DC Time S2674swB S6581 to S3966 to S290 7 22:12 See 721016,0834 GIS 721018,20,21 Exclude 720825,32,3,4,6 | September | 2011 | 2012Q1 | 2012 | ZN2602:PA23 | ZN35600:PA19 | ZN35600/000019 | RANDWICK | UG | Not Veg | 2011-09-07 | N | 54.0204 | N | 6 | N | N | 1.1101 | 39.4971 | 60675.3513
| 214:8665 | 1398 | 1303.9504 | 35.71 | 0.93273 | 35.71 | 20257 | 17915 | 720786 | 2011-09-07 18:20 | 2011-09-07 23:05 | 285.4833 | 11kV | 3711.2833 | 13 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 117388 Car hit Pole JS-12426 Woodberry Rd, Millers Forest. Trip & Reclose recorded OMS 720995 - LID 117387 | September | 2011 | 2012Q1 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2011-09-07 | N | 285.4833 | N | 6 | N | N | 1.1101 | 39.4971 | 2712.0964
| 214:8666 | 1517 | 1122.4925 | 33.87 | 0.73994 | 33.87 | 19756 | 12451 | 720935 | 2011-09-08 09:43 | 2011-09-08 10:55 | 72 | 11kV | 30218 | 447 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn384 Camperdown Pa10 Guihen etc Fdr tripped. No relays found operated except EFI@Zn384 11kv trip Tx5GE Tx2GE See 722097,8,9,100 exclude 720935 From To Restored DC Time Zn384:Pa10 S98 1 1037 S98 S6446 1 1042 S6446 S8923 1 1051 S8923 S1088 1 1055 | September | 2011 | 2012Q1 | 2012 | ZN384:PA10 | ZN116:PA23 | ZN00116/000023 | INNER WEST | UG | Not Veg | 2011-09-08 | N | 67.6018 | N | 5 | N | N | 1.1101 | 39.4971 | 22082.4231
| 214:8667 | 972 | 936.1701 | 39.83 | 0.96314 | 39.83 | 18904 | 3153 | 721029 | 2011-09-08 11:41 | 2011-09-08 12:45 | 64 | 11kV | 320 | 5 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117404 A Phase DOLF : 10Amp Excluded OMS 721029 OMS 721298 | September | 2011 | 2012Q1 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2011-09-08 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 233.8466
| 214:8669 | 1184 | 1242.8334 | 39.44 | 1.0497 | 39.44 | 20438 | 20408 | 721204 | 2011-09-08 17:06 | 2011-09-08 18:10 | 64 | 11kV | 77856 | 1264 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | @ Zn15005 Belrose, Panel 4 "Sorlie Rd" tripped on: Relays: Sensitive Earth Leakage, EFI Signals:11kV Trip Field EFIs: Nil Suspect faulty SEL relay at Zn 15005 Belrose Panel 4 "Sorlie Rd" fedder. | September | 2011 | 2012Q1 | 2012 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | Unknown | Not Veg | 2011-09-08 | N | 61.5949 | N | 5 | N | N | 1.1101 | 39.4971 | 56894.8684
| 214:8670 | 1000 | 1107.52 | 42.54 | 1.1075 | 42.54 | 18652 | 734 | 721213 | 2011-09-08 17:24 | 2011-09-08 18:40 | 76 | 11kV | 152 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117411 A Phase DOLF : 10Amp | September | 2011 | 2012Q1 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-09-08 | N | 76 | N | 5 | N | N | 1.1101 | 39.4971 | 111.0771
| 214:8671 | 81 | 298.7657 | 62.52 | 3.6885 | 62.52 | 19473 | 8894 | 721239 | 2011-09-08 19:51 | 2011-09-09 02:00 | 369 | 11kV | 369 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 117414 Replaced faulty Transformer. Excluded OMS 721239 OMS 721311 | September | 2011 | 2012Q1 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2011-09-08 | N | 369 | N | 5 | N | N | 1.1101 | 39.4971 | 269.6543
| 214:8672 | 32 | 127.4434 | #N/A | 3.9826 | 39.4971 | 18788 | 2039 | 721280 | 2011-09-09 06:08 | 2011-09-09 08:10 | 122 | 11kV | 488 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 117415 A Phase DOLF : 10Amp. 17Amp @ 246 Volts excluded OMS 721280 OMS 722238 | September | 2011 | 2012Q1 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-09-09 | N | 122 | N | 1 | N | N | 1.1101 | 39.4971 | 356.616
| ZN15010:PA24 | 1416 | 1282.5497 | 33.52 | 0.90576 | 33.52 | 20303 | 18979 | 721675 | 2011-09-10 03:09 | 2011-09-10 08:29 | 320 | 11kV | 149551 | 1731 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn12570 Avoca Pnl.1 tripped / reclosed / tripped & locked out on: A phase timed O/C, lockout, timing relay Remarks: 1 bay of HV mains fallen into LV @ USL43513. 11kV feeder from AB42287 to AB43518 to AB43514 tee PT13766 Isolated. LV checked by EMSO mains effect repairs. | September | 2011 | 2012Q1 | 2012 | ZN12570:PA1 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2011-09-10 | N | 86.3957 | N | 4 | N | N | 1.1101 | 39.4971 | 109287.4598
| ZN15010:PA25 | 481 | 438.9176 | 31.88 | 0.91251 | 31.88 | 19205 | 5874 | 721717 | 2011-09-10 09:08 | 2011-09-10 09:20 | 12 | 11kV | 5472 | 456 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 117422 Section of 11kV feeder interupted to close by pass ABS at Bollwara Reg 38205 see SI 16072A Excluded OMS 721717 OMS 722291 | September | 2011 | 2012Q1 | 2012 | 501:48115 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2011-09-10 | N | 12 | N | 4 | N | N | 1.1101 | 39.4971 | 3998.7762
| ZN15010:PA26 | 340 | 288.619 | 31.58 | 0.84888 | 31.58 | 18642 | 703 | 721689 | 2011-09-10 08:01 | 2011-09-10 09:25 | 84 | 11kV | 84 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117421 Single phase DOLF : 10Amp Excluded OMS 721689 OMS 722262 | September | 2011 | 2012Q1 | 2012 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2011-09-10 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 61.3847
| ZN15010:PA28 | 1113 | 1038.2119 | 35.14 | 0.9328 | 35.14 | 19974 | 14652 | 721856 | 2011-09-10 19:48 | 2011-09-10 21:03 | 75.1167 | 11kV | 61682.6 | 2031 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | @ ZN.10995 Riverwood P-1 'Meadowland Rd',11kV OCB tripped and reclosed on, RELAYS: C phase IOC, timing relay, lockout relay SIGNALS: 11kV trip, REMARKS: Burnt off bond on 11kV AB 31327. Footpath phase bottom side bond flicker blade is also stuck in on same phase | September | 2011 | 2012Q1 | 2012 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2011-09-10 | N | 30.3706 | N | 4 | N | N | 1.1101 | 39.4971 | 45075.8248
| ZN15010:PA29 | 571 | 438.1128 | 29.83 | 0.76727 | 29.83 | 19099 | 4642 | 721889 | 2011-09-11 01:07 | 2011-09-11 04:30 | 203 | 11kV | 11778 | 1072 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 117430/02 C Phase Dist fuse : 315Amp Car hit pole - LV down | September | 2011 | 2012Q1 | 2012 | 213:33775 | 213:33775 | ZN00213/033775 | NEWCASTLE | OH | Not Veg | 2011-09-11 | N | 10.9869 | N | 4 | N | N | 1.1101 | 39.4971 | 8607.015
| ZN15010:PA30 | 1837 | 1659.3296 | 40.71 | 0.90328 | 40.71 | 19737 | 12253 | 721894 | 2011-09-11 04:46 | 2011-09-11 05:28 | 42 | 11kV | 84882 | 2021 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At ZN.10994 Mortdale, P-12L (formerly 48) "Mortdale Aux No.2" 11kV feeder tripped: RELAYS: 1.2.1, 52BC, 5oT BC, 5oT N SIGNALS: 11kv Trip FIELD EFIs: S.10035, S.10683, S.10901, S.10018, S.10682 & S.10581 REMARKS: Possum on 11kV UGOH above S.10324 Whitfield Seymour (Sw B) side. No damage to UGOH. CC1: 22-"Refer to SOp" | September | 2011 | 2012Q1 | 2012 | ZN10994:PA48 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2011-09-11 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 62029.262
| ZN15010:PA33 | 87 | 61.5411 | 35.32 | 0.70737 | 35.32 | 19912 | 13917 | 721988 | 2011-09-11 14:07 | 2011-09-11 14:18 | 11 | 11kV | 58927 | 5357 | HV | Staff Operation | Utility Process Issue | DC Transformer | Unplanned | Unselected | N | Transformer #3 outage at Avoca Zone DOp switching error. 1-2 Bus Section closed whilst isolating TX #3 2-3 Bus Section was the correct CB - DOp reports poorly laid out composite board across two rooms | September | 2011 | 2012Q1 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | UG | Not Veg | 2011-09-11 | N | 11 | N | 4 | N | N | 1.1101 | 39.4971 | 43062.1135
| ZN9035:PA1 | 553 | 794.0719 | 53.36 | 1.4359 | 53.36 | 18643 | 713 | 722048 | 2011-09-11 22:12 | 2011-09-11 22:53 | 41 | 11kV | 153504 | 3744 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | @ Zn 15006 Dee Why West - 11kV Pnl 12 feeder tripped Relays: Earth Fault, Frame Leakage, EFI Signals: 11kV, Zone Earth, Tx 1 H/L volts. Field EFI's: Sub 16803 S.15149 Possum on 11kV UGOH adjacent s15149 Campbell South Creek | September | 2011 | 2012Q1 | 2012 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2011-09-11 | N | 41 | N | 4 | N | N | 1.1101 | 39.4971 | 112176.1956
| ZN9035:PA10 | 611 | 957.2035 | 49.08 | 1.5666 | 49.08 | 19475 | 8901 | 722054 | 2011-09-12 00:23 | 2011-09-12 01:20 | 57 | 11kV | 25422 | 446 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.12650 West Gosford - 11kV Pnl.14R "Erina St" feeder tripped on: Earth fault, EFI, Fault Check. Nil EFIs Remarks: Possum on 11kV UGOH to S47762 | September | 2011 | 2012Q1 | 2012 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Not Veg | 2011-09-12 | N | 57 | N | 4 | N | N | 1.1101 | 39.4971 | 18577.6478
| ZN9035:PA11 | 2042 | 1889.3041 | 37.06 | 0.92522 | 37.06 | 19189 | 5442 | 722367 | 2011-09-12 12:42 | 2011-09-12 13:31 | 49 | 11kV | 1566 | 33 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | @Zn1788 Matraville:Pa21 tripped onBph Earth Fault EFI 11kv trip ZE GE UG cable fault from Pa21 to S5180 to S43854 to S7169. Contractors dug up cable See 722684,7 exclude 722367 From To Restored DC Time S6789 S7169SwA 2 1314 S5382 S5180 3 1331 | September | 2011 | 2012Q1 | 2012 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | UG | Not Veg | 2011-09-12 | N | 47.4545 | N | 4 | N | N | 1.1101 | 39.4971 | 1144.3866
| ZN9035:PA2 | 885 | 755.997 | 52.73 | 0.85423 | 52.73 | 20318 | 19166 | 722550 | 2011-09-12 19:23 | 2011-09-12 20:18 | 55 | 11kV | 77378 | 1444 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S187 Crows Nest Pa16 tripped on Earth Fault With EFI. Signals:11kV Trip. Cause: UG cable fault between S3232 to S3785 See OMS 722691 722693 722692 | September | 2011 | 2012Q1 | 2012 | ZN187:PA16 | ZN187:PA16 | ZN00187/000016 | NORTH SYDNEY | UG | Not Veg | 2011-09-12 | N | 53.5859 | N | 4 | N | N | 1.1101 | 39.4971 | 56545.5601
| ZN9035:PA4 | 2149 | 2560.496 | 52.61 | 1.1915 | 52.61 | 20342 | 19441 | 722561 | 2011-09-12 20:12 | 2011-09-12 21:33 | 81 | 11kV | 47446 | 710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills Panel 24 Tripped reclosed tripped and locked out on Relays: Earth Fault, EFI, Reclose Timing and Reclose Lockout. Abnormal Swtching: S5768 to S6159 tee S5928 O/O/S SwB at S6203 Closed CP1013 Open CP1027 Closed. See OMS 722725 722730 722728 722562/563/564/568 Cause: UG cable fault between S5568 - S6048 - S5598. Defective EFI at S5568 indicated front line feeder fault. | September | 2011 | 2012Q1 | 2012 | ZN965:PA24 | ZN965:PA24 | ZN00965/000024 | HORNSBY | UG | Not Veg | 2011-09-12 | N | 66.8254 | N | 4 | N | N | 1.1101 | 39.4971 | 34672.1374
| ZN9035:PA5 | 335 | 326.742 | #N/A | 0.97535 | 39.4971 | 20179 | 16703 | 722916 | 2011-09-13 23:31 | 2011-09-14 01:27 | 116 | 11kV | 312620 | 2870 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ Sub 3922 Drummoyne Panel #29 labelled "Sub 8351" tripped on C phase OC EFI #2 Tx GE and ZE Field EFIs S8351-S4019-S4372-S1511 Remarks: UG cable fault between Sub 4732 Rosser St Sw B to Sub 1511 Hyam Reynolds Sw A Related jobs: #722918, 722916, 722985, 722987 | September | 2011 | 2012Q1 | 2012 | ZN3922:PA29 | ZN3922:PA29 | ZN03922/000029 | INNER WEST | UG | Not Veg | 2011-09-13 | N | 108.9268 | N | 1 | N | N | 1.1101 | 39.4971 | 228453.4753
| ZN9035:PA7 | 1128 | 798.9047 | 32.38 | 0.70825 | 32.38 | 19453 | 8735 | 722921 | 2011-09-14 01:06 | 2011-09-14 06:30 | 324 | 11kV | 23976 | 74 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT2378 Day Robecq Roadside HV fuse failed due to fuse fatigue. SeeOMS 723336 722919 722921 | September | 2011 | 2012Q1 | 2012 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Not Veg | 2011-09-14 | N | 324 | N | 5 | N | N | 1.1101 | 39.4971 | 17520.9536
| ZN9035:PA8 | 123 | 1487.3038 | 39.76 | 12.0919 | 39.76 | 20095 | 15932 | 722928 | 2011-09-14 06:26 | 2011-09-14 07:45 | 79 | 11kV | 51084 | 706 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9900 Menai P-19 "Menai Exchange' tripped, reclosed and locked out on: Earth fault, EFI, SIGNALS: 11kV Trip, Zone Earth, TX.2 Grp Eth REMARKS: Suspect UG cable fault from S.9742 Coorgool Rd East to S.9426 Menai Coorgool tee to S.9760 Yates Rd | September | 2011 | 2012Q1 | 2012 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | UG | Not Veg | 2011-09-14 | N | 72.3569 | N | 5 | N | N | 1.1101 | 39.4971 | 37330.6805
| ZN3425:PA11 | 159 | 542.555 | 49.57 | 3.4123 | 49.57 | 19298 | 7321 | 723067 | 2011-09-14 11:27 | 2011-09-14 12:09 | 42 | 11kV | 44730 | 1065 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S339 Glenayr 11kv cb tripped on translay with IT send Relay @ S354 Hastongs Pde SwC Tripped with IT recieve relay Ex Panel 16 from Zn269 Waverley Remarks: 11kv cable fault from S339 tee no1 tx 11kv/415v @ S339 to S4481 See 724023 LV// 724024 exclude 723067,75 From To Restored DC Time S354 S4481 2 1209 | September | 2011 | 2012Q1 | 2012 | ZN269:PA16 | ZN36800:PA33 | ZN36800/000033 | WAVERLEY | UG | Not Veg | 2011-09-14 | N | 42 | N | 5 | N | N | 1.1101 | 39.4971 | 32687.3647
| ZN3425:PA12 | 1177 | 1455.9322 | 33.52 | 1.237 | 33.52 | 19547 | 9588 | 723085 | 2011-09-14 11:56 | 2011-09-14 18:40 | 404 | 11kV | 1129 | 5 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 117462 2 fault operations, 3 phase SEF, Overcurrent & Earth fault Tree trimmers brought mains down at pole bm-20020. section isolated for repair (grass fie started) Mark Telfer at Bayswater gen asked why did the tree trimmers not notify that they were on their site, as due to what happened they had an 11kV line tahh feel directly onto their conveyor and had difficulty contact Ausgrid to report the damage and grass fire. Mark's number is 02 65420787. The control room was nott advised tree trimmers were working in close proximity to the line at the time of the incident.Excluded OMS 723085, 723103, 7231 | September | 2011 | 2012Q1 | 2012 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Veg | 2011-09-14 | N | 225.8 | N | 5 | N | N | 1.1101 | 39.4971 | 825.0399
| ZN3425:PA15 | 1335 | 1217.4732 | 36.11 | 0.91196 | 36.11 | 20425 | 20265 | 723236 | 2011-09-14 16:49 | 2011-09-14 19:17 | 148 | 11kV | 79523 | 1107 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2602 Clovelly Pa9 tripped on: RELAYS Earth Fault (sealing contgact), Fault Check EFI SIGNALS 11kv trip Tx3 ZE GE EFI S7390 S2983 Suspect UG cable fault from S2984 to S2223 to S184 S184D3 ABC 400A in LV// at pa9 trip See 724472,5,6 Exclude 723236 From To Resotred DC Time S184 S184 1 1742 Zn2602 P9 S2984 2 1749 S1873 S2223 3 1800 S184 S184D3 1917 | September | 2011 | 2012Q1 | 2012 | ZN2602:PA9 | ZN36800:PA31 | ZN36800/000031 | WAVERLEY | UG | Not Veg | 2011-09-14 | N | 71.8365 | N | 5 | N | N | 1.1101 | 39.4971 | 58113.0629
| ZN3425:PA16 | 757 | 1009.7857 | 44.41 | 1.3339 | 44.41 | 20332 | 19350 | 723581 | 2011-09-15 14:34 | 2011-09-15 15:49 | 75 | 11kV | 118200 | 1576 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At S116 Leichhardt Panel 34 "Balmain Derby" tripped on: C phase IOC EFI fault check Remarks: Contractors for ausgrid struck 11kv feeder in leichardt zone premises Related jobs: #723611, 723606, 723605, 730156, 730155, 730152, 724436, 723581, 723591, 723590 | September | 2011 | 2012Q1 | 2012 | ZN116:PA34 | ZN116:PA12 | ZN00116/000012 | INNER WEST | UG | Not Veg | 2011-09-15 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 86377.0737
| ZN3425:PA17 | 1038 | 1928.291 | #N/A | 1.8577 | 39.4971 | 20327 | 19339 | 723639 | 2011-09-15 16:08 | 2011-09-15 16:13 | 5 | 11kV | 11406 | 2942 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S965 Pennant Hills. Pa33 and Pa38 tripped on SEL with 11kV Trip. Cause: SEL protection Auto during switching for D&R276419 Abnormal Switching: SW/B @ S5768 Open SW/A @ S6159 Open Sw/B @ S6203 Closed Sw/B @ S5568 Open Sw/B @ S6048 Open Sw/B @ S5769 Closed. | September | 2011 | 2012Q1 | 2012 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | OH | Not Veg | 2011-09-15 | N | 3.877 | N | 2 | N | N | 1.1101 | 39.4971 | 8335.1684
| ZN3425:PA18 | 632 | 1075.84 | #N/A | 1.7023 | 39.4971 | 19670 | 11109 | 723881 | 2011-09-16 13:19 | 2011-09-16 15:00 | 101 | 11kV | 6565 | 65 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117491 section isolated to repair damaged mains at sub 1299 Quorrobolong Excluded OMS 723881 OMS 724649 | September | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2011-09-16 | N | 101 | N | 1 | N | N | 1.1101 | 39.4971 | 4797.5084
| ZN3425:PA19 | 154 | 546.0453 | 53.05 | 3.5457 | 53.05 | 19438 | 8562 | 724125 | 2011-09-17 07:14 | 2011-09-17 09:30 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117499 C Phase DOLF : 10Amp. Excluded OMS 724125 (multiple subs on single property) OMS 724711 | September | 2011 | 2012Q1 | 2012 |  |  |  | MUSWELLBROOK | OH | Veg | 2011-09-17 | N | 136 | N | 5 | N | N | 1.1101 | 39.4971 | 198.7696
| ZN3425:PA21 | 59 | 504.6743 | 47.25 | 8.5538 | 47.25 | 19307 | 7346 | 724205 | 2011-09-17 13:40 | 2011-09-17 14:20 | 40 | 11kV | 146180 | 3698 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.9 tripped and locked out on: A Phase IOC and Timed OC Abnormal Switching: AB42680 CLOSED - Pnl.11 @ Avoca OPEN REC40428 CLOSED - Sw A @ S12855 OPEN Remarks: Tree trimmers dropped tree brnach on 11kV mains near 53 Willoughby St Terrigal | September | 2011 | 2012Q1 | 2012 | ZN12570:PA9 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Veg | 2011-09-17 | N | 39.5295 | N | 5 | N | N | 1.1101 | 39.4971 | 106824.0324
| ZN3425:PA22 | 1110 | 1075.9018 | 40.42 | 0.96928 | 40.42 | 20173 | 16662 | 724233 | 2011-09-17 16:50 | 2011-09-17 17:54 | 64 | 11kV | 704 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 117506 C Phase DOLF : 5Amps Element Fatigue Excluded OMS 724233, 724236 OMS 724659 | September | 2011 | 2012Q1 | 2012 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2011-09-17 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 514.4624
| ZN3425:PA23 | 741 | 661.013 | 43.92 | 0.89206 | 43.92 | 19115 | 4724 | 724257 | 2011-09-17 20:29 | 2011-09-17 21:36 | 67 | 11kV | 53133 | 859 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S129 Hunters Hill Panel 18 tripped on c phase O/L with EFI. Alarms: 11kV trip. Tx3 Group Earth, Zone Earth. Cause: Suspect cable fault from S4272 Passy Rooke SW/B to S35708 Crescent Woolwich. See OMS 724613 724626 | September | 2011 | 2012Q1 | 2012 | ZN129:PA18 | ZN129:PA47 | ZN00129/000047 | HUNTERS HILL | UG | Not Veg | 2011-09-17 | N | 61.8545 | N | 5 | N | N | 1.1101 | 39.4971 | 38828.0292
| ZN3425:PA24 | 1406 | 1133.0949 | 36.83 | 0.8059 | 36.83 | 19481 | 8963 | 724264 | 2011-09-17 21:10 | 2011-09-17 22:55 | 105 | 11kV | 69100 | 2693 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.15008 Harbord Pnl.7 "Curl Curl" feeder was opened by AOp due to HV mains on the ground Remarks: Footpath phase Cnr pitt & Granger came adrift from OH mains due to fatigue of the wire | September | 2011 | 2012Q1 | 2012 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2011-09-17 | N | 25.6591 | N | 5 | N | N | 1.1101 | 39.4971 | 50496.2419
| ZN3425:PA27 | 179 | 436.0055 | 38.17 | 2.4358 | 38.17 | 19098 | 4641 | 724275 | 2011-09-18 03:12 | 2011-09-18 04:50 | 98 | 11kV | 13126 | 1001 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | Zn.12640 Umina Pnl.15 feeder tripped & Reclosed on A Phase Overload PT13859 Ocean Beach Pozieres - A & B Phase 31.5A HDO's operated Remarks: Possum on tank of TX at PT13859 | September | 2011 | 2012Q1 | 2012 | ZN12640:PA15 | ZN12640:PA5 | ZN12640/000005 | CENTRAL COAST | OH | Not Veg | 2011-09-18 | N | 13.1129 | N | 4 | N | N | 1.1101 | 39.4971 | 9592.0936
| ZN3425:PA28 | 747 | 932.6192 | 33.82 | 1.2485 | 33.82 | 19731 | 12050 | 724323 | 2011-09-18 13:04 | 2011-09-18 13:44 | 40 | 11kV | 3516 | 162 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn.14144 Wamberal Pnl.10L REC46525 Coachwood Rd north - Tripped / Closed on A & B Phase O/C REC44582 Erina tripped / closed / locked out on A & B Phase O/C and lock out Remarks: O/S 56 Clyde Rd DOp found a branch on HV (Cleared by DOp) | September | 2011 | 2012Q1 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2011-09-18 | N | 21.7037 | N | 4 | N | N | 1.1101 | 39.4971 | 2569.3891
| ZN3425:PA30 | 1511 | 1296.803 | 35.98 | 0.85824 | 35.98 | 19568 | 9671 | 724345 | 2011-09-18 15:37 | 2011-09-18 16:55 | 77.9667 | 11kV | 155.9333 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" LID 117518 A & C Phases DOLF : 10Amp | September | 2011 | 2012Q1 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2011-09-18 | N | 77.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 113.9515
| ZN3425:PA32 | 179 | 728.2039 | 59.81 | 4.0682 | 59.81 | 19238 | 6410 | 724366 | 2011-09-18 19:07 | 2011-09-18 20:03 | 56 | 11kV | 18256 | 326 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S80 Chatswood Panel 31 tripped on IOC EFI, Fault check 11kV Trip Tx11 Group Earth. Cause: Dead possum near 11kV UGOH Abnormal Switching Pa31 at Chatswood Closed and LB2778 Open. See OMS 724536 724366 724368 | September | 2011 | 2012Q1 | 2012 | ZN1193:PA6 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Not Veg | 2011-09-18 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 13340.9463
| ZN3425:PA33 | 453 | 517.5607 | 39.72 | 1.1425 | 39.72 | 18809 | 2222 | 724400 | 2011-09-19 06:30 | 2011-09-19 08:10 | 100 | 11kV | 459.3667 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 117522 B Phase DOLF : 40Amp. Operator suspects fuse fatigue Excluded OMS 724400 OMS 725008 | September | 2011 | 2012Q1 | 2012 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2011-09-19 | N | 91.8733 | N | 3 | N | N | 1.1101 | 39.4971 | 335.6916
| ZN3425:PA34 | 671 | 1627.4541 | 40.96 | 2.4254 | 40.96 | 19598 | 9823 | 724763 | 2011-09-19 15:59 | 2011-09-19 16:09 | 10 | 11kV | 4220 | 422 | HV | Staff Operation | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 117525 Inadvertent interruption during switching SI-16349 Excluded OMS 724763, 724767, 724771, 724775, 724776 OMS 724896 | September | 2011 | 2012Q1 | 2012 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Not Veg | 2011-09-19 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 3083.8515
| ZN3425:PA35 | 1005 | 719.506 | 45.29 | 0.71593 | 45.29 | 19801 | 12794 | 724577 | 2011-09-19 15:00 | 2011-09-19 17:10 | 130 | 11kV | 390 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 117526 C Phase LV Transformer tail sub isolated to repair damaged lv transformer lead excluded OMS 724577 OMS 725015 | September | 2011 | 2012Q1 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2011-09-19 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 285.0005
| ZN3425:PA36 | 3 | 512.7568 | 39.95 | 170.9189 | 39.95 | 20367 | 19889 | 724856 | 2011-09-20 00:43 | 2011-09-20 03:30 | 167 | 11kV | 167010 | 1949 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9700 Kirrawee, P-11 the "Flora Bath" 11kV feeder, closed, tripped & locked out on: Earth Fault, lockout, timing, fault check, with 11kV trip, zone earth and TX.1 Group Earth FIELD EFIs: S.9518, 9325, 9242, 9448, 9340, 9394, 9054, 9359 & 9109 REMARKS: Suspected underground fault between S.9359 Haynet St to S.9111 Helena Forrest to S.9190 Forest Oak | September | 2011 | 2012Q1 | 2012 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | UG | Not Veg | 2011-09-20 | N | 85.6901 | N | 35 | Y | Y | 1.1101 | 39.4971 | 122045.982
| ZN3425:PA39 | 723 | 609.8135 | 38.04 | 0.84345 | 38.04 | 18834 | 2376 | 724868 | 2011-09-20 02:54 | 2011-09-20 04:30 | 96 | 11kV | 11040 | 115 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | PT.9141 Belmont St was interrupted due to fault to LV tails which set pole on fire. REMARKS: LV tails at PT.9141 Belmont St are burnt on both distributors. | September | 2011 | 2012Q1 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2011-09-20 | N | 96 | N | 35 | Y | Y | 1.1101 | 39.4971 | 8067.7064
| ZN3425:PA43 | 1362 | 1131.5289 | 35.04 | 0.83078 | 35.04 | 19149 | 4914 | 724871 | 2011-09-20 06:39 | 2011-09-20 07:14 | 35 | 11kV | 33834 | 1262 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Wind | N | At S.15005 Belrose Panel 4 Fdr CB tripped and reclosed on B and C phase OC, lockout and timing relay, 11kV trip. No Field efi's operated. At Recloser 21801 the recloser tripped and locked out on Group A active, A and B phase OC protection trip, lockout, protection trip 1. Bird shorted 11kV mains at USL.24494. Panel 4 at Belrose successfully with Recloser 21801 locked out | September | 2011 | 2012Q1 | 2012 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2011-09-20 | N | 26.8098 | N | 35 | Y | Y | 1.1101 | 39.4971 | 24724.8893
| ZN3425:PA44 | 935 | 1214.8362 | 33.79 | 1.2993 | 33.79 | 19554 | 9611 | 724887 | 2011-09-20 07:18 | 2011-09-20 09:35 | 137 | 11kV | 10105 | 112 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117540 2 fault operations Overcurrent No cause found RAGCB Sw 74203 low gas non operable. Excluded OMS 724862 OMS 725383, 725385, 725386, 725388, 725391 | September | 2011 | 2012Q1 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2011-09-20 | N | 90.2232 | N | 35 | Y | Y | 1.1101 | 39.4971 | 7384.436
| ZN3425:PA45 | 6 | 403.5052 | 40.22 | 67.2509 | 40.22 | 18664 | 782 | 724897 | 2011-09-20 08:30 | 2011-09-20 11:05 | 155 | 11kV | 310 | 2 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 117555 A & B Phase DOLF : 10Amp Excluded OMS 724897 OMS 725877 | September | 2011 | 2012Q1 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2011-09-20 | N | 155 | N | 35 | Y | Y | 1.1101 | 39.4971 | 226.5389
| ZN3425:PA46 | 200 | 891.9689 | 47.93 | 4.4598 | 47.93 | 19145 | 4899 | 725872 | 2011-09-20 04:10 | 2011-09-20 11:25 | 435 | 11kV | 9594 | 62 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 117532 3 fault operations Sensitive Earth fault Trip & Lock out. Faulty lighning arrestor at sub 51592 Excluded OMS 724862, 724867, 725029 OMS 725872, 725873, 725874 | September | 2011 | 2012Q1 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2011-09-20 | N | 154.7419 | N | 35 | Y | Y | 1.1101 | 39.4971 | 7011.0122
| ZN3425:PA7 | 429 | 475.3105 | 51.01 | 1.1079 | 51.01 | 20142 | 16250 | 724963 | 2011-09-20 09:48 | 2011-09-20 11:49 | 121 | 11kV | 38597 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117556 3 fault operations 3 phasr Instantaneous Overcurrent Tree branch on mains adjacent pole DQ-10060 Excluded OMS 724963, 724970 OMS 725890, 725892, 725893, 725894 | September | 2011 | 2012Q1 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2011-09-20 | N | 118.76 | N | 35 | Y | Y | 1.1101 | 39.4971 | 28205.5492
| ZN3425:PA8 | 273 | 2655.2585 | #N/A | 9.7262 | 39.4971 | 19226 | 6220 | 725087 | 2011-09-20 11:41 | 2011-09-20 12:36 | 55 | 11kV | 31735 | 577 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117551 1 fault operation Overcurrent Excluded OMS 725087 OMS 725698 | September | 2011 | 2012Q1 | 2012 | 260:33350 | 270:83583 | ZN00270/083583 | LAKE MACQUARIE | OH | Veg | 2011-09-20 | N | 55 | N | 35 | Y | Y | 1.1101 | 39.4971 | 23191.002
| 522:83121 | 342 | 682.4407 | 45.91 | 1.9954 | 45.91 | 20029 | 15347 | 725061 | 2011-09-20 11:29 | 2011-09-20 12:49 | 80 | 11kV | 125760 | 1572 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117552 2 fault operations B & C Phase Overcurrent Tree branch found under HV OHM Excluded OMS 725061 OMS 725691 | September | 2011 | 2012Q1 | 2012 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Veg | 2011-09-20 | N | 80 | N | 35 | Y | Y | 1.1101 | 39.4971 | 91901.6987
| 522:83123 | 1414 | 1034.7531 | 32.08 | 0.73179 | 32.08 | 18653 | 735 | 724999 | 2011-09-20 10:19 | 2011-09-20 12:50 | 151 | 11kV | 604 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 117564 Broken LL Clamp at sub 51287 | September | 2011 | 2012Q1 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2011-09-20 | N | 151 | N | 35 | Y | Y | 1.1101 | 39.4971 | 441.3854
| 522:83124 | 1434 | 1176.0916 | 36.78 | 0.82015 | 36.78 | 19815 | 12907 | 725036 | 2011-09-20 11:10 | 2011-09-20 13:30 | 140 | 11kV | 50092 | 587 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | LID 117550 2 fault operations A & B Phase Overcurrent A + B 11kV phases together at pole IV-50303. Excluded OMS 725036 OMS 725674, 725676 | September | 2011 | 2012Q1 | 2012 | 206:34438 | 206:34438 | ZN00206/034438 | LAKE MACQUARIE | OH | Not Veg | 2011-09-20 | N | 85.3356 | N | 35 | Y | Y | 1.1101 | 39.4971 | 36605.7561
| 522:83126 | 1185 | 865.2469 | 33.95 | 0.73017 | 33.95 | 18987 | 3876 | 725044 | 2011-09-20 11:25 | 2011-09-20 13:35 | 130 | 11kV | 3250 | 25 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117560 B Phase DOLF : 20Amp Excluded OMS 725053, 725044 OMS 725731 | September | 2011 | 2012Q1 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2011-09-20 | N | 130 | N | 35 | Y | Y | 1.1101 | 39.4971 | 2375.0041
| 522:83129 | 1444 | 942.1056 | 32.93 | 0.65243 | 32.93 | 20429 | 20316 | 725064 | 2011-09-20 11:24 | 2011-09-20 13:37 | 133 | 11kV | 6384 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117558 2 fault operations 3 phase Overcurrent Excluded OMS 725064 OMS 725804 | September | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2011-09-20 | N | 133 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4665.2389
| 522:83130 | 174 | 716.8096 | 44.14 | 4.1196 | 44.14 | 19095 | 4610 | 725018 | 2011-09-20 10:48 | 2011-09-20 14:00 | 192 | 11kV | 65894 | 657 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117549 2 fault operations Overcurrent Tree into Main at Pole BU-10341. Excluded oms 725018, 725021, 725022 OMS 725642, 725644, 725645 | September | 2011 | 2012Q1 | 2012 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2011-09-20 | N | 100.2953 | N | 35 | Y | Y | 1.1101 | 39.4971 | 48153.3917
| 522:83131 | 1328 | 826.3736 | 34.91 | 0.62227 | 34.91 | 18776 | 1916 | 725174 | 2011-09-20 12:40 | 2011-09-20 14:00 | 80 | 11kV | 5440 | 68 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 117557 C Phase dist fuse : 400Amp excluded OMS 725174 OMS 725701 | September | 2011 | 2012Q1 | 2012 | 258:80779 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Not Veg | 2011-09-20 | N | 80 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3975.3915
| 522:83132 | 650 | 624.2399 | 34.92 | 0.96037 | 34.92 | 18933 | 3365 | 725212 | 2011-09-20 12:59 | 2011-09-20 14:09 | 70 | 11kV | 9534 | 170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC44947 Gravenlock Rd - Tripped / Reclosed / Tripped and locked out on IOC and OC Remarks: Tree branch found on PT12036 | September | 2011 | 2012Q1 | 2012 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2011-09-20 | N | 56.0824 | N | 35 | Y | Y | 1.1101 | 39.4971 | 6967.166
| 261:81864 | 1189 | 921.1924 | 31.75 | 0.77476 | 31.75 | 20320 | 19214 | 725178 | 2011-09-20 12:42 | 2011-09-20 14:57 | 135 | 11kV | 135 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 117566 sub isolated to repair both live line clamps CC1: 06-"Urgent - O.H Mains - No others"replaced 11kv lead fron 11kv O/H main to top of dolf | September | 2011 | 2012Q1 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2011-09-20 | N | 135 | N | 35 | Y | Y | 1.1101 | 39.4971 | 98.654
| 261:81865 | 1217 | 1045.8334 | 34.52 | 0.85935 | 34.52 | 20361 | 19854 | 725343 | 2011-09-20 14:52 | 2011-09-20 15:00 | 8 | 11kV | 32 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 117568 Single phase DOLF : 10Amp Excluded OMS 725343 OMS 725936 | September | 2011 | 2012Q1 | 2012 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2011-09-20 | N | 8 | N | 35 | Y | Y | 1.1101 | 39.4971 | 23.3847
| 261:81867 | 154 | 580.2803 | #N/A | 3.7681 | 39.4971 | 19754 | 12449 | 725321 | 2011-09-20 14:23 | 2011-09-20 15:16 | 53 | 11kV | 1099 | 319 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Recloser CP427 tripped and reclosed on A and B phase O/C Recloser CP554 tripped reclosed tripped and locked out on A and B phase O/C Cause: Tree branch near PT656 Rosscommon Rd. Abnormal Switching: CP497 CP9 closed, CP65 CLosed CP1126 Open. see OMS 725697 725695 725671 725366 | September | 2011 | 2012Q1 | 2012 | ZN847:PA45 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2011-09-20 | N | 3.4451 | N | 35 | Y | Y | 1.1101 | 39.4971 | 803.1168
| 261:81870 | 1782 | 1286.3899 | 31.17 | 0.72188 | 31.17 | 19215 | 6055 | 725279 | 2011-09-20 13:55 | 2011-09-20 15:39 | 104 | 11kV | 90268 | 994 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S1673 Turramurra Panel 38 tripped and reclosed on A phase O/C and earth fault, EFI, Timing and lockout Cause: Tree branch on mains near PT2401 Morong Eurong - Removed By DOp. See OMS 725773 725774 725297 | September | 2011 | 2012Q1 | 2012 | ZN1673:PA38 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2011-09-20 | N | 90.8129 | N | 35 | Y | Y | 1.1101 | 39.4971 | 65965.1919
| 261:81876 | 1034 | 615.1445 | 29.53 | 0.59492 | 29.53 | 18837 | 2394 | 725242 | 2011-09-20 13:29 | 2011-09-20 15:45 | 136 | 11kV | 136 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 117570 C Phase Sub isolated to repair Live Line Lead | September | 2011 | 2012Q1 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2011-09-20 | N | 136 | N | 35 | Y | Y | 1.1101 | 39.4971 | 99.3848
| 261:81877 | 52 | 321.0441 | #N/A | 6.1739 | 39.4971 | 19927 | 14074 | 725317 | 2011-09-20 14:31 | 2011-09-20 15:54 | 83 | 11kV | 2122 | 26 | HV | Excavation 3rd Party | 3rd Party Impact | DC Not Transformer | Unplanned | Wind | N | @S262 Marrickville Panel 13 'S7116 Lillian Fitz' feeder tripped on Relays - Earth Fault, EFI, Fault Check Signals - 11kv trip, ZE, TX 4 GE Remarks: 11kv fdr from S7116 Lillian Fitz to S4399 Chapel Fitz to S7069 EOI No 2 VIA S5886 EOI No 1. S5886 EOI No.1 has been demolished by excavation contractors, damaging RMI, Relays & Possible TX Related jobs: #726204, 726206, 726202, 725317, 725337 | September | 2011 | 2012Q1 | 2012 | ZN262:PA13 | ZN262:PA13 | ZN00262/000013 | INNER WEST | UG | Not Veg | 2011-09-20 | N | 81.6154 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1550.695
| 261:81879 | 2264 | 1428.661 | 34.2 | 0.63103 | 34.2 | 20351 | 19589 | 725355 | 2011-09-20 14:52 | 2011-09-20 16:11 | 79 | 11kV | 33180 | 420 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | REC44999 Warner Av Tripped and locked out on: IOC and OC Trip Note: Recloser was manual at time of trip due to switching Ex Zn.12690 Berkeley Vale Pnl.12 - NOT WYONG PNL.10 - OPEN POINT CHANGE PREVIOUS WEEKEND | September | 2011 | 2012Q1 | 2012 | ZN14891:PA10 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2011-09-20 | N | 79 | N | 35 | Y | Y | 1.1101 | 39.4971 | 24246.9654
| 261:81882 | 1570 | 1619.9012 | 41.04 | 1.0318 | 41.04 | 18926 | 3340 | 725941 | 2011-09-20 15:19 | 2011-09-20 17:40 | 141 | 11kV | 1410 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117575 Single phase Line DOLF; | September | 2011 | 2012Q1 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2011-09-20 | N | 141 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1030.3864
| 261:81885 | 1068 | 1444.8805 | 48.03 | 1.3529 | 48.03 | 20118 | 16089 | 725333 | 2011-09-20 14:44 | 2011-09-20 17:42 | 178.2667 | 11kV | 52272.7667 | 805 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S.15001 Brookvale, Panel 10 tripped on OC, E/F (51 B/C) all field efi's operated. Abnormal switching | September | 2011 | 2012Q1 | 2012 | ZN15001:PA16 | ZN15001:PA16 | ZN15001/000016 | NORTHERN BEACHES | OH | Veg | 2011-09-20 | N | 64.9351 | N | 35 | Y | Y | 1.1101 | 39.4971 | 38199.3961
| 261:81886 | 798 | 673.9675 | 33.2 | 0.84457 | 33.2 | 20379 | 19969 | 725527 | 2011-09-20 14:00 | 2011-09-20 18:15 | 255 | 11kV | 6375 | 25 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117574 A Phase sub isolaled to repair hv dropper Excluded OMS 725527 OMS 725808 | September | 2011 | 2012Q1 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2011-09-20 | N | 255 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4658.662
| ZN14892:PA1 | 1245 | 1071.5131 | 34.45 | 0.86065 | 34.45 | 20346 | 19488 | 725964 | 2011-09-20 15:37 | 2011-09-20 18:15 | 158 | 11kV | 2054 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117578 Single phase DOLF : 5Amp | September | 2011 | 2012Q1 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-09-20 | N | 158 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1501.0026
| ZN14892:PA10 | 1029 | 560.2369 | 29.34 | 0.54445 | 29.34 | 19172 | 5233 | 725403 | 2011-09-20 15:24 | 2011-09-20 18:23 | 179 | 11kV | 34972 | 283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | n.12630 peats Ridge Pnl.5 tripped / reclosed / tripped and locked out on: Earth Fault, SEL and EFI Remarks: Tree branch brought down 11kV mains O/S 257 Peats Ridge Road | September | 2011 | 2012Q1 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2011-09-20 | N | 123.576 | N | 35 | Y | Y | 1.1101 | 39.4971 | 25556.5061
| ZN14892:PA12 | 225 | 135.7311 | 32.88 | 0.60325 | 32.88 | 19965 | 14621 | 725480 | 2011-09-20 16:13 | 2011-09-20 19:05 | 172 | 11kV | 172 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 117579 B Phase DOLF : 10Amp. Excluded OMS 725480 OMS 725814 | September | 2011 | 2012Q1 | 2012 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2011-09-20 | N | 172 | N | 35 | Y | Y | 1.1101 | 39.4971 | 125.6925
| ZN14892:PA13 | 1556 | 1089.0416 | 30.46 | 0.6999 | 30.46 | 19430 | 8511 | 725468 | 2011-09-20 16:03 | 2011-09-20 19:06 | 183 | 11kV | 46185 | 1566 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | At S1673 Turramurra Bond Burnt Off CP2598 (Pole PY59564) At S1673 Turramurra Panel 40 tripped on SEF. Cause: when shitching across panels 38,44 and panel 40 tripped. Abnormal switching AB1441 Open, SW/B S4723 Closed, SW/B 4703 SW B Open, CP373 SW/B Closed See OMS 725601 725797 725468 | September | 2011 | 2012Q1 | 2012 | ZN1673:PA40 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Not Veg | 2011-09-20 | N | 29.4923 | N | 35 | Y | Y | 1.1101 | 39.4971 | 33750.6358
| ZN14892:PA14 | 897 | 800.0656 | 35.59 | 0.89193 | 35.59 | 19543 | 9531 | 725081 | 2011-09-20 11:43 | 2011-09-20 19:35 | 472 | 11kV | 54361.8833 | 852 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12600 Lisarow Pnl.1 - tripped / reclosed / tripped and locked out on A & C Phase IOC, SEF, reclose timing, lock out Remarks: Tree brought down mains adjacent PT12038 | September | 2011 | 2012Q1 | 2012 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2011-09-20 | N | 63.805 | N | 35 | Y | Y | 1.1101 | 39.4971 | 39726.0609
| ZN14892:PA16 | 2031 | 1480.7004 | 31.11 | 0.72905 | 31.11 | 19046 | 4359 | 725569 | 2011-09-20 19:31 | 2011-09-20 22:07 | 156 | 11kV | 11366 | 85 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117583 1 fault operation 3 phase please do detailed patrol in daylight hours Excluded OMS 725569 OMS 725846, 725847, 725848 | September | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2011-09-20 | N | 133.7176 | N | 35 | Y | Y | 1.1101 | 39.4971 | 8305.9376
| ZN14892:PA17 | 432 | 9060.6986 | 39.59 | 20.9738 | 39.59 | 18685 | 1035 | 725849 | 2011-09-20 22:15 | 2011-09-20 23:00 | 45 | 11kV | 2544 | 85 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117585 1 fault operation 3 phase Found tree in mains near Sub 14369 on main line. | September | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2011-09-20 | N | 29.9294 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1859.0802
| ZN14892:PA19 | 1840 | 1465.9774 | 34.3 | 0.79673 | 34.3 | 19017 | 4183 | 725604 | 2011-09-21 05:01 | 2011-09-21 05:39 | 38 | 11kV | 20558 | 541 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind | N | At S965 Pennant Hills Panel 12 Tripped on A phase Timed O/C, B phase timed leakage and EFI. Cause: Linesman earthed live feeder At Ab214/ 1 flicker blade stayed closed of AB stayed closed. Modiewark failed to indicate live feeder. See OMS 726263 725604 | September | 2011 | 2012Q1 | 2012 | ZN965:PA12 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Not Veg | 2011-09-21 | N | 38 | N | 4 | N | N | 1.1101 | 39.4971 | 15023.18
| ZN14892:PA20 | 16 | 967.9643 | #N/A | 60.4978 | 39.4971 | 20256 | 17900 | 725593 | 2011-09-20 22:20 | 2011-09-21 06:00 | 460 | 11kV | 17480 | 38 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 117588 HV leads between Hazemeyer switchgear & Tx burning up, switchgear damaged requires replacement. Excluded OMS No 72559, 725859 OMS 725865 | September | 2011 | 2012Q1 | 2012 | 507:80917 | 507:80914 | ZN00507/080914 | CESSNOCK | UG | Not Veg | 2011-09-20 | N | 460 | N | 35 | Y | Y | 1.1101 | 39.4971 | 12773.8684
| ZN14892:PA21 | 1095 | 984.7297 | #N/A | 0.8993 | 39.4971 | 18816 | 2250 | 725602 | 2011-09-21 01:50 | 2011-09-21 06:25 | 275 | 11kV | 89950 | 1028 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | At S965 Pennant Hills Panel 12 tripped on A phase timed O/L, B phase timed leakage and EFI. Cause: 1 Bay of OH mains on groundbetween AB214 and AB 514 Tee PT799. HV into LV at PT799. See OMS 726224 726225 726222 | September | 2011 | 2012Q1 | 2012 | ZN965:PA12 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Not Veg | 2011-09-21 | N | 87.5 | N | 4 | N | N | 1.1101 | 39.4971 | 65732.8069
| ZN14892:PA3 | 1266 | 788.5003 | 29.59 | 0.62283 | 29.59 | 19549 | 9596 | 725714 | 2011-09-21 09:22 | 2011-09-21 10:27 | 65.0833 | 11kV | 45327.85 | 1123 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn,12650 West Gosford Pnl.9 tripped EFIs: S.13582 S14853 S18260 S18254 Remarks: Cable fault in one of the UGOH's adjacent to PT14016 - reported by customer seeing blue smoke flash out of it. GCC sewer Manns on stand by supply | September | 2011 | 2012Q1 | 2012 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | Unknown | Unknown | 2011-09-21 | N | 40.3632 | N | 4 | N | N | 1.1101 | 39.4971 | 33124.2558
| ZN14892:PA5 | 317 | 663.7089 | 60.04 | 2.0937 | 60.04 | 20186 | 16777 | 725597 | 2011-09-20 23:13 | 2011-09-21 11:00 | 707 | 11kV | 24319 | 137 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117586 3 fault operations Earth fault, Sensitive Earth fault Mains down near L/F 74748. Excluded OMS NO's 725597, 725599 & 725613 OMS 725998, 725999 | September | 2011 | 2012Q1 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-09-20 | N | 177.5109 | N | 35 | Y | Y | 1.1101 | 39.4971 | 17771.6079
| ZN14892:PA6 | 1727 | 1102.6728 | 33.34 | 0.63849 | 33.34 | 19220 | 6127 | 725967 | 2011-09-21 15:28 | 2011-09-21 16:57 | 89 | 11kV | 116585 | 1990 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.12 tripped on: Earth Fault, EFI, TX 13 Earth Fault Check EFI's: S18658 S18373 S14838 Remarks: Suspect faulty section of UG cable from S.14838 to REC 46929 See OMS # 731667 731669 731663 | September | 2011 | 2012Q1 | 2012 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | UG | Not Veg | 2011-09-21 | N | 58.5854 | N | 4 | N | N | 1.1101 | 39.4971 | 85196.8793
| ZN14892:PA8 | 909 | 1105.5253 | 45.23 | 1.2162 | 45.23 | 18666 | 795 | 726141 | 2011-09-22 07:47 | 2011-09-22 09:00 | 73.1833 | 11kV | 195 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 117598 C Phase DOLF : 20Amp. C ph 10Amp fuse replaced with 20A Excluded OMS 726141 OMS 726669 | September | 2011 | 2012Q1 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2011-09-22 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 142.5002
| ZN14892:PA9 | 357 | 1375.9401 | 39.95 | 3.8542 | 39.95 | 19478 | 8922 | 726275 | 2011-09-22 11:09 | 2011-09-22 17:00 | 351 | 11kV | 39350 | 250 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 117604 2 fault operations 3 phase Overcurrent Car hit pole IQ-71103 Tocal Rd. Excluded OMS 726275, 726331 OMS 726630, 726631 | September | 2011 | 2012Q1 | 2012 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2011-09-22 | N | 157.4 | N | 2 | N | N | 1.1101 | 39.4971 | 28755.8194
| ZN80:PA21 | 1121 | 1568.4367 | 44.58 | 1.3991 | 44.58 | 19573 | 9680 | 726518 | 2011-09-23 13:13 | 2011-09-23 14:40 | 87 | 11kV | 93018 | 1565 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S1114 North Ryde 11kV OCB pane 10 tripped on B phase OC, Earth Fault wih EFI. Cause: 11kV feeder fault between LB411 to S2115 tee S991. 11kV feeder was hit by an excavator. See OMS 728270/271/275/277/292/290/288 | September | 2011 | 2012Q1 | 2012 | ZN1114:PA10 | ZN35500:PA36 | ZN35500/000036 | RYDE | UG | Not Veg | 2011-09-23 | N | 59.4364 | N | 6 | N | N | 1.1101 | 39.4971 | 67974.8108
| ZN80:PA22 | 1498 | 966.3345 | 35 | 0.64508 | 35 | 19495 | 9052 | 726742 | 2011-09-23 12:17 | 2011-09-23 15:03 | 166 | 11kV | 1991.2667 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11373 Collies Old Mait 1.0 (ex pnl.8 Wyong) 11kV 16K footpath side Dropout fuse operated. Remarks: Fuse fatigue | September | 2011 | 2012Q1 | 2012 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2011-09-23 | N | 165.9389 | N | 6 | N | N | 1.1101 | 39.4971 | 1455.1589
| ZN80:PA24 | 1082 | 1906.9522 | 46.18 | 1.7624 | 46.18 | 19415 | 8411 | 726924 | 2011-09-23 17:02 | 2011-09-23 17:42 | 40 | 11kV | 31000 | 775 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Z.12570 Avoca Pnl.15 "Terrigal" tripped / reclosed & locked out on: B + C Phase timed O/C Remarks: Tree branch on 11kV mains O/S 2 Lake Shore Drive | September | 2011 | 2012Q1 | 2012 | ZN12570:PA15 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2011-09-23 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 22653.8857
| ZN80:PA25 | 1502 | 1020.8223 | 37.06 | 0.67964 | 37.06 | 18878 | 2879 | 726949 | 2011-09-23 17:31 | 2011-09-23 19:37 | 126 | 11kV | 32909 | 275 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117618 3 fault operations Excluded OMS 726949 OMS 728207, 728211, 728212, 728213. | September | 2011 | 2012Q1 | 2012 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2011-09-23 | N | 119.6691 | N | 6 | N | N | 1.1101 | 39.4971 | 24048.9265
| ZN80:PA27 | 790 | 681.928 | #N/A | 0.8632 | 39.4971 | 20096 | 15933 | 726910 | 2011-09-23 16:40 | 2011-09-23 20:25 | 225 | 11kV | 12821 | 57 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S7821 Blaxland Beihler 400A fuse blown on A and B phase of distributor 2. Cause: Tree branch brought distributor wires together. See OMS 728361 726982 726910. 726922 | September | 2011 | 2012Q1 | 2012 | ZN4545:PA24 | ZN35500:PA16 | ZN35500/000016 | RYDE | OH | Veg | 2011-09-23 | N | 224.9298 | N | 6 | N | N | 1.1101 | 39.4971 | 9369.2086
| ZN80:PA28 | 514 | 692.428 | 39.64 | 1.3471 | 39.64 | 20150 | 16337 | 726989 | 2011-09-23 20:45 | 2011-09-24 00:30 | 225 | 11kV | 7520 | 34 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV Pnl.10L Ex Wamberal Zone - PT13057 Coachwood Oak - Interrupted by Dop to remove large tree from HV & LV mains | September | 2011 | 2012Q1 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2011-09-23 | N | 221.1765 | N | 6 | N | N | 1.1101 | 39.4971 | 5495.3942
| ZN80:PA30 | 1332 | 1389.07 | 42.17 | 1.0428 | 42.17 | 19560 | 9628 | 727049 | 2011-09-24 08:27 | 2011-09-24 18:20 | 593 | 11kV | 593 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 117627 A & B Phase dist fuses : 80Amp switch fuse faulty transformer at sub 57535 please arrange replacement. Excluded OMS (incorrect premise correct customer) 727049 OMS 728168 | September | 2011 | 2012Q1 | 2012 |  |  |  |  | UG | Not Veg | 2011-09-24 | N | 593 | N | 9 | N | N | 1.1101 | 39.4971 | 433.3469
| ZN80:PA31 | 906 | 714.0719 | 34.1 | 0.78816 | 34.1 | 19872 | 13496 | 727238 | 2011-09-24 18:56 | 2011-09-24 20:11 | 75 | 11kV | 100575 | 1341 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12600 Lisarow Pnl.9 -REC47607 Toomeys Rd opened & locked out Remarks: tree branch removed from 11kV OH pole GO1009 inside Henry Kendal Village. CT cable needs to be extended from main line through to UGOH to S.14191 | September | 2011 | 2012Q1 | 2012 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2011-09-24 | N | 75 | N | 9 | N | N | 1.1101 | 39.4971 | 73497.2435
| ZN80:PA32 | 3593 | 2380.1135 | 34.69 | 0.66243 | 34.69 | 18861 | 2652 | 727320 | 2011-09-24 21:21 | 2011-09-24 22:33 | 72 | 11kV | 146592 | 2036 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.12 opened on A & C Phase Inst. & Timed O/C Remarks: Tree branch removed from 11kV OH on USL44867 | September | 2011 | 2012Q1 | 2012 | ZN12570:PA12 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2011-09-24 | N | 72 | N | 9 | N | N | 1.1101 | 39.4971 | 107125.1099
| ZN80:PA34 | 554 | 517.8293 | #N/A | 0.93471 | 39.4971 | 20168 | 16477 | 727375 | 2011-09-24 23:51 | 2011-09-25 00:52 | 61 | 11kV | 39467 | 647 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12630 peats Ridge Pnl.4 feeder tripped / reclosed & locked out on A phase timed Overcurrent Remarks: Large brnach removed from adjacent LB40538 by DOp | September | 2011 | 2012Q1 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2011-09-24 | N | 61 | N | 9 | N | N | 1.1101 | 39.4971 | 28841.3195
| ZN80:PA36 | 376 | 247.8238 | 37.88 | 0.65911 | 37.88 | 20376 | 19956 | 727342 | 2011-09-24 22:17 | 2011-09-25 01:00 | 163 | 11kV | 163 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117655 A Phase DOLF : 10Amp 243 volts. 58, 70, 60 amps Excluded oms 727342 OMS 727978 | September | 2011 | 2012Q1 | 2012 |  |  |  |  | OH | Veg | 2011-09-24 | N | 163 | N | 9 | N | N | 1.1101 | 39.4971 | 119.1156
| ZN80:PA37 | 1208 | 2383.8226 | 38.69 | 1.9734 | 38.69 | 20171 | 16556 | 727367 | 2011-09-24 23:30 | 2011-09-25 03:00 | 210 | 11kV | 420 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 117664 A Phase DOLF : 16Amp. L/A cut away. Please replace asap 240 volts. 98, 102, 96 amps Excluded oms 727367 OMS 728065 | September | 2011 | 2012Q1 | 2012 | 243:80074 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2011-09-24 | N | 210 | N | 9 | N | N | 1.1101 | 39.4971 | 306.9236
| ZN80:PA39 | 608 | 438.4898 | 29.86 | 0.7212 | 29.86 | 18624 | 455 | 727384 | 2011-09-25 00:28 | 2011-09-25 03:05 | 157 | 11kV | 16014 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117666 2 fault operations B Phase Overcurrent | September | 2011 | 2012Q1 | 2012 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2011-09-25 | N | 157 | N | 34 | Y | Y | 1.1101 | 39.4971 | 11702.5589
| ZN80:PA40 | 2733 | 2617.7125 | 37.21 | 0.95782 | 37.21 | 20126 | 16155 | 727380 | 2011-09-25 00:18 | 2011-09-25 03:10 | 172 | 11kV | 169997 | 1011 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.7 feeder tripped & locked out on SEF-EFI protection Remarks: Branch removed from HV fuse assembly @ PT11286 | September | 2011 | 2012Q1 | 2012 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2011-09-25 | N | 168.1474 | N | 34 | Y | Y | 1.1101 | 39.4971 | 124228.7935
| ZN4990:PA51 52ABC | 1626 | 4525.5786 | #N/A | 2.7833 | 39.4971 | 19852 | 13353 | 727389 | 2011-09-25 01:34 | 2011-09-25 03:25 | 111 | 11kV | 222 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117665 Single phase DOLF : 10Amp. Excluded OMS 727389 OMS 728331 | September | 2011 | 2012Q1 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2011-09-25 | N | 111 | N | 34 | Y | Y | 1.1101 | 39.4971 | 162.2311
| ZN4990:PA51 52DEF | 554 | 2950.294 | #N/A | 5.3254 | 39.4971 | 19899 | 13736 | 727401 | 2011-09-25 03:06 | 2011-09-25 03:38 | 32 | 11kV | 62144 | 1942 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.18 tripped on B & C phase timed overcurrent Remarks: Branch on first HV UGOH from Zone removed by DOp | September | 2011 | 2012Q1 | 2012 | ZN12570:PA18 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Veg | 2011-09-25 | N | 32 | N | 34 | Y | Y | 1.1101 | 39.4971 | 45413.0023
| ZN4990:PA51 52GHJ | 350 | 4452.7282 | #N/A | 12.7221 | 39.4971 | 19192 | 5562 | 727391 | 2011-09-25 01:28 | 2011-09-25 04:16 | 168 | 11kV | 207702 | 1309 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S.15008 Harbord, Panel 4 Fdr CB tripped on A and C phase OC, reclose timing and lockout realys plus 11kV trip. large tree branch on 11kV mains in Quinlan Pde Manly Vale. | September | 2011 | 2012Q1 | 2012 | ZN15008:PA4 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Veg | 2011-09-25 | N | 158.6723 | N | 34 | Y | Y | 1.1101 | 39.4971 | 151782.4954
| ZN4990:PA51 52KLM | 422 | 3831.0693 | #N/A | 9.0784 | 39.4971 | 19629 | 10485 | 727969 | 2011-09-24 21:15 | 2011-09-25 04:30 | 435 | 11kV | 67535 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 117636 8 fault operations 3 phase Overcurrent, Earth fault removed tree branch from Fdr at sub 3475 & sub 17020 | September | 2011 | 2012Q1 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2011-09-24 | N | 213.0442 | N | 9 | N | N | 1.1101 | 39.4971 | 49352.5861
| ZN4990:PA53 54ABC | 835 | 2858.7004 | #N/A | 3.4236 | 39.4971 | 20414 | 20219 | 727392 | 2011-09-25 01:34 | 2011-09-25 04:30 | 176 | 11kV | 148663 | 1094 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At S129 Hunters Hill Panel 9 tripped on C phase O/C, reclose relay, Lockout relay. Signals: 11kV Trip, Zone Earth, TX1 Group Earth. Cause: Tree branches on 11kV mains on riverview Rd. DOp removed Branches. See OMS 728770 728778 727392/396 | September | 2011 | 2012Q1 | 2012 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2011-09-25 | N | 135.8894 | N | 34 | Y | Y | 1.1101 | 39.4971 | 108638.5356
| ZN4990:PA53 54DEF | 1006 | 1348.2583 | #N/A | 1.3402 | 39.4971 | 18892 | 3043 | 727403 | 2011-09-25 03:26 | 2011-09-25 04:39 | 73 | 11kV | 9271 | 127 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12600 Lisarow Pnl.2 - REC41020 tripped on A & B phase overcurrent Remarks: Branch removed from AB45186 by DOp | September | 2011 | 2012Q1 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2011-09-25 | N | 73 | N | 34 | Y | Y | 1.1101 | 39.4971 | 6774.9734
| ZN4990:PA53 54GHJ | 281 | 3344.0807 | #N/A | 11.9006 | 39.4971 | 19224 | 6196 | 731991 | 2011-09-25 01:29 | 2011-09-25 04:55 | 206 | 11kV | 4982 | 62 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117669 2 fault operations Sectionaliser operated. Excluded OMS 727388 | September | 2011 | 2012Q1 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2011-09-25 | N | 80.3548 | N | 34 | Y | Y | 1.1101 | 39.4971 | 3640.6987
| ZN4990:PA53 54KLM | 302 | 1773.5159 | #N/A | 5.8726 | 39.4971 | 19071 | 4466 | 728024 | 2011-09-24 23:50 | 2011-09-25 05:10 | 320 | 11kV | 92552 | 1855 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 117671 2 fault operations A Phase Overcurrent, Earth fault 33kV mains down near ABS 2241 South Belmont. 33kV into 11kV. L/A also blown at UGOH pole to PMG Belmont sub & UGOH pole to Sw 22280 Coles Belmont sub. OMS 728021, 728029, 728033, 728035, 728039 | September | 2011 | 2012Q1 | 2012 | 222:2017 | 222:33597 | ZN00222/033597 | LAKE MACQUARIE | OH | Not Veg | 2011-09-24 | N | 49.8933 | N | 9 | N | N | 1.1101 | 39.4971 | 67634.2718
| ZN4990:PA55 56DEF | 399 | 2705.9892 | #N/A | 6.7819 | 39.4971 | 20273 | 18086 | 727362 | 2011-09-24 23:10 | 2011-09-25 05:20 | 370 | 11kV | 180481 | 1237 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 117671 2 fault operations A Phase Overcurrent, Earth fault 33kV mains down near ABS 2241 South Belmont. 33kV into 11kV. L/A also blown at UGOH pole to PMG Belmont sub & UGOH pole to Sw 22280 Coles Belmont sub. OMS 728021, 728029, 728033, 728035, 728039 | September | 2011 | 2012Q1 | 2012 | 222:2017 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2011-09-24 | N | 145.9022 | N | 9 | N | N | 1.1101 | 39.4971 | 131890.1915
| ZN4990:PA55 56GHJ | 787 | 2079.1164 | #N/A | 2.6418 | 39.4971 | 18965 | 3545 | 727387 | 2011-09-25 01:00 | 2011-09-25 06:05 | 305 | 11kV | 19935 | 175 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117648 2 fault operations Sectionaliser operated. Excluded OMS 727387 | September | 2011 | 2012Q1 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-09-25 | N | 113.9143 | N | 34 | Y | Y | 1.1101 | 39.4971 | 14567.91
| ZN4990:PA55 56KLM | 827 | 2955.1527 | #N/A | 3.5733 | 39.4971 | 19074 | 4472 | 727409 | 2011-09-25 03:54 | 2011-09-25 06:05 | 131 | 11kV | 2358 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117673 A & B Phase DOLF 16Amp Excluded oms 727409, 727413 OMS 728355 | September | 2011 | 2012Q1 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-09-25 | N | 131 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1723.1569
| ZN4990:PA55ABC | 418 | 1262.7809 | #N/A | 3.021 | 39.4971 | 18590 | 128 | 727428 | 2011-09-25 06:36 | 2011-09-25 08:15 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117675 A Phase DOLF : 10Amp volts 243, 243, 243 Excluded oms 727428 OMS 728359 | September | 2011 | 2012Q1 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-09-25 | N | 99 | N | 34 | Y | Y | 1.1101 | 39.4971 | 72.3463
| ZN4990:PA57K | 109 | 310.6765 | #N/A | 2.8502 | 39.4971 | 18876 | 2861 | 727437 | 2011-09-25 07:00 | 2011-09-25 08:45 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117677 A Phase DOLF : 10Amp | September | 2011 | 2012Q1 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2011-09-25 | N | 105 | N | 34 | Y | Y | 1.1101 | 39.4971 | 76.7309
| ZN4990:PA57M | 17 | 412.5587 | #N/A | 24.2682 | 39.4971 | 18790 | 2067 | 727422 | 2011-09-25 07:00 | 2011-09-25 09:15 | 135 | 11kV | 135 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117679 A Phase DOLF : 10Amp Excluded oms 727422 OMS 728371 | September | 2011 | 2012Q1 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-09-25 | N | 135 | N | 34 | Y | Y | 1.1101 | 39.4971 | 98.654
| ZN1600:PA21ABC | 319 | 2036.4885 | #N/A | 6.384 | 39.4971 | 18583 | 89 | 727457 | 2011-09-25 07:00 | 2011-09-25 09:45 | 165 | 11kV | 660 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117680 A Phase DOLF : 10Amp Excluded oms 727457 OMS 728375 | September | 2011 | 2012Q1 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-09-25 | N | 165 | N | 34 | Y | Y | 1.1101 | 39.4971 | 482.3085
| ZN1600:PA21DEF | 240 | 1455.9067 | #N/A | 6.0663 | 39.4971 | 18723 | 1290 | 727492 | 2011-09-25 08:30 | 2011-09-25 10:55 | 145 | 11kV | 415 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117685 Single phase DOLF : 10Amps | September | 2011 | 2012Q1 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2011-09-25 | N | 138.3333 | N | 34 | Y | Y | 1.1101 | 39.4971 | 303.2698
| ZN1600:PA22ABC | 547 | 2766.4562 | #N/A | 5.0575 | 39.4971 | 19635 | 10529 | 727514 | 2011-09-25 09:52 | 2011-09-25 11:15 | 82.5167 | 11kV | 43952.1 | 571 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn711 Blackwattle Bay Pa23 no relay operation except for EFI Alarms TX2 ZE GE Front line feeder fault Protection to check pa23 relays as O/C relay did not flag on 2 occasions See 727931 LV// 727521 GIS 727518 exclude 727514 From To Restored DC Time S5459SwA S560SwN to S2983 to S35333 3 1109 | September | 2011 | 2012Q1 | 2012 | ZN711:PA23 | ZN116:PA25 | ZN00116/000025 | SYDNEY | UG | Not Veg | 2011-09-25 | N | 76.9739 | N | 34 | Y | Y | 1.1101 | 39.4971 | 32118.8983
| ZN1600:PA22DEF | 420 | 2441.7102 | #N/A | 5.8136 | 39.4971 | 20175 | 16690 | 727550 | 2011-09-25 10:31 | 2011-09-25 11:46 | 75 | 11kV | 6447 | 100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 117683 Pole mounted RAGCB operated - BROKEN BRANCH FOUND AT POLE FP-90704 Refer related jobs 729076, 729073, 729072 and 727550 | September | 2011 | 2012Q1 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-09-25 | N | 64.47 | N | 34 | Y | Y | 1.1101 | 39.4971 | 4711.2774
| ZN1600:PA23ABC | 286 | 975.0856 | #N/A | 3.4094 | 39.4971 | 19722 | 12004 | 727431 | 2011-09-25 08:30 | 2011-09-25 12:10 | 220 | 11kV | 220 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 117688 Single phase DOLF Excluded OMS 727431 OMS 728400 | September | 2011 | 2012Q1 | 2012 | 803:74010 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2011-09-25 | N | 220 | N | 34 | Y | Y | 1.1101 | 39.4971 | 160.7695
| ZN1600:PA23DEF | 227 | 1604.7059 | #N/A | 7.0692 | 39.4971 | 19166 | 5160 | 727525 | 2011-09-25 10:15 | 2011-09-25 13:00 | 165 | 11kV | 48050 | 400 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | TCTAAT 14470 Pacific Mt White tripped on Earth Fault with EFI Remarks: Large tree branch on HV mains near PT13520 - removed by DOp | September | 2011 | 2012Q1 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2011-09-25 | N | 120.125 | N | 34 | Y | Y | 1.1101 | 39.4971 | 35113.5228
| ZN1600:PA24ABC | 3 | 106.0309 | #N/A | 35.3436 | 39.4971 | 20146 | 16304 | 727420 | 2011-09-25 10:30 | 2011-09-25 13:20 | 170 | 11kV | 32810 | 193 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 117691 Section isolated to make emergency repairs & Replace Transformer 26992. Excluded OMS No 727420. OMS 728118 | September | 2011 | 2012Q1 | 2012 | 243:80074 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2011-09-25 | N | 170 | N | 34 | Y | Y | 1.1101 | 39.4971 | 23976.5803
| ZN1600:PA24DEF | 142 | 1288.0547 | #N/A | 9.0708 | 39.4971 | 20365 | 19871 | 727661 | 2011-09-25 14:20 | 2011-09-25 14:35 | 15 | 11kV | 15 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117693 Fuse Size 3 Amp, Substation Dolf replaced Related record 727661 | September | 2011 | 2012Q1 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2011-09-25 | N | 15 | N | 34 | Y | Y | 1.1101 | 39.4971 | 10.9616
| ZN8700:PA61 62ABC | 510 | 2341.6735 | #N/A | 4.5915 | 39.4971 | 20048 | 15577 | 727684 | 2011-09-25 15:08 | 2011-09-25 15:55 | 47 | 11kV | 62651 | 1333 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S2400 Berowra panel 22 feeder tripped Relay: OC trip B and C phase Signals: 11kV trip. Tree Branch on HV mains near AB442-removed by DOp See OMS 727684 727694 | September | 2011 | 2012Q1 | 2012 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2011-09-25 | N | 47 | N | 34 | Y | Y | 1.1101 | 39.4971 | 45783.5029
| ZN8700:PA61 62DEF | 264 | 2287.5233 | #N/A | 8.6649 | 39.4971 | 18996 | 3972 | 727627 | 2011-09-25 13:03 | 2011-09-25 16:55 | 232 | 11kV | 232 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 117694 No protection operation sub isolated to repair faulty LL Clamp Refer OMS 727627 related record - 25/09/11 17:17 CASS: Repaired live line lead | September | 2011 | 2012Q1 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2011-09-25 | N | 232 | N | 34 | Y | Y | 1.1101 | 39.4971 | 169.5388
| ZN8700:PA61 62GHJ | 1815 | 3432.024 | #N/A | 1.8909 | 39.4971 | 19286 | 7260 | 727664 | 2011-09-25 14:25 | 2011-09-25 17:05 | 160 | 11kV | 42954 | 663 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.10 feeder opened on Earth fault with EFI Field EFIs: S.18824 S.18765 S.18763 & S.18523 Remarks: Defective 11kV UGOH from S.18523 to S.18762 to Open bonds | September | 2011 | 2012Q1 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | Unknown | Unknown | 2011-09-25 | N | 64.7873 | N | 34 | Y | Y | 1.1101 | 39.4971 | 31389.5163
| ZN8700:PA61 62KLM | 953 | 4988.6116 | #N/A | 5.2346 | 39.4971 | 20265 | 18017 | 727629 | 2011-09-25 13:04 | 2011-09-25 17:30 | 266 | 11kV | 58891 | 276 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | TCAT 14084 Wise Ferry Ingoola tripped Ex Zn12630 peats Ridge Pnl.2 Remarks: 11kv Down between AB40598 & REC45013 | September | 2011 | 2012Q1 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2011-09-25 | N | 213.3732 | N | 34 | Y | Y | 1.1101 | 39.4971 | 43035.8058
| ZN8700:PA63 64ABC | 621 | 3247.0521 | #N/A | 5.2287 | 39.4971 | 19878 | 13567 | 727243 | 2011-09-25 19:09 | 2011-09-25 20:09 | 60 | 11kV | 64260 | 1071 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At S80 Chatswood Panel 25 tripped reclosed tripped and locked out on Relays: Earth Fault, B and C phase Timed O/C, timing relay, Lockout relay and EFI. Signals: 11kV Zone Earth. Cause:Tree branch on 11kV O/S 6 Elizabeth Pde. Based on customer calls suspect S2471//Panel 25 at the time of interruption. See OMS 728766/727255/249/244/243/242 | September | 2011 | 2012Q1 | 2012 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2011-09-25 | N | 60 | N | 34 | Y | Y | 1.1101 | 39.4971 | 46959.3127
| ZN8700:PA63 64DEF | 983 | 5632.7278 | #N/A | 5.7301 | 39.4971 | 19614 | 10335 | 727743 | 2011-09-25 17:39 | 2011-09-25 20:35 | 176 | 11kV | 312935 | 2281 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | At S847 Hornsby Panel 21 tripped reclosed and locded out Relays: A and C phase IOC and O/C, Lockout, Timing Relay, Fault Check and EFI. Signals: 11kV Trip, No2 Tx Group Earth, No2 Tx protn Under volts and Zone Earth. Cause: N/O Ab 3191 centre phase contact broken of and Ab 2701 has broken insulators and contacts insulators while operating. See OMS 728579/582/583 | September | 2011 | 2012Q1 | 2012 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2011-09-25 | N | 137.192 | N | 34 | Y | Y | 1.1101 | 39.4971 | 228683.668
| ZN8700:PA63 64GHJ | 535 | 1982.413 | #N/A | 3.7054 | 39.4971 | 18843 | 2494 | 727617 | 2011-09-25 12:48 | 2011-09-25 21:00 | 492 | 11kV | 163125 | 1460 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID 117690 2 fault operations A Phase Overcurrent Excluded OMS 727617, 727655 OMS 728158, 728159, 728162 | September | 2011 | 2012Q1 | 2012 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | UG | Not Veg | 2011-09-25 | N | 111.7295 | N | 34 | Y | Y | 1.1101 | 39.4971 | 119206.9386
| ZN8700:PA63 64KLM | 408 | 1484.3159 | #N/A | 3.638 | 39.4971 | 20350 | 19570 | 727761 | 2011-09-25 19:21 | 2011-09-25 21:00 | 99 | 11kV | 3168 | 32 | HV | Animal Possum | Animal | Fuse | Unplanned | Rain Light | N | LID 117698 B & C Phase DOLF : 20Amp. DOLF's down after possum attack, supply restored OK. Excluded OMS No's 727761 & 727763. OMS 728127 | September | 2011 | 2012Q1 | 2012 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2011-09-25 | N | 99 | N | 34 | Y | Y | 1.1101 | 39.4971 | 2315.081
| ZN8700:PA65 66ABC | 973 | 6466.125 | #N/A | 6.6456 | 39.4971 | 19918 | 13992 | 727709 | 2011-09-25 16:17 | 2011-09-25 21:20 | 303.3833 | 11kV | 1213.5333 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117699 Fuse size: 4 Amp Line DOLF replaced | September | 2011 | 2012Q1 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2011-09-25 | N | 303.3833 | N | 34 | Y | Y | 1.1101 | 39.4971 | 886.8144
| ZN8700:PA65 66DEF | 471 | 1534.9972 | #N/A | 3.259 | 39.4971 | 20203 | 17024 | 727749 | 2011-09-25 18:06 | 2011-09-25 22:30 | 264 | 11kV | 264 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 117697 A & B Phase DOLF Replaced arrestors | September | 2011 | 2012Q1 | 2012 | 231:8405 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2011-09-25 | N | 264 | N | 34 | Y | Y | 1.1101 | 39.4971 | 192.9234
| ZN8700:PA65 66GHJ | 576 | 2979.641 | #N/A | 5.173 | 39.4971 | 18713 | 1223 | 727780 | 2011-09-25 20:40 | 2011-09-26 00:14 | 214 | 11kV | 55806 | 283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12630 Peats Ridge Pnl.5 feeder tripped / reclosed / tripped & locked out on C phase OC Remarks: Tree brnach removed from 11kV OH near tee to PT13257 | September | 2011 | 2012Q1 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2011-09-25 | N | 197.1943 | N | 34 | Y | Y | 1.1101 | 39.4971 | 40781.3788
| ZN8700:PA65 66KLM | 293 | 1346.8894 | #N/A | 4.5969 | 39.4971 | 19626 | 10465 | 727774 | 2011-09-25 20:16 | 2011-09-26 00:55 | 279 | 11kV | 761.85 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117700 Fuse Size: 10 Amp Substation DOLF replaced Refer related records 727774 and 727776 | September | 2011 | 2012Q1 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2011-09-25 | N | 253.95 | N | 34 | Y | Y | 1.1101 | 39.4971 | 556.7375
| ZN8700:PA67 68G | 3 | 9.6167 | #N/A | 3.2056 | 39.4971 | 19668 | 11082 | 727853 | 2011-09-26 08:11 | 2011-09-26 09:15 | 64 | 11kV | 320 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117702 Phase C, Fuse size : 10 Amp Substation DOLF, refer to related record 727853 | September | 2011 | 2012Q1 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2011-09-26 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 233.8466
| ZN8700:PA67 68H | 65 | 1155.281 | #N/A | 17.7736 | 39.4971 | 18611 | 301 | 727890 | 2011-09-26 08:48 | 2011-09-26 10:20 | 92 | 11kV | 184 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117703 Phase B - Fuse Size: 3 Amp, Substation DOLF Refer related record 727890, Volts: 250V - 251V - 250V | September | 2011 | 2012Q1 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2011-09-26 | N | 92 | N | 4 | N | N | 1.1101 | 39.4971 | 134.4618
| ZN8700:PA67 68J | 484 | 979.4143 | #N/A | 2.0236 | 39.4971 | 19100 | 4645 | 728519 | 2011-09-26 11:03 | 2011-09-26 11:50 | 47 | 11kV | 470 | 10 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | Ex Pnl.8 @ Wyong Zone - PT11818 Old Tuggerah Pacific - Road Side Phase 16A HDO Fuse Operated Remarks: Defective 11kv/514V Transformer @ PT11818. PT11818 was in LV // with PT12036 & MG connected Abnormal Switching: AB43004 CLOSED, AB44748 OPEN, AB41094 OPEN (PT11818 normally supplied from Berkeley Vale Pnl.12) | September | 2011 | 2012Q1 | 2012 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2011-09-26 | N | 47 | N | 4 | N | N | 1.1101 | 39.4971 | 343.4621
| ZN8700:PA67A 68A | 2 | 0.84737 | #N/A | 0.42368 | 39.4971 | 18912 | 3203 | 728208 | 2011-09-26 13:17 | 2011-09-26 14:27 | 70 | 11kV | 140 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117705 Phase A - Fuse size: 10 AMP Substation DOLF - related record 728208 | September | 2011 | 2012Q1 | 2012 | 234:2005 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2011-09-26 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 102.3079
| ZN3288:PA41 42ABC | 846 | 2740.8828 | #N/A | 3.2398 | 39.4971 | 19688 | 11395 | 727748 | 2011-09-25 17:27 | 2011-09-26 18:20 | 1493 | 11kV | 65134 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | At CP1268 Milsons Passage CB tripped and locked out Relays: A and C Phase O/C, SEF trip. Fault is ABS464 in feeder to Milson Passage. AB464 is open and danger tagged. Hornsby OH to patrol Based on OMS 728167 suspect wires down. See OMS 728710 728709 728708 OK-DQ1 | September | 2011 | 2012Q1 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2011-09-25 | N | 1123 | N | 34 | Y | Y | 1.1101 | 39.4971 | 47598.0061
| ZN3288:PA41 42DEF | 1342 | 3924.3193 | #N/A | 2.9242 | 39.4971 | 19706 | 11728 | 728953 | 2011-09-28 07:30 | 2011-09-28 10:00 | 150 | 11kV | 300 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117731 Substation DOLF Fuse - size: 10 Amp replaced - no cause found - not storm conditions | September | 2011 | 2012Q1 | 2012 | 234:2005 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2011-09-28 | N | 150 | N | 1 | N | N | 1.1101 | 39.4971 | 219.2312
| ZN3288:PA41 42GHJ | 301 | 2396.9141 | #N/A | 7.9632 | 39.4971 | 18993 | 3918 | 729369 | 2011-09-29 05:42 | 2011-09-29 08:41 | 179 | 11kV | 179 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117740 LLC burnt off 29/09/11 07:10 CASS: Hv dof, Lead dropped fromm 11KV mains HV DOF removed reffered to SO3 | September | 2011 | 2012Q1 | 2012 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2011-09-29 | N | 179 | N | 19 | N | N | 1.1101 | 39.4971 | 130.8079
| ZN3288:PA41 42KLM | 1504 | 4230.9196 | #N/A | 2.8131 | 39.4971 | 18716 | 1242 | 729401 | 2011-09-29 07:43 | 2011-09-29 09:35 | 112 | 11kV | 1232 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117741 Replace 3 blown dolfs 20A on line fuses 40751 | September | 2011 | 2012Q1 | 2012 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2011-09-29 | N | 112 | N | 19 | N | N | 1.1101 | 39.4971 | 900.3093
| ZN3288:PA43 44ABC | 1225 | 3269.6225 | #N/A | 2.6691 | 39.4971 | 20381 | 19981 | 729606 | 2011-09-29 12:06 | 2011-09-29 13:25 | 79 | 11kV | 1817 | 23 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | LID 117745 Fuse size: 16 Amp, LINE DOLF REPLACED LINE FUSES Refer related record 729606 | September | 2011 | 2012Q1 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2011-09-29 | N | 79 | N | 19 | N | N | 1.1101 | 39.4971 | 1327.81
| ZN3288:PA43 44DEF | 26 | 1156.4283 | #N/A | 44.478 | 39.4971 | 19119 | 4739 | 729572 | 2011-09-29 11:25 | 2011-09-29 15:25 | 240 | 11kV | 240 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117748 DOLF operated, no cause found, Fuse size: 10 Amp | September | 2011 | 2012Q1 | 2012 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Veg | 2011-09-29 | N | 240 | N | 19 | N | N | 1.1101 | 39.4971 | 175.3849
| ZN3288:PA43 44GHJ | 765 | 3742.2878 | #N/A | 4.8919 | 39.4971 | 19299 | 7322 | 729728 | 2011-09-29 14:43 | 2011-09-29 15:53 | 70 | 11kV | 2520 | 36 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | Zn.14143 Somersby Pnl.21 tripped / reclosed and locked out on B & C phase OL Remarks: Cause not found. Feeder patrolled by DOp nothing found. Very strong wind storm a time of occurrence | September | 2011 | 2012Q1 | 2012 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2011-09-29 | N | 70 | N | 19 | N | N | 1.1101 | 39.4971 | 1841.5417
| ZN3288:PA43 44KLM | 1281 | 2796.9836 | #N/A | 2.1834 | 39.4971 | 19707 | 11731 | 729730 | 2011-09-29 14:48 | 2011-09-29 16:00 | 72 | 11kV | 64477 | 917 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Wind | N | Recloser 20397 tripped and locked out after tree came down on 11kV OH which snapped crossarm near recloser 20397 | September | 2011 | 2012Q1 | 2012 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2011-09-29 | N | 70.313 | N | 19 | N | N | 1.1101 | 39.4971 | 47117.8899
| ZN3288:PA45 46ABC | 1329 | 3806.679 | #N/A | 2.8643 | 39.4971 | 19496 | 9055 | 729559 | 2011-09-29 11:13 | 2011-09-29 16:10 | 297.5 | 11kV | 8330 | 28 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117744 Line Dolf operated due to HV Wires down beyond pole HT-14040 at 493 Averys Lane Buchanan | September | 2011 | 2012Q1 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2011-09-29 | N | 297.5 | N | 19 | N | N | 1.1101 | 39.4971 | 6087.3183
| ZN3288:PA45 46DEF | 600 | 3192.0408 | #N/A | 5.3201 | 39.4971 | 20207 | 17087 | 729744 | 2011-09-29 14:56 | 2011-09-29 16:20 | 84 | 11kV | 75180 | 895 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | REC 44982 tripped and locked out on SEF ex Avoca Zone Pnl.2 Remarks: 11kV conductors blown into concrete pole erected between mains on section of feeder. leaving Rec44982 and heading up mountain conductors burnt through and down on ground | September | 2011 | 2012Q1 | 2012 | ZN12570:PA2 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2011-09-29 | N | 84 | N | 19 | N | N | 1.1101 | 39.4971 | 54939.3266
| ZN3288:PA45 46GHJ | 314 | 2349.9713 | #N/A | 7.484 | 39.4971 | 19488 | 9021 | 730299 | 2011-09-29 14:00 | 2011-09-29 17:45 | 225 | 11kV | 5175 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117754 Fuse size: 16 Amp 2nd time today that Line dolf has operated - refer to LID 117745 and OMS 730295 | September | 2011 | 2012Q1 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2011-09-29 | N | 225 | N | 19 | N | N | 1.1101 | 39.4971 | 3781.7374
| ZN3288:PA45 46KLM | 1212 | 3993.736 | #N/A | 3.2952 | 39.4971 | 19366 | 7879 | 729784 | 2011-09-29 15:14 | 2011-09-29 18:03 | 169 | 11kV | 66586 | 394 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117755 4 Fault operations, Pole Mounted RAGCB, Earth Fault Unknown trigger for recloser to lock out | September | 2011 | 2012Q1 | 2012 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2011-09-29 | N | 169 | N | 19 | N | N | 1.1101 | 39.4971 | 48659.0848
| ZN2602:PA27 | 460 | 2657.5342 | #N/A | 5.7772 | 39.4971 | 19808 | 12864 | 729842 | 2011-09-29 16:13 | 2011-09-29 18:07 | 114 | 11kV | 3876 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117756 3 Fault operations Pole Mounted RAGCB, Overcurrent - unknown cause for recloser to lock out Refer related record 729842 | September | 2011 | 2012Q1 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2011-09-29 | N | 114 | N | 19 | N | N | 1.1101 | 39.4971 | 2832.4665
| ZN2602:PA28 | 1230 | 1289.9918 | 36.28 | 1.0488 | 36.28 | 19168 | 5180 | 729725 | 2011-09-29 14:43 | 2011-09-29 18:15 | 212 | 11kV | 27020 | 369 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12690 Berkeley Vale - Pnl.16 tripped / reclosed / tripped and locked out on: A & B phase Overcurrent, SEF, Reclose timing, lockout Remarks: Tree brought down 11kV mains near PT13987 | September | 2011 | 2012Q1 | 2012 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2011-09-29 | N | 73.2249 | N | 19 | N | N | 1.1101 | 39.4971 | 19745.419
| ZN2602:PA29 | 1557 | 962.4896 | 37.3 | 0.61817 | 37.3 | 20374 | 19916 | 729862 | 2011-09-29 16:22 | 2011-09-29 18:20 | 118 | 11kV | 4290 | 88 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 117758 Feeder isolated to repair fault, HV wires down near Pole AL-30023 | September | 2011 | 2012Q1 | 2012 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2011-09-29 | N | 48.75 | N | 19 | N | N | 1.1101 | 39.4971 | 3135.0055
| ZN2602:PA30 | 2161 | 1963.8485 | 41.72 | 0.90877 | 41.72 | 18718 | 1259 | 729776 | 2011-09-29 15:13 | 2011-09-29 19:20 | 247 | 11kV | 1235 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 117761 Single Fuse operation: Fuse size: 100 AMP No trigger determined | September | 2011 | 2012Q1 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2011-09-29 | N | 247 | N | 19 | N | N | 1.1101 | 39.4971 | 902.5016
| ZN2602:PA31 | 2320 | 1545.5828 | 37.18 | 0.6662 | 37.18 | 19824 | 12997 | 729643 | 2011-09-29 13:03 | 2011-09-29 20:10 | 427.1833 | 11kV | 62781.1833 | 277 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | TCAT 14084 Wise ferry Ingoola tripped on SEF - EX Pnl.2 Peats Ridge Zn Remarks: Section of 11kV mains found down on ground between USL42686 and AB43179 | September | 2011 | 2012Q1 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2011-09-29 | N | 226.6469 | N | 19 | N | N | 1.1101 | 39.4971 | 45878.637
| ZN2602:PA32 | 1619 | 1482.4635 | 36.22 | 0.91567 | 36.22 | 19650 | 10844 | 729811 | 2011-09-29 12:00 | 2011-09-29 20:55 | 535 | 11kV | 1605 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 117763 Single Phase - Fuse size - 10 Amp 29/09/11 22:08 CASS: Replaced lightning arrestor and repaired DOLF - OK | September | 2011 | 2012Q1 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2011-09-29 | N | 535 | N | 19 | N | N | 1.1101 | 39.4971 | 1172.8867
| ZN2602:PA33 | 1069 | 613.0995 | 34.23 | 0.57353 | 34.23 | 20404 | 20174 | 729914 | 2011-09-29 17:17 | 2011-09-29 22:30 | 313 | 11kV | 313 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 117771 Customer reports on related job 729914, that lightning struck the pole and power was cut | September | 2011 | 2012Q1 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2011-09-29 | N | 313 | N | 19 | N | N | 1.1101 | 39.4971 | 228.7312
| ZN2602:PA34 | 1290 | 1259.3179 | 35.78 | 0.97622 | 35.78 | 19631 | 10496 | 729789 | 2011-09-29 15:52 | 2011-09-29 23:47 | 475 | 11kV | 61492 | 1084 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | N | LID 117749 Emergency isolation live 11kV pole leaning over house. Fdr switched off by SOp. Excluded OMS 729823, 729850. OMS 731338, 731339 | September | 2011 | 2012Q1 | 2012 | 214:8667 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Not Veg | 2011-09-29 | N | 56.7269 | N | 19 | N | N | 1.1101 | 39.4971 | 44936.5399
| ZN2602:PA35 | 2551 | 1623.3065 | 35.71 | 0.63634 | 35.71 | 20330 | 19343 | 730005 | 2011-09-30 02:09 | 2011-09-30 05:31 | 202 | 11kV | 69423 | 888 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14892 Charmhaven Pnl.1 tripped on: 51N earth fault - reclose without timing - fault check Field EFI: S.18361 18320 18105 Remarks: 11kV Wire down cnr Hakone Haiwatha St - 11kV arcing horn found stuck in at AB42855 (see Outage for for Pnl.12) | September | 2011 | 2012Q1 | 2012 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | OH | Not Veg | 2011-09-30 | N | 78.1791 | N | 5 | N | N | 1.1101 | 39.4971 | 50732.2808
| ZN2602:PA36 | 7 | 1319.445 | #N/A | 188.4921 | 39.4971 | 19426 | 8492 | 729877 | 2011-09-29 16:37 | 2011-09-30 11:15 | 1118 | 11kV | 71686 | 565 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 117760 5 fault operations OHM down to sub 26829 excluded OMD 729877, 729984 OMS 731264, 731266, 731267, 731268, 731269, 731271, 731272, 731275, 731276, 731278, 731280. | September | 2011 | 2012Q1 | 2012 | 234:2005 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2011-09-29 | N | 126.8779 | N | 19 | N | N | 1.1101 | 39.4971 | 52386.0144
| ZN2602:PA41 | 1037 | 854.9983 | 34.39 | 0.82449 | 34.39 | 19896 | 13720 | 730115 | 2011-09-30 10:06 | 2011-09-30 11:40 | 94.1667 | 11kV | 9699.1667 | 103 | HV | Vegetation Blow/Fall In | Vegetation | Fuse | Unplanned | Wind | N | At 11kV fuses F.24966 (Pnl 7 'Mona Vale Pittwater' Fdr) A & B phase HV BBLAS 80 amp drop out fuses blew Tree branch on HV mains adjacent Pt 15395 Elimatta Rd. | September | 2011 | 2012Q1 | 2012 | ZN15014:PA7 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | OH | Veg | 2011-09-30 | N | 94.1667 | N | 5 | N | N | 1.1101 | 39.4971 | 7087.8649
| ZN2602:PA42 | 2815 | 1922.0848 | 37.54 | 0.6828 | 37.54 | 19739 | 12292 | 730263 | 2011-09-30 13:19 | 2011-09-30 15:10 | 111 | 11kV | 15096 | 136 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV feeder from USL 42684 to AB41236 isolated for emergency removal of large tree from OH feeder. Section of panel 1L ex Wamberal zone | September | 2011 | 2012Q1 | 2012 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Veg | 2011-09-30 | N | 111 | N | 5 | N | N | 1.1101 | 39.4971 | 11031.7115
| ZN2602:PA46 | 968 | 937.8059 | #N/A | 0.96881 | 39.4971 | 18670 | 896 | 730254 | 2011-09-30 13:22 | 2011-09-30 18:00 | 278 | 11kV | 278 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117775 No protection operations. Sub isolated to replace faulty LL clamps under A/P. Excluded OMS # 730254. OMS 731371 | September | 2011 | 2012Q1 | 2012 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Not Veg | 2011-09-30 | N | 278 | N | 5 | N | N | 1.1101 | 39.4971 | 203.1542
| ZN874:PA10 | 1339 | 782.7733 | #N/A | 0.5846 | 39.4971 | 19349 | 7629 | 730154 | 2011-09-30 10:48 | 2011-09-30 20:25 | 577 | 11kV | 20649 | 120 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117773 1 fault operation A Phase Overcurrent, Earth fault Excluded OMS 730154, 730234 OMS 731353, 731354, 731357 | September | 2011 | 2012Q1 | 2012 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2011-09-30 | N | 172.075 | N | 5 | N | N | 1.1101 | 39.4971 | 15089.6802
| ZN874:PA11 | 144 | 98.3166 | 39.75 | 0.68275 | 39.75 | 19855 | 13360 | 730575 | 2011-10-01 17:04 | 2011-10-01 18:15 | 71 | 11kV | 1420 | 20 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 117782 A Phase DOLF : 16Amp A Phase LV L/A Cut away Excluded OMS 730575 OMS 731382 | October | 2011 | 2012Q2 | 2012 | 225:33670 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Not Veg | 2011-10-01 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 1037.6941
| ZN874:PA12 | 103 | 88.2693 | 35.86 | 0.85698 | 35.86 | 18566 | 9 | 730593 | 2011-10-01 18:56 | 2011-10-01 20:43 | 107 | 11kV | 109185 | 1029 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN965 Pennant Hills Panel 38 tripped on 51N - Earth Fault, SEL EFI Signals: 11kV Trip Cause: Suspect UG fault between S5613 and S5929. See OMS 731149 148 146 730606 730593 | October | 2011 | 2012Q2 | 2012 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | UG | Not Veg | 2011-10-01 | N | 106.1079 | N | 4 | N | N | 1.1101 | 39.4971 | 79789.1776
| ZN874:PA15 | 542 | 509.2273 | 38.5 | 0.93953 | 38.5 | 19587 | 9746 | 730612 | 2011-10-01 20:01 | 2011-10-01 21:40 | 99 | 11kV | 4851 | 49 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 117783 A phase DOLF : 31Amp Substation commissioned 30/9 with incorrect sized DOLF fuses (3.15A). All elements replaced. Excluded OMS # 730612 OMS 731456 | October | 2011 | 2012Q2 | 2012 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2011-10-01 | N | 99 | N | 4 | N | N | 1.1101 | 39.4971 | 3544.9677
| ZN874:PA16 | 810 | 781.7441 | 44.53 | 0.96512 | 44.53 | 19311 | 7357 | 730628 | 2011-10-01 23:14 | 2011-10-02 03:17 | 243 | 11kV | 242150 | 1344 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9700 Kirrawee 11kV trip zone earth TX.3 group earth. P-20 The Belmont Cook fdr, tripped reclosed and locked out on: Overcurrent EFI, Earth fault check, reclose timing and lockout. Field EFIs down at S.9432, S.9434, S.9839 and S.9244, note no access to S.9764 REMARKS: Suspect UG cable fault between S.9244 and S.9777 | October | 2011 | 2012Q2 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | UG | Not Veg | 2011-10-01 | N | 180.1711 | N | 4 | N | N | 1.1101 | 39.4971 | 176956.0778
| ZN874:PA17 | 1136 | 1243.7078 | 43.73 | 1.0948 | 43.73 | 19550 | 9597 | 730647 | 2011-10-02 07:56 | 2011-10-02 08:55 | 59 | 11kV | 43549 | 743 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14143 Somersby Pnl.17 tripped on A & B phase Overcurrent Remarks: Branch removed from USL 44302 | October | 2011 | 2012Q2 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2011-10-02 | N | 58.6124 | N | 7 | N | N | 1.1101 | 39.4971 | 31824.3247
| ZN874:PA18 | 1892 | 1272.0934 | 34.91 | 0.67235 | 34.91 | 18677 | 926 | 730651 | 2011-10-02 08:14 | 2011-10-02 10:00 | 106 | 11kV | 212 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.18229 C phase HV Fuse Ooperated (15A) Remarks: No Cause | October | 2011 | 2012Q2 | 2012 | ZN12640:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2011-10-02 | N | 106 | N | 7 | N | N | 1.1101 | 39.4971 | 154.9233
| ZN874:PA2 | 244 | 1378.4205 | 44.37 | 5.6493 | 44.37 | 19774 | 12566 | 730774 | 2011-10-02 14:04 | 2011-10-02 16:20 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117786 C Phase DOLF : 10Amp 247 volts; 14, 6, 2 Amp Excluded OMS 730774 (Incorrect premise) OMS 731461 | October | 2011 | 2012Q2 | 2012 | 234:2005 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2011-10-02 | N | 136 | N | 7 | N | N | 1.1101 | 39.4971 | 198.7696
| ZN874:PA22 | 1342 | 1231.2573 | 35.8 | 0.91748 | 35.8 | 18823 | 2305 | 730806 | 2011-10-02 15:18 | 2011-10-02 16:30 | 72 | 11kV | 2664 | 37 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | PT569 Shaw Long 400A fuse blown on C phase of distributor 1. Cause: Tree branch outside 44 long st brought down LV mains. See OMS 631184 631186 730806 | October | 2011 | 2012Q2 | 2012 | ZN1114:PA11 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Veg | 2011-10-02 | N | 72 | N | 7 | N | N | 1.1101 | 39.4971 | 1946.7726
| ZN874:PA24 | 40 | 244.5576 | 49.02 | 6.1139 | 49.02 | 20292 | 18725 | 730822 | 2011-10-02 15:57 | 2011-10-02 18:18 | 141 | 11kV | 8262 | 94 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn.14144 Wamberal Pnl.10 - REC44607 tripped on A & B phase O/C, Earth fault trip Remarks: O/S 272 Matchan Rd 11kV feeder on ground See OMS # 731158 731159 | October | 2011 | 2012Q2 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2011-10-02 | N | 87.8936 | N | 7 | N | N | 1.1101 | 39.4971 | 6037.6259
| ZN874:PA25 | 330 | 331.0523 | 46.04 | 1.0032 | 46.04 | 19069 | 4460 | 730898 | 2011-10-02 21:52 | 2011-10-02 23:15 | 83 | 11kV | 7455 | 649 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S1193 Lindfield Panel 10 tripped and reclosed on C phase IOC, Timing Relay, Lockout relay,Sealing Contactpor and EFI. Cause: Section of 11kV from Panel 10 at S1191 Lindfield to Ab1362 tee AB1362 to S928. All three bonds burnt off on tess to S928 Nelson Rd. Caused By Possin on UGOH. See OMS 731164 731165 730904 730898/903/900/901 | October | 2011 | 2012Q2 | 2012 | ZN1193:PA10 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2011-10-02 | N | 11.4869 | N | 7 | N | N | 1.1101 | 39.4971 | 5447.8941
| ZN874:PA26 | 642 | 385.4741 | 34.96 | 0.60043 | 34.96 | 19799 | 12782 | 730795 | 2011-10-02 14:39 | 2011-10-02 23:59 | 560 | 11kV | 13901 | 50 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 117785 1 fault operation 3 phase DOLF : 10Amp RAGCB Earth fault - Line fuse: Sw 42026 T/R. 1 ph L/F 40660 found blown. 11kV mains broken from pole DN-20344 to sub 51520. Repaired under A/P Excluded OMS # 730795, 730796, 730799, 730830, 730841 OMS 731507, 731508, 731511, 731512 | October | 2011 | 2012Q2 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2011-10-02 | N | 278.02 | N | 7 | N | N | 1.1101 | 39.4971 | 10158.4408
| ZN874:PA3 | 1039 | 722.873 | 42.21 | 0.69574 | 42.21 | 18807 | 2207 | 731443 | 2011-10-03 09:45 | 2011-10-03 14:05 | 260 | 11kV | 260 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | 117790 No protection operation. Report from Mine staff Adrian 0418 269363. Isolated area for mine staff. | October | 2011 | 2012Q2 | 2012 |  |  |  |  | OH | Not Veg | 2011-10-03 | N | 260 | N | 2 | N | N | 1.1101 | 39.4971 | 190.0003
| ZN874:PA4 | 1642 | 1448.9625 | 40.74 | 0.88244 | 40.74 | 19571 | 9677 | 731025 | 2011-10-03 13:20 | 2011-10-03 14:30 | 70 | 11kV | 1750 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 117791 section isolated to repair OHM beyond LF 40660 Excluded OMS 731025 OMS 731521 | October | 2011 | 2012Q2 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2011-10-03 | N | 70 | N | 2 | N | N | 1.1101 | 39.4971 | 1278.8484
| ZN874:PA7 | 950 | 745.5743 | 34.91 | 0.78482 | 34.91 | 19151 | 4925 | 731262 | 2011-10-04 10:29 | 2011-10-04 13:20 | 171 | 11kV | 257127 | 2030 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3425 Castle Cove Panel 30 tripped reclosed tripped and locked out on B phase earth Leakage, Timing, lockout, Fault Check and EFI. Signals: 11kV Trip At S1193 Lindfield Panel 8 tripped. Relays: C phase IOC and EFI Signals : 11kV Trip, Zone Earth No1 group earth. Cause: UG HV cable fault between Panel 8 Lindfield and 11kVUSL 1643. See OMS 731288 733502 733484/485/486/489/491/493/494/496/495/497/498 | October | 2011 | 2012Q2 | 2012 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | WILLOUGHBY | UG | Not Veg | 2011-10-04 | N | 126.6635 | N | 2 | N | N | 1.1101 | 39.4971 | 187900.8276
| ZN874:PA8 | 571 | 2046.7043 | 40.08 | 3.5844 | 40.08 | 19958 | 14407 | 731439 | 2011-10-04 14:03 | 2011-10-04 17:23 | 199.95 | 11kV | 42807.8 | 480 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC705 Knights Chadd tripped reclosed tripped and locked out on IOC. Cause: Tree brough 1 span of 11kV Mains down om Tee to PT1616 Mansfield Bayfield. See OMS 732378 732382 732383 732384 | October | 2011 | 2012Q2 | 2012 | ZN847:PA47 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2011-10-04 | N | 89.1829 | N | 2 | N | N | 1.1101 | 39.4971 | 31282.6776
| ZN874:PA9 | 374 | 304.0415 | 40.22 | 0.81295 | 40.22 | 19332 | 7548 | 731685 | 2011-10-05 08:21 | 2011-10-05 08:35 | 14 | 11kV | 1078 | 77 | HV | Staff Other | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | HW SW labelling incorrect when carrying out switching at S3694 Vivian st. Abnormal Switching for disc 268162 incorrect labelling of HV switches. See 731678, exlcdue 731676 | October | 2011 | 2012Q2 | 2012 | ZN3155:PA23 | ZN3155:PA40 | ZN03155/000040 | WOOLLAHRA | UG | Not Veg | 2011-10-05 | N | 14 | N | 9 | N | N | 1.1101 | 39.4971 | 787.7706
| ZN9118:PA11 | 2018 | 1408.6993 | 34.07 | 0.69807 | 34.07 | 20033 | 15369 | 731673 | 2011-10-05 08:11 | 2011-10-05 09:09 | 58 | 11kV | 3748 | 75 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At Sub 35800 Bankstown panel 4 "Sub 7397 Fairfiord Gow" feeder tripped and locked out on: Relays: Earth fault, Fault Check and EFI Signals: 11kv trip Field EFI's: Sub 7397, Sub 8888 Remarks: Foot path Lightning arrestor on UGOH to Sub 1262 Gow Nelson failed and has damaged centre phase insulator on the UGOH. Section of feeder from AB 81 to Sub 1262 Gow Nelson No.2 Related jobs: #733662, 733660, 733658, 731673, 731682 | October | 2011 | 2012Q2 | 2012 | ZN35800:PA4 | ZN35800:PA4 | ZN35800/000004 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2011-10-05 | N | 49.9733 | N | 9 | N | N | 1.1101 | 39.4971 | 2738.9279
| ZN9118:PA12 | 1328 | 1344.3543 | 31.86 | 1.0123 | 31.86 | 19394 | 8231 | 731657 | 2011-10-05 07:47 | 2011-10-05 11:10 | 203 | 11kV | 5552 | 34 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117805 2 fault operations B & C Phase conductor off insulator, section isolated to repair mains at pole FM-90025 Excluded oms 731657 OMS 732244, 732245 | October | 2011 | 2012Q2 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2011-10-05 | N | 163.2941 | N | 9 | N | N | 1.1101 | 39.4971 | 4057.2378
| ZN9118:PA13 | 1246 | 865.2968 | 32.46 | 0.69446 | 32.46 | 19323 | 7482 | 731862 | 2011-10-05 11:54 | 2011-10-05 13:33 | 99 | 11kV | 34650 | 350 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At CP2691 CB tripped, reclosed, tripped and locked out on Overcurrent. Cause Not ascertained for outage. | October | 2011 | 2012Q2 | 2012 | ZN965:PA33 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2011-10-05 | N | 99 | N | 9 | N | N | 1.1101 | 39.4971 | 25321.198
| ZN9118:PA15 | 2076 | 1211.9037 | 31.97 | 0.58377 | 31.97 | 19515 | 9160 | 731863 | 2011-10-05 11:30 | 2011-10-05 14:30 | 180 | 11kV | 10688 | 152 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117808 B Phase Earth fault SECTION ISOLATED TO REPAIR MAINS BEYOND 11 KV LINKS 6L702 AT POLE AJ-90033 Excluded OMS 731863 OMS 732231, 732232, 732234 | October | 2011 | 2012Q2 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2011-10-05 | N | 70.3158 | N | 9 | N | N | 1.1101 | 39.4971 | 7810.4752
| ZN9118:PA16 | 1224 | 991.9964 | 43.9 | 0.81045 | 43.9 | 19679 | 11324 | 731795 | 2011-10-05 10:55 | 2011-10-05 14:45 | 230 | 11kV | 33185 | 202 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1687 400A Fuse blown on ABC phase of distributor 2 At S1984 400A fuse blown on ABC phase of distributor 2. At S1911 400A fuse blown on A phase pof distributor 2 At S5680 400A fuse blown on B and C phase of distirbutor 1. Cause: Above DC's were in parallel with Pa30 castle cove at the time of interruption (04/10/2011) LV parallel failed See OMS 731808 733526 731796 731802 | October | 2011 | 2012Q2 | 2012 | ZN3425:PA30 | ZN1193:PA25 | ZN01193/000025 | WILLOUGHBY | UG | Not Veg | 2011-10-05 | N | 164.2822 | N | 9 | N | N | 1.1101 | 39.4971 | 24250.6192
| ZN9118:PA17 | 1054 | 1137.5989 | 31.1 | 1.0793 | 31.1 | 20338 | 19396 | 732150 | 2011-10-05 16:47 | 2011-10-05 17:03 | 16 | 11kV | 1616 | 101 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.19 tripped on earth fault. EFIs: S.14737 NOTE: EFI at new S.46804 Hely Anzac not energised long enough to charge battery & operate. Remarks: Suspect UG cable fault from S.46804 Hely Anzac to S.12049. New feeders & sub had only been energised for appromiately 30mins prior to failing (SAO#276300) Abnormal Switching: AB44880 OPEN - Sw B @ S.18164 CLOSED | October | 2011 | 2012Q2 | 2012 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | UG | Not Veg | 2011-10-05 | N | 16 | N | 9 | N | N | 1.1101 | 39.4971 | 1180.9251
| ZN9118:PA2 | 873 | 641.5423 | 32.57 | 0.73487 | 32.57 | 19691 | 11460 | 732064 | 2011-10-05 17:32 | 2011-10-05 18:18 | 46 | 11kV | 33488 | 728 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn.12660 Woy Woy Pnl.5 - REC 49100 Empire Awinya opened & Locked out Remarks: Tree brnach removed from 11kV OH near AB40701 | October | 2011 | 2012Q2 | 2012 | ZN12660:PA5 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2011-10-05 | N | 46 | N | 9 | N | N | 1.1101 | 39.4971 | 24472.0427
| ZN9118:PA20 | 2153 | 1422.1062 | 32.02 | 0.66052 | 32.02 | 19324 | 7484 | 732080 | 2011-10-05 15:30 | 2011-10-05 19:00 | 210 | 11kV | 630 | 3 | HV | Staff Operation | Utility Process Issue | Fuse | Unplanned | Unselected | N | LID 117810 SEE PLANNED OUTAGE REPORT 117801.(SI 15737).DOLF LEFT OPEN AFTER PLANNED OUTAGE. Excluded OMS REPORT 732080 . OMS 732187 | October | 2011 | 2012Q2 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2011-10-05 | N | 210 | N | 9 | N | N | 1.1101 | 39.4971 | 460.3854
| ZN9118:PA21 | 1381 | 1306.2875 | 30.92 | 0.9459 | 30.92 | 19054 | 4375 | 732124 | 2011-10-06 04:47 | 2011-10-06 06:10 | 83 | 11kV | 9296 | 112 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 117813 11kV mains on ground at ABS 123. ABS 123 lock had been cut, switch opened & 3 span of mains stolen on live side of ABS 123. Earths found stolen from Mackay sub 27538 & Blackhill Rd sub 25602. Excluded OMS 732124, 732155, 732472, 732535 OMS 732676, 732680 | October | 2011 | 2012Q2 | 2012 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2011-10-06 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 6793.2426
| ZN9118:PA22 | 1479 | 1225.787 | 34.19 | 0.82879 | 34.19 | 19231 | 6327 | 732472 | 2011-10-06 06:28 | 2011-10-06 16:55 | 627 | 11kV | 50799 | 112 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 117813 11kV mains on ground at ABS 123. ABS 123 lock had been cut, switch opened & 3 span of mains stolen on live side of ABS 123. Earths found stolen from Mackay sub 27538 & Blackhill Rd sub 25602. Excluded OMS 732124, 732155, 732472, 732535 OMS 732676, 732680 | October | 2011 | 2012Q2 | 2012 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2011-10-06 | N | 453.5625 | N | 4 | N | N | 1.1101 | 39.4971 | 37122.4109
| ZN9118:PA24 | 1337 | 1097.8349 | 40.45 | 0.82112 | 40.45 | 19677 | 11191 | 732525 | 2011-10-06 20:09 | 2011-10-06 21:18 | 69 | 11kV | 8567 | 747 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | PT13690 Cams Yeramba Centre Phase HDO 31.5Amp fuse blown - REC 45138 also tripped Remarks: Cause not ascertained. See # 732573 for interruptiong to REC45138. TCon to inspect PT13690 in day light. DOp unable to read MDI requires new cover. | October | 2011 | 2012Q2 | 2012 | ZN12590:PA6 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2011-10-06 | N | 11.4685 | N | 4 | N | N | 1.1101 | 39.4971 | 6260.5109
| ZN9118:PA26 | 1728 | 1593.7281 | 30.34 | 0.9223 | 30.34 | 20214 | 17153 | 732509 | 2011-10-06 18:51 | 2011-10-06 21:23 | 152 | 11kV | 2888 | 19 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117820 Sub isolated to repair faulty LV tapping. Excluded OMS Job No. 732509. OMS 732597 | October | 2011 | 2012Q2 | 2012 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2011-10-06 | N | 152 | N | 4 | N | N | 1.1101 | 39.4971 | 2110.4652
| ZN9118:PA3 | 780 | 678.8024 | 30.23 | 0.87026 | 30.23 | 19798 | 12781 | 732548 | 2011-10-07 03:03 | 2011-10-07 05:30 | 147 | 11kV | 2352 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 117821 A Phase DOLF : 16Amp Excluded OMS 732548 OMS 732570 | October | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-10-07 | N | 147 | N | 8 | N | N | 1.1101 | 39.4971 | 1718.7722
| ZN9118:PA6 | 1874 | 1969.0441 | 44.08 | 1.0507 | 44.08 | 19137 | 4874 | 732551 | 2011-10-07 04:00 | 2011-10-07 05:45 | 105 | 11kV | 101888 | 1185 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ S15003 Balgowlah Pnl 1 "S16980 Sydney Waratah" Feeder tripped Relays - EF, Fault Check, EFI Signals - 11kV, ZE 11kV feeder fault from S16980 Sydney Waratah to S17011 Kanangra Peronne to S17102 New west tee PT15597 Peronne Av See, 732592, 732594 | October | 2011 | 2012Q2 | 2012 | ZN15003:PA1 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2011-10-07 | N | 85.9814 | N | 8 | N | N | 1.1101 | 39.4971 | 74456.7452
| ZN9118:PA7 | 1008 | 1370.8372 | 51.77 | 1.36 | 51.77 | 20331 | 19348 | 732755 | 2011-10-07 12:27 | 2011-10-07 17:08 | 281.1833 | 11kV | 130250.8667 | 1858 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 1610 Homebush Bay - Panel 13 "Sub 7637 Holker Jamison #2" tripped on - O/C relay GIN - B phase and neutral with EFI. Alarms - 11kv trip, Zone Earth, TX 1 group Earth EFI down - Sub 7637 Remarks: 11kv UG fault between Sub 7637 Holker Jamison #2 and Sub 4595 Blaxland Plover Related jobs: #732784, 732758, 732755, 737496, 737494 | October | 2011 | 2012Q2 | 2012 | ZN1610:PA13 | ZN1610:PA13 | ZN01610/000013 | PARRAMATTA | UG | Not Veg | 2011-10-07 | N | 70.1027 | N | 8 | N | N | 1.1101 | 39.4971 | 95183.4916
| ZN9118:PA8 | 1375 | 1328.3537 | 30.31 | 0.96608 | 30.31 | 20148 | 16321 | 732947 | 2011-10-07 21:12 | 2011-10-07 23:12 | 120 | 11kV | 91212 | 1497 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | Remarks: stormy night lightning strikes in the area Zn.12580 Erina pnl.16 tripped on A & B Phase Overcurrent & EFI Remarks: stormy night lightning strikes in the area | October | 2011 | 2012Q2 | 2012 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2011-10-07 | N | 60.9299 | N | 8 | N | N | 1.1101 | 39.4971 | 66655.0393
| 206:34432 | 1165 | 1182.6872 | 33.46 | 1.0152 | 33.46 | 20066 | 15773 | 732953 | 2011-10-07 21:22 | 2011-10-07 23:28 | 126 | 11kV | 109998 | 873 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | Avoca zone pnl.19 tripped on : OC, EFI remarks: Lightning strike near AB43616 | October | 2011 | 2012Q2 | 2012 | ZN12570:PA19 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Not Veg | 2011-10-07 | N | 126 | N | 8 | N | N | 1.1101 | 39.4971 | 80383.294
| 206:34434 | 1533 | 1077.0565 | 31.31 | 0.70258 | 31.31 | 19213 | 5985 | 732955 | 2011-10-07 21:22 | 2011-10-07 23:41 | 139 | 11kV | 92435 | 665 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | Wamberal Zone Pnl.10 tripped on B & C Phase Overcurrent (bazler realy 1.2.1, 51BC EFI) Remarks: Stormy night lightning strikes in the area | October | 2011 | 2012Q2 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2011-10-07 | N | 139 | N | 8 | N | N | 1.1101 | 39.4971 | 67548.7716
| 206:34435 | 164 | 111.9274 | 31.51 | 0.68248 | 31.51 | 19016 | 4180 | 732949 | 2011-10-07 21:14 | 2011-10-07 23:50 | 156 | 11kV | 205295 | 1741 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Zn 12570 Avoca Pnl.9 tripped on Inst OC, Timed OC and EFI. Remarks: Storm See OMS # 733542 733543 733542 733544 733547 Excluded: 732949 | October | 2011 | 2012Q2 | 2012 | ZN12570:PA9 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Veg | 2011-10-07 | N | 117.9179 | N | 8 | N | N | 1.1101 | 39.4971 | 150023.5308
| 206:34437 | 30 | 41.0322 | #N/A | 1.3677 | 39.4971 | 19180 | 5359 | 732950 | 2011-10-07 21:14 | 2011-10-08 00:50 | 216 | 11kV | 278170 | 1431 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.11 tripped on Overcurrent, timed OC, SEF and EFI Remarks: Bond burnt at tee between AB40872 AB42968 and LK44425 See OMS # 733578 733580 733579 Excluded: 732952 732950 | October | 2011 | 2012Q2 | 2012 | ZN12570:PA11 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Not Veg | 2011-10-07 | N | 194.3885 | N | 8 | N | N | 1.1101 | 39.4971 | 203278.4314
| 206:34438 | 619 | 520.4301 | 36.67 | 0.84076 | 36.67 | 18959 | 3504 | 732970 | 2011-10-08 01:11 | 2011-10-08 02:15 | 64 | 11kV | 5760 | 90 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | PT.14963 Clarence Digby - Roadside HV dropout fuse blew (BBLAS 31.5K) Remarks: Road side lightning arrestor blown causeing HV drop out fuse to blwon. LA not cut away - restored via LV // | October | 2011 | 2012Q2 | 2012 | ZN12580:PA16 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2011-10-08 | N | 64 | N | 20 | Y | Y | 1.1101 | 39.4971 | 4209.2381
| 206:34440 | 1306 | 708.7574 | 31.19 | 0.54269 | 31.19 | 20276 | 18121 | 732967 | 2011-10-08 00:13 | 2011-10-08 02:50 | 157 | 11kV | 8478 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117832 3 phase DOLF : 20Amp. Excluded OMS 732967, 732969, 732971 OMS 733668 | October | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 157 | N | 20 | Y | Y | 1.1101 | 39.4971 | 6195.4723
| 206:34441 | 1359 | 1561.1132 | 41.07 | 1.1487 | 41.07 | 19257 | 6619 | 732972 | 2011-10-08 02:48 | 2011-10-08 03:30 | 42 | 11kV | 168 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117837 A Phase DOLF : 10Amp. Excluded OMS 732972 OMS 733682 | October | 2011 | 2012Q2 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 42 | N | 20 | Y | Y | 1.1101 | 39.4971 | 122.7694
| ZN187:PA10 | 520 | 923.9266 | #N/A | 1.7768 | 39.4971 | 20210 | 17122 | 733567 | 2011-10-08 03:31 | 2011-10-08 03:52 | 21 | 11kV | 1197 | 1177 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117838 Trip & Reclose 1 fault operation A & C Phase Overcurrent | October | 2011 | 2012Q2 | 2012 | 222:2014 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Veg | 2011-10-08 | N | 1.017 | N | 20 | Y | Y | 1.1101 | 39.4971 | 874.7323
| ZN187:PA12 | 44 | 570.3717 | #N/A | 12.963 | 39.4971 | 19528 | 9300 | 732976 | 2011-10-08 03:45 | 2011-10-08 05:45 | 120 | 11kV | 186136 | 1667 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Zn.12600 Lisarwo pnl9 tripped on A phase Overcurrent EFI FIELD EFIs: S.14911 14921 18461 4686 Remarks: No cause found See OMS # 733620 733621 733619 733616 733611 Excluded: 732976 | October | 2011 | 2012Q2 | 2012 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2011-10-08 | N | 111.6593 | N | 20 | Y | Y | 1.1101 | 39.4971 | 136022.6987
| ZN187:PA13 | 1315 | 848.8725 | 36.22 | 0.64553 | 36.22 | 18588 | 117 | 732978 | 2011-10-08 04:42 | 2011-10-08 08:10 | 208 | 11kV | 624 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117848 A Phase DOLF Excluded OMS 732978 OMS 733688 | October | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 208 | N | 20 | Y | Y | 1.1101 | 39.4971 | 456.0008
| ZN187:PA14 | 665 | 764.6186 | 48.03 | 1.1498 | 48.03 | 20109 | 16064 | 732991 | 2011-10-08 03:49 | 2011-10-08 09:00 | 311 | 11kV | 9019 | 29 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | PT.11931 Portsmouth Worthing - Roadside HDo 16Amp fuse blown Remarks: Storm Note: suspect PT11287 in LV // with PT11931 due to customer calls when feeder tripped / reclosed @3:48 still off @ 04:00 | October | 2011 | 2012Q2 | 2012 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Not Veg | 2011-10-08 | N | 311 | N | 20 | Y | Y | 1.1101 | 39.4971 | 6590.8192
| ZN187:PA16 | 1552 | 1099.2546 | 38.51 | 0.70828 | 38.51 | 18787 | 2029 | 732986 | 2011-10-08 06:35 | 2011-10-08 09:05 | 150 | 11kV | 150 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117850 Single phase DOLF : 10Amp Excluded OMS 732986 OMS 733694 | October | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 150 | N | 20 | Y | Y | 1.1101 | 39.4971 | 109.6156
| ZN187:PA17 | 1423 | 1193.1687 | 39.92 | 0.83849 | 39.92 | 18810 | 2227 | 733015 | 2011-10-08 08:27 | 2011-10-08 09:30 | 63 | 11kV | 630 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | PT.11671 Loivers Taylors -Footpath side phase HDO 16Amp fuse blown Remarks: Storm | October | 2011 | 2012Q2 | 2012 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2011-10-08 | N | 63 | N | 20 | Y | Y | 1.1101 | 39.4971 | 460.3854
| ZN187:PA19 | 309 | 378.7927 | 36.54 | 1.2259 | 36.54 | 19848 | 13253 | 733030 | 2011-10-08 09:06 | 2011-10-08 09:40 | 34 | 11kV | 68 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117853 A & C Phase DOLF : 10Amp Excluded OMS 733030 LID 733698 | October | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 34 | N | 20 | Y | Y | 1.1101 | 39.4971 | 49.6924
| ZN187:PA20 | 2119 | 1508.9813 | 38.47 | 0.71212 | 38.47 | 19840 | 13145 | 733014 | 2011-10-08 08:25 | 2011-10-08 10:53 | 148 | 11kV | 296 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117858 Single phase DOLF : 10Amp. Excluded OMS 733014 OMS 733697 | October | 2011 | 2012Q2 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2011-10-08 | N | 148 | N | 20 | Y | Y | 1.1101 | 39.4971 | 216.3081
| ZN187:PA21 | 1957 | 1281.6076 | 36.08 | 0.65488 | 36.08 | 18587 | 114 | 733081 | 2011-10-08 10:41 | 2011-10-08 11:54 | 73 | 11kV | 73 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117859 B Phase DOLF : 10Amp. Excluded OMS 733081 OMS 733713 | October | 2011 | 2012Q2 | 2012 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 73 | N | 20 | Y | Y | 1.1101 | 39.4971 | 53.3462
| ZN187:PA22 | 1120 | 972.4838 | 43.88 | 0.86829 | 43.88 | 20010 | 15003 | 732974 | 2011-10-08 03:08 | 2011-10-08 12:00 | 532 | 11kV | 160144 | 814 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 117842 7 fault operations Earth fault RMU failed at Victory Parade sub 39822 Excluded OMS 732974, 732982. OMS 733447, 733449, 733451 | October | 2011 | 2012Q2 | 2012 | 225:33679 | 270:83594 | ZN00270/083594 | LAKE MACQUARIE | UG | Not Veg | 2011-10-08 | N | 196.7371 | N | 20 | Y | Y | 1.1101 | 39.4971 | 117028.5118
| ZN187:PA23 | 375 | 1146.4812 | 42.89 | 3.0573 | 42.89 | 19692 | 11479 | 733086 | 2011-10-08 10:54 | 2011-10-08 12:30 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117860 Single phase DOLF : 10Amp Excluded OMS 733086 OMS 733718 | October | 2011 | 2012Q2 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2011-10-08 | N | 96 | N | 20 | Y | Y | 1.1101 | 39.4971 | 70.154
| ZN187:PA24 | 112 | 191.7214 | 47.8 | 1.7118 | 47.8 | 18989 | 3887 | 732984 | 2011-10-08 06:15 | 2011-10-08 16:00 | 585 | 11kV | 348597 | 1119 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 117854 Cable fault occured between 34846 & 35058, Coincidently, Switch 90267 Newbolds failed in service Fdr 34849 supplied from Fdr 34843 at the time of tripping. CASS Job No. 626426. CB 90267 failed which caused field connection to fail. Excluded OMS 733061, 733066, 733085, 733118 OMS 734144, 734147, 734163 | October | 2011 | 2012Q2 | 2012 | 240:34846 | 240:34846 | ZN00240/034846 | NEWCASTLE | UG | Not Veg | 2011-10-08 | N | 311.5255 | N | 20 | Y | Y | 1.1101 | 39.4971 | 254744.4057
| ZN187:PA26 | 190 | 281.9721 | #N/A | 1.4841 | 39.4971 | 19900 | 13738 | 733158 | 2011-10-08 15:51 | 2011-10-08 16:48 | 57 | 11kV | 17100 | 300 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S2400 Berowra Panel 23 tripped Signals: Eroup Earth, Zone Earth, 11kV Trip. Relays: B phase overcurrent, EFI, Earth Fault Check. Cause: Dop patrolled feeder but could not find anything. Report of lightning stricke in area at the same time. | October | 2011 | 2012Q2 | 2012 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | OH | Veg | 2011-10-08 | N | 57 | N | 20 | Y | Y | 1.1101 | 39.4971 | 12496.1756
| ZN187:PA28 | 732 | 1184.6461 | 47.7 | 1.6184 | 47.7 | 20344 | 19447 | 733154 | 2011-10-08 15:39 | 2011-10-08 18:10 | 151 | 11kV | 231207 | 2355 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At Sub 1285 Greenacre Park - Panel 27 "Sub 7025 Wentworth Mayvic, Sub 4861, Sub 6424 "Feeder tripped on - 27 Right with - Earth faults with EFI Alarms - 11kv trip, Zone Earth TX 2 Group Earth EFIs down - Subs 725, 4585, 8293, 7427, 7461 and 4296 Remarks: Ausgrid contractors cut HV cable when digging near Sub 2065. Feeder - AB2939 to S2065 to S3331 Tee PT1734. OMS 733165. Related jobs: #733607, 733165, 733614, 733610, 733613, 733154 | October | 2011 | 2012Q2 | 2012 | ZN1285:PA27 | ZN1285:PA27 | ZN01285/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-10-08 | N | 98.1771 | N | 20 | Y | Y | 1.1101 | 39.4971 | 168959.2561
| ZN187:PA29 | 136 | 137.0651 | 64.31 | 1.0078 | 64.31 | 18938 | 3389 | 733203 | 2011-10-08 19:35 | 2011-10-08 20:39 | 64 | 11kV | 576 | 9 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 117863 Section isolated for repairs Lightning hit pole Excluded OMS 733170, 733171, 733203 OMS 733727 | October | 2011 | 2012Q2 | 2012 | 807:74179 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2011-10-08 | N | 64 | N | 20 | Y | Y | 1.1101 | 39.4971 | 420.9238
| ZN187:PA30 | 1746 | 1375.1747 | 39.17 | 0.78761 | 39.17 | 20131 | 16174 | 733209 | 2011-10-08 20:19 | 2011-10-08 22:00 | 101 | 11kV | 505 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 117866 B Phase DOLF : 10Amp. Excluded OMS (incorrect premise) 733209 OMS 733759 | October | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2011-10-08 | N | 101 | N | 20 | Y | Y | 1.1101 | 39.4971 | 369.0391
| ZN187:PA4 | 1298 | 1425.5615 | 41.36 | 1.0983 | 41.36 | 19738 | 12281 | 733228 | 2011-10-09 04:25 | 2011-10-09 05:29 | 64 | 11kV | 31076 | 665 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Wamberal Zonw Pnl.10 tripped on A & B phase IOC, Trip Alarm 121 Remarks: USL 40062 Road & Centre phase flashed pver breaking bonds and possible link damage | October | 2011 | 2012Q2 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2011-10-09 | N | 46.7308 | N | 5 | N | N | 1.1101 | 39.4971 | 22709.4242
| ZN187:PA6 | 181 | 616.9176 | #N/A | 3.4084 | 39.4971 | 18635 | 554 | 733241 | 2011-10-09 08:15 | 2011-10-09 09:35 | 80 | 11kV | 3840 | 48 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Section of 11kV feeder from AB41727 to LK41726 was interrupted to reapir faulty LK40062 - See previous interrution @ 4:25 | October | 2011 | 2012Q2 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2011-10-09 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 2806.1587
| ZN187:PA7 | 423 | 380.6141 | #N/A | 0.8998 | 39.4971 | 18992 | 3910 | 733244 | 2011-10-09 07:51 | 2011-10-09 10:50 | 179 | 11kV | 179 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117869 B Phase DOLF : 10Amp cause of blown dolf not ascertained. after dolf replaced section of fdr interupted to repair llc to sub 51196 see report 117870 Excluded oms 733244 OMS 733766 | October | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-10-09 | N | 179 | N | 5 | N | N | 1.1101 | 39.4971 | 130.8079
| ZN187:PA8 | 995 | 594.5499 | 39.46 | 0.59754 | 39.46 | 19272 | 6876 | 733262 | 2011-10-09 09:27 | 2011-10-09 10:50 | 83 | 11kV | 415 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117870 fdr intrupted to repair llc at sub 51196 McTaggart see report 117869 | October | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-10-09 | N | 83 | N | 5 | N | N | 1.1101 | 39.4971 | 303.2698
| ZN35555:PA13 | 2293 | 1616.5598 | 37.69 | 0.705 | 37.69 | 20249 | 17750 | 733287 | 2011-10-09 12:19 | 2011-10-09 14:40 | 141 | 11kV | 846 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 117871 Trip & Lockout 3 phase Excluded OMS 733287 OMS 733786 | October | 2011 | 2012Q2 | 2012 |  |  |  | SINGLETON | OH | Veg | 2011-10-09 | N | 141 | N | 5 | N | N | 1.1101 | 39.4971 | 618.2318
| ZN35555:PA14 | 244 | 176.3012 | 59.85 | 0.72255 | 59.85 | 20078 | 15857 | 734653 | 2011-10-08 14:43 | 2011-10-09 15:30 | 1487 | 11kV | 3652 | 341 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | Ex Pnl.1 Somersby - REC46763 Grants Keighley 0.3 tripped / reclosed on IOC/EF Abnormal Switching: AB43334 CLOSED, CB PNL.5 Peats Ridge OPEN remarks: Defective PT @ PT.14029 -to be replaced See Also # 734657 734653 734656 Duration checked - OK-DQ1 | October | 2011 | 2012Q2 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2011-10-08 | N | 10.7097 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2668.7739
| ZN35555:PA16 | 1580 | 754.3799 | 34.18 | 0.47746 | 34.18 | 19341 | 7596 | 733394 | 2011-10-10 07:15 | 2011-10-10 08:33 | 78 | 11kV | 77844 | 998 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3155 Double Bay Pa24 fdr tripped on trnaslay fault check Tx3 GE Fault check Signals- 11kv trip tx3 ge ze Abnormal - S535/SwE Closed S6754/SwA Open From To Restored Time S5547 Whole Fdr 6 0833 Suspect UG fdr fault @ Double Bay Pa24 See 733990 LV// 733434 733420 733415 733398 exclude 733394,6,7 | October | 2011 | 2012Q2 | 2012 | ZN3155:PA24 | ZN3155:PA24 | ZN03155/000024 | WOOLLAHRA | UG | Not Veg | 2011-10-10 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 56886.0992
| ZN35555:PA17 | 1509 | 1516.6181 | 39.32 | 1.005 | 39.32 | 19726 | 12029 | 733407 | 2011-10-10 07:42 | 2011-10-10 09:11 | 89 | 11kV | 205679 | 2311 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3922 Drummoyne Panel 5 "S36165 Byrnes Manning etc Fdr" tripped. Relays - C phase IOC and Timed O/C, EFI, Fault check Signals - 11kv trip, #1 TX group earth, Zone earth Field EFIs: - Nil Remarks: UG feeder fault from Panel 5 at S3922 Drummoyne to SwA at S36165 Byrnes Manning to Sw B at S2401 Sibbick Eden to Sw B at S1528 M.W.S & D.B Martin St (Zn 1 Five Dock) Related jobs: #733968, 733407, 733457 | October | 2011 | 2012Q2 | 2012 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2011-10-10 | N | 89 | N | 4 | N | N | 1.1101 | 39.4971 | 150304.1467
| ZN35555:PA19 | 1348 | 1194.6891 | 38.31 | 0.88627 | 38.31 | 18687 | 1038 | 733520 | 2011-10-10 10:16 | 2011-10-10 12:45 | 149 | 11kV | 149 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 117882 Single phase bond Tail burnt off sub dolf (dolf support fitted) Excluded OMS 733520 OMS 734006 | October | 2011 | 2012Q2 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2011-10-10 | N | 149 | N | 4 | N | N | 1.1101 | 39.4971 | 108.8848
| ZN35555:PA2 | 1367 | 1125.1908 | 40.84 | 0.82311 | 40.84 | 19263 | 6641 | 733725 | 2011-10-10 13:51 | 2011-10-10 14:35 | 44.25 | 11kV | 3318.75 | 75 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse | Unplanned | Unselected | N | LID 117885 A Phase DOLF : 40Amp. Fuse fatigue. No readings taken. Excluded OMS 733733 OMS 733725 | October | 2011 | 2012Q2 | 2012 | 256:80652 | 256:80652 | ZN00256/080652 | NEWCASTLE | OH | Not Veg | 2011-10-10 | N | 44.25 | N | 4 | N | N | 1.1101 | 39.4971 | 2425.2446
| ZN35555:PA20 | 1671 | 1470.8688 | 36.19 | 0.88023 | 36.19 | 19525 | 9244 | 734190 | 2011-10-11 16:11 | 2011-10-12 01:30 | 559 | 11kV | 12343 | 120 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | LID 117902 2 fault operations, Earth Fault Full tension sleeve failed between poles HV-10006 and HV-10173 Refer to related records: 734945. 734940, 734936 and 734933 | October | 2011 | 2012Q2 | 2012 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | Unknown | Not Veg | 2011-10-11 | N | 102.8583 | N | 1 | N | N | 1.1101 | 39.4971 | 9019.9003
| ZN35555:PA3 | 1562 | 1357.1859 | 38.6 | 0.86888 | 38.6 | 18628 | 468 | 734283 | 2011-10-12 06:04 | 2011-10-12 07:40 | 96 | 11kV | 1728 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.15065 Cooyong Rd East (Ex Pnl 6) Road side 31.5K HDO Blown No Apparent cause | October | 2011 | 2012Q2 | 2012 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2011-10-12 | N | 96 | N | 4 | N | N | 1.1101 | 39.4971 | 1262.7714
| ZN35555:PA5 | 2276 | 1566.6941 | 39.42 | 0.68835 | 39.42 | 19843 | 13170 | 734338 | 2011-10-12 09:35 | 2011-10-12 10:30 | 55 | 11kV | 1265 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117908 Line DOLF replaced, Phase C Fuse size: 16Amp Note LID references OMS 734339, unable to locate this OMS number when this record was entered | October | 2011 | 2012Q2 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2011-10-12 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 924.4247
| ZN35555:PA6 | 974 | 1136.6944 | 35.46 | 1.167 | 35.46 | 19101 | 4646 | 734358 | 2011-10-12 09:54 | 2011-10-12 13:20 | 206 | 11kV | 412 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.14317 Bloodtree Geroge 0.3 - C Phase HDO blown (16A) Remarks: Fuse Fatigue | October | 2011 | 2012Q2 | 2012 | ZN12630:PA4 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2011-10-12 | N | 206 | N | 4 | N | N | 1.1101 | 39.4971 | 301.0774
| ZN35555:PA8 | 1316 | 1035.5527 | 44.57 | 0.78689 | 44.57 | 19489 | 9022 | 734436 | 2011-10-12 13:06 | 2011-10-12 13:55 | 49 | 11kV | 1127 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117916 CC1: 06-"Urgent - O.H Mains - No others"replaced spur fuse - refer OMS 734436 Fuse size: 16 Amp No cause found, not storm condition, Note C phase lie dolf had blown earlier in the day refer to OMS 734826, unable to determine if events are related | October | 2011 | 2012Q2 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2011-10-12 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 823.5784
| ZN35555:PA9 | 1719 | 764.7454 | 31.58 | 0.44488 | 31.58 | 20213 | 17147 | 734648 | 2011-10-13 06:00 | 2011-10-13 09:50 | 230 | 11kV | 230 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117924 Fuse size: 63Amo Line Dolf replaced, no cause found, not storm conditions | October | 2011 | 2012Q2 | 2012 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2011-10-13 | N | 230 | N | 3 | N | N | 1.1101 | 39.4971 | 168.0772
| ZN263:PA31 32DEF | 80 | 727.1626 | #N/A | 9.0895 | 39.4971 | 20105 | 16032 | 734958 | 2011-10-13 15:43 | 2011-10-13 16:43 | 60 | 11kV | 101228 | 2543 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S1114 North Ryde Panel 10 Tripped on Earth Fault. At S129 Hunters Hill. Panel 17 Tripped on Earth Fault Cause: Feeder Failed after repairs whilst switching. Abnormal Switching: SW B closed at S597 SW B Open at S2115. See OMS 735172 735169 734996/974/984/979/960/973/978/985/966/972/968/977/970/958 | October | 2011 | 2012Q2 | 2012 | ZN1114:PA10 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Veg | 2011-10-13 | N | 39.8065 | N | 3 | N | N | 1.1101 | 39.4971 | 73974.4367
| ZN263:PA31 32GHJ | 815 | 4793.0255 | #N/A | 5.881 | 39.4971 | 19517 | 9179 | 735054 | 2011-10-13 18:52 | 2011-10-13 20:24 | 91.6833 | 11kV | 47260.2333 | 540 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1285 Greenacre Park 22 "Jacobs Heatth' Fdr tripped on B phase timed OC, EFI, Fault check Remarks: Suspect UG fdr fault S1285 Greenacre Park P22 to S5443 Jacobs Heath Related jobs: #735054, 735074, 737391 | October | 2011 | 2012Q2 | 2012 | ZN1285:PA22 | ZN1285:PA22 | ZN01285/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-10-13 | N | 87.519 | N | 3 | N | N | 1.1101 | 39.4971 | 34536.3846
| ZN263:PA31 32KLM | 361 | 1997.1137 | #N/A | 5.5322 | 39.4971 | 19260 | 6626 | 735117 | 2011-10-14 07:00 | 2011-10-14 10:00 | 180 | 11kV | 180 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 117941 Fuse size: 10Amp. It is likely that the Dolf operated during the previous electrical storm Note: LID references 735171, at this time I am unable to locate that LID report in OMS, and have replicated the outage | October | 2011 | 2012Q2 | 2012 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2011-10-14 | N | 180 | N | 5 | N | N | 1.1101 | 39.4971 | 131.5387
| ZN263:PA33 34ABC | 170 | 1954.4855 | #N/A | 11.497 | 39.4971 | 19980 | 14722 | 735343 | 2011-10-14 13:58 | 2011-10-14 15:56 | 118 | 11kV | 40474 | 343 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.398 Dulwich Hill 11kV trip, Zone Earth, TX.1 & 2 Group Earth. P-31 The Holden Liverpool fdr tripped on earth fault 51N. REMARKS: HV cable fault between S.35656 (swB) and S.48818 (swA) | October | 2011 | 2012Q2 | 2012 | ZN398:PA31 | ZN37300:PA6 | ZN37300/000006 | INNER WEST | UG | Not Veg | 2011-10-14 | N | 118 | N | 5 | N | N | 1.1101 | 39.4971 | 29577.2054
| ZN263:PA33 34KLM | 37 | 578.9119 | #N/A | 15.6463 | 39.4971 | 20080 | 15872 | 735372 | 2011-10-14 14:26 | 2011-10-14 16:50 | 144 | 11kV | 144 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 117951/01 Fuse Size 10 Amp No Cause found ( Not storm condition) 240V, 90A Refer to OMS 735372 | October | 2011 | 2012Q2 | 2012 | 232:33413 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Veg | 2011-10-14 | N | 144 | N | 5 | N | N | 1.1101 | 39.4971 | 105.231
| ZN263:PA35 37ABC | 115 | 1199.5078 | #N/A | 10.4305 | 39.4971 | 19725 | 12025 | 735434 | 2011-10-14 16:14 | 2011-10-14 21:30 | 316 | 11kV | 44626 | 394 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 117952. 1 Fault operations, Sensitive earth fault. It appears tapping contacted the cross arem and burnt into it at pole GM-61705, this x-arm will need replacing in the near future as it was not replaced at the time the tapping was repaired. Trigger: Inadequate Design and Construction Restoration switching, refer to replicated records 736166, 736168, 736171, 7367172,736175, 736176, 736178 and 736179 | October | 2011 | 2012Q2 | 2012 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2011-10-14 | N | 113.264 | N | 5 | N | N | 1.1101 | 39.4971 | 32611.3646
| ZN263:PA35 37DEF | 122 | 1795.5755 | #N/A | 14.7178 | 39.4971 | 19402 | 8347 | 735506 | 2011-10-14 22:34 | 2011-10-15 00:35 | 121 | 11kV | 82111 | 1076 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa14 lavelled CP 491 tripped on Earth leakage EFI 11kv trip ZE #4 GE EFI- CP491 S6574 S5186 S35272 S609 Suspect UG fault btw S609 - S35133 - S35273 See 736147,8,51 GIS 736162,3 Exclude 735506,17,18 From To Restored DC Time Zn1788Pa14 S35272SwB 9 2333 S2291 S35133SwA 2 2353 S35272SwB S609SwC 1 0012 S35273 Via LV// 1 0035 | October | 2011 | 2012Q2 | 2012 | ZN1788:PA14 | ZN1788:PA14 | ZN01788/000014 | RANDWICK | UG | Not Veg | 2011-10-14 | N | 76.3113 | N | 5 | N | N | 1.1101 | 39.4971 | 60004.2969
| ZN263:PA35 37GHJ | 185 | 843.6956 | #N/A | 4.5605 | 39.4971 | 20025 | 15263 | 735522 | 2011-10-15 00:13 | 2011-10-15 01:19 | 66 | 11kV | 2376 | 36 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14143 Somersby - Pnl.21 tripped on: ABC phase Overcurrent Field EFIs: S.18108 ,18052 18270 18849 14902 Remarks: Branch near PT11047 | October | 2011 | 2012Q2 | 2012 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2011-10-15 | N | 66 | N | 5 | N | N | 1.1101 | 39.4971 | 1736.3107
| ZN7481:PA10 | 24 | 662.6802 | #N/A | 27.6117 | 39.4971 | 19558 | 9623 | 735644 | 2011-10-15 14:00 | 2011-10-15 14:43 | 43 | 11kV | 72584 | 1688 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.13 tripped / reclosed / tripped and locked out on: B & C Phase Overcurrent, IOC reclose timing, lockout EFI Field EFIs: S.14116 18117 12869 14215 14568 Remarks: Branch found on mains near LK44105 | October | 2011 | 2012Q2 | 2012 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2011-10-15 | N | 43 | N | 5 | N | N | 1.1101 | 39.4971 | 53042.2463
| ZN7481:PA12 | 2872 | 2581.0886 | #N/A | 0.89871 | 39.4971 | 20266 | 18022 | 735584 | 2011-10-15 09:40 | 2011-10-15 19:05 | 565 | 11kV | 5905 | 17 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Previous Storm | N | LID 117960 - 2 pages Lightning strike pole EC-50024. Mains fell away from pole EC-50023 to pole EC-80025. Pole EC-50024 & Link 74126 X arm also needed replacing. Staff noticed DOLF 70357 blown whilst replacing pole damaged by lightning Replication switching required - refer to OMS 736195, 736197, 736198 and 736200 | October | 2011 | 2012Q2 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2011-10-15 | N | 347.3529 | N | 5 | N | N | 1.1101 | 39.4971 | 4315.1998
| ZN7481:PA13 | 1633 | 3085.0458 | #N/A | 1.8892 | 39.4971 | 19381 | 8077 | 735660 | 2011-10-15 18:00 | 2011-10-15 19:10 | 70 | 11kV | 70 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 117962 No OMS number as an Ausgrid staff member spotted the fault. Fault was a HV main on the ground between sub 72966 and ple SM-20078. No protection operated | October | 2011 | 2012Q2 | 2012 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2011-10-15 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 51.1539
| ZN7481:PA14 | 1400 | 2352.2419 | 43.8 | 1.6802 | 43.8 | 19987 | 14883 | 735753 | 2011-10-16 08:11 | 2011-10-16 09:17 | 66 | 11kV | 42259 | 674 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3425 Castle Cove Pa17 tripped on Earth Fault, EFI Fault Check and 11kV Trip Cause: Suspect UG cable fault S35061 to S7881 to S4108 Suspected UG fault between S35061 Cambridge Help to S7881 Obrien Railway SW/D to S4108 Railway Chatswood Plaza SW/A See OMS 736956 736957 735753 | October | 2011 | 2012Q2 | 2012 | ZN3425:PA17 | ZN3425:PA17 | ZN03425/000017 | WILLOUGHBY | UG | Not Veg | 2011-10-16 | N | 62.6988 | N | 8 | N | N | 1.1101 | 39.4971 | 30881.6308
| ZN7481:PA16 | 95 | 675.1115 | #N/A | 7.1064 | 39.4971 | 19313 | 7363 | 735713 | 2011-10-15 19:20 | 2011-10-16 12:05 | 1005 | 11kV | 26055 | 100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 117963 Earth Fault, No fault shown past fault indicator adjacent to ABS 40652, so tried feeder back no fault found. Feeder was patrolled between garland Valley TAGCB and ABS 40652, request the remainder of the feeder is patrolled ASAP. Tree on mains Near pole 9V-50033. Feeder isolated at 11kV links 5116 to allow treee to be removed in daylight hours refer to OMS 736144, 736146, 736149, 736153 and 736155 | October | 2011 | 2012Q2 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2011-10-15 | N | 260.55 | N | 5 | N | N | 1.1101 | 39.4971 | 19040.2255
| ZN7481:PA17 | 1034 | 1515.1237 | 47.11 | 1.4653 | 47.11 | 19417 | 8416 | 736081 | 2011-10-16 11:23 | 2011-10-16 12:50 | 87 | 11kV | 62740 | 880 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | @Sub 3154 St Ives the "Stanley Richard" fdr panel #17 tripped closed tripped on Earth fault Recloser timing / lockout ZE EFI 11kv Trip Field EFIs subs - 35868, 4914, 4020, 7416, 7417 Defective UGOH above AB 1388 in Waterhouse St Section of 11kV feeder from sub 7418 Hovey Ave to AB 1388 tee to PT1066 Hunter St Ives is isolated only Dop Lman and Jnter required | October | 2011 | 2012Q2 | 2012 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | Unknown | Unknown | 2011-10-16 | N | 71.2955 | N | 8 | N | N | 1.1101 | 39.4971 | 45848.5415
| ZN7481:PA19 | 586 | 1379.6904 | 41.83 | 2.3544 | 41.83 | 19150 | 4923 | 735793 | 2011-10-16 12:37 | 2011-10-16 13:42 | 65.4667 | 11kV | 21355.6667 | 474 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn2568 St Peters Part Pa39 from S660-S22 CB was Open @ S1827. When Closed @ S22 & opened @ SwAS660 fdr was interupted. D&R274651 See 736185 GIS 735801,3 exclude 735794 From To Restored DC Time S1827 S660 3 1322 | October | 2011 | 2012Q2 | 2012 | ZN2568:PA39 | ZN2568:PA38 | ZN02568/000038 | INNER WEST | OH | Veg | 2011-10-16 | N | 45.0541 | N | 8 | N | N | 1.1101 | 39.4971 | 15606.0913
| ZN7481:PA1R | 1717 | 1292.9129 | 40.06 | 0.75301 | 40.06 | 18853 | 2590 | 735791 | 2011-10-16 12:27 | 2011-10-16 14:20 | 113 | 11kV | 565 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117971 Fuse Size: 20Amp Line DOLF No Cause found - not storm conditions, refer to related record 735791 | October | 2011 | 2012Q2 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2011-10-16 | N | 113 | N | 8 | N | N | 1.1101 | 39.4971 | 412.8853
| ZN7481:PA2 | 10 | 14.8405 | #N/A | 1.4841 | 39.4971 | 19637 | 10582 | 735782 | 2011-10-16 11:33 | 2011-10-16 14:22 | 168.6333 | 11kV | 418.2 | 3 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Outage cant be explained, no gis or parallel error. possibile abnormal protection operation at customers supply point. @Sub 3154 St Ives the "Stanley Richard" fdr panel #17 tripped closed tripped on Earth fault Recloser timing / lockout ZE EFI 11kv Trip Field EFIs subs - 35868, 4914, 4020, 7416, 7417 Cant explain outage Defective UGOH above AB 1388 in Waterhouse St Section of 11kV feeder from sub 7418 Hovey Ave to AB 1388 tee to PT1066 Hunter St Ives is isolated only Dop Lman and Jnter required | October | 2011 | 2012Q2 | 2012 | ZN3154:PA3 | ZN3154:PA4 | ZN03154/000004 | KU-RING-GAI | Unknown | Unknown | 2011-10-16 | N | 139.4 | N | 8 | N | N | 1.1101 | 39.4971 | 305.6082
| ZN7481:PA20 | 1532 | 3477.7804 | 41.05 | 2.2701 | 41.05 | 20242 | 17579 | 735819 | 2011-10-16 14:51 | 2011-10-16 16:00 | 69 | 11kV | 69 | 1 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 117974 Suspected cause of ault wa sa dead possum found at the base of the pole Note: Field staff were not provided with the OMS number Fuse: size: 10 AMP replaced on DOLF Refer to related record 735819 | October | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2011-10-16 | N | 69 | N | 8 | N | N | 1.1101 | 39.4971 | 50.4232
| ZN7481:PA21 | 1175 | 1555.2557 | 40.82 | 1.3236 | 40.82 | 19146 | 4902 | 735833 | 2011-10-16 15:40 | 2011-10-16 16:51 | 71 | 11kV | 120061 | 1691 | HV | Vegetation Blow/Fall In | Vegetation | Circuit Breaker | Unplanned | Unselected | N | At Zn 2196 Milperra Panel 25 "Turey River" tripped on A and B phase OC. Signals : 11kv trip Remarks: Tree branch on the 11kv mains, adjacent to AB.1517 Related jobs: #735860, 735856, 735855, 736130, 736139, 736133, 736118, 735832, 735833, 735854 | October | 2011 | 2012Q2 | 2012 | ZN2196:PA25 | ZN2196:PA25 | ZN02196/000025 | CANTERBURY-BANKSTOWN | OH | Veg | 2011-10-16 | N | 71 | N | 8 | N | N | 1.1101 | 39.4971 | 87737.0376
| ZN7481:PA3 | 695 | 2381.2071 | #N/A | 3.4262 | 39.4971 | 19229 | 6274 | 735861 | 2011-10-16 16:42 | 2011-10-16 17:01 | 19.0167 | 11kV | 19.0167 | 1 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | @ S15008 Harbord the "Curl Curl" Fdr panel #17 opened with no protection relays operating Whilst switching the 33kV at Harbord Aop clicked on master A/C which tripped panel #7 | October | 2011 | 2012Q2 | 2012 | ZN15001:PA2 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | Unknown | Not Veg | 2011-10-16 | N | 19.0167 | N | 8 | N | N | 1.1101 | 39.4971 | 13.8968
| ZN7481:PA5 | 9 | 18.7811 | #N/A | 2.0868 | 39.4971 | 19175 | 5263 | 736255 | 2011-10-17 14:43 | 2011-10-17 21:15 | 392 | 11kV | 26311 | 223 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Pnl.12 Wyong - REC 40075 Yarramalong tripped on phase protection #1. Abnormal Switching: AB44997 OPEN - AB 40899 CLOSED Remarks: Branch on 11kV near Auto Links 44773 which are bonded through | October | 2011 | 2012Q2 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2011-10-17 | N | 117.9865 | N | 2 | N | N | 1.1101 | 39.4971 | 19227.3028
| ZN7481:PA6R | 1001 | 2097.572 | 44.01 | 2.0955 | 44.01 | 19388 | 8163 | 736466 | 2011-10-17 20:34 | 2011-10-17 22:54 | 140 | 11kV | 4012 | 35 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | LID 117982 3 Fault operations, Phases A and B, Overcurrent, Pole Mounted RAGCB 11kV Mains twisted near Belmont sub 72378 refer to OMS 737033, 737032, 737029, 737051, 737045, 736466 | October | 2011 | 2012Q2 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2011-10-17 | N | 114.6286 | N | 2 | N | N | 1.1101 | 39.4971 | 2931.8513
| ZN7481:PA8 | 1 | 0 | #N/A | 0 | 39.4971 | 19982 | 14866 | 737481 | 2011-10-18 17:30 | 2011-10-18 18:17 | 47 | 11kV | 14131 | 1777 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S1193 Lindfield Panel 10 tripped reclosed tripped and locked out on Earth Fault, Sealing contactor, EFI, Timing and reclose lockout 11kV UGOH O/S 43 Nelson Rd lindfield failed on energising. Abnormal Switching: CP244 Closed, SW/B S35803 See OMS 737481 737482 736861 | October | 2011 | 2012Q2 | 2012 | ZN1193:PA16 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | Unknown | Unknown | 2011-10-18 | N | 7.9522 | N | 4 | N | N | 1.1101 | 39.4971 | 10326.518
| ZN7481:PA9 | 1205 | 3164.0888 | #N/A | 2.6258 | 39.4971 | 20359 | 19851 | 736875 | 2011-10-18 18:50 | 2011-10-18 21:00 | 130 | 11kV | 19370 | 149 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Ex Zn.12580 Erina Pnl.4 - USL41076 to USL44033 interrupted to reapir USL 43367 PT1115, S.12531 & S.12817 interrupted | October | 2011 | 2012Q2 | 2012 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2011-10-18 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 14155.0247
| ZN931:PA1 | 183 | 914.5228 | #N/A | 4.9974 | 39.4971 | 19181 | 5375 | 736863 | 2011-10-18 19:55 | 2011-10-18 22:00 | 125 | 11kV | 38097 | 1283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.10995 Riverwood P-12 (Eldon St fdr) tripped. Relays: A phase Inst & timed OC Signals: 11kV trip ABNORMAL: Sw A at S.10323 Johnstone Evans with AB 31240 opened. SEL and reclose functions were N/A at time on P-12 & 5 at Riverwood. REMARKS: Tree on HV wires between Sw B at S.10897 Amy Belmore and AB 31240 and Sw A at S.10239 Clarendon Clarke. Mains have removed tree. | October | 2011 | 2012Q2 | 2012 | ZN10995:PA12 | ZN10995:PA12 | ZN10995/000012 | GEORGES RIVER | OH | Veg | 2011-10-18 | N | 29.6937 | N | 4 | N | N | 1.1101 | 39.4971 | 27840.1639
| ZN931:PA10 | 1816 | 1714.7301 | 42.53 | 0.94423 | 42.53 | 19648 | 10775 | 736925 | 2011-10-18 23:34 | 2011-10-19 00:48 | 74 | 11kV | 5920 | 80 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" LID No. 118005/01; Fatigued fuse. Readings as left 85A, 95A, 100A @250V. Fuse size 20 Amp; DOLF Refer to OMS Job 736925; 736926; 736928 - re-entered to correct customers affected. | October | 2011 | 2012Q2 | 2012 | 803:74007 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2011-10-18 | N | 74 | N | 4 | N | N | 1.1101 | 39.4971 | 4326.1614
| ZN931:PA11 | 1358 | 1478.9692 | 41.99 | 1.0891 | 41.99 | 19937 | 14146 | 737030 | 2011-10-19 10:30 | 2011-10-19 11:27 | 57 | 11kV | 5472 | 96 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Dist found in LV// with Sub S166 after field check Zn342 Paddington 11kv Fdr Pa26 tirpped on ACph OC 25R relay SIGNALS Tx2 GE EFI OC Trip Suspect UG fdr fault from Zn342Pa26R to S6899 to S8252 to S778 See 737517,5,6 LV// 742794,814 Exclude 737030,4,40,6,56,75,546 From To Restored DC Time S3223 S6899 5 11:27 S2121 S8252 6 11:47 S778 S778 1 11:55 | October | 2011 | 2012Q2 | 2012 | ZN342:PA21 | ZN342:PA21 | ZN00342/000021 | SYDNEY | UG | Not Veg | 2011-10-19 | N | 57 | N | 6 | N | N | 1.1101 | 39.4971 | 3998.7762
| ZN931:PA12 | 442 | 662.4774 | 41.77 | 1.4988 | 41.77 | 19664 | 11049 | 737023 | 2011-10-19 10:30 | 2011-10-19 11:55 | 85 | 11kV | 189218 | 2694 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington 11kv Fdr Pa26 tirpped on ACph OC 25R relay SIGNALS Tx2 GE EFI OC Trip Suspect UG fdr fault from Zn342Pa26R to S6899 to S8252 to S778 See 737517,5,6 LV// 742794,814 Exclude 737030,4,40,6,56,75,546 From To Restored DC Time S3223 S6899 5 11:27 S2121 S8252 6 11:47 S778 S778 1 11:55 | October | 2011 | 2012Q2 | 2012 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2011-10-19 | N | 70.2368 | N | 6 | N | N | 1.1101 | 39.4971 | 138274.9334
| ZN931:PA13 | 497 | 1598.754 | 40.38 | 3.2168 | 40.38 | 20188 | 16787 | 737221 | 2011-10-19 14:37 | 2011-10-19 15:44 | 67 | 11kV | 19751 | 381 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S1610 Homebush Bay Panel 2 "S7057 Bennelong 2SM' Feeder tripped on Relays - A & C phase O/C, EF Signals _ 11kv trip, #1 TX GE, ZE Field EFI's operated @ S7057, 35731, CP1818 EFI did not not operate @S5696 Remarks: 11kv ug feeder fault from Cp1818 Burroway Rd No1 to S7059 Baywater Hill Tee S1700 Montague Meyer No1. Note: S1700 Montague Meyer No.1 found with HV fuse switch in the open position with HV TX tails cut away at TX & LV TX tails & switchboard removed. Related jobs: #737407, 737403, 737221 | October | 2011 | 2012Q2 | 2012 | ZN1610:PA2 | ZN1610:PA22 | ZN01610/000022 | PARRAMATTA | UG | Not Veg | 2011-10-19 | N | 51.8399 | N | 6 | N | N | 1.1101 | 39.4971 | 14433.4482
| ZN931:PA14 | 299 | 271.4864 | #N/A | 0.90798 | 39.4971 | 19675 | 11167 | 737206 | 2011-10-19 14:24 | 2011-10-19 18:50 | 266 | 11kV | 35517 | 329 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | OMS Report No. 737231. Please investigate possible misgrade between 42025 and 35192. 35192 locked out on A & B earth Fault(Scott Bailey) and 42025 tripped and reclosed on A&C phase overcurrent. | October | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-10-19 | N | 107.9544 | N | 6 | N | N | 1.1101 | 39.4971 | 25954.776
| ZN931:PA18 | 594 | 1820.2609 | 42.7 | 3.0644 | 42.7 | 19680 | 11333 | 737344 | 2011-10-19 19:49 | 2011-10-19 21:50 | 121.4333 | 11kV | 5707.3667 | 47 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" The footpath 31.5 amp fuse failed due to fatigue at PT.11004 FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | October | 2011 | 2012Q2 | 2012 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2011-10-19 | N | 121.4333 | N | 6 | N | N | 1.1101 | 39.4971 | 4170.7752
| ZN931:PA2 | 2705 | 1506.1947 | 39.15 | 0.55682 | 39.15 | 19991 | 14897 | 737269 | 2011-10-19 20:52 | 2011-10-20 02:55 | 363 | 11kV | 118701 | 327 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | As per notepad comment on OMS 737269 - and customer calls in comments - "20/10/11 02:55 T45340: W Morgan replaced ABS 27108. 19/10/11 20:52 CASS: Job referred by T45123 in CASS 19/10/11 15:44 CASS: Job assigned to Emso 135_ - event has been replicated based on these contacts as there is no lid report entered, | October | 2011 | 2012Q2 | 2012 | 234:2000 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Not Veg | 2011-10-19 | N | 363 | N | 6 | N | N | 1.1101 | 39.4971 | 86743.1897
| ZN931:PA21 | 219 | 835.0237 | #N/A | 3.8129 | 39.4971 | 18949 | 3474 | 737807 | 2011-10-20 23:24 | 2011-10-21 02:48 | 204 | 11kV | 414564 | 2039 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At ZN.10999 Kogarah P-11 "AB 30242 etc' tripped. Relays: C phase Inst OC. Signals: 11kV Trip REMARKS: UGOH between AB 30501, AB 30212 and AB 31097 (clsest AB 30501) has failed | October | 2011 | 2012Q2 | 2012 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | Unknown | Unknown | 2011-10-20 | N | 203.3173 | N | 1 | N | N | 1.1101 | 39.4971 | 302951.1436
| ZN931:PA22 | 550 | 897.6939 | #N/A | 1.6322 | 39.4971 | 20418 | 20239 | 738016 | 2011-10-21 13:01 | 2011-10-21 14:00 | 59 | 11kV | 45076 | 764 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington pa23 tripped RELAYS FNG1 C*N* Pa23 efi Pa26 efi Earth Fault Check Relay Tx4 & Tx2 SIGNALS Tx2GE 11kv trip frontline UG fdr fault from Zn342:Pa23 - S7839 See 738016 LV// 738017,9 From To Restored DC TIme S292SwA S7839SwA 3 14:00 | October | 2011 | 2012Q2 | 2012 | ZN342:PA23 | ZN342:PA23 | ZN00342/000023 | WOOLLAHRA | UG | Not Veg | 2011-10-21 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 32940.2113
| ZN931:PA23 | 480 | 380.4898 | #N/A | 0.79269 | 39.4971 | 20392 | 20049 | 737945 | 2011-10-21 11:04 | 2011-10-21 14:10 | 186 | 11kV | 7440 | 40 | HV | 3rd Party Vehicle | 3rd Party Impact | Pillar | Unplanned | Unselected | N | LID No. 118054/01; Bobcat hit LV Pillar IQ 70215, LV isolated and repaired. Distribution LV Fuse; Fuse Size - 400 Amp. | October | 2011 | 2012Q2 | 2012 | 501:48115 | 528:83014 | ZN00528/083014 | MAITLAND | UG | Not Veg | 2011-10-21 | N | 186 | N | 5 | N | N | 1.1101 | 39.4971 | 5436.9326
| ZN931:PA24 | 308 | 684.7617 | #N/A | 2.2233 | 39.4971 | 20432 | 20366 | 738112 | 2011-10-21 16:12 | 2011-10-21 16:58 | 46 | 11kV | 10588.4 | 232 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | @S753 fdr 'S2983' found open Ex Pa22 'S5471' fdr from Zn711 No relay operations @ S753 No apparent Cause See 738112 LV// 738119 LV// LV// 738126 GIS 738127 From To Restored DC Time S753 S2983 1 16:58 | October | 2011 | 2012Q2 | 2012 | ZN711:PA22 | ZN384:PA65 | ZN00384/000065 | SYDNEY | UG | Not Veg | 2011-10-21 | N | 45.6397 | N | 5 | N | N | 1.1101 | 39.4971 | 7737.6904
| ZN931:PA25 | 1156 | 1410.7925 | 45.75 | 1.2204 | 45.75 | 19403 | 8348 | 738182 | 2011-10-21 19:11 | 2011-10-21 20:00 | 49 | 11kV | 98 | 2 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa5 fdr tripped on RELAYS - Trip Led efi SIGNALS - 11kv trip #5Tx GE ZE 11kv UG cable failure from PZn1788:Pa5 to S5931 to S7639 to No.4 HVC@S7424 Malabar Sewage Treatment Plant From To Restored DC Time S5931 S5931 1 20:00 | October | 2011 | 2012Q2 | 2012 |  |  |  | RANDWICK | UG | Not Veg | 2011-10-21 | N | 49 | N | 5 | N | N | 1.1101 | 39.4971 | 71.6155
| ZN931:PA26 | 197 | 390.3432 | 53.21 | 1.9814 | 53.21 | 19828 | 13008 | 738199 | 2011-10-21 23:12 | 2011-10-22 01:05 | 113 | 11kV | 7684 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118057/01; DOLF replaced ok. As left 245V, 55A, 246V, 25A & 248V, 29A. Fuse Size 31 AMP; No cause found. | October | 2011 | 2012Q2 | 2012 | 232:11459 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2011-10-21 | N | 113 | N | 5 | N | N | 1.1101 | 39.4971 | 5615.2406
| ZN931:PA3 | 536 | 1283.4769 | #N/A | 2.3945 | 39.4971 | 20044 | 15550 | 738331 | 2011-10-22 16:13 | 2011-10-22 17:40 | 87 | 11kV | 59258 | 974 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Zn.12660 Woy Woy pnl.6 tripped on SEF and EFI EFi down @ S.18564 Remarks: Centre Ph Lightning Arrestor exploaded @ PT.11250 and blew 2 HV fuses | October | 2011 | 2012Q2 | 2012 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2011-10-22 | N | 60.8398 | N | 2 | N | N | 1.1101 | 39.4971 | 43303.9986
| ZN931:PA30 | 144 | 93.663 | #N/A | 0.65044 | 39.4971 | 20255 | 17885 | 738470 | 2011-10-23 17:12 | 2011-10-23 18:23 | 71 | 11kV | 15699 | 229 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.257 South Parade, Sw/C 'Gibbons Verona etc' feeder tripped on B & C phase O/C, EFI At S.1068 Lidcombe, Panel 17 EFI operated. Alarms; TX3 GE, ZE Field EFI's operated at; S.3367, S.6136, S.35368 ABNORMAL: Sw/B closed at S.35368 Harrow Mary No.1 Remarks: suspect UG cable fault from S.257 South Pde (Sw/C) to S.8863 Crescent Alice No.3 (Sw/A) to S.3946 Gibbons Verona (Sw/A). Dop reports burning smell at S.257 Related jobs: #739104, 739102, 738470 | October | 2011 | 2012Q2 | 2012 | ZN1068:PA18 | ZN36000:PA24 | ZN36000/000024 | CUMBERLAND | UG | Not Veg | 2011-10-23 | N | 68.5546 | N | 1 | N | N | 1.1101 | 39.4971 | 11472.3662
| ZN931:PA31 | 304 | 1131.4525 | #N/A | 3.7219 | 39.4971 | 20020 | 15097 | 738211 | 2011-10-22 07:28 | 2011-10-24 08:04 | 2916.15 | 11kV | 68206 | 377 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Zn.12630 Peats Ridge pnl.1 tripped / reclosed & locked out on: Earth fault, A Ph IOC & Timed O/C, EFI Abnormal Switching: Pnl.5 Peats Ridge CB OPEN - AB43334 CLOSED Remarks: 11kV Lightning arrestor failed @ PT.18615. Note: 33kV "720" feeder tripped @ same time. See unusal occurance report | October | 2011 | 2012Q2 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2011-10-22 | N | 180.9178 | N | 2 | N | N | 1.1101 | 39.4971 | 49842.9331
| ZN931:PA32 | 60 | 265.3913 | #N/A | 4.4232 | 39.4971 | 19998 | 14915 | 738513 | 2011-10-24 07:46 | 2011-10-24 08:26 | 40 | 11kV | 31800 | 795 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At Zn1114 North Ryde Panel 15 tripped on Relays: Cphase timed overload, EFI, Sealing Contator. Signals: 11kV trip, No3 gorup earth, capacitor protection trip. Cause: Large Kookaburra found on ground on cnr of Ford and Ada St Pole No GL33576 | October | 2011 | 2012Q2 | 2012 | ZN1114:PA15 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2011-10-24 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 23238.5021
| ZN931:PA33 | 172 | 97.2267 | #N/A | 0.56527 | 39.4971 | 20064 | 15766 | 738679 | 2011-10-24 13:50 | 2011-10-24 14:15 | 25 | 11kV | 25 | 1 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118084/01; Fuse Size 10 Amp; Substation DOLF; Repalce blown surge diverters. | October | 2011 | 2012Q2 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2011-10-24 | N | 25 | N | 6 | N | N | 1.1101 | 39.4971 | 18.2693
| ZN931:PA4 | 89 | 241.7458 | 42.64 | 2.7162 | 42.64 | 19163 | 5103 | 738853 | 2011-10-24 15:21 | 2011-10-24 15:47 | 26.4333 | 11kV | 5154.5 | 195 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7900 Campbell st 11kv fdr Pa15 tripped on Earth Fault, EFI, Fault Check Signals ZE Pa15 trip From To Restored DC Time S3722 S6833 3 15:47 Suspect UG cable fault Zn7900 Campbell st Pa15 to S6833 to S7749 | October | 2011 | 2012Q2 | 2012 | ZN7900:PA15 | ZN7900:PA15 | ZN07900/000015 | SYDNEY | UG | Not Veg | 2011-10-24 | N | 26.4333 | N | 6 | N | N | 1.1101 | 39.4971 | 3766.7566
| ZN931:PA7 | 136 | 173.8613 | #N/A | 1.2784 | 39.4971 | 20140 | 16246 | 738864 | 2011-10-24 15:45 | 2011-10-24 15:49 | 4 | 11kV | 3084 | 771 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Primary Equip | Unplanned | No Weather Impact | N | LID No. 118086/01; Regulator faulty & unable to operate. Feeder opened at Millfield RAGCB & regulator was by-passed. 24/10/11 15:43 T45365: Urgent switching - should only be off 10 minutes Refer to related record 738664 | October | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | Exclude | Not Veg | 2011-10-24 | N | 4 | N | 6 | N | N | 1.1101 | 39.4971 | 2253.6962
| ZN931:PA8 | 184 | 218.1589 | #N/A | 1.1856 | 39.4971 | 19274 | 6979 | 738990 | 2011-10-24 23:41 | 2011-10-25 00:53 | 72 | 11kV | 77080 | 1775 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118088 Timed earth fault. C-phase arrestor failed on Pole Ju-67120 (UG/OH supplying Whitecrest sub 13050). OMS Job Nos. 738990 & 738992. refer replication switching, refer to Jobs 742035 and 742041 | October | 2011 | 2012Q2 | 2012 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2011-10-24 | N | 43.4254 | N | 6 | N | N | 1.1101 | 39.4971 | 56327.7905
| ZN931:PA9 | 1540 | 1115.7408 | 40.62 | 0.72451 | 40.62 | 19860 | 13390 | 738986 | 2011-10-24 23:27 | 2011-10-25 06:25 | 418 | 11kV | 33167 | 84 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 118089 2 Fault operations, Earth Fault Trees brought down 11kV mains near Halliwell sub 52871. Excluded - OMS Job Nos. 738986-8, 738991& 738993. Restoration switching required - refer to replicated jobs 740397, 740398 and 740399 | October | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-10-24 | N | 394.8452 | N | 6 | N | N | 1.1101 | 39.4971 | 24237.4653
| ZN15006:PA1 | 656 | 469.1456 | 40.85 | 0.71516 | 40.85 | 18765 | 1789 | 739017 | 2011-10-25 07:19 | 2011-10-25 08:10 | 51 | 11kV | 51 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118092/01; Fuse Size: 16 Amp; DOLF; Volts: Aph 244V - Bph 241V - Cph 242V | October | 2011 | 2012Q2 | 2012 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Veg | 2011-10-25 | N | 51 | N | 18 | N | N | 1.1101 | 39.4971 | 37.2693
| ZN15006:PA12 | 3763 | 3113.5354 | 37.76 | 0.82741 | 37.76 | 19160 | 5031 | 739239 | 2011-10-25 11:54 | 2011-10-25 13:53 | 119 | 11kV | 27006 | 1611 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.14891 Wyong - Pnl.19 tripped on: E/F, O/C, EFI, fault Check Field EFIs: NIL initially found. See separate interruption Pnl.5 due to faulty EFI indication #739639 Remarks: Suspet UG fault between S.12636 & AB40001 tee PT14979. PT.14979 is non // customer at this stage does not require MG | October | 2011 | 2012Q2 | 2012 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | UG | Not Veg | 2011-10-25 | N | 16.7635 | N | 18 | N | N | 1.1101 | 39.4971 | 19735.1883
| ZN15006:PA13 | 1397 | 1414.6178 | 35.74 | 1.0126 | 35.74 | 20101 | 15999 | 739005 | 2011-10-25 05:55 | 2011-10-25 14:30 | 515 | 11kV | 49664 | 382 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Zn.12630 Peats Ridge Pnl.1 tripped / reclosed / tripped on earth leakage, EFI Remarks: Surge arrestor blown @ S.13556 Mooney Da Pumping Station. Isolated at LK40297 Abnormal Switching: AB43334 CLOSED. Pnl.5 @ Peats Ridge OPEN | October | 2011 | 2012Q2 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2011-10-25 | N | 130.0105 | N | 18 | N | N | 1.1101 | 39.4971 | 36292.9864
| ZN15006:PA14 | 119 | 1075.0196 | #N/A | 9.0338 | 39.4971 | 19179 | 5358 | 739647 | 2011-10-25 14:25 | 2011-10-25 14:30 | 5 | 11kV | 6605 | 1321 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At Sub 15012 Killarney 11kV Fdr Pnl 8 tripped on C phase timed and IOC 11kV came down on energising Protection Non-auto at time of interruption for switching See D/R 277389 | October | 2011 | 2012Q2 | 2012 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2011-10-25 | N | 5 | N | 18 | N | N | 1.1101 | 39.4971 | 4826.7392
| ZN15006:PA15 | 2070 | 1257.8128 | 32.71 | 0.60764 | 32.71 | 19813 | 12894 | 740502 | 2011-10-25 14:33 | 2011-10-25 14:44 | 11 | 11kV | 3619 | 329 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 1180098 1 Fault operations Overcurrent storm in area | October | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2011-10-25 | N | 11 | N | 18 | N | N | 1.1101 | 39.4971 | 2644.6585
| ZN15006:PA16 | 3314 | 2290.4146 | 36.69 | 0.69113 | 36.69 | 19408 | 8374 | 739406 | 2011-10-25 15:45 | 2011-10-25 16:08 | 23 | 11kV | 1679 | 73 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118102 1 fault operation Phases B and C Overcurrent Device operated during storm reclose off for si-17320 feeder closed ok after 20 mins. | October | 2011 | 2012Q2 | 2012 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2011-10-25 | N | 23 | N | 18 | N | N | 1.1101 | 39.4971 | 1226.9637
| ZN15006:PA2 | 2297 | 1480.0549 | 39.16 | 0.64434 | 39.16 | 19076 | 4490 | 739207 | 2011-10-25 11:55 | 2011-10-25 16:30 | 275 | 11kV | 275 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14761 pacific Old Tuggerah 0.1 - HDO fuse footpath side (10A) Remarks: Fuse Fatigue | October | 2011 | 2012Q2 | 2012 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2011-10-25 | N | 275 | N | 18 | N | N | 1.1101 | 39.4971 | 200.9619
| ZN15006:PA4 | 1258 | 927.3119 | 36.95 | 0.73713 | 36.95 | 19228 | 6252 | 739449 | 2011-10-25 16:33 | 2011-10-25 18:29 | 116 | 11kV | 116 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118113 storm in area at time of device operation Refer related OMS 739449 Fuse size: 10 Amp | October | 2011 | 2012Q2 | 2012 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2011-10-25 | N | 116 | N | 18 | N | N | 1.1101 | 39.4971 | 84.7694
| ZN15006:PA6 | 606 | 904.6832 | 41.74 | 1.4929 | 41.74 | 18951 | 3482 | 739487 | 2011-10-25 17:30 | 2011-10-25 18:40 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118117 Dolf operated during storm in area Refer related record 739487 Fuse size: 10 Amp | October | 2011 | 2012Q2 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2011-10-25 | N | 70 | N | 18 | N | N | 1.1101 | 39.4971 | 51.1539
| ZN15006:PA8 | 1927 | 1320.0982 | 33.58 | 0.68505 | 33.58 | 19604 | 10153 | 739507 | 2011-10-25 18:29 | 2011-10-25 19:11 | 42.25 | 11kV | 56904.25 | 1459 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID No. 118111/01; Overcurrent; Reclose off for scheduled switching; Tree in mains outside 10 Jarett St. Urgent trimming required. Refer to OMS 739509. | October | 2011 | 2012Q2 | 2012 | 211:33602 | 257:81987 | ZN00257/081987 | NEWCASTLE | OH | Veg | 2011-10-25 | N | 39.0022 | N | 18 | N | N | 1.1101 | 39.4971 | 41583.9475
| ZN15006:PA9 | 2596 | 1781.5103 | 36.76 | 0.68625 | 36.76 | 19282 | 7234 | 739469 | 2011-10-25 16:55 | 2011-10-25 19:15 | 140 | 11kV | 560 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118118 Related record 739469 Line DOLF operated during thunderstorm Fuse size: 20 Amp | October | 2011 | 2012Q2 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2011-10-25 | N | 140 | N | 18 | N | N | 1.1101 | 39.4971 | 409.2315
| 807:74179 | 131 | 130.7684 | 51.52 | 0.99823 | 51.52 | 20270 | 18052 | 739520 | 2011-10-25 19:02 | 2011-10-25 20:35 | 93 | 11kV | 3698 | 478 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | cAt S35370 Galston Panel 2 tripped reclosed tripped and locked out on A and C phase Timed O/C Auto Link367 Operated . Cause: Tree Branch on 11kV Mains Adjacent Auto Link 367. See OMS 740230 740228 Abnormal Switching: AB2161 Open AB2912 Closed | October | 2011 | 2012Q2 | 2012 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2011-10-25 | N | 7.7364 | N | 18 | N | N | 1.1101 | 39.4971 | 2702.3893
| 807:74180 | 109 | 115.3913 | 39.36 | 1.0586 | 39.36 | 19428 | 8499 | 739455 | 2011-10-25 18:55 | 2011-10-25 21:10 | 135 | 11kV | 810 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118116 Dolf operated during Thunderstorm refer 739455 Fuse size: 16 Amp | October | 2011 | 2012Q2 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2011-10-25 | N | 135 | N | 18 | N | N | 1.1101 | 39.4971 | 591.9241
| 807:74181 | 738 | 654.223 | 32.46 | 0.88648 | 32.46 | 19362 | 7820 | 739529 | 2011-10-25 19:23 | 2011-10-25 21:25 | 122 | 11kV | 122 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118121 storm in area at time of device operation Refer to related record 739529 Fuse size: 10 Amp | October | 2011 | 2012Q2 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2011-10-25 | N | 122 | N | 18 | N | N | 1.1101 | 39.4971 | 89.154
| 807:74183 | 87 | 197.1052 | 47.22 | 2.2656 | 47.22 | 20164 | 16453 | 739439 | 2011-10-25 16:25 | 2011-10-25 22:46 | 380.65 | 11kV | 44586.5833 | 509 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 118110 OMS Report No 739452. tree into mains Dolaheney st. RH LVF Sub 71562 opened as LV Alive at fault. Refer to related records 742129 and 742132 | October | 2011 | 2012Q2 | 2012 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | OH | Veg | 2011-10-25 | N | 87.5964 | N | 18 | N | N | 1.1101 | 39.4971 | 32582.56
| 807:74184 | 495 | 468.3312 | 39.7 | 0.94612 | 39.7 | 18735 | 1413 | 739506 | 2011-10-25 18:39 | 2011-10-25 23:00 | 261 | 11kV | 522 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118126 storm in area at time of device operation Refer to OMS 739506 Fuse size: 10 Amp | October | 2011 | 2012Q2 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2011-10-25 | N | 261 | N | 18 | N | N | 1.1101 | 39.4971 | 381.4622
| ZN3155:PA11 | 607 | 1567.0222 | 42.31 | 2.5816 | 42.31 | 20191 | 16834 | 739533 | 2011-10-25 19:29 | 2011-10-26 02:00 | 391 | 11kV | 28934 | 74 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 118125 3 Fault operations, Earth Fault Distribution Transformer requires replacement Refer to OMS 739535 | October | 2011 | 2012Q2 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2011-10-25 | N | 391 | N | 18 | N | N | 1.1101 | 39.4971 | 21144.1138
| ZN3155:PA12 | 1256 | 887.6424 | 34.4 | 0.70672 | 34.4 | 19994 | 14906 | 739567 | 2011-10-26 03:06 | 2011-10-26 07:45 | 279 | 11kV | 102922 | 1044 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | At S847 Hornsby Panel 44 tripped reclosed tripped and ;locked out on Relays: C phase IOC and Timed O/C, EFI HV Cross arm broken at AB150 - HV to into LV See OMS 740106 740110 740109 740144 740146 | October | 2011 | 2012Q2 | 2012 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Not Veg | 2011-10-26 | N | 98.5843 | N | 3 | N | N | 1.1101 | 39.4971 | 75212.3619
| ZN3155:PA15 | 1443 | 1641.9985 | 44.13 | 1.1379 | 44.13 | 18658 | 749 | 739584 | 2011-10-26 07:21 | 2011-10-26 10:50 | 209 | 11kV | 836 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 118129 Line dolf operated during storm Refer 739485 Fuse size: 40 Amp | October | 2011 | 2012Q2 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2011-10-26 | N | 209 | N | 3 | N | N | 1.1101 | 39.4971 | 610.9241
| ZN3155:PA16 | 754 | 1232.9627 | 39.39 | 1.6352 | 39.39 | 19165 | 5156 | 739493 | 2011-10-25 17:43 | 2011-10-26 15:00 | 1277 | 11kV | 6385 | 5 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 118124 No protection operations. Operator found volts at txf 250, 250, 120. txf to be changed tomorrow. OMS # 739493 | October | 2011 | 2012Q2 | 2012 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2011-10-25 | N | 1277 | N | 18 | N | N | 1.1101 | 39.4971 | 4665.9697
| ZN3155:PA17 | 1130 | 1374.326 | 39.7 | 1.2162 | 39.7 | 19085 | 4534 | 740007 | 2011-10-26 18:26 | 2011-10-26 20:30 | 124 | 11kV | 124 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Nil Remarks: Bond burnt off at AB24 Leightonfield 2F7. Section of Pn11 "Biloela Gurr #2" fdr Related jobs: #740007, 740224 | October | 2011 | 2012Q2 | 2012 | ZN1290:PA11 | ZN1290:PA11 | ZN01290/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2011-10-26 | N | 124 | N | 3 | N | N | 1.1101 | 39.4971 | 90.6155
| ZN3155:PA18 | 478 | 934.0033 | #N/A | 1.954 | 39.4971 | 18783 | 1949 | 740111 | 2011-10-27 09:27 | 2011-10-27 11:20 | 113 | 11kV | 3503 | 31 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID No. 118139/01; Fuse size 16 AMP; DOLF; 11kv fuse carrier failure; OMS 740111. | October | 2011 | 2012Q2 | 2012 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2011-10-27 | N | 113 | N | 1 | N | N | 1.1101 | 39.4971 | 2559.8891
| ZN3155:PA19 | 1018 | 1247.6406 | 32.86 | 1.2256 | 32.86 | 19007 | 4101 | 740599 | 2011-10-28 09:23 | 2011-10-28 10:05 | 42 | 11kV | 42 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118141/01; Fuse Size: 31 Amp; DOLF; Refer OMS 740599; Reading 241 volts 210 amps per phase. | October | 2011 | 2012Q2 | 2012 |  |  |  |  | OH | Veg | 2011-10-28 | N | 42 | N | 2 | N | N | 1.1101 | 39.4971 | 30.6924
| ZN3155:PA20 | 1178 | 1095.6977 | 42.9 | 0.93013 | 42.9 | 18651 | 730 | 740727 | 2011-10-28 11:28 | 2011-10-28 20:25 | 537 | 11kV | 10203 | 19 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 118143 No protection operation feeder opened by SO. Pole erected under A/P See report LID 118143 and OMS 741378 | October | 2011 | 2012Q2 | 2012 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2011-10-28 | N | 537 | N | 2 | N | N | 1.1101 | 39.4971 | 7456.0515
| ZN3155:PA21 | 500 | 823.923 | 34.1 | 1.6478 | 34.1 | 19917 | 13957 | 740944 | 2011-10-29 10:05 | 2011-10-29 12:10 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID NO. 118158/01; Fuse size 10 Amp; DOLF; OMS Report No. 740944 - storm on 25/10/11 - previous storm. | October | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-10-29 | N | 125 | N | 2 | N | N | 1.1101 | 39.4971 | 91.3463
| ZN3155:PA22 | 655 | 1221.3183 | 32.09 | 1.8646 | 32.09 | 18847 | 2539 | 741022 | 2011-10-29 17:43 | 2011-10-29 22:10 | 267 | 11kV | 11474.85 | 43 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT15216 West head Rd - HDO assembly failed - requires replacement restored via LV // | October | 2011 | 2012Q2 | 2012 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2011-10-29 | N | 266.857 | N | 2 | N | N | 1.1101 | 39.4971 | 8385.4819
| ZN3155:PA23 | 2154 | 2379.6116 | 36.8 | 1.1047 | 36.8 | 19466 | 8834 | 741060 | 2011-10-30 02:59 | 2011-10-30 04:45 | 106 | 11kV | 176059 | 1954 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12610 Long Jetty Pnl.13 tripped on: A Phase timed Overcurrent, Earth Fault, EFI, Fault Check Remarks: Suspected underground cable fault from S.18424 SwA to 11kV UGOH. | October | 2011 | 2012Q2 | 2012 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | UG | Not Veg | 2011-10-30 | N | 90.1018 | N | 14 | N | N | 1.1101 | 39.4971 | 128658.7243
| ZN3155:PA24 | 643 | 1315.0753 | 40.74 | 2.0452 | 40.74 | 20294 | 18782 | 741114 | 2011-10-30 10:26 | 2011-10-30 12:12 | 106 | 11kV | 106 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118175/01; Fuse Size: 10 Amp; DOLF. | October | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-10-30 | N | 106 | N | 14 | N | N | 1.1101 | 39.4971 | 77.4617
| ZN3155:PA27 | 194 | 1815.3653 | #N/A | 9.3576 | 39.4971 | 20061 | 15688 | 741139 | 2011-10-30 12:10 | 2011-10-30 14:30 | 140 | 11kV | 780 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LI D 118180 and 118181, Fuse size: 10 Amp refer to replicated OMS records 741643 and 741645, Line dolf and sub dolf operated at same time, also refer to 741180 with customer call in details | October | 2011 | 2012Q2 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-10-30 | N | 130 | N | 14 | N | N | 1.1101 | 39.4971 | 570.001
| ZN3155:PA28 | 2 | 472.3315 | #N/A | 236.1657 | 39.4971 | 19448 | 8668 | 741138 | 2011-10-30 12:05 | 2011-10-30 14:55 | 170 | 11kV | 850 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118182/01; Fuse Size: 10 Amp; DOLF; Refer to OMS 741138; | October | 2011 | 2012Q2 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-10-30 | N | 170 | N | 14 | N | N | 1.1101 | 39.4971 | 621.1549
| ZN3155:PA29 | 1788 | 1453.2514 | 36.44 | 0.81278 | 36.44 | 20197 | 16905 | 741204 | 2011-10-30 14:17 | 2011-10-30 15:05 | 48 | 11kV | 48 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Lid NO. 118184/01; Fuse Size 10 Amp; DOLF; Volts 243; load 6 amps. | October | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2011-10-30 | N | 48 | N | 14 | N | N | 1.1101 | 39.4971 | 35.077
| ZN3155:PA30 | 294 | 691.2269 | #N/A | 2.3511 | 39.4971 | 19138 | 4875 | 741219 | 2011-10-30 15:07 | 2011-10-30 15:55 | 48 | 11kV | 23952 | 499 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118188/01; 2 fault operations; overcurrent; OMS 741220 - couldn't find at time of re-entry; Section patrolled by DOPs nothing found, fdr restored. | October | 2011 | 2012Q2 | 2012 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2011-10-30 | N | 48 | N | 14 | N | N | 1.1101 | 39.4971 | 17503.4151
| ZN3155:PA31 | 1 | 77.1394 | #N/A | 77.1394 | 39.4971 | 20352 | 19595 | 741127 | 2011-10-30 11:08 | 2011-10-30 17:10 | 362 | 11kV | 362 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118192 Fuse size: 10 Amp 249 Volts, 6 amps, refer to related record 741127 | October | 2011 | 2012Q2 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2011-10-30 | N | 362 | N | 14 | N | N | 1.1101 | 39.4971 | 264.5389
| ZN3155:PA32 | 788 | 790.9626 | 33.27 | 1.0038 | 33.27 | 18872 | 2793 | 741223 | 2011-10-30 15:31 | 2011-10-30 17:15 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118191/01; Fuse size 10 Amp; DOLF; OMS 741223. | October | 2011 | 2012Q2 | 2012 | 526:34635 | 526:34635 | ZN00526/034635 | CESSNOCK | OH | Veg | 2011-10-30 | N | 104 | N | 14 | N | N | 1.1101 | 39.4971 | 76.0001
| ZN3155:PA33 | 1405 | 1153.0273 | 33.61 | 0.82066 | 33.61 | 18645 | 715 | 741690 | 2011-10-30 15:06 | 2011-10-30 17:20 | 134 | 11kV | 1206 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118193/01; Fuse Size: 10 Amp; DOLF; Refer to OMS 741216. | October | 2011 | 2012Q2 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2011-10-30 | N | 134 | N | 14 | N | N | 1.1101 | 39.4971 | 881.3092
| ZN3155:PA34 | 783 | 761.2857 | 33.4 | 0.97227 | 33.4 | 18745 | 1510 | 741181 | 2011-10-30 13:03 | 2011-10-30 18:25 | 322 | 11kV | 2576 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118196/01; Fuse Size: 10 Amp; DOLF; | October | 2011 | 2012Q2 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2011-10-30 | N | 322 | N | 14 | N | N | 1.1101 | 39.4971 | 1882.4648
| ZN3155:PA35 | 1618 | 964.0111 | 33.81 | 0.5958 | 33.81 | 19161 | 5068 | 741116 | 2011-10-30 10:35 | 2011-10-30 18:56 | 501 | 11kV | 30326 | 138 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 118164 and 118166 2 Fault operations, BPh 11kV OH main down a pole 7L-50090 and 7L-40037, Section isolated to carry out repairs Restoration switching required, refer to OMS 741704/06/09/10/11/12/13 | October | 2011 | 2012Q2 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2011-10-30 | N | 219.7536 | N | 14 | N | N | 1.1101 | 39.4971 | 22161.3463
| ZN3155:PA36 | 326 | 689.3472 | #N/A | 2.1146 | 39.4971 | 20383 | 19999 | 741267 | 2011-10-30 19:48 | 2011-10-30 21:15 | 87 | 11kV | 435 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118198 Fuse Size: 10 Amp Volts 248, 250, 252 Load 15,16,2 | October | 2011 | 2012Q2 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2011-10-30 | N | 87 | N | 14 | N | N | 1.1101 | 39.4971 | 317.8852
| ZN3155:PA44 | 2161 | 1959.3631 | 40.58 | 0.90669 | 40.58 | 19393 | 8206 | 741226 | 2011-10-30 15:58 | 2011-10-30 22:20 | 382 | 11kV | 382 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 118194 Fuse size 10 Amp Sub isolated to replace faulty Tx, refer to related record 741226 | October | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-10-30 | N | 382 | N | 14 | N | N | 1.1101 | 39.4971 | 279.1543
| ZN3922:PA1 | 304 | 181.5368 | 29.42 | 0.59716 | 29.42 | 18578 | 83 | 741248 | 2011-10-30 19:30 | 2011-10-31 00:40 | 310 | 11kV | 1155 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 118199 Replaced faulty L/A at UGOH pole ER-53066. OMS 741248 refer to replicated records 742148 and 742146 | October | 2011 | 2012Q2 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2011-10-30 | N | 288.75 | N | 14 | N | N | 1.1101 | 39.4971 | 844.0399
| ZN3922:PA10 | 1188 | 933.4859 | 33.21 | 0.78576 | 33.21 | 20219 | 17170 | 741293 | 2011-10-31 06:48 | 2011-10-31 08:10 | 82 | 11kV | 164 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Lid No. 118201/01; Fuse Size: 10 Amp; DOLF; OMS 741293; Volts 244, load A 15A, B 5A, C 5A. | October | 2011 | 2012Q2 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2011-10-31 | N | 82 | N | 2 | N | N | 1.1101 | 39.4971 | 119.8464
| ZN3922:PA11 | 1959 | 1654.0402 | 40.87 | 0.84433 | 40.87 | 20230 | 17391 | 741353 | 2011-10-31 08:41 | 2011-10-31 13:28 | 287 | 11kV | 287 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID No. 118209/01; Fuse Size: 10 Amp; DOLF; Faulty transformer following storm yesterday. | October | 2011 | 2012Q2 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2011-10-31 | N | 287 | N | 2 | N | N | 1.1101 | 39.4971 | 209.7311
| ZN3922:PA12 | 1371 | 1249.1236 | 33.12 | 0.9111 | 33.12 | 20051 | 15611 | 741847 | 2011-11-01 07:11 | 2011-11-01 07:19 | 8 | 11kV | 24985 | 3372 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | Unselected | N | Zn.15005 Belrose Pnl.8 tripped on SEL, Zone Earth, clc Defect. Remarks: SEL right side panel 8 was out of scan & left auto while switching. See interruption in conjunctions Pnl.12 #742425 | November | 2011 | 2012Q2 | 2012 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2011-11-01 | N | 7.4095 | N | 5 | N | N | 1.1101 | 39.4971 | 18258.3011
| ZN3922:PA13 | 1406 | 1116.0296 | 39.66 | 0.79376 | 39.66 | 19436 | 8540 | 742378 | 2011-11-01 12:00 | 2011-11-01 13:25 | 85 | 11kV | 170 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID No. 118223/1; Fuse Size: 10 Amp; DOLF; Previous storm. | November | 2011 | 2012Q2 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2011-11-01 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 124.231
| ZN3922:PA14 | 1813 | 1263.4157 | 36.84 | 0.69686 | 36.84 | 18703 | 1183 | 742140 | 2011-11-01 15:41 | 2011-11-01 17:30 | 109 | 11kV | 327 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Lid No. 118229/01; Fuse Size: 10 Amp; DOLF; Volts = 248V; Load not checked sub not retrofitted. Refer OMS 742140 | November | 2011 | 2012Q2 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2011-11-01 | N | 109 | N | 5 | N | N | 1.1101 | 39.4971 | 238.962
| ZN3922:PA17 | 1259 | 1018.317 | 40.11 | 0.80883 | 40.11 | 19217 | 6071 | 742189 | 2011-11-01 18:04 | 2011-11-01 18:50 | 46 | 11kV | 92 | 2 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118230/01; Fuse Size: 16 Amp; DOLF; Found DOLF down, fuse fatigued, replaced ok. Refer OMS 742189. | November | 2011 | 2012Q2 | 2012 | 256:80632 | 256:80632 | ZN00256/080632 | LAKE MACQUARIE | OH | Not Veg | 2011-11-01 | N | 46 | N | 5 | N | N | 1.1101 | 39.4971 | 67.2309
| ZN3922:PA18 | 882 | 1872.4246 | 40.4 | 2.1229 | 40.4 | 19372 | 7974 | 742218 | 2011-11-01 23:05 | 2011-11-02 00:53 | 108 | 11kV | 294648 | 2736 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.10999 Kogarah 11kV CB panel 28 "S.10223 Post Office derby" fdr tripped on: RELAYS: Basler relay 1.2.1 Traget 50 TBC FIELD EFIs: Nil SIGNALS: P-28 Open ABNORMAL: Sw B cloase @ S.10076 Harrow Victor, AB 31097 OPEN (SHT5 A4) REMARKS: Bat found on 11kV mains near S.10292 The Strand Hayburn | November | 2011 | 2012Q2 | 2012 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | OH | Not Veg | 2011-11-01 | N | 107.693 | N | 5 | N | N | 1.1101 | 39.4971 | 215320.0678
| ZN3922:PA19 | 1148 | 783.2622 | 38.1 | 0.68228 | 38.1 | 19866 | 13447 | 742228 | 2011-11-02 02:38 | 2011-11-02 03:30 | 52 | 11kV | 24302 | 476 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Zn.12630 Peats Ridge Pnl.4 - TCAT 14227 Peats Ridge George Downes tripped and locked out on A + C phase diff, reclose prohibition relay Remarks: TCAT 14227 failed | November | 2011 | 2012Q2 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2011-11-02 | N | 51.0546 | N | 2 | N | N | 1.1101 | 39.4971 | 17759.1848
| ZN3922:PA2 | 2311 | 1575.677 | 39.04 | 0.68182 | 39.04 | 19911 | 13911 | 742572 | 2011-11-02 15:14 | 2011-11-02 17:50 | 156 | 11kV | 25116 | 161 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | @S.15474 Fisher Rd 96 Centre phase 40A HV fues Operated Ex panel 12R 's 16803 Middleton Warringah from S15006 Dee Why West Truck clipped pole breaking LV X arm and bringing D/Ws down on CNR regent & fisher | November | 2011 | 2012Q2 | 2012 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2011-11-02 | N | 156 | N | 2 | N | N | 1.1101 | 39.4971 | 18354.032
| ZN3922:PA21 | 684 | 646.2153 | 40.64 | 0.94476 | 40.64 | 18625 | 464 | 742965 | 2011-11-03 01:44 | 2011-11-03 03:40 | 116 | 11kV | 130419 | 1349 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | At ZN.9700 Kirrawee 11kV P-20 The Belmont Cook fdr, tripped on: A and B phase inst. Overcurrent, timing relay and lock out relay. 11kv trip signal. REMARKS: Cause not ascertained. Mains to patrol in daylight. | November | 2011 | 2012Q2 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2011-11-03 | N | 96.6783 | N | 7 | N | N | 1.1101 | 39.4971 | 95306.3585
| ZN3922:PA22 | 938 | 709.6838 | 37.49 | 0.75659 | 37.49 | 19695 | 11573 | 742735 | 2011-11-03 07:31 | 2011-11-03 08:39 | 68.1333 | 11kV | 59773.2667 | 1245 | HV | Animal Bird | Animal | O/H Link | Unplanned | Unselected | N | LID 118247 dead crow found at links 19653, refer to OMS 743240, 743239 and 742737 2 Fault operations, Overcurrent , Earth Fault | November | 2011 | 2012Q2 | 2012 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Not Veg | 2011-11-03 | N | 48.0107 | N | 7 | N | N | 1.1101 | 39.4971 | 43680.5403
| ZN3922:PA23 | 746 | 458.3034 | 36.13 | 0.61435 | 36.13 | 19185 | 5409 | 743899 | 2011-11-03 10:26 | 2011-11-03 10:30 | 4 | 11kV | 7852 | 1963 | HV | Staff Operation | Utility Process Issue | DC Transformer | Unplanned | Unselected | N | Zn.12600 Lisarow 33kV & 11kV No.2 TX CBs tripped interrupting panels 8,11 ,12 & 13. On Busbar Protection panel No.2 - A phase trip & multitrip No Tx2 panel - A Phase diff, autoclose prohibition & multitrip Remarks: Staff error. T/PE tripped TX on Busbar protection when working on panel 9. | November | 2011 | 2012Q2 | 2012 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | UG | Not Veg | 2011-11-03 | N | 4 | N | 7 | N | N | 1.1101 | 39.4971 | 5738.01
| ZN3922:PA26 | 1903 | 1216.5784 | 33.16 | 0.6393 | 33.16 | 19191 | 5534 | 742727 | 2011-11-03 07:18 | 2011-11-03 11:35 | 257 | 11kV | 514 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118257 Fuse size: 10 AMP Refer to OMS 742727 for call taken job | November | 2011 | 2012Q2 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2011-11-03 | N | 257 | N | 7 | N | N | 1.1101 | 39.4971 | 375.616
| ZN3922:PA27 | 650 | 425.9168 | 32.85 | 0.65526 | 32.85 | 19690 | 11433 | 743922 | 2011-11-03 14:30 | 2011-11-03 14:55 | 25 | 11kV | 575 | 23 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | DOp interrupted section of pnale 14 feeder between AB40109 and AB40158 and IS41987 tee PT11811 and PT 14474 for repiars following car hit pole in Wyee Rd near Pacific Hwy, Doyalson | November | 2011 | 2012Q2 | 2012 | ZN14892:PA14 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2011-11-03 | N | 25 | N | 7 | N | N | 1.1101 | 39.4971 | 420.193
| ZN3922:PA29 | 2294 | 1643.8013 | 36.23 | 0.71657 | 36.23 | 19223 | 6193 | 743925 | 2011-11-03 15:10 | 2011-11-03 15:15 | 5 | 11kV | 490 | 98 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | DOp interrupted section of panel 14 from IS41987 to N/O 40955(does not phase) for switching to restore 11kV feeder between AB40109 and AB40158 and IS41987 for repairs following car hit pole in Wyee Rd near Pacific Hwy, Doyalson PT13318 PT14335 PT11153 PT13317 PT12898 S12195 PT11811 PT14474 interrupted | November | 2011 | 2012Q2 | 2012 | ZN14892:PA14 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2011-11-03 | N | 5 | N | 7 | N | N | 1.1101 | 39.4971 | 358.0775
| ZN3922:PA3 | 806 | 588.7787 | 35.99 | 0.73049 | 35.99 | 19757 | 12452 | 743883 | 2011-11-03 23:00 | 2011-11-03 23:43 | 43 | 11kV | 17071 | 397 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn384 Camperdown Pa10 fdr tripped on RELAYS-Aph O/C EFI SIGNALS 5kV trip tx5 GE CB10 trip, Battery defect 5kV UG fdr fault from Pa10@Zn384 Camperdown to S98 Guihenst to S267 Ross st. | November | 2011 | 2012Q2 | 2012 | ZN384:PA10 | ZN116:PA23 | ZN00116/000023 | INNER WEST | UG | Not Veg | 2011-11-03 | N | 43 | N | 7 | N | N | 1.1101 | 39.4971 | 12474.9833
| ZN3922:PA30 | 150 | 75.4203 | #N/A | 0.5028 | 39.4971 | 18675 | 919 | 743561 | 2011-11-05 09:45 | 2011-11-05 10:45 | 60 | 11kV | 120 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118273/01 - Fuse size: 16 Amp; DOLF; Volts = 239; Refer OMS 743561. | November | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-11-05 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN3922:PA5 | 2519 | 1733.4917 | 37.87 | 0.68817 | 37.87 | 20357 | 19833 | 743579 | 2011-11-05 10:42 | 2011-11-05 11:37 | 55 | 11kV | 29755 | 541 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.847 Hornsby Pnl.48 tripped / reclosed and locked out on: C phase IOC and timed O/C timing relay, lockout EFI Remarks: Tree brnach in 11kV wires removed by DOp adjacent to UGOH to S.5091 | November | 2011 | 2012Q2 | 2012 | ZN847:PA48 | ZN847:PA48 | ZN00847/000048 | HORNSBY | OH | Veg | 2011-11-05 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 21744.0764
| ZN3922:PA7 | 1880 | 1399.2799 | 33.99 | 0.7443 | 33.99 | 19971 | 14640 | 743696 | 2011-11-05 23:54 | 2011-11-06 02:37 | 163 | 11kV | 25061 | 255 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12610 Long jetty Pnl.5 tripped on: C phase IOC, EFI, Fault Check Remarks: 11kV feeder fault between LB42080 to S.14747 Sw A to AB44558 tee S.11885. | November | 2011 | 2012Q2 | 2012 | ZN12610:PA5 | ZN12610:PA5 | ZN12610/000005 | CENTRAL COAST | UG | Not Veg | 2011-11-05 | N | 98.2784 | N | 3 | N | N | 1.1101 | 39.4971 | 18313.8396
| ZN398:PA10 | 615 | 960.6331 | #N/A | 1.562 | 39.4971 | 19094 | 4609 | 743721 | 2011-11-06 08:10 | 2011-11-06 09:20 | 70 | 11kV | 13580 | 194 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | LID 118279 oms report no 743721.Please Investigate LV CB 35371 at Hunter no 5 sub,this LV circuit breaker has tripped numerous times.(Merlin Gerin LV Unit may be faulty). Note: all customers attached to Hunter 1-7 have been replicated in this event as unable to determine which actual customers were affected | November | 2011 | 2012Q2 | 2012 | 503:48076 | 532:83312 | ZN00532/083312 | MAITLAND | Unknown | Not Veg | 2011-11-06 | N | 70 | N | 1 | N | N | 1.1101 | 39.4971 | 9923.8635
| ZN398:PA11 | 904 | 807.9998 | #N/A | 0.89381 | 39.4971 | 18593 | 140 | 744036 | 2011-11-07 11:17 | 2011-11-07 12:46 | 89 | 11kV | 445 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118294/01; Fuse size: 40 Amp; DOLF; Refer to OMS 744036. | November | 2011 | 2012Q2 | 2012 | 234:2006 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Veg | 2011-11-07 | N | 89 | N | 9 | N | N | 1.1101 | 39.4971 | 325.1929
| ZN398:PA15 | 1602 | 1317.0369 | 36.02 | 0.82212 | 36.02 | 19347 | 7626 | 744064 | 2011-11-07 13:00 | 2011-11-07 13:30 | 30 | 11kV | 450 | 15 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Unselected | N | Lid No. 118295/01; Fuse size: 40 Amp; Refer OMS 744064; Changes a 20A fuse with a 40A fuse. | November | 2011 | 2012Q2 | 2012 | 234:2000 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Not Veg | 2011-11-07 | N | 30 | N | 9 | N | N | 1.1101 | 39.4971 | 328.8467
| ZN398:PA16 | 2366 | 1276.6975 | 33.9 | 0.5396 | 33.9 | 20433 | 20368 | 744164 | 2011-11-07 17:15 | 2011-11-07 18:35 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118297/01; Fuse Size: 10 Amp; Substation DOLF; Refer OMS 744164; Volts = 248. | November | 2011 | 2012Q2 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2011-11-07 | N | 80 | N | 9 | N | N | 1.1101 | 39.4971 | 58.4616
| ZN398:PA19 | 863 | 949.2209 | 37.57 | 1.0999 | 37.57 | 19053 | 4374 | 744218 | 2011-11-07 18:18 | 2011-11-07 20:18 | 120 | 11kV | 132848 | 1270 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn1610 Homebush Bay 11KV feeder panel 11 "Aux TX1 etc" tripped on, Earth fault, EFI Field EFI's operated at: S4127, S5114, S5115, S46780, S4287, S1148 Remarks: Suspect UG cable fault from S1148 Paramatta Flemington (sw B) to S.5451 Parramatta Bedford (sw A) Related jobs: #744241, 744223, 744219, 744218, 745372, 745289 | November | 2011 | 2012Q2 | 2012 | ZN1610:PA11 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2011-11-07 | N | 104.6047 | N | 9 | N | N | 1.1101 | 39.4971 | 97081.4
| ZN398:PA2 | 2254 | 1442.9907 | 36.3 | 0.64019 | 36.3 | 18863 | 2681 | 744268 | 2011-11-07 20:39 | 2011-11-07 22:39 | 120.3667 | 11kV | 2166.6 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118313/01; Fuse size: 20 Amp; DOLF. | November | 2011 | 2012Q2 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2011-11-07 | N | 120.3667 | N | 9 | N | N | 1.1101 | 39.4971 | 1583.2874
| ZN398:PA20 | 1464 | 950.5349 | 33.76 | 0.64927 | 33.76 | 19735 | 12110 | 744283 | 2011-11-07 20:56 | 2011-11-07 23:30 | 154 | 11kV | 11242 | 73 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID No. 118321/01; Fuse size: 31 Amp; DO found 2 flown HV fuses at Kiosk; HV Cable was blackened, inspection required of cable and Hazemeyer S/F. Section was interr. to change fuses. | November | 2011 | 2012Q2 | 2012 | 213:33773 | 213:33777 | ZN00213/033777 | NEWCASTLE | UG | Not Veg | 2011-11-07 | N | 154 | N | 9 | N | N | 1.1101 | 39.4971 | 8215.322
| ZN398:PA22 | 308 | 1377.6971 | #N/A | 4.473 | 39.4971 | 19943 | 14207 | 744292 | 2011-11-07 20:58 | 2011-11-08 00:30 | 212 | 11kV | 187365.2 | 1777 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Electrical Storm | N | LID 118315 2 Fault operations, Overcurrent Earth Fault Refer to OMS 746080, 746087, 746090, 746091, 744301 and 744297 OMS jobs withdrawn: 744321 and 744320 | November | 2011 | 2012Q2 | 2012 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2011-11-07 | N | 105.4391 | N | 9 | N | N | 1.1101 | 39.4971 | 136920.9618
| ZN398:PA24 | 2074 | 993.6587 | 34.94 | 0.4791 | 34.94 | 19176 | 5264 | 744259 | 2011-11-07 20:14 | 2011-11-08 01:20 | 306 | 11kV | 306 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Lid No. 118322/01; Fuse size: 10 Amp; Line DOLF; Substation DOLF; Line DOLF 10020 & sub DOLF 52371 replaced. Refer to OMS 744259 | November | 2011 | 2012Q2 | 2012 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2011-11-07 | N | 306 | N | 9 | N | N | 1.1101 | 39.4971 | 223.6158
| ZN398:PA25 | 893 | 909.4583 | 44.95 | 1.0184 | 44.95 | 20258 | 17929 | 744298 | 2011-11-07 21:16 | 2011-11-08 03:55 | 399 | 11kV | 1197 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118323/01; Fuse size: 10 Amp; DOLF; | November | 2011 | 2012Q2 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2011-11-07 | N | 399 | N | 9 | N | N | 1.1101 | 39.4971 | 874.7323
| ZN398:PA26 | 1101 | 713.7692 | 34.95 | 0.64829 | 34.95 | 19541 | 9498 | 744544 | 2011-11-08 14:07 | 2011-11-08 15:19 | 72 | 11kV | 64008 | 889 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Hot >35C | N | At TCAT 1615 the 11kV CB tripped on A and C phase Differential. Zone earth and #3 Tx Group Earth operated, DField efi down @ S.8760. 11kV cable end box on TCAT failed explosively. | November | 2011 | 2012Q2 | 2012 | ZN847:PA45 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | Unknown | Not Veg | 2011-11-08 | N | 72 | N | 15 | N | N | 1.1101 | 39.4971 | 46775.1585
| ZN398:PA29 | 1051 | 852.5552 | 37.33 | 0.81118 | 37.33 | 18680 | 981 | 744506 | 2011-11-08 12:40 | 2011-11-08 16:20 | 220 | 11kV | 4400 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.13348 Claga pacific - B phase HDO operated (31.5K) Fuse fatigued | November | 2011 | 2012Q2 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2011-11-08 | N | 220 | N | 15 | N | N | 1.1101 | 39.4971 | 3215.3902
| ZN398:PA3 | 2211 | 1423.5221 | 38.54 | 0.64384 | 38.54 | 19141 | 4890 | 744702 | 2011-11-08 17:24 | 2011-11-08 18:59 | 95 | 11kV | 118750 | 1250 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | At S.195 Pymble, Panel 9 Fdr CB tripped on A phase timed OC, efi, fault check. 11kV trip, #2 group earth. Field efi's operated at S.47348, S.1102 and S.35377. 11kV middle and roadside phases adjacent AB.1710 were twisted together. The footpath side CCT LA earth tail blown off O.S 44 Heathcote Ave. | November | 2011 | 2012Q2 | 2012 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Not Veg | 2011-11-08 | N | 95 | N | 15 | N | N | 1.1101 | 39.4971 | 86778.9975
| ZN398:PA30 | 2028 | 1075.58 | #N/A | 0.53036 | 39.4971 | 19869 | 13462 | 744659 | 2011-11-08 16:39 | 2011-11-08 19:00 | 141 | 11kV | 563.6 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.14861 Little Jilliby 1.2 - Footpath phase 16.5k HDO Fatigued fuse element GIS connectivity error | November | 2011 | 2012Q2 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2011-11-08 | N | 140.9 | N | 15 | N | N | 1.1101 | 39.4971 | 411.8623
| ZN398:PA31 | 962 | 1134.8174 | 48.28 | 1.1796 | 48.28 | 19281 | 7190 | 744795 | 2011-11-08 18:00 | 2011-11-08 20:22 | 142 | 11kV | 1562 | 11 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID No. 118334/01; interrupted to replace pole KQ-40080. | November | 2011 | 2012Q2 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2011-11-08 | N | 142 | N | 15 | N | N | 1.1101 | 39.4971 | 1141.4635
| ZN398:PA4 | 1457 | 712.041 | 32.03 | 0.4887 | 32.03 | 20300 | 18958 | 744693 | 2011-11-08 17:14 | 2011-11-08 21:06 | 232 | 11kV | 381879 | 2009 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At ZN.10994 Mortdale, P-12L (labelled S.49538) tripped on: RELAYS: EF, Ins EF, B & C IOC, GE SIGNALS: 11kv Trip FIELD EFIs: S.10683, S.10901, S.10018, S.10682 & S.10581 REMARKS: No cause found. Mains to patrol in daylight. At ZN.10994 Mortdale, P-12L (labelled S.49538) tripped on: RELAYS: EF, Ins EF, B & C IOC, GE SIGNALS: 11kv Trip FIELD EFIs: S.10683, S.10901, S.10018, S.10682 & S.10581 REMARKS: No cause found. Mains to patrol in daylight. | November | 2011 | 2012Q2 | 2012 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Veg | 2011-11-08 | N | 190.0841 | N | 15 | N | N | 1.1101 | 39.4971 | 279065.9097
| ZN398:PA9 | 837 | 591.5614 | 43.9 | 0.70676 | 43.9 | 19208 | 5897 | 744685 | 2011-11-08 17:03 | 2011-11-08 21:14 | 251 | 11kV | 204268 | 1300 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Rain Heavy | N | Zn35800 Bankstown 11kv feeder pnl 1 "Gow Gibson" tripped on, earth fault, EFI Remarks: Lightning strike, arrestor blown UGOH to S5006 Eldridge Rd Related jobs: #744747, 744722, 744685, 744683, 744679, 745206, 745203, 744681 | November | 2011 | 2012Q2 | 2012 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2011-11-08 | N | 157.1292 | N | 15 | N | N | 1.1101 | 39.4971 | 149273.0295
| 216:10722 | 1777 | 1714.2499 | 34.3 | 0.96469 | 34.3 | 20329 | 19342 | 744823 | 2011-11-08 19:05 | 2011-11-08 22:40 | 215 | 11kV | 508534.4 | 3251 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | At S15003 Balgowlah Panel #10 Fdr tripped on SEL HV Bond off 4 way tee to PT15479 Brighton St to AB22777 to USL22419 to UGOH brighton ST NR rickard St | November | 2011 | 2012Q2 | 2012 | ZN15003:PA10 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2011-11-08 | N | 156.424 | N | 15 | N | N | 1.1101 | 39.4971 | 371621.9403
| 216:10723 | 780 | 556.8141 | 33.25 | 0.71386 | 33.25 | 19420 | 8427 | 744916 | 2011-11-08 22:32 | 2011-11-08 23:32 | 60 | 11kV | 66720 | 1112 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S3154 St Ives Panel #13 Nambucca Burns Fdr Tripped on A & B ph O/C & IOC 11kV trip Stick removed ajacent AB2320 | November | 2011 | 2012Q2 | 2012 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | OH | Veg | 2011-11-08 | N | 60 | N | 15 | N | N | 1.1101 | 39.4971 | 48757.0081
| 216:10724 | 1401 | 803.2263 | 31.32 | 0.57332 | 31.32 | 19819 | 12946 | 745252 | 2011-11-08 23:00 | 2011-11-09 01:20 | 140 | 11kV | 140 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | At S.10914 Harslett Water Board. Road & Footpath phase 40 Amp fuses blown. Waternoard staff member Greg 0417 246 785. EX "LB 30185" fdr P-4 at S.10999 Kogarah. REMARKS: lightning storm at time of notification. Water board staff notified of supply problems at 23.30 8/11/2011. | November | 2011 | 2012Q2 | 2012 |  |  |  | GEORGES RIVER | OH | Not Veg | 2011-11-08 | N | 140 | N | 15 | N | N | 1.1101 | 39.4971 | 102.3079
| 216:10726 | 988 | 1053.7319 | 41.48 | 1.0665 | 41.48 | 18936 | 3386 | 744570 | 2011-11-08 14:48 | 2011-11-09 02:57 | 729 | 11kV | 85452.3333 | 119 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | MVA Car hit pole 11kV Fdr Killarney Zone Pnl 8 USL24837 to USL 21332 tee PT 15379 Deakin St 2 Failed ***This report is not supported by control room hard copy*** | November | 2011 | 2012Q2 | 2012 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2011-11-08 | N | 718.0868 | N | 15 | N | N | 1.1101 | 39.4971 | 62446.0448
| 216:10727 | 843 | 368.6491 | 31.7 | 0.43731 | 31.7 | 19783 | 12650 | 744500 | 2011-11-08 12:34 | 2011-11-09 03:05 | 871 | 11kV | 871 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID NO. 118339/01; Fuse Size: 10 Amp; Substation DOLF; Replaced faulty L/A. | November | 2011 | 2012Q2 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2011-11-08 | N | 871 | N | 15 | N | N | 1.1101 | 39.4971 | 636.5011
| 216:10728 | 1202 | 893.9295 | 34.24 | 0.7437 | 34.24 | 19850 | 13345 | 744913 | 2011-11-08 22:18 | 2011-11-09 04:30 | 372 | 11kV | 1860 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Lightning | N | PT.12371 Dooralong Yambo 1.2 - Dist #1 - B phase fuse blown (200Amp) Lightning storm at time of interruption | November | 2011 | 2012Q2 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2011-11-08 | N | 372 | N | 15 | N | N | 1.1101 | 39.4971 | 1359.2331
| 216:10729 | 824 | 603.3464 | 31.71 | 0.73222 | 31.71 | 18913 | 3204 | 744955 | 2011-11-09 05:40 | 2011-11-09 06:21 | 41 | 11kV | 48749 | 1189 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Intellirupter 2935 tripped OC. Car hit pole. | November | 2011 | 2012Q2 | 2012 | ZN847:PA22 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2011-11-09 | N | 41 | N | 8 | N | N | 1.1101 | 39.4971 | 35624.3313
| ZN36200:PA1 | 1419 | 1082.6226 | 33.53 | 0.76295 | 33.53 | 18785 | 2013 | 745996 | 2011-11-09 06:51 | 2011-11-09 06:55 | 4 | 11kV | 1468 | 367 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Circuit Breaker | Unplanned | Unselected | N | LID No. 118341/01; 1 fault operation; pole mounted RAGCB; Trip and reclose. | November | 2011 | 2012Q2 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | Unknown | Unknown | 2011-11-09 | N | 4 | N | 8 | N | N | 1.1101 | 39.4971 | 1072.7711
| ZN36200:PA11 | 1305 | 1000.1863 | 30.46 | 0.76643 | 30.46 | 20063 | 15734 | 744926 | 2011-11-08 23:03 | 2011-11-09 07:25 | 502 | 11kV | 166757 | 1248 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 118338 11KV main C phase contacted LV distributor when crossarm on pole IU60117 (Second and Pine Cardiff) broke and main came down. 11KV main repaired OK. Inspections arranged. Note: Some installations have damage from 11kV into 433V LVF LH 9428 315 A fuse replaced | November | 2011 | 2012Q2 | 2012 | 214:8666 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2011-11-08 | N | 133.6194 | N | 15 | N | N | 1.1101 | 39.4971 | 121861.0971
| ZN36200:PA4 | 938 | 863.8793 | 30.74 | 0.92098 | 30.74 | 19314 | 7370 | 747733 | 2011-11-09 08:32 | 2011-11-09 09:27 | 55 | 11kV | 52635 | 957 | HV | Staff Other | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | Subs Technican working in S.280 was erecting screening may have bumped BV relay causing the 11kV CB and #1 tX 415v CB to trip. At S.297 Rainbow Mount, the 11kV CB also tripped | November | 2011 | 2012Q2 | 2012 | ZN35600:PA2 | ZN35600:PA2 | ZN35600/000002 | RANDWICK | UG | Not Veg | 2011-11-09 | N | 55 | N | 8 | N | N | 1.1101 | 39.4971 | 38464.1055
| ZN36200:PA8 | 1389 | 1231.631 | 34.18 | 0.8867 | 34.18 | 18811 | 2229 | 744897 | 2011-11-08 21:39 | 2011-11-09 11:30 | 831 | 11kV | 254577 | 595 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | At Recloser 1239 tripped - blown LA @ PT.953 (RIVERSIDE PHASE) | November | 2011 | 2012Q2 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2011-11-08 | N | 427.8605 | N | 15 | N | N | 1.1101 | 39.4971 | 186037.3628
| ZN1648:PA10 | 353 | 250.1674 | 38.79 | 0.70869 | 38.79 | 20196 | 16904 | 745216 | 2011-11-09 11:12 | 2011-11-09 13:00 | 108.45 | 11kV | 542.25 | 5 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118349/01; Fuse size: 40 Amp; DOLF; Mechanical failure of fuse element; A=251V, B=253V, C=253V; RHF - A=121A, B=96A, C=84A; LHF - A=29A, B=9A, C=2A. | November | 2011 | 2012Q2 | 2012 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Not Veg | 2011-11-09 | N | 108.45 | N | 8 | N | N | 1.1101 | 39.4971 | 396.2603
| ZN1648:PA11 | 393 | 230.8173 | 39.1 | 0.58732 | 39.1 | 19087 | 4555 | 744970 | 2011-11-09 06:29 | 2011-11-09 13:45 | 436 | 11kV | 2461 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 118350 Sub 52826 - HV Dropper burnt of top of DOLFs Replication switching - refer 749163 and 749164, OMS 744970 withdrawn | November | 2011 | 2012Q2 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2011-11-09 | N | 246.1 | N | 8 | N | N | 1.1101 | 39.4971 | 1798.4262
| ZN1648:PA13 | 252 | 455.0273 | 56.91 | 1.8057 | 56.91 | 20304 | 18996 | 745511 | 2011-11-09 15:51 | 2011-11-09 17:20 | 89 | 11kV | 57922 | 683 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn7900 Campbell St Panel 19 tripped on Signals: 11kv trip, GE Relays: OC, EF, EFI Field EFI's: Sub 8555 Remarks: Suspected UG Cable fault from sub 8555 to sub 35152 to sub 4247 Related jobs: #745511, 748762, 748764, 748729, 748727 | November | 2011 | 2012Q2 | 2012 | ZN7900:PA19 | ZN7900:PA19 | ZN07900/000019 | SYDNEY | UG | Not Veg | 2011-11-09 | N | 84.8053 | N | 8 | N | N | 1.1101 | 39.4971 | 42327.6892
| ZN1648:PA15 | 1137 | 1007.5882 | 36.91 | 0.88618 | 36.91 | 19936 | 14137 | 745656 | 2011-11-10 00:27 | 2011-11-10 03:09 | 161.7 | 11kV | 154093.6833 | 1544 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.10999 Kogarah P-7 "S.10613 Carlton Short" fdr tripped, reclosed, tripped and locked out on. RELAYS: A 7 B phase Timed Overcurrent, Reclose relay & EFI. SIGNALS: 11kV trip FIELD EFIs: S.10613 at S.10925 Forest Water Board: SW.B tripped on A & C phase O/C, SW.A tripped and SW B tripped on A & C phase O/C. REMARKS: Suspect cable fault from S.10925 Forest Water Board SW.A to S.10920 Croydon Forest SW.B to AB 30019. | November | 2011 | 2012Q2 | 2012 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | BAYSIDE | UG | Not Veg | 2011-11-10 | N | 99.8016 | N | 5 | N | N | 1.1101 | 39.4971 | 112607.1188
| ZN1648:PA16 | 999 | 707.0034 | 36.24 | 0.70771 | 36.24 | 19981 | 14865 | 745664 | 2011-11-10 03:53 | 2011-11-10 05:45 | 112.2 | 11kV | 71353.9 | 759 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | Zn.195 Pymble Pnl.25 tripped on: Earth Fault, Fault Check and EFI Field EFIs: S.5341, 5239, 7058, 5693, 3956, 4638 Remarks: Dead Possum found at base of PT.1425. Tcon to inspect PT in daylight | November | 2011 | 2012Q2 | 2012 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | OH | Not Veg | 2011-11-10 | N | 94.0104 | N | 5 | N | N | 1.1101 | 39.4971 | 52143.3255
| ZN1648:PA2 | 287 | 476.2109 | 59.35 | 1.6593 | 59.35 | 19267 | 6689 | 745586 | 2011-11-09 16:23 | 2011-11-10 08:15 | 952 | 11kV | 422762 | 1185 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn901 Surry Hills panel 20 tripped on "George Redfern" Signals: 11kv trip, GE, ZE. Relays: EL, EFI Field EFI'sL Sub 8555 Remarks: Suspected cable fault. Note see separate interruption report on Panel No.19 in conjunction Related jobs: #745632, 745586, 748790, 748821, 748826, 748788, 748500, 748499 | November | 2011 | 2012Q2 | 2012 | ZN901:PA20 | ZN901:PA29 | ZN00901/000029 | SYDNEY | UG | Not Veg | 2011-11-09 | N | 356.7612 | N | 8 | N | N | 1.1101 | 39.4971 | 308942.0002
| ZN1648:PA20 | 378 | 231.5544 | 32.28 | 0.61258 | 32.28 | 20130 | 16172 | 745539 | 2011-11-09 16:23 | 2011-11-10 08:27 | 964 | 11kV | 683174 | 710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn901 Surry Hills Panel 19 tripped on Signals: 11kv trip, GE, ZE Relays: EL, EFI Field EFI's: Nil Remarks: Suspected cable fault between Zn901 Surry Hills Panel 19 and Sub 3744 Redfern Gib "Surry Hills Panel 19" feeder. Note: See separate interruption report on Panel 20 in conjunction. Related jobs: #745552, 745539, 748794, 748776 | November | 2011 | 2012Q2 | 2012 | ZN901:PA19 | ZN901:PA31 | ZN00901/000031 | SYDNEY | UG | Not Veg | 2011-11-09 | N | 962.2169 | N | 8 | N | N | 1.1101 | 39.4971 | 499243.409
| ZN1648:PA21 | 474 | 379.6764 | 40.43 | 0.80101 | 40.43 | 19284 | 7238 | 745809 | 2011-11-10 10:05 | 2011-11-10 13:06 | 180.8 | 11kV | 86062.75 | 1226 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | At Sub 1287 Revesby Panel No.17 "Hinemoa St" opened & reclosed on A & C phase IOC, Lockout, Fault Check Relays, EFI Zone Earth, No.1 Group Earth & 11kv trip. Field efi's operated @ Subs 5036, 35325, 5035, 5829 & 48600 Remarks: Car hit pole 30 Lucas Rd East Hills. Bankstown OH have Driver/Car/Police Details Related jobs: #745822, 745809, 747339, 747341, 747337 | November | 2011 | 2012Q2 | 2012 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2011-11-10 | N | 70.198 | N | 5 | N | N | 1.1101 | 39.4971 | 62892.1193
| ZN9245:PA1 | 1229 | 1074.6223 | 35.91 | 0.87439 | 35.91 | 20337 | 19395 | 746145 | 2011-11-10 17:21 | 2011-11-10 18:14 | 53 | 11kV | 108915 | 2055 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.10 tripped on: (51) A & B phase timed OC Branch on HV mains on Tuggerawong Rd. Between USL40139 tee PT13098 | November | 2011 | 2012Q2 | 2012 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2011-11-10 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 79591.8696
| ZN9245:PA10 | 1501 | 1368.4601 | 33.68 | 0.9117 | 33.68 | 18706 | 1186 | 746177 | 2011-11-10 18:55 | 2011-11-10 20:55 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118374 Fuse size: 10 Amp Refer related record 746177, cause not ascertained | November | 2011 | 2012Q2 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2011-11-10 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN9245:PA13 | 1833 | 1424.6038 | 32.62 | 0.7772 | 32.62 | 19928 | 14098 | 746561 | 2011-11-11 16:33 | 2011-11-11 16:56 | 23 | 11kV | 1240 | 310 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ex Zn.12570 Avoca Pnl.12 - REC 45180 tripped & reclosed on IOC/OC Abnormal Switching: AB41682 OPEN / Sw B @ S.18689 CLOSED After trip/reclose, AOp opened REC45180 @ 16:53 for DOp to remove brnach near PT.11784 | November | 2011 | 2012Q2 | 2012 |  |  |  | CENTRAL COAST | OH | Veg | 2011-11-11 | N | 4 | N | 1 | N | N | 1.1101 | 39.4971 | 906.1554
| ZN9245:PA15 | 950 | 1408.6836 | 44.68 | 1.4828 | 44.68 | 19610 | 10292 | 751694 | 2011-11-12 07:49 | 2011-11-12 10:20 | 151 | 11kV | 1857 | 231 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | PT13229 A & B Phase HDOs blown Lightning strike in area | November | 2011 | 2012Q2 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2011-11-12 | N | 8.039 | N | 5 | N | N | 1.1101 | 39.4971 | 1357.0408
| ZN9245:PA19 | 1358 | 1323.0224 | 30.31 | 0.97424 | 30.31 | 20354 | 19741 | 746772 | 2011-11-12 08:38 | 2011-11-12 10:27 | 109 | 11kV | 15486 | 205 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Lightning | N | Zn.14891 Wyong Pnl.6 tripped / reclosed / tripped on: 51T ABC O/C - Lockout timing relay - EFI fault CHeck Field EFIs: S.18496 18493 14826 18464 14404 UGOH damanged by Lightning above S.18538 | November | 2011 | 2012Q2 | 2012 | ZN14891:PA6 | ZN14891:PA6 | ZN14891/000006 | CENTRAL COAST | Unknown | Unknown | 2011-11-12 | N | 75.5415 | N | 5 | N | N | 1.1101 | 39.4971 | 11316.712
| ZN9245:PA21 | 1222 | 951.0833 | 30.38 | 0.7783 | 30.38 | 18824 | 2323 | 746862 | 2011-11-12 16:23 | 2011-11-12 18:10 | 107 | 11kV | 107 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118403/01; Fuse Size: 10 Amp; DOLF; Refer OMS 746862; 256 Volts 5, 5, 2 amps; See LID Report 118402/01. | November | 2011 | 2012Q2 | 2012 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Veg | 2011-11-12 | N | 107 | N | 5 | N | N | 1.1101 | 39.4971 | 78.1924
| ZN9245:PA3 | 1204 | 1063.2131 | 35.23 | 0.88307 | 35.23 | 19931 | 14102 | 746880 | 2011-11-12 19:39 | 2011-11-12 23:50 | 251 | 11kV | 10793 | 43 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID No. 118406/01; Feeder isolated to repair broken tappings at pole SI-60002. Refer to OMS 746880. | November | 2011 | 2012Q2 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2011-11-12 | N | 251 | N | 5 | N | N | 1.1101 | 39.4971 | 7887.2061
| ZN9245:PA4 | 1058 | 860.3021 | 36.88 | 0.81314 | 36.88 | 19546 | 9578 | 746895 | 2011-11-12 22:24 | 2011-11-13 00:20 | 116 | 11kV | 110321 | 1242 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9245 Engadine P-13 "Engadine Aux No.1" FDR tripped & reclosed on: RELAYS: B phase leakage, EFI, Reclose SIGNALS: 11kV trip, No.2 Grp Eth. FIELD EFI's: S.48146, S.9199, UGOH in Banksia Ave nr Bullecourt S.9288 REMARKS: Section of 11kV fdr from S.9288 Kulinia St (SwB) to CP.35931 thurlgona Cooreiengah (SwA) tee to S.9362 Kurwin Thurlgona failed with suspect cable fault. | November | 2011 | 2012Q2 | 2012 | ZN9245:PA13 | ZN9245:PA21 | ZN09245/000021 | SUTHERLAND | UG | Not Veg | 2011-11-12 | N | 88.8253 | N | 5 | N | N | 1.1101 | 39.4971 | 80619.3329
| ZN9245:PA6 | 357 | 312.592 | 42.23 | 0.87561 | 42.23 | 19755 | 12450 | 746902 | 2011-11-13 03:58 | 2011-11-13 07:05 | 187 | 11kV | 193917 | 1433 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn.12600 Lisarow -Pnl.3 - tripped on: IOC and timed Overcurrent, EFI Car hit pole Pacific Hwy Narara. Gold Holden Station Wagon rego: WND 685 | November | 2011 | 2012Q2 | 2012 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2011-11-13 | N | 135.3224 | N | 7 | N | N | 1.1101 | 39.4971 | 141708.824
| ZN9245:PA9 | 390 | 246.4008 | #N/A | 0.6318 | 39.4971 | 19336 | 7577 | 746941 | 2011-11-13 09:11 | 2011-11-13 10:48 | 97 | 11kV | 18818 | 194 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 118411 LV CB 35371 tripped 0911hrs , Closed 0943 hrs, Tripped 0945 hrs, Closed at request of Centre Management 1045 hrs. Load approx 540A per phase., URGENT ATTENTION REQUIRED Multiple customer from across all Hunter No 1-7 have had outages over the past couple of weeks, from the notepad comment on vrelated records generator to be installed | November | 2011 | 2012Q2 | 2012 | 503:48076 | 532:83312 | ZN00532/083312 | MAITLAND | Unknown | Unknown | 2011-11-13 | N | 97 | N | 7 | N | N | 1.1101 | 39.4971 | 13751.6394
| ZN2635:PA31 | 970 | 710.7337 | 34.74 | 0.73272 | 34.74 | 19441 | 8572 | 746905 | 2011-11-13 01:10 | 2011-11-13 11:37 | 627 | 11kV | 19210 | 126 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID No. 118407/01; 2 fault operations; earth fault; pole mounted RAGCB; 11KV main down between subs 5409 & 54008 Dist Sheet 511/6 B2. Pelican hit mains. Refer OMS jobs - 749014, 749012, 749017, 749018, 749021. | November | 2011 | 2012Q2 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2011-11-13 | N | 152.4603 | N | 7 | N | N | 1.1101 | 39.4971 | 14038.1014
| ZN2635:PA32 | 500 | 781.5266 | 36.6 | 1.5631 | 36.6 | 20240 | 17556 | 746979 | 2011-11-13 13:38 | 2011-11-13 18:35 | 297 | 11kV | 297 | 1 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118415/01; Fuse size: 10 Amp; DOLF; Refer OMS 746979. | November | 2011 | 2012Q2 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2011-11-13 | N | 297 | N | 7 | N | N | 1.1101 | 39.4971 | 217.0388
| ZN2635:PA33 | 7 | 738.197 | #N/A | 105.4567 | 39.4971 | 18988 | 3885 | 746989 | 2011-11-13 15:06 | 2011-11-13 20:20 | 314 | 11kV | 2720 | 51 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 118416 section isolated from abs 6852 to repair tapping at pole GW-60319 also see report # 118412 Trip and reclose on 13014 Note from Greg Sessions 11KV line in area of 38A Marshall street Cooranbong ( sub 3502 pole 630 ) needs heavy trimming of trees fom 11KV | November | 2011 | 2012Q2 | 2012 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Not Veg | 2011-11-13 | N | 53.3333 | N | 7 | N | N | 1.1101 | 39.4971 | 1987.6958
| ZN2635:PA35 | 1685 | 1216.3086 | 34.46 | 0.72184 | 34.46 | 18886 | 2970 | 747008 | 2011-11-13 16:50 | 2011-11-13 20:20 | 210 | 11kV | 1890 | 9 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118417/01; Fuse size: 10 Amp; DOLF; Refer to OMS 747008. | November | 2011 | 2012Q2 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2011-11-13 | N | 210 | N | 7 | N | N | 1.1101 | 39.4971 | 1381.1563
| ZN2635:PA38 | 1014 | 856.8249 | 32.05 | 0.845 | 32.05 | 20368 | 19894 | 747037 | 2011-11-13 19:47 | 2011-11-13 21:06 | 79 | 11kV | 79 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118418/01; Fuse Size: 3 Amp; DOLF; Refer OMS 747037. | November | 2011 | 2012Q2 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2011-11-13 | N | 79 | N | 7 | N | N | 1.1101 | 39.4971 | 57.7309
| ZN2635:PA39 | 291 | 1814.0267 | 40.8 | 6.2338 | 40.8 | 18565 | 8 | 747054 | 2011-11-14 04:29 | 2011-11-14 07:32 | 182.4833 | 11kV | 2054.4833 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID No. 118419/01; Fuse Size: 10 Amp; DOLF; may have been fuse fatique; please patrol feeder. Refer to OMS 747056. | November | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-11-14 | N | 158.0372 | N | 13 | N | N | 1.1101 | 39.4971 | 1501.3558
| ZN2635:PA40 | 431 | 1193.0262 | 38.15 | 2.768 | 38.15 | 19859 | 13374 | 747214 | 2011-11-14 11:02 | 2011-11-14 12:14 | 71.9833 | 11kV | 4653.2333 | 80 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID No. 118424/01; Fuse size: 40 Amp; DOLF; Fuse Fatigued; Readings as left 152A, 42A, 15A @ 251V. Refer OMS 747221. | November | 2011 | 2012Q2 | 2012 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2011-11-14 | N | 58.1654 | N | 13 | N | N | 1.1101 | 39.4971 | 3400.4457
| ZN2635:PA41 | 250 | 156.029 | 39.74 | 0.62412 | 39.74 | 18838 | 2413 | 747167 | 2011-11-14 10:00 | 2011-11-14 14:40 | 280 | 11kV | 178397 | 1487 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S847 Hornsby Panel 2 tripped on EFI - Earth Fault 11kV Trip - Zone Earth Tx1 Group Earth. Cause: UG cable fault between S47399 Clarke Marillian and S4505 Russell Unwin. See OMS 747896 747903 747900 747187 747235 747175 | November | 2011 | 2012Q2 | 2012 | ZN847:PA2 | ZN847:PA2 | ZN00847/000002 | HORNSBY | UG | Not Veg | 2011-11-14 | N | 119.9711 | N | 13 | N | N | 1.1101 | 39.4971 | 130367.2658
| ZN2635:PA43 | 1327 | 941.5681 | 35 | 0.70955 | 35 | 20071 | 15796 | 747364 | 2011-11-14 15:07 | 2011-11-14 16:23 | 76.0333 | 11kV | 6158.7 | 81 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S6176 Wilson Killaloe 400A fuse blown on A and B phase of distributor 1. Cause: Tree branch fell on Mains O/S 5 Wilson Rd Pennant Hills. See OMS 747364 747372 747377 | November | 2011 | 2012Q2 | 2012 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Veg | 2011-11-14 | N | 76.0333 | N | 13 | N | N | 1.1101 | 39.4971 | 4500.5963
| ZN2635:PA44 | 1143 | 1238.9339 | 39.37 | 1.0839 | 39.37 | 19123 | 4758 | 747427 | 2011-11-14 16:35 | 2011-11-14 18:25 | 110 | 11kV | 92714 | 1223 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S129 Hunters Hill Panel 9 Tripped on A phase Timed Overcurrent. Cause: Large Tree branch hitting mains O/S135 Riverview RD Lane Cove. See OMS 748297 748301 748300 | November | 2011 | 2012Q2 | 2012 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2011-11-14 | N | 75.8087 | N | 13 | N | N | 1.1101 | 39.4971 | 67752.6566
| ZN2635:PA46 | 1111 | 803.857 | 35.4 | 0.72354 | 35.4 | 19005 | 4087 | 747446 | 2011-11-14 16:34 | 2011-11-14 18:27 | 113 | 11kV | 8588 | 76 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID No. 118426/01; 1 fault opeation; Pole mounted RAGCB, Sensitive earth fault; Refer OMS 747446. No cause found. Please patrol feeder. Refer OMS 749025; 749029 & 749030 | November | 2011 | 2012Q2 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2011-11-14 | N | 113 | N | 13 | N | N | 1.1101 | 39.4971 | 6275.8571
| ZN2635:PA47 | 39 | 719.2256 | 43.75 | 18.4417 | 43.75 | 19158 | 4986 | 747403 | 2011-11-14 16:02 | 2011-11-14 18:35 | 153 | 11kV | 153 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID No. 118427/01; Fuse size: 3 Amp; DOLF; Refer OMS No. 747037; Sub DOLF blew previous day (LID Report 118418). Sub isolated to replace LAs. | November | 2011 | 2012Q2 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2011-11-14 | N | 153 | N | 13 | N | N | 1.1101 | 39.4971 | 111.8079
| ZN2635:PA50 | 795 | 1138.2419 | 39.72 | 1.4318 | 39.72 | 19306 | 7337 | 747492 | 2011-11-14 17:30 | 2011-11-14 20:10 | 160 | 11kV | 201056 | 2075 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN.10999 Kogarah. 11kV fdr P-11 "USL 30242" Tripped on EF EFI Field FIs Nil REMARKS: 11kV cable fault below USL 30403 tee PT.10257 Railway Paine and above AB 30501 | November | 2011 | 2012Q2 | 2012 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | UG | Not Veg | 2011-11-14 | N | 96.8945 | N | 13 | N | N | 1.1101 | 39.4971 | 146925.7947
| ZN2635:PA51 | 251 | 1141.1295 | 39.83 | 4.5463 | 39.83 | 20127 | 16165 | 747563 | 2011-11-14 21:50 | 2011-11-14 22:46 | 56 | 11kV | 29288 | 523 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S15014 Mona Vale: 11kV feeder Pnl 18 "Whitney Samuel" Tripped on: Signals:11kV trip Relays: A,B,C phase O/C Dop patrolled no cause ascertained, next available L/men to patrol during daylight hours | November | 2011 | 2012Q2 | 2012 | ZN15014:PA18 | ZN15014:PA18 | ZN15014/000018 | NORTHERN BEACHES | OH | Veg | 2011-11-14 | N | 56 | N | 13 | N | N | 1.1101 | 39.4971 | 21402.8066
| ZN2635:PA52 | 1372 | 952.0005 | 31.11 | 0.69388 | 31.11 | 19439 | 8567 | 747731 | 2011-11-14 21:47 | 2011-11-14 23:15 | 88 | 11kV | 9497 | 536 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At rec No23609 Rickard Veronia Tripped and Reclosed At PT15857 Carefree Rd centre phase dropper failure Tx end Section of 11kV feeder ex S15001 Narrabeen panel No4 "Collaroy Feeder" Put in LV// by Dop | November | 2011 | 2012Q2 | 2012 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Not Veg | 2011-11-14 | N | 17.7183 | N | 13 | N | N | 1.1101 | 39.4971 | 6940.1275
| ZN2635:PA53 | 2 | 1404.0031 | #N/A | 702.0015 | 39.4971 | 18923 | 3316 | 747595 | 2011-11-14 23:14 | 2011-11-15 00:18 | 64 | 11kV | 3520 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | West Gosford Zone Pnl.1 - REC44604 tripped / reclosed / tripped on : O/C Patrolled - nothing found | November | 2011 | 2012Q2 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2011-11-14 | N | 64 | N | 13 | N | N | 1.1101 | 39.4971 | 2572.3122
| ZN2635:PA55 | 2184 | 1252.1854 | 38.17 | 0.57334 | 38.17 | 19784 | 12666 | 747594 | 2011-11-14 22:45 | 2011-11-15 01:42 | 177 | 11kV | 3885 | 103 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | S.14483 Gallipoli Memorial Club interrupted by Dop from 11kV links 40871 to allow tree branch touching HV wires to be cut by OH mains. | November | 2011 | 2012Q2 | 2012 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Veg | 2011-11-14 | N | 37.7184 | N | 13 | N | N | 1.1101 | 39.4971 | 2839.0434
| ZN2635:PA57 | 1071 | 853.3928 | 42.59 | 0.79682 | 42.59 | 20212 | 17145 | 747543 | 2011-11-14 19:20 | 2011-11-15 01:55 | 395 | 11kV | 395 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID No. 118430/01; Fuse size: 10 Amp; DOLF; Refer OMS 747543; Reading 250 Volts. | November | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-11-14 | N | 395 | N | 13 | N | N | 1.1101 | 39.4971 | 288.6543
| ZN2635:PA58 | 2108 | 1331.3598 | 29.84 | 0.63157 | 29.84 | 18679 | 965 | 747762 | 2011-11-15 01:50 | 2011-11-15 02:17 | 27 | 11kV | 19683 | 729 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.7 tripped on : B & C phase inst & timed O/C, Undervoltage B & C Ph TX 12 A +B, Undervoltage B & C Ph Tx 13 A +B Remarks: Cause was possum on UGOH between Sw A @ S.14935 and N/O AB433777 and N/O AB40025 | November | 2011 | 2012Q2 | 2012 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | OH | Not Veg | 2011-11-15 | N | 27 | N | 7 | N | N | 1.1101 | 39.4971 | 14383.7558
| ZN2635:PA59 | 152 | 755.7893 | 39.91 | 4.9723 | 39.91 | 20057 | 15648 | 747609 | 2011-11-15 04:09 | 2011-11-15 05:44 | 95 | 11kV | 82500 | 1137 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.690 Campsie P-30 "S.2141 Alan Cant", feeder tripped: RELAYS: A phase timed over current, Fault check, EFI SIGNALS: 11kV trip, No #4 group earth, Field EFI: S.2141, S.35760, S.8943, S.1968, S.4261 REMARKS: OG HV cable fault between SwB at S.4261 Coney Rd and SwA at S.2040 Homer St North and SwD at CP.1651 Hocking Ave and SwB at S.4049 Homer Bayview with tee to S.2350 The Walk. | November | 2011 | 2012Q2 | 2012 | ZN690:PA30 | ZN690:PA30 | ZN00690/000030 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2011-11-15 | N | 72.5594 | N | 7 | N | N | 1.1101 | 39.4971 | 60288.5667
| ZN2635:PA62 | 48 | 996.3105 | 45.03 | 20.7565 | 45.03 | 18722 | 1287 | 747895 | 2011-11-15 12:06 | 2011-11-15 12:52 | 46 | 11kV | 56258 | 1223 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Panel 15 Tripped. Cause: Branch removed form OH adjacent PT2046 Curtin Page. | November | 2011 | 2012Q2 | 2012 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2011-11-15 | N | 46 | N | 7 | N | N | 1.1101 | 39.4971 | 41111.6871
| ZN2635:PA64 | 250 | 800.1326 | 43.83 | 3.2005 | 43.83 | 18899 | 3112 | 747607 | 2011-11-15 01:59 | 2011-11-15 13:15 | 676 | 11kV | 676 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID No. 118432/01; No protection operation sub isolated to repair HV lead at trans. Refer OMS 747607. | November | 2011 | 2012Q2 | 2012 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2011-11-15 | N | 676 | N | 7 | N | N | 1.1101 | 39.4971 | 494.0009
| ZN2635:PA65 | 11 | 504.7161 | #N/A | 45.8833 | 39.4971 | 19526 | 9292 | 748038 | 2011-11-15 15:38 | 2011-11-15 18:10 | 152 | 11kV | 80515 | 1295 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Panel 21 Tripped reclosed tripped and locked out on Relays: A and C phase IOC and Timed O/C, EFI, Lockout Relay and Reclose Relay. Cause: Tree on Mains O/S29 Manor Rd Hornsby. See OMS 748458 748456 748040 748110 748038 | November | 2011 | 2012Q2 | 2012 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2011-11-15 | N | 62.1737 | N | 7 | N | N | 1.1101 | 39.4971 | 58837.9872
| 402:H785 | 1 | 0 | #N/A | 0 | 39.4971 | 20274 | 18087 | 748112 | 2011-11-15 16:04 | 2011-11-15 19:50 | 226 | 11kV | 3616 | 16 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | Unselected | N | LID 118445 ABS 26962 FOUND OPEN AFTER PREVIOUS SI 17753 HAD BEEN COMPLETED EARLIER IN THE DAY | November | 2011 | 2012Q2 | 2012 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2011-11-15 | N | 226 | N | 7 | N | N | 1.1101 | 39.4971 | 2642.4661
| 402:H786 | 2 | 0 | #N/A | 0 | 39.4971 | 19939 | 14161 | 748108 | 2011-11-15 22:57 | 2011-11-16 00:52 | 115 | 11kV | 75856 | 1154 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.9 tripped on Earth Fault & SEF Centre phase bond burnt off between AB40500 & S.13582 See OMS # 748454 748455 Excluded: 748007 | November | 2011 | 2012Q2 | 2012 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | OH | Not Veg | 2011-11-15 | N | 65.7331 | N | 7 | N | N | 1.1101 | 39.4971 | 55433.3274
| ZN12580:PA1 | 1179 | 1260.8109 | 35.23 | 1.0694 | 35.23 | 20336 | 19393 | 748230 | 2011-11-16 09:03 | 2011-11-16 12:30 | 207 | 11kV | 19213 | 189 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 118457 Refer OMS 749196 and 749194 HV mains down on Dartbrook Lane 2 Fault operations, Overcurrent Earth Fault | November | 2011 | 2012Q2 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2011-11-16 | N | 101.6561 | N | 9 | N | N | 1.1101 | 39.4971 | 14040.2937
| ZN12580:PA10 | 1671 | 1025.5517 | 32.65 | 0.61374 | 32.65 | 18640 | 652 | 748419 | 2011-11-16 13:20 | 2011-11-16 14:35 | 75.4167 | 11kV | 1357.5 | 18 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | CC1: 22-"Refer to SOp" LID No. 118461/01; Fuse size: 20 Amp; DOLF; Please patrol feeder. | November | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2011-11-16 | N | 75.4167 | N | 9 | N | N | 1.1101 | 39.4971 | 992.021
| ZN12580:PA12 | 363 | 477.0911 | 44.79 | 1.3143 | 44.79 | 19531 | 9380 | 748288 | 2011-11-16 10:23 | 2011-11-16 15:00 | 277 | 11kV | 132612 | 1591 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.9037 Miranda P-2 "Sylvania Heights" fdr tripped, reclosed, tripped and locked out on. RELAYS: B phase overcurrent, EFI, Lockout and Timming SIGNALS: 11kV trip, Zone Earth, Grp 1 TX Eth. FIELD EFIs: UGOH in Sylvania Rd nr Garnet Rd S.9531 REMARKS: Tree branch brought down 11kV OH feeder O/S 18 Kanagroo Point Rd. Linesman have repaired. | November | 2011 | 2012Q2 | 2012 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2011-11-16 | N | 83.3514 | N | 9 | N | N | 1.1101 | 39.4971 | 96908.9382
| ZN12580:PA13 | 103 | 487.7568 | 47.37 | 4.7355 | 47.37 | 19187 | 5437 | 748361 | 2011-11-16 11:44 | 2011-11-16 15:40 | 236 | 11kV | 11880 | 177 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 118459 Refer to OMS 749397 and 749398 OMS REPORT NO 748360 .FEEDER DID NOT RECLOSE DUE TO FAULTY SCADA. MAINS DOWN AT GLENRIDING RD. ISOLATED AT LINKS 40835. | November | 2011 | 2012Q2 | 2012 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2011-11-16 | N | 67.1186 | N | 9 | N | N | 1.1101 | 39.4971 | 8681.5536
| ZN12580:PA14 | 1888 | 1403.8362 | 36.85 | 0.74356 | 36.85 | 19663 | 11048 | 748558 | 2011-11-16 16:45 | 2011-11-16 18:11 | 86 | 11kV | 131762 | 1561 | HV | Animal Bird | Animal | UGOH | Unplanned | Rain Heavy | N | LID 118466 2 Fault operations, Pole Mounted RAGCB, Earth Fault BIRDS NEST ON UGOH POLE HW 87002 RESULTING IN BLOWN LA. LA NEEDS REPLACEMENT Replication swithching - refer to OMS 749405 and 749406 | November | 2011 | 2012Q2 | 2012 | 243:80081 | 243:80078 | ZN00243/080078 | LAKE MACQUARIE | OH | Not Veg | 2011-11-16 | N | 84.4087 | N | 9 | N | N | 1.1101 | 39.4971 | 96287.7833
| ZN12580:PA16 | 859 | 1167.8572 | 38.2 | 1.3596 | 38.2 | 18746 | 1565 | 748633 | 2011-11-16 19:30 | 2011-11-16 21:22 | 112 | 11kV | 103434 | 1211 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S847 Hornsby Panel 1 Tripped on B and C phase Timed O/C Cause not ascertained - Mains to patrol in daylight See OMS 749048 749049 749051 748647 | November | 2011 | 2012Q2 | 2012 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | OH | Veg | 2011-11-16 | N | 85.4121 | N | 9 | N | N | 1.1101 | 39.4971 | 75586.5164
| ZN12580:PA2 | 386 | 948.8612 | #N/A | 2.4582 | 39.4971 | 19421 | 8428 | 748656 | 2011-11-16 21:14 | 2011-11-16 21:22 | 8 | 11kV | 53696 | 6712 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Rain Light | N | Note: No further entry made, this record to stand NOTE: LV Connectivity Issues relating to Job. Waiting for Anosh & GIS corrections to rectify problem. Job is expected to be excluded and a new one entered once parallels are removed. At ZN3155 Double Bay the 1B 11KV CB has tripped on SEE SCADA LOG. ABNORMAL: No.4 TX OOS Remarks: When the No.1 FIU CB was closed the 1B transformer CB tripped. Suspected Battery Earth Issue. Mark DeLacey Notified. Auxillary Supply failed to change over to standby Supply. Related jobs: #752452, 748662, 748660, 748658, 748656 | November | 2011 | 2012Q2 | 2012 | ZN3155:PA23 | ZN3155:PA40 | ZN03155/000040 | WOOLLAHRA | Unknown | Not Veg | 2011-11-16 | N | 8 | N | 9 | N | N | 1.1101 | 39.4971 | 39239.453
| ZN12580:PA4 | 2192 | 1602.3756 | 31.23 | 0.73101 | 31.23 | 19844 | 13200 | 748432 | 2011-11-16 13:41 | 2011-11-16 22:17 | 516.1 | 11kV | 17575.25 | 90 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Electrical Storm | N | LID No. 118464/01; Trip and reclose; 1 fault operation; Pole Mounted RAGCB; Bph incoming link 3771 found burning up. RAGCB 3772 left bypassed. Refer to jobs - 118462 / 748792 and 118463 / 748808. | November | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-11-16 | N | 195.2806 | N | 9 | N | N | 1.1101 | 39.4971 | 12843.4743
| ZN12580:PA7 | 183 | 1338.528 | 46.26 | 7.3144 | 46.26 | 19529 | 9309 | 748580 | 2011-11-16 17:04 | 2011-11-16 23:44 | 400 | 11kV | 124906 | 752 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | Zn.14891 Wyong Pnl.20 tripped on B & C phase Overcurrent, EFI, Fault Check Remarks: Open Wire to bundle near pT14447 all lightning arrestors and stand offs found blown. UGOH before LK44677 found with broken stand offs and hanging only by mains Abnormal Switching: REC45070 CLOSED - AB40915 OPEN | November | 2011 | 2012Q2 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2011-11-16 | N | 166.0984 | N | 9 | N | N | 1.1101 | 39.4971 | 91277.6207
| ZN12580:PA8 | 837 | 1452.8219 | 46.08 | 1.7357 | 46.08 | 18895 | 3063 | 748686 | 2011-11-17 05:54 | 2011-11-17 08:30 | 156 | 11kV | 312 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 118470 2 x 10 A DOLF elements replaced 246 V Single Phase, Fuse size: 10 Amp | November | 2011 | 2012Q2 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2011-11-17 | N | 156 | N | 12 | N | N | 1.1101 | 39.4971 | 228.0004
| ZN2466:PA1 | 241 | 887.4128 | #N/A | 3.6822 | 39.4971 | 19156 | 4945 | 748644 | 2011-11-17 07:37 | 2011-11-17 08:49 | 72 | 11kV | 81102 | 1136 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2466 Flemington: 11kv feeder panel No.5 "Swete St" feeder tripped Relays: Timed E/F Field EFI's: At S2928 Swete St the diagram indicated only a mechanical efi installed, Dop found also an electronic efi the only one that operated was the out of service electronic. Remarks: 11kv feeder fault between S2928 Swete St(SwB) to S4023 Mary Fred (SwA) (Haz), cut out required to be extended due to HAZ RMI at S4023. NOTE SEE SEPARATE INTERRUPTION @ 0857 Frontline feeder Ex Panel No5 Related jobs: #749472, 749471, 748720, 748718, 749461 | November | 2011 | 2012Q2 | 2012 | ZN2466:PA5 | ZN2466:PA5 | ZN02466/000005 | CUMBERLAND | UG | Not Veg | 2011-11-17 | N | 71.3926 | N | 12 | N | N | 1.1101 | 39.4971 | 59266.9495
| ZN2466:PA11 | 82 | 859.1417 | #N/A | 10.4773 | 39.4971 | 20243 | 17592 | 748741 | 2011-11-17 08:23 | 2011-11-17 08:50 | 27 | 11kV | 432 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Section of Panel47 Hornsby PT2136 Arcadia Cobah 31.5A fuse found blownon road side phase. Cause: fuse fatigue See OMS 748741 750391 | November | 2011 | 2012Q2 | 2012 | ZN847:PA47 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2011-11-17 | N | 27 | N | 12 | N | N | 1.1101 | 39.4971 | 315.6929
| ZN2466:PA12 | 662 | 393.8702 | #N/A | 0.59497 | 39.4971 | 19518 | 9183 | 748712 | 2011-11-17 07:23 | 2011-11-17 08:55 | 92 | 11kV | 368 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 118471 3 x 10A DOLFs 248V, 248V, 248V | November | 2011 | 2012Q2 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2011-11-17 | N | 92 | N | 12 | N | N | 1.1101 | 39.4971 | 268.9235
| ZN2466:PA15 | 591 | 488.4997 | 31.93 | 0.82656 | 31.93 | 19933 | 14121 | 748791 | 2011-11-17 08:57 | 2011-11-17 09:20 | 23 | 11kV | 3174 | 138 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2466 Flemington: 11kV feeder panel No5 "Swete St" feeder tripped Relays: B and C phase Inst ABNORMAL: After earlier failure @ 0737 hrs Feeder S2928 to S4023 OOS failed, SWA closed @ S8718 Remarks: 11kv feeder failure from S2466 Flemington: 11kv feeder panel No5 to S2928 Swete St (Sw A) NOTE SEE SEPARATE INTERRUPTION @ 0737 hrs, this later failure to be repaired and RTS prior to extending for repairs to second fault Related jobs: #748938, 748930, 748873, 748795, 748791, 749483 | November | 2011 | 2012Q2 | 2012 | ZN2466:PA5 | ZN2466:PA5 | ZN02466/000005 | CUMBERLAND | UG | Not Veg | 2011-11-17 | N | 23 | N | 12 | N | N | 1.1101 | 39.4971 | 2319.4656
| ZN2466:PA16 | 735 | 1143.0428 | 39.14 | 1.5552 | 39.14 | 19955 | 14285 | 748957 | 2011-11-17 11:35 | 2011-11-17 12:50 | 75 | 11kV | 68567 | 1067 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills Pa3 Tripped reclosed tripped and locked out on Earth Fault - EFI - Timing and Lockout. Cause: Suspect UG fault between S4976 The Crescent Kirkham ans S8331. See OMS 750477 750479 750480 750725 750723 750730 Note: Based on customer calls suspect S5839 was in parallel with Pa3 at the time of interruption See excluded 748957/967 | November | 2011 | 2012Q2 | 2012 | ZN965:PA3 | ZN965:PA3 | ZN00965/000003 | HORNSBY | UG | Not Veg | 2011-11-17 | N | 64.2615 | N | 12 | N | N | 1.1101 | 39.4971 | 50106.7412
| ZN2466:PA17 | 3 | 173.8828 | 39.92 | 57.9609 | 39.92 | 20241 | 17557 | 748995 | 2011-11-17 12:02 | 2011-11-17 13:30 | 88 | 11kV | 176 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118477 No Cause found not storm conditions Fuse 100Amp replaced | November | 2011 | 2012Q2 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2011-11-17 | N | 88 | N | 12 | N | N | 1.1101 | 39.4971 | 128.6156
| ZN2466:PA18 | 401 | 860.8812 | #N/A | 2.1468 | 39.4971 | 19641 | 10656 | 749187 | 2011-11-17 16:17 | 2011-11-17 18:01 | 104 | 11kV | 120293 | 1202 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S847 Hornsby Panel 1 Tripped on B phase timed O/C, Earth Fault, Fault Check and EFI. Cause: UG fault from S3866 Lymoore Sefton SWD to S6267 Sefton Keith Harris Sw B. See OMS 750324 750331 750376 749190 750370 749172/187 | November | 2011 | 2012Q2 | 2012 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | UG | Not Veg | 2011-11-17 | N | 100.0774 | N | 12 | N | N | 1.1101 | 39.4971 | 87906.5764
| ZN2466:PA19 | 23 | 483.1162 | #N/A | 21.0051 | 39.4971 | 19502 | 9093 | 749219 | 2011-11-17 17:07 | 2011-11-17 18:34 | 87 | 11kV | 4429 | 51 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 3 tripped on: Earth Fault, Fault Check and EFI. Signals: 11kV trip, Tx1 Group Earth. Cause: 11kV feeder fault from S5395 to S8387. See OMS 750756 750760 749219 | November | 2011 | 2012Q2 | 2012 | ZN8000:PA3 | ZN8000:PA3 | ZN08000/000003 | RYDE | UG | Not Veg | 2011-11-17 | N | 86.8431 | N | 12 | N | N | 1.1101 | 39.4971 | 3236.5826
| ZN2466:PA2 | 139 | 1040.7112 | 59.7 | 7.4871 | 59.7 | 18601 | 253 | 749195 | 2011-11-17 16:27 | 2011-11-17 19:00 | 153 | 11kV | 153 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 118479 Volts 248 - Fuse 5 Amp replaced | November | 2011 | 2012Q2 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2011-11-17 | N | 153 | N | 12 | N | N | 1.1101 | 39.4971 | 111.8079
| ZN2466:PA20 | 760 | 1909.8099 | 40.54 | 2.5129 | 40.54 | 19056 | 4389 | 749228 | 2011-11-17 17:14 | 2011-11-17 21:15 | 241 | 11kV | 8717 | 94 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Pnl.10 @ Wamberal zone - REC 44607 Matcham North tripped / reclosed / tripped & locked out. Remarks: Span of 11kV on the ground beyond LK42162. Came into contact with 415v. EMSO has checked all services OK | November | 2011 | 2012Q2 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2011-11-17 | N | 92.734 | N | 12 | N | N | 1.1101 | 39.4971 | 6370.1265
| ZN2466:PA21 | 8 | 207.0312 | 61.59 | 25.8789 | 61.59 | 19871 | 13493 | 749277 | 2011-11-17 19:48 | 2011-11-17 22:13 | 145 | 11kV | 290 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Blown fuse on sub 51124, as advised by customer, assuming start and end times are correct, Note this event is not supported by LID documentation | November | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-11-17 | N | 145 | N | 12 | N | N | 1.1101 | 39.4971 | 211.9234
| ZN2466:PA22 | 19 | 291.7253 | #N/A | 15.354 | 39.4971 | 19088 | 4562 | 749299 | 2011-11-18 05:15 | 2011-11-18 07:05 | 110 | 11kV | 440 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 118480 A Phase DOLF : 10Amp Possum on pole | November | 2011 | 2012Q2 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2011-11-18 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 321.539
| ZN2466:PA4 | 33 | 341.7866 | 40.34 | 10.3572 | 40.34 | 18754 | 1633 | 749319 | 2011-11-18 07:50 | 2011-11-18 09:55 | 125 | 11kV | 250 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | No LID - HV Sub fuse replaced. | November | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-11-18 | N | 125 | N | 6 | N | N | 1.1101 | 39.4971 | 182.6926
| ZN2466:PA5 | 1694 | 1492.924 | 36.29 | 0.8813 | 36.29 | 20422 | 20257 | 749526 | 2011-11-18 12:40 | 2011-11-18 15:30 | 170 | 11kV | 21986 | 133 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of 11kV ex Pnl.16L Erina Zn - from LK41267 via N/O AB4186 to LB40403 and LK42682 (Avoca Zone) - interrupted by DOp. Cracked insulators on normally open AB41286 and 1000V measured on pole. Interrupted to allow line crew to bare back bonds. | November | 2011 | 2012Q2 | 2012 | ZN12580:PA16 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2011-11-18 | N | 165.3083 | N | 6 | N | N | 1.1101 | 39.4971 | 16066.7203
| ZN2466:PA6 | 37 | 1133.2856 | 41.52 | 30.6293 | 41.52 | 19326 | 7511 | 749644 | 2011-11-18 16:49 | 2011-11-18 18:46 | 117 | 11kV | 351 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | No LID Found | November | 2011 | 2012Q2 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2011-11-18 | N | 117 | N | 6 | N | N | 1.1101 | 39.4971 | 256.5004
| ZN2466:PA7 | 298 | 1236.6522 | 56.55 | 4.1498 | 56.55 | 19572 | 9679 | 750673 | 2011-11-18 23:00 | 2011-11-19 01:30 | 150 | 11kV | 2400 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118486 A Phase DOLF : 10Amp | November | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-11-18 | N | 150 | N | 6 | N | N | 1.1101 | 39.4971 | 1753.8492
| ZN35370:PA10 | 584 | 1124.362 | 45.97 | 1.9253 | 45.97 | 19993 | 14905 | 749730 | 2011-11-19 06:51 | 2011-11-19 08:05 | 74 | 11kV | 89096 | 1204 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12610 long Jetty Pnl.24 tripped on : B Phase IOC, EFI, Fault Check Front Line feeder fault | November | 2011 | 2012Q2 | 2012 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | UG | Not Veg | 2011-11-19 | N | 74 | N | 7 | N | N | 1.1101 | 39.4971 | 65108.7289
| ZN35370:PA2 | 374 | 744.1884 | 32.31 | 1.9898 | 32.31 | 18827 | 2353 | 749731 | 2011-11-19 06:58 | 2011-11-19 09:05 | 127 | 11kV | 508 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118489 A Phase DOLF: 10Amp Excluded OMS 749731 OMS 750674 | November | 2011 | 2012Q2 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2011-11-19 | N | 127 | N | 7 | N | N | 1.1101 | 39.4971 | 371.2314
| ZN35370:PA4 | 774 | 982.009 | 37.27 | 1.2687 | 37.27 | 20222 | 17274 | 749702 | 2011-11-18 21:01 | 2011-11-19 13:00 | 959.1167 | 11kV | 333772.6 | 348 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | 18/11/11 22:31 T39745: NOTE DUE TO WATER TRANSPORT REQUIRED EA STAFF TO INVESTIGATE 1st AM ,STAFF SAFETY . AT THIS STAGE ISOLATED ON MAINLAND ONLYl 18/11/11 21:03 CASS: Job referred by T31745 in CASS UGOH connections where report of explosion was, were taken apart and checked thenremade. No fault found. Restored successfully | November | 2011 | 2012Q2 | 2012 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | Unknown | Unknown | 2011-11-18 | N | 959.1167 | N | 6 | N | N | 1.1101 | 39.4971 | 243911.1715
| ZN35370:PA8 | 736 | 925.4867 | 32.16 | 1.2575 | 32.16 | 19682 | 11356 | 749857 | 2011-11-19 09:25 | 2011-11-19 13:10 | 225 | 11kV | 225 | 1 | HV | Customer Installation Fault | Customer Installation | DC Not Transformer | Unplanned | Unselected | N | At S5201 Sydney Cricket Club: "Paddington Fdr" tripped B ph o/c Customer had fault on own equipmnet. At S342 Paddington on Panel #28 "Sydney Cricket Ground Fdr" EFI - # tx group earth Remarks: Customer switchgear fault Related jobs: #750750, 749857 | November | 2011 | 2012Q2 | 2012 |  |  |  |  | Unknown | Unknown | 2011-11-19 | N | 225 | N | 7 | N | N | 1.1101 | 39.4971 | 164.4234
| 221:11893 | 1172 | 726.5495 | 31.1 | 0.61992 | 31.1 | 19661 | 11029 | 749781 | 2011-11-19 09:40 | 2011-11-19 13:15 | 215 | 11kV | 1075 | 5 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 118491 B Phase DOLF : 10Amp Excluded OMS 749781 OMS 750685 | November | 2011 | 2012Q2 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2011-11-19 | N | 215 | N | 7 | N | N | 1.1101 | 39.4971 | 785.5783
| 221:11894 | 928 | 741.5666 | 39.84 | 0.7991 | 39.84 | 19924 | 14044 | 749822 | 2011-11-19 11:22 | 2011-11-19 13:30 | 128.4167 | 11kV | 19929.4167 | 272 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 1126 Mona Vale Rd ex Panel 10 "terrey Hills" Fdr tripped, reclosed, tripped and locked out. Phase of 11kV near Wattle Rd down | November | 2011 | 2012Q2 | 2012 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2011-11-19 | N | 73.2699 | N | 7 | N | N | 1.1101 | 39.4971 | 14563.8299
| 221:11895 | 977 | 804.3633 | 42.94 | 0.8233 | 42.94 | 18758 | 1731 | 749907 | 2011-11-19 16:02 | 2011-11-19 16:41 | 39 | 11kV | 35022 | 898 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | At ZN.10994 Mortdale P-19L "USL 30746 etc" has tripped SIGNALS: 11kV Trip RELAYS: 51, B & C REMARKS: Large branch into fdr outside 60 Lugarno Pde, Lugarno | November | 2011 | 2012Q2 | 2012 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Veg | 2011-11-19 | N | 39 | N | 7 | N | N | 1.1101 | 39.4971 | 25593.0446
| 221:11897 | 889 | 1301.4221 | 38.19 | 1.4639 | 38.19 | 19522 | 9197 | 749897 | 2011-11-19 15:43 | 2011-11-19 18:18 | 155 | 11kV | 155 | 1 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | LID 118495 B Phase DOLF : 10Amp Possum found beneath sub. Volts: Aph-245V, Bph-246V, Cph-248V. Excluded OMS 749897 OMS 750719 | November | 2011 | 2012Q2 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2011-11-19 | N | 155 | N | 7 | N | N | 1.1101 | 39.4971 | 113.2694
| 221:11898 | 400 | 1078.3076 | 52.77 | 2.6958 | 52.77 | 19510 | 9138 | 750026 | 2011-11-20 11:54 | 2011-11-20 12:39 | 44.65 | 11kV | 39745.1333 | 1168 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 42 tripped on 11kV trip, A and B phase timed O/C Cause: Branch on HV mains Outside 36 Wesson RD West Pennant Hills See OMS 750026 750028 | November | 2011 | 2012Q2 | 2012 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Veg | 2011-11-20 | N | 34.0284 | N | 5 | N | N | 1.1101 | 39.4971 | 29044.5712
| 221:11899 | 1339 | 1104.4865 | 37.32 | 0.82486 | 37.32 | 19826 | 13003 | 749997 | 2011-11-20 09:36 | 2011-11-20 13:20 | 224 | 11kV | 224510 | 1588 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At 129 Hunters Hill Panel 10 tripped on Earth Fault, Fault Check and EFI. Alarms: 11kV trip, Zone Earth and Tx1 Group Earth. Cause: Suspect UG cable fault UGOH to S5070. Reports of strong smell of GAS near Cnr of Arnold and Frederick - Appears recent excavation in area. See OMS 750825/833/834/836 | November | 2011 | 2012Q2 | 2012 | ZN129:PA10 | ZN129:PA49 | ZN00129/000049 | RYDE | UG | Not Veg | 2011-11-20 | N | 141.3791 | N | 5 | N | N | 1.1101 | 39.4971 | 164065.2861
| 221:11900 | 1109 | 724.7769 | 30.63 | 0.65354 | 30.63 | 19446 | 8610 | 750057 | 2011-11-20 13:39 | 2011-11-20 15:16 | 97.8833 | 11kV | 10406.1667 | 107 | HV | Overload | Utility Process Issue | Fuse | Unplanned | Hot >35C | N | LID 118504 C Phase DOLF : 40Amps Replaced blown DOLF. As left 240A, 130A & 100A, 240V. OMS No's 750057, 750065 & 750074. | November | 2011 | 2012Q2 | 2012 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2011-11-20 | N | 97.2539 | N | 5 | N | N | 1.1101 | 39.4971 | 7604.5197
| ZN5868:PA10 | 289 | 708.0389 | 55.21 | 2.45 | 55.21 | 18650 | 725 | 750037 | 2011-11-20 12:20 | 2011-11-20 20:55 | 515 | 11kV | 24584.3333 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | S8729 dist 2 A phase 400 AMP Cause not ascertained ( reports of wires down CNR of Waters and Reynolds) | November | 2011 | 2012Q2 | 2012 | ZN180:PA19 | ZN180:PA19 | ZN00180/000019 | NORTH SYDNEY | OH | Not Veg | 2011-11-20 | N | 229.7601 | N | 5 | N | N | 1.1101 | 39.4971 | 17965.5057
| ZN5868:PA13 | 824 | 832.0354 | #N/A | 1.0098 | 39.4971 | 19841 | 13155 | 750109 | 2011-11-20 18:12 | 2011-11-21 | 348 | 11kV | 348 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 118509 A Phase Sub isolated to repair burnt off ll clamp lead. Excluded OMS 750109 (residence) OMS 750779 | November | 2011 | 2012Q2 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2011-11-20 | N | 348 | N | 5 | N | N | 1.1101 | 39.4971 | 254.3081
| ZN5868:PA14 | 1918 | 1458.8609 | 42.36 | 0.76062 | 42.36 | 20199 | 16947 | 750157 | 2011-11-21 07:10 | 2011-11-21 10:50 | 220 | 11kV | 220 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 118520 Single phase LLC vibrated off. Excluded oms 750157/750211 OMS 750822 | November | 2011 | 2012Q2 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2011-11-21 | N | 220 | N | 3 | N | N | 1.1101 | 39.4971 | 160.7695
| ZN5868:PA15 | 31 | 1196.1025 | #N/A | 38.584 | 39.4971 | 19956 | 14315 | 750482 | 2011-11-21 14:55 | 2011-11-21 16:25 | 90 | 11kV | 180 | 2 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 118525 A Phase DORF : 10Amp 255V, 5A. Dead magpie found. Excluded OMS 750482 OMS 750799 | November | 2011 | 2012Q2 | 2012 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2011-11-21 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
| ZN5868:PA17 | 245 | 892.0264 | 45.78 | 3.6409 | 45.78 | 19533 | 9383 | 750579 | 2011-11-21 17:30 | 2011-11-21 18:43 | 73 | 11kV | 56291 | 1643 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At ZN.9037 Miranda P-8 "Alkaringa Rd" fdr tripped & reclosed on. RELAYS: C phase inst, EF, Lockout, Timing SIGNALS: 11kV trip, Zone Earth, TX.1 Grp Eth, REMARKS: Centre phase bond burnt off AB 35655 on ZN side | November | 2011 | 2012Q2 | 2012 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2011-11-21 | N | 34.2611 | N | 3 | N | N | 1.1101 | 39.4971 | 41135.8025
| ZN5868:PA2 | 255 | 795.0739 | 53.8 | 3.1179 | 53.8 | 19097 | 4620 | 750635 | 2011-11-22 00:28 | 2011-11-22 03:00 | 152 | 11kV | 9576 | 63 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | PT.12941 Davis Wilma - 11kV centre phase HDO failed centre phase HV bushing has a large piece of procelain missing. PT found with centre phase HDO blown. Isolated and restored via LV // | November | 2011 | 2012Q2 | 2012 | ZN12570:PA18 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2011-11-22 | N | 152 | N | 6 | N | N | 1.1101 | 39.4971 | 6997.8584
| ZN5868:PA21 | 4 | 283.7382 | #N/A | 70.9345 | 39.4971 | 19129 | 4842 | 750643 | 2011-11-22 03:26 | 2011-11-22 05:49 | 143 | 11kV | 101181 | 846 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn.12600 Lisarow Pnl.13 tripped / reclosed / tripped & locked out on: A + B Phase O/C, reclose, timer, lockout Cause not ascertained - linesman to patrol in daylight | November | 2011 | 2012Q2 | 2012 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2011-11-22 | N | 119.5993 | N | 6 | N | N | 1.1101 | 39.4971 | 73940.0905
| ZN5868:PA22 | 686 | 1142.0654 | #N/A | 1.6648 | 39.4971 | 19561 | 9638 | 750890 | 2011-11-22 12:41 | 2011-11-22 13:18 | 37 | 11kV | 1554 | 42 | HV | 3rd Party Vehicle | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | LID 118537 Truck hit operating handle & opened ABS 42575. Closed Sw 39928 to restore supply. Excluded OMS Jobs 750890, 750892, 750894, 750896 & 750902. OMS 751210 | November | 2011 | 2012Q2 | 2012 | 205:12203 | 205:12203 | ZN00205/012203 | NEWCASTLE | OH | Not Veg | 2011-11-22 | N | 37 | N | 6 | N | N | 1.1101 | 39.4971 | 1135.6174
| ZN5868:PA23 | 1003 | 2297.8174 | 41.88 | 2.2909 | 41.88 | 19406 | 8353 | 750992 | 2011-11-22 15:45 | 2011-11-22 16:55 | 70 | 11kV | 5110 | 73 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.13737 James Peel - 11kV footpath phase HDO operated. Fuses were replced earlier in the day during routine maintenance. Possible bad batch. | November | 2011 | 2012Q2 | 2012 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2011-11-22 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 3734.2373
| ZN5868:PA24 | 72 | 2065.7899 | #N/A | 28.6915 | 39.4971 | 19748 | 12420 | 751027 | 2011-11-22 16:48 | 2011-11-22 18:19 | 91 | 11kV | 63049 | 1063 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118541 1 fault operation Instantaneous Overcurrent, Earth fault Leg 1 protection operation. Fdr sectionalised no fault found. Please investigate. Excluded OMS 751027, 751030, 751034, 751044 OMS 751303, 751304, 751306, 751310 | November | 2011 | 2012Q2 | 2012 | 202:34259 | 202:34240 | ZN00202/034240 | NEWCASTLE | OH | Veg | 2011-11-22 | N | 59.3123 | N | 6 | N | N | 1.1101 | 39.4971 | 46074.3496
| ZN5868:PA25 | 76 | 1034.4775 | 45.29 | 13.6115 | 45.29 | 18691 | 1061 | 751075 | 2011-11-22 19:09 | 2011-11-22 21:55 | 166 | 11kV | 168015 | 2914 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At Zn80 Chatswood Panel 32 tripped on B and Cphase O/C Cause: Bond burnt off tee to S2385 Greenwich Hospital. See OMS 751324326/329/1085 751075/080/082 | November | 2011 | 2012Q2 | 2012 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Not Veg | 2011-11-22 | N | 57.6579 | N | 6 | N | N | 1.1101 | 39.4971 | 122780.4064
| ZN5868:PA28 | 45 | 124.0783 | 62.35 | 2.7573 | 62.35 | 20308 | 19038 | 751115 | 2011-11-23 00:19 | 2011-11-23 02:05 | 106 | 11kV | 179469 | 1888 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Zn.12570 Avoca Pnl.15 tripped on: SE, lockout Burnt Bond at AB 44119 See OMS # 751209 751211 751212 751215 Excluded: 75116 75115 | November | 2011 | 2012Q2 | 2012 | ZN12570:PA15 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2011-11-23 | N | 95.0577 | N | 4 | N | N | 1.1101 | 39.4971 | 131150.6518
| ZN5868:PA3 | 12 | 69.8676 | #N/A | 5.8223 | 39.4971 | 19613 | 10334 | 751535 | 2011-11-23 08:57 | 2011-11-23 19:15 | 618 | 11kV | 50029 | 1249 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn195 Pymble section of 11kV feeder from Ab1710 to LB2593 was interrupted by Tree which brough down 11kV Mains. At Zn195 Pymble panel 9 was interrupted by Dop. Tree brough down 11kV mains. See OMS 752216 752215 752214 751535/540/541/542 | November | 2011 | 2012Q2 | 2012 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Veg | 2011-11-23 | N | 40.0552 | N | 4 | N | N | 1.1101 | 39.4971 | 36559.7176
| ZN5868:PA30 | 1735 | 1626.9228 | 36.69 | 0.93771 | 36.69 | 19034 | 4265 | 751581 | 2011-11-23 17:48 | 2011-11-23 22:54 | 306 | 11kV | 30528 | 318 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID 118549 2 fault operations 3 phase Tree accross OHM at pole GV-70037. Excluded OMS 751581, 751584, 751586, 751606, 751611 OMS 751 749, 751751 | November | 2011 | 2012Q2 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2011-11-23 | N | 96 | N | 4 | N | N | 1.1101 | 39.4971 | 22308.962
| ZN5868:PA5 | 825 | 807.7211 | 39.94 | 0.97906 | 39.94 | 20077 | 15848 | 751627 | 2011-11-23 20:09 | 2011-11-24 04:18 | 489 | 11kV | 16137 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 118550 3 fault operation A Phase Overcurrent Mains down near sub 71715. Excluded OMS # 751627 (start time) OMS 751670 | November | 2011 | 2012Q2 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2011-11-23 | N | 489 | N | 4 | N | N | 1.1101 | 39.4971 | 11792.4436
| ZN5868:PA6 | 1104 | 1125.2529 | 43.77 | 1.0193 | 43.77 | 19061 | 4408 | 751666 | 2011-11-24 07:37 | 2011-11-24 12:55 | 318 | 11kV | 57240 | 180 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 118551 3 fault operations A & B Phase Fallen tree hit mains past RAGCB 13642 Field staff had trouble closing RAGCB 13642 Excluded OMS 751666,751774, 751841 OMS 752154 | November | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-11-24 | N | 318 | N | 2 | N | N | 1.1101 | 39.4971 | 41829.3037
| ZN5868:PA7 | 209 | 541.8662 | #N/A | 2.5927 | 39.4971 | 20407 | 20194 | 752109 | 2011-11-24 21:15 | 2011-11-24 23:00 | 105 | 11kV | 187446 | 2047 | HV | Animal Possum | Animal | UGOH | Unplanned | Rain Light | N | aT s.15003 Balgowlah, Panel 10 Fdr CB tripped on A phase IOC and timed OC, frame leakage, efi. Possum damaged UG/OH to S.15852. Bond to L/A burnt off | November | 2011 | 2012Q2 | 2012 | ZN15003:PA10 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2011-11-24 | N | 91.5711 | N | 2 | N | N | 1.1101 | 39.4971 | 136980.0081
| ZN8100:PA1 | 194 | 195.0113 | #N/A | 1.0052 | 39.4971 | 20014 | 15054 | 752124 | 2011-11-25 02:29 | 2011-11-25 03:35 | 66 | 11kV | 86614 | 1571 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Panel 18 tripped reclosed tripped and locked out on A and C phase Tree on 11kV Mains See OMS 752165 752169 752124 | November | 2011 | 2012Q2 | 2012 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2011-11-25 | N | 55.133 | N | 5 | N | N | 1.1101 | 39.4971 | 63294.9565
| ZN8100:PA10 | 338 | 756.9469 | 45.82 | 2.2395 | 45.82 | 19159 | 5007 | 752126 | 2011-11-25 05:19 | 2011-11-25 07:07 | 107.6 | 11kV | 2103.6167 | 2005 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Rain Light | N | At ZN.10990 Arncliffe P-2 'S.10957 Darling Hirst' fdr tripped & reclosed on: RELAYS: C phase IOC, Timing & LO EFIs: Defective SIGNALS: 11kV Trip REMARKS: Not ascertained. Possible large birds in the area at time of the interruption. | November | 2011 | 2012Q2 | 2012 | ZN10990:PA2 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Not Veg | 2011-11-25 | N | 1.0492 | N | 5 | N | N | 1.1101 | 39.4971 | 1537.261
| ZN8100:PA12 | 1264 | 1199.6582 | 45.82 | 0.9491 | 45.82 | 20182 | 16730 | 752247 | 2011-11-25 09:20 | 2011-11-25 09:45 | 25 | 11kV | 175 | 7 | HV | Vandalism | 3rd Party Impact | DC Not Transformer | Unplanned | Rain Light | N | LID 118553 Outage to replace stolen sub earths Excluded OMS 752247 OMS 753537 | November | 2011 | 2012Q2 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | Unknown | Not Veg | 2011-11-25 | N | 25 | N | 5 | N | N | 1.1101 | 39.4971 | 127.8848
| ZN8100:PA17 | 232 | 1067.4996 | #N/A | 4.6013 | 39.4971 | 19305 | 7333 | 752142 | 2011-11-25 06:57 | 2011-11-25 10:58 | 241 | 11kV | 101133.3 | 1204 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | At ZN.9252 Jannali , P-12 "S.9823 Victoria Mitchell" Fdr tripped, closed and tripped: RELAYS: C & B phase (leakage) phase and Timed O/C, lockout, timing relay FIELD EFIs: Nil REMARKS: Defective AB 35559. LV// 1706, 717, 23123, 500 & 1631 | November | 2011 | 2012Q2 | 2012 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2011-11-25 | N | 83.9978 | N | 5 | N | N | 1.1101 | 39.4971 | 73905.2327
| ZN8100:PA19 | 156 | 431.6568 | #N/A | 2.767 | 39.4971 | 19500 | 9088 | 752300 | 2011-11-25 10:31 | 2011-11-25 15:00 | 269 | 11kV | 164568 | 1279 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Zn.12690 Berkeley Vale Pnl.12 tripped / reclosed / tripped & locked out on: Timed Overcurrent, reclose relay, EFI Car into pole at 77 Pollock Ave Wyoing. 11kV mains down and inot LV mains. Section of 11kV from LB41055 to S.18367 tee PT13538 See OMS # 753459 753461 753464 753466 753463 753471 Excluded: 752300 | November | 2011 | 2012Q2 | 2012 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2011-11-25 | N | 128.6693 | N | 5 | N | N | 1.1101 | 39.4971 | 120261.4405
| ZN8100:PA2 | 212 | 672.0015 | 58.87 | 3.1698 | 58.87 | 19386 | 8149 | 752779 | 2011-11-26 08:39 | 2011-11-26 13:20 | 281 | 11kV | 15174 | 54 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 118559 6 fault operations single phase Branch across mains at Pole MN-83948. Sw 42090 initially locked out. It was retried when staff arrived and held in. % minutes later it tripped and locked out again. Trees were then found on mains. Excluded OMS #: 752779 OMS 753755 | November | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-11-26 | N | 281 | N | 3 | N | N | 1.1101 | 39.4971 | 11088.7116
| ZN8100:PA20 | 783 | 1078.38 | 46.82 | 1.3772 | 46.82 | 18970 | 3592 | 752979 | 2011-11-26 11:55 | 2011-11-26 15:50 | 235 | 11kV | 13865 | 59 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | TUGGERAH BUSINESS PARK PTY LTD 1711959 POLE WY1394 LOCATED AT REAR OF SUPERCENTRE OPPOSITE DOCK 3 SPARKING/ARCING - PART SUPPLY TO SUPER CENTRE -CONTACT IS PAUL Burnt bond on pole near LB 46518 No blue form to support outage | November | 2011 | 2012Q2 | 2012 | ZN12690:PA17 | ZN12690:PA17 | ZN12690/000017 | CENTRAL COAST | OH | Not Veg | 2011-11-26 | N | 235 | N | 3 | N | N | 1.1101 | 39.4971 | 10132.1331
| ZN8100:PA22 | 324 | 837.3342 | 56.98 | 2.5844 | 56.98 | 19862 | 13404 | 753112 | 2011-11-26 22:50 | 2011-11-27 01:05 | 135 | 11kV | 7020 | 52 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 118562 33kV Conductors and insulators at Pole HR-80482 damaged by lightning strike. Isolation of 11kV and 33kV to repair. | November | 2011 | 2012Q2 | 2012 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2011-11-26 | N | 135 | N | 3 | N | N | 1.1101 | 39.4971 | 5130.0089
| ZN8100:PA28 | 450 | 914.9086 | 47.97 | 2.0331 | 47.97 | 19897 | 13724 | 753194 | 2011-11-27 02:39 | 2011-11-27 06:40 | 241 | 11kV | 179656 | 1386 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 118563 4 fault operations Earth fault Fdr CB 61 Broadmeadow triped once on fault during fault finding Excluded oms 753194 see outage 118564 OMS 753693, 753694, 753695, 753699, 753701, 753703, 753704, 753709, 753712 | November | 2011 | 2012Q2 | 2012 | 203:8084 | 204:82689 | ZN00204/082689 | NEWCASTLE | UG | Not Veg | 2011-11-27 | N | 129.6219 | N | 6 | N | N | 1.1101 | 39.4971 | 131287.3058
| ZN8100:PA30 | 1311 | 2624.1153 | 44.74 | 2.0016 | 44.74 | 19273 | 6976 | 753242 | 2011-11-27 10:00 | 2011-11-27 11:04 | 63.8667 | 11kV | 111659.2 | 1902 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.10994 Mortdale, P-49 "Letita Frederick" fdr tripped, closed & tripped locked out on: RELAYS: C phase overcurrent, Timing relay, Lockout relay SIGNALS: 11kV trip REMARKS: Large branch on 11kV 219 Queens Rd Connells Point | November | 2011 | 2012Q2 | 2012 | ZN10994:PA49 | ZN10994:PA7 | ZN10994/000007 | GEORGES RIVER | OH | Veg | 2011-11-27 | N | 58.7062 | N | 6 | N | N | 1.1101 | 39.4971 | 81597.25
| ZN8100:PA31 | 571 | 1221.0351 | 53.73 | 2.1384 | 53.73 | 20000 | 14933 | 753255 | 2011-11-27 10:16 | 2011-11-27 11:49 | 93 | 11kV | 77646 | 838 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Zn847 Hornsby Panel 74 tripped reclosed tripped and locke dout on Timed O/C, EFI lockout and Timing relays. Signals: 11kV Trip. Cause: Feeder patrolled by DOp Cause not ascertained. See OMS 753486 753488 753489 7536255 753259 | November | 2011 | 2012Q2 | 2012 | ZN847:PA47 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2011-11-27 | N | 92.6563 | N | 6 | N | N | 1.1101 | 39.4971 | 56741.4066
| ZN8100:PA33 | 757 | 589.0801 | 48.7 | 0.77818 | 48.7 | 20133 | 16190 | 753340 | 2011-11-27 15:15 | 2011-11-27 17:00 | 105 | 11kV | 1995 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 118572 3 fault operations Overcurrent Tree across OHM near pole KQ-80046. Boat required to access pole. Excluded OMS 753340 OMS 753515 | November | 2011 | 2012Q2 | 2012 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2011-11-27 | N | 105 | N | 6 | N | N | 1.1101 | 39.4971 | 1457.8872
| ZN8100:PA34 | 49 | 700.181 | 45.43 | 14.2894 | 45.43 | 18833 | 2372 | 753359 | 2011-11-27 16:54 | 2011-11-27 19:29 | 155.85 | 11kV | 97635.9667 | 1169 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 118573 2 fault operations Overcurrent, Earth fault Blown L/A at UGOH pole to sub 57869. | November | 2011 | 2012Q2 | 2012 | 238:34147 | 532:83301 | ZN00532/083301 | MAITLAND | Unknown | Unknown | 2011-11-27 | N | 83.5209 | N | 6 | N | N | 1.1101 | 39.4971 | 71349.4847
| ZN8100:PA37 | 174 | 419.0853 | #N/A | 2.4085 | 39.4971 | 19335 | 7559 | 753387 | 2011-11-27 19:36 | 2011-11-27 20:49 | 73 | 11kV | 14256 | 282 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.22 tripped on: Earth Fulth Trip , EFI Field EFIs: S.18333 18097 18184 18667 18532 18180 18411 18794 11kV underground cable fault between Sw A @ S.14794 and Sw B S.14959 | November | 2011 | 2012Q2 | 2012 | ZN12690:PA22 | ZN12690:PA22 | ZN12690/000022 | CENTRAL COAST | UG | Not Veg | 2011-11-27 | N | 50.5532 | N | 6 | N | N | 1.1101 | 39.4971 | 10417.8643
| ZN8100:PA38 | 1810 | 1835.3215 | 45.99 | 1.014 | 45.99 | 19790 | 12694 | 753439 | 2011-11-28 07:40 | 2011-11-28 08:30 | 50 | 11kV | 400 | 8 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | S.18020 Wisemans Inghams - Both Supplies low volts due to switching across panel 3 and 5 from Peats Ridge zone. Involved TCAT 46991 being on neutral tap resulting in low volts @ S.18020. TCAT restored auto on completion of switching | November | 2011 | 2012Q2 | 2012 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | UG | Not Veg | 2011-11-28 | N | 50 | N | 9 | N | N | 1.1101 | 39.4971 | 292.3082
| ZN8100:PA39 | 1199 | 1327.3076 | 45.83 | 1.107 | 45.83 | 19728 | 12034 | 753547 | 2011-11-28 09:26 | 2011-11-28 10:11 | 45 | 11kV | 79110 | 1758 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ S.1068 Lidcombe panel 26 the "Hargrave Hel" feeder tripped on- Relays - Earth Fault, EFI Signals - 11kv trip, TX 1 Group Earth Remarks: 11kv feeder fault from S.1068 Lidcombe panel 26 to S.2909 Hargrave hel. Note S.2909 is Hazemyer and cut out will have to be extended Related jobs: #753547, 754139 | November | 2011 | 2012Q2 | 2012 | ZN1068:PA26 | ZN1068:PA26 | ZN01068/000026 | CUMBERLAND | UG | Not Veg | 2011-11-28 | N | 45 | N | 9 | N | N | 1.1101 | 39.4971 | 57811.2547
| ZN8100:PA4 | 855 | 1901.5627 | 42.79 | 2.224 | 42.79 | 19814 | 12899 | 753467 | 2011-11-28 10:29 | 2011-11-28 10:58 | 29 | 11kV | 22997 | 793 | HV | Overload Operational | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Peats Ridge Zone Pnl.3 - REC 46992 Goolara Holy Cross tripped & locked out on: A Phase Overcurrent Overload through recloser 46992 due to switching for D/R # 280636 | November | 2011 | 2012Q2 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2011-11-28 | N | 29 | N | 9 | N | N | 1.1101 | 39.4971 | 16805.5293
| ZN8100:PA7 | 378 | 1727.7065 | 43.68 | 4.5707 | 43.68 | 19932 | 14110 | 753576 | 2011-11-28 09:59 | 2011-11-28 11:02 | 63 | 11kV | 165186 | 2622 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 118578 & 118579 Car hit pole NB-10272. Feeder abnormally switched for SI 18058. Reclose Function switched off for SI. Also see reports 118578/9. Excluded OMS 753576, 753579, 753581, 753601, 753685, 755187, 755203, 755215. OMS 756813 | November | 2011 | 2012Q2 | 2012 | 232:33411 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Not Veg | 2011-11-28 | N | 63 | N | 9 | N | N | 1.1101 | 39.4971 | 120713.0566
| ZN8100:PA9 | 96 | 621.7271 | #N/A | 6.4763 | 39.4971 | 18855 | 2592 | 753458 | 2011-11-28 08:10 | 2011-11-28 11:35 | 205 | 11kV | 1025 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT.15774 the footpath fuse failed due to fatigue | November | 2011 | 2012Q2 | 2012 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2011-11-28 | N | 205 | N | 9 | N | N | 1.1101 | 39.4971 | 749.0398
| ZN1285:PA10 | 858 | 2054.2173 | #N/A | 2.3942 | 39.4971 | 19081 | 4515 | 753591 | 2011-11-28 10:05 | 2011-11-28 13:50 | 225 | 11kV | 248961.5 | 1633 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn3425 Castle Cove Panel 12 tripped reclosed tripped and locked out on Overcurrent and Earth Fault, reclose, Lockout and Timing Relays. Suspect UG cable fault to tee S554 Glencroft Ave. See OMS 754213 754214 | November | 2011 | 2012Q2 | 2012 | ZN3425:PA12 | ZN3425:PA12 | ZN03425/000012 | KU-RING-GAI | UG | Not Veg | 2011-11-28 | N | 152.4565 | N | 9 | N | N | 1.1101 | 39.4971 | 181933.7211
| ZN1285:PA17 | 1579 | 2107.4191 | 47.11 | 1.3347 | 47.11 | 20246 | 17742 | 753584 | 2011-11-28 10:06 | 2011-11-28 15:04 | 298 | 11kV | 127974 | 1953 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | At ZN.9700 Kirrawee, P-11 the "Flora Bath" 11kV feeder, tripped, reclosed, tripped & locked out on: RELAYS: Lockout, timing, A & C phase Inst & Timed O/C SIGNALS: 11kV Trip, UPC 184/185 defect, TX.3 T/C no volt REMARKS: 11kV FDR from S.9148 Forest Mundakal to AB 35795 to AB 35796 to S.9106 Forest Corella tee PT.9644 Bligh Meehan isolated. Broken HV X-arm and 11kv down in Blight St, Kirrawee near PT.9644. | November | 2011 | 2012Q2 | 2012 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | OH | Not Veg | 2011-11-28 | N | 65.5269 | N | 9 | N | N | 1.1101 | 39.4971 | 93519.6246
| ZN1285:PA20 | 925 | 2194.3002 | 44.64 | 2.3722 | 44.64 | 20190 | 16827 | 753801 | 2011-11-28 12:58 | 2011-11-28 16:43 | 225 | 11kV | 51975 | 231 | HV | Staff Operation | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Peats Ridge zone Pnl.5 - Rec 44995 Kulnura CB opened via DNMS. Rec 44995 opened by AOp to shed approx 20Amps from Panel 3 @ Peats Ridge Zone to avoid further interruption by Rec 46992 opening on overload AB 50441 is CLOSED with LB40538 OPENED for D/R 280636 | November | 2011 | 2012Q2 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2011-11-28 | N | 225 | N | 9 | N | N | 1.1101 | 39.4971 | 37981.797
| ZN1285:PA21 | 313 | 416.5594 | #N/A | 1.3309 | 39.4971 | 20298 | 18941 | 754274 | 2011-11-28 08:03 | 2011-11-28 19:55 | 712 | 11kV | 2759 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Pnl.1 Peats Ridge - Feeder from USL40518 to AB4181 to LB45201 tee PT18615 to USL 42097 was isolated and earthed to reapir 11kV bond burnt off @ USL 40297 related: 754274 754275 754277 | November | 2011 | 2012Q2 | 2012 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2011-11-28 | N | 689.75 | N | 9 | N | N | 1.1101 | 39.4971 | 2016.1958
| ZN1285:PA22 | 605 | 902.6618 | #N/A | 1.492 | 39.4971 | 19615 | 10370 | 754280 | 2011-11-29 11:26 | 2011-11-29 12:40 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118592 B Phase DOLF : 31Amp. Excluded OMS 754280 OMS 754656 | November | 2011 | 2012Q2 | 2012 |  |  |  |  | OH | Veg | 2011-11-29 | N | 74 | N | 5 | N | N | 1.1101 | 39.4971 | 54.077
| ZN1285:PA23 | 2052 | 1568.7328 | 39.29 | 0.76449 | 39.29 | 19999 | 14921 | 754349 | 2011-11-29 12:51 | 2011-11-29 13:06 | 15 | 11kV | 32010 | 2134 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | Call 1713661 says COUNCIL TEAM HAS DUG UP A CABLE At S2473 North Sydney Pane;l 32 Tripped on intertrip with 11kV trip. At S218 T/PE have working Access permit to test LV pilots on Tx2. The T/PE injected into the Tx1 feeder resulting in Pa32 tripping. See OMS 754658 754407/345/349/344 | November | 2011 | 2012Q2 | 2012 | ZN2473:PA32 | ZN35400:PA110 | ZN35400/000110 | NORTH SYDNEY | UG | Not Veg | 2011-11-29 | N | 15 | N | 5 | N | N | 1.1101 | 39.4971 | 23391.9639
| ZN1285:PA24 | 1573 | 1065.8545 | 31.71 | 0.67759 | 31.71 | 18778 | 1921 | 754546 | 2011-11-29 20:14 | 2011-11-29 21:11 | 56.7667 | 11kV | 3065.4 | 54 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | CC1: 22-"Refer to SOp" LID 118600 B Phase DOLF : 20Amp | November | 2011 | 2012Q2 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2011-11-29 | N | 56.7667 | N | 5 | N | N | 1.1101 | 39.4971 | 2240.1039
| ZN1285:PA27 | 1796 | 2582.3671 | 43.62 | 1.4378 | 43.62 | 18849 | 2561 | 754533 | 2011-11-29 19:53 | 2011-11-29 21:30 | 96.5833 | 11kV | 1448.75 | 15 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118601 B Phase DOLF : 20Amp. | November | 2011 | 2012Q2 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2011-11-29 | N | 96.5833 | N | 5 | N | N | 1.1101 | 39.4971 | 1058.7038
| ZN1285:PA28 | 2 | 383.8439 | #N/A | 191.922 | 39.4971 | 20132 | 16178 | 754562 | 2011-11-29 21:01 | 2011-11-29 22:15 | 74 | 11kV | 296 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118602 A Phase DOLF : 10Amp. Excluded OMS 754562, 754564 OMS 754677 | November | 2011 | 2012Q2 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2011-11-29 | N | 74 | N | 5 | N | N | 1.1101 | 39.4971 | 216.3081
| ZN1285:PA29 | 501 | 919.9822 | #N/A | 1.8363 | 39.4971 | 19835 | 13031 | 754573 | 2011-11-30 01:30 | 2011-11-30 02:45 | 75 | 11kV | 300 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118604 A & C phase DOLF : 10Amp excluded OMS 754573 (customer multiple premise) OMS 754693 | November | 2011 | 2012Q2 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2011-11-30 | N | 75 | N | 8 | N | N | 1.1101 | 39.4971 | 219.2312
| ZN1285:PA30 | 35 | 75.5903 | 61.93 | 2.1597 | 61.93 | 19967 | 14628 | 754576 | 2011-11-30 05:36 | 2011-11-30 10:06 | 270 | 11kV | 1890 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 118610 A & B Phase DOLF : 10Amp Excluded OMS 754575, 754576 OMS 755332 | November | 2011 | 2012Q2 | 2012 | 803:74007 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2011-11-30 | N | 270 | N | 8 | N | N | 1.1101 | 39.4971 | 1381.1563
| ZN1285:PA31 | 1977 | 2000.7519 | 43.79 | 1.012 | 43.79 | 18768 | 1853 | 755348 | 2011-11-30 11:20 | 2011-11-30 12:10 | 50 | 11kV | 400 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 118609 No protection operations. Section isolated to repair stranded mains at pole SF-30191 under A/P | November | 2011 | 2012Q2 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2011-11-30 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 292.3082
| ZN1285:PA32 | 223 | 1154.1482 | #N/A | 5.1756 | 39.4971 | 19628 | 10479 | 754785 | 2011-11-30 12:11 | 2011-11-30 13:10 | 59 | 11kV | 4838 | 82 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118613 B Phase DOLF : 31Amp. Fatigued fuse element. Readings as left 45A, 55A, 101A @ 250V. Excluded OMS 754785 OMS 755226 | November | 2011 | 2012Q2 | 2012 | 223:14393 | 223:14393 | ZN00223/014393 | LAKE MACQUARIE | OH | Veg | 2011-11-30 | N | 59 | N | 8 | N | N | 1.1101 | 39.4971 | 3535.4677
| ZN1285:PA33 | 2776 | 2448.2892 | 34.84 | 0.88195 | 34.84 | 19708 | 11756 | 754854 | 2011-11-30 13:59 | 2011-11-30 15:51 | 112 | 11kV | 60256 | 538 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Pnl.5 Peats Ridge - iR 61083 Bushells Peats 0.1 - newly installed intellirupter found auto with pick up of 200Amps. Suspect to be operating on load According to system diagrams switch had no protection or Supervisory Control capabilities. | November | 2011 | 2012Q2 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2011-11-30 | N | 112 | N | 8 | N | N | 1.1101 | 39.4971 | 44033.3075
| ZN1285:PA34 | 5 | 629.5062 | 61.52 | 125.9012 | 61.52 | 19769 | 12532 | 754960 | 2011-11-30 16:11 | 2011-11-30 16:45 | 34 | 11kV | 61914 | 1821 | HV | Staff Other | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Pnl.4 Erina - Intellirupter 49612 tripped on SEL While restoring for D/R 280052 - iR49612 opened. Staff Error. iR49612 shown on diagram with no protection or SC control. Fully operational on DNMS | November | 2011 | 2012Q2 | 2012 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Not Veg | 2011-11-30 | N | 34 | N | 8 | N | N | 1.1101 | 39.4971 | 45244.925
| ZN1285:PA35 | 455 | 298.0025 | 48.29 | 0.65495 | 48.29 | 20427 | 20312 | 755262 | 2011-11-30 15:00 | 2011-11-30 17:35 | 155 | 11kV | 54095 | 349 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Pnl.9 Lisarow - 11kV feeder from AB44074 to LB 45039 tee PT11434 & S.14191 via USL44256 was interrupted for safety to remove trees from 11kV feeder related jobs: 755263 755262 | November | 2011 | 2012Q2 | 2012 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2011-11-30 | N | 155 | N | 8 | N | N | 1.1101 | 39.4971 | 39531.0305
| ZN1285:PA36 | 2 | 3.724 | #N/A | 1.862 | 39.4971 | 19761 | 12467 | 755045 | 2011-11-30 18:46 | 2011-11-30 18:55 | 9 | 11kV | 15228 | 1692 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | Ex Noraville Pnl.1L - D/R 281664 - While switching 11kV fdr for RMI outage DOp Fennell opened Sw C @ S.14068 Noraville Aux instead of opening Sw C @ S.12620 Noraville, thus causing the interruptiong to the remaining feeder. The labbelling at the two locations needs to be recified so not to confuse outages. | November | 2011 | 2012Q2 | 2012 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | UG | Not Veg | 2011-11-30 | N | 9 | N | 8 | N | N | 1.1101 | 39.4971 | 11128.1733
| ZN1285:PA8 | 219 | 317.4143 | 39 | 1.4494 | 39 | 19210 | 5950 | 756524 | 2011-12-01 02:25 | 2011-12-01 05:43 | 198 | 11kV | 77220 | 1168 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | At S965 Pennnant Hills Panel 42 Tripped on Relays: B and Cphase timed O/C, EFI Signals: 11kV Trip, #2 Tx group earth, Zone Earth Cause: 2 HDO fuses operated at PT1352 - Defective bushing on metering unit. See OMS 756524 756526 | December | 2011 | 2012Q2 | 2012 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Not Veg | 2011-12-01 | N | 66.113 | N | 10 | N | N | 1.1101 | 39.4971 | 56430.0984
| ZN9550:PA1 | 964 | 1018.1885 | 41.49 | 1.0562 | 41.49 | 20312 | 19067 | 755107 | 2011-12-01 03:37 | 2011-12-01 07:00 | 203 | 11kV | 52072 | 836 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 118622 2 fault operations tree across 11kv ohm at pole IS-62344 Anderson Dr excluded OMS 755107, 755108. OMS 755304, 755307, 755308, 755309 | December | 2011 | 2012Q2 | 2012 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Veg | 2011-12-01 | N | 62.2871 | N | 10 | N | N | 1.1101 | 39.4971 | 38052.6817
| ZN9550:PA11 | 420 | 1064.7067 | 62.43 | 2.535 | 62.43 | 19344 | 7615 | 755111 | 2011-12-01 04:55 | 2011-12-01 07:20 | 145 | 11kV | 20300 | 140 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Wind | N | @ S 17115 Ocean Devitt 11kV C Phase 80A SIBA Suspected Tx internal fault @ 17115 Ocean Devitt. restored via LV// | December | 2011 | 2012Q2 | 2012 | ZN15006:PA4 | ZN15006:PA4 | ZN15006/000004 | NORTHERN BEACHES | UG | Not Veg | 2011-12-01 | N | 145 | N | 10 | N | N | 1.1101 | 39.4971 | 14834.6413
| ZN9550:PA27 | 252 | 584.6358 | 59.03 | 2.32 | 59.03 | 19976 | 14663 | 755122 | 2011-12-01 06:24 | 2011-12-01 07:55 | 91 | 11kV | 2366 | 26 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14524 South pacific Ocean 11kV C Phase HDO blown Fuse Fatigue | December | 2011 | 2012Q2 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2011-12-01 | N | 91 | N | 10 | N | N | 1.1101 | 39.4971 | 1729.003
| ZN9550:PA28 | 789 | 833.6264 | 40.74 | 1.0566 | 40.74 | 20200 | 16951 | 755136 | 2011-12-01 07:18 | 2011-12-01 08:05 | 47 | 11kV | 48974 | 1042 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 118626 Blown 11kV tapping at ABS 10784 during parallel of Fdr 33602 Shortland sub & 58 Broadmeadow sub. Fdr 33602 abnormally switched, (switched to item 8 DSI 17686) | December | 2011 | 2012Q2 | 2012 | 211:33602 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2011-12-01 | N | 47 | N | 10 | N | N | 1.1101 | 39.4971 | 35788.7547
| ZN9550:PA3 | 1279 | 1429.0509 | 38.96 | 1.1173 | 38.96 | 19369 | 7944 | 755198 | 2011-12-01 08:38 | 2011-12-01 09:50 | 72.1167 | 11kV | 9086.7 | 126 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118632 C Phase DOLF 40Amp. C Pahse 40A DOLF - Fatigue Volts 248V, 248V, 248V Load 80A, 80A, 200A | December | 2011 | 2012Q2 | 2012 | 234:2001 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2011-12-01 | N | 72.1167 | N | 10 | N | N | 1.1101 | 39.4971 | 6640.2923
| ZN9550:PA33 | 484 | 846.9517 | 44.36 | 1.7499 | 44.36 | 18882 | 2915 | 755235 | 2011-12-01 09:19 | 2011-12-01 10:55 | 96 | 11kV | 192 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 118634 A Phase DOLF : 20Amp Excluded OMS 755235 OMS 755812 | December | 2011 | 2012Q2 | 2012 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2011-12-01 | N | 96 | N | 10 | N | N | 1.1101 | 39.4971 | 140.3079
| ZN9550:PA36 | 789 | 807.7273 | 30.43 | 1.0237 | 30.43 | 20026 | 15308 | 755371 | 2011-12-01 11:54 | 2011-12-01 15:30 | 216 | 11kV | 864 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118637 C phase DOLF : 16Amp Load readings: 250/246/248V & 6/17/31A. DOLF element fatigue. Excluded OMS Job No. 755371. OMS 755793 | December | 2011 | 2012Q2 | 2012 | 218:7478 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Veg | 2011-12-01 | N | 216 | N | 10 | N | N | 1.1101 | 39.4971 | 631.3857
| ZN9550:PA4 | 469 | 491.0002 | 34.95 | 1.0469 | 34.95 | 19385 | 8148 | 755431 | 2011-12-01 13:37 | 2011-12-01 17:05 | 208 | 11kV | 33072 | 159 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118638 A Phase DOLF : 5Amp. defective surge arrestor replaced at sub 53078 Army sub. line dolf did not grade with sub dolf Excluded OMS 755431 OMS 755826 | December | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-12-01 | N | 208 | N | 10 | N | N | 1.1101 | 39.4971 | 24168.0421
| ZN9550:PA41 | 46 | 534.1486 | 41.93 | 11.6119 | 41.93 | 18585 | 111 | 755604 | 2011-12-01 19:37 | 2011-12-01 22:26 | 169 | 11kV | 11323 | 67 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1167 Dunrossil Ave 31.5A HVDO fuse operated. Cause: Fuse Fatigue. See OMS756480 755602 755611 7555604 | December | 2011 | 2012Q2 | 2012 | ZN2635:PA10 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Not Veg | 2011-12-01 | N | 169 | N | 10 | N | N | 1.1101 | 39.4971 | 8274.5144
| ZN9550:PA42 | 1095 | 1004.1206 | 33.64 | 0.91701 | 33.64 | 19944 | 14208 | 755653 | 2011-12-02 07:56 | 2011-12-02 08:50 | 54 | 11kV | 23868 | 442 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn384 Camperdown 5kv fdr pa9 S46773 Parra Sydney Uni Tripped on Bph leakage EFI SIGNALS 5kv trip GE Pa9 Trip Cable Failure (frontline fdr) Access Permits issued to tester/jointer at Camperdown. See 756590 GIS 756577,86 Exclude 755653,60,1 | December | 2011 | 2012Q2 | 2012 | ZN384:PA9 | ZN384:PA2 | ZN00384/000002 | SYDNEY | UG | Not Veg | 2011-12-02 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 17442.0304
| ZN9550:PA43 | 1117 | 1171.3453 | 34.07 | 1.0487 | 34.07 | 19542 | 9505 | 755851 | 2011-12-02 12:25 | 2011-12-02 13:41 | 76 | 11kV | 85673 | 1510 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn.12580 Erina Pnl.16 tripped on Overcurrent A phase No cause ascertained (Windy) | December | 2011 | 2012Q2 | 2012 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2011-12-02 | N | 56.7371 | N | 4 | N | N | 1.1101 | 39.4971 | 62607.3015
| ZN9550:PA6 | 944 | 1050.0166 | 33.82 | 1.1123 | 33.82 | 19586 | 9744 | 756072 | 2011-12-02 20:03 | 2011-12-02 22:15 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118655 A phase DOLF : 10Amp. 248V 16A Excluded OMS 756072 OMS 756484 | December | 2011 | 2012Q2 | 2012 | 503:48011 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2011-12-02 | N | 132 | N | 4 | N | N | 1.1101 | 39.4971 | 96.4617
| ZN9550:PA9 | 663 | 581.3076 | 36.07 | 0.87678 | 36.07 | 19370 | 7958 | 756085 | 2011-12-02 21:22 | 2011-12-02 23:00 | 98 | 11kV | 196 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118656 A Phase DOLF : 10Amp 246, 244, 243V 5, 2, 18A excluded OMS 756085 OMS 756512 | December | 2011 | 2012Q2 | 2012 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2011-12-02 | N | 98 | N | 4 | N | N | 1.1101 | 39.4971 | 143.231
| ZN15008:PA1 | 1979 | 1073.2669 | 33.78 | 0.54233 | 33.78 | 19838 | 13070 | 765942 | 2011-12-03 02:54 | 2011-12-03 04:31 | 97 | 11kV | 96418 | 994 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.9550 Gwawley Bay P-43 "S.48722 Gwawley Bay Aux No.2" fdr tripped on: RELAYS: 1.2.1 Targets, 150TN, 51 BC SIGNALS: 11kV trip REMARKS: No cause ascertained | December | 2011 | 2012Q2 | 2012 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Veg | 2011-12-03 | N | 97 | N | 4 | N | N | 1.1101 | 39.4971 | 70459.4306
| ZN15008:PA10 | 1867 | 1335.5907 | 34.53 | 0.71537 | 34.53 | 19619 | 10389 | 756115 | 2011-12-03 06:50 | 2011-12-03 07:43 | 53 | 11kV | 91690 | 1730 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Centre phase 11kV bond burnt off at AB 30032. Section of Panel No.8 "Firth Queen" feeder ex ZN.10990 Arncliffe ABNORMAL: SW B at S.47415 Bonar Hirst No.1 closed. AB 31129 Open for Disc 280051 REMARKS: Centre phase 11kV bond hurnt off at AB 30032 | December | 2011 | 2012Q2 | 2012 | ZN10990:PA8 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | OH | Not Veg | 2011-12-03 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 67004.3476
| ZN15008:PA5 | 1335 | 1293.78 | 38.68 | 0.96912 | 38.68 | 18634 | 553 | 756143 | 2011-12-03 07:06 | 2011-12-03 11:10 | 243.9 | 11kV | 6341.4 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118661 B & C Phase DOLF : 10Amp. No obvious cause, a full feeder patrol should be performed. | December | 2011 | 2012Q2 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2011-12-03 | N | 243.9 | N | 4 | N | N | 1.1101 | 39.4971 | 4634.1081
| ZN15008:PA6 | 1337 | 673.0891 | 38.54 | 0.50343 | 38.54 | 20107 | 16034 | 756254 | 2011-12-03 21:18 | 2011-12-03 23:00 | 102 | 11kV | 12726 | 1818 | HV | Animal Possum | Animal | Circuit Breaker | Unplanned | Unselected | N | At S.1287 Revesby Panel 15 the "Eastern Tomp etc" feeder tripped and reclosed on: Relays - Earth fault , EFI, fault check, Lockout Signals - 11kv trip, ZE, TX 1 GE Remarks: @PT1330 Lochinvar Av, Possum committed suicide, Damaging Centre phase HV fuse assembly. Restored via LV// Related jobs: #756254, 756503, 756502 | December | 2011 | 2012Q2 | 2012 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2011-12-03 | N | 7 | N | 4 | N | N | 1.1101 | 39.4971 | 9299.7854
| ZN15008:PA7 | 2553 | 1690.6301 | 31.85 | 0.66221 | 31.85 | 19892 | 13657 | 756266 | 2011-12-04 03:07 | 2011-12-04 05:26 | 139.45 | 11kV | 266.4333 | 147 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118667 Trip & Reclose 1 fault operation Overcurrent Fdr also feeding most of Fdr 30020. ABS 19389 CLOSED & ABS 42515 OPEN. Flash over at UGOH pole HW-40134. excluded OMS-756266. | December | 2011 | 2012Q2 | 2012 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2011-12-04 | N | 1.8125 | N | 5 | N | N | 1.1101 | 39.4971 | 194.7016
| ZN15008:PA9 | 2369 | 1654.0165 | 32.38 | 0.69819 | 32.38 | 19536 | 9452 | 756333 | 2011-12-04 13:42 | 2011-12-04 15:54 | 131.5 | 11kV | 20121.5667 | 1285 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Rain Light | N | At ZN.10991 Blakehurst P-1 "Woids Ave" fdr tripped, reclosed & tripped again on: RELAYS: Earthed fault, reclose relay, timing relay, & EFI SIGNALS: 11kV trip, FIELD EFIs: S.10137 & S.10860 REMARKS: Large tree branch on UGOH to S.10956 Princes Blake removed by DOp. | December | 2011 | 2012Q2 | 2012 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Veg | 2011-12-04 | N | 15.6588 | N | 5 | N | N | 1.1101 | 39.4971 | 14704.2474
| ZN1610:PA1 | 4 | 316.6934 | 44.37 | 79.1733 | 44.37 | 19701 | 11654 | 756353 | 2011-12-04 14:15 | 2011-12-04 18:20 | 245 | 11kV | 29652 | 150 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID 118678 6 fault operations single phase Earth fault. Excluded OMS 756353, 756354 OMS 756611, 756614, 756615, 756616, 756618, 756622, 756624, 756625, 756626. | December | 2011 | 2012Q2 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | UG | Not Veg | 2011-12-04 | N | 197.68 | N | 5 | N | N | 1.1101 | 39.4971 | 21668.807
| ZN1610:PA10 | 53 | 633.2475 | #N/A | 11.9481 | 39.4971 | 19247 | 6494 | 756361 | 2011-12-04 15:40 | 2011-12-04 18:50 | 190 | 11kV | 21840 | 130 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 118680 No protection operations. Broken 11kV bonds at poles HR-61861 & HR-61034 repaired under A/P. Excluded OMS # 756361 OMS 756567 | December | 2011 | 2012Q2 | 2012 | 502:48010 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2011-12-04 | N | 168 | N | 5 | N | N | 1.1101 | 39.4971 | 15960.0278
| ZN1610:PA11 | 9 | 379.8997 | #N/A | 42.2111 | 39.4971 | 19575 | 9703 | 756407 | 2011-12-04 18:26 | 2011-12-04 20:05 | 99 | 11kV | 297 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118681 A Phase DOLF : 16Amp Excluded OMS 756407 OMS 756704 | December | 2011 | 2012Q2 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2011-12-04 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 217.0388
| ZN1610:PA12 | 30 | 298.2399 | #N/A | 9.9413 | 39.4971 | 19110 | 4694 | 756471 | 2011-12-05 08:08 | 2011-12-05 11:30 | 202 | 11kV | 1212 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118690 A Phase DOLF : 10Amp Sub supplies a pump, operator suspects the fuse blew in a previous storm. Excluded OMS 756471 (reporting fault) OMS 757078 | December | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2011-12-05 | N | 202 | N | 4 | N | N | 1.1101 | 39.4971 | 885.6939
| ZN1610:PA13 | 1057 | 643.1005 | #N/A | 0.60842 | 39.4971 | 18595 | 148 | 756654 | 2011-12-05 11:02 | 2011-12-05 12:30 | 88 | 11kV | 264 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 118691 A & C Phase DOLF : 20Amp Operator suspects fuses blew in a previous storm. Excluded OMS 756654 OMS 757060 | December | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2011-12-05 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 192.9234
| ZN1610:PA14 | 1160 | 710.4854 | #N/A | 0.61249 | 39.4971 | 19947 | 14242 | 756953 | 2011-12-05 17:58 | 2011-12-05 20:58 | 180 | 11kV | 44792 | 856 | HV | 3rd Party Vehicle | 3rd Party Impact | UGOH | Unplanned | Unselected | N | Zn.12660 Woy Woy Pnl.16 tripped on: A phase Inst & Timed O/C, EFI Field EFI: S.18242 11kV feeder from S.18156 to Open Span of HV mains. Car hit HV UGOH pole to S.18156 | December | 2011 | 2012Q2 | 2012 | ZN12660:PA16 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | UG | Not Veg | 2011-12-05 | N | 52.3271 | N | 4 | N | N | 1.1101 | 39.4971 | 32732.6725
| ZN1610:PA16 | 9 | 2026.5431 | #N/A | 225.1715 | 39.4971 | 20167 | 16476 | 756998 | 2011-12-05 20:08 | 2011-12-05 21:19 | 71 | 11kV | 82586 | 1251 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.8 feeder tripped on Earth Fault with EFI. UG feeder fault from Zn.12620 Noraville to S.18799 to S.18491 | December | 2011 | 2012Q2 | 2012 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | UG | Not Veg | 2011-12-05 | N | 66.016 | N | 4 | N | N | 1.1101 | 39.4971 | 60351.4129
| ZN1610:PA17 | 382 | 857.1701 | 50.58 | 2.2439 | 50.58 | 19032 | 4255 | 757023 | 2011-12-06 02:17 | 2011-12-06 04:28 | 131 | 11kV | 645 | 5 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S5868 Gore Hill Panel 21 tripped. Cause: Translay EFI and Fault Check. Abnroamal Switching: Section of 11kV feeder O/O/S due to 11kV CB's at S7346 and S1770 RND Hospital No 2 Not serviceable. CBs will not close. Cause: Front line feeder fault Gore HIll See OMS 757342 757341 757023 | December | 2011 | 2012Q2 | 2012 | ZN5868:PA21 | ZN5868:PA21 | ZN05868/000021 | WILLOUGHBY | UG | Not Veg | 2011-12-06 | N | 129 | N | 4 | N | N | 1.1101 | 39.4971 | 471.347
| ZN1610:PA18 | 62 | 156.9045 | #N/A | 2.5307 | 39.4971 | 19207 | 5890 | 757043 | 2011-12-06 07:40 | 2011-12-06 10:01 | 141 | 11kV | 17202 | 122 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 118699 Cockatoo contacted the mains just beyond the recloser, the contact also damaged the conductor tie which needed to be replaced. Excluded OMS 757043 OMS 757503 | December | 2011 | 2012Q2 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2011-12-06 | N | 141 | N | 4 | N | N | 1.1101 | 39.4971 | 12570.7142
| ZN1610:PA19 | 1129 | 1167.1076 | 37.51 | 1.0338 | 37.51 | 19639 | 10595 | 757121 | 2011-12-06 09:36 | 2011-12-06 10:57 | 81 | 11kV | 90317 | 1121 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ Zn3922 Drummoyne - 11kv Panel No.2 "Sub 1212 Edenholme Rd" feeder tripped Relays: Earth fault, EFI, Fault check Signals: 11kv trip, No.1 Group Earth, Zn Earth Field EFI's: Sub 1212 Remarks: 11KV UG feeder fault from Sub 1212 Edenholme Rd to Sub 1521 Springside St Related jobs: #757168, 757151, 757131, 757121, 757547, 757548, 757551, 757554, 757558 | December | 2011 | 2012Q2 | 2012 | ZN3922:PA2 | ZN3922:PA2 | ZN03922/000002 | INNER WEST | UG | Not Veg | 2011-12-06 | N | 80.5682 | N | 4 | N | N | 1.1101 | 39.4971 | 66000.9997
| ZN1610:PA2 | 614 | 1195.8576 | #N/A | 1.9477 | 39.4971 | 19882 | 13587 | 757306 | 2011-12-06 13:04 | 2011-12-06 15:15 | 131 | 11kV | 76097 | 3567 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Zn931 Darlinghurst Tx2 11kv group was interrupted to inspect busbar after endbox fault on panel 26 Busbar interrupted to inspect busbars after endbox fault See 757665 757594 exclude 757272 757306 757315 | December | 2011 | 2012Q2 | 2012 | ZN931:PA25 | ZN931:PA25 | ZN00931/000025 | SYDNEY | Unknown | Not Veg | 2011-12-06 | N | 21.3336 | N | 4 | N | N | 1.1101 | 39.4971 | 55609.4431
| ZN1610:PA20 | 78 | 426.412 | 58.31 | 5.4668 | 58.31 | 19091 | 4571 | 757487 | 2011-12-07 03:41 | 2011-12-07 08:20 | 279 | 11kV | 5021.7833 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | LID 118708 B Phase DOLF : 10Amp Volts: Aph 248V, Bph 236V, Cph 252V Aslo refer related records 757589, 757487 | December | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2011-12-07 | Y | 278.988 | N |  | N | Y | 1.1101 | 39.4971 | 3669.7711
| ZN1610:PA22 | 1883 | 1103.6902 | #N/A | 0.58613 | 39.4971 | 19482 | 8969 | 758023 | 2011-12-07 19:50 | 2011-12-07 20:07 | 17 | 11kV | 17 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | Unselected | Y | Section of feeders Panel 12, 19 & 21 Tooheys Lidcombe Ring from Zn 2466 Flemington. Sub 3620 Tooheys Lidcombe:- Protection defect alarm and voltage supervision relay frequency rate trip. Circuit breakers labelled SwA, SwB & SwC all tripped @ sub 3620 Tooheys Lidcombe. Remarks: Due to the load on Tx3 (approx 1400amps) and the load on (Tx4 approx 400amps) field switching across these Tx's will not be possible on there group feeders. The load of Tx 4 was transferred to TX2 approx 1050amps now. TPE to investigate why Sub 3620 Tooheys Lidcombe so sensitive to voltage changes. Related jobs: #712356, 758023,758209 | December | 2011 | 2012Q2 | 2012 |  |  |  | CUMBERLAND | Unknown | Unknown | 2011-12-07 | Y | 17 | N |  | N | Y | 1.1101 | 39.4971 | 12.4231
| ZN1610:PA23 | 21 | 103.6949 | #N/A | 4.9379 | 39.4971 | 20149 | 16336 | 758157 | 2011-12-08 08:58 | 2011-12-08 11:00 | 121.85 | 11kV | 487.4 | 4 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 118725 During programmed switching 18298 the District Operator found all earths were stolen from the Salt Ash Regulator (Plant # 19090). The removal of the earthing for this regulator creates a hazardous situation and the field staff requested the control room attempt to remove the hazard ASAP. Sub 48617 and sub 16903 were interrupted to remove the hazard. No protection operated the outage was for safety only. | December | 2011 | 2012Q2 | 2012 | 231:8405 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Not Veg | 2011-12-08 | N | 121.85 | N | 5 | N | N | 1.1101 | 39.4971 | 356.1775
| ZN1610:PA25 | 26 | 382.3838 | #N/A | 14.7071 | 39.4971 | 19921 | 14009 | 758219 | 2011-12-08 10:27 | 2011-12-08 12:00 | 93.3667 | 11kV | 7282.6 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 3280 Hunt Ave Tripped. Cause: DOp removed branch of OH mains O/S 11 Cotswold Rd See OMS 758219 758243 758224 | December | 2011 | 2012Q2 | 2012 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2011-12-08 | N | 93.3667 | N | 5 | N | N | 1.1101 | 39.4971 | 5321.9093
| ZN1610:PA26 | 53 | 749.3736 | #N/A | 14.1391 | 39.4971 | 18800 | 2151 | 758382 | 2011-12-08 13:22 | 2011-12-08 14:55 | 93 | 11kV | 279 | 3 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 118729 B Phase DOLF Dead bird base of pole Excluded OMS 758382 OMS 759757 | December | 2011 | 2012Q2 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2011-12-08 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 203.885
| ZN1610:PA27 | 12 | 249.4298 | #N/A | 20.7858 | 39.4971 | 18999 | 3990 | 758440 | 2011-12-08 14:37 | 2011-12-08 15:40 | 63 | 11kV | 5292 | 84 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Tee off to PT.9263 Murchison Craigholm open circuit 11kV bond footpath side corner of Murchison and Corea. LV//LKs closed 960, 1389, 338 & 339. | December | 2011 | 2012Q2 | 2012 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2011-12-08 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 3867.2375
| ZN1610:PA28 | 866 | 899.5695 | #N/A | 1.0388 | 39.4971 | 19876 | 13550 | 758062 | 2011-12-08 03:46 | 2011-12-08 19:00 | 914 | 11kV | 1139 | 6 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2635 Epping Panel 5 Tripped on Signals: 11kV Trip, Eroup Earth Relays: Earth Fault and EFI. Cause: Section of 11kV UG feeder between S6154 to S4421 failed. See OMS 758854 758856 758062 758431 | December | 2011 | 2012Q2 | 2012 | ZN2635:PA5 | ZN2635:PA65 | ZN02635/000065 | RYDE | UG | Not Veg | 2011-12-08 | N | 189.8333 | N | 5 | N | N | 1.1101 | 39.4971 | 832.3476
| ZN1610:PA29 | 1010 | 435.7579 | 32.48 | 0.43144 | 32.48 | 18696 | 1124 | 758823 | 2011-12-09 13:03 | 2011-12-09 16:10 | 187 | 11kV | 1309 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | 11kv HV Fuse blew due to no apparent reason See 759532 exclude 758823 | December | 2011 | 2012Q2 | 2012 | ZN188:PA44 | ZN188:PA44 | ZN00188/000044 | SYDNEY | OH | Not Veg | 2011-12-09 | N | 187 | N | 1 | N | N | 1.1101 | 39.4971 | 956.5786
| ZN1610:PA3 | 471 | 871.0743 | #N/A | 1.8494 | 39.4971 | 18738 | 1427 | 758995 | 2011-12-10 00:12 | 2011-12-10 01:25 | 73 | 11kV | 14454 | 198 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 118747 C Phase DOLF : 40Amp C PHASE L/A cut away. needs replacing. Volts 252 LH LVF CCT 100A RH LVF CCT 70 Excluded OMS 758995, 758996, 758997 OMS 759508 | December | 2011 | 2012Q2 | 2012 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2011-12-10 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 10562.5569
| ZN1610:PA4 | 43 | 51.975 | #N/A | 1.2087 | 39.4971 | 20226 | 17336 | 759105 | 2011-12-10 13:28 | 2011-12-10 14:46 | 78 | 11kV | 68989 | 899 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At ZN.10994 Mortdale 11kV fdr P-19 "Mortdale depot etc" tripped: RELAYS: SEL Trip SIGNALS: 11kV trip FIELD EFIs: Nil REMARKS: 11kV roadside bond off at AB 30063 | December | 2011 | 2012Q2 | 2012 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2011-12-10 | N | 76.7397 | N | 4 | N | N | 1.1101 | 39.4971 | 50415.1264
| ZN1610:PA5 | 6 | 285.5695 | #N/A | 47.5949 | 39.4971 | 19898 | 13732 | 759155 | 2011-12-10 20:17 | 2011-12-10 21:39 | 81.2333 | 11kV | 19983.4 | 246 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kV P-7 "S.10613" fdr ex ZN.10999 Kogarah. 11kV footpath bond off at AB 30019. ABNORMAL: Due sto HR LK 30608. AB 301998 closed with AB 31262 closed and 30019 closed with Sw B open at S.10925 Forest Waterboard. | December | 2011 | 2012Q2 | 2012 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | GEORGES RIVER | OH | Not Veg | 2011-12-10 | N | 81.2333 | N | 4 | N | N | 1.1101 | 39.4971 | 14603.2793
| ZN1610:PA7 | 15 | 123.4865 | #N/A | 8.2324 | 39.4971 | 19785 | 12667 | 759144 | 2011-12-10 18:36 | 2011-12-10 21:45 | 189 | 11kV | 14704 | 1459 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 118756 & 188757 Trans fault at sub 72292 Everleigh Ct. Sub placed in parallel. Transformer to be replaced at a later date. Excluded OMS 759144, 759169 OMS 759743, 759745, 759746 | December | 2011 | 2012Q2 | 2012 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2011-12-10 | N | 10.0781 | N | 4 | N | N | 1.1101 | 39.4971 | 10745.2495
| ZN1610:PA8 | 364 | 1244.361 | #N/A | 3.4186 | 39.4971 | 19957 | 14317 | 759202 | 2011-12-11 07:39 | 2011-12-11 11:40 | 241 | 11kV | 106281 | 441 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | 11kv OCB and 415V ACB for Tx1 and Tx2 opened. Tx2 tripped on Bucholz and Tx1 tripped on prallel tripping. Opened due ot low oil in Tx2. T-Pe has topped up Tx2 and Tx was RTS Se 759551 LV// 759586 exclude 759203 759214 759202 | December | 2011 | 2012Q2 | 2012 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2011-12-11 | N | 241 | N | 4 | N | N | 1.1101 | 39.4971 | 77667.02
| ZN847:PA1 | 1240 | 1161.6085 | 36.63 | 0.93678 | 36.63 | 20314 | 19099 | 759255 | 2011-12-11 12:17 | 2011-12-11 14:00 | 102.7333 | 11kV | 102.7333 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | CC1: 22-"Refer to SOp" LID 118760 B Phase DOLF Tension spring on DOLF mount stuck, freed up using link stick. | December | 2011 | 2012Q2 | 2012 |  |  |  |  | OH | Not Veg | 2011-12-11 | N | 102.7333 | N | 4 | N | N | 1.1101 | 39.4971 | 75.0745
| ZN847:PA10 | 1074 | 1747.1223 | 39.52 | 1.6267 | 39.52 | 18978 | 3797 | 759359 | 2011-12-11 18:54 | 2011-12-11 21:00 | 125.7 | 11kV | 2514 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 118767 Line DOLF | December | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2011-12-11 | N | 125.7 | N | 4 | N | N | 1.1101 | 39.4971 | 1837.157
| ZN847:PA12 | 330 | 280.5898 | 36.8 | 0.85027 | 36.8 | 19155 | 4944 | 759392 | 2011-12-12 03:18 | 2011-12-12 04:39 | 81 | 11kV | 35892 | 638 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN.9900 Menai P-2 "S.9066 Belbowrie Cl' fdr tripped: RELAYS: B phase earth leakage, EFI SIGNALS: 11kV Trip, TX.1 Group Earth, Zone Earth, CLC Defect FIELD EFIs: S.9066, S.9160, S.9122, S.9139 REMARKS: 11kV UG fdr between S.9024/B Yala Torumba and S.9175/A Yala Tycannah. EFI indications initially were that fault was between S.9139/B Yala Menai & S.9024/A Yala Torumba (i.e. EFI at S.9024 had not operated. | December | 2011 | 2012Q2 | 2012 | ZN9900:PA2 | ZN9900:PA2 | ZN09900/000002 | SUTHERLAND | UG | Not Veg | 2011-12-12 | N | 56.2571 | N | 5 | N | N | 1.1101 | 39.4971 | 26228.815
| ZN847:PA14 | 436 | 828.8166 | 41.27 | 1.901 | 41.27 | 19851 | 13352 | 759380 | 2011-12-11 22:46 | 2011-12-12 06:20 | 454 | 11kV | 96486 | 681 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Light | N | LID 118769 2 fault operations A & B Phase Overcurrent First paragraph of this report indicates no subs interrrupted. There were 9 subs interrupted. Fire on Hazemeyer unit at Windarra Cl sub 24573. Supply restored to LV feeders 24578 & 24137 at 2350hrs. Prot: 50T A & B; Fdr lockout. Excluded OMS Job Nos. 759380, 759381, 759382, 759385 & 759386. OMS 759791, 759792, 759796, 759797. | December | 2011 | 2012Q2 | 2012 | 258:80790 | 258:80790 | ZN00258/080790 | NEWCASTLE | UG | Not Veg | 2011-12-11 | N | 141.6828 | N | 4 | N | N | 1.1101 | 39.4971 | 70509.1229
| ZN847:PA15 | 1152 | 1218.4182 | 37.72 | 1.0577 | 37.72 | 18743 | 1466 | 759397 | 2011-12-12 04:19 | 2011-12-12 08:15 | 235.8167 | 11kV | 2935.8167 | 13 | HV | Animal Bird | Animal | Fuse | Unplanned | Previous Storm | N | LID 118771 Single phase DOLF : Excluded OMS 759411 OMS 760107 | December | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-12-12 | N | 225.8321 | N | 5 | N | N | 1.1101 | 39.4971 | 2145.4082
| ZN847:PA18 | 893 | 790.7511 | 34.3 | 0.8855 | 34.3 | 19827 | 13004 | 759604 | 2011-12-12 10:41 | 2011-12-12 12:05 | 84 | 11kV | 84 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 118774 Single phase DOLF : 10Amp Excluded OMS 759604 OMS 760112 | December | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-12-12 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 61.3847
| ZN847:PA19 | 1287 | 1133.6127 | 44.67 | 0.88082 | 44.67 | 20147 | 16313 | 760086 | 2011-12-12 13:00 | 2011-12-12 16:30 | 210 | 11kV | 420 | 2 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | Zn.12630 Peats Ridge - Section of Pnl.3 - From AB43765 to S.14480 tee S.14640, tee S.12355, tee S12354. Defective 11kV UGOH near AB43765 interrupted by DOp for cable repairs | December | 2011 | 2012Q2 | 2012 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | Unknown | Unknown | 2011-12-12 | N | 210 | N | 5 | N | N | 1.1101 | 39.4971 | 306.9236
| ZN847:PA2 | 1863 | 1483.6446 | 34.28 | 0.79637 | 34.28 | 20364 | 19868 | 760019 | 2011-12-12 20:20 | 2011-12-12 22:20 | 120 | 11kV | 120 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 118781 Burnt Bond Excluded OMS 760019 OMS 760122 | December | 2011 | 2012Q2 | 2012 |  |  |  |  | OH | Not Veg | 2011-12-12 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN847:PA21 | 1857 | 1478.4634 | 36.04 | 0.79616 | 36.04 | 20030 | 15357 | 760070 | 2011-12-13 07:56 | 2011-12-13 11:50 | 234 | 11kV | 702 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118786 Single phase DOLF : 10Amp. sub isolated to replace 2 x LA's | December | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-12-13 | N | 234 | N | 3 | N | N | 1.1101 | 39.4971 | 513.0009
| ZN847:PA22 | 1348 | 1098.9348 | 39.26 | 0.81523 | 39.26 | 19157 | 4977 | 760266 | 2011-12-13 12:09 | 2011-12-13 13:25 | 76 | 11kV | 53732 | 707 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 6 Tripped on A phase Earth Fault and Fault Check. Signals: 11kV Trip, No1 Tx group Earth. Cause: Dop howell reports workmen opposite Macquariepark Zone Doing Horizontal Boring appear to have hit the Front line section of feeder. | December | 2011 | 2012Q2 | 2012 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2011-12-13 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 39265.7608
| ZN847:PA23 | 1312 | 1278.5272 | 43.05 | 0.97449 | 43.05 | 19062 | 4418 | 760367 | 2011-12-13 14:21 | 2011-12-13 15:03 | 42 | 11kV | 11070 | 297 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn2568 St Peters Zone Pa25 fdr tiped on EF, Fault Check, EFI Signals - Tx3 ZE 11kv trip Remarks - UG fdr fault btw S1560SwB to S7558SwA to S8409SwA. COntractor hit cable with star pickett 90-96 Bourke rd Alexandria See 761319,22,2373 GIS 762383 Exclude 760367,75,6,8 | December | 2011 | 2012Q2 | 2012 | ZN2568:PA25 | ZN2568:PA25 | ZN02568/000025 | SYDNEY | UG | Not Veg | 2011-12-13 | N | 37.2727 | N | 3 | N | N | 1.1101 | 39.4971 | 8089.6295
| ZN847:PA26 | 178 | 123.6179 | #N/A | 0.69448 | 39.4971 | 18889 | 3006 | 761082 | 2011-12-15 09:00 | 2011-12-15 14:45 | 345 | 11kV | 690 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118808 A & C phase DOLF : 10Amp. ISOLATED LA . FOUND SUB 71280 FAULTY.TRIPPED OFF SW 15124 BOW RAGCB.( SEE U/P OUTAGE REPORT 118815 ). Faulty Txf replaced under A/P Excluded OMS REPORT NO 761082. OMS 761473 | December | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2011-12-15 | N | 345 | N | 1 | N | N | 1.1101 | 39.4971 | 504.2316
| ZN847:PA28 | 1200 | 1465.3957 | 37.54 | 1.2212 | 37.54 | 19915 | 13938 | 761546 | 2011-12-16 11:04 | 2011-12-16 12:49 | 105 | 11kV | 16664 | 196 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 118830 3 fault operations C phase to Earth fault SUSPECT 11kV cable fault between Sw 35345 ans Sw 35352. OMS 763471, 763476, 763477, 763479, 763480, 763483, 763484, 763485, 763490 Exculded OMS 761546, 762259, 762265, 762266, 762267, 762270, 762271, 762274, 762277. | December | 2011 | 2012Q2 | 2012 | 503:48076 | 532:83312 | ZN00532/083312 | MAITLAND | UG | Not Veg | 2011-12-16 | N | 85.0204 | N | 4 | N | N | 1.1101 | 39.4971 | 12177.5597
| ZN847:PA29 | 242 | 1815.7081 | #N/A | 7.5029 | 39.4971 | 20157 | 16382 | 761519 | 2011-12-16 09:50 | 2011-12-16 13:30 | 220 | 11kV | 220 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 118831 C Phase DOLF : 10Amp 10A DOLF - Fuse Fatigue ?? 252, 250, 251V 1, 1, 2 Amps Excluded OMS 761519 OMS 762160 | December | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2011-12-16 | N | 220 | N | 4 | N | N | 1.1101 | 39.4971 | 160.7695
| ZN847:PA30 | 597 | 362.3175 | #N/A | 0.6069 | 39.4971 | 19068 | 4459 | 761615 | 2011-12-16 13:08 | 2011-12-16 14:05 | 57 | 11kV | 114 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 118832 C Phase DOLF 16Amp. RExcluded OMS 761615 OMS 762325 | December | 2011 | 2012Q2 | 2012 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2011-12-16 | N | 57 | N | 4 | N | N | 1.1101 | 39.4971 | 83.3078
| ZN847:PA31 | 164 | 1095.5794 | 43.3 | 6.6804 | 43.3 | 19804 | 12847 | 761757 | 2011-12-16 18:48 | 2011-12-16 19:30 | 41.8167 | 11kV | 46871.3333 | 1421 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2568 St Peters Pa16 fdr tripped on EF, Fault Check, Tx4 ZE & GE 11kV UG cable fault from Pa16 to S8251 See 762508 GIS 762532 Exclude 761757,59 | December | 2011 | 2012Q2 | 2012 | ZN2568:PA16 | ZN2568:PA16 | ZN02568/000016 | SYDNEY | UG | Not Veg | 2011-12-16 | N | 32.9848 | N | 4 | N | N | 1.1101 | 39.4971 | 34252.1879
| ZN847:PA35 | 386 | 167.1621 | #N/A | 0.43306 | 39.4971 | 18708 | 1198 | 107 | 2011-12-17 | 2011-12-17 01:36 | 95.95 | 11kV | 3646 | 38 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting Extract update(s) | December | 2011 | 2012Q2 | 2012 |  |  |  |  | Unknown | Unknown | 2011-12-17 | N | 95.9474 | N | 11 | N | N | 1.1101 | 39.4971 | 2664.3893
| ZN847:PA36 | 2120 | 1196.9462 | 36.03 | 0.5646 | 36.03 | 19870 | 13463 | 761787 | 2011-12-17 02:09 | 2011-12-17 03:40 | 91 | 11kV | 96223 | 1241 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9245 Engadine P-15 "Railway Mianga" FDR tripped & reclosed on: RELAYS: A phase Timed O/C, TSealing contactor, Reclose Lockout relays FIELD EFI's: S.48146, S.9199, UGOH in Bullecourt, S.9288 REMARKS: Suspected feeder fault in the 11 kv feeder from S.9288 Kulinia to CP 35831 Thurgona Cooriengah Tee S.9362 Kurwin Thurlgona. | December | 2011 | 2012Q2 | 2012 | ZN9245:PA13 | ZN9245:PA21 | ZN09245/000021 | SUTHERLAND | UG | Not Veg | 2011-12-17 | N | 77.5367 | N | 11 | N | N | 1.1101 | 39.4971 | 70316.9303
| ZN847:PA38 | 278 | 196.0136 | #N/A | 0.70509 | 39.4971 | 19240 | 6434 | 761861 | 2011-12-17 11:12 | 2011-12-17 11:39 | 27 | 11kV | 4185 | 155 | HV | Vandalism | 3rd Party Impact | Circuit Breaker | Unplanned | Unselected | N | LID 118837 HV earths removed from Sw 75031 Fdr off loaded to make safe Excluded OMS 761861 OMS 762365 | December | 2011 | 2012Q2 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | Unknown | Not Veg | 2011-12-17 | N | 27 | N | 11 | N | N | 1.1101 | 39.4971 | 3058.2746
| ZN847:PA39 | 1730 | 1452.0044 | 35.56 | 0.83931 | 35.56 | 19762 | 12471 | 761899 | 2011-12-17 14:23 | 2011-12-17 14:28 | 5 | 11kV | 985 | 197 | HV | Vandalism | 3rd Party Impact | Circuit Breaker | Unplanned | Unselected | N | LID 118841 eartths stolen at giants ck ragcb 11874. fdr 74058 off loaded to make safe abs 42117 Excluded OMS 761899 - incorrect times OMS 762378 | December | 2011 | 2012Q2 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | Unknown | Not Veg | 2011-12-17 | N | 5 | N | 11 | N | N | 1.1101 | 39.4971 | 719.8089
| ZN847:PA44 | 1054 | 1011.5641 | 35.79 | 0.95974 | 35.79 | 20155 | 16371 | 761918 | 2011-12-17 14:55 | 2011-12-17 15:57 | 62 | 11kV | 9548 | 154 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn35800 Bankstown Zone Pa16 fdr tripped on A/B IOC OC (50TAB), EF check (50TN) EFI - S5149 S5112 S4115 S5412 UGOH in Cottam Ave Abnormal - AB2487 def 7 open S6089SwB Tree on 11kV cnr Hoskins & Cottam Sts Bankstown removed by DOp See 762572 exclude 761918 | December | 2011 | 2012Q2 | 2012 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2011-12-17 | N | 62 | N | 11 | N | N | 1.1101 | 39.4971 | 6977.3968
| ZN847:PA45 | 492 | 963.943 | 41.16 | 1.9592 | 41.16 | 19640 | 10655 | 761912 | 2011-12-17 14:36 | 2011-12-17 17:15 | 159 | 11kV | 230530 | 1984 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.12 tripped on Timmed earth Fault, EFI 11kV feeder fault from Pnl.12 to S.18658 Sw/A to S.11973 Sw/6651 tee PT.18463 | December | 2011 | 2012Q2 | 2012 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | UG | Not Veg | 2011-12-17 | N | 116.1946 | N | 11 | N | N | 1.1101 | 39.4971 | 168464.5245
| ZN847:PA46 | 1266 | 1078.7007 | 38.42 | 0.85205 | 38.42 | 19884 | 13602 | 761954 | 2011-12-17 19:07 | 2011-12-17 20:35 | 88 | 11kV | 98286 | 1204 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Sub 3154 St Ives Panel 19 Tripped on Earth Fault ZE EFI 11kV trip UG feeder fault between LB 1831 to AB 529 to S 484 SWA tee PT 1419 Kulgoa Bristol | December | 2011 | 2012Q2 | 2012 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | UG | Not Veg | 2011-12-17 | N | 81.6329 | N | 11 | N | N | 1.1101 | 39.4971 | 71824.5099
| ZN847:PA47 | 930 | 866.5676 | 30.33 | 0.93179 | 30.33 | 19913 | 13918 | 761958 | 2011-12-17 19:31 | 2011-12-17 21:02 | 91 | 11kV | 73381 | 847 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Zn.12600 Lisarow Pnl.13 tripped on : Basler relay 51A, 51N AB41188 failed See OMS # 762299 762300 | December | 2011 | 2012Q2 | 2012 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2011-12-17 | N | 86.6364 | N | 11 | N | N | 1.1101 | 39.4971 | 53624.6704
| ZN847:PA48 | 483 | 491.597 | 61.73 | 1.0178 | 61.73 | 20216 | 17155 | 761982 | 2011-12-17 20:59 | 2011-12-17 22:17 | 78 | 11kV | 34086 | 437 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.8 tripped on B/C phase Overcurrent Defective HV connection between ABC and CCT cable between tee off to PT12291 and PT14438 | December | 2011 | 2012Q2 | 2012 | ZN12570:PA9 | ZN14144:PA8 | ZN14144/000008 | CENTRAL COAST | OH | Not Veg | 2011-12-17 | N | 78 | N | 11 | N | N | 1.1101 | 39.4971 | 24909.0434
| ZN847:PA5 | 938 | 1593.3425 | 44.49 | 1.6987 | 44.49 | 19395 | 8241 | 762004 | 2011-12-17 22:14 | 2011-12-17 23:00 | 46 | 11kV | 1104 | 24 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | LID 118843 A & B Phase DOLF : 63Amp possum flashed over ugoh possum now resting at base of pole . please check 11kV ugoh in daylight OS 39 Corristion Cr Adamstown Heights Excluded oms 762010/ 762008/762007/762006/762004 OMS 762145 | December | 2011 | 2012Q2 | 2012 | 218:7476 | 261:81886 | ZN00261/081886 | NEWCASTLE | OH | Not Veg | 2011-12-17 | N | 46 | N | 11 | N | N | 1.1101 | 39.4971 | 806.7706
| ZN847:PA7 | 1330 | 864.4775 | 36.92 | 0.64998 | 36.92 | 19422 | 8456 | 762005 | 2011-12-17 21:55 | 2011-12-18 00:17 | 142 | 11kV | 98822 | 958 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.14892 Charmhaven Pnl.14 tripped on B & C Phase Overcurrent, EFI Cause not ascertained | December | 2011 | 2012Q2 | 2012 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Veg | 2011-12-17 | N | 103.1545 | N | 11 | N | N | 1.1101 | 39.4971 | 72216.2028
| ZN129:PA34 | 434 | 815.6086 | 32.7 | 1.8793 | 32.7 | 18688 | 1039 | 762060 | 2011-12-18 11:42 | 2011-12-18 13:15 | 93 | 11kV | 93 | 1 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 118851 C Phase DOLF : 10Amp Excluded OMS 762060 LID 762385 | December | 2011 | 2012Q2 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2011-12-18 | N | 93 | N | 1 | N | N | 1.1101 | 39.4971 | 67.9617
| ZN129:PA35 | 1394 | 1742.3028 | 39.31 | 1.2499 | 39.31 | 18682 | 993 | 762342 | 2011-12-19 11:17 | 2011-12-19 12:16 | 59 | 11kV | 2110 | 36 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2466 Flemington Zone Pa32 fdr tripped on Earth Leakage Fault Check EFI EFI - S8125 Remarks - DOp Suspects UG cable fault Signals - P32 trip GE & ZE See 762844,6 Multi Sub 762861 exclude 762342,53 | December | 2011 | 2012Q2 | 2012 | ZN2466:PA32 | ZN2466:PA6 | ZN02466/000006 | CUMBERLAND | UG | Not Veg | 2011-12-19 | N | 58.6111 | N | 6 | N | N | 1.1101 | 39.4971 | 1541.9258
| ZN129:PA36 | 1178 | 966.0949 | 33.95 | 0.82011 | 33.95 | 19574 | 9683 | 762323 | 2011-12-19 10:59 | 2011-12-19 12:50 | 111 | 11kV | 999 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118863 C phase DOLF : 31 Amp Excluded OMS 762323 OMS 800259 | December | 2011 | 2012Q2 | 2012 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | OH | Veg | 2011-12-19 | N | 111 | N | 6 | N | N | 1.1101 | 39.4971 | 730.0397
| ZN129:PA38 | 1240 | 1296.2241 | 35.43 | 1.0453 | 35.43 | 19789 | 12690 | 762444 | 2011-12-19 13:36 | 2011-12-19 14:31 | 55 | 11kV | 185955 | 3381 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S35500 Top Ryde Panel 28 tripped on Relays: A and C phase IOC Cause: Tree Hit 11kV mains O/S 55 Greene St Ryde. At PT1481 Dobson Quarry 400A fuses blown on A B and C phase of distributor 1. Above Pt in parallel with Pa28 at the time of interruption. See OMS 762450 762450 76244 | December | 2011 | 2012Q2 | 2012 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2011-12-19 | N | 55 | N | 6 | N | N | 1.1101 | 39.4971 | 135890.4293
| ZN129:PA39 | 916 | 712.1102 | 30.81 | 0.77741 | 30.81 | 19940 | 14186 | 762635 | 2011-12-19 19:50 | 2011-12-19 21:00 | 70 | 11kV | 1330 | 19 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Light | N | PT13331 Brooks Hill Entrance - 11kV footpath phase DropOut fuse operated Wet tree bark across tx bushings @ PT13331 | December | 2011 | 2012Q2 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2011-12-19 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 971.9248
| ZN129:PA40 | 1192 | 849.2322 | 31.5 | 0.71244 | 31.5 | 18821 | 2287 | 762616 | 2011-12-19 18:47 | 2011-12-19 22:01 | 194 | 11kV | 970 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 118868 A & C Phase DOLF : 5Amp Excluded OMS 762616, 762639. OMS 762928, 762930 | December | 2011 | 2012Q2 | 2012 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2011-12-19 | N | 194 | N | 6 | N | N | 1.1101 | 39.4971 | 708.8474
| ZN129:PA41 | 1089 | 1031.1906 | 32.34 | 0.94692 | 32.34 | 18636 | 560 | 762638 | 2011-12-19 20:05 | 2011-12-19 22:35 | 150 | 11kV | 218623 | 2913 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn80 Chatswood Panel 32 Tripped. Signals: 11kV trip. Relays: Trip OC B and C phase Cause: Tree found in mains near PT200 Wyndarra and Has been removed. Bond burnt at tee between S6984, LB1733 and PT1854. See OMS 762891/894/896/895 | December | 2011 | 2012Q2 | 2012 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Veg | 2011-12-19 | N | 75.0508 | N | 6 | N | N | 1.1101 | 39.4971 | 159763.2401
| ZN129:PA43 | 105 | 645.6264 | 53.25 | 6.1488 | 53.25 | 19057 | 4391 | 763084 | 2011-12-20 17:22 | 2011-12-20 18:56 | 94 | 11kV | 55930 | 595 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC1239 Brooklyn Tripped Reclosed Tripped and locked out on Overcurrent Cause: Bird Caught between 11kV bonds near 128 Brooklyn Rd. See OMS 763323 763087 763084 | December | 2011 | 2012Q2 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2011-12-20 | N | 94 | N | 1 | N | N | 1.1101 | 39.4971 | 40871.9943
| ZN129:PA46 | 1586 | 1175.6623 | 38.18 | 0.74128 | 38.18 | 19463 | 8815 | 763627 | 2011-12-21 04:36 | 2011-12-21 11:45 | 429 | 11kV | 323708 | 1915 | HV | Animal Possum | Animal | O/H Link | Unplanned | Unselected | N | At S.15014 Newport, Panel 19 Fdr CB tripped :- No Protection details. OMS Connectivity different to SSystem Diagram. Possum on USL.23532, bonds burnt off USL.23532 and 23533, 11kV OH down at PT.15434 | December | 2011 | 2012Q2 | 2012 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | OH | Not Veg | 2011-12-21 | N | 169.0381 | N | 2 | N | N | 1.1101 | 39.4971 | 236556.2586
| ZN129:PA47 | 904 | 1399.0247 | 34.74 | 1.5476 | 34.74 | 19555 | 9613 | 763550 | 2011-12-21 19:30 | 2011-12-21 20:30 | 60 | 11kV | 43860 | 731 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9252 Jannali , P-11 "Victoria Alice etc" Fdr tripped, reclosed, tripped and locked out on: PROT: Leakage, EFI, lockout, timing relays ALARMS: 11kV trip, Zone Eth No.2, Group Eartth 1-2-3 T/C no volts CLC defect, C/O switch operated REMARKS: Suspect UG fault P-11 to S.9762 Victoria Alice (Haz RMI). AB 35696 closed. No.2 Aux TX isolated. region staff to arrange LV// for S.9762 and PT.9637 before test. | December | 2011 | 2012Q2 | 2012 | ZN9252:PA11 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | UG | Not Veg | 2011-12-21 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 32051.5943
| ZN129:PA49 | 1064 | 674.1502 | 37.43 | 0.6336 | 37.43 | 20366 | 19888 | 763601 | 2011-12-22 01:49 | 2011-12-22 03:25 | 96 | 11kV | 214308 | 2506 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15006 Dee Why West, Panel 9 Fdr CB tripped on A and C phase OC, efi, fault check, 11kV trip, zone earth. Field efi's operated at S.16792, S.17031, S.16733 and S.16734. Possum on UG/OH to PT.15755 (opposite #1 Westmoreland - Pole LR66585) Centre phase surge arrestor had burnt off. | December | 2011 | 2012Q2 | 2012 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | OH | Not Veg | 2011-12-22 | N | 85.518 | N | 6 | N | N | 1.1101 | 39.4971 | 156609.9654
| ZN129:PA51 | 198 | 1282.7102 | 56.39 | 6.4783 | 56.39 | 19216 | 6063 | 763707 | 2011-12-22 10:06 | 2011-12-22 11:00 | 54 | 11kV | 1188 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118912 A Phase DOLF : 31.5Amp found blown 3.15A DOLF repaced with 31.5A DOLF Excluded OMS 763707 OMS 764078 | December | 2011 | 2012Q2 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2011-12-22 | N | 54 | N | 6 | N | N | 1.1101 | 39.4971 | 868.1554
| ZN129:PA52 | 1176 | 1301.5725 | 39.08 | 1.1068 | 39.08 | 19011 | 4150 | 763726 | 2011-12-22 10:27 | 2011-12-22 11:42 | 75 | 11kV | 147712 | 2078 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN.10995 Riverwood P-1 'Meadowland Rd' fdr tripped, reclosed and locked out: PROT: C phase IOC & timed O/C SIGNALS: 11kV trip, No1 Grp Eth FIELD EFIs: S,10231 REMARKS: Suspect 11kV fault from LK 30370 to S.10418 Mercury Edgbaston. | December | 2011 | 2012Q2 | 2012 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | UG | Not Veg | 2011-12-22 | N | 71.0837 | N | 6 | N | N | 1.1101 | 39.4971 | 107943.5728
| ZN129:PA55 | 177 | 397.155 | 43.75 | 2.2438 | 43.75 | 19280 | 7183 | 763955 | 2011-12-22 16:05 | 2011-12-22 18:20 | 135 | 11kV | 4590 | 34 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex Zn.965 Pennant Hills Pnl.33 iR2691 opened due to AB2928 defective and now bonded through Abnormal Switching: LB46334 OPEN - AB1621 CLOSED | December | 2011 | 2012Q2 | 2012 | ZN965:PA33 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2011-12-22 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 3354.2366
| ZN129:PA56 | 1422 | 1556.8812 | 48.61 | 1.0949 | 48.61 | 19508 | 9116 | 764052 | 2011-12-22 22:05 | 2011-12-22 23:40 | 95 | 11kV | 570 | 6 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 118917 C Phase DOLF : 10Amp Bird caused interruption. Load readings: 239V & 14A. Excluded OMS Job No. 764052. OMS 764076 | December | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-12-22 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 416.5392
| ZN129:PA57 | 1611 | 1263.1201 | 32.61 | 0.78406 | 32.61 | 20416 | 20235 | 764059 | 2011-12-22 22:58 | 2011-12-22 23:46 | 48 | 11kV | 13632 | 284 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.5 tripped on: Basler 1.2.1 target 51AB Freshly burnt stick on ground discovered after customer advised DOp of explosion in the area, adjacent PT12277. | December | 2011 | 2012Q2 | 2012 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2011-12-22 | N | 48 | N | 6 | N | N | 1.1101 | 39.4971 | 9961.8635
| ZN129:PA62 | 360 | 355.8095 | 37.15 | 0.98836 | 37.15 | 20169 | 16551 | 764392 | 2011-12-23 16:34 | 2011-12-23 17:32 | 58 | 11kV | 116 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 118922 Fuse size: 10 Amp Refer OMS No: 764392. Volts: Aph - 244V, Bph - 245V , Cph - 242V | December | 2011 | 2012Q2 | 2012 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2011-12-23 | N | 58 | N | 2 | N | N | 1.1101 | 39.4971 | 84.7694
| ZN129:PA63 | 713 | 1739.2541 | 45.22 | 2.4393 | 45.22 | 18887 | 2993 | 764440 | 2011-12-23 23:24 | 2011-12-24 04:05 | 281 | 11kV | 141661 | 1687 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118925 Replaced blown L/A on 11kV ABC at pole HW-60198 Beach Rd - refer to OMS765311 and 765314 | December | 2011 | 2012Q2 | 2012 | 260:33347 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2011-12-23 | N | 83.9721 | N | 2 | N | N | 1.1101 | 39.4971 | 103521.6805
| ZN129:PA64 | 1814 | 1392.9987 | 31.9 | 0.76792 | 31.9 | 20110 | 16076 | 764470 | 2011-12-24 07:50 | 2011-12-24 08:31 | 41 | 11kV | 7462 | 182 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 118927, Earth Fault, Overcurrent Fdr CB 48048 did not reclose due to ac rectifer fault. Fuse found blown by Andrew Burgman. Restored from Rothbury refer to oms 764470 | December | 2011 | 2012Q2 | 2012 | 512:48048 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2011-12-24 | N | 41 | N | 7 | N | N | 1.1101 | 39.4971 | 5453.0095
| ZN10993:PA22 | 1183 | 999.2793 | 38.96 | 0.8447 | 38.96 | 18840 | 2470 | 764454 | 2011-12-24 07:20 | 2011-12-24 09:10 | 110.0667 | 11kV | 4310.8667 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118926 Fuse size: 32 Amp Also refer to 764454 and 764468, patrol required | December | 2011 | 2012Q2 | 2012 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2011-12-24 | N | 87.9769 | N | 7 | N | N | 1.1101 | 39.4971 | 3150.2542
| ZN10993:PA23 | 1678 | 1317.9024 | 45.32 | 0.7854 | 45.32 | 18967 | 3557 | 764474 | 2011-12-24 08:18 | 2011-12-24 09:30 | 72 | 11kV | 73512 | 1021 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 118925 2 Fault operations, pole mounted RAGCB, Overcurrent suspect faulty ugoh at pole IV-47044 adjacent Blackalls Sewerage sub. when supply restored trans 91942 & 91946 found tripped off. | December | 2011 | 2012Q2 | 2012 | 225:33670 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | Unknown | Unknown | 2011-12-24 | N | 72 | N | 7 | N | N | 1.1101 | 39.4971 | 53720.4014
| ZN10993:PA26 | 689 | 1421.8625 | 43.26 | 2.0637 | 43.26 | 19839 | 13100 | 764543 | 2011-12-24 12:37 | 2011-12-24 13:40 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118923 Fuse size: 32 Amp No Cause found, not storm conditions, refer to OMS 764543 | December | 2011 | 2012Q2 | 2012 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2011-12-24 | N | 63 | N | 7 | N | N | 1.1101 | 39.4971 | 46.0385
| ZN10993:PA27 | 942 | 936.3094 | 37.06 | 0.99396 | 37.06 | 18737 | 1423 | 764595 | 2011-12-24 17:27 | 2011-12-24 18:50 | 83 | 11kV | 83 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 118929, Fuse size: 10 Amp Refer OMS No: 764595 Volts: 245V | December | 2011 | 2012Q2 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2011-12-24 | N | 83 | N | 7 | N | N | 1.1101 | 39.4971 | 60.654
| ZN10993:PA33 | 767 | 1093.8682 | 43.58 | 1.4262 | 43.58 | 19039 | 4285 | 764608 | 2011-12-24 18:34 | 2011-12-24 21:05 | 151 | 11kV | 156603 | 2913 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.80 Chatswood P-32 RHS "S.5279 Helen Shore Motel" tripped with 11kV trip, LHS - alarm LED, EFI, RHS - Alarm LED, Trip B to C phase Oversurrent and EFI EFIs down - S.5279, 4221, 6433 & 6278 REMARKS; large tree branch on 11kV OH near tee to S.2385Greenwich Hospital between LB 1733 & AB 1994 | December | 2011 | 2012Q2 | 2012 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Veg | 2011-12-24 | N | 53.76 | N | 7 | N | N | 1.1101 | 39.4971 | 114440.8534
| ZN10993:PA34 | 1103 | 1112.8238 | #N/A | 1.0089 | 39.4971 | 19893 | 13678 | 764628 | 2011-12-24 22:11 | 2011-12-25 09:00 | 649 | 11kV | 9735 | 15 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | At PT.12658 Marlow Creek No.1 16 Amp HDO creek side operated. Ex S.12630 Peats Ridge Panel No.2 "Peats Island Fdr" REMARKS: Flashover due to possum, removed, supply restored ok. | December | 2011 | 2012Q2 | 2012 | ZN12630:PA2 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2011-12-24 | N | 649 | N | 7 | N | N | 1.1101 | 39.4971 | 7114.0509
| ZN10993:PA35 | 816 | 1162.7734 | 45.85 | 1.425 | 45.85 | 19786 | 12670 | 764662 | 2011-12-25 09:51 | 2011-12-25 11:35 | 104 | 11kV | 178323 | 1952 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.12610 Long jetty 11kv fdr P-13 "Blue bay' fdr tripped on: RELAYS: E/F & EFI FIELD EFIs: Nil REMARKS: No cause ascertained NOTE: refer Subs to repair/replace field EFI at UGOH on Boondila Rd | December | 2011 | 2012Q2 | 2012 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Veg | 2011-12-25 | N | 91.354 | N | 1 | N | N | 1.1101 | 39.4971 | 130313.1888
| ZN10993:PA39 | 828 | 725.5654 | 36.44 | 0.87629 | 36.44 | 19581 | 9732 | 764742 | 2011-12-26 00:48 | 2011-12-26 02:05 | 77 | 11kV | 4851 | 63 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 118933 Fuse size 31 Amp Possum on arresters at sub. Possum removed & blown DOLF's replaced OK. As left 243V - 125A, 100A & 145A. OMS No's 764742, 764743 & 764745. | December | 2011 | 2012Q2 | 2012 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2011-12-26 | N | 77 | N | 6 | N | N | 1.1101 | 39.4971 | 3544.9677
| ZN10993:PA43 | 1412 | 770.1155 | #N/A | 0.54541 | 39.4971 | 20069 | 15784 | 764746 | 2011-12-26 05:47 | 2011-12-26 07:25 | 98 | 11kV | 392 | 4 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 118934 Fuse size: 10 Amp Possum on Tx. 245 volts. 6 amps oms 764746 | December | 2011 | 2012Q2 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2011-12-26 | N | 98 | N | 6 | N | N | 1.1101 | 39.4971 | 286.462
| ZN9252:PA21 | 958 | 1007.2656 | 38.23 | 1.0514 | 38.23 | 19686 | 11380 | 764758 | 2011-12-26 07:24 | 2011-12-26 09:40 | 136 | 11kV | 378 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118936 and 118937 Fuse Size: 10 Amp protection did not grade cause not ascertained, refer to OMS 764758, 765195 and 765196 | December | 2011 | 2012Q2 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2011-12-26 | N | 126 | N | 6 | N | N | 1.1101 | 39.4971 | 276.2313
| ZN9252:PA22 | 1558 | 1046.88 | 31.73 | 0.67194 | 31.73 | 18819 | 2274 | 764775 | 2011-12-26 09:12 | 2011-12-26 13:10 | 238 | 11kV | 714 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118938, Fuse size 10Amp also refer 764775 | December | 2011 | 2012Q2 | 2012 | 501:48117 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2011-12-26 | N | 238 | N | 6 | N | N | 1.1101 | 39.4971 | 521.7701
| ZN9252:PA24 | 1989 | 1679.4581 | 32.76 | 0.84437 | 32.76 | 19026 | 4222 | 764817 | 2011-12-26 14:17 | 2011-12-26 15:25 | 68 | 11kV | 204 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 118940: Fuse size: 10 Amp Fuse element Fatigue Refer OMS # 764817 | December | 2011 | 2012Q2 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2011-12-26 | N | 68 | N | 6 | N | N | 1.1101 | 39.4971 | 149.0772
| ZN9252:PA25 | 881 | 911.6044 | 31.09 | 1.0347 | 31.09 | 18619 | 382 | 764863 | 2011-12-26 21:33 | 2011-12-26 23:46 | 133 | 11kV | 212856 | 1842 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | OMS 118942, 118943. 1 Fault operations, Sensitive Earth Fault Removed palm branch from OHM at pole IV-31387. Refer OMS 765850, 765849 Records Withdrawn: 765085;765084;765082;764865;764864 | December | 2011 | 2012Q2 | 2012 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2011-12-26 | N | 115.557 | N | 6 | N | N | 1.1101 | 39.4971 | 155548.8866
| ZN9252:PA27 | 1740 | 1704.2166 | 31.36 | 0.97943 | 31.36 | 19714 | 11884 | 764876 | 2011-12-27 04:44 | 2011-12-27 06:33 | 109.6667 | 11kV | 31364.6667 | 286 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Recloser 428 Bayfield Rd tripped. Ex P-47 Hornsby. REMARKS: DOp patrolled, no cause found CC1: 22-"Refer to SOp" | December | 2011 | 2012Q2 | 2012 | ZN847:PA47 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2011-12-27 | N | 109.6667 | N | 3 | N | N | 1.1101 | 39.4971 | 22920.3733
| ZN9252:PA28 | 1776 | 1622.6 | 32.26 | 0.91363 | 32.26 | 19184 | 5408 | 764871 | 2011-12-27 00:46 | 2011-12-27 10:21 | 575 | 11kV | 158006 | 1231 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.12660 Woy Woy 11kv fdr P-8 "North Burge rd' fdr tripped on: RELAYS: c phase overcurrent, Earth fault, EFI, lockout led SIGNALS: 11kV trip FIELD EFIs: S.18313 REMARKS: 11kV down beyond LB 45205. Appears to be fatigue. | December | 2011 | 2012Q2 | 2012 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2011-12-27 | N | 128.3558 | N | 3 | N | N | 1.1101 | 39.4971 | 115466.1244
| ZN9252:PA30 | 1318 | 1022.158 | 31.58 | 0.77554 | 31.58 | 19992 | 14903 | 764992 | 2011-12-27 13:54 | 2011-12-27 21:10 | 436 | 11kV | 262352 | 2909 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 118949 Mains down into trees Thurlow Ave x Christmas bush Ave, Nelson Bay. Tappings burnt off on restoration at pole OR-30282 feed to sub 2683. OMS No's 764992/993 & 994 withdrawn, replaced with 765282, 765281, 765280 and 765279 | December | 2011 | 2012Q2 | 2012 | 232:11459 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2011-12-27 | N | 90.1863 | N | 3 | N | N | 1.1101 | 39.4971 | 191719.1035
| ZN9252:PA31 | 1489 | 1192.2409 | 31.1 | 0.8007 | 31.1 | 19926 | 14068 | 765070 | 2011-12-28 00:36 | 2011-12-28 01:54 | 78 | 11kV | 4714 | 72 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.35500 Top Ryde P-14 "Richardson Place No.3 etc" feeder tripped on: RELAYS: Earth Fault & Under frequency SIGNALS: TX.2 Grp Eth, Prot Trip FIELD EFIs: S.8899, S.8900, S.8, S.7888, S.7889 & S.7979 REMARKS: Suspect UG cable fault from S.7979 Richardson Leda No.1 (SwB) to S.1869 Delhi Fujitsu (SwB) | December | 2011 | 2012Q2 | 2012 | ZN35500:PA14 | ZN35500:PA14 | ZN35500/000014 | RYDE | UG | Not Veg | 2011-12-28 | N | 65.4722 | N | 5 | N | N | 1.1101 | 39.4971 | 3444.8522
| 258:80773 | 384 | 761.0069 | 44.39 | 1.9818 | 44.39 | 20237 | 17439 | 765128 | 2011-12-28 09:04 | 2011-12-28 10:30 | 86 | 11kV | 86 | 1 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118953 Fuse size: 10 Amp Bird. As left volts = 245. Amps = 4. OMS # 765128 - Note not advised as to what the bird came into contact with | December | 2011 | 2012Q2 | 2012 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2011-12-28 | N | 86 | N | 5 | N | N | 1.1101 | 39.4971 | 62.8463
| 258:80775 | 2043 | 1173.7208 | 31.2 | 0.57451 | 31.2 | 19534 | 9426 | 765149 | 2011-12-28 09:32 | 2011-12-28 10:48 | 75.5 | 11kV | 30621.6333 | 690 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7900 Campbell St Pa7 11kv fdr tripped on EF, EFI, EFC Alarms: Tx1 GE Suspect UG cable from S133 Goodchip st No3 RMCB to S35851 Reservoir Riley No1 See 767479 767480 exclude 765151 765149 | December | 2011 | 2012Q2 | 2012 | ZN7900:PA7 | ZN7900:PA7 | ZN07900/000007 | SYDNEY | UG | Not Veg | 2011-12-28 | N | 44.3792 | N | 5 | N | N | 1.1101 | 39.4971 | 22377.3865
| 258:80776 | 375 | 475.733 | 47.09 | 1.2686 | 47.09 | 20065 | 15769 | 765273 | 2011-12-28 12:37 | 2011-12-28 13:30 | 53 | 11kV | 17596 | 332 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118956 2 Fault operations, overcurrent, earth fault Surge arrester at Sw 42013 faulty. Changed under A/P. Targets: A ph O/C, E/F. | December | 2011 | 2012Q2 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2011-12-28 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 12858.6378
| 258:80778 | 1236 | 1145.5038 | 36.11 | 0.92678 | 36.11 | 19345 | 7621 | 765457 | 2011-12-28 20:35 | 2011-12-28 22:40 | 125 | 11kV | 4375 | 35 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 118958 Section isolated for emergency repairs, pole replacement. Pole damaged possibly by car over christmas, not witnessed. refer OMS 765457 | December | 2011 | 2012Q2 | 2012 | 218:7482 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Not Veg | 2011-12-28 | N | 125 | N | 5 | N | N | 1.1101 | 39.4971 | 3197.121
| 258:80779 | 1169 | 937.9825 | 33.62 | 0.80238 | 33.62 | 20011 | 15008 | 765629 | 2011-12-29 12:28 | 2011-12-29 16:05 | 217 | 11kV | 308.25 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | CC1: 19-"Complete - Network related fault" FRC1: 300-"Specify details by voice" LID 118961 No protection operated, outage caused by 11kV Live Line connector coming loose and falling away. Note: also referred this nmi to GIS corrections to check electrical connectivity of the model Refer OMS 765629 and 765826 CC1: 06-"Urgent - O.H Mains - No others" FRC1: 300-"Specify details by voice" | December | 2011 | 2012Q2 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2011-12-29 | N | 154.125 | N | 5 | N | N | 1.1101 | 39.4971 | 225.26
| 258:80781 | 1531 | 1257.3856 | 35.95 | 0.82128 | 35.95 | 19397 | 8308 | 765924 | 2011-12-29 15:40 | 2011-12-29 16:37 | 57 | 11kV | 84612 | 1556 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9037 Miranda P-10 "Kumbardang Kiora" etc fdr tripped/closed/tripped on. RELAYS: C phase IOC with sealing contactor, Lockout, & EFI SIGNALS: 11kV trip, Zone Earth, TX.3 Grp Eth, EFIs DOWN: S.9516, S.9795 & S.9634 REMARKS: 11kV UG feeder fault between S.9634 to S.9005 to S.9503 | December | 2011 | 2012Q2 | 2012 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | UG | Not Veg | 2011-12-29 | N | 54.3779 | N | 5 | N | N | 1.1101 | 39.4971 | 61831.954
| 258:80784 | 1748 | 1304.5967 | 34.58 | 0.74634 | 34.58 | 19724 | 12017 | 765712 | 2011-12-29 15:40 | 2011-12-29 17:20 | 99.7833 | 11kV | 132.0167 | 2 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9037 Miranda P-10 "Kumbardang Kiora" etc fdr tripped/closed/tripped on. RELAYS: C phase IOC with sealing contactor, Lockout, & EFI SIGNALS: 11kV trip, Zone Earth, TX.3 Grp Eth, EFIs DOWN: S.9516, S.9795 & S.9634 REMARKS: 11kV UG feeder fault between S.9634 to S.9005 to S.9503 Refer to GIS corrections for investigation, however unlikely as too far from a connection point between panles on LV network. CC1: 22-"Refer to SOp" | December | 2011 | 2012Q2 | 2012 | ZN9035:PA11 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | UG | Not Veg | 2011-12-29 | N | 66.0083 | N | 5 | N | N | 1.1101 | 39.4971 | 96.4739
| 258:80785 | 1519 | 1599.3724 | 38.76 | 1.0529 | 38.76 | 20420 | 20242 | 765783 | 2011-12-29 19:42 | 2011-12-29 20:03 | 21 | 11kV | 2877 | 137 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | Unselected | N | At ZN.931 Darlinghurst the 11kv P-26 "S.8491 etc" fdr CB had tripped SIGNALS: 11kV trip, TX.2 GE, ZE RELAYS: EFI, B phase EF OC trip FIELD EFIs: Nil REMARKS: The 11kV feeder from ZN.931 Darlinghurst ti S,8491 Forbes Boiurke (Sw/A) has failed | December | 2011 | 2012Q2 | 2012 | ZN931:PA26 | ZN931:PA26 | ZN00931/000026 | SYDNEY | UG | Not Veg | 2011-12-29 | N | 21 | N | 5 | N | N | 1.1101 | 39.4971 | 2102.4267
| 258:80787 | 1919 | 1426.9297 | 35.05 | 0.74358 | 35.05 | 19131 | 4848 | 765808 | 2011-12-30 01:03 | 2011-12-30 01:55 | 52 | 11kV | 77428 | 1489 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | At ZN.12580 Erina 11kV fdr P-10 "Erina High Ernest" tripped RELAYS: Nil FIELD EFIs: Nil REMARKS: No signals or relays operated at Zone or in field Tpe to investigate | December | 2011 | 2012Q2 | 2012 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | UG | Not Veg | 2011-12-30 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 56582.0987
| 258:80790 | 826 | 602.478 | 37.49 | 0.72939 | 37.49 | 19254 | 6568 | 765803 | 2011-12-29 22:35 | 2011-12-30 06:04 | 448.5667 | 11kV | 6330.35 | 13 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 118962 Fuse size: 16 Amp sub dolf blown, HV & LV earths stolen at sub. sub isolated & left interconnected on LV. | December | 2011 | 2012Q2 | 2012 | 238:34144 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Not Veg | 2011-12-29 | N | 486.95 | N | 5 | N | N | 1.1101 | 39.4971 | 4626.0331
| 258:80791 | 854 | 601.2024 | 43.22 | 0.70398 | 43.22 | 18818 | 2271 | 765828 | 2011-12-30 07:55 | 2011-12-30 09:05 | 70 | 11kV | 13440 | 192 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of P-11 from ZN.12610 Long Jetty REMARKS: DOp found ph bond burnt off at AB42091 | December | 2011 | 2012Q2 | 2012 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2011-12-30 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 9821.5556
| 258:80793 | 1488 | 1222.5199 | 34.12 | 0.82159 | 34.12 | 19905 | 13795 | 766090 | 2011-12-30 16:45 | 2011-12-30 17:20 | 35 | 11kV | 245 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 118972 Interruption for the repair of Live Line Clamp Faulty LL Clamps sub 53120 broken under A/P Excluded OMS 766090 OMS 766651 | December | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-12-30 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 179.0388
| 258:80794 | 5 | 32.2132 | 44.86 | 6.4426 | 44.86 | 20059 | 15656 | 765949 | 2011-12-30 13:15 | 2011-12-30 20:17 | 422 | 11kV | 844 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 118971 B phase DOLF : 10Amp Faulty arrestors replaced under A/P Faulty LL Clamps broken under A/P see report 118972 Faulty trans replaced under A/P Excluded OMS 765949 OMS 766650 | December | 2011 | 2012Q2 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2011-12-30 | N | 422 | N | 4 | N | N | 1.1101 | 39.4971 | 616.7703
| 220:8687 | 1587 | 1116.4151 | 33.16 | 0.70348 | 33.16 | 19261 | 6635 | 766280 | 2011-12-31 21:40 | 2011-12-31 23:00 | 80 | 11kV | 119382 | 2585 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 118978 1 fault operation faulty UGHO at pole JU-61270 Excluded OMS 766280, 766281, 766283 OMS 766789, 766791 | December | 2011 | 2012Q2 | 2012 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | Unknown | Unknown | 2011-12-31 | N | 46.1826 | N | 1 | N | N | 1.1101 | 39.4971 | 87240.8444
| 220:8688 | 453 | 340.4101 | 29.27 | 0.75146 | 29.27 | 20145 | 16294 | 766291 | 2012-01-01 02:18 | 2012-01-01 03:42 | 84 | 11kV | 72369 | 1223 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S2400 Berowra Panel 15 tripped on relays: A phase Overcurrent, Earth Fault and EFI. Signals: 11kV Trip. Report of explosion near Oxley Drive. Dop patrolled but could not find anything. Mains/Dop to patrol in daylight hours. See 766779 766780 | January | 2012 | 2012Q3 | 2012 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2012-01-01 | N | 59.1733 | N | 3 | N | N | 1.1101 | 39.4971 | 52885.1307
| 220:8689 | 1541 | 1078.208 | 38.13 | 0.69968 | 38.13 | 19432 | 8525 | 766295 | 2012-01-01 05:06 | 2012-01-01 06:07 | 61 | 11kV | 94314 | 1668 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S.2310 Punchbowl Panel 31 "Roselands no.4" fdr tripped. Relays - C phase overcurrent, EFI Signals - 11kv trip, Tx4 group earth, Zone earth EFI's - S.4689, S.2856, S.3435 Remarks: Underground cable fault between S.3435 McCourt Punchbowl and S.2625 Hillard St Related jobs: #766640, 766642, 766295 | January | 2012 | 2012Q3 | 2012 | ZN2310:PA31 | ZN35800:PA2 | ZN35800/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-01-01 | N | 56.5432 | N | 3 | N | N | 1.1101 | 39.4971 | 68921.8894
| 220:8691 | 1178 | 1247.7618 | 38.25 | 1.0592 | 38.25 | 19985 | 14873 | 766294 | 2012-01-01 03:52 | 2012-01-01 09:58 | 366 | 11kV | 47493 | 332 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 128980 5 fault operations Earth fault Fruit bat brought mains down beyond Lk 40710 AP issued for repairs excluded OMS 766294, 766300 OMS 766710, 766717, 766718, 766720, 766722, 766723, 766725, 766727, 766730, 766731, 766733, 766738, 766739 | January | 2012 | 2012Q3 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-01-01 | N | 143.0512 | N | 3 | N | N | 1.1101 | 39.4971 | 34706.4836
| 220:8692 | 894 | 901.6606 | 34.21 | 1.0086 | 34.21 | 19444 | 8587 | 766412 | 2012-01-02 08:22 | 2012-01-02 09:25 | 63 | 11kV | 252 | 4 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | LID 128986 A phase DOLF : 10 Amp Dead Cockatoo found at base of pole. Volts: Aph - 245V, Bph - 248V, Cph - 248V Excluded OMS No.: 766412. OMS 766754 | January | 2012 | 2012Q3 | 2012 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2012-01-02 | N | 63 | N | 2 | N | N | 1.1101 | 39.4971 | 184.1542
| ZN15012:PA2 | 1372 | 1263.7629 | 32.57 | 0.92111 | 32.57 | 18731 | 1370 | 766391 | 2012-01-02 03:28 | 2012-01-02 09:28 | 360 | 11kV | 7943 | 559 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | HV fuse blown at PT 1947 Cause was Possum | January | 2012 | 2012Q3 | 2012 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2012-01-02 | N | 14.2093 | N | 2 | N | N | 1.1101 | 39.4971 | 5804.5101
| ZN15012:PA4 | 1232 | 963.6933 | 30.67 | 0.78222 | 30.67 | 18781 | 1936 | 766639 | 2012-01-03 09:37 | 2012-01-03 11:00 | 82.65 | 11kV | 6529.35 | 79 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Recloser 45017 WWhiteman opened by D.OP to affect emergency repairs after previous car hit pole | January | 2012 | 2012Q3 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2012-01-03 | N | 82.65 | N | 5 | N | N | 1.1101 | 39.4971 | 4771.4564
| ZN15012:PA6 | 1470 | 1362.53 | 35.56 | 0.92689 | 35.56 | 18897 | 3096 | 766868 | 2012-01-03 12:21 | 2012-01-03 16:45 | 264 | 11kV | 1584 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 118995 A Phase DOLF : 16 Amp exclude OMS 766868 OMS 767044 | January | 2012 | 2012Q3 | 2012 | 227:13020 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2012-01-03 | N | 264 | N | 5 | N | N | 1.1101 | 39.4971 | 1157.5405
| ZN15012:PA8 | 1177 | 1275.1505 | 37.88 | 1.0834 | 37.88 | 19935 | 14136 | 766905 | 2012-01-03 16:48 | 2012-01-03 17:30 | 42 | 11kV | 36834 | 877 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 128996 2 fault operations B & C Phase Overcurrent magpie in mains at pole IR-71204 Brunswick x Rous St . excluded OMS 766905, 766907, 766909, 766913, 766914, 766916, 766918 OMS 767075 | January | 2012 | 2012Q3 | 2012 | 503:48012 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Not Veg | 2012-01-03 | N | 42 | N | 5 | N | N | 1.1101 | 39.4971 | 26917.2008
| ZN35600:PA1 | 2676 | 2283.6102 | 37.69 | 0.85337 | 37.69 | 20285 | 18402 | 766958 | 2012-01-03 21:07 | 2012-01-03 22:47 | 100 | 11kV | 72326 | 848 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.12600 Lisarow, Panel 13 Fdr CB tripped on B and C phase OC, 11kV trip. Cause not found | January | 2012 | 2012Q3 | 2012 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2012-01-03 | N | 85.2901 | N | 5 | N | N | 1.1101 | 39.4971 | 52853.7075
| ZN35600:PA10 | 508 | 354.3823 | 36.98 | 0.6976 | 36.98 | 18862 | 2671 | 766971 | 2012-01-04 02:14 | 2012-01-04 04:15 | 121 | 11kV | 22997 | 202 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.14891 Wyong, Panel 19 Fdr CB tripped on earth fault relay and efi. 11kV trip and #2 Tx group Earth. Field efi down at S.14737. Suspect UG cable fault between S.14737 and S.46808 tee AB.44880 | January | 2012 | 2012Q3 | 2012 | ZN14891:PA19 | ZN14891:PA19 | ZN14891/000019 | CENTRAL COAST | UG | Not Veg | 2012-01-04 | N | 113.8465 | N | 20 | Y | Y | 1.1101 | 39.4971 | 16805.5293
| ZN35600:PA12 | 712 | 619.6102 | 30.26 | 0.87024 | 30.26 | 20251 | 17757 | 766916 | 2012-01-03 17:22 | 2012-01-04 05:00 | 698 | 11kV | 91271 | 1591 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 128997 2 fault operations B & C Phases Instantaneous Overcurrent Faulty UGOH at pole IU-50799 AB Rea sub. Excluded OMS 766916, 766918 OMS 767145, 767146, 767143 | January | 2012 | 2012Q3 | 2012 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | Unknown | Unknown | 2012-01-03 | N | 57.3671 | N | 5 | N | N | 1.1101 | 39.4971 | 66698.1548
| ZN35600:PA14 | 1934 | 1300.8506 | 39.71 | 0.67262 | 39.71 | 19148 | 4913 | 767096 | 2012-01-04 10:31 | 2012-01-04 12:02 | 91 | 11kV | 64365 | 795 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | UGOH between Sub 16642 Oates Forest Way, Sub 16494 Wyatt Forest Way and LB 22982 has failed. Surge arrestor at UGOH has blown. Also Smoke was found in switchroom at belorse Zone(No cause found) At Zn 15005 Belrose the 11kV Feeder Pnl 10 "Forest Way Dawes" feeder has tripped reclosed and tripped. Signals: 11kV Trip, ZE | January | 2012 | 2012Q3 | 2012 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | Unknown | Unknown | 2012-01-04 | N | 80.9623 | N | 20 | Y | Y | 1.1101 | 39.4971 | 47036.0436
| ZN35600:PA16 | 3291 | 2404.975 | 37.58 | 0.73077 | 37.58 | 19000 | 3998 | 767172 | 2012-01-04 12:43 | 2012-01-04 14:15 | 92 | 11kV | 1380 | 15 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | Unselected | N | @Sub 6641 Park Reents Park No3 Tx 1 tee switch tripped. HV fuse blown C phase 90 Amp Remarks: @ Sub 6641 Park Regents Park No3 the No1 transformer tripped de energising the section 1 busbar and interrupting three distributors 1,2 & 3. The No 1 transformer is now isolated and earthed with A/P's issued @ Sub 6641 park Regents Park No 3 Related jobs: #769667, 769665, 767172, 767179, 767180 | January | 2012 | 2012Q3 | 2012 | ZN3472:PA16 | ZN3472:PA16 | ZN03472/000016 | CUMBERLAND | UG | Not Veg | 2012-01-04 | N | 92 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1008.4633
| ZN35600:PA17 | 2 | 276.4295 | #N/A | 138.2147 | 39.4971 | 19112 | 4696 | 767191 | 2012-01-04 13:13 | 2012-01-04 14:40 | 87 | 11kV | 80805 | 1104 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | @Zn 1287 Revesby Panel 5 Davis Bank No 3 Feeder Relays: - Earth fault, Fault check relay, EFI and lock out relay Signals - Zone earth, Group earth and 11kv feeder trip Remarks: 11kv feeder isolated and earthed from Sub 6360 Davies banks No3 Sw D to Sub 6525 Davies Banks No1 to Sub 4665 Davies Banks No2 tee to PT 1671 Bridge Davies. Fault located on the UGOH to PT 1671 Bridge Davies Related jobs: #767197, 767191, 767731, 767730, 767729 | January | 2012 | 2012Q3 | 2012 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2012-01-04 | N | 73.1929 | N | 20 | Y | Y | 1.1101 | 39.4971 | 59049.9107
| ZN35600:PA19 | 2755 | 1792.8436 | 37.42 | 0.65076 | 37.42 | 20055 | 15645 | 767177 | 2012-01-04 12:48 | 2012-01-04 14:44 | 116 | 11kV | 104981 | 1114 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At ZN.10990 Arncliffe 11kv fdr P-1 "Stanley BARDEN' etc tripped on signals: Earth Leakage, EFI, F Check, SSL relay REMARKS: DOp reports 11kV UGOH to S.10880 Knights Forest defective | January | 2012 | 2012Q3 | 2012 | ZN10990:PA1 | ZN10998:PA3 | ZN10998/000003 | BAYSIDE | Unknown | Unknown | 2012-01-04 | N | 94.2379 | N | 20 | Y | Y | 1.1101 | 39.4971 | 76717.0184
| ZN35600:PA2 | 1290 | 648.005 | 30.51 | 0.50233 | 30.51 | 18621 | 397 | 767164 | 2012-01-04 13:50 | 2012-01-04 14:50 | 60 | 11kV | 60 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129009 A phase 11KV LEAD TO DOLF BURNT OFF. Excluded OMS 767164 | January | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2012-01-04 | N | 60 | N | 20 | Y | Y | 1.1101 | 39.4971 | 43.8462
| ZN35600:PA20 | 207 | 294.1287 | #N/A | 1.4209 | 39.4971 | 20050 | 15599 | 767259 | 2012-01-04 14:07 | 2012-01-04 14:50 | 43 | 11kV | 43 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129010 A phase DOLF : 10 Amp Excluded OMS 767259 OMS 767875 | January | 2012 | 2012Q3 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2012-01-04 | N | 43 | N | 20 | Y | Y | 1.1101 | 39.4971 | 31.4231
| ZN35600:PA22 | 1860 | 1238.1752 | 39.8 | 0.66569 | 39.8 | 19125 | 4830 | 768270 | 2012-01-04 13:34 | 2012-01-04 15:05 | 91 | 11kV | 58746 | 769 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S965 Pennant Hills Panel 4 Tripped Reclosed Tripped and locked out on Earth Fault, Timer, Lockout and EFI. Alarms: Zone Earth Tx1 Group Earth and 11kV Trip. Cause not ascertined mains to patrol in daylight - See OMS 768270/272/274/275 767252 767219 | January | 2012 | 2012Q3 | 2012 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Veg | 2012-01-04 | N | 76.3927 | N | 20 | Y | Y | 1.1101 | 39.4971 | 42929.8441
| ZN35600:PA25 | 1322 | 895.5807 | 39.38 | 0.67744 | 39.38 | 19363 | 7823 | 767219 | 2012-01-04 13:34 | 2012-01-04 15:20 | 106 | 11kV | 5300 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Unselected | N | At S7350 James Henty New LIne 400A fuse blown on AB and C phase of distributor 2. Cause: LV Parallel failed as a result of feeder outage below. At S965 Pennant Hills Panel 4 Tripped Reclosed Tripped and locked out on Earth Fault, Timer, Lockout and EFI. Alarms: Zone Earth Tx1 Group Earth and 11kV Trip. Cause not ascertined mains to patrol in daylight - See OMS 768270/272/274/275 767252 767219 | January | 2012 | 2012Q3 | 2012 | ZN965:PA46 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Veg | 2012-01-04 | N | 106 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3873.0837
| ZN35600:PA3 | 2592 | 3116.0595 | 39.62 | 1.2022 | 39.62 | 18877 | 2872 | 767374 | 2012-01-04 17:20 | 2012-01-04 18:10 | 50 | 11kV | 50 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129020 A phase DOLF : 10 Amp excluded OMS 767374 OMS 767885 | January | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-01-04 | N | 50 | N | 20 | Y | Y | 1.1101 | 39.4971 | 36.5385
| ZN35600:PA4 | 1070 | 1209.1557 | 37.54 | 1.1301 | 37.54 | 20135 | 16194 | 767356 | 2012-01-04 17:09 | 2012-01-04 18:19 | 70 | 11kV | 97650 | 1395 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | @ Zn116 Leichhardt Panel 44 Ainsworth Piper Feeder Relays - Overcurrent A & B phases Signals - 11kv trip Remarks: Tree branch on wires in Moody St near Sub 1436 Callan Park No.1 Related jobs:#767356, 767701 | January | 2012 | 2012Q3 | 2012 | ZN116:PA44 | ZN116:PA31 | ZN00116/000031 | INNER WEST | OH | Veg | 2012-01-04 | N | 70 | N | 20 | Y | Y | 1.1101 | 39.4971 | 71359.7398
| ZN35600:PA6 | 1265 | 1250.6531 | 38.65 | 0.98866 | 38.65 | 19583 | 9734 | 767399 | 2012-01-04 17:33 | 2012-01-04 19:12 | 99 | 11kV | 87417 | 883 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | @Zn2196 Milperra Panel 3 Beaconsfield Horsley feeder. Relay: - B & C phase IOC + timed, Timing relay + lock out relay Signals - 11KV trip Remarks: No cause ascertained Related jobs: #767548, 770138, 767399 | January | 2012 | 2012Q3 | 2012 | ZN2196:PA3 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-01-04 | N | 99 | N | 20 | Y | Y | 1.1101 | 39.4971 | 63881.7652
| ZN35600:PA7 | 1381 | 612.7738 | 33 | 0.44372 | 33 | 19655 | 10897 | 767323 | 2012-01-04 16:05 | 2012-01-04 19:57 | 232 | 11kV | 180875 | 1223 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 129021 2 fault operations B & C phase Overcurrent No. 1 Prot. B&C Phase OC. B Phase leg of UGOH has signs of burning. Isolated at Sw 14960 and Open Taps on pole JR-90832.. Excluded OMS 767323, 767332, 767357 OMS 767811, 767813, 767818 | January | 2012 | 2012Q3 | 2012 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | Unknown | Unknown | 2012-01-04 | N | 147.8945 | N | 20 | Y | Y | 1.1101 | 39.4971 | 132178.1151
| ZN35600:PA9 | 3034 | 2077.5921 | 35.96 | 0.68477 | 35.96 | 20413 | 20214 | 767536 | 2012-01-04 20:07 | 2012-01-04 21:16 | 68.8667 | 11kV | 153337.1 | 2746 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3155 Double Bay Zone 11kv fdr pa23 tripped on: Relays: Timed O/C EFI Fault Check Field EFI S48928 S2816 11kv fdr failure from S2816 to S8234 Note HAZ at S2816 will require extending for testers once LV// organized See 770209,10 LV// 770180 GIS 770203,6 Exclude 767553,7,62,7,8,70 | January | 2012 | 2012Q3 | 2012 | ZN3155:PA23 | ZN3155:PA40 | ZN03155/000040 | WOOLLAHRA | UG | Not Veg | 2012-01-04 | N | 55.8402 | N | 20 | Y | Y | 1.1101 | 39.4971 | 112054.23
| ZN9700:PA11 | 963 | 656.2884 | 44.21 | 0.6815 | 44.21 | 19910 | 13901 | 767571 | 2012-01-04 18:20 | 2012-01-04 21:29 | 189 | 11kV | 9915 | 121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | S4704 Bannockburn Princes B Phase HV 40A OQFRN operated Trees on LV near 9 Coolabah Ave Turramurra | January | 2012 | 2012Q3 | 2012 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | OH | Veg | 2012-01-04 | N | 81.9421 | N | 20 | Y | Y | 1.1101 | 39.4971 | 7245.5896
| ZN9700:PA12 | 906 | 1223.886 | 50.56 | 1.3509 | 50.56 | 18659 | 752 | 767175 | 2012-01-04 15:30 | 2012-01-04 22:00 | 390 | 11kV | 390 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129023 C Phase HV bond BURNT OFF HV TAPPING AT POLE IQ-42202 WOODVILLE. Excluded OMS REPORT NO 767175. OMS 767862 | January | 2012 | 2012Q3 | 2012 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2012-01-04 | N | 390 | N | 20 | Y | Y | 1.1101 | 39.4971 | 285.0005
| ZN9700:PA15 | 1243 | 1209.9981 | 31.34 | 0.97345 | 31.34 | 20232 | 17399 | 767470 | 2012-01-04 18:36 | 2012-01-04 22:30 | 234 | 11kV | 1872 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S2728 Epping Boys High. 25A HV fuse operated. Dop reported Tree On mains - Sub restored via LV parallel. See OMS 768405 767558 767516 | January | 2012 | 2012Q3 | 2012 | ZN2635:PA2 | ZN2635:PA59 | ZN02635/000059 | RYDE | OH | Veg | 2012-01-04 | N | 234 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1368.0024
| ZN9700:PA16 | 834 | 587.8427 | 29.67 | 0.70485 | 29.67 | 19288 | 7263 | 767435 | 2012-01-04 17:30 | 2012-01-04 23:30 | 360 | 11kV | 172888.2 | 1482 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.847 Hornsby Panel 21 Tripped and reclosed and locked out on A phase IOC and Timed LO and timer. Branch removed from 11kV O/S 54 Manor Rd Near PT1566 See OMS 767400/381/392 | January | 2012 | 2012Q3 | 2012 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2012-01-04 | N | 116.6587 | N | 20 | Y | Y | 1.1101 | 39.4971 | 126341.5972
| ZN9700:PA17 | 2313 | 2274.1364 | 33.81 | 0.9832 | 33.81 | 20074 | 15811 | 767766 | 2012-01-04 19:07 | 2012-01-04 23:50 | 283 | 11kV | 17722 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 44607 Matcham North tripped/reclosed/tripped and locked out on A phase OC and earth fault. At Zn.14144 Wamberal OPanel 10 efi and #2 Group Earth. Tree branch on 11kV OH near PT.13453. 11kV bond burnt off near PT.11815 | January | 2012 | 2012Q3 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2012-01-04 | N | 188.5319 | N | 20 | Y | Y | 1.1101 | 39.4971 | 12950.7149
| ZN9700:PA18 | 2485 | 1811.4304 | 32.79 | 0.72895 | 32.79 | 19319 | 7449 | 767605 | 2012-01-05 00:06 | 2012-01-05 09:41 | 575 | 11kV | 195258 | 585 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129024 5 fault operations Earth fault, Sensivity Earth fault wire down daj pole AH-20120 excluded OMS 767632, 767605, 767650, 767649, 768310, 768317, 768318, 768320, 768321, 768327, 768329, 768330, 768332, 768334, 768337, 768339 OMS 771136, 771137, 771138, 771142, 771143, 771145, 771146, 771147, 771148, 771149, 771150, 771151, 771152, 771153, 771156 | January | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-01-05 | N | 333.7744 | N | 13 | N | N | 1.1101 | 39.4971 | 142688.7873
| ZN9700:PA19 | 1117 | 1109.0078 | 47.08 | 0.99284 | 47.08 | 19182 | 5400 | 767711 | 2012-01-04 22:51 | 2012-01-05 10:36 | 704.6667 | 11kV | 1321.15 | 1249 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.9037 Miranda P-16 "Sylvania Dwyer" RELAYS: Earth fault, timing relay, lockout relay, & EFI SIGNALS: 11kV trip, Zone Earth, TX.3 Grp Eth, REMARKS: No cause ascertained. Windy weather. | January | 2012 | 2012Q3 | 2012 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | OH | Not Veg | 2012-01-04 | N | 1.0578 | N | 20 | Y | Y | 1.1101 | 39.4971 | 965.4575
| ZN9700:PA20 | 1537 | 1498.2934 | 40.84 | 0.97482 | 40.84 | 20067 | 15777 | 767613 | 2012-01-05 00:41 | 2012-01-05 13:30 | 769 | 11kV | 27375 | 79 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Ex Zn.14891 Wyong Pnl.5 - REC 45017 Whiteman tripped on: Earth Fault EFI @ S.14891 Section of UGOH feeder beneath USL42504 to AB44350 to USL44841 - Tee off section of feeder to USL44841 $ PT14965 broken away to effect repairs to UGOH cable. | January | 2012 | 2012Q3 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | Unknown | Unknown | 2012-01-05 | N | 346.519 | N | 13 | N | N | 1.1101 | 39.4971 | 20004.8426
| ZN9700:PA21 | 491 | 1043.8469 | 49.1 | 2.126 | 49.1 | 18639 | 619 | 767941 | 2012-01-05 15:29 | 2012-01-05 18:41 | 192.4 | 11kV | 15969.2 | 83 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Rec 24722 Forest Crozier tripped and locked out. Ex panel 10 Fdr Large branch on mains near AB 25021 | January | 2012 | 2012Q3 | 2012 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2012-01-05 | N | 192.4 | N | 13 | N | N | 1.1101 | 39.4971 | 11669.8203
| ZN9700:PA22 | 324 | 1308.521 | 53.08 | 4.0386 | 53.08 | 19889 | 13636 | 768368 | 2012-01-05 20:58 | 2012-01-05 22:27 | 89 | 11kV | 68263 | 767 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129049 2 fault operation | January | 2012 | 2012Q3 | 2012 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2012-01-05 | N | 89 | N | 13 | N | N | 1.1101 | 39.4971 | 49884.587
| ZN9700:PA23 | 1644 | 1475.0849 | 34.98 | 0.89725 | 34.98 | 18820 | 2280 | 768055 | 2012-01-05 21:06 | 2012-01-05 22:30 | 84 | 11kV | 82356 | 1207 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129052 1 fault operation Earth fault | January | 2012 | 2012Q3 | 2012 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Veg | 2012-01-05 | N | 68.232 | N | 13 | N | N | 1.1101 | 39.4971 | 60183.3357
| ZN9700:PA24 | 1488 | 1625.6025 | 38.09 | 1.0925 | 38.09 | 19378 | 8018 | 768072 | 2012-01-05 23:55 | 2012-01-06 00:25 | 30 | 11kV | 360 | 12 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Unselected | N | LID 129059 Isolated section to replace transformer & switchgear at sub 16465. Excluded OMS No 768072. OMS 768209 | January | 2012 | 2012Q3 | 2012 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2012-01-05 | N | 30 | N | 13 | N | N | 1.1101 | 39.4971 | 263.0774
| ZN10999:PA1 | 251 | 689.2512 | 38.92 | 2.746 | 38.92 | 19255 | 6581 | 768500 | 2012-01-05 22:50 | 2012-01-06 01:10 | 140 | 11kV | 1680 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129058 section isolated to repair mains at abs 43226 see report 129057 and 129052 | January | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2012-01-05 | N | 140 | N | 13 | N | N | 1.1101 | 39.4971 | 1227.6944
| ZN10999:PA10 | 1915 | 1451.5317 | 34.08 | 0.75798 | 34.08 | 19825 | 13002 | 768499 | 2012-01-05 22:45 | 2012-01-06 01:15 | 150 | 11kV | 4200 | 28 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 129057 section isolated to repair mains at abs 43226 see report 129052 and 129058 | January | 2012 | 2012Q3 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2012-01-05 | N | 150 | N | 13 | N | N | 1.1101 | 39.4971 | 3069.2361
| ZN10999:PA11 | 1632 | 1240.6796 | 41.04 | 0.76022 | 41.04 | 19452 | 8720 | 767835 | 2012-01-05 12:34 | 2012-01-06 02:30 | 836 | 11kV | 4180 | 5 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Previous Storm | N | LID 129062 Lighning damaged transformer & switchgear replaced. Excluded OMS No 767835, OMS 768208 SEE Also OMS No.768072 & outage report No. 129059. | January | 2012 | 2012Q3 | 2012 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2012-01-05 | N | 836 | N | 13 | N | N | 1.1101 | 39.4971 | 3054.6207
| ZN10999:PA12 | 2609 | 1647.7242 | 33.65 | 0.63155 | 33.65 | 18727 | 1309 | 768096 | 2012-01-06 00:02 | 2012-01-06 02:33 | 151 | 11kV | 183767 | 1217 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Ex Zn.12570 Avoca Pnl.5 - REC44855 tripped & locked out on OC Linesman Patrolled - lightning | January | 2012 | 2012Q3 | 2012 | ZN12570:PA5 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Veg | 2012-01-06 | N | 151 | N | 9 | N | N | 1.1101 | 39.4971 | 134291.5034
| ZN10999:PA14 | 355 | 1315.9172 | #N/A | 3.7068 | 39.4971 | 18955 | 3495 | 768091 | 2012-01-05 23:52 | 2012-01-06 08:56 | 544 | 11kV | 411630 | 1916 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Lightning | N | Zn.12650 West Gosford Pnl.20 tripped on OC, EFI Lightning in area - section of 11kV from S.11142 to S.18143 to LB40348 | January | 2012 | 2012Q3 | 2012 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Not Veg | 2012-01-05 | N | 214.8382 | N | 13 | N | N | 1.1101 | 39.4971 | 300807.063
| ZN10999:PA15 | 1522 | 1067.2849 | 33.79 | 0.70124 | 33.79 | 19399 | 8344 | 768064 | 2012-01-05 22:03 | 2012-01-06 09:00 | 657 | 11kV | 212224.5167 | 1196 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | At S985 Pennant Hills Panel 43 tripped on A and C phase IOC and EFI. Cause 11kV Down below AB378 after Lightning Strike. See OMS 768486 488 489 768064/066/067/065 | January | 2012 | 2012Q3 | 2012 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2012-01-05 | N | 177.4452 | N | 13 | N | N | 1.1101 | 39.4971 | 155087.4172
| ZN10999:PA16 | 1385 | 1441.4127 | 39.14 | 1.0407 | 39.14 | 20435 | 20391 | 768099 | 2012-01-06 00:19 | 2012-01-06 09:00 | 521 | 11kV | 63041 | 121 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | PT.14181 Riviera South Parry -A,B,C phase HDOs found blown & failed on restoration. Weather - lightning strike | January | 2012 | 2012Q3 | 2012 | ZN12570:PA9 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Not Veg | 2012-01-06 | N | 521 | N | 9 | N | N | 1.1101 | 39.4971 | 46068.5034
| ZN10999:PA17 | 1827 | 1117.9972 | 31.35 | 0.61193 | 31.35 | 19447 | 8644 | 768062 | 2012-01-05 21:17 | 2012-01-06 09:15 | 718 | 11kV | 38916 | 161 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 129054 5 fault operations Suspected faulty transformer at Lyndale sub 70943. Please patrol fdr from Rec 74456 Broomfield RAGCB. Tx was faulty at sub 70943 however this would mean the protection did not grade with sub dolf 10A and line dolf 74462 20A Excluded OMS No 768057, 768080 OMS 768458, 768459, 768460, 768466, 768467, 768469, 768471, 768472, 768474 | January | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2012-01-05 | N | 241.7143 | N | 13 | N | N | 1.1101 | 39.4971 | 28438.665
| ZN10999:PA19 | 1213 | 1429.5342 | 43.21 | 1.1785 | 43.21 | 19492 | 9034 | 768249 | 2012-01-06 09:51 | 2012-01-06 10:54 | 63 | 11kV | 3465 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44604 Dog Trap Rd opened / reclsoed / opened & locked out tree branch removed from 11kV OH adjacent AB44391 | January | 2012 | 2012Q3 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-01-06 | N | 63 | N | 9 | N | N | 1.1101 | 39.4971 | 2532.1198
| ZN10999:PA2 | 239 | 440.1511 | 52.78 | 1.8416 | 52.78 | 19400 | 8345 | 768090 | 2012-01-05 23:38 | 2012-01-06 11:00 | 682 | 11kV | 159464 | 975 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Lightning | N | Ex Zn.12660 Woy Woy Pnl.6 tripped and locked out on Timed OC, Earth Fault Lightning in area - end box blown @ S.14409 | January | 2012 | 2012Q3 | 2012 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | UG | Not Veg | 2012-01-05 | N | 163.5528 | N | 13 | N | N | 1.1101 | 39.4971 | 116531.5878
| ZN10999:PA22 | 2144 | 1392.5354 | 32.83 | 0.6495 | 32.83 | 20236 | 17417 | 768154 | 2012-01-06 07:42 | 2012-01-06 13:30 | 348 | 11kV | 348 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 129076 skingle phase DOLF : 10 Amp Transformer replaced as well as two DOLF's | January | 2012 | 2012Q3 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2012-01-06 | N | 348 | N | 9 | N | N | 1.1101 | 39.4971 | 254.3081
| ZN10999:PA23 | 507 | 1221.7256 | 49.88 | 2.4097 | 49.88 | 19252 | 6553 | 769663 | 2012-01-06 14:00 | 2012-01-06 15:20 | 80 | 11kV | 10320 | 129 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of feeder ex Pnl.1 Umina Zn was interrupted between AB42488 and LB41168 tee PT11254 & PT11520 inetrrupted for safety due to large branch broken and hanging over mains See OMS # 769655 769663 | January | 2012 | 2012Q3 | 2012 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Veg | 2012-01-06 | N | 80 | N | 9 | N | N | 1.1101 | 39.4971 | 7541.5516
| ZN10999:PA24 | 1384 | 794.2417 | 35.97 | 0.57387 | 35.97 | 19578 | 9707 | 768453 | 2012-01-06 12:23 | 2012-01-06 16:15 | 232 | 11kV | 29479 | 206 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | @PT13033 Brooklyn View - Centre Phase 20Amp HDO found blown & fails to hold on replacement - Suspect defective transformer @PT13592 View Steyne - Dist #1 "View Pde" - ABC Phase fuses blown (400Amp) - restored via LV // - TX tails from top of fuse carrier to LV mains failed inside conduit Dop isolated Dist #2 @ PT13592 for safety while working out which dist failed. Customers @ PT13033, PT11250 & PT13592 expereienced low volts and outages due to LV //'s common to both outages | January | 2012 | 2012Q3 | 2012 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2012-01-06 | N | 143.1019 | N | 9 | N | N | 1.1101 | 39.4971 | 21542.3837
| ZN10999:PA25 | 1316 | 1020.0682 | 43.18 | 0.77513 | 43.18 | 19491 | 9029 | 768518 | 2012-01-06 15:39 | 2012-01-06 18:20 | 161 | 11kV | 5625 | 79 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV from REC 45017 Whiteman was interrupted for safety so a section of defective UG cable could be returned to service. Ex Pnl.5 Wyong See OMS # 769674 769675 769685 769681 769682 769684 769683 | January | 2012 | 2012Q3 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2012-01-06 | N | 71.2025 | N | 9 | N | N | 1.1101 | 39.4971 | 4110.5841
| ZN10999:PA28 | 622 | 1256.3547 | 51.1 | 2.0199 | 51.1 | 19698 | 11621 | 768619 | 2012-01-06 21:20 | 2012-01-06 22:08 | 48 | 11kV | 22416 | 467 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.14R & 14L tripped on 14L feeder A Phase IOC, Earth fault, EFI EFI @ UGOH defective Possum committed suicide @ 11kV UGOH to S.14127 damaging centre phase lightning arrestor | January | 2012 | 2012Q3 | 2012 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Not Veg | 2012-01-06 | N | 48 | N | 9 | N | N | 1.1101 | 39.4971 | 16380.9516
| ZN10999:PA29 | 2347 | 1507.3784 | 37.14 | 0.64226 | 37.14 | 19791 | 12710 | 768623 | 2012-01-06 23:07 | 2012-01-07 00:55 | 108 | 11kV | 216 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129078 single phase DOLF : 10 Amp Excluded OMS 768623 OMS 769776 | January | 2012 | 2012Q3 | 2012 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2012-01-06 | N | 108 | N | 9 | N | N | 1.1101 | 39.4971 | 157.8464
| ZN10999:PA3 | 3 | 1182.9947 | #N/A | 394.3316 | 39.4971 | 19107 | 4681 | 768629 | 2012-01-07 04:20 | 2012-01-07 07:46 | 206 | 11kV | 261122 | 1674 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 Meadowbank Panel 44 Tripped on Relays: Earth Fault Relay Overcurrent, EFI. Abnormal Switching: LB1503 Closed with AB3099 Open and Defective. Cause: 2 UG HV feeder faults Fault 1. S3952 - S4225 Fault 2. S46229 - S2883 - S2117 EFIS at S1575 and S46229 dis not operate on the first Trip sequence. Operated on the 1st Unsuccessful Try back. See OMS 769818 769820 769819 768629 | January | 2012 | 2012Q3 | 2012 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | UG | Not Veg | 2012-01-07 | N | 155.9869 | N | 4 | N | N | 1.1101 | 39.4971 | 190820.2558
| ZN10999:PA30 | 210 | 187.6008 | 53.35 | 0.89334 | 53.35 | 19023 | 4206 | 768633 | 2012-01-07 06:44 | 2012-01-07 09:00 | 135.7833 | 11kV | 3530.3667 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129080 A Phase DOLF : 10 Amp Quick Patrol done beyond LF 74800. Nothing found. | January | 2012 | 2012Q3 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2012-01-07 | N | 135.7833 | N | 4 | N | N | 1.1101 | 39.4971 | 2579.8878
| ZN10999:PA32 | 1914 | 1493.0899 | 35.86 | 0.78009 | 35.86 | 19519 | 9187 | 768741 | 2012-01-07 15:07 | 2012-01-07 18:15 | 188 | 11kV | 188 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129083 C Phase DOLF : 10 Amp excluded OMS 768741 | January | 2012 | 2012Q3 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2012-01-07 | N | 188 | N | 4 | N | N | 1.1101 | 39.4971 | 137.3849
| ZN10999:PA35 | 102 | 282.8501 | #N/A | 2.773 | 39.4971 | 18808 | 2219 | 768786 | 2012-01-07 20:07 | 2012-01-07 22:47 | 160 | 11kV | 800 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13564 Wise Ferry Maroney - C phase 16K HV fuse replaced Fuse fatigue failed at crimp | January | 2012 | 2012Q3 | 2012 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2012-01-07 | N | 160 | N | 4 | N | N | 1.1101 | 39.4971 | 584.6164
| ZN10999:PA36 | 1207 | 756.9837 | 32.98 | 0.62716 | 32.98 | 19287 | 7262 | 768808 | 2012-01-08 06:20 | 2012-01-08 07:16 | 56 | 11kV | 91032 | 1666 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.262 Marrickville Panel 17 "Gladstone Marrickville" 11KV feeder tripped on; Earth leakage, EFC, EFI Alarms: 11kv trip, tx4 GE Field efi's operated at; S6365, S3776, S169, S2842 Remarks: Suspect UG cable fault from S2842 Wardell Fraser (Sw/B) to S.317 Jarvie Ave Related jobs: #769176, 768808 | January | 2012 | 2012Q3 | 2012 | ZN262:PA17 | ZN262:PA17 | ZN00262/000017 | INNER WEST | UG | Not Veg | 2012-01-08 | N | 54.6411 | N | 12 | N | N | 1.1101 | 39.4971 | 66523.5006
| ZN10999:PA37 | 3 | 1092.2897 | #N/A | 364.0966 | 39.4971 | 19025 | 4219 | 768935 | 2012-01-08 20:44 | 2012-01-08 22:25 | 101 | 11kV | 85820 | 1035 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | At Zn965 Pennant Hills Panel 38 tripped on Signals: Zone Earth, Group Earth No1 Tx, 11kV trip Relays: A and B phase OC Possible Lightning strike on Tx at PT2234 - CENTRE phase HVDo fuse blown See OMS 769460/463/469/8954 768935 768984 | January | 2012 | 2012Q3 | 2012 | ZN965:PA38 | ZN965:PA38 | ZN00965/000038 | HORNSBY | OH | Not Veg | 2012-01-08 | N | 82.9179 | N | 12 | N | N | 1.1101 | 39.4971 | 62714.7247
| ZN10999:PA38 | 1368 | 1052.2932 | 39.89 | 0.76922 | 39.89 | 18728 | 1311 | 768963 | 2012-01-08 21:08 | 2012-01-08 23:17 | 129 | 11kV | 56115 | 435 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | At Zn1193 Lindfield Recloser CP2751 Tripped On O/C Suspect Lightning Strike | January | 2012 | 2012Q3 | 2012 | ZN1193:PA1 | ZN1193:PA28 | ZN01193/000028 | WILLOUGHBY | OH | Not Veg | 2012-01-08 | N | 129 | N | 12 | N | N | 1.1101 | 39.4971 | 41007.1869
| ZN10999:PA39 | 930 | 823.0528 | 45.21 | 0.885 | 45.21 | 19750 | 12429 | 769011 | 2012-01-08 21:08 | 2012-01-08 23:59 | 171 | 11kV | 7729.9667 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129089 5 fault operations A & C phase Overcurrent tree branch removed from OHM at pole CN-40234. Excluded OMS 768952 OMS 769901 | January | 2012 | 2012Q3 | 2012 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2012-01-08 | N | 168.0428 | N | 12 | N | N | 1.1101 | 39.4971 | 5648.8316
| ZN10999:PA4 | 1663 | 1381.3062 | 35.74 | 0.83061 | 35.74 | 19651 | 10862 | 768942 | 2012-01-08 20:48 | 2012-01-09 00:07 | 199 | 11kV | 37213 | 187 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel ex Panel 33 REC2691 Duneba Drive Tripped and Locked out on Overcurrent. See OMS769474 768942 | January | 2012 | 2012Q3 | 2012 | ZN965:PA33 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-01-08 | N | 199 | N | 12 | N | N | 1.1101 | 39.4971 | 27194.1628
| ZN10999:PA7 | 1023 | 795.3336 | 45.46 | 0.77745 | 45.46 | 20202 | 16980 | 768973 | 2012-01-08 21:33 | 2012-01-09 00:10 | 157 | 11kV | 471 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 129091 A & B phase DOLF 20 Amp faulty LA's at sub 71366 cut away. Excluded OMS 768973 OMS 769911 & 769912 | January | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2012-01-08 | N | 157 | N | 12 | N | N | 1.1101 | 39.4971 | 344.1929
| ZN10999:PA9 | 113 | 46.9089 | #N/A | 0.41512 | 39.4971 | 18846 | 2535 | 768993 | 2012-01-08 21:58 | 2012-01-09 00:25 | 147 | 11kV | 4026.4833 | 28 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129093 A & C Phase DOLF : 16 Amp DOLF down & arresters blown & damaged at sub. Excluded OMS No. 768991. oms 769646 | January | 2012 | 2012Q3 | 2012 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2012-01-08 | N | 143.803 | N | 12 | N | N | 1.1101 | 39.4971 | 2942.4353
| 417:80491 | 6 | 0 | #N/A | 0 | 39.4971 | 20070 | 15787 | 769047 | 2012-01-08 22:52 | 2012-01-09 00:30 | 98 | 11kV | 490 | 5 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129088 5 Fault operations HV conductor down wires down past 11kV Links 40610 Excluded OMS 768945 OMS 769844, 7697845, 769746, 769748, 769752, 769753, 769874, 769875, | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-01-08 | N | 98 | N | 12 | N | N | 1.1101 | 39.4971 | 358.0775
| 417:80500 | 23 | 0 | #N/A | 0 | 39.4971 | 19810 | 12881 | 769844 | 2012-01-08 21:00 | 2012-01-09 00:40 | 220 | 11kV | 10315 | 115 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 129088 5 Fault operations HV conductor down wires down past 11kV Links 40610 Excluded OMS 768945 OMS 769844, 7697845, 769746, 769748, 769752, 769753, 769874, 769875, | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-01-08 | N | 89.6957 | N | 12 | N | N | 1.1101 | 39.4971 | 7537.8978
| 417:80504 | 19 | 0 | #N/A | 0 | 39.4971 | 20206 | 17070 | 769846 | 2012-01-08 21:36 | 2012-01-09 00:40 | 184 | 11kV | 6948 | 81 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129088 5 Fault operations HV conductor down wires down past 11kV Links 40610 Excluded OMS 768945 OMS 769844, 7697845, 769746, 769748, 769752, 769753, 769874, 769875, | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-01-08 | N | 85.7778 | N | 12 | N | N | 1.1101 | 39.4971 | 5077.3935
| 417:80507 | 12 | 0 | #N/A | 0 | 39.4971 | 19734 | 12102 | 768951 | 2012-01-08 21:11 | 2012-01-09 02:50 | 338.5833 | 11kV | 338.5833 | 1 | HV | Customer Installation Fault | Customer Installation | OTHER - REFER COMMENTS | Unplanned | Rain Wind Storm | N | CP 1623 TRIPPED. All3 HV fuses operated(90A Kemxo) 11KV MAINS ARE CUSTOMERS RESPONSIBILITIES. CUST INFORMED TO HAVE OH MAINS PATROLLED AND CONTACT AUSGRID WHEN READY FOR RESTORATION | January | 2012 | 2012Q3 | 2012 |  |  |  | NORTHERN BEACHES | Unknown | Unknown | 2012-01-08 | N | 338.5833 | N | 12 | N | N | 1.1101 | 39.4971 | 247.4267
| 205:12202 | 3 | 371.4491 | 39.98 | 123.8164 | 39.98 | 20272 | 18084 | 769853 | 2012-01-08 22:52 | 2012-01-09 04:15 | 323 | 11kV | 2847 | 61 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129088 5 Fault operations HV conductor down wires down past 11kV Links 40610 Excluded OMS 768945 OMS 769844, 7697845, 769746, 769748, 769752, 769753, 769874, 769875, | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-01-08 | N | 46.6721 | N | 12 | N | N | 1.1101 | 39.4971 | 2080.5036
| 205:12203 | 677 | 1017.1898 | 46.91 | 1.5025 | 46.91 | 18648 | 719 | 769058 | 2012-01-09 04:16 | 2012-01-09 05:50 | 94 | 11kV | 8366 | 89 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At S4699 Alan Duff centre phase HV fuse operated Cause: Customer reported Tree brought mains down.\ See OMS 769715 769058 | January | 2012 | 2012Q3 | 2012 | ZN1673:PA40 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2012-01-09 | N | 94 | N | 9 | N | N | 1.1101 | 39.4971 | 6113.626
| 205:12204 | 46 | 1133.7527 | 41.72 | 24.6468 | 41.72 | 20084 | 15877 | 769062 | 2012-01-09 04:58 | 2012-01-09 06:00 | 62 | 11kV | 14622 | 237 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | @ S1285 Greenacre Park Panel 8 'S 1202 BMC DEPOT ETC' feeder tripped on Relays - Earth Fault, EFI, Fault Check Signals - 11kv trip, Ze Field EFI operated @ S 1202 Remarks: 11kv feeder fault from S1202 BMC Depot to S 4476 Noble Cardigan Related jobs: #769318, 769062, 769320 | January | 2012 | 2012Q3 | 2012 | ZN1285:PA8 | ZN37100:PA36 | ZN37100/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-01-09 | N | 61.6962 | N | 9 | N | N | 1.1101 | 39.4971 | 10685.3263
| 205:12205 | 1226 | 915.9614 | 30.11 | 0.74711 | 30.11 | 19847 | 13230 | 769107 | 2012-01-09 08:02 | 2012-01-09 09:30 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129099 single phase DOLF : 10 Amp Excluded OMS 769107 OMS 769915 | January | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-01-09 | N | 88 | N | 9 | N | N | 1.1101 | 39.4971 | 64.3078
| 205:12206 | 868 | 626.5136 | 38.38 | 0.72179 | 38.38 | 18662 | 773 | 769160 | 2012-01-09 07:46 | 2012-01-09 09:50 | 124 | 11kV | 372 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129100 single phase DOLF : 10 Amp | January | 2012 | 2012Q3 | 2012 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2012-01-09 | N | 124 | N | 9 | N | N | 1.1101 | 39.4971 | 271.8466
| 205:12208 | 48 | 655.0663 | 40.91 | 13.6472 | 40.91 | 19822 | 12994 | 769213 | 2012-01-09 09:29 | 2012-01-09 10:30 | 61 | 11kV | 61 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129101 single phase DOLF : 10 Amp excluded OMS 769213 OMS 769918 | January | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-01-09 | N | 61 | N | 9 | N | N | 1.1101 | 39.4971 | 44.577
| 205:12209 | 59 | 143.6192 | 40.11 | 2.4342 | 40.11 | 18623 | 449 | 769240 | 2012-01-09 09:43 | 2012-01-09 12:00 | 137 | 11kV | 137 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129102 Single phase DOLF : 10 Amp excluded OMS 769240 OMS 769722 | January | 2012 | 2012Q3 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-01-09 | N | 137 | N | 9 | N | N | 1.1101 | 39.4971 | 100.1156
| 205:12210 | 1523 | 1288.6814 | 35.73 | 0.84615 | 35.73 | 18598 | 240 | 769497 | 2012-01-09 14:51 | 2012-01-09 16:00 | 69 | 11kV | 276 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129105 A Phase DOLF : 10 Amp Customer stated probably out since storm last night. Excluded OMS 769497 OMS 769939 | January | 2012 | 2012Q3 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2012-01-09 | N | 69 | N | 9 | N | N | 1.1101 | 39.4971 | 201.6927
| 205:12213 | 907 | 1033.858 | 36.97 | 1.1399 | 36.97 | 19666 | 11062 | 769610 | 2012-01-09 21:01 | 2012-01-09 22:35 | 94 | 11kV | 57892 | 1307 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At S35800 Bankstown Panel #1 "Gow Gibson" 11kv fdr CB tripped on: IOC B & C Phase, EFC, EFI Alarm; 11kv trip Field EFI's operated at S35208 EFI at UGOH irvine st did not operate Remarks: Lightning Arrestors at UGOH on Eldridge rd, near chapel rd appear defective. From AB 1797 to S.8060 Chapel Eldridge No1 (Sw/A) to S35260 Hoskins Chapel (sw/A) tee to S5006 Eldridge Rd. EFI at UGOH irvine st did not operate. - Earth wire has been removed by persons unknown - subs to repair. Related jobs: #769617, 769614, 769613, 769611, 769734, 769732, 769727, 769725, 769724, 769610 | January | 2012 | 2012Q3 | 2012 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-01-09 | N | 44.2938 | N | 9 | N | N | 1.1101 | 39.4971 | 42305.7661
| ZN9534:PA10 | 2 | 4.3644 | #N/A | 2.1822 | 39.4971 | 18805 | 2187 | 769603 | 2012-01-09 20:23 | 2012-01-09 22:50 | 147 | 11kV | 294 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 129107 No protection operation Isolated sub to replace LV fuse complete Excluded OMS 769603 (attached to residence) OMS 769952 | January | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-01-09 | N | 147 | N | 9 | N | N | 1.1101 | 39.4971 | 214.8465
| ZN9534:PA11 | 242 | 234.0809 | 41.82 | 0.96728 | 41.82 | 18931 | 3359 | 769624 | 2012-01-10 01:46 | 2012-01-10 02:41 | 55 | 11kV | 29535 | 537 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S80 Chatswood panel 31 tripped on A phase IOC EFI Cause: Possum at base of UGOH O/S 2 Goodchap Rd Chatswood. | January | 2012 | 2012Q3 | 2012 | ZN80:PA31 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Not Veg | 2012-01-10 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 21583.3069
| ZN9534:PA15 | 56 | 179.3497 | #N/A | 3.2027 | 39.4971 | 19024 | 4207 | 769645 | 2012-01-10 07:24 | 2012-01-10 10:15 | 171 | 11kV | 4446 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129113 C Phase DOLF : 10Amp Same fuses operated on Saturday 7/01/2012. No Storms. excluded OMS # 769639, 45, 49, 50. OMS 770135 | January | 2012 | 2012Q3 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2012-01-10 | N | 171 | N | 5 | N | N | 1.1101 | 39.4971 | 3249.0057
| ZN9534:PA17 | 721 | 707.4278 | 37.29 | 0.98118 | 37.29 | 19582 | 9733 | 769797 | 2012-01-10 10:55 | 2012-01-10 12:08 | 73.3833 | 11kV | 88626.2167 | 2061 | HV | Animal Bird | Animal | O/H Conductor ABC | Unplanned | No Weather Impact | N | At ZN.10994 Mortdale, P-12L S.49538 Mortdale Aux.2 tripped on: RELAYS: A & B IOC SIGNALS: 11kv Trip REMARKS: Dead bird found on ground near AB 31296 | January | 2012 | 2012Q3 | 2012 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2012-01-10 | N | 43.0016 | N | 5 | N | N | 1.1101 | 39.4971 | 64765.4251
| ZN9534:PA18 | 42 | 248.4091 | 56.47 | 5.9145 | 56.47 | 18683 | 1007 | 769766 | 2012-01-10 10:13 | 2012-01-10 12:42 | 149 | 11kV | 149 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129115 single phase HV Dropper pulled out of Line side of DOLF excluded OMS 769766. OMS 770147 | January | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2012-01-10 | N | 149 | N | 5 | N | N | 1.1101 | 39.4971 | 108.8848
| 507:80914 | 1268 | 1078.0419 | 37.05 | 0.85019 | 37.05 | 18952 | 3483 | 769917 | 2012-01-10 13:54 | 2012-01-10 14:57 | 63 | 11kV | 2961 | 47 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11004 Sydney Ocean Beach - Footpath phase 31.5A HDO fuse Operated cause not ascertained | January | 2012 | 2012Q3 | 2012 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2012-01-10 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 2163.8115
| 507:80917 | 983 | 807.4943 | 35.68 | 0.82146 | 35.68 | 19262 | 6640 | 770184 | 2012-01-11 10:00 | 2012-01-11 10:25 | 25 | 11kV | 25 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129129 3 phase DOLF : 10 Amp | January | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-01-11 | N | 25 | N | 14 | N | N | 1.1101 | 39.4971 | 18.2693
| 507:80920 | 89 | 101.1573 | 52.64 | 1.1366 | 52.64 | 18626 | 465 | 770350 | 2012-01-11 12:23 | 2012-01-11 13:36 | 73 | 11kV | 4234 | 58 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | At S.15011 Beacon Hill 11kV trip. Panel 4 the rodborough Rd fdr tripped on Cph IOC and timed O/L Tree branch fell through 11kV mains near Beacon Hill zn | January | 2012 | 2012Q3 | 2012 | ZN15011:PA4 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | OH | Not Veg | 2012-01-11 | N | 73 | N | 14 | N | N | 1.1101 | 39.4971 | 3094.0823
| 507:80922 | 1343 | 917.5988 | 32.2 | 0.68325 | 32.2 | 19468 | 8853 | 770394 | 2012-01-11 13:32 | 2012-01-11 14:15 | 43 | 11kV | 43 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 129132 B Phase DOLF : 10 Amp Excluded OMS 770394 ( incorrectly logged) OMS 770964 | January | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-01-11 | N | 43 | N | 14 | N | N | 1.1101 | 39.4971 | 31.4231
| 507:80923 | 1496 | 986.5003 | 38.42 | 0.65943 | 38.42 | 19683 | 11357 | 770985 | 2012-01-11 15:50 | 2012-01-11 16:20 | 30 | 11kV | 150 | 5 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Wind | N | LID 129137 Feeder isolated to retension sagging mains. | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-01-11 | N | 30 | N | 14 | N | N | 1.1101 | 39.4971 | 109.6156
| 507:80925 | 1542 | 1103.3691 | 33.3 | 0.71554 | 33.3 | 19659 | 10981 | 770507 | 2012-01-11 15:26 | 2012-01-11 16:41 | 75 | 11kV | 30335 | 717 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn901 Surry hills Panel 8 11kv fdr tripped on Earth & EFI on RHS fdr Ze No4 Group Earth & 11kv trip Abnormal: N/O Sw B CB@ S568 Tech College No1 is at workshop for repair No2 Tx offloaded & Tx CB moved to N/O Sw B in order to restore supply Cable damaged in footpath O/S Zone Zn901 Pa8 to S8825 to S6423 to CP2917 See 77104,3,4 exclude 770507 | January | 2012 | 2012Q3 | 2012 | ZN901:PA8 | ZN7900:PA12 | ZN07900/000012 | SYDNEY | UG | Not Veg | 2012-01-11 | N | 42.3082 | N | 14 | N | N | 1.1101 | 39.4971 | 22167.9233
| 507:80926 | 47 | 256.5297 | 62.14 | 5.4581 | 62.14 | 20262 | 18010 | 770524 | 2012-01-11 15:45 | 2012-01-11 18:30 | 165 | 11kV | 7095 | 43 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn.12650 West Gosford Pnl.1 - REC 44853 Ourimbah Bumble tripped on A & B phase O/C Strong gusty winds at time of interruption | January | 2012 | 2012Q3 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-01-11 | N | 165 | N | 14 | N | N | 1.1101 | 39.4971 | 5184.8167
| 507:80931 | 924 | 970.3444 | 36.8 | 1.0502 | 36.8 | 20100 | 15995 | 770425 | 2012-01-11 14:00 | 2012-01-11 18:50 | 290 | 11kV | 13247 | 79 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129133 found mains down adjacent sub 51471, isolated at 4524 for repairs Excluded OMS No. 770425 & 770434 OMS 771030, 771031, 771033, 771034, 771036 | January | 2012 | 2012Q3 | 2012 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2012-01-11 | N | 167.6835 | N | 14 | N | N | 1.1101 | 39.4971 | 9680.5169
| 507:80932 | 1411 | 1429.7834 | 36.66 | 1.0133 | 36.66 | 19407 | 8373 | 770668 | 2012-01-11 18:37 | 2012-01-11 20:22 | 105 | 11kV | 129225 | 1267 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | At S1610 Homebush Bay Panel 11 S4127 RAS Showring North Feeder tripped on leakage EFI. 11kv trip No1 Group Earth Efi's S4127 S5114 S5115 S46780 S7662 Remarks: UG feeder failure S7662 S5050 S4287 Related jobs: #770668, 770935, 770938, 770942, 770687, 770695 | January | 2012 | 2012Q3 | 2012 | ZN1610:PA11 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2012-01-11 | N | 101.9929 | N | 14 | N | N | 1.1101 | 39.4971 | 94433.8185
| ZN13000:PA1 | 777 | 406.0928 | 33.43 | 0.52264 | 33.43 | 19625 | 10462 | 770698 | 2012-01-11 19:39 | 2012-01-11 20:26 | 47 | 11kV | 49303 | 1049 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | At S1290 Leightonfield panel 12 "Miller Bil No1" feeder tripped/reclosed tripped on A phase time & IOC timing and lockout relays 11KV trip Remarks: tree on 11kv 100 Belar St Villawood Related jobs: #770715, 770705, 770703, 770698, 770991 | January | 2012 | 2012Q3 | 2012 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-01-11 | N | 47 | N | 14 | N | N | 1.1101 | 39.4971 | 36029.1782
| ZN13000:PA10 | 862 | 544.6993 | 30.96 | 0.6319 | 30.96 | 20380 | 19980 | 770597 | 2012-01-11 16:52 | 2012-01-11 20:30 | 218.1667 | 11kV | 2399.8333 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 129142 B & C phase DOLF 10 Amp | January | 2012 | 2012Q3 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2012-01-11 | N | 218.1667 | N | 14 | N | N | 1.1101 | 39.4971 | 1753.7274
| ZN13000:PA11 | 1651 | 1618.4917 | 36.8 | 0.98031 | 36.8 | 19465 | 8825 | 770660 | 2012-01-11 18:21 | 2012-01-11 21:25 | 184 | 11kV | 920 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129141 LV mains down from transformer. Sub isolated for repairs. Excluded OMS No. 770660 & 770707 OMS 770996 | January | 2012 | 2012Q3 | 2012 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2012-01-11 | N | 184 | N | 14 | N | N | 1.1101 | 39.4971 | 672.3089
| ZN13000:PA2 | 1398 | 987.3109 | 32.69 | 0.70623 | 32.69 | 19919 | 14002 | 770436 | 2012-01-11 14:07 | 2012-01-11 21:52 | 465 | 11kV | 8560 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 129143 129134 and LID 129143 2 fault operations Overcurrent Isolated from ABS 14480 to allow repairs to fallen mains Refer to OMS 770436, 770934 and 770937 LID 129134 2 fault operations Overcurrent | January | 2012 | 2012Q3 | 2012 | 501:48117 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2012-01-11 | N | 450.5263 | N | 14 | N | N | 1.1101 | 39.4971 | 6255.3955
| ZN13000:PA4 | 320 | 172.6096 | 39 | 0.53941 | 39 | 20180 | 16715 | 770757 | 2012-01-11 21:30 | 2012-01-12 00:45 | 195 | 11kV | 98565 | 781 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | LID 129144 pole fire at pole SW-60116. Fdr opened by SO. Vandalism - small size welding flex (approx 35mm2) with an attached lug was used to throw up on the road side phase of the 11kV ABS. see report # 129147 Excluded OMS 770757, 770776, 770777, 770778, 770779, 770780, 770781 OMS 771052 | January | 2012 | 2012Q3 | 2012 | 222:2015 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2012-01-11 | N | 126.2036 | N | 14 | N | N | 1.1101 | 39.4971 | 72028.3948
| ZN13000:PA5 | 1697 | 1376.1498 | 33.49 | 0.81093 | 33.49 | 19462 | 8806 | 770784 | 2012-01-12 06:01 | 2012-01-12 06:35 | 34 | 11kV | 544 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129148 Suspect faulty MG LV ACB. 600A load on restoration of supply. excluded OMS# 770784. | January | 2012 | 2012Q3 | 2012 |  |  |  | MAITLAND | OH | Veg | 2012-01-12 | N | 34 | N | 6 | N | N | 1.1101 | 39.4971 | 397.5392
| ZN13000:PA7 | 1435 | 1020.3957 | 44.79 | 0.71108 | 44.79 | 18915 | 3212 | 770791 | 2012-01-12 06:51 | 2012-01-12 08:05 | 74.3333 | 11kV | 1932.6667 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CC1: 06-"Urgent - O.H Mains - No others"dolf at 74800 LID 129155 A Phase DOLF : 10 Amp | January | 2012 | 2012Q3 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2012-01-12 | N | 74.3333 | N | 6 | N | N | 1.1101 | 39.4971 | 1412.3358
| ZN13000:PA8 | 450 | 344.4787 | 36.06 | 0.76551 | 36.06 | 19842 | 13167 | 772206 | 2012-01-12 12:20 | 2012-01-12 12:28 | 8 | 11kV | 208 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129155/02 3 phase DOLF : 16 Amp 10A Line DOLFs replaced with 16A on advice from prot calcs sect. | January | 2012 | 2012Q3 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2012-01-12 | N | 8 | N | 6 | N | N | 1.1101 | 39.4971 | 152.0003
| ZN116:PA1 | 265 | 4601.6815 | #N/A | 17.3648 | 39.4971 | 20233 | 17403 | 770880 | 2012-01-12 08:30 | 2012-01-12 13:20 | 290 | 11kV | 870 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129156 B Phase DOLF : 10 Amp Excluded OMS 770880 OMS 772210 | January | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-01-12 | N | 290 | N | 6 | N | N | 1.1101 | 39.4971 | 635.7703
| ZN116:PA12 | 1933 | 1808.3314 | 37.78 | 0.93551 | 37.78 | 20139 | 16233 | 770990 | 2012-01-12 08:00 | 2012-01-12 13:30 | 330 | 11kV | 68640 | 208 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | No Weather Impact | N | S.18291 lost supply based on customer calls due to bushfire in the area. no report from control room Sub has DM&C monitoring equipment - no supply lost to surrounding subs or feeder cause unknown | January | 2012 | 2012Q3 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Veg | 2012-01-12 | N | 330 | N | 6 | N | N | 1.1101 | 39.4971 | 50160.0875
| ZN116:PA14 | 961 | 813.1024 | 44.19 | 0.8461 | 44.19 | 19431 | 8514 | 770642 | 2012-01-11 17:43 | 2012-01-12 15:23 | 1299.5 | 11kV | 3921.5 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S4851 King Leeming 400A fuse blown on B and C phase of distributor 2. Cause: Weather related - strong winds. See OMS 770637 770642 770654 | January | 2012 | 2012Q3 | 2012 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2012-01-11 | N | 170.5 | N | 14 | N | N | 1.1101 | 39.4971 | 2865.7165
| ZN116:PA19 | 2411 | 1931.175 | 42.01 | 0.80099 | 42.01 | 20144 | 16277 | 770966 | 2012-01-12 11:30 | 2012-01-12 16:00 | 270 | 11kV | 188450 | 1332 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S2400 Berowra Panel 22 Tripped on Earth Fault EFI and Fault Check. Cause: Cable damaged by contactor (Front line sections) See OMS 773383/386/387/388 | January | 2012 | 2012Q3 | 2012 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | UG | Not Veg | 2012-01-12 | N | 141.479 | N | 6 | N | N | 1.1101 | 39.4971 | 137713.7017
| ZN116:PA2 | 1446 | 1023.3312 | 36.24 | 0.7077 | 36.24 | 19977 | 14666 | 773737 | 2012-01-13 04:49 | 2012-01-13 06:45 | 116 | 11kV | 62708 | 806 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S195 Pymble Panel 10 tripped on Relays: C phase IOC and Timed Signals: 11kV Trip, Zone Earth, Tx2 Group Earth. Abnormal Switching: Panel 10 Pymble Closed, SW/A open at S484 Cause: dead possum found at the bottom of REC231 Mt IDa st. See OMS 773738 773737 | January | 2012 | 2012Q3 | 2012 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Not Veg | 2012-01-13 | N | 77.8015 | N | 12 | N | N | 1.1101 | 39.4971 | 45825.1568
| ZN116:PA20 | 1207 | 1597.2375 | 42.94 | 1.3233 | 42.94 | 20275 | 18113 | 775608 | 2012-01-13 08:43 | 2012-01-13 08:50 | 7 | 11kV | 378 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129162 RAGCB tripped on O/C when ABS 74933 was opened on SI 18775. | January | 2012 | 2012Q3 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2012-01-13 | N | 7 | N | 12 | N | N | 1.1101 | 39.4971 | 276.2313
| ZN116:PA23 | 1407 | 924.3691 | 37.82 | 0.65698 | 37.82 | 18770 | 1879 | 771131 | 2012-01-13 08:45 | 2012-01-13 11:20 | 155 | 11kV | 3255 | 21 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | LID 129164 Mains low between poles CO-13707 & CO-13704. | January | 2012 | 2012Q3 | 2012 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-01-13 | N | 155 | N | 12 | N | N | 1.1101 | 39.4971 | 2378.658
| ZN116:PA25 | 1971 | 1188.5489 | 35.16 | 0.60302 | 35.16 | 20225 | 17333 | 771260 | 2012-01-13 05:06 | 2012-01-13 12:35 | 449 | 11kV | 7394 | 26 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129161 C Phase DOLF 16 Amp HV mians down into LV mains at pole 6O-40039 Excluded OMS 771260 OMS 772326, 772328 | January | 2012 | 2012Q3 | 2012 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2012-01-13 | N | 284.3846 | N | 12 | N | N | 1.1101 | 39.4971 | 5403.3171
| ZN116:PA26 | 1023 | 810.4766 | 44.04 | 0.79225 | 44.04 | 18724 | 1299 | 771257 | 2012-01-13 04:54 | 2012-01-13 13:30 | 516 | 11kV | 90017 | 368 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129166 3 fault operations single phase Earth fault Mains down at pole IQ-42207 Excluded OMS 771257 OMS 772242, 772246, 772247, 772248, 772249 | January | 2012 | 2012Q3 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-01-13 | N | 244.6114 | N | 12 | N | N | 1.1101 | 39.4971 | 65781.7685
| ZN116:PA29 | 804 | 573.8094 | 35.72 | 0.71369 | 35.72 | 19416 | 8412 | 772203 | 2012-01-13 14:28 | 2012-01-13 14:34 | 6 | 11kV | 16248 | 2708 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @Zn 15008 Harbord - 11kV Panel No.7 "Curl Curl" feeder tripped and locked out (recloser N/A) Relays: IOC & Earth fault check Signals: 11kV trip Field EFI's : Nil Panel 7 tripped when trying to restore failure on on panel 5 See 722163, 772180 | January | 2012 | 2012Q3 | 2012 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2012-01-13 | N | 6 | N | 12 | N | N | 1.1101 | 39.4971 | 11873.5592
| ZN116:PA30 | 1802 | 1064.4312 | 39.08 | 0.59069 | 39.08 | 19885 | 13610 | 771450 | 2012-01-13 12:48 | 2012-01-13 18:02 | 314.5 | 11kV | 135407.2833 | 2126 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At 15008 harbord panel 5 feeder tripped relays IOC, Earth Fault check, EFI timing relay and lockout Signals 11 trip and zone fault Bond burnt off @ LK22539 due to fault beyond suspect faulty 11kv LA's or 11kV fault from LK 23561 to 16849 Beach carrington | January | 2012 | 2012Q3 | 2012 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2012-01-13 | N | 63.6911 | N | 12 | N | N | 1.1101 | 39.4971 | 98951.6488
| ZN116:PA31 | 2186 | 1607.9091 | 42.03 | 0.73555 | 42.03 | 19222 | 6192 | 771585 | 2012-01-13 17:34 | 2012-01-13 18:42 | 68 | 11kV | 52468 | 1542 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.2 feeder opened, reclosed, opened & locked out on A & C phase IOC & C phase timed OC with EFI Tree on 11kV OH adjacent PT12039 | January | 2012 | 2012Q3 | 2012 | ZN12570:PA2 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2012-01-13 | N | 34.0259 | N | 12 | N | N | 1.1101 | 39.4971 | 38342.0669
| ZN116:PA8 | 539 | 361.6062 | 34.35 | 0.67088 | 34.35 | 20393 | 20053 | 771572 | 2012-01-13 17:05 | 2012-01-13 21:00 | 235 | 11kV | 470 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14595 main Road Gallard No.1 - Water tank side HDO 31.5K operated fuse failure - unable to read batch number | January | 2012 | 2012Q3 | 2012 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2012-01-13 | N | 235 | N | 12 | N | N | 1.1101 | 39.4971 | 343.4621
| ZN1290:PA10 | 37 | 278.9374 | #N/A | 7.5388 | 39.4971 | 20224 | 17305 | 771659 | 2012-01-13 22:31 | 2012-01-13 23:49 | 78 | 11kV | 75186 | 1069 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.10994 Mortdale 11kV fdr P-3 "Mi Mi Street" feeder tripped on: RELAYS: A & B phase Overcurrent, Earth Fault, EFI SIGNALS: 11kV trip, TX.2 Grp Eth FIELD EFIs: S.47566, S.10647 & S.10162 REMARKS: Mains to patrol in Daylight | January | 2012 | 2012Q3 | 2012 | ZN10994:PA3 | ZN10994:PA3 | ZN10994/000003 | GEORGES RIVER | OH | Veg | 2012-01-13 | N | 70.333 | N | 12 | N | N | 1.1101 | 39.4971 | 54943.7112
| ZN1290:PA11 | 8 | 1451.9548 | 51.39 | 181.4944 | 51.39 | 20143 | 16276 | 771662 | 2012-01-13 23:23 | 2012-01-14 00:30 | 67 | 11kV | 7303 | 109 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1347 Ostend Street foot path HV drop out fuse blown 31.5A Remarks: Fatigue Related jobs: #772098, 771662, 771663 | January | 2012 | 2012Q3 | 2012 | ZN35800:PA1 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-01-13 | N | 67 | N | 12 | N | N | 1.1101 | 39.4971 | 5336.817
| ZN1290:PA12 | 1069 | 1753.0683 | 53.92 | 1.6399 | 53.92 | 18592 | 138 | 771668 | 2012-01-14 01:47 | 2012-01-14 03:10 | 83 | 11kV | 5395 | 65 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT12570 Manoa Natuna - Roadside and Centre phase HDOs found blown 31.5A Cause not ascertained | January | 2012 | 2012Q3 | 2012 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2012-01-14 | N | 83 | N | 5 | N | N | 1.1101 | 39.4971 | 3942.5069
| ZN1290:PA13 | 165 | 1551.6691 | #N/A | 9.4041 | 39.4971 | 19126 | 4833 | 771680 | 2012-01-14 04:43 | 2012-01-14 06:53 | 130 | 11kV | 160662 | 1708 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | ZN.9252 Jannali 11kV fdr P-8 'Toronto Buller' tripped & reclosed, tripped and locked out on: RELAYS: SIGNALS: FIELD EFIs: S.9690, S.9558, S.9236 & S.9237 REMARKS: 11kV cable halfway up PT.9188 Cowan Scylla has a visible fault on it. | January | 2012 | 2012Q3 | 2012 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | UG | Not Veg | 2012-01-14 | N | 94.0644 | N | 5 | N | N | 1.1101 | 39.4971 | 117407.0509
| ZN1290:PA16 | 22 | 107.2148 | #N/A | 4.8734 | 39.4971 | 18957 | 3497 | 771686 | 2012-01-14 05:43 | 2012-01-14 07:32 | 109 | 11kV | 158598 | 2070 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn.14891 Wyong Pnl.10 tripped on: B & C phase O/C EFI Field EFI: S14857 Lightning in area, no direct cause found due to lack of field recloser - extnded delay in restoration | January | 2012 | 2012Q3 | 2012 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2012-01-14 | N | 76.6174 | N | 5 | N | N | 1.1101 | 39.4971 | 115898.7406
| ZN1290:PA17 | 181 | 770.0439 | 46.7 | 4.2544 | 46.7 | 19570 | 9675 | 771613 | 2012-01-13 18:42 | 2012-01-14 15:40 | 1258 | 11kV | 7224 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129173 Mains down from pole FM-10091 Repaired under A/P excluded OMS 771613, 771664 OMS 772344, 772346, 772347 | January | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-01-13 | N | 301 | N | 12 | N | N | 1.1101 | 39.4971 | 5279.0861
| ZN1290:PA2 | 1227 | 737.685 | #N/A | 0.60121 | 39.4971 | 18981 | 3834 | 771715 | 2012-01-14 08:35 | 2012-01-14 16:15 | 460 | 11kV | 1780 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129181 Single phase DOLF : 20 Amp replaced both 20A fuses at LF 8556 & 10A DOLF at sub 3401. | January | 2012 | 2012Q3 | 2012 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-01-14 | N | 445 | N | 5 | N | N | 1.1101 | 39.4971 | 1300.7715
| ZN1290:PA3 | 1221 | 1077.2057 | #N/A | 0.88223 | 39.4971 | 19797 | 12779 | 771861 | 2012-01-15 00:33 | 2012-01-15 01:08 | 35 | 11kV | 3955 | 113 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | At PT742 Hills Dent footpath HDO operated 50K type ACEA BB Cause: Suspected fuse fatigue - supply all restored Ok. See OMS 772425 771861 | January | 2012 | 2012Q3 | 2012 | ZN2635:PA10 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Not Veg | 2012-01-15 | N | 35 | N | 6 | N | N | 1.1101 | 39.4971 | 2890.1973
| ZN1290:PA8 | 753 | 997.5383 | 50.3 | 1.3248 | 50.3 | 20384 | 20000 | 771873 | 2012-01-15 02:38 | 2012-01-15 07:15 | 277 | 11kV | 7756 | 28 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13763 Mimosa Ourringo - Burnt off HV drop out assembly ex Pnl.2 Noraville zone | January | 2012 | 2012Q3 | 2012 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2012-01-15 | N | 277 | N | 6 | N | N | 1.1101 | 39.4971 | 5667.856
| ZN1290:PA9 | 79 | 394.1283 | 44.26 | 4.989 | 44.26 | 19445 | 8609 | 771842 | 2012-01-14 19:16 | 2012-01-15 08:10 | 774 | 11kV | 3870 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | PT13362 Ironbark Kirk 1.7 - Roadside HV arrestor blown - HV drop out | January | 2012 | 2012Q3 | 2012 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2012-01-14 | N | 774 | N | 5 | N | N | 1.1101 | 39.4971 | 2828.0819
| 516:48065 | 34 | 62.0915 | 62.06 | 1.8262 | 62.06 | 18874 | 2836 | 772796 | 2012-01-15 08:47 | 2012-01-15 10:50 | 123 | 11kV | 6434 | 55 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 129186 4 fault operations 3 phase Earth fault, Overcurrent Found dead Cockatoo on mains at Pole 9L-40343, knocked off ok. Please patrol Excluded OMS 771912 OMS 772796, 772800, 772801 | January | 2012 | 2012Q3 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2012-01-15 | N | 116.9818 | N | 6 | N | N | 1.1101 | 39.4971 | 4701.7774
| 516:48066 | 93 | 86.7865 | 55.07 | 0.93319 | 55.07 | 19235 | 6344 | 771994 | 2012-01-15 14:46 | 2012-01-15 15:33 | 47 | 11kV | 80699 | 1717 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn.12650 West Gosford Pnl.6 tripped on 6R OC Burnt tree branch on ground next to AB44248 | January | 2012 | 2012Q3 | 2012 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Veg | 2012-01-15 | N | 47 | N | 6 | N | N | 1.1101 | 39.4971 | 58972.449
| 516:48067 | 281 | 393.3831 | 45.3 | 1.3999 | 45.3 | 19569 | 9673 | 772045 | 2012-01-15 19:50 | 2012-01-15 23:35 | 225 | 11kV | 225 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129193 single phase DOLF : 3 Amp Excluded OMS 772045 (heirarchy) OMS 772786 | January | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-01-15 | N | 225 | N | 6 | N | N | 1.1101 | 39.4971 | 164.4234
| ZN1068:PA16 | 691 | 699.3991 | 41.91 | 1.0122 | 41.91 | 19821 | 12962 | 772065 | 2012-01-15 23:46 | 2012-01-16 09:35 | 589 | 11kV | 177141 | 1368 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 129194 3 fault operations A phase Overcurrent UGOH at pole IU-91126 Macquarie Rd isolated. Sw 8670 T & R, approx 30 secs later Sw 8670 L/O. Sw 3553 L/O. 0140hrs supply restored to pole IU-91126 OK. 33kV Fdr 3553 closed at 0146hrs. Both Fdrs tripped at 0147hrs. Fire Brigade called to extinguish pole fire Pole to be replaced. Excluded OMS 772065, 772066, 772067, 772069 OMS 772615, 772616, 772619, 772620, 772621, 772623, 772625 | January | 2012 | 2012Q3 | 2012 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | OH | Not Veg | 2012-01-15 | N | 129.489 | N | 6 | N | N | 1.1101 | 39.4971 | 129449.418
| ZN1068:PA17 | 932 | 932.2888 | 37.14 | 1.0003 | 37.14 | 20434 | 20373 | 772082 | 2012-01-16 06:24 | 2012-01-16 11:00 | 276 | 11kV | 20134 | 159 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 46803 Wise Ferry Dog Trap 0.1 tripped / reclosed / tripped / locked out on OP and IOC Tree brought down OH mains near PT14928 See OMS # 774126 774127 | January | 2012 | 2012Q3 | 2012 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2012-01-16 | N | 126.6289 | N | 7 | N | N | 1.1101 | 39.4971 | 14713.3333
| ZN1068:PA18 | 555 | 977.9683 | 50.9 | 1.7621 | 50.9 | 20170 | 16554 | 772139 | 2012-01-16 08:00 | 2012-01-16 11:00 | 180 | 11kV | 1080 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129204 3 Phase DOLF : 20 Amp Excluded OMS 772139 OMS 772831 | January | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-01-16 | N | 180 | N | 7 | N | N | 1.1101 | 39.4971 | 789.2321
| ZN1068:PA19 | 115 | 100.1642 | #N/A | 0.87099 | 39.4971 | 19854 | 13355 | 772264 | 2012-01-16 10:00 | 2012-01-16 12:50 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129206 Single phase DOLF : 10 Amp | January | 2012 | 2012Q3 | 2012 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2012-01-16 | N | 170 | N | 7 | N | N | 1.1101 | 39.4971 | 124.231
| ZN1068:PA20 | 343 | 644.7088 | #N/A | 1.8796 | 39.4971 | 19276 | 7116 | 772373 | 2012-01-16 12:45 | 2012-01-16 13:10 | 25 | 11kV | 1675 | 67 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | Ex Pnl.2 peats Ridge - IR44316 Wisemans Ferry opened by AOp AB42503 opened by DOp Pole in danger of falling with 11kV still in service See OMS # 774151 774155 774156 774157 774159 774158 | January | 2012 | 2012Q3 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2012-01-16 | N | 25 | N | 7 | N | N | 1.1101 | 39.4971 | 1224.0406
| ZN1068:PA21 | 333 | 748.5559 | 43.26 | 2.2479 | 43.26 | 19711 | 11839 | 774168 | 2012-01-16 15:52 | 2012-01-16 16:29 | 37 | 11kV | 1923 | 67 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | Ex Pnl.2 Peats Ridge - IR44316 opened by AOp at 15:52 interrupting 6 centres AB45074 opened by DOp at 16:05 interrupting 9 centres Abnormal: AB45074 closed through to open USL43530 all centres between are now fed from Endeavour Energy Interruption to restore network after emergency reapirs to damaged pole | January | 2012 | 2012Q3 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2012-01-16 | N | 28.7015 | N | 7 | N | N | 1.1101 | 39.4971 | 1405.2717
| ZN1068:PA22 | 172 | 110.3568 | 25.65 | 0.64161 | 25.65 | 20012 | 15023 | 772563 | 2012-01-16 18:00 | 2012-01-16 21:15 | 195 | 11kV | 390 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129209 No protection operations. tapping open at pole FL-70012. Repaired under A/P. Excluded OMS # 772563 OMS 772840 | January | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-01-16 | N | 195 | N | 7 | N | N | 1.1101 | 39.4971 | 285.0005
| ZN1068:PA26 | 1389 | 844.2391 | 24.62 | 0.6078 | 24.62 | 18958 | 3502 | 772595 | 2012-01-17 03:49 | 2012-01-17 05:30 | 101 | 11kV | 62350 | 746 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Recloser CP46113 Whark Coronga Tripped reclosed tripped and locked out on O/C and IOC Unknown fault in gully crossing. Mains to patrol in Daylight. See OMS 773303 773300 772595 | January | 2012 | 2012Q3 | 2012 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2012-01-17 | N | 83.5791 | N | 7 | N | N | 1.1101 | 39.4971 | 45563.541
| ZN1068:PA27 | 1628 | 1917.2332 | 39.99 | 1.1777 | 39.99 | 18617 | 380 | 772596 | 2012-01-17 04:31 | 2012-01-17 05:34 | 63 | 11kV | 168996 | 2808 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S262 Marrickville Panel 16 'S 7843 Victoria Sydenham' Feeder tripped on Relays - Earth Fault, EFI, Fault Check Signals - 11kv trip, TX4 GE, ZE Related jobs: #772668, 772596, 772669 | January | 2012 | 2012Q3 | 2012 | ZN262:PA16 | ZN262:PA16 | ZN00262/000016 | INNER WEST | UG | Not Veg | 2012-01-17 | N | 60.1838 | N | 7 | N | N | 1.1101 | 39.4971 | 123497.2923
| ZN1068:PA28 | 89 | 427.894 | #N/A | 4.8078 | 39.4971 | 19770 | 12540 | 772602 | 2012-01-17 06:21 | 2012-01-17 11:10 | 289 | 11kV | 1734 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11878 Bushells Peats 0.6 11kV HDO fatigued | January | 2012 | 2012Q3 | 2012 | ZN12630:PA5 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2012-01-17 | N | 289 | N | 7 | N | N | 1.1101 | 39.4971 | 1267.1561
| ZN1193:PA10 | 457 | 463.1143 | 36.63 | 1.0134 | 36.63 | 20252 | 17787 | 773149 | 2012-01-17 12:07 | 2012-01-17 12:23 | 16 | 11kV | 80 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | LID 129218 Trip & Reclose 1 fault operation C phase Intertrip, Directional Overcurrent Sub 38241 interrupted only see para 2. Dir OC C phase David Jones sub. | January | 2012 | 2012Q3 | 2012 | 202:34238 43 48 | 202:34238 43 48 | ZN00202/34238 43 48 | NEWCASTLE | UG | Not Veg | 2012-01-17 | N | 16 | N | 7 | N | N | 1.1101 | 39.4971 | 58.4616
| ZN1193:PA11 | 398 | 712.5953 | 37.38 | 1.7904 | 37.38 | 18830 | 2364 | 772898 | 2012-01-17 13:00 | 2012-01-17 18:45 | 345 | 11kV | 29670 | 86 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S6503 Ivanhoe PLace supply manually interrupted to carry out emergency repairs. See OMS 772898 773667 | January | 2012 | 2012Q3 | 2012 |  |  |  |  | UG | Not Veg | 2012-01-17 | N | 345 | N | 7 | N | N | 1.1101 | 39.4971 | 21681.9609
| ZN1193:PA12 | 1309 | 1474.9138 | 31.83 | 1.1267 | 31.83 | 19942 | 14199 | 772982 | 2012-01-17 16:49 | 2012-01-17 20:59 | 250 | 11kV | 53272 | 264 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At RE556 Bay Coolamon ex Panel 18 Berowra Tripped on Earth Fault Recloser CP556 has and initial trip at 1505 - Subsequent trip and reclose at 1527,1541 and 1640 when recloser was made non auto. Cause: Lineworker and DOp patrolled section of feeder and located faulty lightning arresstor adjacent to PT745 Calabash RD. See OMS773610 773617 | January | 2012 | 2012Q3 | 2012 | ZN847:PA47 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2012-01-17 | N | 201.7879 | N | 7 | N | N | 1.1101 | 39.4971 | 38929.6063
| ZN1193:PA15 | 1417 | 1251.3809 | 32.82 | 0.88312 | 32.82 | 19067 | 4450 | 773110 | 2012-01-17 23:51 | 2012-01-18 02:19 | 148 | 11kV | 4943 | 42 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | At S2400 Berowra section of Panel 18, Recloser CP556 Tripped and locked iout on Earth Fault. Cause: Surge Diverter cut away off pole to PT659. Abnormal Switching Section of feeder from AB2874 to AB2063 tee PT745 Isolated. Cause: Surge diverter cut away on tee of to PT656. See OMS773424/422/420/419/423 773110 | January | 2012 | 2012Q3 | 2012 | ZN2400:PA18 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2012-01-17 | N | 117.6905 | N | 7 | N | N | 1.1101 | 39.4971 | 3612.1986
| ZN1193:PA16 | 993 | 1014.9103 | 34.74 | 1.0221 | 34.74 | 19237 | 6346 | 773114 | 2012-01-18 01:37 | 2012-01-18 03:37 | 120 | 11kV | 8220 | 76 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Rec 1014 Suakin Drive tripped and locked out on: over current Ex panel 17 "2723 Almora Muston" @ Sub 180 Mosman Flying Fox on section of OH mains to Sub 3674 MWS & DB clifton Gardens. Mains to patrol in daylight. | January | 2012 | 2012Q3 | 2012 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Not Veg | 2012-01-18 | N | 108.1579 | N | 3 | N | N | 1.1101 | 39.4971 | 6006.9336
| ZN1193:PA17 | 408 | 557.9326 | 39.64 | 1.3675 | 39.64 | 18602 | 264 | 772141 | 2012-01-16 08:52 | 2012-01-18 12:00 | 3068 | 11kV | 11160 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 129208 A phase DOLF :10 Amp defective distribution transformer OK-DQ1 - duration checked against LID report | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-01-16 | N | 2232 | N | 7 | N | N | 1.1101 | 39.4971 | 8155.3988
| ZN1193:PA20 | 99 | 101.1051 | #N/A | 1.0213 | 39.4971 | 19269 | 6708 | 773363 | 2012-01-18 12:58 | 2012-01-18 17:25 | 267 | 11kV | 12816 | 48 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S6661 Tx1 HV Fuse Blown. Both Tx interrupted to do isolation due to LV TX links restored vie LV baord LV bus section. Younf Danks S6661 Defective #1 Transformer See 773684,87 exclude 773363,517 | January | 2012 | 2012Q3 | 2012 | ZN188:PA44 | ZN188:PA44 | ZN00188/000044 | SYDNEY | UG | Not Veg | 2012-01-18 | N | 267 | N | 3 | N | N | 1.1101 | 39.4971 | 9365.5548
| ZN1193:PA21 | 843 | 721.5983 | 29.81 | 0.85599 | 29.81 | 19437 | 8554 | 773492 | 2012-01-18 16:10 | 2012-01-18 18:45 | 155 | 11kV | 127795 | 976 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1673 Turramurra Panel 44 tripped on Relays: Earth Fault, C phase IOC and EFI. Signals:Zone Earth, Tx2 Group earth and 11kV trip. Cause: Cable Fault S4241 to S35157 to S4703 | January | 2012 | 2012Q3 | 2012 | ZN1673:PA44 | ZN1673:PA21 | ZN01673/000021 | KU-RING-GAI | UG | Not Veg | 2012-01-18 | N | 130.9375 | N | 3 | N | N | 1.1101 | 39.4971 | 93388.8167
| ZN1193:PA25 | 602 | 591.1446 | 44.05 | 0.98197 | 44.05 | 18908 | 3188 | 773635 | 2012-01-19 08:35 | 2012-01-19 09:25 | 50 | 11kV | 50 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129234 A Phase DOLF : 10 Amp Fuse fatigue Volts 250V per phase A = 4A, B = 6A, C = 17A. OMS # 773635 | January | 2012 | 2012Q3 | 2012 | 501:48117 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2012-01-19 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 36.5385
| ZN1193:PA26 | 1572 | 1165.0551 | 39.8 | 0.74113 | 39.8 | 19567 | 9666 | 773746 | 2012-01-19 11:24 | 2012-01-19 12:04 | 40.3333 | 11kV | 41180.3333 | 1021 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 Zetland Pa16 fdr tripped Signals: 11kv trip Relays : Earth Fault, EFI, Fault check Frontline feeder fault from Panel 16 to S4552 Joynton Eliz | January | 2012 | 2012Q3 | 2012 | ZN188:PA16 | ZN188:PA16 | ZN00188/000016 | SYDNEY | UG | Not Veg | 2012-01-19 | N | 40.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 30093.373
| ZN1193:PA27 | 1134 | 1090.0453 | 30.94 | 0.96124 | 30.94 | 19720 | 12000 | 773787 | 2012-01-19 12:25 | 2012-01-19 13:15 | 50 | 11kV | 2900 | 58 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Unselected | N | PT12112 Wycombe Hastings - Footpath phase 31.5 Blown small branch found on PT12122 | January | 2012 | 2012Q3 | 2012 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-01-19 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 2119.2345
| ZN1193:PA28 | 2678 | 2198.664 | 33.85 | 0.82101 | 33.85 | 20279 | 18160 | 773757 | 2012-01-19 11:35 | 2012-01-19 14:03 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129240 A Phase DOLF : 10 Amp Fuse fatigue Excluded OMS 773757 (incorrect premise customer has multiple premises) OMS 774083 | January | 2012 | 2012Q3 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2012-01-19 | N | 148 | N | 5 | N | N | 1.1101 | 39.4971 | 108.154
| ZN12600:PA1 | 616 | 749.0233 | 36.27 | 1.2159 | 36.27 | 19693 | 11520 | 773992 | 2012-01-19 21:12 | 2012-01-19 23:00 | 108 | 11kV | 188343 | 1952 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.12610 Long Jetty Pnl.13 tripped on Earth Fault UG cable fault from UGOH to S.11903 Warrigal park See OMS # 774196 774194 774195 | January | 2012 | 2012Q3 | 2012 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | UG | Not Veg | 2012-01-19 | N | 96.4872 | N | 5 | N | N | 1.1101 | 39.4971 | 137635.5092
| ZN12600:PA11 | 967 | 826.871 | 30.43 | 0.85509 | 30.43 | 19019 | 4190 | 778347 | 2012-01-20 01:34 | 2012-01-20 03:25 | 111 | 11kV | 77589 | 699 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.14892 Charmhaven Pnl.9 tripped on Earth Fault, Fault Check, Reclose time, Reclosed lockout 11kV UG cable fault from Pnl.9 @ Charmhaven zone to S.14513 Whiel trying to restore feeder through panel 9. Feeder tripped again tripping TX no.1. see separate report | January | 2012 | 2012Q3 | 2012 | ZN14892:PA9 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | UG | Not Veg | 2012-01-20 | N | 111 | N | 6 | N | N | 1.1101 | 39.4971 | 56699.7527
| ZN12600:PA12 | 282 | 840.0831 | 50.65 | 2.979 | 50.65 | 19511 | 9139 | 774016 | 2012-01-20 07:48 | 2012-01-20 09:05 | 77 | 11kV | 58043 | 1003 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn965 Pennant Hills Panel 6 tripped on Signals: 11kV Trip No1 and No2 Tx Group Earth, Zone Earth. Relays: EFI -Lockout, Timer and B phase EF. Cause: UG fault between Zn965 Pennant Hills and S5480 Eddy Jannet. See OMS 774024 774748 774753 774016 | January | 2012 | 2012Q3 | 2012 | ZN965:PA6 | ZN965:PA6 | ZN00965/000006 | HORNSBY | UG | Not Veg | 2012-01-20 | N | 57.8694 | N | 6 | N | N | 1.1101 | 39.4971 | 42416.1124
| ZN12600:PA13 | 860 | 830.5185 | 37.1 | 0.96572 | 37.1 | 19812 | 12884 | 774890 | 2012-01-20 09:04 | 2012-01-20 09:09 | 5 | 11kV | 270 | 54 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129247 OC Trip during Disconnection SI 18229. When M.Brown opened ABS 74933 it drew a large arc on one phase. There was minimal load on the feeder. It tripped RAGCB 74927 Rouchel Road. This is second time this has happend in two weeks. Please check recloser for correct protection operations. Reclose was off at the time. | January | 2012 | 2012Q3 | 2012 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2012-01-20 | N | 5 | N | 6 | N | N | 1.1101 | 39.4971 | 197.308
| ZN12600:PA2 | 791 | 1233.6412 | 33 | 1.5596 | 33 | 19368 | 7925 | 774067 | 2012-01-20 09:32 | 2012-01-20 10:30 | 58.0333 | 11kV | 6151.5333 | 106 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129248 Replcaed carrier & fuse fuser fatigue 245 Volt - 126, 120, 133 Amp Excluded OMS 774067, 774077, 774097 OMS 774096 | January | 2012 | 2012Q3 | 2012 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2012-01-20 | N | 58.0333 | N | 6 | N | N | 1.1101 | 39.4971 | 4495.3591
| ZN12600:PA3 | 1750 | 1320.793 | 30.77 | 0.75474 | 30.77 | 19242 | 6439 | 774054 | 2012-01-20 09:14 | 2012-01-20 12:48 | 214 | 11kV | 1070 | 5 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 129257 A & B Phase DOLF : 20 Amp Possibly birds hit mains at river crossing Excluded OMS 774054 OMS 774917 | January | 2012 | 2012Q3 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2012-01-20 | N | 214 | N | 6 | N | N | 1.1101 | 39.4971 | 781.9244
| ZN12600:PA5 | 173 | 340.3421 | 61.68 | 1.9673 | 61.68 | 19212 | 5984 | 774089 | 2012-01-20 10:00 | 2012-01-20 14:00 | 240 | 11kV | 720 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129258 B phase 11kV tapping burnt off at UGOH pole IU-80725. Re[pairs complete. see report 129242 T & R Fdr 80337 Excluded oms 774089 OMS 774724 | January | 2012 | 2012Q3 | 2012 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Not Veg | 2012-01-20 | N | 240 | N | 6 | N | N | 1.1101 | 39.4971 | 526.1548
| ZN12600:PA9 | 1502 | 942.9426 | 31.53 | 0.62779 | 31.53 | 18780 | 1923 | 774433 | 2012-01-21 08:53 | 2012-01-21 10:38 | 104.8 | 11kV | 373.85 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129263 A Phase DOLF : 10 Amp. Excluded OMS 774433 OMS 774868 | January | 2012 | 2012Q3 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2012-01-21 | N | 93.4625 | N | 4 | N | N | 1.1101 | 39.4971 | 273.1986
| ZN12610:PA10 | 2092 | 1521.8961 | 34.59 | 0.72748 | 34.59 | 20323 | 19247 | 774458 | 2012-01-21 10:45 | 2012-01-21 14:30 | 225 | 11kV | 24075 | 107 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Transformer | Unplanned | Rain Heavy | N | At S4555 Lucinda Fox Valley Panel 37 ex Zn1673 Turramurra interrupted by DOp to replace TX after vehicle hit Kiosk. Supply restored Via LV parallel. See OMS 774458 774460 777702 | January | 2012 | 2012Q3 | 2012 | ZN1673:PA37 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | UG | Not Veg | 2012-01-21 | N | 225 | N | 4 | N | N | 1.1101 | 39.4971 | 17593.2999
| ZN12610:PA11 | 1556 | 1068.737 | 34.9 | 0.68685 | 34.9 | 18752 | 1616 | 774517 | 2012-01-21 13:52 | 2012-01-21 15:10 | 78 | 11kV | 24266 | 386 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129264 2 fault operations 3 phase Overcurrent Excluded OMS 774517 OMS 775009, 775010 | January | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-01-21 | N | 62.8653 | N | 4 | N | N | 1.1101 | 39.4971 | 17732.8771
| ZN12610:PA13 | 2127 | 1036.022 | 34.16 | 0.48708 | 34.16 | 19483 | 8987 | 774445 | 2012-01-21 09:23 | 2012-01-21 21:00 | 697 | 11kV | 1024 | 328 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | At S35370 Galston Panel 10 Tripped on IOC and EFI. Cause: Transformer Failed at PT2077 See OMS 774918 774920 774445 | January | 2012 | 2012Q3 | 2012 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-01-21 | N | 3.122 | N | 4 | N | N | 1.1101 | 39.4971 | 748.309
| ZN12610:PA16 | 1422 | 1062.8133 | 43.1 | 0.74741 | 43.1 | 19456 | 8756 | 774589 | 2012-01-22 04:52 | 2012-01-22 05:58 | 66 | 11kV | 70554 | 1069 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN.10994 Mortdale 11kV fdr P-13 "Linda Gungoh Bay" feeder tripped on: RELAYS: Earth Fault, EF chack, EFI FIELD EFIs: S.10785 & S.10676 REMARKS: Possum on UGOH near S.10107 B8 | January | 2012 | 2012Q3 | 2012 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2012-01-22 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 51558.7822
| ZN12610:PA17 | 1090 | 806.5233 | 32.6 | 0.73993 | 32.6 | 18801 | 2165 | 774604 | 2012-01-22 07:53 | 2012-01-22 09:35 | 102 | 11kV | 204 | 2 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129270 B & C Phase DOLF : 31 Amp Dead possum found at base of pole Excluded OMS 774604 OMS 775025 | January | 2012 | 2012Q3 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2012-01-22 | N | 102 | N | 3 | N | N | 1.1101 | 39.4971 | 149.0772
| ZN12610:PA18 | 1111 | 1329.5345 | 35.81 | 1.1967 | 35.81 | 19014 | 4168 | 774628 | 2012-01-22 11:14 | 2012-01-22 15:30 | 256 | 11kV | 119101 | 690 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.12 tripped on Timed O/C Cause not ascertained. Fault suspected to be from tree barks. Patrolled by DOps See OMS # 774813 774815 774816 774817 774818 774820 | January | 2012 | 2012Q3 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-01-22 | N | 172.6101 | N | 3 | N | N | 1.1101 | 39.4971 | 87035.4979
| ZN12610:PA2 | 1580 | 1276.6716 | 35.16 | 0.80802 | 35.16 | 20089 | 15891 | 774699 | 2012-01-23 00:37 | 2012-01-23 01:50 | 73 | 11kV | 42484 | 604 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | SIGNALS: 11kv trip, Zone Earth, Group 4 Earth Relays: Earth Fault, EFI EFI: S35797 S48601 S8517 Remarks: Cable fault btw S8517 & S35440 See 774985,6 exclude 774699 | January | 2012 | 2012Q3 | 2012 | ZN901:PA1 | ZN188:PA4 | ZN00188/000004 | SYDNEY | UG | Not Veg | 2012-01-23 | N | 70.3377 | N | 3 | N | N | 1.1101 | 39.4971 | 31046.0541
| ZN12610:PA20 | 917 | 724.2854 | 30.98 | 0.78984 | 30.98 | 18700 | 1167 | 774943 | 2012-01-23 11:20 | 2012-01-23 12:17 | 57 | 11kV | 82947 | 1526 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Fdr tripped Relays: Cph IOC EFI Signals: 11kv trip, Zone Eath, #2 Group Earth EFI: S4280 11kv UG fault btw SwB at S4280 & SwA at S7971 See 775386 exclude 774943 | January | 2012 | 2012Q3 | 2012 | ZN269:PA26 | ZN36800:PA49 | ZN36800/000049 | WAVERLEY | UG | Not Veg | 2012-01-23 | N | 54.3558 | N | 3 | N | N | 1.1101 | 39.4971 | 60615.2211
| ZN12610:PA22 | 1258 | 850.4133 | 33.38 | 0.676 | 33.38 | 20016 | 15072 | 775254 | 2012-01-23 20:23 | 2012-01-23 21:17 | 54 | 11kV | 4194 | 86 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S.2196 Milperra Panel 17 "Armour Ladbroke" fdr tripped Signals - 11KV trip, Zone Earth, Group Earth Relays - earth fault, EFI, fault check EFI's - S.6979, S4354, S7504, S8563, S7544, S8887, S7103, S49766 Remarks: Cable fault between S49766 Horsley Ladbroke and S3325 Horseley Amour Related jobs: #775254, 775393, 775394 | January | 2012 | 2012Q3 | 2012 | ZN2196:PA17 | ZN2196:PA17 | ZN02196/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-01-23 | N | 48.7674 | N | 3 | N | N | 1.1101 | 39.4971 | 3064.8515
| ZN12610:PA23 | 1048 | 805.5493 | 32.34 | 0.76865 | 32.34 | 19404 | 8349 | 775286 | 2012-01-24 01:42 | 2012-01-24 03:12 | 90 | 11kV | 71232 | 917 | HV | Animal Flying Fox | Animal | DC-PT Transformer | Unplanned | Unselected | N | At ZN.9550 Gwawley Bay P-42 "Box Bellingara" fdr tripped on: SIGNALS: 11kV Trip, Zone Earth, TX.1 grp Eth RELAYS: C Phase overcurrent, Earth Fault, EFI EFIs: S.9773, S,9201, S.9830 REMARKS: Bat found to be across phases of Q type PT.9408 Doris Ave. UGOH connections appear to be damaged. | January | 2012 | 2012Q3 | 2012 | ZN9550:PA42 | ZN9550:PA42 | ZN09550/000042 | SUTHERLAND | OH | Not Veg | 2012-01-24 | N | 77.6794 | N | 8 | N | N | 1.1101 | 39.4971 | 52054.2446
| ZN12610:PA24 | 1322 | 718.8488 | 29.58 | 0.54376 | 29.58 | 19793 | 12729 | 775429 | 2012-01-24 09:52 | 2012-01-24 10:40 | 47.65 | 11kV | 2573.1 | 54 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 129289 faulty x arm found at pole bl-10187 during SI 20171. SECTION ISOLATED TO REPAIR UNDER AP | January | 2012 | 2012Q3 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2012-01-24 | N | 47.65 | N | 8 | N | N | 1.1101 | 39.4971 | 1880.3456
| ZN12610:PA25 | 1371 | 1148.8127 | 38.74 | 0.83794 | 38.74 | 18712 | 1222 | 775445 | 2012-01-24 10:24 | 2012-01-24 11:07 | 43 | 11kV | 18920 | 440 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn711 Blackwattle Bay Pa15 Murray Pyrmont etc fdr tripped on Bph O/C EFI: S7527 S6351 Remarks: cnr O'Conner st & abercrombie st chippendale See 775942 exclude 775445,9 | January | 2012 | 2012Q3 | 2012 | ZN711:PA15 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2012-01-24 | N | 43 | N | 8 | N | N | 1.1101 | 39.4971 | 13826.178
| ZN12610:PA5 | 213 | 519.6724 | 38.78 | 2.4398 | 38.78 | 19667 | 11064 | 775384 | 2012-01-24 09:05 | 2012-01-24 12:30 | 205 | 11kV | 615 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129294 Single phase DOLF : 10 Amp. Excluded OMS 775384 OMS 775909 | January | 2012 | 2012Q3 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2012-01-24 | N | 205 | N | 8 | N | N | 1.1101 | 39.4971 | 449.4239
| ZN12610:PA6 | 1833 | 985.2385 | 30.92 | 0.5375 | 30.92 | 19253 | 6562 | 776016 | 2012-01-24 11:50 | 2012-01-24 12:38 | 48 | 11kV | 720 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Section of 11kV feeder ex Pnl.2 Lisarow, from AB41934 to LK 41935 interrupted to allow repairs. Car hit pole near AB41934 and dislodged HV | January | 2012 | 2012Q3 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2012-01-24 | N | 48 | N | 8 | N | N | 1.1101 | 39.4971 | 526.1548
| ZN12610:PA7 | 846 | 606.4117 | 29.89 | 0.7168 | 29.89 | 19591 | 9761 | 775674 | 2012-01-24 16:01 | 2012-01-24 16:50 | 49 | 11kV | 49 | 1 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129297 Single phase DOLF : 10 Amp Dead Bird found at sub 26199. Excluded OMS No.: 775674. (heirarchy) OMS 775928 | January | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-01-24 | N | 49 | N | 8 | N | N | 1.1101 | 39.4971 | 35.8078
| ZN12610:PA9 | 1409 | 1099.8274 | 46.88 | 0.78057 | 46.88 | 18633 | 542 | 775772 | 2012-01-24 21:55 | 2012-01-24 23:30 | 95 | 11kV | 6786.75 | 72 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | PT49303 Cliffview Wideview has blown centre phase fuse. Cause not ascertained.. See OMS 775770 775772 | January | 2012 | 2012Q3 | 2012 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2012-01-24 | N | 94.2604 | N | 8 | N | N | 1.1101 | 39.4971 | 4959.5567
| ZN9171:PA1 | 4 | 184.2261 | 40.02 | 46.0565 | 40.02 | 19322 | 7480 | 775778 | 2012-01-24 22:54 | 2012-01-25 04:30 | 336 | 11kV | 37248 | 473 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn.14891 Wyong Pnl.12 - REC 40075 Yarramalong has tripped and locked out on OC and EF Auto link 44775 failed to isolate fault, tree between autolink and PT14375 | January | 2012 | 2012Q3 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-01-24 | N | 78.7484 | N | 8 | N | N | 1.1101 | 39.4971 | 27219.7398
| ZN8000:PA10 | 409 | 1396.7075 | 40.85 | 3.4149 | 40.85 | 19656 | 10900 | 777648 | 2012-01-25 03:42 | 2012-01-25 04:44 | 62 | 11kV | 3534 | 57 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn4990 City Central 11kv "51/52A" fdr has tripped Relays: 52 fdr leg Earth fault Signals: 11kv trip Suspected UG fault See 777652 777648 | January | 2012 | 2012Q3 | 2012 | ZN3288:PA43 44DEF | ZN4990:PA51 52ABC | ZN04990/51 52ABC | SYDNEY | UG | Not Veg | 2012-01-25 | N | 62 | N | 14 | N | N | 1.1101 | 39.4971 | 2582.543
| ZN8000:PA12 | 61 | 793.5489 | #N/A | 13.009 | 39.4971 | 19556 | 9616 | 775817 | 2012-01-25 07:11 | 2012-01-25 07:46 | 34.7167 | 11kV | 50964.1 | 1593 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At ZN.9037 Miranda P-2 "Huntingdale Ave" RELAYS: A & B phase IOC, EFI SIGNALS: 11kV trip, No.1 Group Eth, Zone Eth EFIs: 1st UGOH out, S.9531 REMARKS: Branch on mains cnr Princes Hwy & Holt Rd | January | 2012 | 2012Q3 | 2012 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2012-01-25 | N | 31.9925 | N | 14 | N | N | 1.1101 | 39.4971 | 37243.0611
| ZN8000:PA14 | 19 | 1249.6472 | 46.57 | 65.7709 | 46.57 | 18647 | 718 | 775970 | 2012-01-25 10:10 | 2012-01-25 11:35 | 85 | 11kV | 255 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 129299 Fuse size: 10 Amp Volts: 243 Refer to related record 775970 | January | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-01-25 | N | 85 | N | 14 | N | N | 1.1101 | 39.4971 | 186.3465
| ZN8000:PA15 | 97 | 705.9122 | 57.7 | 7.2774 | 57.7 | 19470 | 8865 | 776085 | 2012-01-25 12:38 | 2012-01-25 15:50 | 192 | 11kV | 10809 | 161 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID129300 3 fault operations 3 phase Overcurrent UGOH joint failed at Pole -FR74801. Generator installed at LVL 29680 until weather clears for repairs. Excluded OMS 776137, 776085 OMS 777547, 777555, 777556, 777557 | January | 2012 | 2012Q3 | 2012 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | Unknown | Unknown | 2012-01-25 | N | 67.1366 | N | 14 | N | N | 1.1101 | 39.4971 | 7898.8984
| ZN8000:PA17 | 42 | 1812.1717 | 40.52 | 43.1469 | 40.52 | 19715 | 11898 | 776201 | 2012-01-25 15:27 | 2012-01-25 17:00 | 93 | 11kV | 168237 | 1809 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | LID 129304 2 fault operations Overcurrent Hot joint at Medowie Regulator No. 2. Recloser bypassed for repairs. Excluded OMS Job No. 776201. OMS 777707 | January | 2012 | 2012Q3 | 2012 | 229:34989 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Not Veg | 2012-01-25 | N | 93 | N | 14 | N | N | 1.1101 | 39.4971 | 122942.6374
| ZN8000:PA19 | 890 | 1701.1079 | 37.53 | 1.9114 | 37.53 | 18813 | 2244 | 776192 | 2012-01-25 15:16 | 2012-01-25 17:47 | 151 | 11kV | 25066 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 45012 Bar Point tripped & reclosed & locked out on B & C phase O/C Branch removed from OH mains, adjacent to PT13610 | January | 2012 | 2012Q3 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-01-25 | N | 151 | N | 14 | N | N | 1.1101 | 39.4971 | 18317.4935
| ZN8000:PA2 | 494 | 743.0248 | #N/A | 1.5041 | 39.4971 | 19250 | 6517 | 776296 | 2012-01-25 17:26 | 2012-01-25 18:37 | 71 | 11kV | 160105 | 2255 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S.15005 Belrose, Panel 4 Fdr CB tripped, reclosed and locked out on A,B and C phase IOC, reclose lockout and timing relays, efi, zone earth and 11kV trip. Field efi's down @ S.15824, S17097, S16661 and S.16611. Tree on OH O/S #63A The Esplanade between USL.24637 and tee S.15542 | January | 2012 | 2012Q3 | 2012 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Veg | 2012-01-25 | N | 71 | N | 14 | N | N | 1.1101 | 39.4971 | 117000.0117
| ZN8000:PA20 | 62 | 806.8754 | 48.38 | 13.0141 | 48.38 | 19989 | 14890 | 777792 | 2012-01-25 18:00 | 2012-01-25 19:15 | 75 | 11kV | 108586 | 1755 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn129 Hunters Hill - Panel 19 Tripped and reclosed on Relays: A phase O/C and C phase IOC, Timer Relay and Lockout Relay. Cause: Tree Fell Against OH mains O/S 7 McCallum Ave. See OMS 777792/94/96. 776356/353/351/350/341 | January | 2012 | 2012Q3 | 2012 | ZN129:PA19 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2012-01-25 | N | 61.8724 | N | 14 | N | N | 1.1101 | 39.4971 | 79351.4461
| ZN8000:PA23 | 18 | 270.7033 | 40.75 | 15.0391 | 40.75 | 19890 | 13652 | 776198 | 2012-01-25 15:20 | 2012-01-25 20:10 | 290 | 11kV | 195920 | 1688 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | LID 129303 2 fault operations Earth Fault Broken crossarm at pole HW-60093. Suspected HV mains into LV. Checked by EMSO - no damage found. Targets :E/F. excluded OMS # 776198, 776203, 776202 OMS 777664, 777668 | January | 2012 | 2012Q3 | 2012 | 260:33347 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2012-01-25 | N | 116.0664 | N | 14 | N | N | 1.1101 | 39.4971 | 143172.5573
| ZN8000:PA24 | 44 | 860.135 | 45.59 | 19.5485 | 45.59 | 20345 | 19448 | 776410 | 2012-01-25 20:05 | 2012-01-25 21:09 | 64 | 11kV | 151424 | 2366 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | S1285 Greenacre Park Panel 27 "Stiller Place, Wentworth Mayvic" fdr tripped and locked out Signals - 11kv trip, Group 2 Earth Relays - A phase IOC, Earth Fault, EFI, Lockout EFI's - S4861, S36235 Remarks: Ibis came into contact with UGOH. No damge to UGOH. Damge to bird. Feeder did not reclose as solenoid fuses were blown in Panel Related jobs: #776422, 776418, 776410, 776792 | January | 2012 | 2012Q3 | 2012 | ZN1285:PA27 | ZN1285:PA27 | ZN01285/000027 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-01-25 | N | 64 | N | 14 | N | N | 1.1101 | 39.4971 | 110656.1929
| ZN8000:PA25 | 30 | 1515.4482 | 42.02 | 50.5149 | 42.02 | 19022 | 4205 | 776314 | 2012-01-25 17:36 | 2012-01-25 21:15 | 219 | 11kV | 3504 | 16 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Rain Heavy | N | LID 129305 Sub 50906 isolated to investigate cause of electrical shock hazard in homes. Excluded OMS No.: 775963+776314. OMS 777978 | January | 2012 | 2012Q3 | 2012 | 524:33572 | 524:33572 | ZN00524/033572 | CESSNOCK | Unknown | Not Veg | 2012-01-25 | N | 219 | N | 14 | N | N | 1.1101 | 39.4971 | 2560.6198
| ZN8000:PA28 | 48 | 836.8028 | 49.07 | 17.4334 | 49.07 | 19803 | 12842 | 776426 | 2012-01-25 20:38 | 2012-01-25 22:15 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129308 Fuse size: 10 Amp, 247 volts, refer to OMS 776426 | January | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-01-25 | N | 97 | N | 14 | N | N | 1.1101 | 39.4971 | 70.8847
| ZN8000:PA3 | 105 | 1826.5742 | #N/A | 17.3959 | 39.4971 | 18594 | 146 | 776469 | 2012-01-25 23:57 | 2012-01-26 00:45 | 48 | 11kV | 3024 | 63 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | PT12089 Kangaroo Kookaburra - Cphase HDO operated 31.5K Brush tail possum cooked itself on top of PT12089 | January | 2012 | 2012Q3 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2012-01-25 | N | 48 | N | 14 | N | N | 1.1101 | 39.4971 | 2209.85
| ZN8000:PA34 | 29 | 557.1466 | 43.45 | 19.212 | 43.45 | 18753 | 1620 | 776474 | 2012-01-26 04:01 | 2012-01-26 04:06 | 5 | 11kV | 2080 | 416 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Pnl19 ex Charmhaven Zone interrupted beyond AB41880 Interrupted to allow linesman to remove large tree branch from 11kV between PT13590 abd AB44399 | January | 2012 | 2012Q3 | 2012 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Veg | 2012-01-26 | N | 5 | N | 2 | N | N | 1.1101 | 39.4971 | 1520.0027
| ZN8000:PA38 | 657 | 1183.449 | 43.27 | 1.8013 | 43.27 | 19018 | 4184 | 776176 | 2012-01-25 14:28 | 2012-01-26 08:10 | 1062 | 11kV | 82222 | 706 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 129302 3 fault operations Earth fault Faulty 11kV cable at Unimin sub 39506. Customer OK for Ausgrid to connect generator at a later date. Gen connected 26/01/2012 Excluded OMS 776232 OMS 777616, 777620, 777621, 777626 | January | 2012 | 2012Q3 | 2012 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | UG | Not Veg | 2012-01-25 | N | 116.4618 | N | 14 | N | N | 1.1101 | 39.4971 | 60085.4125
| ZN8000:PA39 | 46 | 660.8566 | 47.09 | 14.3664 | 47.09 | 19109 | 4693 | 776593 | 2012-01-26 11:30 | 2012-01-26 13:30 | 120 | 11kV | 600 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129311 B Phase DOLF : 16 Amp Elemant fatigue excluded OMS 776593 OMS 778213 | January | 2012 | 2012Q3 | 2012 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2012-01-26 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 438.4623
| ZN8000:PA4 | 141 | 180.8841 | 51.35 | 1.2829 | 51.35 | 20184 | 16741 | 778762 | 2012-01-27 01:00 | 2012-01-27 03:50 | 170 | 11kV | 50830 | 299 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | AB482 Centre Phase Bond Open circuit Ex Pa4 Pennant Hills. | January | 2012 | 2012Q3 | 2012 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Not Veg | 2012-01-27 | N | 170 | N | 11 | N | N | 1.1101 | 39.4971 | 37145.0648
| ZN8000:PA6 | 708 | 986.7897 | 34.13 | 1.3938 | 34.13 | 19353 | 7671 | 776681 | 2012-01-27 02:50 | 2012-01-27 04:32 | 102 | 11kV | 235110 | 2305 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At ZN.10994 Mortdale P-20 "LB 64155" 11kV feeder tripped ON: RELAYS: A & B phase IOC, OL, EFI ALARMS: TX.3 Grp Eth EFIs: Nil REMARKS: 11kV UGOH in Universal St, near Boundary St appears to have failed explosively | January | 2012 | 2012Q3 | 2012 | ZN10994:PA20 | ZN10994:PA20 | ZN10994/000020 | GEORGES RIVER | Unknown | Unknown | 2012-01-27 | N | 102 | N | 11 | N | N | 1.1101 | 39.4971 | 171811.4534
| ZN8000:PA7 | 34 | 1803.0962 | #N/A | 53.0322 | 39.4971 | 20099 | 15968 | 776738 | 2012-01-27 08:33 | 2012-01-27 09:34 | 61 | 11kV | 72834 | 1194 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | At ZN.9252 Jannali P-12 "Victoria Mitchell" 11kV feeder tripped, reclosed, tripped locked out on: RELAYS: A phase IOC, Timing and Lockout relay ALARMS: 11kv Trip REMARKS: Tree branch removed | January | 2012 | 2012Q3 | 2012 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2012-01-27 | N | 61 | N | 11 | N | N | 1.1101 | 39.4971 | 53224.939
| 528:83011 | 471 | 502.6568 | 41.9 | 1.0672 | 41.9 | 19325 | 7485 | 776678 | 2012-01-27 07:30 | 2012-01-27 09:45 | 135 | 11kV | 270 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 129313 Fuse size: 10 Amp Element Fatigue Refer to OMS 776678 | January | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-01-27 | N | 135 | N | 11 | N | N | 1.1101 | 39.4971 | 197.308
| 528:83013 | 1437 | 1427.7008 | 38.46 | 0.99353 | 38.46 | 19291 | 7276 | 776853 | 2012-01-27 10:59 | 2012-01-27 11:50 | 50.5167 | 11kV | 353.6167 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" LID 129317 C Phase DOLF : 16 Amp Line fuse 16A replaced with 16A BUT System diagram states 25A fitted. Please investigate & rectify by SAO or fitting correct size fuse. Trees very close to mains at pole JS-11504 require trimming. | January | 2012 | 2012Q3 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2012-01-27 | N | 50.5167 | N | 11 | N | N | 1.1101 | 39.4971 | 258.4126
| 528:83014 | 1104 | 782.8288 | 33.19 | 0.70908 | 33.19 | 18584 | 109 | 776866 | 2012-01-27 11:08 | 2012-01-27 12:45 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129319 B Phase : 20 Amp fatigued fuse | January | 2012 | 2012Q3 | 2012 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2012-01-27 | N | 97 | N | 11 | N | N | 1.1101 | 39.4971 | 70.8847
| 528:83017 | 106 | 340.6583 | #N/A | 3.2138 | 39.4971 | 19950 | 14245 | 776838 | 2012-01-27 10:42 | 2012-01-27 13:11 | 149.1667 | 11kV | 24912.2167 | 724 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2602 Clovelly 11kv OCB Pa10 fdr tripped Relays: IOC, E/F relay, EFI, Fault check EFI: S713 Douglas st Signals: 11kv Trip, ZN Earth, Tx3 GE Remarks: 11kv fdr btw S713 to S998SwA to S2395SwA See 777742 776861 exdclude 776838 776854 | January | 2012 | 2012Q3 | 2012 | ZN2602:PA10 | ZN36800:PA31 | ZN36800/000031 | RANDWICK | UG | Not Veg | 2012-01-27 | N | 34.4091 | N | 11 | N | N | 1.1101 | 39.4971 | 18205.1132
| 528:83019 | 1030 | 715.4565 | 31.7 | 0.69462 | 31.7 | 18950 | 3477 | 776994 | 2012-01-27 14:49 | 2012-01-27 17:00 | 131 | 11kV | 131 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 129323 Fuse size: 5 Amp Refer to OMS 776994 | January | 2012 | 2012Q3 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-01-27 | N | 131 | N | 11 | N | N | 1.1101 | 39.4971 | 95.7309
| 528:83020 | 1376 | 873.2555 | 35.61 | 0.63463 | 35.61 | 18719 | 1267 | 777049 | 2012-01-27 16:46 | 2012-01-27 18:00 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129322 Fuse size: 10Amp Volts 242 Refer to related record 777049 | January | 2012 | 2012Q3 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2012-01-27 | N | 74 | N | 11 | N | N | 1.1101 | 39.4971 | 54.077
| 528:83022 | 281 | 772.2572 | 52.62 | 2.7482 | 52.62 | 18714 | 1225 | 777072 | 2012-01-27 17:20 | 2012-01-27 18:20 | 60 | 11kV | 56220 | 937 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129324 1 fault operation B Phase fuse : 80 Amp Sensitive Earth fault, Line DOLF Cap bank isolated at DOLF 42167 Excluded OMS 777072, 777073,777074, 777075, 777080, 777084, 777086 OMS 777827 | January | 2012 | 2012Q3 | 2012 | 234:2001 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2012-01-27 | N | 60 | N | 11 | N | N | 1.1101 | 39.4971 | 41083.9178
| 528:83024 | 741 | 958.0575 | 45.48 | 1.2929 | 45.48 | 19794 | 12767 | 777122 | 2012-01-27 20:54 | 2012-01-28 00:20 | 206 | 11kV | 14832 | 72 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID 129325 DOLF : 20 Amp. Tree across service wire to No 16 Rexton Pde Blackalls Park. Excluded OMS 777122, 777124,777126 OMS 777839. | January | 2012 | 2012Q3 | 2012 | 225:33676 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2012-01-27 | N | 206 | N | 11 | N | N | 1.1101 | 39.4971 | 10838.7881
| ZN15009:PA1 | 2325 | 2339.016 | 44.01 | 1.006 | 44.01 | 18865 | 2684 | 777114 | 2012-01-28 00:25 | 2012-01-28 02:31 | 126 | 11kV | 56196 | 446 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Pnl.2 Peats Ridge inettrupted by DOp to repair damaged mains from MVA Feeder interrupted from AB44613 to extent of feeder. | January | 2012 | 2012Q3 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2012-01-28 | N | 126 | N | 4 | N | N | 1.1101 | 39.4971 | 41066.3793
| ZN15009:PA11 | 2391 | 1783.5398 | 39.65 | 0.74594 | 39.65 | 19294 | 7314 | 777162 | 2012-01-28 09:04 | 2012-01-28 11:30 | 146 | 11kV | 83266 | 1350 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 129327 2 fault operations B & C Phases Earth fault, Overcurrent Hazemeyer failure at Alpha Close sub 21411. Excluded OMS Job Nos. 777161, 777162, 777163, 777164, 777166, 777172 & 777191, 777874, 777879 OMS 780032, 780036 | January | 2012 | 2012Q3 | 2012 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2012-01-28 | N | 61.6785 | N | 4 | N | N | 1.1101 | 39.4971 | 60848.3369
| ZN15009:PA12 | 87 | 234.0308 | 49.22 | 2.69 | 49.22 | 20037 | 15431 | 777261 | 2012-01-28 10:00 | 2012-01-28 16:30 | 390 | 11kV | 3120 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129335 Fuse size: 20 Amp Line dolf, no cause found, not storm conditions Refer to related record 777192 and LID 129329 | January | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-01-28 | N | 390 | N | 4 | N | N | 1.1101 | 39.4971 | 2280.004
| ZN15009:PA3 | 837 | 603.721 | 40.89 | 0.72129 | 40.89 | 20160 | 16411 | 777283 | 2012-01-28 17:50 | 2012-01-28 19:00 | 70 | 11kV | 70 | 1 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129336 Fuse size 10 Amp Refer to related record 777283 No further details provided | January | 2012 | 2012Q3 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2012-01-28 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 51.1539
| ZN15009:PA5 | 1537 | 1436.7491 | 41.36 | 0.93477 | 41.36 | 20245 | 17631 | 777412 | 2012-01-29 18:18 | 2012-01-29 18:56 | 37.8833 | 11kV | 4034.7333 | 148 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129345 B Phase DOLF : 31 Amp fatigue Excluded OMS 777414 OMS 777412 | January | 2012 | 2012Q3 | 2012 | 218:7482 | 214:8666 | ZN00214/008666 | LAKE MACQUARIE | OH | Veg | 2012-01-29 | N | 27.2617 | N | 4 | N | N | 1.1101 | 39.4971 | 2948.4641
| ZN15009:PA7 | 1448 | 958.5546 | 34.01 | 0.66199 | 34.01 | 20079 | 15867 | 777453 | 2012-01-29 21:48 | 2012-01-29 22:20 | 32 | 11kV | 68416 | 2138 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.6 feeder tripped on Earth Fault, EFI Field EFIs: S.18349 Possum on UGOH bond burnt off UGOH on feeder nearest S.14858 and S.18042 | January | 2012 | 2012Q3 | 2012 | ZN12570:PA6 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2012-01-29 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 49996.3949
| ZN15009:PA9 | 629 | 702.3162 | #N/A | 1.1166 | 39.4971 | 18934 | 3367 | 777461 | 2012-01-29 22:55 | 2012-01-30 00:02 | 67 | 11kV | 148338 | 2214 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12590 Lake Munmorah Pnl.7 tripped on SEF 11kV bond burnt off AB44043 | January | 2012 | 2012Q3 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2012-01-29 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 108401.0352
| ZN3672:PA13 | 1834 | 1164.3706 | 32.7 | 0.63488 | 32.7 | 19021 | 4199 | 777997 | 2012-01-29 23:25 | 2012-01-30 00:40 | 75 | 11kV | 1238 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129350 and LID 129348 1 Fault operations Fuse size: 10 Amp, Line DOLF No Cause found, not storm conditions Refer to OM S779322 and 779326 | January | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-01-29 | N | 22.9259 | N | 4 | N | N | 1.1101 | 39.4971 | 904.6939
| ZN3672:PA21 | 123 | 154.284 | 36 | 1.2543 | 36 | 19694 | 11527 | 777488 | 2012-01-30 06:09 | 2012-01-30 06:50 | 41 | 11kV | 369 | 9 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129351 A Phase DOLF : 31 Amp. Dead Possum at pole Excluded OMS 777488 OMS 778221 | January | 2012 | 2012Q3 | 2012 | 264:81240 | 265:81645 | ZN00265/081645 | PORT STEPHENS | OH | Not Veg | 2012-01-30 | N | 41 | N | 13 | N | N | 1.1101 | 39.4971 | 269.6543
| ZN3672:PA23 | 649 | 1470.2801 | #N/A | 2.2655 | 39.4971 | 18948 | 3473 | 777492 | 2012-01-30 06:23 | 2012-01-30 08:20 | 117 | 11kV | 117 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129356 Single phase DOLF :10 Amp Job began amended from 30/01/12 07:00 as per first no supply call in on OMS 777492 | January | 2012 | 2012Q3 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2012-01-30 | N | 117 | N | 13 | N | N | 1.1101 | 39.4971 | 85.5001
| ZN3672:PA26 | 187 | 114.4891 | #N/A | 0.61224 | 39.4971 | 18880 | 2903 | 777490 | 2012-01-30 06:17 | 2012-01-30 08:35 | 137.85 | 11kV | 5789.7 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129354 A & B phase DOLF : 16 Amp | January | 2012 | 2012Q3 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-01-30 | N | 137.85 | N | 13 | N | N | 1.1101 | 39.4971 | 4230.942
| ZN3672:PA29 | 178 | 143.0131 | #N/A | 0.80344 | 39.4971 | 20403 | 20169 | 777479 | 2012-01-30 03:43 | 2012-01-30 09:25 | 342 | 11kV | 52615 | 2371 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12610 Long Jetty Pnl.11 feeder tripped and reclosed on: Earth Fault, EFI, fault check Signals: 11kV trip, Zone Earth, TX1 Group Earth EFI's: UGOH in Lcinda, UGOH in Melaluecu, S.14377 OH mains down near LK42098 See OMS # 778393 778388 | January | 2012 | 2012Q3 | 2012 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2012-01-30 | N | 22.1911 | N | 13 | N | N | 1.1101 | 39.4971 | 38449.4901
| ZN3672:PA32 | 147 | 168.8126 | #N/A | 1.1484 | 39.4971 | 20398 | 20090 | 777666 | 2012-01-30 10:41 | 2012-01-30 12:02 | 81 | 11kV | 118926 | 1515 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S187 Crows Nest Panel 17 tripped on C phase earth fault, fault check and efi. Cause: UG cable Fault. See OMS 778766 778767 777666 | January | 2012 | 2012Q3 | 2012 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2012-01-30 | N | 78.499 | N | 13 | N | N | 1.1101 | 39.4971 | 86907.6131
| ZN3672:PA34 | 274 | 846.4434 | #N/A | 3.0892 | 39.4971 | 19464 | 8822 | 777754 | 2012-01-30 11:43 | 2012-01-30 12:50 | 67 | 11kV | 41587 | 621 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 129359 2 fault operations Earth fault, Instantaneous Earth fault Excluded OMS 777754 OMS 778302, 778305 | January | 2012 | 2012Q3 | 2012 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | UG | Not Veg | 2012-01-30 | N | 66.9678 | N | 13 | N | N | 1.1101 | 39.4971 | 30390.553
| ZN3672:PA35 | 1101 | 1282.1602 | 44.46 | 1.1645 | 44.46 | 19891 | 13656 | 777776 | 2012-01-30 12:03 | 2012-01-30 12:58 | 55 | 11kV | 49133 | 895 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S5868 Gore Hill Panel 6 Tripped on EFI and Fault Check. Cause: Suspect UG fault from S5632 to S3454 See OMS 778859 778857 777776 | January | 2012 | 2012Q3 | 2012 | ZN5868:PA6 | ZN5868:PA6 | ZN05868/000006 | WILLOUGHBY | UG | Not Veg | 2012-01-30 | N | 54.8972 | N | 13 | N | N | 1.1101 | 39.4971 | 35904.9472
| ZN3672:PA36 | 1865 | 1483.9007 | 38.46 | 0.79566 | 38.46 | 19865 | 13439 | 777834 | 2012-01-30 13:09 | 2012-01-30 14:10 | 61 | 11kV | 366 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129360 A Phase DOLF : 31 Amp Fuse broke mechanically, either faulty fuse or possible over tighten at soem point was the DOPS's guess. Excluded OMS 777834 OMS 778400 | January | 2012 | 2012Q3 | 2012 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2012-01-30 | N | 61 | N | 13 | N | N | 1.1101 | 39.4971 | 267.462
| ZN3672:PA37 | 1874 | 1766.7499 | 40.7 | 0.94277 | 40.7 | 19174 | 5244 | 777798 | 2012-01-30 12:00 | 2012-01-30 14:30 | 150 | 11kV | 3450 | 23 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 129362 DOLF Sub HV fuse carrier in poor condition, staff advised will put sub in for maintenance. Excluded OMS 777798 OMS 778327 | January | 2012 | 2012Q3 | 2012 | 501:48125 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2012-01-30 | N | 150 | N | 13 | N | N | 1.1101 | 39.4971 | 2521.1582
| ZN3672:PA4 | 118 | 502.1956 | #N/A | 4.2559 | 39.4971 | 18678 | 936 | 778009 | 2012-01-30 16:53 | 2012-01-30 18:34 | 101 | 11kV | 174039.35 | 1757 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S129 Hunters Hill Panel 19 tripped on SEL. At USL201 - Road Side Phase Bond Open Circuited. See OMS 778885 778888 778886 778063 NOTE: Based on customer calls suspect S5276 was in parallel with pa19 at the time of interruption. | January | 2012 | 2012Q3 | 2012 | ZN129:PA19 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2012-01-30 | N | 99.0548 | N | 13 | N | N | 1.1101 | 39.4971 | 127182.8237
| ZN3672:PA42 | 575 | 1115.858 | 51.66 | 1.9406 | 51.66 | 19509 | 9131 | 778086 | 2012-01-30 17:50 | 2012-01-30 18:41 | 51 | 11kV | 81738 | 1894 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn 12580 Erina Pnl 1 feeder tripped on A phase timed O/C & EFI Field EFI's: Sub 18318, 18217, 18864, 14272, 18865, 11628, 13031 & 14986 UGOH Fault open circuit on pole No.ww 6401 Adjacent AB 40388. See OMS 778721 & 778716 | January | 2012 | 2012Q3 | 2012 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | Unknown | Unknown | 2012-01-30 | N | 43.1563 | N | 13 | N | N | 1.1101 | 39.4971 | 59731.7195
| ZN3672:PA43 | 2040 | 1833.9033 | 38.38 | 0.89897 | 38.38 | 18888 | 2997 | 778169 | 2012-01-30 21:00 | 2012-01-30 23:30 | 150 | 11kV | 1350 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | At PT1752 Quarry Eloura Reserve HVDO fuse operated. Cause: Fuse blown - Suspect Tx Failure. See OMS 778759 778169 778177 778187 | January | 2012 | 2012Q3 | 2012 | ZN965:PA33 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-01-30 | N | 150 | N | 13 | N | N | 1.1101 | 39.4971 | 986.5402
| ZN3672:PA44 | 2011 | 1074.0991 | 34.21 | 0.53411 | 34.21 | 19342 | 7599 | 778186 | 2012-01-30 22:48 | 2012-01-30 23:45 | 57 | 11kV | 456 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129370 A Phase DOLF : 10 Amp. Excluded OMS 778186 OMS 778421 | January | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-01-30 | N | 57 | N | 13 | N | N | 1.1101 | 39.4971 | 333.2314
| ZN3672:PA46 | 1565 | 1022.2517 | 37.96 | 0.6532 | 37.96 | 19577 | 9706 | 778198 | 2012-01-31 05:59 | 2012-01-31 08:20 | 141 | 11kV | 141 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129372 Single phase DOLF : 3 Amp Excluded OMS 778198 OMS 778755 | January | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-01-31 | N | 141 | N | 6 | N | N | 1.1101 | 39.4971 | 103.0386
| ZN3672:PA6 | 1291 | 1153.1565 | 40.33 | 0.89323 | 40.33 | 19705 | 11717 | 778201 | 2012-01-31 06:31 | 2012-01-31 08:20 | 109 | 11kV | 109 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129373 Single phase DOLF : 10 Amp Excluded OMS 778201 OMS 778760 | January | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-01-31 | N | 109 | N | 6 | N | N | 1.1101 | 39.4971 | 79.654
| ZN3672:PA9 | 1335 | 774.6369 | 31.83 | 0.58025 | 31.83 | 18943 | 3438 | 778226 | 2012-01-31 08:05 | 2012-01-31 08:35 | 30 | 11kV | 90 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129374 A phase DOLF : 10 Amp. Excluded OMS 778226 OMS 778801 | January | 2012 | 2012Q3 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-01-31 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 65.7693
| ZN262:PA13 | 113 | 321.8514 | 49.87 | 2.8482 | 49.87 | 18835 | 2383 | 778237 | 2012-01-31 08:18 | 2012-01-31 09:00 | 42 | 11kV | 84 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129375 Single phase DOLF : 10 Amp Excluded OMS 778273 OMS 778807 | January | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-01-31 | N | 42 | N | 6 | N | N | 1.1101 | 39.4971 | 61.3847
| ZN262:PA14 | 129 | 277.8482 | #N/A | 2.1539 | 39.4971 | 19669 | 11094 | 778446 | 2012-01-31 12:34 | 2012-01-31 14:15 | 101 | 11kV | 101 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129385 Single phase DOLF : 10 Amp. Excluded OMS 778446 (times) OMS 778828 | January | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-01-31 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 73.8078
| ZN262:PA15 | 1976 | 1348.6614 | 44.22 | 0.68252 | 44.22 | 20382 | 19998 | 778672 | 2012-01-31 22:14 | 2012-01-31 23:45 | 91 | 11kV | 364 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 129390 A phase DOLF : 10 Amp Excluded OMS 778672 OMS 778743 | January | 2012 | 2012Q3 | 2012 | 504:48026 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-01-31 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 266.0005
| ZN262:PA16 | 2403 | 1696.4038 | 40.17 | 0.70595 | 40.17 | 19304 | 7332 | 778715 | 2012-02-01 07:56 | 2012-02-01 08:52 | 56 | 11kV | 1344 | 24 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | At ZN.9301 Kurnell P-13 "Captain Cook Drive etc" fdr tripped on: A phase inst/timed OC and Lockout relay REMARKS: Broken Xarm o/s S.9492 Continental carbon | February | 2012 | 2012Q3 | 2012 | ZN9301:PA13 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2012-02-01 | N | 56 | N | 6 | N | N | 1.1101 | 39.4971 | 982.1556
| ZN262:PA17 | 1647 | 1000.3235 | 36.24 | 0.60736 | 36.24 | 19348 | 7627 | 778746 | 2012-02-01 08:31 | 2012-02-01 09:15 | 44 | 11kV | 44 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 129393 B Phase DOLF : 10 Amp. Excluded OMS 778746 (Incorrect sub) OMS 779220 | February | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-02-01 | N | 44 | N | 6 | N | N | 1.1101 | 39.4971 | 32.1539
| ZN262:PA19 | 1880 | 1181.1142 | 40.76 | 0.62825 | 40.76 | 19029 | 4246 | 778719 | 2012-02-01 08:02 | 2012-02-01 09:35 | 92.5333 | 11kV | 5644.0667 | 61 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Footpath phase HDO operated at PT 15936 Lady Davidson Crct. Ex panel 4 the "Forrestville West" feeder. Fuse fatigue | February | 2012 | 2012Q3 | 2012 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | OH | Not Veg | 2012-02-01 | N | 92.5257 | N | 6 | N | N | 1.1101 | 39.4971 | 4124.5174
| ZN262:PA20 | 617 | 612.2652 | 45.03 | 0.99233 | 45.03 | 19846 | 13223 | 778765 | 2012-02-01 09:01 | 2012-02-01 12:35 | 214 | 11kV | 642 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Rain Heavy | N | LID 129394 A & C Phase DOLF : 10 Amp. Faulty Transformer Excluded OMS 778765 OMS 779223 | February | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-02-01 | N | 214 | N | 6 | N | N | 1.1101 | 39.4971 | 469.1547
| ZN262:PA21 | 122 | 494.06 | 57.43 | 4.0497 | 57.43 | 18729 | 1324 | 778967 | 2012-02-01 13:08 | 2012-02-01 14:20 | 72 | 11kV | 8568 | 119 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | open circuit HDO at PT 13706 Seabrooke Hillcrest At PT 13706 Seabrooke Hillcrest HDO bond HR. Dop put PT 13706 in LV// & switched feeder for Sub's to repaired HR HDO. A/P issued at 1530 to T/Con | February | 2012 | 2012Q3 | 2012 | ZN12610:PA7 | ZN12610:PA7 | ZN12610/000007 | CENTRAL COAST | OH | Not Veg | 2012-02-01 | N | 72 | N | 6 | N | N | 1.1101 | 39.4971 | 6261.2417
| ZN262:PA25 | 157 | 286.0071 | 55.39 | 1.8217 | 55.39 | 19010 | 4149 | 779883 | 2012-02-01 15:59 | 2012-02-01 17:32 | 93 | 11kV | 23489 | 263 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S80 Chatswood Panel 11Tripped on CFI, Fault Check and Translay. Alarms: 11kV Trip Zone Earth and Group Earth. At S7712 Artarmon Edward. SW/A Tripped on Translay. Cause: UG cable fault between S47513 and S4059 See OMS 779883 77955 | February | 2012 | 2012Q3 | 2012 | ZN80:PA36 | ZN80:PA36 | ZN00080/000036 | WILLOUGHBY | UG | Not Veg | 2012-02-01 | N | 89.3118 | N | 6 | N | N | 1.1101 | 39.4971 | 17165.0684
| ZN262:PA26 | 317 | 479.836 | 56.11 | 1.5137 | 56.11 | 19387 | 8155 | 779570 | 2012-02-02 19:21 | 2012-02-02 20:11 | 50 | 11kV | 19850 | 397 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn35800 Bankstown Pa18 "Gibson Atkinson" fdr tripped on B&Cph IOC - 11kv trip Patrol by DOp found no cause See 780902 exclude 779570,2 | February | 2012 | 2012Q3 | 2012 | ZN35800:PA18 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-02-02 | N | 50 | N | 1 | N | N | 1.1101 | 39.4971 | 14505.7945
| ZN262:PA27 | 1116 | 619.7504 | 33.66 | 0.55533 | 33.66 | 18797 | 2098 | 779781 | 2012-02-03 06:02 | 2012-02-03 07:40 | 98 | 11kV | 98 | 1 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Rain Heavy | N | LID 129403 Single phase DOLF : 10 Amp Possum Excluded OMS 779781 OMS 780711 | February | 2012 | 2012Q3 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-02-03 | N | 98 | N | 5 | N | N | 1.1101 | 39.4971 | 71.6155
| ZN262:PA28 | 157 | 1072.0619 | 45.1 | 6.8284 | 45.1 | 18937 | 3388 | 779775 | 2012-02-03 05:05 | 2012-02-03 09:47 | 282 | 11kV | 15786 | 77 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser 1014 tripped, reclosed and locked out; cause indicated as weather related | February | 2012 | 2012Q3 | 2012 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Veg | 2012-02-03 | N | 205.013 | N | 5 | N | N | 1.1101 | 39.4971 | 11535.9432
| ZN262:PA29 | 433 | 312.6941 | 42.62 | 0.72216 | 42.62 | 18910 | 3191 | 779772 | 2012-02-03 00:30 | 2012-02-03 13:10 | 760 | 11kV | 13050 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV feeder from REC 47742 Euloo Peats Ridge tripped & locked out on C Phase O/C and Earth Fault Tree brought 11kV wire down on tee to PT12736 | February | 2012 | 2012Q3 | 2012 | ZN12630:PA5 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2012-02-03 | N | 435 | N | 5 | N | N | 1.1101 | 39.4971 | 9536.5551
| ZN262:PA30 | 1648 | 1534.0597 | 40.81 | 0.93086 | 40.81 | 19636 | 10548 | 780103 | 2012-02-03 13:34 | 2012-02-03 14:56 | 82 | 11kV | 59296 | 739 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S35370 Galston Panel 10 Tripped on SEL. Cause: Ab2270 Middle phase bond open circuit on Zn side ofr AB. Abnormal Switching: SW/A closed at S8401 AB482 Open. See OMS 781463 781464 781457 780103 780106 780108 780110 780115 | February | 2012 | 2012Q3 | 2012 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-02-03 | N | 80.2382 | N | 5 | N | N | 1.1101 | 39.4971 | 43331.7679
| ZN262:PA31 | 2009 | 1468.7884 | 34.64 | 0.7311 | 34.64 | 19816 | 12918 | 780089 | 2012-02-03 13:11 | 2012-02-03 15:00 | 109 | 11kV | 76242 | 789 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 129406 3 fault operations B Phase Overcurrent, Earth fault Scott Bailey heard cable fault adjacent 56610 D'Arbon Sub. Cable Isolated at Sw 56608 & 11kV Link 40902 Gardiner Cct Sw Cubicle. Sw 56110 CLOSED, Mines rescue Sub, to back feed customers Excluded OMS 780089 OMS 781333, 781336, 781337 | February | 2012 | 2012Q3 | 2012 | 523:33503 | 523:33503 | ZN00523/033503 | SINGLETON | UG | Not Veg | 2012-02-03 | N | 96.6312 | N | 5 | N | N | 1.1101 | 39.4971 | 55715.4048
| ZN262:PA32 | 868 | 678.0592 | 38.93 | 0.78117 | 38.93 | 19036 | 4269 | 780315 | 2012-02-04 07:57 | 2012-02-04 11:05 | 188 | 11kV | 7484 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 44853 Ourimbah Bumble (ex Pnl.1 West Gosford) CB opened and locked out. Rec 44853 was out of scan at the time (RTU fail) so no trip alarm or indication of status was available. 11kV wire on ground adjacent PT12244. See OMS # 781604 781603 | February | 2012 | 2012Q3 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-02-04 | N | 174.0465 | N | 2 | N | N | 1.1101 | 39.4971 | 5469.0865
| ZN262:PA33 | 105 | 143.528 | 46.9 | 1.3669 | 46.9 | 20401 | 20136 | 780415 | 2012-02-04 12:02 | 2012-02-04 13:15 | 73 | 11kV | 1387 | 19 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.1329 Cullens Melville - Centre phase HV BB-LAS 20Amp fuse replaced High resistance contact on fuse holder GIS errors # 781610 781613 | February | 2012 | 2012Q3 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2012-02-04 | N | 73 | N | 2 | N | N | 1.1101 | 39.4971 | 1013.5787
| ZN262:PA34 | 408 | 780.6404 | 54.1 | 1.9133 | 54.1 | 19781 | 12634 | 780664 | 2012-02-05 23:33 | 2012-02-06 01:05 | 92 | 11kV | 82626 | 1073 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At Zn 15014 Mona Vale - 11Kv panel No. 7 Relays: B & C phase IOC, EFI, Fault check relay Signals: 11Kv trip, Zone Earth At PT15395 Elimatta Rd - Centre and road side 11Kv drop fuses operated with 11Kv SA's damaged due to flashover caused by possum. See job #780664, #780665, #781112, #781107 | February | 2012 | 2012Q3 | 2012 | ZN15014:PA7 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | OH | Not Veg | 2012-02-05 | N | 77.0047 | N | 1 | N | N | 1.1101 | 39.4971 | 60380.6437
| ZN262:PA39 | 798 | 989.7664 | 51.02 | 1.2403 | 51.02 | 19964 | 14620 | 780767 | 2012-02-06 08:39 | 2012-02-06 11:11 | 152 | 11kV | 198892.3667 | 3841 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn.36300 Balgowlah Nth Panel 11 Fdr CB tripped on 11R A and B phase OC, 11kV trip. Tree/branch brought down 11kV OH in Rickard St | February | 2012 | 2012Q3 | 2012 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Veg | 2012-02-06 | N | 51.7814 | N | 6 | N | N | 1.1101 | 39.4971 | 145344.6752
| ZN262:PA40 | 560 | 723.0796 | 44.25 | 1.2912 | 44.25 | 19532 | 9382 | 780724 | 2012-02-06 08:15 | 2012-02-06 11:50 | 215 | 11kV | 99408 | 874 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | At S965 Pennant Hills Panel 26 tripped reclosed tripped and locked out on A phase IOC and Timed OC. B phase IOC. Timing and Lockout Cause: Broken Pin insulator on AB2157,. AB Bonden Through See OMS 781914 781919 781918 781917 | February | 2012 | 2012Q3 | 2012 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Not Veg | 2012-02-06 | N | 113.7391 | N | 6 | N | N | 1.1101 | 39.4971 | 72644.4344
| ZN262:PA41 | 1202 | 1015.3878 | 43.06 | 0.84475 | 43.06 | 20117 | 16088 | 780687 | 2012-02-06 07:50 | 2012-02-06 12:40 | 290 | 11kV | 148976.8667 | 2954 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | At Zone 15014 Mona Vale Panel #5, feeder interrupted by Aop. S.17003 sw/A closed; S.16465 sw/B open. During routine switching between Mona Vale Zone and Narrabeen Zone the point of isolation 11Kv link 24366 failed (fell apart) whilst the Dop was opening link with his HV link stick. Poe requested both feeders involved be opened at the respective zones. See also jobs #781924/926/934/933/942 & #780691/688. | February | 2012 | 2012Q3 | 2012 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2012-02-06 | N | 50.4323 | N | 6 | N | N | 1.1101 | 39.4971 | 108867.9001
| ZN262:PA42 | 2153 | 1248.0471 | 34.96 | 0.57968 | 34.96 | 18580 | 85 | 780880 | 2012-02-06 10:15 | 2012-02-06 14:00 | 225 | 11kV | 225 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129421 C Phase DOLF LAs Blown. Crew replaced under AP. Volts: Excluded OMS780880 OMS 781423 | February | 2012 | 2012Q3 | 2012 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2012-02-06 | N | 225 | N | 6 | N | N | 1.1101 | 39.4971 | 164.4234
| ZN262:PA5 | 2022 | 1432.3711 | 43.63 | 0.70839 | 43.63 | 19315 | 7398 | 781114 | 2012-02-06 15:16 | 2012-02-06 18:35 | 199 | 11kV | 199 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 129422 Single phase DOLF : 3 Amp. sub isolated to replace 2 x la's replaced 2 x fuses Excluded OMS 781114 OMS 781428 | February | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2012-02-06 | N | 199 | N | 6 | N | N | 1.1101 | 39.4971 | 145.4233
| ZN262:PA6 | 1302 | 961.07 | 35.37 | 0.73815 | 35.37 | 19858 | 13373 | 781412 | 2012-02-06 19:15 | 2012-02-06 21:45 | 150 | 11kV | 15750 | 105 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | LID 129423 No protection operation, sub isolated on advice of excessively high discharge noises on termination to Sw 29005 at Shortland Sewerage Plant sub. Staff advised the end box will need permanant repairs to the end box for Sw 29005 in the near future. | February | 2012 | 2012Q3 | 2012 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | UG | Not Veg | 2012-02-06 | N | 150 | N | 6 | N | N | 1.1101 | 39.4971 | 11509.6355
| ZN262:PA7 | 2271 | 1514.6569 | 38.44 | 0.66696 | 38.44 | 20041 | 15521 | 781312 | 2012-02-07 03:48 | 2012-02-07 05:00 | 72 | 11kV | 144 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129425 A Phase DOLF : 10 Amp Excluded OMS 781312 OMS 781421 | February | 2012 | 2012Q3 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2012-02-07 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 105.231
| ZN262:PA8 | 114 | 825.8475 | 55.92 | 7.2443 | 55.92 | 19856 | 13361 | 781331 | 2012-02-07 07:57 | 2012-02-07 08:20 | 23.05 | 11kV | 2051.45 | 89 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | CC1: 22-"Refer to SOp" LID 129427 A Phase DOLF : 40 Amp. Excluded OMS 781331, 781335 OMS 781334 | February | 2012 | 2012Q3 | 2012 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Veg | 2012-02-07 | N | 23.05 | N | 5 | N | N | 1.1101 | 39.4971 | 1499.1392
| 213:33769 | 1218 | 650.0166 | 30.27 | 0.53368 | 30.27 | 19888 | 13635 | 781351 | 2012-02-07 08:23 | 2012-02-07 09:42 | 79 | 11kV | 1915 | 45 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 129428 Feeder deenergised after reports of live LV mains on vehicle after Trip & Reclose. See LID Report No. 129426. Car hit pole CN-60008 at sub 51047. LV mains on vehicle. LVF 51047 did not operate. Excluded OMS 781351, 781388 OMS 781848,781850 | February | 2012 | 2012Q3 | 2012 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2012-02-07 | N | 42.5556 | N | 5 | N | N | 1.1101 | 39.4971 | 1399.4255
| 213:33770 | 869 | 526.065 | 29.9 | 0.60537 | 29.9 | 19209 | 5908 | 781462 | 2012-02-07 10:38 | 2012-02-07 15:00 | 262 | 11kV | 6812 | 26 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn.12690 Berkeley Vale Pnl.24R feeder from AB42102 to extent of feeder interrupted by DOp. Inetrrupted for safety reasons - 11kV CCT O/H conductor down O/S 145 Palmdale Rd. AB42102 opened section of 11kV feeder isolated and earthed. Linesman have repaired and feeder returned to service | February | 2012 | 2012Q3 | 2012 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2012-02-07 | N | 262 | N | 5 | N | N | 1.1101 | 39.4971 | 4978.0087
| 213:33771 | 1628 | 1415.735 | 36.19 | 0.86962 | 36.19 | 20263 | 18012 | 782290 | 2012-02-07 17:51 | 2012-02-07 19:00 | 69 | 11kV | 18804 | 356 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S35500 Top Ryde Panel 16 tripped on Relays:B phase O/C, EFI and Fault Check. Signals: 11kV Trip, Zone Earth and No2 Group Earth. Cause: At S950 Hancott Dobson 11kV endbox failed. See OMS 782290 782292 | February | 2012 | 2012Q3 | 2012 | ZN35500:PA16 | ZN35500:PA16 | ZN35500/000016 | RYDE | UG | Not Veg | 2012-02-07 | N | 52.8202 | N | 5 | N | N | 1.1101 | 39.4971 | 13741.4086
| 213:33773 | 1423 | 910.9736 | 33.75 | 0.64018 | 33.75 | 19576 | 9704 | 782097 | 2012-02-08 15:41 | 2012-02-08 16:50 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129443 Single phase DOLF : 10 Amp. fuse fatigue Excluded OMS 782097 OMS 782329 | February | 2012 | 2012Q3 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-02-08 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 50.4232
| 213:33774 | 1374 | 847.6321 | 31.56 | 0.61691 | 31.56 | 19227 | 6234 | 782273 | 2012-02-08 16:40 | 2012-02-08 17:52 | 72 | 11kV | 22824 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 129444 3 fault operations B & C Phase Overcurrent Tree branch removed from 11kv OHM near ABS 12767. Excluded OMS 782129. OMS 782273 | February | 2012 | 2012Q3 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-02-08 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 16679.106
| 213:33775 | 1158 | 1023.986 | 42.23 | 0.88427 | 42.23 | 19357 | 7733 | 782204 | 2012-02-08 21:27 | 2012-02-09 00:10 | 163 | 11kV | 20864 | 128 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | LID 129445 B Phase DOLF : 20 Amp lv mains clashed together excluded oms 782204, 782208, 782213 oms 782300 | February | 2012 | 2012Q3 | 2012 | 230:34051 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2012-02-08 | N | 163 | N | 3 | N | N | 1.1101 | 39.4971 | 15246.7958
| 213:33777 | 800 | 743.7835 | 41.64 | 0.92973 | 41.64 | 18907 | 3186 | 782225 | 2012-02-09 05:07 | 2012-02-09 06:45 | 98 | 11kV | 294 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129446 DOLF excluded OMS 782225 OMS 782268 | February | 2012 | 2012Q3 | 2012 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2012-02-09 | N | 98 | N | 4 | N | N | 1.1101 | 39.4971 | 214.8465
| ZN630:PA10 | 306 | 314.0796 | #N/A | 1.0264 | 39.4971 | 19861 | 13393 | 782332 | 2012-02-09 10:13 | 2012-02-09 11:20 | 67 | 11kV | 134 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129452 Fuse size: 10 Amp No Cause Found - Not Storm Conditions No readings taken | February | 2012 | 2012Q3 | 2012 | 227:13020 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Veg | 2012-02-09 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 97.9232
| ZN630:PA16 | 304 | 106.6486 | #N/A | 0.35082 | 39.4971 | 18767 | 1825 | 782435 | 2012-02-09 12:10 | 2012-02-09 16:30 | 260 | 11kV | 37180 | 143 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Planned LID 129456 Excluded OMS 782787 | February | 2012 | 2012Q3 | 2012 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Veg | 2012-02-09 | N | 260 | N | 4 | N | N | 1.1101 | 39.4971 | 27170.0474
| ZN630:PA18 | 200 | 270.0497 | 45.42 | 1.3502 | 45.42 | 20307 | 19025 | 782583 | 2012-02-09 15:59 | 2012-02-09 18:09 | 129.7 | 11kV | 94690.2333 | 798 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15005 Belrose, Panel 10 Fdr CB tripped on B phase OC, reclose, timing relay lockout, frame leakage fault check, efi, #1 and #2 Tx fault check, 11kV trip, zone earth. Field efi's down at S.16807, S.16752, S.17065, S.16782, S.16781, S.16642, S.16494 and S.16819. Initially efi's were NOT reset from previous fault; hence unsuccessful try-back | February | 2012 | 2012Q3 | 2012 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | UG | Not Veg | 2012-02-09 | N | 118.6594 | N | 4 | N | N | 1.1101 | 39.4971 | 69196.8296
| ZN630:PA19 | 20 | 732.3343 | 46.84 | 36.6167 | 46.84 | 18673 | 910 | 782913 | 2012-02-10 12:58 | 2012-02-10 14:10 | 72 | 11kV | 118008 | 1639 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 129466 C Phase Earth fault cable fault at P HS 82208, section isolated, fdr restored Excluded OMS 782913 | February | 2012 | 2012Q3 | 2012 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2012-02-10 | N | 72 | N | 7 | N | N | 1.1101 | 39.4971 | 86236.7658
| ZN630:PA22 | 640 | 1238.423 | #N/A | 1.935 | 39.4971 | 19275 | 7006 | 782996 | 2012-02-10 15:57 | 2012-02-10 17:20 | 83 | 11kV | 72758 | 2204 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Lightning | N | @ Long Jetty Zone - Pnl.24 tripped on C phase O/C, Earth Fault, fault check relay Abnormal Switching: N/O AB41312 Closed and AB 42528 open & defective Pnl.20 tripped and reclosed on C phase O/C, Earth Fault Both feeders tripped at the same time. Fault located near N/O AB 44165. Pnl.20 reclosed suseccfully. AB44171 bond blown off and PT.14094 Debra Ann Melisa - Internal tank fault HDO blown twice and surge arrestor blown clear. restored via LV // See OMS # 783764 783765 783766 | February | 2012 | 2012Q3 | 2012 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Not Veg | 2012-02-10 | N | 33.0118 | N | 7 | N | N | 1.1101 | 39.4971 | 53169.4004
| ZN630:PA24 | 743 | 739.9756 | #N/A | 0.99593 | 39.4971 | 18627 | 466 | 783050 | 2012-02-10 16:10 | 2012-02-10 19:15 | 185 | 11kV | 4116 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129489 A Phase DOLF : 10 Amp Excluded OMS 783077, 784500, 785223 OMS 790487 | February | 2012 | 2012Q3 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2012-02-10 | N | 16.3333 | N | 7 | N | N | 1.1101 | 39.4971 | 3007.8514
| ZN630:PA25 | 127 | 1060.6418 | 50.87 | 8.3515 | 50.87 | 20375 | 19927 | 782991 | 2012-02-10 15:56 | 2012-02-10 19:20 | 204.1833 | 11kV | 37161.3667 | 182 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129479 Tree on mains in Brooks St .Sub 11714 isolated for clearance. Sub placed in parallel. Excluded OMS 783085 OMS 782991 | February | 2012 | 2012Q3 | 2012 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Veg | 2012-02-10 | N | 204.1833 | N | 7 | N | N | 1.1101 | 39.4971 | 27156.4307
| ZN630:PA27 | 428 | 531.648 | 49.46 | 1.2422 | 49.46 | 19090 | 4568 | 784505 | 2012-02-10 16:10 | 2012-02-10 20:00 | 230 | 11kV | 460 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129492 A Phase DOLF : 10 Amp. Excluded OMS 784505 OMS 785222 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-10 | N | 230 | N | 7 | N | N | 1.1101 | 39.4971 | 336.1544
| ZN630:PA30 | 1 | 16.2575 | #N/A | 16.2575 | 39.4971 | 19505 | 9101 | 783104 | 2012-02-10 19:51 | 2012-02-11 01:05 | 314 | 11kV | 145679.7833 | 1229 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At ZN.9245 Engadine P-8 "Numantia Copeland" fdr tripped, reclosed, tripped and locked out on: RELAYS: C phase time overcurrent, Lockout SIGNALS: 11kV trip REMARKS: at N/O AB.35535 insulator on the AB.35610 side was found to be cracked | February | 2012 | 2012Q3 | 2012 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2012-02-10 | N | 118.5352 | N | 7 | N | N | 1.1101 | 39.4971 | 106458.4888
| ZN630:PA31 | 707 | 1165.1514 | 44.93 | 1.648 | 44.93 | 18786 | 2017 | 783037 | 2012-02-10 16:48 | 2012-02-11 08:00 | 912 | 11kV | 1878 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129494 single phase DOLF : 20 Amp. Sub 27794 also had blown DOLF Excluded OMS 783037 OMS 783813, 783815. | February | 2012 | 2012Q3 | 2012 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-02-10 | N | 469.5 | N | 7 | N | N | 1.1101 | 39.4971 | 1372.387
| ZN630:PA32 | 292 | 408.4002 | 53.26 | 1.3986 | 53.26 | 19218 | 6073 | 783135 | 2012-02-11 07:48 | 2012-02-11 08:28 | 40 | 11kV | 71800 | 1795 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Electrical Storm | N | LID 129497 2 fault operations A & C Phase Instantaneous Overcurrent Lightning struck ABS 49891. Fdr 80329 T/Reclose see report # 129496. Fdr 80332 L/O. | February | 2012 | 2012Q3 | 2012 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Not Veg | 2012-02-11 | N | 40 | N | 27 | Y | Y | 1.1101 | 39.4971 | 52469.3223
| ZN630:PA33 | 55 | 662.6026 | #N/A | 12.0473 | 39.4971 | 18839 | 2415 | 783197 | 2012-02-11 11:32 | 2012-02-11 12:15 | 43 | 11kV | 86 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129502 C phase DOLF : 10 Amp. Excluded OMS 783197 OMS 784523 | February | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2012-02-11 | N | 43 | N | 27 | Y | Y | 1.1101 | 39.4971 | 62.8463
| ZN630:PA34 | 176 | 631.0113 | 52.58 | 3.5853 | 52.58 | 20217 | 17160 | 783158 | 2012-02-11 11:20 | 2012-02-11 12:45 | 85 | 11kV | 2210 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Berekely Vale Zone Pnl.16 - USL 43748 interrupted by DOp for lineworks to remove tree brnach off the HV mains | February | 2012 | 2012Q3 | 2012 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 85 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1615.0028
| ZN630:PA35 | 406 | 409.2493 | 41.9 | 1.008 | 41.9 | 19248 | 6505 | 783781 | 2012-02-11 11:50 | 2012-02-11 14:30 | 160 | 11kV | 960 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Woy Woy Zone Pnl.14 - USL40638 opened by DOp to remove large tree into the HV mains and on top of PT.13935 Mullet Creek | February | 2012 | 2012Q3 | 2012 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 160 | N | 27 | Y | Y | 1.1101 | 39.4971 | 701.5397
| ZN630:PA38 | 2242 | 1302.5633 | 33.78 | 0.58098 | 33.78 | 18954 | 3485 | 783196 | 2012-02-11 13:45 | 2012-02-11 14:35 | 50 | 11kV | 2950 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | DOp isolated and earthed feeder at PT.1262 and line crew removed tree branch | February | 2012 | 2012Q3 | 2012 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 50 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2155.773
| ZN630:PA4 | 231 | 280.6202 | #N/A | 1.2148 | 39.4971 | 19538 | 9488 | 783208 | 2012-02-11 13:50 | 2012-02-11 14:45 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129505 Fuse: 10 Amp Ken garland on site | February | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-02-11 | N | 55 | N | 27 | Y | Y | 1.1101 | 39.4971 | 40.1924
| ZN630:PA40 | 303 | 1271.1381 | 47.36 | 4.1952 | 47.36 | 19916 | 13948 | 783238 | 2012-02-11 14:00 | 2012-02-11 15:01 | 61 | 11kV | 65936 | 1796 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At ZN.10994 Mortdale 11kV fdr P-13 "Linda Gungah Bay" feeder tripped on: RELAYS: 50 T A B & C phase, EFI, Lockout SIGNALS: 11kV Trip, ZE, TX.3 GE FIELD EFIs: S.10785 & S.10676 REMARKS: No cause found. Lightning in area. | February | 2012 | 2012Q3 | 2012 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Veg | 2012-02-11 | N | 36.7127 | N | 27 | Y | Y | 1.1101 | 39.4971 | 48184.084
| ZN1788:PA14 | 1144 | 986.4795 | 35.42 | 0.86231 | 35.42 | 20389 | 20040 | 783315 | 2012-02-11 15:32 | 2012-02-11 16:55 | 83 | 11kV | 136037 | 1639 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129519 1 fault operation C Phase Overcurrent RECLOSE TURNED OFF FOR EMERGENCY JOB .CLOSED BACK ON AFTER FAULT. | February | 2012 | 2012Q3 | 2012 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2012-02-11 | N | 83 | N | 27 | Y | Y | 1.1101 | 39.4971 | 99411.8272
| ZN1788:PA15 | 1045 | 1725.6747 | 41.08 | 1.6514 | 41.08 | 18789 | 2041 | 783213 | 2012-02-11 12:08 | 2012-02-11 17:01 | 293 | 11kV | 586 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | No L details only details available are from customer call in on 783213 and the job was referred to sop | February | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-02-11 | N | 293 | N | 27 | Y | Y | 1.1101 | 39.4971 | 428.2315
| ZN1788:PA16 | 1181 | 1537.5479 | 38.11 | 1.3019 | 38.11 | 19777 | 12602 | 783277 | 2012-02-11 15:08 | 2012-02-11 17:53 | 165 | 11kV | 12045 | 73 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV Pnl.8 Ex Wyong Zn - REC 48425 Kangy Angy tripped reclosed and locked out on IOC & OC Tree brnach n OH mains O/S 31 Old Maitland Rd | February | 2012 | 2012Q3 | 2012 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 165 | N | 27 | Y | Y | 1.1101 | 39.4971 | 8802.1307
| ZN1788:PA17 | 1583 | 936.0786 | 36.86 | 0.59133 | 36.86 | 18773 | 1897 | 783404 | 2012-02-11 16:58 | 2012-02-11 18:12 | 74 | 11kV | 740 | 10 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Erina Zn Pnl.16R - 11kV USL 40148 opened and isolated by DOp to remove tree from mains. | February | 2012 | 2012Q3 | 2012 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 74 | N | 27 | Y | Y | 1.1101 | 39.4971 | 540.7702
| ZN1788:PA42 | 890 | 1081.5733 | #N/A | 1.2153 | 39.4971 | 19461 | 8793 | 783308 | 2012-02-11 15:21 | 2012-02-11 18:59 | 218 | 11kV | 8118 | 48 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129518 2 fault operations C Phase Earth fault MAIN DOWN AT POLE ES-62990 POKOLBIN. Excluded OMS 783308,783313, 783323, 783342 OMS 784172, 784175 | February | 2012 | 2012Q3 | 2012 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2012-02-11 | N | 169.125 | N | 27 | Y | Y | 1.1101 | 39.4971 | 5932.395
| ZN1788:PA43 | 1447 | 1274.9466 | 40.82 | 0.8811 | 40.82 | 20360 | 19853 | 783257 | 2012-02-11 14:48 | 2012-02-11 19:40 | 292 | 11kV | 143092 | 525 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Pnl.2 Ex peats Ridge Zn - REC 45189 Cooks Peats Ridge 0.5 tripped reclosed and locked out on IOC and OC. 11kV feeder was tried back after tree was removed off mains. Did not restore due to more trees on mains in Neverfail Caravan Park Lineworkers removed most of the brnaches of the 11kV mains. See OMS # 783860 783861 783863 | February | 2012 | 2012Q3 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 272.5562 | N | 27 | Y | Y | 1.1101 | 39.4971 | 104567.4131
| ZN1788:PA44 | 1340 | 1039.8457 | 33.93 | 0.776 | 33.93 | 20094 | 15929 | 785013 | 2012-02-11 16:44 | 2012-02-11 21:00 | 256 | 11kV | 22784 | 89 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At S1673 Turramurra ex Pa48. CP2407 Yound Billyard B phase HV Fuse Operated. 40A fuse blown Cause: At S4725 Randolf Young Transformer Failed. See OMS 785037 785013 783393/391/396 | February | 2012 | 2012Q3 | 2012 | ZN1673:PA48 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | UG | Not Veg | 2012-02-11 | N | 256 | N | 27 | Y | Y | 1.1101 | 39.4971 | 16649.8752
| ZN1788:PA47 | 854 | 806.0431 | 48.49 | 0.94384 | 48.49 | 18707 | 1193 | 783408 | 2012-02-11 21:07 | 2012-02-11 21:35 | 28 | 11kV | 2996 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Peats Ridge Zn section of Pnl.2 from LB43711 interrupted by DOp to remove numerous large branches off 11kV CCT | February | 2012 | 2012Q3 | 2012 | ZN12630:PA2 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 28 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2189.3884
| ZN1788:PA61 | 1156 | 1131.1271 | #N/A | 0.97848 | 39.4971 | 19874 | 13534 | 783467 | 2012-02-11 21:18 | 2012-02-11 22:50 | 92 | 11kV | 91422 | 1657 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn342 Paddington Pa18 tripped on OC EF Pa18L EFI - S935 remarks - UG fault. Suspected 1kV S935 to S6816 to S3692 @S730 Dist 5 ABCph blown Dist found in LV// for Paddington Pa18 fdr fault LV link box 12016 appears to have links closed. UG mains to investigate and remove LV// link See 783946,8,50 GIS 783957 LV// 783960 Exclude 783467,8,72 | February | 2012 | 2012Q3 | 2012 | ZN342:PA18 | ZN342:PA18 | ZN00342/000018 | SYDNEY | UG | Not Veg | 2012-02-11 | N | 55.1732 | N | 27 | Y | Y | 1.1101 | 39.4971 | 66808.5011
| ZN1788:PA67 | 75 | 313.5466 | #N/A | 4.1806 | 39.4971 | 20234 | 17406 | 783293 | 2012-02-11 15:16 | 2012-02-11 23:15 | 479 | 11kV | 87684 | 315 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV Pnl.12 ex Berkeley Vale zone. REC 44999 Warner tripped reclsoed and locked out on IOC & OC Tree brnach nrought down OH adjacent PT12046 and 11kV down Adj PT48816 See OMS # 783880 783881 783882 | February | 2012 | 2012Q3 | 2012 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 278.3619 | N | 27 | Y | Y | 1.1101 | 39.4971 | 64076.881
| ZN1788:PA69 | 770 | 1098.5947 | #N/A | 1.4267 | 39.4971 | 18812 | 2239 | 783481 | 2012-02-11 22:22 | 2012-02-11 23:35 | 73 | 11kV | 73 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129521 Fuse : 10 Amp | February | 2012 | 2012Q3 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2012-02-11 | N | 73 | N | 27 | Y | Y | 1.1101 | 39.4971 | 53.3462
| ZN1788:PA70 | 770 | 610.5951 | #N/A | 0.79298 | 39.4971 | 19277 | 7147 | 783239 | 2012-02-11 16:04 | 2012-02-11 23:45 | 461 | 11kV | 162421 | 801 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | OHM down between pole IQ-86416 & IQ-86424 LID 129515 2 Fault operations Overcurrent, Earth Fault Excluded OMS 783485, 783386, 783367 OMS 784407, 784410, 784411 | February | 2012 | 2012Q3 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-02-11 | N | 202.7728 | N | 27 | Y | Y | 1.1101 | 39.4971 | 118692.4762
| 240:34835 | 936 | 1061.4918 | 45.43 | 1.1341 | 45.43 | 18573 | 58 | 783456 | 2012-02-11 20:21 | 2012-02-12 | 219 | 11kV | 2190 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129523 C Phase DOLF : 10 Amp. Excluded OMS 783456 OMS 784478 | February | 2012 | 2012Q3 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2012-02-11 | N | 219 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1600.3874
| 240:34840 | 1505 | 1057.1645 | 39.17 | 0.70243 | 39.17 | 20378 | 19967 | 783403 | 2012-02-11 18:57 | 2012-02-12 | 303 | 11kV | 303 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 129522 A Phase DOLF : 10 Amp. Excluded OMS 783403 OMS 784456 | February | 2012 | 2012Q3 | 2012 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2012-02-11 | N | 303 | N | 27 | Y | Y | 1.1101 | 39.4971 | 221.4235
| 240:34843 | 375 | 764.3809 | 45.16 | 2.0383 | 45.16 | 19674 | 11131 | 783407 | 2012-02-11 17:23 | 2012-02-12 02:00 | 517 | 11kV | 4653 | 9 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Electrical Storm | N | LID 129527 Sub Isolated Terasaki LV switch 29414 faulty at sub temporary LV fuses installed (1000 amp) at sub. Excluded oms # 783407 OMS 784440 | February | 2012 | 2012Q3 | 2012 | 503:48077 | 532:83295 | ZN00532/083295 | MAITLAND | Unknown | Not Veg | 2012-02-11 | N | 517 | N | 27 | Y | Y | 1.1101 | 39.4971 | 3400.2752
| 240:34846 | 853 | 1282.5676 | 43.77 | 1.5036 | 43.77 | 19836 | 13052 | 783426 | 2012-02-11 18:26 | 2012-02-12 10:15 | 949 | 11kV | 5694 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129531 3 phase DOLF's : 20 Amp. All three line fuses had blown. Note operators G Mulvaney and D Robertson assisted as previously staff sent to attend during the night shift were blocked by floods which caused the delay in accessing the area to OMS number 783454, 783426 and 783498 as OMS malfuntion prevented jobbs rolling into one job. OMS 784447 | February | 2012 | 2012Q3 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2012-02-11 | N | 949 | N | 27 | Y | Y | 1.1101 | 39.4971 | 4161.0073
| 240:34849 | 2232 | 1761.4714 | 36.76 | 0.78919 | 36.76 | 20104 | 16025 | 783253 | 2012-02-11 14:43 | 2012-02-12 12:18 | 1295 | 11kV | 297762 | 543 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV Pnl.17 ex Somersby Zone - REC 48437 Peats Ridge Cooks 1.35 tripped / reclosed / locked out on IOC & OC Tree on mains wires on ground around PT13127. Treeremoved from HV and the LV has been isolated. Line worker to make repairs to x arm and LV mains. See OMS # 783844 783845 783846 783847 | February | 2012 | 2012Q3 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 548.3646 | N | 27 | Y | Y | 1.1101 | 39.4971 | 217595.6871
| 240:34852 | 305 | 1291.7906 | 47.08 | 4.2354 | 47.08 | 19033 | 4260 | 784088 | 2012-02-11 15:48 | 2012-02-12 14:15 | 1347 | 11kV | 12123 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV feeder ex Peats Ridge Zn Pnl.1 from LK42028 to repair PT11843 Brnach brought down LV OH and caused damage to PT11843. Dop isolated HV & LV for safety @ 19:00 (11/2) Dop isolated PT.13901 and extended isolation to LK42028 on 12/2 @ 8:28 and issued access permit for T/Con and L/man to repair PT | February | 2012 | 2012Q3 | 2012 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 1347 | N | 27 | Y | Y | 1.1101 | 39.4971 | 8859.1308
| ZN4545:PA11 | 645 | 358.7082 | 35.76 | 0.55614 | 35.76 | 19765 | 12480 | 783344 | 2012-02-11 15:18 | 2012-02-12 15:00 | 1422 | 11kV | 457168 | 2067 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn 14891 Wyong Pnl10 tripped on B phase O/C, Earth Fault, Fault Check. Field EFI S14857 Tree brnach brought OH down in various sections of feeder in Tuggerawong Rd. PT.13100 left inetrrupted due to HV into LV See OMS # 784093 784094 784095 784100 | February | 2012 | 2012Q3 | 2012 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 221.1746 | N | 27 | Y | Y | 1.1101 | 39.4971 | 334084.8902
| ZN4545:PA13 | 303 | 264.0471 | 56.08 | 0.87144 | 56.08 | 20319 | 19183 | 783602 | 2012-02-12 15:23 | 2012-02-12 17:46 | 142.7833 | 11kV | 26358.3667 | 1121 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Unselected | N | At ZN.1290 Leightonfield P-4 "Miller Sir Thomas" fdr tripped, & reclosed: RELAYS: A & C phase IOC, reclose timer and Lockout. SIGNALS: 11kV trip REMARKS: Lightning strike to PT.108 Mundamata St | February | 2012 | 2012Q3 | 2012 | ZN1290:PA4 | ZN1290:PA2 | ZN01290/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-02-12 | N | 23.5133 | N | 9 | N | N | 1.1101 | 39.4971 | 19261.9169
| ZN4545:PA17 | 31 | 399.1772 | #N/A | 12.8767 | 39.4971 | 20235 | 17415 | 783597 | 2012-02-12 16:10 | 2012-02-12 19:14 | 184 | 11kV | 17450 | 248 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Unselected | N | CP229 Cobah Rd Tripped on A and C phase OC CP555 Arcadia Park Tripped and reclosed Cause: PT2201 Cobah Sunny Ridge - Surge arrestor defective aftre lightning strike. Abnormal Switching:CP1233 Closed, CP13 Open, CP493 Closed, CP859 Open. See OMS 785102 785104 783597 783617 | February | 2012 | 2012Q3 | 2012 | ZN2400:PA18 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2012-02-12 | N | 70.3629 | N | 9 | N | N | 1.1101 | 39.4971 | 12751.9453
| ZN4545:PA19 | 893 | 1181.7976 | 40.2 | 1.3234 | 40.2 | 19657 | 10939 | 785115 | 2012-02-12 16:10 | 2012-02-12 20:55 | 285 | 11kV | 37905 | 133 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn2400 Berowra ex Pa18 Recloser CP3281 Tripped. Cause: Tree on HV mains in Bay Rd. Line workers removed tree. NOTE: DOp check the LV network and found 130Volts coming from eith LV parallel or customer Generator CP229 Cobah Rd Tripped on A and C phase OC Abnormal Switching:CP1233 Closed, CP13 Open, CP493 Closed, CP859 Open. | February | 2012 | 2012Q3 | 2012 | ZN2400:PA18 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2012-02-12 | N | 285 | N | 9 | N | N | 1.1101 | 39.4971 | 27699.856
| ZN4545:PA2 | 1909 | 1416.727 | 39.3 | 0.74213 | 39.3 | 19863 | 13407 | 783278 | 2012-02-11 15:03 | 2012-02-12 21:00 | 1797 | 11kV | 39522 | 76 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Berkeley Vale - Section of Pnl.24R - REC 47878 tripped / reclosed / locked out on timed O/C Tree branch on OH mains - P.T 12439 did not phase. Supply restored via L.V// @21:00 See OMS # 785004 785005 785006 | February | 2012 | 2012Q3 | 2012 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2012-02-11 | N | 520.0263 | N | 27 | Y | Y | 1.1101 | 39.4971 | 28881.5119
| ZN4545:PA21 | 843 | 599.6258 | 34.38 | 0.7113 | 34.38 | 19194 | 5584 | 783647 | 2012-02-12 17:31 | 2012-02-12 21:15 | 224 | 11kV | 2135 | 10 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | Ex Peats Ridge zone Pnl.4 - REC44995 Kulnura Tripped & reclosed on IOC @ 17:31 & 17:43 PT.12128 george Downs Greta - Centre phase 16A HV Drop Out fuse blown PT.11857 Collins George - Roadside Phase HV Drop Out fuse blown (16A) Lightning strike See OMS # 784145 784142 784144 784143 | February | 2012 | 2012Q3 | 2012 | ZN12630:PA4 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2012-02-12 | N | 213.5 | N | 9 | N | N | 1.1101 | 39.4971 | 1560.195
| ZN4545:PA24 | 539 | 318.0537 | 33.52 | 0.59008 | 33.52 | 19352 | 7649 | 783657 | 2012-02-12 16:10 | 2012-02-12 21:50 | 340 | 11kV | 4420 | 13 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | At PT1620 Crosslands End 200A fuses replaced on A and B phase of distributor 1. Cause: Fuses replaced after storm. See OMS784693 783657 783666 | February | 2012 | 2012Q3 | 2012 | ZN847:PA47 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2012-02-12 | N | 340 | N | 9 | N | N | 1.1101 | 39.4971 | 3230.0056
| ZN4545:PA25 | 1169 | 864.1585 | 35.25 | 0.73923 | 35.25 | 19435 | 8536 | 783652 | 2012-02-12 19:34 | 2012-02-12 22:50 | 196 | 11kV | 392 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 129537 A & B Phase DOLF : 10 Amp. Faulty Arrestors Excluded OMS 783652 OMS 784491 | February | 2012 | 2012Q3 | 2012 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2012-02-12 | N | 196 | N | 9 | N | N | 1.1101 | 39.4971 | 286.462
| ZN4545:PA26 | 1280 | 1363.973 | 45.03 | 1.0656 | 45.03 | 18657 | 745 | 783684 | 2012-02-12 23:26 | 2012-02-13 01:05 | 99 | 11kV | 172900 | 1880 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.36300 Balgowlah North, Panel 5 Fdr Cb tripped on A and C phase IOC, 11kV trip.Cause unknown | February | 2012 | 2012Q3 | 2012 | ZN15008:PA3 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Veg | 2012-02-12 | N | 91.9681 | N | 9 | N | N | 1.1101 | 39.4971 | 126350.2203
| ZN4545:PA27 | 905 | 680.7739 | 37.53 | 0.75224 | 37.53 | 18747 | 1568 | 783678 | 2012-02-12 22:35 | 2012-02-13 01:11 | 156.0667 | 11kV | 9750.9667 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129538 C Phase DOLF : 20 Amp. | February | 2012 | 2012Q3 | 2012 | 230:34051 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2012-02-12 | N | 125.0124 | N | 9 | N | N | 1.1101 | 39.4971 | 7125.7188
| ZN4545:PA28 | 1099 | 414.8267 | 33.99 | 0.37746 | 33.99 | 19997 | 14914 | 783670 | 2012-02-12 21:59 | 2012-02-13 01:50 | 231 | 11kV | 60879.65 | 1072 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.151012 Killarney, the 11kV Fdr CB tripped, reclosed and locked out on A and C phase OC, C phase IOC, sel, reclose, timing and lockout relays, 11kV trip. Bat on 11kV OH adjacent PT.15935 causing wires down | February | 2012 | 2012Q3 | 2012 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2012-02-12 | N | 56.7907 | N | 9 | N | N | 1.1101 | 39.4971 | 44489.0526
| ZN4545:PA29 | 1770 | 1166.2422 | 34.51 | 0.65889 | 34.51 | 19817 | 12942 | 783691 | 2012-02-13 02:56 | 2012-02-13 10:00 | 424 | 11kV | 13396 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Pnl.12 ex Wyong Zn: REC 45015 Brush Creek tripped / reclosed & locked out on IOC, O/C, E/F Tree brought down 11kV adjacent AB40893 See OMS # 784427 784428 784429 784430 | February | 2012 | 2012Q3 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-02-13 | N | 239.2143 | N | 14 | N | N | 1.1101 | 39.4971 | 9789.4017
| ZN4545:PA3 | 1679 | 1540.7056 | 40.73 | 0.91763 | 40.73 | 18676 | 920 | 783725 | 2012-02-13 08:15 | 2012-02-13 12:15 | 240 | 11kV | 240 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129541 A Phase DOLF : 10 Amp Excluded OMS 782725 OMS 784616 | February | 2012 | 2012Q3 | 2012 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2012-02-13 | N | 240 | N | 14 | N | N | 1.1101 | 39.4971 | 175.3849
| ZN4545:PA31 | 3055 | 2210.04 | 39.19 | 0.72342 | 39.19 | 20125 | 16138 | 783975 | 2012-02-13 12:54 | 2012-02-13 13:57 | 63 | 11kV | 177937 | 3373 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129540 1 fault operation System in abnormal status for SI 20629. excluded OMS 783978 & 783975 OMS 784555, 784559 LID 129540 1 fault operation System in abnormal status for SI 20629. excluded OMS 783978 & 783975 OMS 784555, 784559 | February | 2012 | 2012Q3 | 2012 | 243:80074 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2012-02-13 | N | 52.7533 | N | 14 | N | N | 1.1101 | 39.4971 | 130031.1113
| ZN4545:PA32 | 823 | 1460.3901 | 46.31 | 1.7745 | 46.31 | 18581 | 87 | 784229 | 2012-02-13 15:46 | 2012-02-13 16:40 | 54 | 11kV | 5724 | 106 | HV | Staff Operation | Utility Process Issue | Fuse | Unplanned | Unselected | N | LID 129543 B & C Phase fuses not closed correctly during SI20577 Excluded oms 784227,784229,784253 | February | 2012 | 2012Q3 | 2012 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Not Veg | 2012-02-13 | N | 54 | N | 14 | N | N | 1.1101 | 39.4971 | 4182.9304
| ZN4545:PA33 | 1368 | 805.5401 | #N/A | 0.58885 | 39.4971 | 19902 | 13755 | 784311 | 2012-02-13 18:22 | 2012-02-13 19:05 | 43 | 11kV | 559 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129553 3 Phase Overcurrent | February | 2012 | 2012Q3 | 2012 | 514:18141 | 514:18141 | ZN00514/018141 | SINGLETON | OH | Veg | 2012-02-13 | N | 43 | N | 14 | N | N | 1.1101 | 39.4971 | 408.5007
| ZN4545:PA35 | 1269 | 1170.4344 | 40.09 | 0.92233 | 40.09 | 20405 | 20182 | 784529 | 2012-02-13 13:19 | 2012-02-13 19:28 | 369 | 11kV | 46609 | 1229 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Unselected | N | At ZN.9245 Engadine P-8 "Numantia Copeland" fdr tripped, reclosed, and locked out on: RELAYS: A phase timed O/L, EFI and Lockout flag. SIGNALS: 11kV trip ZE, TX.1 GE FIELD EFIs: at S.9279, 9445, 9075, 9346, 9246, 9586, 9688, 9225 plus UGOH Princes Hwy nr Whitton, Garvan Rd nr Pattison. REMARKS: Lightning strike PT.9462 | February | 2012 | 2012Q3 | 2012 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2012-02-13 | N | 37.9243 | N | 14 | N | N | 1.1101 | 39.4971 | 34060.4825
| ZN4545:PA36 | 1310 | 854.9954 | 33.16 | 0.65267 | 33.16 | 19443 | 8583 | 784326 | 2012-02-13 19:31 | 2012-02-13 20:54 | 83 | 11kV | 1079 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129555 Single Phase DOLF : 5 Amp Excluded OMS 784326 | February | 2012 | 2012Q3 | 2012 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2012-02-13 | N | 83 | N | 14 | N | N | 1.1101 | 39.4971 | 788.5014
| ZN4545:PA39 | 113 | 289.6924 | #N/A | 2.5636 | 39.4971 | 20394 | 20055 | 784354 | 2012-02-13 20:34 | 2012-02-13 21:30 | 55.9667 | 11kV | 9794.1667 | 175 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 129557 A Phase DOLF : 40 Amp. excluded OMS 784358, 784360 | February | 2012 | 2012Q3 | 2012 | 240:34835 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Not Veg | 2012-02-13 | N | 55.9667 | N | 14 | N | N | 1.1101 | 39.4971 | 7157.2881
| ZN4545:PA4 | 1396 | 1225.657 | 35.06 | 0.87798 | 35.06 | 19920 | 14006 | 784325 | 2012-02-13 19:27 | 2012-02-13 21:49 | 142.55 | 11kV | 248.1 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | CC1: 22-"Refer to SOp" LID 129558 C Phase DOLF : 5 Amp. OMS 784339 | February | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2012-02-13 | N | 124.05 | N | 14 | N | N | 1.1101 | 39.4971 | 181.3042
| ZN4545:PA40 | 1889 | 1342.6986 | 31.75 | 0.7108 | 31.75 | 19414 | 8391 | 784344 | 2012-02-13 20:06 | 2012-02-13 22:20 | 134 | 11kV | 402 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129560 A Phase DOLF : 10 Amp Excluded OMS 784344 OMS 784634 | February | 2012 | 2012Q3 | 2012 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2012-02-13 | N | 134 | N | 14 | N | N | 1.1101 | 39.4971 | 293.7697
| ZN4545:PA41 | 1182 | 866.5122 | 38.39 | 0.73309 | 38.39 | 20039 | 15499 | 784329 | 2012-02-13 19:58 | 2012-02-13 22:51 | 172.8667 | 11kV | 7779 | 45 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | At S1847 Surada Ave 400A fuse blown on A and Cphase of distributor 3. O/S 45 Kallaroos tree brought down OH. See OMS 784341 784332 784336 784342 | February | 2012 | 2012Q3 | 2012 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2012-02-13 | N | 172.8667 | N | 14 | N | N | 1.1101 | 39.4971 | 5684.6638
| ZN4545:PA42 | 1403 | 735.8366 | 33.96 | 0.52447 | 33.96 | 20201 | 16956 | 784301 | 2012-02-13 17:38 | 2012-02-13 23:03 | 325 | 11kV | 64350 | 198 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129563 2 fault operations Earth fault excluded OMS 784301 OMS 784670 | February | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-02-13 | N | 325 | N | 14 | N | N | 1.1101 | 39.4971 | 47025.082
| ZN4545:PA44 | 1223 | 1613.5998 | 45.52 | 1.3194 | 45.52 | 20289 | 18548 | 784308 | 2012-02-13 18:10 | 2012-02-13 23:20 | 310 | 11kV | 44000 | 258 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129556 1 fault operation Sensitive Earth fault Excluded OMS 784662 OMS 789340 | February | 2012 | 2012Q3 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-02-13 | N | 170.5426 | N | 14 | N | N | 1.1101 | 39.4971 | 32153.9022
| ZN4545:PA6 | 757 | 1029.2946 | 45.05 | 1.3597 | 45.05 | 19143 | 4892 | 784328 | 2012-02-13 19:37 | 2012-02-14 01:15 | 338 | 11kV | 22380 | 118 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 129565 2 fault operations Sensitive earth fault. Excluded OMS 784328, 785134, 785137, 785139, 785141 OMS 789352, 789354, 789355, 789357 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-02-13 | N | 189.661 | N | 14 | N | N | 1.1101 | 39.4971 | 16354.6439
| ZN4545:PA9 | 38 | 1295.5567 | 40.52 | 34.0936 | 40.52 | 19031 | 4253 | 784372 | 2012-02-14 07:30 | 2012-02-14 09:50 | 140 | 11kV | 1820 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129569 B Phase DOLF : 10 Amp. Excluded OMS 784372 OMS 784981 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-14 | N | 140 | N | 13 | N | N | 1.1101 | 39.4971 | 1330.0023
| 233:82812 | 805 | 1033.8946 | 37.89 | 1.2843 | 37.89 | 19450 | 8699 | 784387 | 2012-02-14 09:00 | 2012-02-14 10:05 | 65 | 11kV | 195 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129570 C Phase DOLF : 10 Amp Excluded OMS 784387 OMS 785050 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-14 | N | 65 | N | 13 | N | N | 1.1101 | 39.4971 | 142.5002
| 233:82813 | 451 | 251.5353 | #N/A | 0.55773 | 39.4971 | 20220 | 17203 | 784399 | 2012-02-14 09:00 | 2012-02-14 11:00 | 120 | 11kV | 360 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129572 C Phase DOLF : 10 Amp. Excluded OMS 784399 (incorrect sub) OMS 785084 | February | 2012 | 2012Q3 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-02-14 | N | 120 | N | 13 | N | N | 1.1101 | 39.4971 | 263.0774
| 233:82815 | 1345 | 1025.9465 | 30.82 | 0.76279 | 30.82 | 19652 | 10872 | 784389 | 2012-02-14 07:30 | 2012-02-14 12:00 | 270 | 11kV | 810 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129574 A phase DOLF : 3 Amp 245 Volts Excluded OMS 784389 OMS 785008 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-14 | N | 270 | N | 13 | N | N | 1.1101 | 39.4971 | 591.9241
| 233:82818 | 33 | 79.2734 | 45.71 | 2.4022 | 45.71 | 20297 | 18838 | 784377 | 2012-02-14 07:30 | 2012-02-14 12:10 | 280 | 11kV | 560 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129573 3 phase DOLF : 3 Amp Excluded OMS 784377 OMS 784994 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-14 | N | 280 | N | 13 | N | N | 1.1101 | 39.4971 | 409.2315
| 233:82819 | 1266 | 825.8202 | 30.6 | 0.65231 | 30.6 | 20259 | 17954 | 784735 | 2012-02-14 15:15 | 2012-02-14 16:00 | 45.05 | 11kV | 495.55 | 11 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 129577 tree on mains at pole GW-10243 | February | 2012 | 2012Q3 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-02-14 | N | 45.05 | N | 13 | N | N | 1.1101 | 39.4971 | 362.1333
| 233:82821 | 268 | 188.7785 | 29.5 | 0.7044 | 29.5 | 18945 | 3449 | 784749 | 2012-02-14 16:00 | 2012-02-14 17:10 | 70 | 11kV | 3570 | 51 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 129578 mains low at pole KQ-60075 Excluded OMS 784739 OMS 784944 | February | 2012 | 2012Q3 | 2012 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2012-02-14 | N | 70 | N | 13 | N | N | 1.1101 | 39.4971 | 2608.8507
| ZN9900:PA1 | 1278 | 1450.8649 | 31.68 | 1.1353 | 31.68 | 18756 | 1668 | 784723 | 2012-02-14 15:04 | 2012-02-14 17:30 | 146 | 11kV | 146 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129581 A phase DOLF : 3 Amp Excluded OMS 784723 OMS 785092 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-14 | N | 146 | N | 13 | N | N | 1.1101 | 39.4971 | 106.6925
| ZN9900:PA10 | 431 | 702.1494 | 39.6 | 1.6291 | 39.6 | 20441 | 20428 | 784785 | 2012-02-14 16:17 | 2012-02-14 18:05 | 108 | 11kV | 13500 | 125 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129584 C Phase DOLF : 40 Amp Excluded OMS 784785, 784789, 784795 OMS 784968 | February | 2012 | 2012Q3 | 2012 | 501:48125 | 528:83024 | ZN00528/083024 | MAITLAND | OH | Not Veg | 2012-02-14 | N | 108 | N | 13 | N | N | 1.1101 | 39.4971 | 9865.4018
| ZN9900:PA12 | 1177 | 1253.7425 | 29.92 | 1.0652 | 29.92 | 19049 | 4362 | 784799 | 2012-02-14 16:39 | 2012-02-14 18:11 | 92 | 11kV | 130640 | 1420 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn4545 Meadowbank Panel 41 Tripped and locked out on IOC. Cause: Tree branch on 11kV OH Cnr Oak and Wishardt Rd. DOp removed tree and restored supply. See OMS 784952 784948 784954 784950 784799/810/809/815/836 | February | 2012 | 2012Q3 | 2012 | ZN4545:PA41 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Veg | 2012-02-14 | N | 92 | N | 13 | N | N | 1.1101 | 39.4971 | 95467.8588
| ZN9900:PA13 | 830 | 849.5588 | 32.1 | 1.0236 | 32.1 | 18603 | 265 | 784803 | 2012-02-14 17:00 | 2012-02-14 18:30 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129583 B Phase DOLF : 10 Amp Excluded OMS 784803 OMS 785097 | February | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-02-14 | N | 90 | N | 13 | N | N | 1.1101 | 39.4971 | 65.7693
| ZN9900:PA14 | 61 | 557.8879 | #N/A | 9.1457 | 39.4971 | 20397 | 20088 | 784817 | 2012-02-14 18:56 | 2012-02-14 19:32 | 36 | 11kV | 144 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129586 C Phase DOLF : 10 Amp. Excluded OMS 784877 OMS 785117 | February | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-02-14 | N | 36 | N | 13 | N | N | 1.1101 | 39.4971 | 105.231
| ZN9900:PA16 | 86 | 170.5759 | #N/A | 1.9834 | 39.4971 | 19105 | 4670 | 784857 | 2012-02-14 18:52 | 2012-02-14 20:35 | 103 | 11kV | 206 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129587 A Phase DOLF : 10 Amp Excluded OMS 784857 OMS 785106 | February | 2012 | 2012Q3 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2012-02-14 | N | 103 | N | 13 | N | N | 1.1101 | 39.4971 | 150.5387
| ZN9900:PA17 | 824 | 946.2407 | 30.06 | 1.1484 | 30.06 | 19364 | 7831 | 784889 | 2012-02-15 02:01 | 2012-02-15 04:44 | 163 | 11kV | 6846 | 42 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Rain Light | N | LID 129591 C Phase DOLF : 31 Amp Magpie across arrestor Excluded OMS 784889 OMS 784965 | February | 2012 | 2012Q3 | 2012 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Not Veg | 2012-02-15 | N | 163 | N | 5 | N | N | 1.1101 | 39.4971 | 5002.8549
| ZN9900:PA19 | 705 | 873.3545 | 34.21 | 1.2388 | 34.21 | 18845 | 2525 | 784898 | 2012-02-15 05:30 | 2012-02-15 07:00 | 90 | 11kV | 105606 | 1184 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | At S965 Pennant Hill Pa8. Tripped on unknown cause. Tele control advised of trip after work was carried out previous night on Scada System. TPE to investigate Panel 8 Relays due to no indication. 785422 785426 784898 | February | 2012 | 2012Q3 | 2012 | ZN965:PA8 | ZN965:PA8 | ZN00965/000008 | HORNSBY | UG | Not Veg | 2012-02-15 | N | 89.1943 | N | 5 | N | N | 1.1101 | 39.4971 | 77173.75
| ZN9900:PA2 | 664 | 868.2909 | 35.39 | 1.3077 | 35.39 | 18569 | 27 | 784891 | 2012-02-15 04:49 | 2012-02-15 07:12 | 143 | 11kV | 170885 | 1195 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 43 Tripped on SEL. Tree Branch on Mains below CP2888 | February | 2012 | 2012Q3 | 2012 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Veg | 2012-02-15 | N | 143 | N | 5 | N | N | 1.1101 | 39.4971 | 124877.7177
| ZN9900:PA20 | 722 | 727.7882 | 32.85 | 1.008 | 32.85 | 19329 | 7527 | 784914 | 2012-02-15 07:43 | 2012-02-15 10:45 | 182 | 11kV | 364 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129600 Single phase DOLF : 10 Amp Arrestors cut away under AP Excluded OMS 784914 OMS 785376 | February | 2012 | 2012Q3 | 2012 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2012-02-15 | N | 182 | N | 5 | N | N | 1.1101 | 39.4971 | 266.0005
| ZN9900:PA21 | 804 | 767.6339 | 29.92 | 0.95477 | 29.92 | 19266 | 6678 | 784971 | 2012-02-15 09:10 | 2012-02-15 12:44 | 214 | 11kV | 9202 | 43 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Ex Pa11 Zn711 Blackwattle Bay @S7511 Ada Pyrmont Bridge - 11kV No1 & No2 RMCB's tripped -No2 RMCB tripped on Low Gas -No1 RMCB tripped on Parrallel Tripping Remarks - Low SF6 Gas in No2 RMCB See 785696 exclude 784971 | February | 2012 | 2012Q3 | 2012 | ZN711:PA11 | ZN7481:PA17 | ZN07481/000017 | SYDNEY | Unknown | Not Veg | 2012-02-15 | N | 214 | N | 5 | N | N | 1.1101 | 39.4971 | 6724.5502
| ZN9900:PA3 | 888 | 874.0615 | 29.31 | 0.9843 | 29.31 | 19356 | 7717 | 785517 | 2012-02-16 10:00 | 2012-02-16 13:35 | 215 | 11kV | 215 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129616 C Phase DOLF : 16 Amp | February | 2012 | 2012Q3 | 2012 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2012-02-16 | N | 215 | N | 3 | N | N | 1.1101 | 39.4971 | 157.1157
| ZN9900:PA5 | 464 | 472.4325 | 29.94 | 1.0182 | 29.94 | 18986 | 3875 | 785666 | 2012-02-16 15:44 | 2012-02-16 18:56 | 191.9667 | 11kV | 6012.7333 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129617 C Phase DOLF : 40 Amp. Volts 243; 240 Amps 80; 80. Excluded OMS 785675 OMS 785666 | February | 2012 | 2012Q3 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2012-02-16 | N | 77.0863 | N | 3 | N | N | 1.1101 | 39.4971 | 4393.9282
| ZN9900:PA6 | 723 | 770.6494 | 29.87 | 1.0659 | 29.87 | 18771 | 1885 | 786846 | 2012-02-16 20:42 | 2012-02-16 22:26 | 104 | 11kV | 84084 | 948 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 Meadowbank Panel 7 tripped reclosed tripped and loced out Earth fault, EFI, iming, Lockout and fault check. Signals: 11kV Trip, Zone Earth, Tx2 Group earth. Cause: Cable fault from S5305 Phillip Princes to LB2382 to S129. See OMS 786848 786486 785773 | February | 2012 | 2012Q3 | 2012 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | UG | Not Veg | 2012-02-16 | N | 88.6962 | N | 3 | N | N | 1.1101 | 39.4971 | 61446.1071
| ZN9900:PA8 | 968 | 1129.433 | 35.54 | 1.1668 | 35.54 | 19410 | 8382 | 785782 | 2012-02-17 00:23 | 2012-02-17 01:47 | 84 | 11kV | 165494 | 2084 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.7 tripped on A & C phase O/C Cause not ascertained - possible tree branch contact See OMS # 785805 785806 785807 | February | 2012 | 2012Q3 | 2012 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Veg | 2012-02-17 | N | 79.4117 | N | 7 | N | N | 1.1101 | 39.4971 | 120938.134
| ZN9900:PA9 | 376 | 574.0828 | #N/A | 1.5268 | 39.4971 | 19030 | 4249 | 785787 | 2012-02-17 02:24 | 2012-02-17 03:15 | 51 | 11kV | 82926 | 1626 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | At ZN.9245 Engadine P-4 "AB 35536 etc" Fdr tripped & reclosed on: RELAYS: A phase IOC and Timed O/C, Reclosing relay, Timing relay, Lockout relay FIELD EFI's: UGOH REMARKS: possum in contat with 11kV on PT.9734 Warilda Appin. | February | 2012 | 2012Q3 | 2012 | ZN9245:PA4 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2012-02-17 | N | 51 | N | 7 | N | N | 1.1101 | 39.4971 | 60599.8749
| 810:74050 | 140 | 173.6128 | 39.83 | 1.2401 | 39.83 | 20166 | 16460 | 785827 | 2012-02-17 08:43 | 2012-02-17 11:40 | 177 | 11kV | 1770 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129632 C Phase DOLF : 10 Amp. Fuse carrier was burnt up. Excluded OMS (heirarchy) 785827 & 785874 OMS 787191 | February | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-02-17 | N | 177 | N | 7 | N | N | 1.1101 | 39.4971 | 1293.4638
| 810:74054 | 323 | 261.053 | 34.34 | 0.80821 | 34.34 | 20295 | 18784 | 785922 | 2012-02-17 11:00 | 2012-02-17 11:50 | 50 | 11kV | 140 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129630 C Phase DOLF : 10 Amp. Faulty arrestor blew fuse at both sub and line fuse. Excluded OMS 785922 OMS 787205; 787212 | February | 2012 | 2012Q3 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2012-02-17 | N | 12.7273 | N | 7 | N | N | 1.1101 | 39.4971 | 102.3079
| 810:74058 | 203 | 132.0632 | 29.2 | 0.65056 | 29.2 | 20286 | 18439 | 786961 | 2012-02-17 12:59 | 2012-02-17 15:55 | 176 | 11kV | 681 | 331 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 129634 Trip & Reclse 1 fault operation Earth fault, Overcurrent Line DOLF : 63Amp. A PHASE 2506AMPS, B PHASE 2453 AMPS, C PHASE 1006 AMPS, EARTHS FAULT 383 AMPS Found cable fault to sub 52345 & blown LF 41540. Sub 52345 interconnected & 11kV taps broken P. FS-93227, TAP issued. | February | 2012 | 2012Q3 | 2012 | 504:48032 | 522:83121 | ZN00522/083121 | CESSNOCK | UG | Not Veg | 2012-02-17 | N | 2.0574 | N | 7 | N | N | 1.1101 | 39.4971 | 497.6547
| 810:74062 | 593 | 551.4795 | 39.02 | 0.92998 | 39.02 | 19602 | 10088 | 786944 | 2012-02-17 13:56 | 2012-02-17 17:20 | 204 | 11kV | 80304 | 648 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S1193 Lindfield Panel 10 tripped and reclosed on Cause: Tree branch brought down 11kV at corner Tryon Rd and Robinson St East Lindfield. HV contacted LV distributor see OMS 786944 786947 786000 | February | 2012 | 2012Q3 | 2012 | ZN1193:PA10 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Veg | 2012-02-17 | N | 123.9259 | N | 7 | N | N | 1.1101 | 39.4971 | 58683.7946
| 532:83293 | 995 | 740.6817 | 35.2 | 0.7444 | 35.2 | 19142 | 4891 | 786092 | 2012-02-17 16:57 | 2012-02-17 18:47 | 109.6 | 11kV | 38973.55 | 523 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN.1648 Enfield P-10 "Sub Hill Hume" Fdr tripped on: RELAYS: B phase timed O/C, and EFI SIGNALS: 11kV trip, Zone Earth and TX.1 GE REMARKS: UG Fault. Suspected UG between S.35721 and S.36054 | February | 2012 | 2012Q3 | 2012 | ZN1648:PA10 | ZN4853:PA12 | ZN04853/000012 | STRATHFIELD | UG | Not Veg | 2012-02-17 | N | 74.5192 | N | 7 | N | N | 1.1101 | 39.4971 | 28480.7208
| 532:83295 | 654 | 747.8499 | 35.35 | 1.1435 | 35.35 | 19350 | 7640 | 786146 | 2012-02-18 02:24 | 2012-02-18 04:30 | 126 | 11kV | 15246 | 121 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129638 B Phase DOLF : 40 Amp Possum at sub Excluded OMS 786146, 786148 OMS 786708 | February | 2012 | 2012Q3 | 2012 | 230:34047 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2012-02-18 | N | 126 | N | 7 | N | N | 1.1101 | 39.4971 | 11141.3271
| 532:83298 | 1326 | 1189.3807 | 41.44 | 0.89697 | 41.44 | 20108 | 16043 | 786159 | 2012-02-18 08:20 | 2012-02-18 10:10 | 110 | 11kV | 880 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | PT.12383 Patterson Wattle Tree - Road Side HDO operated (16A) Tree brnach reported to have fallen on mains next to PT. No damage to PT | February | 2012 | 2012Q3 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2012-02-18 | N | 110 | N | 7 | N | N | 1.1101 | 39.4971 | 643.078
| 532:83300 | 1008 | 575.3326 | 29.41 | 0.57077 | 29.41 | 18693 | 1082 | 786304 | 2012-02-18 19:42 | 2012-02-18 21:00 | 77.6833 | 11kV | 1864.4 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129663 3 phase DOLF : 16 Amp | February | 2012 | 2012Q3 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-02-18 | N | 77.6833 | N | 7 | N | N | 1.1101 | 39.4971 | 1362.4485
| 532:83301 | 2264 | 2026.4437 | 42.39 | 0.89507 | 42.39 | 18922 | 3284 | 786303 | 2012-02-18 19:33 | 2012-02-18 22:30 | 177 | 11kV | 531 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129665 Single phase DOLF : 5 Amp. Excluded OMS 786303 | February | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-02-18 | N | 177 | N | 7 | N | N | 1.1101 | 39.4971 | 388.0391
| 532:83302 | 13 | 705.0265 | #N/A | 54.2328 | 39.4971 | 20358 | 19846 | 786294 | 2012-02-18 18:54 | 2012-02-18 22:35 | 221.3 | 11kV | 2876.9 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129666 C Phase DOLF : 10 Amp | February | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-02-18 | N | 221.3 | N | 7 | N | N | 1.1101 | 39.4971 | 2102.3537
| 532:83306 | 15 | 1117.4982 | #N/A | 74.4999 | 39.4971 | 18804 | 2181 | 786297 | 2012-02-18 19:05 | 2012-02-19 00:30 | 324.8667 | 11kV | 722.7167 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129670 Single phase DOLF : 10 Amp. OMS 786325 | February | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-02-18 | N | 240.9056 | N | 7 | N | N | 1.1101 | 39.4971 | 528.14
| 532:83307 | 1217 | 690.8447 | 30.64 | 0.56766 | 30.64 | 19662 | 11030 | 787511 | 2012-02-18 23:30 | 2012-02-19 01:30 | 120 | 11kV | 1080 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129673 A Phase DOLF : 16 Amp | February | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-02-18 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 789.2321
| 532:83309 | 2131 | 1546.109 | 37.78 | 0.72553 | 37.78 | 19723 | 12011 | 786341 | 2012-02-19 01:31 | 2012-02-19 02:04 | 33 | 11kV | 52371 | 1587 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 129675 2 fault operations Earth fault Possum at UGOH pole IV-31828 to James St sub. Inspection required. Excluded OMS 786341. OMS 786738 | February | 2012 | 2012Q3 | 2012 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2012-02-19 | N | 33 | N | 20 | Y | Y | 1.1101 | 39.4971 | 38271.1821
| 532:83312 | 439 | 859.0643 | #N/A | 1.9569 | 39.4971 | 19795 | 12773 | 786351 | 2012-02-19 07:57 | 2012-02-19 09:39 | 102 | 11kV | 136936 | 1516 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S187 Crows Nest Panel 17 tripped on: A B and C phase IOC, Earth Fault, FEFI, Fault Check. Signals: 11kV Trip, Zone Earth and No23 Group Earth Cause: 11kV UG fault from S1391 Amherst St to S4726 Cairo Carter to S8545 Amherest Miller. See OMS 787117 787120 786351 786352 | February | 2012 | 2012Q3 | 2012 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2012-02-19 | N | 90.3272 | N | 20 | Y | Y | 1.1101 | 39.4971 | 100068.7899
| 532:83314 | 1873 | 1163.3695 | 33.87 | 0.62113 | 33.87 | 20244 | 17606 | 786349 | 2012-02-19 07:57 | 2012-02-19 12:15 | 258 | 11kV | 258 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 129680 Single phase DOLF : 10 Amp. SUB ISOLATED TO REPLACE LA'S REPLACED 2 X HV FUSES VOLTS 242 Excluded OMS 786349 (customer has multiple NMI's) OMS 787561 | February | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-02-19 | N | 258 | N | 20 | Y | Y | 1.1101 | 39.4971 | 188.5388
| ZN2196:PA1 | 12 | 179.5135 | #N/A | 14.9595 | 39.4971 | 19359 | 7776 | 786346 | 2012-02-19 07:49 | 2012-02-19 13:40 | 351 | 11kV | 1635 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129686 DOLF : 10 Amp Replaced HV L/As + sevice fuse on private pole. Advised cust refer to elect contractor Excluded OMS 786346, 787545 OMS 797190 | February | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2012-02-19 | N | 327 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1194.8098
| ZN2196:PA10 | 37 | 486.8554 | 43.74 | 13.1583 | 43.74 | 19075 | 4474 | 786376 | 2012-02-19 08:30 | 2012-02-19 14:10 | 340 | 11kV | 8160 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129681 Single phase DOLF : 10 Amp. REPLACED 2 X HV FUSES AND 2 X 80 AMP LV FUSES Excluded OMS 786376, 792195 See OMS 797207 | February | 2012 | 2012Q3 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-02-19 | N | 340 | N | 20 | Y | Y | 1.1101 | 39.4971 | 5963.0873
| ZN2196:PA11 | 123 | 1001.7685 | 62.66 | 8.1445 | 62.66 | 19564 | 9648 | 786419 | 2012-02-19 14:56 | 2012-02-19 16:17 | 81 | 11kV | 3481 | 69 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At Zn 1290 Leightonfield 11kv feeder panel No9 "Christina Birmingham etc" feeder tripped on: Relays: timed E/F, EFI Field EFIs: S664, S5764, S5923, S3119, S1288 Remarks: 11kv UGOH within section of 11Kv feeder from SWB @ S1288 Marple Biloela to AB189 to SWA @ CP311 Marple Telecom Related jobs: #786815, 786810, 786419, 786421 | February | 2012 | 2012Q3 | 2012 | ZN1290:PA9 | ZN1290:PA9 | ZN01290/000009 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2012-02-19 | N | 50.4493 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2543.8121
| ZN2196:PA12 | 12 | 1114.2757 | 63.02 | 92.8563 | 63.02 | 19617 | 10374 | 786380 | 2012-02-19 10:20 | 2012-02-19 18:30 | 490 | 11kV | 980 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129691 A & C Phase DOLF : 10 Amp. Excluded OMS 786380 OMS 787626 | February | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-02-19 | N | 490 | N | 20 | Y | Y | 1.1101 | 39.4971 | 716.1551
| ZN2196:PA13 | 32 | 292.6153 | 61.19 | 9.1442 | 61.19 | 20250 | 17756 | 786345 | 2012-02-19 07:32 | 2012-02-19 22:40 | 908 | 11kV | 11596 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 129684 4 fault operations L/F blown (10A) before 15A Ragcb Sw 74821. Changed L/F to 20A faulty Tx sub 70357 - isolate & A/P to replace Tx Excluded OMS 786345 & 786442 OMS 787531 & 787533 | February | 2012 | 2012Q3 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-02-19 | N | 682.1176 | N | 20 | Y | Y | 1.1101 | 39.4971 | 8474.0148
| ZN2196:PA14 | 131 | 638.7705 | 56.08 | 4.8761 | 56.08 | 19877 | 13566 | 786471 | 2012-02-19 21:08 | 2012-02-19 23:25 | 137 | 11kV | 212329 | 1639 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | At ZN.9037 Miranda P-8 "Alkaringa Rd" fdr tripped & reclosed, tripped and locked out on. RELAYS: A & C phase inst, EF, Lockout, Timing FIELD EFIs: S.9521 REMARKS: Lightning / Surge Arrestor. Severe lightning at time of P-8 locking out, P-16 tripped and reclosed at same time. UGOH damaged by lightning below S.9521. | February | 2012 | 2012Q3 | 2012 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2012-02-19 | N | 129.5479 | N | 20 | Y | Y | 1.1101 | 39.4971 | 155163.7706
| ZN2196:PA17 | 98 | 1090.7478 | 56.58 | 11.1301 | 56.58 | 18564 | 6 | 786515 | 2012-02-19 22:19 | 2012-02-20 00:10 | 111 | 11kV | 103608 | 1098 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S129 Hunters Hill panel 9 tripped on Relays: A and C phase O/C with EFI. Cause not ascertained for outage | February | 2012 | 2012Q3 | 2012 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2012-02-19 | N | 94.3607 | N | 20 | Y | Y | 1.1101 | 39.4971 | 75713.6705
| ZN2196:PA18 | 1783 | 1671.703 | 44.19 | 0.93758 | 44.19 | 19202 | 5812 | 786536 | 2012-02-19 22:33 | 2012-02-20 00:45 | 132 | 11kV | 147950 | 1595 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At S.15002 Narrabeen, Panel 6 Fdr CB tripped on A and C phase timed OC, efi, 11kV trip, zone earth, Fdr UV change over. Field efi's down at S.16441 and S.16903. At S.15002 Narrabeen, Panel 6 Fdr CB tripped on A and C phase timed OC, efi, 11kV trip, zone earth, Fdr UV change over. Field efi's down at S.16441 and S.16903. | February | 2012 | 2012Q3 | 2012 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Veg | 2012-02-19 | N | 92.7586 | N | 20 | Y | Y | 1.1101 | 39.4971 | 108117.4962
| ZN2196:PA19 | 13 | 12.4207 | #N/A | 0.95544 | 39.4971 | 19409 | 8380 | 786492 | 2012-02-19 21:56 | 2012-02-20 00:57 | 181 | 11kV | 463304 | 3344 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Zn.15006 Dee Why West Pnl.2 tripped on Overcurrent & earth Fault, C phase IOC. Field EFI @ S.16618 Abnormal Switching: SwA @ S.16618 CLOSED - LK 23749 OPEN - PT15398 isolated in LV // Surge arrestor has blown on UGOH between LK24253, S.15777 in right of way near 93 cumberland Av, Collaroy See OMS # 788053 788055 | February | 2012 | 2012Q3 | 2012 | ZN15006:PA2 | ZN15006:PA2 | ZN15006/000002 | NORTHERN BEACHES | OH | Not Veg | 2012-02-19 | N | 138.5478 | N | 20 | Y | Y | 1.1101 | 39.4971 | 338568.898
| ZN2196:PA2 | 759 | 1240.4907 | 37.24 | 1.6344 | 37.24 | 20340 | 19419 | 786541 | 2012-02-19 23:11 | 2012-02-20 01:03 | 112 | 11kV | 18928 | 169 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | Zn12580 Erina Pnl.7 tripped on A & C Phase IOC, C phase Timed OC, EFI Lightning strike | February | 2012 | 2012Q3 | 2012 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | OH | Not Veg | 2012-02-19 | N | 112 | N | 20 | Y | Y | 1.1101 | 39.4971 | 13832.0241
| ZN2196:PA20 | 101 | 190.4654 | 62.01 | 1.8858 | 62.01 | 19310 | 7355 | 786511 | 2012-02-19 22:26 | 2012-02-20 02:15 | 229 | 11kV | 615323 | 2687 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn.15006 Dee Why West Pnl.9 tripped on Overcurrent Spaj No.4, Fault Check & EFI Field EFis: S.16792 17031 16733 16734 Lightning - mains to patrol section of OH from 12-20 Westmoreland Ave Collaroy | February | 2012 | 2012Q3 | 2012 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | OH | Veg | 2012-02-19 | N | 229 | N | 20 | Y | Y | 1.1101 | 39.4971 | 449659.8994
| ZN2196:PA21 | 784 | 528.3637 | 33.8 | 0.67393 | 33.8 | 20024 | 15262 | 786508 | 2012-02-19 22:14 | 2012-02-20 02:15 | 241 | 11kV | 271222 | 1324 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At S2635 Epping Panel 21 Tripped Reclosed Tripped and locked out on A and B phase O/C, lockout, Timing, EFI and Fault Check. Cause: Light arrestor failed. See OMS 787204 787207 787206 | February | 2012 | 2012Q3 | 2012 | ZN2635:PA21 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Not Veg | 2012-02-19 | N | 204.8505 | N | 20 | Y | Y | 1.1101 | 39.4971 | 198201.0379
| ZN2196:PA22 | 25 | 512.4691 | #N/A | 20.4988 | 39.4971 | 19644 | 10702 | 786588 | 2012-02-20 00:57 | 2012-02-20 02:33 | 96 | 11kV | 139200 | 1450 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 129706 2 fault operations B Phase Earth fault 33kv earth wire burnt off & hit 11kv at pole IR-70386 Excluded OMS 786588; 786589; 786590; 786591 OMS 787080 | February | 2012 | 2012Q3 | 2012 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | OH | Not Veg | 2012-02-20 | N | 96 | N | 26 | Y | Y | 1.1101 | 39.4971 | 101723.2543
| ZN2196:PA25 | 1377 | 1342.5556 | 37.06 | 0.97499 | 37.06 | 20238 | 17464 | 786534 | 2012-02-19 22:33 | 2012-02-20 02:47 | 254 | 11kV | 272547 | 1075 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | At S.15014 Mona Vale; Panel 7 Fdr CB tripped on A and B phase OC, fault check, efi, 11kV trip | February | 2012 | 2012Q3 | 2012 | ZN15014:PA7 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | OH | Veg | 2012-02-19 | N | 253.5321 | N | 20 | Y | Y | 1.1101 | 39.4971 | 199169.3088
| ZN2196:PA26 | 748 | 1365.8127 | 46.72 | 1.826 | 46.72 | 18669 | 868 | 786527 | 2012-02-19 22:33 | 2012-02-20 02:55 | 262 | 11kV | 184952 | 854 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | At S.15014 Mona Vale; Panel 22 Fdr CB tripped OC, fault check, efi, 11kV trip. AB.20303 had bond burnt off on the roadside outgoing side | February | 2012 | 2012Q3 | 2012 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Not Veg | 2012-02-19 | N | 216.5714 | N | 20 | Y | Y | 1.1101 | 39.4971 | 135157.4664
| ZN2196:PA28 | 146 | 1296.7129 | #N/A | 8.8816 | 39.4971 | 20183 | 16733 | 786382 | 2012-02-19 23:49 | 2012-02-20 04:10 | 261 | 11kV | 310851 | 1191 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | IR 2935 Somerville Pike Tripped reclosed and locked out Cause: Tree branch on OH mains O/S 14 Somberville Rd Hornsby Heighs, treee branch removed by DOp. | February | 2012 | 2012Q3 | 2012 | ZN847:PA22 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Veg | 2012-02-19 | N | 261 | N | 20 | Y | Y | 1.1101 | 39.4971 | 227160.7422
| ZN2196:PA3 | 602 | 557.5045 | 39.07 | 0.92609 | 39.07 | 19763 | 12472 | 786533 | 2012-02-19 22:15 | 2012-02-20 05:00 | 405 | 11kV | 179259 | 743 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S3425 Castle Cove panel 28 tripped reclosed tripped and locked out on B and C phase Timed O/, Lockout, Timing Relay, EFI and SEF. Cause: 11kV on ground O/S 22 Willowie Rd Castle Cove - 11kV UGOH between AB2852 and S1723 is Damaged. See OMS 788451 788453 788452 | February | 2012 | 2012Q3 | 2012 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | Unknown | Unknown | 2012-02-19 | N | 241.2638 | N | 20 | Y | Y | 1.1101 | 39.4971 | 130997.19
| ZN2196:PA4 | 43 | 545.756 | #N/A | 12.692 | 39.4971 | 19251 | 6533 | 786621 | 2012-02-20 03:19 | 2012-02-20 06:00 | 161 | 11kV | 3864 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129719 C Phase DOLF : 16 Amp Excluded OMS 786621 & 786624 OMS 787673 | February | 2012 | 2012Q3 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-02-20 | N | 161 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2823.6972
| ZN2196:PA5 | 1692 | 1623.618 | 35.33 | 0.95959 | 35.33 | 19806 | 12857 | 786626 | 2012-02-20 03:39 | 2012-02-20 07:00 | 201 | 11kV | 2170 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129721 B & C Phase DOLF : 10 Amp Excluded OMS 786626 | February | 2012 | 2012Q3 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2012-02-20 | N | 144.6667 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1585.772
| ZN2196:PA6 | 62 | 439.2371 | 63.67 | 7.0845 | 63.67 | 20356 | 19830 | 786656 | 2012-02-20 06:32 | 2012-02-20 08:10 | 98 | 11kV | 4802 | 49 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | PT14371 Red Cedar Shirley - Road Side HDO replaced 40K Lightning stormat time of interruption Lightning Arrestor blown - restored via LV // | February | 2012 | 2012Q3 | 2012 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2012-02-20 | N | 98 | N | 26 | Y | Y | 1.1101 | 39.4971 | 3509.16
| ZN2196:PA9 | 974 | 790.2927 | 38.88 | 0.81139 | 38.88 | 19355 | 7715 | 786627 | 2012-02-20 03:41 | 2012-02-20 09:15 | 334 | 11kV | 1002 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129725 A & B Phase DOLF : 10 Amp noticed dolf down when attending oms job 786627 Excluded OMS 788239, OMS 788246 | February | 2012 | 2012Q3 | 2012 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2012-02-20 | N | 334 | N | 26 | Y | Y | 1.1101 | 39.4971 | 732.232
| ZN9037:PA10 | 1532 | 1303.6664 | 37.22 | 0.85096 | 37.22 | 19331 | 7542 | 786642 | 2012-02-20 05:45 | 2012-02-20 10:21 | 276.15 | 11kV | 7732.2 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129735 A Phase DOLF : | February | 2012 | 2012Q3 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2012-02-20 | N | 276.15 | N | 26 | Y | Y | 1.1101 | 39.4971 | 5650.4637
| ZN9037:PA14 | 475 | 886.9704 | 45.79 | 1.8673 | 45.79 | 20302 | 18973 | 786734 | 2012-02-20 08:05 | 2012-02-20 10:45 | 160 | 11kV | 3840 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129734 A Phase DOLF : 16 Amp | February | 2012 | 2012Q3 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-02-20 | N | 160 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2806.1587
| ZN9037:PA15 | 429 | 1311.2306 | 40.52 | 3.0565 | 40.52 | 18900 | 3117 | 786797 | 2012-02-20 07:41 | 2012-02-20 11:00 | 199 | 11kV | 1791 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129745 A Phase DOLF : 16 Amp. Excluded OMS786797 OMS 788335 | February | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-02-20 | N | 199 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1308.81
| ZN9037:PA16 | 1376 | 1144.5294 | 34.78 | 0.83178 | 34.78 | 18697 | 1130 | 786648 | 2012-02-20 06:00 | 2012-02-20 11:00 | 300 | 11kV | 600 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 129737 SAingle Phase DOLF Sub isolated to replace LA's | February | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2012-02-20 | N | 300 | N | 26 | Y | Y | 1.1101 | 39.4971 | 438.4623
| ZN9037:PA17 | 35 | 1285.5851 | #N/A | 36.731 | 39.4971 | 18644 | 714 | 786606 | 2012-02-20 01:55 | 2012-02-20 11:30 | 575 | 11kV | 35788 | 387 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 129717 1 fault operation Sensitive Earth Fault Defective sub 27616 Excluded OMS 786606, 786608, 786612, 786614, 786709, 786710 786715 OMS 787741, 787742, 787743, 787744, 787745, 787746, 787747, 787748 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-02-20 | N | 92.4755 | N | 26 | Y | Y | 1.1101 | 39.4971 | 26152.8148
| ZN9037:PA2 | 1084 | 1216.1324 | 34.31 | 1.1219 | 34.31 | 18610 | 291 | 786866 | 2012-02-20 06:00 | 2012-02-20 11:30 | 330 | 11kV | 660 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129747 A Phase DOLF : 16 Amp | February | 2012 | 2012Q3 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2012-02-20 | N | 330 | N | 26 | Y | Y | 1.1101 | 39.4971 | 482.3085
| ZN9037:PA3 | 121 | 738.8833 | 39.55 | 6.1065 | 39.55 | 19027 | 4228 | 786928 | 2012-02-20 10:17 | 2012-02-20 11:50 | 93 | 11kV | 55017 | 982 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | LID 129744 2 fault operations Earth fault Magpie on UGOH at ole JU-26938 Wallace St. repairs arranged Excluded oms 786747, 786928, 786931, 786935, 786936, 786937, 786938, 786943, 786968. OMS 788038, 788039 | February | 2012 | 2012Q3 | 2012 | 208:58 | 257:81987 | ZN00257/081987 | NEWCASTLE | OH | Not Veg | 2012-02-20 | N | 56.0255 | N | 26 | Y | Y | 1.1101 | 39.4971 | 40204.8009
| ZN9037:PA4 | 476 | 1162.4497 | 38.54 | 2.4421 | 38.54 | 19064 | 4429 | 786762 | 2012-02-20 05:00 | 2012-02-20 12:10 | 430 | 11kV | 430 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129738 C Phase DOLF : 10 Amp Excluded OMS 786762 OMS 788269 | February | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-02-20 | N | 430 | N | 26 | Y | Y | 1.1101 | 39.4971 | 314.2313
| ZN9037:PA7 | 670 | 1167.3218 | 37.14 | 1.7423 | 37.14 | 19906 | 13807 | 786761 | 2012-02-20 08:25 | 2012-02-20 12:30 | 245 | 11kV | 245 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129740 Volts - 240 Excluded OMS 786761 OMS 788193 | February | 2012 | 2012Q3 | 2012 | 235:2124 | 235:2124 | ZN00235/002124 | NEWCASTLE | OH | Veg | 2012-02-20 | N | 245 | N | 26 | Y | Y | 1.1101 | 39.4971 | 179.0388
| ZN9037:PA8 | 1760 | 1588.6156 | 31.25 | 0.90262 | 31.25 | 19480 | 8945 | 787124 | 2012-02-20 13:35 | 2012-02-20 14:50 | 75 | 11kV | 2250 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Section of 11KV feeder from AB 26204 to AB 20129 interupted Ex S.15013 Terrey Hills Zone, Panel 10 'Terrey Hills' feeder Interupted by Dop for urgent repairs to USL 21880, found by linesman after patrolling trip & reclosed during lightning storm previoous night | February | 2012 | 2012Q3 | 2012 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2012-02-20 | N | 75 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1644.2336
| ZN9037:PA9 | 861 | 835.5773 | 31.74 | 0.97047 | 31.74 | 20187 | 16783 | 786517 | 2012-02-19 22:24 | 2012-02-20 15:00 | 996 | 11kV | 167767 | 555 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | Section of 11kV Feeder CP554 Arcadia Rosscommon Tripped and locked out. Abnormal Switching: CP1233 Closed, AB13 Open, LB493 Closed LB859. Cause: Tree brought down 11kV and LV OH O/S 11Greenlands Rd Arcadia. See OMS 788426 788435 788434 788433. See OMS 786517/529/530/558/562/565/566 | February | 2012 | 2012Q3 | 2012 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2012-02-19 | N | 302.2829 | N | 20 | Y | Y | 1.1101 | 39.4971 | 122599.1753
| 812:19065 | 144 | 687.637 | 53.58 | 4.7753 | 53.58 | 18825 | 2325 | 787114 | 2012-02-20 13:10 | 2012-02-20 15:00 | 110 | 11kV | 1980 | 18 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Previous Storm | N | LID 129754 interupted to make emergency repair to sub 51909 see # 129753 (OMS 787114) | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-02-20 | N | 110 | N | 26 | Y | Y | 1.1101 | 39.4971 | 1446.9256
| 812:19066 | 867 | 702.5789 | 23.83 | 0.81036 | 23.83 | 19365 | 7858 | 786780 | 2012-02-20 08:39 | 2012-02-20 15:58 | 439 | 11kV | 878 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 129760 3 Phase DOLF Transformer replaced Excluded OMS786780 OMS 788343 | February | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-02-20 | N | 439 | N | 26 | Y | Y | 1.1101 | 39.4971 | 641.6165
| 812:19071 | 1219 | 1097.3348 | 27.19 | 0.90019 | 27.19 | 20194 | 16883 | 786616 | 2012-02-20 02:42 | 2012-02-20 18:30 | 948 | 11kV | 20698 | 116 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | Ex Pnl.1 West Gosford Zn REC 44602 Ourimbah Creek Rd - tripped, reclosed and locked out on O/C and SEF Lightning See OMS # 787426 787427 | February | 2012 | 2012Q3 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-02-20 | N | 178.431 | N | 26 | Y | Y | 1.1101 | 39.4971 | 15125.4879
| 812:19072 | 201 | 380.8605 | 52.55 | 1.8948 | 52.55 | 18734 | 1407 | 786741 | 2012-02-20 08:04 | 2012-02-20 19:00 | 656 | 11kV | 123547 | 1875 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 129741 2 fault operations Earth Fualt Bus hit sub pole 1919. Pole down. Excluded oms 786741, 786747, 786767, 786839, 787010. OMS 787831, 787832, 787834 | February | 2012 | 2012Q3 | 2012 | 232:33413 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2012-02-20 | N | 65.8917 | N | 26 | Y | Y | 1.1101 | 39.4971 | 90284.5036
| 520:48172 | 474 | 345.9509 | 23.97 | 0.72985 | 23.97 | 19093 | 4593 | 787311 | 2012-02-20 17:03 | 2012-02-20 19:32 | 149 | 11kV | 149 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129763 A Phase DOLF : 10 Amp Excluded OMS 787311 OMS 788404 | February | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-02-20 | N | 149 | N | 26 | Y | Y | 1.1101 | 39.4971 | 108.8848
| ZN15014:PA10 | 1846 | 1926.3122 | 32.24 | 1.0435 | 32.24 | 20098 | 15953 | 787345 | 2012-02-20 19:17 | 2012-02-20 20:29 | 71.9333 | 11kV | 1222.8667 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129764 B Phase DOLF : 20 Amp | February | 2012 | 2012Q3 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2012-02-20 | N | 71.9333 | N | 26 | Y | Y | 1.1101 | 39.4971 | 893.6349
| ZN15014:PA11 | 402 | 765.2459 | 52.37 | 1.9036 | 52.37 | 19506 | 9110 | 787328 | 2012-02-20 18:09 | 2012-02-20 20:50 | 161 | 11kV | 161 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129766 single phase DOLF : 10 Amp Excluded OMS 787328 OMS 788413 | February | 2012 | 2012Q3 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-02-20 | N | 161 | N | 26 | Y | Y | 1.1101 | 39.4971 | 117.6541
| ZN15014:PA14 | 897 | 1453.5636 | 48.46 | 1.6205 | 48.46 | 19398 | 8310 | 787377 | 2012-02-20 22:32 | 2012-02-20 23:45 | 73 | 11kV | 91646 | 1710 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9118 Cronulla P-6 "S.9508 Croydon Kingsway" fdr tripped on: RELAYS: Earth Fault, Sealing Contactor, & EFI SIGNALS: 11kV trip, Zn Earth, TX.1 Grp Eth FIELD EFIs: S.9509, S.9009, S.9610, S,9581, S.9029, S.9059, S.9769, S.9821, S.9439, S.9055 REMARKS: UG cable fault from S.9055 Girrilang Rd SW/B to S.9775 Bate Kirkwood SW/A tee to S.9822 Links Mitchell | February | 2012 | 2012Q3 | 2012 | ZN9118:PA6 | ZN9118:PA6 | ZN09118/000006 | SUTHERLAND | UG | Not Veg | 2012-02-20 | N | 53.5942 | N | 26 | Y | Y | 1.1101 | 39.4971 | 66972.1937
| ZN15014:PA16 | 385 | 785.0918 | 45.64 | 2.0392 | 45.64 | 18606 | 275 | 787390 | 2012-02-21 04:31 | 2012-02-21 06:25 | 114 | 11kV | 97944 | 1072 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.10 tripped on A phase IOC and EFI Cable fault on section of feeder from Pnl.10 to AB42638 to Sw D @ RMI in switchyard tee PT.11113 See OMS # 787492 787489 | February | 2012 | 2012Q3 | 2012 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | UG | Not Veg | 2012-02-21 | N | 91.3657 | N | 7 | N | N | 1.1101 | 39.4971 | 71574.5863
| ZN15014:PA18 | 703 | 533.4542 | 32.25 | 0.75883 | 32.25 | 19730 | 12048 | 786880 | 2012-02-20 08:57 | 2012-02-21 06:51 | 1313.6333 | 11kV | 1313.6333 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | CC1: 22-"Refer to SOp" LID 129755 3 phase DOLF : 40 Amp. Defective transformer Excluded OMS 786731 OMS 786727 Suspected GIS error for this nmi, have emailed to GIS corrections for investigation and rectification if applicable assuming at this stage that nmi was involved in outage represented by OMS 786727 - LID 129755 | February | 2012 | 2012Q3 | 2012 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | UG | Not Veg | 2012-02-20 | N | 1313.6333 | N | 26 | Y | Y | 1.1101 | 39.4971 | 959.9645
| ZN15014:PA19 | 1934 | 1518.7278 | 36.14 | 0.78528 | 36.14 | 19225 | 6213 | 786727 | 2012-02-20 05:17 | 2012-02-21 06:51 | 1534.7 | 11kV | 18173.7833 | 33 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 129755 3 phase DOLF : 40 Amp. Defective transformer Excluded OMS 786731 OMS 786727 | February | 2012 | 2012Q3 | 2012 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | UG | Not Veg | 2012-02-20 | N | 550.7207 | N | 26 | Y | Y | 1.1101 | 39.4971 | 13280.8648
| ZN15014:PA20 | 922 | 1259.6761 | 44.96 | 1.3662 | 44.96 | 18798 | 2100 | 787515 | 2012-02-21 09:17 | 2012-02-21 10:10 | 53 | 11kV | 18126 | 342 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 129770 2 Fault operations A & B Phase Overcurrent Removed piece of bark from 11kV mains at pole MG-20135 MandalongRd Excluded oms 787515 & 787518 OMS 788430 | February | 2012 | 2012Q3 | 2012 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-02-21 | N | 53 | N | 7 | N | N | 1.1101 | 39.4971 | 13245.9462
| ZN15014:PA22 | 966 | 1127.5669 | 44.71 | 1.1673 | 44.71 | 19837 | 13067 | 787416 | 2012-02-21 07:29 | 2012-02-21 10:40 | 191 | 11kV | 191 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129769 Single phase DOLF : 10 Amp sub isolated to replace la's VOLTS 239 LOAD 16 amps Excluded oms 787416 OMS 788440 | February | 2012 | 2012Q3 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2012-02-21 | N | 191 | N | 7 | N | N | 1.1101 | 39.4971 | 139.5772
| ZN15014:PA5 | 1831 | 1489.912 | 38.74 | 0.81371 | 38.74 | 19499 | 9087 | 787361 | 2012-02-20 20:19 | 2012-02-21 11:00 | 881 | 11kV | 56700 | 369 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.16 Tripped, reclosed, tripped and locked out on: Earth Fault trip, timing, lockout Tree Branch brought down OH mains. Section of 11kV from LK44713 to AB400006 to REC45118 to LK44714 tee PTs 12198 13997 12845 12495. See OMS # 788028 788029 | February | 2012 | 2012Q3 | 2012 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2012-02-20 | N | 153.6585 | N | 26 | Y | Y | 1.1101 | 39.4971 | 41434.6876
| ZN15014:PA7 | 1241 | 1217.4837 | 38.68 | 0.98105 | 38.68 | 19204 | 5866 | 787762 | 2012-02-21 13:22 | 2012-02-21 14:24 | 62 | 11kV | 124 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129775 Single phase DOLF : 3 Amp Excluded OMS 787762 OMS 788458 | February | 2012 | 2012Q3 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2012-02-21 | N | 62 | N | 7 | N | N | 1.1101 | 39.4971 | 90.6155
| ZN15014:PA8 | 1044 | 1268.207 | 40.99 | 1.2148 | 40.99 | 19796 | 12777 | 787781 | 2012-02-21 13:35 | 2012-02-21 14:45 | 70 | 11kV | 17962 | 371 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of Pa10 Tryon Fdr Ex Lindfield High Resistance on AB2070 See OMS 790057 790054 787780 787781 787788 | February | 2012 | 2012Q3 | 2012 | ZN1193:PA10 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2012-02-21 | N | 48.4151 | N | 7 | N | N | 1.1101 | 39.4971 | 13126.0998
| 806:82662 | 230 | 390.2647 | 40.05 | 1.6968 | 40.05 | 19055 | 4376 | 787911 | 2012-02-21 16:44 | 2012-02-21 20:11 | 207 | 11kV | 8901 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC44853 Ourimba Bumble tripped and locked out on OC Tree branch brought down 11kV OH mains | February | 2012 | 2012Q3 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-02-21 | N | 207 | N | 7 | N | N | 1.1101 | 39.4971 | 6504.5883
| 806:82667 | 40 | 15.9313 | 30.97 | 0.39828 | 30.97 | 19048 | 4361 | 787998 | 2012-02-21 21:29 | 2012-02-21 22:26 | 57 | 11kV | 81567 | 1431 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S129 Hunters Hill panel 10 Tripped on Earth Fault, Fault Check, EFI. Cause: Possum on UGOH to S6304 Beach Bayview Based on Customer calls - suspect S1315 in parallel with Pa10 See OMS 788272 788273 787998 788002 788000 | February | 2012 | 2012Q3 | 2012 | ZN129:PA10 | ZN129:PA49 | ZN00129/000049 | RYDE | OH | Not Veg | 2012-02-21 | N | 57 | N | 7 | N | N | 1.1101 | 39.4971 | 59606.7578
| 243:80074 | 1927 | 1798.4661 | 43.11 | 0.9333 | 43.11 | 19339 | 7590 | 788040 | 2012-02-22 08:11 | 2012-02-22 08:47 | 36 | 11kV | 81252 | 2257 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.10 tripped on: Trip LED, EFI LED. Field EFI @ S.14857 Abnormal Switching: AB41095 CLOSED - AB43339 OPEN Asplund tree contractors using close approach tree trimming mthods, when a dead tree limb dropped onto 11kV mains in Wolseley Ave Tacoma See OMS # 788651 788650(GIS) | February | 2012 | 2012Q3 | 2012 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Veg | 2012-02-22 | N | 36 | N | 6 | N | N | 1.1101 | 39.4971 | 59376.5651
| 243:80075 | 1022 | 1324.6101 | 40.33 | 1.2961 | 40.33 | 19638 | 10593 | 788261 | 2012-02-22 12:02 | 2012-02-22 12:43 | 41 | 11kV | 59795 | 1494 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At ZN.9245 Engadine P-4 "The Paterson Banjo etc" fdr tripped, reclosed on: RELAYS: A & C phase Inst and timed IOC, Lockout Relay, Timer, EFI SIGNALS: 11kV Trip, TX.1 Grp Eth ABNORMAL: Open at LB 35153 (1B8), Closed at 35800 (Janalli 1C9) REMARKS: Staff error - details below. 11kV Fdr from S.9231 Garvan Rd (Sw B) to S.9892 Burns Prices (Sw A), cable damaged by Jointer whilst excavating. | February | 2012 | 2012Q3 | 2012 | ZN9245:PA4 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | UG | Not Veg | 2012-02-22 | N | 40.0234 | N | 6 | N | N | 1.1101 | 39.4971 | 43696.4223
| 243:80077 | 370 | 413.6703 | 60.06 | 1.118 | 60.06 | 20198 | 16942 | 788299 | 2012-02-22 12:42 | 2012-02-22 14:50 | 128 | 11kV | 19328 | 151 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.13816 painters Campbell - Centre Phase 31.5A HVDO failed Possible fuse fatigue See OMS # 788660 788661 | February | 2012 | 2012Q3 | 2012 | ZN12570:PA9 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2012-02-22 | N | 128 | N | 6 | N | N | 1.1101 | 39.4971 | 14124.3323
| 243:80078 | 1328 | 1070.976 | 33.23 | 0.80646 | 33.23 | 18826 | 2338 | 788389 | 2012-02-22 14:05 | 2012-02-22 15:30 | 85 | 11kV | 630 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129782 A Phase DOLF : 16 Amp Found after replacing LF 74551 report 129781 | February | 2012 | 2012Q3 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2012-02-22 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 460.3854
| 243:80080 | 658 | 761.2233 | 36.8 | 1.1569 | 36.8 | 18990 | 3891 | 788387 | 2012-02-22 14:01 | 2012-02-22 17:20 | 199 | 11kV | 6368 | 32 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn.14891 Wyong Pnl.12 - Auto Links 4740 Bunning Creek Yarramalong found activated. Auto links operated. Roadside activated feeder patrolled nothing found. | February | 2012 | 2012Q3 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2012-02-22 | N | 199 | N | 6 | N | N | 1.1101 | 39.4971 | 4653.5466
| 243:80081 | 1914 | 1156.8298 | 30.65 | 0.6044 | 30.65 | 20321 | 19241 | 788532 | 2012-02-22 18:01 | 2012-02-22 19:40 | 99.45 | 11kV | 3182.4 | 32 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Ex Pnl.12 Wyong Zn - Auto Links 47340 Bunning Creek yarramalong operated. See prior interuption Possible faulty Autolinks. T/Con to investigate. By Pass closed to restore | February | 2012 | 2012Q3 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2012-02-22 | N | 99.45 | N | 6 | N | N | 1.1101 | 39.4971 | 2325.6041
| 243:80083 | 877 | 660.1994 | 34.97 | 0.75279 | 34.97 | 19111 | 4695 | 788772 | 2012-02-23 11:34 | 2012-02-23 13:45 | 131 | 11kV | 2217 | 27 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 129795 A & C Phase DOLF : 20 Amp Suspect excavator hit 11kV mains near sub 26317. Reported to C Chapman Excluded OMS 788772, 788787, 788813 OMS 789199, 789200 | February | 2012 | 2012Q3 | 2012 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Not Veg | 2012-02-23 | N | 82.1111 | N | 2 | N | N | 1.1101 | 39.4971 | 1620.1182
| 243:80084 | 956 | 664.0736 | 32.92 | 0.69464 | 32.92 | 19401 | 8346 | 788921 | 2012-02-23 15:47 | 2012-02-23 17:36 | 109 | 11kV | 5957 | 56 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Panel 45 at sub40 Leichardt Spags 140C RLay L2, 4, EFI 11kv trip ZE GE #3 TX EFI sub 8189, sub 35867, sub 7728, sub 7727 Remarks: UG Fault, Fault between sub 7727 James Craig rd #2 and sub 35805 James craig rd #5 Related jobs: #788940, 788921, 789078, 789077, 788920 | February | 2012 | 2012Q3 | 2012 | ZN116:PA45 | ZN116:PA1 | ZN00116/000001 | INNER WEST | UG | Not Veg | 2012-02-23 | N | 106.375 | N | 2 | N | N | 1.1101 | 39.4971 | 4353.1999
| ZN10994:PA1 | 1018 | 831.4945 | 30.68 | 0.81679 | 30.68 | 18991 | 3909 | 789403 | 2012-02-24 17:33 | 2012-02-24 20:54 | 201 | 11kV | 201 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129809 3 Phase DOLF : 3.15 Amp 3.15 A Fuses. Fuses are in a trial. People only there on weekends. Probably happened in storms last week Excluded OMS # 789403 OMS 789883 | February | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-02-24 | N | 201 | N | 3 | N | N | 1.1101 | 39.4971 | 146.8849
| ZN10994:PA10 | 1135 | 992.1349 | 31.5 | 0.87413 | 31.5 | 20123 | 16127 | 789428 | 2012-02-24 19:18 | 2012-02-24 21:03 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129810 single phase DOLF : 3.15 Amp. 3.15Amp Fuse. In Trial. May have blown in previous storm. 251Volts 3.6Amps Excluded OMS # 789428. OMS 789896 | February | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-02-24 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 76.7309
| ZN10994:PA11 | 771 | 779.7452 | 33.53 | 1.0113 | 33.53 | 20253 | 17843 | 789455 | 2012-02-24 23:13 | 2012-02-25 00:50 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129812 A Phase DOLF : 10 Amp. Excluded OMS 789455 OMS 789778 | February | 2012 | 2012Q3 | 2012 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2012-02-24 | N | 97 | N | 3 | N | N | 1.1101 | 39.4971 | 70.8847
| ZN10994:PA12 | 2219 | 1546.7232 | 34.88 | 0.69704 | 34.88 | 18591 | 129 | 789491 | 2012-02-25 09:30 | 2012-02-25 11:05 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129813 A Phase DOLF : 10 Amp excluded OMS 789491 OMS 789915 | February | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-02-25 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 69.4232
| ZN10994:PA13 | 1103 | 864.417 | 31.72 | 0.7837 | 31.72 | 19106 | 4671 | 789498 | 2012-02-25 09:30 | 2012-02-25 11:15 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129816 A phase DOLF : 3.15 Amp Excluded OMS 789498 OMS 789922 | February | 2012 | 2012Q3 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2012-02-25 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 76.7309
| ZN10994:PA14 | 502 | 536.1741 | 43.78 | 1.0681 | 43.78 | 18655 | 742 | 789501 | 2012-02-25 09:45 | 2012-02-25 12:15 | 150 | 11kV | 150 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129817 A Phase DOLF : 3.15 Amp Excluded OMS 789501 OMS 789940 | February | 2012 | 2012Q3 | 2012 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2012-02-25 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 109.6156
| ZN10994:PA18 | 1006 | 666.1573 | 38.23 | 0.66218 | 38.23 | 18929 | 3351 | 789586 | 2012-02-25 16:39 | 2012-02-25 18:34 | 115 | 11kV | 14084 | 2912 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 129818 Trip & Reclose 1 fault operation C phase Overcurrent Burnt tree branch near sub 966. Excluded OMS 789586. OMS 789832, 789835 | February | 2012 | 2012Q3 | 2012 | 232:11459 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2012-02-25 | N | 4.8365 | N | 4 | N | N | 1.1101 | 39.4971 | 10292.1718
| ZN10994:PA19 | 1019 | 1362.393 | 38.52 | 1.337 | 38.52 | 19743 | 12374 | 789608 | 2012-02-26 00:07 | 2012-02-26 01:00 | 52.6167 | 11kV | 17310.8833 | 329 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 22381 tripped and locked out on IOC - D.Op removed tree branch | February | 2012 | 2012Q3 | 2012 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2012-02-26 | N | 52.6167 | N | 6 | N | N | 1.1101 | 39.4971 | 12650.283
| ZN10994:PA2 | 1699 | 1408.1784 | 37.9 | 0.82883 | 37.9 | 19429 | 8501 | 789612 | 2012-02-26 01:18 | 2012-02-26 02:18 | 60 | 11kV | 960 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129820 A Phase DOLF : 10 Amp Excluded OMS 789612 OMS 789960 | February | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-02-26 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 701.5397
| ZN10994:PA20 | 2377 | 1186.9691 | 30.94 | 0.49936 | 30.94 | 19605 | 10211 | 789625 | 2012-02-26 08:05 | 2012-02-26 09:20 | 75 | 11kV | 99761 | 1347 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At ZN.9700 Kirrawee 11kV P-20 "The Belmont Cook fdr", tripped and locked out on SEF: SIGNALS: 11kV Trip REMARKS: Centre phase bond burnt off at AB.36016. | February | 2012 | 2012Q3 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2012-02-26 | N | 74.0616 | N | 6 | N | N | 1.1101 | 39.4971 | 72902.3963
| ZN10994:PA21 | 1026 | 861.7404 | 29.68 | 0.8399 | 29.68 | 18867 | 2703 | 789657 | 2012-02-26 11:42 | 2012-02-26 13:25 | 103 | 11kV | 38128 | 376 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of Pnl.12 Yarramalong Fdr @ Wyong Zone - AB40499 found Open. Bolts on ground, appears bolts holding bottom down rod to handle fell out as timber mounting holes have rotten & enlarged. DOp made temporary repairs (rope/Bolts) See OMS # 789903 789904 | February | 2012 | 2012Q3 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2012-02-26 | N | 101.4043 | N | 6 | N | N | 1.1101 | 39.4971 | 27862.8178
| ZN10994:PA3 | 1076 | 754.8146 | 37.14 | 0.7015 | 37.14 | 19079 | 4511 | 789641 | 2012-02-26 10:03 | 2012-02-26 14:07 | 244 | 11kV | 244 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129824 Single phase DOLF : 10 Amp Replaced burnt HV fuse carrier. 246V 10A. Excluded OMS 789641. OMS 789843 | February | 2012 | 2012Q3 | 2012 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2012-02-26 | N | 244 | N | 6 | N | N | 1.1101 | 39.4971 | 178.308
| ZN10994:PA4 | 2240 | 1578.981 | 34.49 | 0.7049 | 34.49 | 20417 | 20237 | 789713 | 2012-02-26 18:55 | 2012-02-26 19:55 | 60 | 11kV | 13440 | 224 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Ex Pnl.9 Lisarow Zn - 11kV feeder from AB41054 to AB43629 to AB43628 to AB41049 interrupted to carry out reapirs to broken cross arm & pin insulators. PT12611 12612 12683 18746 interrupted | February | 2012 | 2012Q3 | 2012 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2012-02-26 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 9821.5556
| ZN10994:PA7 | 1714 | 1683.9075 | 33.38 | 0.98244 | 33.38 | 18973 | 3603 | 109 | 2012-02-27 | 2012-02-27 01:12 | 72 | 11kV | 72 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting OMS update(s) | February | 2012 | 2012Q3 | 2012 |  |  |  |  | Unknown | Unknown | 2012-02-27 | N | 72 | N | 8 | N | N | 1.1101 | 39.4971 | 52.6155
| ZN10994:PA8 | 368 | 388.0554 | 59.65 | 1.0545 | 59.65 | 18793 | 2072 | 789912 | 2012-02-27 10:56 | 2012-02-27 12:57 | 121 | 11kV | 127973 | 1457 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129837 2 fault operations A & C phase Overcurrent | February | 2012 | 2012Q3 | 2012 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Veg | 2012-02-27 | N | 87.8332 | N | 8 | N | N | 1.1101 | 39.4971 | 93518.8938
| ZN10994:PA9 | 1234 | 767.9987 | 37.26 | 0.62237 | 37.26 | 18726 | 1303 | 789945 | 2012-02-27 11:32 | 2012-02-27 12:57 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129836 Single phase DOLF : 3.15 Amp | February | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-02-27 | N | 85 | N | 8 | N | N | 1.1101 | 39.4971 | 62.1155
| ZN180:PA10 | 1389 | 1240.984 | 41.91 | 0.89344 | 41.91 | 19178 | 5277 | 789990 | 2012-02-27 12:00 | 2012-02-27 14:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129839 A Phase DOLF : 10 Amp | February | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-02-27 | N | 120 | N | 8 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN180:PA15 | 473 | 517.7547 | 36.55 | 1.0946 | 36.55 | 19135 | 4864 | 790034 | 2012-02-27 13:32 | 2012-02-27 14:38 | 66 | 11kV | 1914 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Peats Ridge Zn P1 - From AB40514 to AB43334 interrupted for safety for OH mains to conduct repairs. OH resting on cross arm | February | 2012 | 2012Q3 | 2012 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2012-02-27 | N | 66 | N | 8 | N | N | 1.1101 | 39.4971 | 1398.6947
| ZN180:PA16 | 568 | 526.3251 | #N/A | 0.92663 | 39.4971 | 19681 | 11355 | 790038 | 2012-02-27 13:40 | 2012-02-27 14:45 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129840 B Phase DOLF : 10 Amp Excluded OMS 790038 OMS 790392 | February | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-02-27 | N | 65 | N | 8 | N | N | 1.1101 | 39.4971 | 95.0002
| ZN180:PA17 | 734 | 934.0383 | 40.21 | 1.2725 | 40.21 | 18875 | 2853 | 790143 | 2012-02-27 16:15 | 2012-02-27 17:55 | 100.0833 | 11kV | 20517.0833 | 205 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" At F.24967 the footpath and centre phase 50 amp fuses blown due to tree branch on mains in Wangara St | February | 2012 | 2012Q3 | 2012 | ZN15014:PA16 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | OH | Veg | 2012-02-27 | N | 100.0833 | N | 8 | N | N | 1.1101 | 39.4971 | 14993.2793
| ZN180:PA19 | 1445 | 1153.8659 | 34.43 | 0.79852 | 34.43 | 20009 | 14998 | 790209 | 2012-02-27 20:07 | 2012-02-27 22:07 | 120 | 11kV | 38553 | 1263 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn901 Surry Hills Pa22 "S832 Belvior st" tripped on Relays-EF EFI Signals-11kV trip Ze Tx2 GE EFI-S832 Note S6960 Does not have EFI S2313 EFI did not operate 11kv UG cable fault from S2313 tee to Tx1 @S2313 to S4504 @Pa33 fdr tripped relay-EF EFI Signal-11kv trip ZE Tx2 GE EFI-All subs on fdr Trying back fdr from S4504 onto fault See 790920,1,2,1003,4 LV// 791023 Exclude 790209,14,5,25,6 | February | 2012 | 2012Q3 | 2012 | ZN901:PA22 | ZN7900:PA11 | ZN07900/000011 | SYDNEY | UG | Not Veg | 2012-02-27 | N | 30.5249 | N | 8 | N | N | 1.1101 | 39.4971 | 28173.3953
| ZN180:PA20 | 1162 | 882.8832 | 38.19 | 0.7598 | 38.19 | 19760 | 12459 | 790350 | 2012-02-28 10:27 | 2012-02-28 12:30 | 123 | 11kV | 18406 | 478 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Panel 10 at Zn35370 Galston has been opened for safety. Cause: 11kV Wires down near PT1764 Hemers Quarry Recloser 2691 Closed AB117 Open. See OMS 790947 790743 790941 790353 790350 | February | 2012 | 2012Q3 | 2012 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-02-28 | N | 38.5063 | N | 5 | N | N | 1.1101 | 39.4971 | 13450.5619
| ZN180:PA21 | 1882 | 1421.2136 | 40.39 | 0.75516 | 40.39 | 20129 | 16171 | 790290 | 2012-02-28 09:09 | 2012-02-28 16:00 | 411 | 11kV | 474497.95 | 2361 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At ZN.10997 Sans Sousi P-11 "Russell Napoleon" fdr tripped, reclosed, tripped & locked out on: RELAYS: IOC, EFI Timing/lockout relay, 11kV trip. SIGNALS: CB No.2 open, Grp Eth, No.1 Grp earth, 11kV Trip. FIELD EFIs: S.10713 - S.10099 REMARKS: Vehicle hit Pole. Truck hit pole Cnr Sandringham & Norman Ave, HV into LV Dist.1 at PT.10453 & Dist.3 S.10099 ISOLATED intil Cust Installation inspected. 11kV fdr SW/B at S.10099 Norman Minton to AB30055 to LK30213 to LK30838, note section beyond LK30838 interrupted (S.10514, S.10215) | February | 2012 | 2012Q3 | 2012 | ZN10997:PA2 | ZN10997:PA2 | ZN10997/000002 | BAYSIDE | OH | Not Veg | 2012-02-28 | N | 200.9733 | N | 5 | N | N | 1.1101 | 39.4971 | 346749.1065
| ZN180:PA22 | 2711 | 1811.0795 | 35.46 | 0.66805 | 35.46 | 19873 | 13503 | 790627 | 2012-02-28 17:15 | 2012-02-28 18:15 | 60 | 11kV | 120 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129851 Single phase DOLF : 3.15 Amp. Excluded OMS 790627 OMS 790940 | February | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-02-28 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN180:PA23 | 1234 | 1471.0999 | 36.29 | 1.1921 | 36.29 | 18997 | 3975 | 790661 | 2012-02-28 18:03 | 2012-02-28 23:20 | 317 | 11kV | 634 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129853 C Phase Burnt off LLC lead. Aph 244V 28A Bph 245V 5A Cph 244V 4A. Excluded OMS 790661. OMS 790851 | February | 2012 | 2012Q3 | 2012 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2012-02-28 | N | 317 | N | 5 | N | N | 1.1101 | 39.4971 | 463.3085
| ZN180:PA24 | 1076 | 1218.7712 | 31.76 | 1.1327 | 31.76 | 19524 | 9208 | 790730 | 2012-02-29 00:46 | 2012-02-29 01:36 | 50 | 11kV | 11200 | 224 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn1610 Homebush Bay Panel 19 "Evans Asia" ect feeder Relays: - FNGIA N*-* Earth Fault trip, EFI Signals - Tx 2 Group Earth Field EFI's: Nil Remarks: UG fault. Front line feeder fault Zn 1610 Homebush Bay Panel 19 "Evans Asia" ect feeder. Panel 19 to Sub 36068 Evans Asia SW A isolated and earthed with Tester/Jointer A/P issued. Related jobs: #791081, 790730 | February | 2012 | 2012Q3 | 2012 | ZN1610:PA19 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2012-02-29 | N | 50 | N | 13 | N | N | 1.1101 | 39.4971 | 8184.6297
| ZN180:PA27 | 979 | 700.3397 | 33.05 | 0.71536 | 33.05 | 19214 | 5999 | 790739 | 2012-02-29 06:06 | 2012-02-29 07:10 | 64 | 11kV | 64 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129855 A Phase DOLF : 10 Amp. Excluded OMS 790739 OMS 790771 | February | 2012 | 2012Q3 | 2012 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2012-02-29 | N | 64 | N | 13 | N | N | 1.1101 | 39.4971 | 46.7693
| ZN180:PA28 | 1404 | 854.2289 | 35.98 | 0.60843 | 35.98 | 19337 | 7582 | 790744 | 2012-02-29 06:32 | 2012-02-29 08:25 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129856 C Phase DOLF : 10 Amp Excluded OMS 790744 OMS 791425 | February | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-02-29 | N | 113 | N | 13 | N | N | 1.1101 | 39.4971 | 82.5771
| ZN180:PA29 | 1207 | 1017.1639 | 40.42 | 0.84272 | 40.42 | 18884 | 2955 | 790753 | 2012-02-29 07:19 | 2012-02-29 08:55 | 96 | 11kV | 192 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129857 A Phase DOLF : 10 Amp Excluded OMS 790753 OMS 791435 | February | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-02-29 | N | 96 | N | 13 | N | N | 1.1101 | 39.4971 | 140.3079
| ZN180:PA30 | 1750 | 1807.0604 | 33.52 | 1.0326 | 33.52 | 19487 | 8997 | 790697 | 2012-02-28 19:41 | 2012-02-29 11:45 | 964 | 11kV | 96709 | 526 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Peats Ridge Zn Pnl.2 - REC 45189 Coooks Peats Ridge 0.5 - Overcurrent and lock out Tree brnach brought down 11kV overhead main across the river beyond AB43285. PT13863, 12658 & 13864 interrupted. @ PT.13864 wires on ground and DOp advised HV into LV, Installation inspectors required. See OMS # 791274 791276 | February | 2012 | 2012Q3 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2012-02-28 | N | 183.8574 | N | 5 | N | N | 1.1101 | 39.4971 | 70672.0848
| ZN180:PA31 | 1636 | 1267.4233 | 37.06 | 0.77471 | 37.06 | 20223 | 17281 | 790910 | 2012-02-29 10:56 | 2012-02-29 12:15 | 79 | 11kV | 26465 | 335 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Panel 16 IOC B and C phase Earth Fault check, EFI All field EFI down Remarks: Tree branch contact - other. Branch on OH adjacent to AB 2487 Related jobs: #790934, 790912, 790910, 790908, 790894, 790887, 791375, 791372 | February | 2012 | 2012Q3 | 2012 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-02-29 | N | 79 | N | 13 | N | N | 1.1101 | 39.4971 | 19339.8414
| ZN180:PA32 | 2546 | 2224.9472 | 39.91 | 0.8739 | 39.91 | 20138 | 16232 | 791449 | 2012-02-29 12:15 | 2012-02-29 12:31 | 16 | 11kV | 32 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129862 A Phase DOLF : 10 Amp D Thomson found & reported LF 40963 blown. | February | 2012 | 2012Q3 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-02-29 | N | 16 | N | 13 | N | N | 1.1101 | 39.4971 | 23.3847
| ZN180:PA33 | 899 | 916.9281 | 45.33 | 1.0199 | 45.33 | 18829 | 2360 | 790978 | 2012-02-29 12:09 | 2012-02-29 13:20 | 71 | 11kV | 284 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129864 C phase DOLF : 10 Amp Excluded OMS 790978 OMS 791384 | February | 2012 | 2012Q3 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2012-02-29 | N | 71 | N | 13 | N | N | 1.1101 | 39.4971 | 207.5388
| ZN180:PA34 | 711 | 795.5041 | 31.33 | 1.1189 | 31.33 | 19316 | 7430 | 790984 | 2012-02-29 12:17 | 2012-02-29 14:10 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129866 Single phase DOLF : 10 Amp Excluded OMS 790984 OMS 791295 | February | 2012 | 2012Q3 | 2012 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-02-29 | N | 113 | N | 13 | N | N | 1.1101 | 39.4971 | 82.5771
| ZN180:PA35 | 1522 | 954.5776 | 33.88 | 0.62719 | 33.88 | 20097 | 15937 | 791005 | 2012-02-29 13:13 | 2012-02-29 15:02 | 109 | 11kV | 127662 | 1188 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129865 A & B phase 1 fault operation Overcurrent Reclose Function was off at time of fault. (Access Permit on section past ABS 9121) Fdr patrolled no cause found. Excluded oms 791005 OMS 791310, 791312 | February | 2012 | 2012Q3 | 2012 | 225:33676 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2012-02-29 | N | 107.4596 | N | 13 | N | N | 1.1101 | 39.4971 | 93291.6242
| ZN180:PA41 | 2193 | 1864.5883 | 37.45 | 0.85025 | 37.45 | 18883 | 2921 | 790995 | 2012-02-29 12:46 | 2012-02-29 15:03 | 137 | 11kV | 104563 | 1099 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.10994 Mortdale, P-10 "Roberts Ave" 11kV feeder tripped on: RELAYS: A phase O/C, Earth Fault, EFI FIELD EFIs: Nil REMARKS: Cause not ascertained. DOp interruption time extended due to recloser being removed from P-10. | February | 2012 | 2012Q3 | 2012 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2012-02-29 | N | 95.1438 | N | 13 | N | N | 1.1101 | 39.4971 | 76411.5563
| ZN180:PA42 | 1874 | 1233.4164 | 32.83 | 0.65817 | 32.83 | 20043 | 15527 | 791191 | 2012-02-29 19:52 | 2012-02-29 21:03 | 71 | 11kV | 57226 | 806 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Heavy | N | At S.3154 St Ives, Panel 3 Fdr CB tripped on A phase OC, efi, 11kV trip, Zone Earth, #1 Tx group earth. Field efi's down at S.7322, S.35798, S.4750, S.46950 and S.4753. At PT.1340 the roadside and centre phase HDO's operated. Tree bark fell across HV Tx tails at PT.1340 | February | 2012 | 2012Q3 | 2012 | ZN3154:PA3 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Veg | 2012-02-29 | N | 71 | N | 13 | N | N | 1.1101 | 39.4971 | 41819.0729
| ZN180:PA43 | 1235 | 1514.7373 | 37.06 | 1.2265 | 37.06 | 20092 | 15906 | 791204 | 2012-02-29 20:56 | 2012-02-29 22:02 | 66 | 11kV | 79266 | 1201 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S129 Hunters Hill Panel 8 tripped on A and C phase O/C, B phase earth leakage, Frame Leakage fault check, efi Signals: 11kV trip, Zone earth, No1 Tx Group Earth. Cause: Possum found at the base of UGOH between S8520 and PT327. Footpath Side bond burnt off on lightning arrestor. See OMS 791204 791211 | February | 2012 | 2012Q3 | 2012 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Not Veg | 2012-02-29 | N | 66 | N | 13 | N | N | 1.1101 | 39.4971 | 57925.2548
| ZN180:PA7 | 1616 | 1248.8772 | 37.34 | 0.77282 | 37.34 | 19132 | 4851 | 791224 | 2012-02-29 22:15 | 2012-03-01 00:29 | 133.3667 | 11kV | 39844.3667 | 428 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Section of 11kV fdr P-10 "S.9516 Kumbardang Kiora" fdr. Bond burnt off footpath load side. Ex ZN.9037 Miranda P-10. REMARKS: At AB.35894 Bond burnt off footpath load side. | February | 2012 | 2012Q3 | 2012 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | OH | Not Veg | 2012-02-29 | N | 93.0943 | N | 13 | N | N | 1.1101 | 39.4971 | 29117.088
| ZN180:PA9 | 873 | 867.2091 | 39.43 | 0.99337 | 39.43 | 18916 | 3214 | 791281 | 2012-03-01 07:53 | 2012-03-01 08:30 | 37 | 11kV | 148 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 129876 C Phase DOLF 16 Amp Carrier found burnt. Volts = 246. Amps = 4,1,1. Excluded OMS # 791281 OMS 791848 | March | 2012 | 2012Q3 | 2012 | 234:2001 | 264:81232 | ZN00264/081232 | MAITLAND | OH | Not Veg | 2012-03-01 | N | 37 | N | 7 | N | N | 1.1101 | 39.4971 | 108.154
| 217:33605 | 828 | 1360.0298 | 36.91 | 1.6425 | 36.91 | 19700 | 11653 | 791242 | 2012-03-01 05:01 | 2012-03-01 09:20 | 259 | 11kV | 144872 | 1148 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 129870 2 fault operations 3 phase Tree growing into mains Excluded OMS 791242, 791244, 791267, 791269, 791270, 791504 OMS 791517, 791518 | March | 2012 | 2012Q3 | 2012 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2012-03-01 | N | 126.1951 | N | 7 | N | N | 1.1101 | 39.4971 | 105868.1846
| 217:33607 | 44 | 40.3192 | 32.52 | 0.91634 | 32.52 | 19963 | 14529 | 791252 | 2012-03-01 06:31 | 2012-03-01 10:20 | 229 | 11kV | 144811 | 1626 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At ZN.9245 Engadine P-4 "The Paterson Banjo etc" fdr tripped on: RELAYS: SEL SIGNALS: ABNORMAL: REMARKS: DOp found bond burnt off at AB.35675, when DOp went to open AB, centre phase operating arm failed and another phase contact failed to Open. | March | 2012 | 2012Q3 | 2012 | ZN9245:PA4 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2012-03-01 | N | 89.0597 | N | 7 | N | N | 1.1101 | 39.4971 | 105823.6076
| 217:33608 | 699 | 666.1973 | 31.47 | 0.95307 | 31.47 | 18925 | 3333 | 791271 | 2012-03-01 07:25 | 2012-03-01 10:30 | 185 | 11kV | 185 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129881 A phase DOLF : 31 Amp | March | 2012 | 2012Q3 | 2012 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2012-03-01 | N | 185 | N | 7 | N | N | 1.1101 | 39.4971 | 135.1925
| 217:33610 | 1717 | 1029.6923 | 30.75 | 0.5997 | 30.75 | 19949 | 14244 | 791542 | 2012-03-01 13:29 | 2012-03-01 14:26 | 57 | 11kV | 87581 | 2047 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2602 Clovelly Zone Pa15 triped on Signals: 11kv trip GE ZE Relays: B&Cph IOC EF EFI FC EFI: S46310 S60 S1874 See 792025,7 exclude 791542 | March | 2012 | 2012Q3 | 2012 | ZN2602:PA15 | ZN36800:PA40 | ZN36800/000040 | RANDWICK | UG | Not Veg | 2012-03-01 | N | 42.7851 | N | 7 | N | N | 1.1101 | 39.4971 | 64001.6116
| 217:33611 | 1358 | 1113.9707 | 31.27 | 0.8203 | 31.27 | 18784 | 1972 | 791667 | 2012-03-01 16:30 | 2012-03-01 19:35 | 185 | 11kV | 185 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 129886 A & C Phase DOLF : 10 Amp Blown Arrestors Excluded OMS 791667 OMS 791931 | March | 2012 | 2012Q3 | 2012 |  |  |  | MUSWELLBROOK | OH | Not Veg | 2012-03-01 | N | 185 | N | 7 | N | N | 1.1101 | 39.4971 | 135.1925
| 217:33612 | 1173 | 733.7975 | 31.62 | 0.62557 | 31.62 | 20042 | 15524 | 791759 | 2012-03-01 21:45 | 2012-03-01 23:10 | 85 | 11kV | 58055 | 683 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Electrical Storm | N | LID 129889 2 fault operations A & C Phase Earth fault, Overcurrent Fault in Australia Meat Holdings sub. Excluded OMS 791759, 791761, 791766, 791769 OMS 791969 | March | 2012 | 2012Q3 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | Unknown | Not Veg | 2012-03-01 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 42424.8817
| 515:35192 | 349 | 397.62 | 42.47 | 1.1393 | 42.47 | 20068 | 15779 | 791790 | 2012-03-02 00:10 | 2012-03-02 00:58 | 48 | 11kV | 63408 | 1321 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Rain Heavy | N | At S.36300 Balgowlah North, Panel 9 Fdr CB tripped on B and C phase IOC | March | 2012 | 2012Q3 | 2012 | ZN36300:PA9 | ZN36300:PA9 | ZN36300/000009 | NORTHERN BEACHES | UG | Not Veg | 2012-03-02 | N | 48 | N | 15 | N | N | 1.1101 | 39.4971 | 46336.6962
| 515:35193 | 149 | 345.4173 | 45.44 | 2.3182 | 45.44 | 20176 | 16697 | 791797 | 2012-03-02 01:14 | 2012-03-02 03:11 | 117 | 11kV | 102708 | 900 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At ZN.10994 Mortdale, P-19 "USL 30746 etc" 11kV feeder tripped on: RELAYS: Unknown ALARMS: TX.3 GE FIELD EFIs: S.10569, 10040 REMARKS: UG Fault. Suspect UG cable fault from LB 31183 to S.10954 Roberts Lorraine (Sw/A) | March | 2012 | 2012Q3 | 2012 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | UG | Not Veg | 2012-03-02 | N | 114.12 | N | 15 | N | N | 1.1101 | 39.4971 | 75055.977
| 515:35197 | 532 | 486.3165 | 38.82 | 0.91413 | 38.82 | 19479 | 8930 | 791792 | 2012-03-02 00:21 | 2012-03-02 05:59 | 338.05 | 11kV | 41676.55 | 126 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | At PT.10379 Endeavour Vista, A phase HDO operated, other phases interrupted by DOp to allow removal of tree from LV mains. REMARKS: Other phases interrupted by DOp to allow removal of tree from LV mains. CC1: 22-"Refer to SOp" | March | 2012 | 2012Q3 | 2012 | ZN10997:PA11 | ZN10997:PA11 | ZN10997/000011 | GEORGES RIVER | OH | Veg | 2012-03-02 | N | 330.7663 | N | 15 | N | N | 1.1101 | 39.4971 | 30455.9935
| 515:35198 | 74 | 242.586 | 43.93 | 3.2782 | 43.93 | 18686 | 1036 | 791844 | 2012-03-02 07:40 | 2012-03-02 07:54 | 14 | 11kV | 602 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129890 C Phase DOLF : 20 Amp Excluded OMS 791844 OMS 793240 | March | 2012 | 2012Q3 | 2012 | 513:48051 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Veg | 2012-03-02 | N | 14 | N | 15 | N | N | 1.1101 | 39.4971 | 439.9238
| 515:35200 | 68 | 619.6878 | 52.11 | 9.1131 | 52.11 | 19717 | 11963 | 791819 | 2012-03-02 06:40 | 2012-03-02 08:00 | 80 | 11kV | 480 | 6 | HV | Animal Flying Fox | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129892 A Phase DOLF : 31 Amp Dead Flying fox found at sub Tx volts Aph - 248V, Bph - 247V, Cph - 244V Excluded OMS 791819 OMS 793231 | March | 2012 | 2012Q3 | 2012 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2012-03-02 | N | 80 | N | 15 | N | N | 1.1101 | 39.4971 | 350.7698
| 801:74117 | 531 | 976.3617 | 37.93 | 1.8387 | 37.93 | 18852 | 2572 | 791816 | 2012-03-02 06:33 | 2012-03-02 08:20 | 107 | 11kV | 1070 | 10 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Rain Heavy | N | PT.11370 Chamberlain Newling - B phase HDO 20 Amp Blown Tree branch in contact with PT See OMS # 792940 792939 | March | 2012 | 2012Q3 | 2012 | ZN12600:PA11 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Veg | 2012-03-02 | N | 107 | N | 15 | N | N | 1.1101 | 39.4971 | 781.9244
| 801:74118 | 919 | 1143.1767 | 43.28 | 1.2439 | 43.28 | 19120 | 4740 | 791845 | 2012-03-02 07:40 | 2012-03-02 10:20 | 160 | 11kV | 320 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | PT.14479 The Ridgeway Paroo 1.2 - B phase 16Amp HDO blown Tree branch contact | March | 2012 | 2012Q3 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2012-03-02 | N | 160 | N | 15 | N | N | 1.1101 | 39.4971 | 233.8466
| 801:74119 | 663 | 554.5551 | 22.2 | 0.83643 | 22.2 | 19697 | 11583 | 791858 | 2012-03-02 08:22 | 2012-03-02 10:23 | 121 | 11kV | 109505 | 905 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S187 Crows Nest Pa21 Tripped on IOC, Fault Check, EFI IT send Group earth, 11KV UG cable damaged by contractor. Private contractor struck 11kV mains between S36023 Miller Shirley and S2921. Telopea Milray. See OMS 796058 796078 791858 791862/917/883/858 | March | 2012 | 2012Q3 | 2012 | ZN187:PA21 | ZN187:PA21 | ZN00187/000021 | NORTH SYDNEY | UG | Not Veg | 2012-03-02 | N | 121 | N | 15 | N | N | 1.1101 | 39.4971 | 80023.0241
| 801:74120 | 584 | 604.3872 | 33.05 | 1.0349 | 33.05 | 20163 | 16442 | 791802 | 2012-03-02 02:24 | 2012-03-02 10:25 | 481 | 11kV | 17454 | 39 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 129895 3 fault operation single phase Earth fault 11kV mains down at pole CV-50376. Excluded OMS 791802 OMS 793157, 793162 | March | 2012 | 2012Q3 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-03-02 | N | 447.5385 | N | 15 | N | N | 1.1101 | 39.4971 | 12754.8684
| 801:74121 | 442 | 520.4621 | 36.83 | 1.1775 | 36.83 | 19849 | 13259 | 791872 | 2012-03-02 08:46 | 2012-03-02 11:50 | 184 | 11kV | 736 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 129894 C phase DOLF : 10 Amp Burnt up fuse element. V = 236V, I = 43A Excluded OMS 791872 OMS 793175 | March | 2012 | 2012Q3 | 2012 | 264:81240 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2012-03-02 | N | 184 | N | 15 | N | N | 1.1101 | 39.4971 | 537.8471
| 801:74122 | 1129 | 1489.0118 | 33.69 | 1.3189 | 33.69 | 19621 | 10409 | 792151 | 2012-03-02 13:36 | 2012-03-02 14:25 | 49 | 11kV | 49 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129897 B Phase DOLF Excluded OMS 792151 (logged against incorrect sub) OMS 793286 | March | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-03-02 | N | 49 | N | 15 | N | N | 1.1101 | 39.4971 | 35.8078
| 801:74123 | 286 | 26.7466 | 37.71 | 0.09352 | 37.71 | 19317 | 7436 | 792190 | 2012-03-02 14:24 | 2012-03-02 16:30 | 126 | 11kV | 8222 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Pnl.5 Wyong Zone - REC 45017 Whiteman - Tripped on Overcurrent trip x 2, A & B phase , lockoutout DOp Linhart found bark on the mains near USL43160. Bark removed and feeder restored See OMS # 792983 792984 792987 | March | 2012 | 2012Q3 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2012-03-02 | N | 104.0759 | N | 15 | N | N | 1.1101 | 39.4971 | 6008.3951
| ZN15002:PA2 | 1271 | 1152.3933 | 31.29 | 0.90668 | 31.29 | 19776 | 12590 | 792078 | 2012-03-02 11:51 | 2012-03-02 16:50 | 299 | 11kV | 3679 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Pnl.20 Wyong - REC 47301 Dickson Hue Hue 0.2 tripped, reclosed, tripped on SEF trip, EF trip Tree brought down OH adj 96 Dickson Rd Jiliby See OMS # 792951 792954 | March | 2012 | 2012Q3 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2012-03-02 | N | 141.5 | N | 15 | N | N | 1.1101 | 39.4971 | 2688.5047
| ZN15002:PA4 | 795 | 629.3048 | 35.31 | 0.79158 | 35.31 | 19268 | 6705 | 792299 | 2012-03-02 17:47 | 2012-03-02 18:45 | 58 | 11kV | 37746 | 767 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 129900 2 fault operation Faulty Lightning arrestors at sub 10380 Excluded OMS 792299, 792300, 792301, 792302, 792303, 792304 OMS 792966, 792967 | March | 2012 | 2012Q3 | 2012 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2012-03-02 | N | 49.2125 | N | 15 | N | N | 1.1101 | 39.4971 | 27583.6635
| ZN15002:PA6 | 1674 | 1894.8019 | 38.78 | 1.1319 | 38.78 | 19592 | 9777 | 792285 | 2012-03-02 17:14 | 2012-03-03 02:50 | 576 | 11kV | 2740 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Pnl.1 West Gosford Zone - REC 45010 Palmgrove - Tripped/reclosed/tripped/ locked out on Earth Fault. Tree brought down 11kV mains near USL 43412 See OMS # 792999 793001 793000 | March | 2012 | 2012Q3 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-03-02 | N | 161.1765 | N | 15 | N | N | 1.1101 | 39.4971 | 2002.3112
| ZN15002:PA8 | 1031 | 1309.03 | 41.62 | 1.2697 | 41.62 | 19340 | 7595 | 792394 | 2012-03-03 08:08 | 2012-03-03 12:35 | 267 | 11kV | 267 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129905 Single phase DOLF : 10 Amp. Excluded OMS 792394 OMS 793197 | March | 2012 | 2012Q3 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2012-03-03 | N | 267 | N | 2 | N | N | 1.1101 | 39.4971 | 195.1157
| ZN15002:PA9 | 14 | 10.2606 | 29.27 | 0.7329 | 29.27 | 18609 | 288 | 792572 | 2012-03-03 19:10 | 2012-03-03 23:10 | 240 | 11kV | 4320 | 18 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 129910 Section of 11kV feeder 74183 isolated to repair broken top of pole 8N-30593. Excluded OMS 792572, 792598. OMS 793297 | March | 2012 | 2012Q3 | 2012 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2012-03-03 | N | 240 | N | 2 | N | N | 1.1101 | 39.4971 | 3156.9286
| 232:11453 | 1363 | 1052.8327 | 36.54 | 0.77244 | 36.54 | 18984 | 3868 | 792633 | 2012-03-04 02:04 | 2012-03-04 03:36 | 92 | 11kV | 154560 | 1680 | HV | Animal Possum | Animal | UGOH | Unplanned | Rain Light | N | At ZN.9700 Kirrawee 11kv fdr P-23 "Talara Kingsway" Tripped on: ABC Overcurrent and EFI EFI: S.9819, S.9813, S.9312, S.9469 & S.9542 REMARKS: Possum on 11kv UGOH adj S.47084 Warcoo Ellesmere. Mains to inspect Mon 5/3/12. | March | 2012 | 2012Q3 | 2012 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2012-03-04 | N | 92 | N | 6 | N | N | 1.1101 | 39.4971 | 112947.8893
| 232:11454 | 1902 | 1372.1554 | 34.27 | 0.72143 | 34.27 | 18715 | 1228 | 792640 | 2012-03-04 06:20 | 2012-03-04 09:50 | 210 | 11kV | 1680 | 8 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129916 A Phase DOLF : 10 Amp Excluded OMS 792640 OMS 793203 | March | 2012 | 2012Q3 | 2012 | 238:34141 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2012-03-04 | N | 210 | N | 6 | N | N | 1.1101 | 39.4971 | 1227.6944
| 232:11455 | 2205 | 1583.1973 | 34.8 | 0.718 | 34.8 | 19043 | 4345 | 792723 | 2012-03-04 12:06 | 2012-03-04 13:13 | 67 | 11kV | 46631 | 836 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3155 Pa11 fdr tripped Relays-EF Fault check relay EFI Signals-11kv trip ZE No.3 GE EFI-S4367 UG Fault 11kv fault from S4367 to S6619 to S47469 See 793184,7 exclude 792723,30 | March | 2012 | 2012Q3 | 2012 | ZN3155:PA11 | ZN3155:PA15 | ZN03155/000015 | WAVERLEY | UG | Not Veg | 2012-03-04 | N | 55.7787 | N | 6 | N | N | 1.1101 | 39.4971 | 34076.5594
| 232:11457 | 1453 | 1087.3905 | 28.67 | 0.74838 | 28.67 | 19083 | 4521 | 792687 | 2012-03-04 10:14 | 2012-03-04 17:30 | 436 | 11kV | 12360 | 173 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12690 berkeley vale Pnl.17 tripped on Earth Fault with EFI signal. Field EFI @ S.14827 Suspect UG cable fault between S.14827 to S.14003 tee PT.14130. Repaired and returned to service @ 1730 See OMS # 793029 793061 | March | 2012 | 2012Q3 | 2012 | ZN12690:PA17 | ZN12690:PA17 | ZN12690/000017 | CENTRAL COAST | UG | Not Veg | 2012-03-04 | N | 71.4451 | N | 6 | N | N | 1.1101 | 39.4971 | 9032.3234
| 232:11460 | 157 | 796.9891 | #N/A | 5.0764 | 39.4971 | 19618 | 10378 | 792805 | 2012-03-04 19:00 | 2012-03-04 20:00 | 60.1333 | 11kV | 9222 | 179 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of 11kV feeder from LB2282 to Ab2285 to S3004 interrupted by DOp. Section of 11kV Feeder Beyond S4617 SW/B interrupted by DOp. Cause: Above section interrupted to perform emergency repairs to AB2285. See OMS 792817 792812 792805 | March | 2012 | 2012Q3 | 2012 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Not Veg | 2012-03-04 | N | 51.5196 | N | 6 | N | N | 1.1101 | 39.4971 | 6739.1656
| 232:33407 | 712 | 933.1022 | 44.2 | 1.3105 | 44.2 | 19809 | 12870 | 792796 | 2012-03-04 18:33 | 2012-03-05 01:40 | 427 | 11kV | 427 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 129931 Tree on sub pulled down service and damaged HV cables to DOLF's. Repaired under A.P. Excluded OMS No.792796. OMS 793337 | March | 2012 | 2012Q3 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2012-03-04 | N | 427 | N | 6 | N | N | 1.1101 | 39.4971 | 312.039
| 232:33409 | 1772 | 1561.8041 | 31.94 | 0.88138 | 31.94 | 20215 | 17154 | 792852 | 2012-03-05 01:12 | 2012-03-05 02:50 | 98 | 11kV | 64252 | 1881 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 129932 1 fault operation C Phase Overcurrent Burnt tapping found at pole JU-41837 Myall Rd. Interconnected temporaarily awaiting repairs. Excluded OMS No's 792852, 792853, 793854, 793855, 793856, 793857, 793859 OMS 793144, 793146 | March | 2012 | 2012Q3 | 2012 | 218:7478 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2012-03-05 | N | 34.1584 | N | 5 | N | N | 1.1101 | 39.4971 | 46953.4665
| 232:33413 | 1077 | 843.6995 | 32.55 | 0.78338 | 32.55 | 19065 | 4430 | 793160 | 2012-03-05 12:41 | 2012-03-05 14:00 | 79 | 11kV | 15405 | 195 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129943 B Phase DOLF : 50 Amp. replaced LA's under AP. Excluded OMS 793160, 793165, 793168, 793190, 793208 OMS 793514 | March | 2012 | 2012Q3 | 2012 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2012-03-05 | N | 79 | N | 5 | N | N | 1.1101 | 39.4971 | 11257.5196
| 210:83465 | 915 | 1464.9535 | 36.92 | 1.601 | 36.92 | 19514 | 9151 | 793219 | 2012-03-05 13:30 | 2012-03-05 15:10 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 129944 A Phase DOLF : 10 Amp. Excluded OMS 793219 OMS 793535 | March | 2012 | 2012Q3 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-03-05 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
| 210:83466 | 861 | 395.3743 | 29.52 | 0.4592 | 29.52 | 20315 | 19102 | 793388 | 2012-03-05 16:57 | 2012-03-05 17:45 | 48 | 11kV | 144 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 129946 B phase DOLF : 10 Amp. Excluded OMS 793388 OMS 793573 | March | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-03-05 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 105.231
| 210:83472 | 356 | 259.3442 | 29.27 | 0.72849 | 29.27 | 20081 | 15874 | 793411 | 2012-03-05 18:28 | 2012-03-05 19:05 | 37 | 11kV | 43364 | 1172 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 42 Tripped on B and Cphase O/C. Cause: Tree branch removed from O/S145 Victoria Rd West Pennant Hills. See OMS 795976 795415/412/411 | March | 2012 | 2012Q3 | 2012 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Veg | 2012-03-05 | N | 37 | N | 5 | N | N | 1.1101 | 39.4971 | 31689.1322
| 210:83473 | 613 | 358.7357 | 36.81 | 0.58521 | 36.81 | 19771 | 12541 | 793460 | 2012-03-06 02:45 | 2012-03-06 05:00 | 135 | 11kV | 3780 | 28 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT.11588 Beufort Wycombe - 31.5K centre phase dropout fuse operated Possum on TX tank, No damage to TX | March | 2012 | 2012Q3 | 2012 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2012-03-06 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 2762.3125
| 210:83474 | 904 | 707.7852 | 40.28 | 0.78295 | 40.28 | 19589 | 9751 | 793717 | 2012-03-06 12:51 | 2012-03-06 15:50 | 179 | 11kV | 358 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129954 A Phase DOLF : 10 Amp. Blown arrester. Replaced all 3 10A fuse on A phase. LID say 3Amp fuse ABC = 248V Ia = 5A, Ib = 10A, Ic = 5A Excluded OMS 793717 OMS 793950 | March | 2012 | 2012Q3 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-03-06 | N | 179 | N | 6 | N | N | 1.1101 | 39.4971 | 261.6158
| 202:34231 37 42 | 397 | 487.5795 | 45.42 | 1.2282 | 45.42 | 18977 | 3760 | 793797 | 2012-03-06 15:15 | 2012-03-06 18:20 | 185 | 11kV | 1110 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 129955 C Phase DOLF : 16 Amp. Burnt up DOLF Carrier replaced. 250V ABCN Excluded OMS 793797, 793851 OMS 793952 | March | 2012 | 2012Q3 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-03-06 | N | 185 | N | 6 | N | N | 1.1101 | 39.4971 | 811.1553
| 202:34232 | 672 | 948.5603 | 41.54 | 1.4115 | 41.54 | 18890 | 3011 | 793826 | 2012-03-06 16:10 | 2012-03-06 19:25 | 195 | 11kV | 195 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129956 single phase DOLF : 3.15 Amp. Blown Surge Arrestor. Polymeric. Replaced 3.15A DOLF 252Volts Excluded OMS 793826 OMS 793982 | March | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-03-06 | N | 195 | N | 6 | N | N | 1.1101 | 39.4971 | 142.5002
| 202:34234 | 138 | 377.9444 | #N/A | 2.7387 | 39.4971 | 19477 | 8919 | 793891 | 2012-03-06 18:48 | 2012-03-06 20:24 | 96 | 11kV | 18816 | 196 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 129957 5 fault operations B phase Earth fault, Overcurrent Suspect Surge arresters adjacent ABS 13570. B Phase lead was touching Earth at arrester. Removed from earth and restored supply. Arrester OK Excluded OMS 793891 OMS 793953 | March | 2012 | 2012Q3 | 2012 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2012-03-06 | N | 96 | N | 6 | N | N | 1.1101 | 39.4971 | 13750.1778
| 202:34238 43 48 | 392 | 845.3638 | 46.77 | 2.1565 | 46.77 | 20369 | 19898 | 793923 | 2012-03-06 21:31 | 2012-03-06 23:10 | 98.6167 | 11kV | 986.1667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" LID 129960 A Phase DOLF : 31.5 Amp | March | 2012 | 2012Q3 | 2012 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-03-06 | N | 98.6167 | N | 6 | N | N | 1.1101 | 39.4971 | 720.6615
| 202:34239 | 125 | 183.3453 | 53.81 | 1.4668 | 53.81 | 20116 | 16087 | 794090 | 2012-03-07 11:12 | 2012-03-07 12:00 | 48 | 11kV | 50986 | 1297 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S1193 Lindfield Panel 11 Tripped and reclosed on Leakage - EFI - Timing and Lockout. Alarms: 11kV Trip, Zone Earth and No2 Group Earth. 11KV end Box failure see OMS 795957/956/958 | March | 2012 | 2012Q3 | 2012 | ZN1193:PA11 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | UG | Not Veg | 2012-03-07 | N | 39.3107 | N | 8 | N | N | 1.1101 | 39.4971 | 37259.065
| 202:34240 | 912 | 1367.5811 | 50.92 | 1.4995 | 50.92 | 20136 | 16195 | 794156 | 2012-03-07 12:09 | 2012-03-07 13:20 | 71.2167 | 11kV | 18163.3 | 502 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788Pa11 fdr tripped on B instant EL See 794609,13,14 Exclude 794156 | March | 2012 | 2012Q3 | 2012 | ZN1788:PA11 | ZN35700:PA10 | ZN35700/000010 | RANDWICK | UG | Not Veg | 2012-03-07 | N | 36.1819 | N | 8 | N | N | 1.1101 | 39.4971 | 13273.2039
| 202:34245 | 1057 | 1534.9924 | 41.49 | 1.4522 | 41.49 | 20111 | 16077 | 794128 | 2012-03-07 11:34 | 2012-03-07 13:25 | 111 | 11kV | 1665 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 129963 C Phase DOLF : 10 Amp Excluded OMS 794128 OMS 794546 | March | 2012 | 2012Q3 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2012-03-07 | N | 111 | N | 8 | N | N | 1.1101 | 39.4971 | 1216.7329
| 202:34249 | 545 | 969.7977 | 45.82 | 1.7794 | 45.82 | 20333 | 19351 | 794251 | 2012-03-07 13:58 | 2012-03-07 14:44 | 46 | 11kV | 69598 | 1513 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa14 fdr tripped on relays:A&Cph IOC EFI Signals: 11kV trip ZE Tx4 GE EFI: CP491 S6574 S8695 S2870 Abnormal: SwB@S8695 Closed, SwA@S4556 Opened Cause: UG Fault btw S2870SwA to S4556SwB S4556 left de-energised untill both fdrs to sub is repaired. Phasing can't be checked due to N// to LV side. No custs connected to S4556. See 796231 exclude 794251,3,7,64,76 | March | 2012 | 2012Q3 | 2012 | ZN1788:PA14 | ZN1788:PA14 | ZN01788/000014 | RANDWICK | UG | Not Veg | 2012-03-07 | N | 46 | N | 8 | N | N | 1.1101 | 39.4971 | 50860.1656
| 202:34250 | 1119 | 876.0936 | 43.49 | 0.78293 | 43.49 | 20385 | 20001 | 794223 | 2012-03-07 13:47 | 2012-03-07 15:30 | 103 | 11kV | 6798 | 66 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kv feeder panel No3 "Canton beach" feeder at S12620 Noraville 11kv bond at LK 43613 middle phase burnt off | March | 2012 | 2012Q3 | 2012 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2012-03-07 | N | 103 | N | 8 | N | N | 1.1101 | 39.4971 | 4967.7779
| 202:34253 | 603 | 712.7177 | 41.92 | 1.182 | 41.92 | 18791 | 2068 | 794415 | 2012-03-07 19:55 | 2012-03-07 20:45 | 49.6333 | 11kV | 1687.5333 | 34 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | LID 129967 B Phase Car hit pole SI-80136. B Phase conductor sitting on x-arm. Isolated for repairs. | March | 2012 | 2012Q3 | 2012 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2012-03-07 | N | 49.6333 | N | 8 | N | N | 1.1101 | 39.4971 | 1233.1996
| 202:34254 | 2105 | 1997.8212 | 43.3 | 0.94908 | 43.3 | 20121 | 16119 | 794387 | 2012-03-07 17:27 | 2012-03-07 23:00 | 333 | 11kV | 66720 | 207 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 129971 4 fault operations Mains down adjacent GQ-47898 Excluded OMS 794387, 794455, 794750, 794758, 794759 OMS 795393, 795398, 795400, 795402 | March | 2012 | 2012Q3 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-03-07 | N | 322.3188 | N | 8 | N | N | 1.1101 | 39.4971 | 48757.0081
| 202:34256 | 953 | 886.2979 | 41.44 | 0.93001 | 41.44 | 18605 | 274 | 794460 | 2012-03-08 02:03 | 2012-03-08 03:15 | 72 | 11kV | 29898 | 440 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Suspect cable fault between zn711:Pa15 to S7527 to S7026 See 794726,9 exclude 794460 | March | 2012 | 2012Q3 | 2012 | ZN711:PA15 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2012-03-08 | N | 67.95 | N | 11 | N | N | 1.1101 | 39.4971 | 21848.5766
| 202:34259 | 394 | 680.8048 | 48.51 | 1.7279 | 48.51 | 19623 | 10427 | 794462 | 2012-03-08 03:27 | 2012-03-08 04:50 | 83 | 11kV | 77771 | 937 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn80 Chatswood Panel 25 tripped on B/C phase IOC, Timing, Lockout, Fault Check Cause: Tree on Mains in the vicinity of Hatfield and Mobray Rds. | March | 2012 | 2012Q3 | 2012 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2012-03-08 | N | 83 | N | 11 | N | N | 1.1101 | 39.4971 | 56832.7529
| 202:34260 | 2424 | 1258.7442 | 33.4 | 0.51928 | 33.4 | 18903 | 3142 | 794625 | 2012-03-08 09:40 | 2012-03-08 10:29 | 48.2167 | 11kV | 482.1667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129977 Single phase | March | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-03-08 | N | 48.2167 | N | 11 | N | N | 1.1101 | 39.4971 | 352.3532
| 202:34261 | 562 | 1163.2639 | 44.77 | 2.0699 | 44.77 | 19845 | 13203 | 794468 | 2012-03-08 05:27 | 2012-03-08 10:55 | 328 | 11kV | 20328 | 125 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Rain Light | N | At ZN167 Auburn: Pnl 2 "S.7794 Parramatta Dartbrook" Relays: Micom P122 type, IOC, EFI, Trip Signals: No.3 Tx Group earth, Protection trip At S544 Progress Rubber Tx1 Tripped on Diff Tx 3 tripped on Diff Field EFI's: S7794, S8353, S7561, S2377, S2766, S2749, S544 Cause of interruption: Transformer Failure Remarks: at S544 Progress Rubber high and LV pits full ofWater. Suppy to S544 restored via LV//, supply restored to S837 Duck short from S544 after busbar/Tx2 rts At ZN167 Auburn: Pnl 2 "S.7794 Parramatta Dartbrook" Relays: Micom P122 type, IOC, EFI, Trip Signals: No.3 Tx Group earth, Protection trip At S544 Progress Rubber Tx1 Tripped on Diff Tx 3 tripped on Diff Field EFI's: S7794, S8353, S7561, S2377, S2766, S2749, S544 Cause of interruption: Transformer Failure Remarks: at S544 Progress Rubber high and LV pits full ofWater. Suppy to S544 restored via LV//, supply restored to S837 Duck short from S544 after busbar/Tx2 rts Related jobs: #794538, 794468, 796031, 796025, 796035, 796033 | March | 2012 | 2012Q3 | 2012 | ZN167:PA2 | ZN167:PA2 | ZN00167/000002 | CUMBERLAND | OH | Not Veg | 2012-03-08 | N | 162.624 | N | 11 | N | N | 1.1101 | 39.4971 | 14855.1028
| 202:34262 | 1052 | 1596.2658 | 47.65 | 1.5174 | 47.65 | 19609 | 10288 | 794497 | 2012-03-08 10:57 | 2012-03-08 12:06 | 69 | 11kV | 6622 | 171 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | Zn384 Camperdown Pa8 fdr trippedon (flags on overcurrent relay) EFI Alarms 5kV trip ZE No4GE, 1 2 3 4 5 Tx no volts bettery defect EFI: S1306 S48306 S8985 Abnormal: S8985 Victoria Park SwB Closed and SwB Open Cause: not ascertained See seperate interruption Pa21 at BWB. Abnormal switching was due to report of water in S2497 Bosch Building (Details of this interruption are unclear as original interruption report was unclear) See 796294,5 exclude 794497,727 | March | 2012 | 2012Q3 | 2012 | ZN384:PA8 | ZN384:PA81 | ZN00384/000081 | SYDNEY | UG | Not Veg | 2012-03-08 | N | 38.7251 | N | 11 | N | N | 1.1101 | 39.4971 | 4839.1623
| 514:18137 | 241 | 393.3567 | 56.91 | 1.6322 | 56.91 | 19880 | 13576 | 794712 | 2012-03-08 09:47 | 2012-03-08 12:59 | 192 | 11kV | 297720 | 1587 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn711 Blackwattle Bay 5kV Pa21 fdr tripped on ABCPh O/C Abnormal: SwB Closed @ S8985 S2497 Bosch Building was flooding at time of interruption. See Separate Interruption on Pa8 @ Zn384 Camperdown Zone (Unsure why Pa8 at Camperdown did not trip at same time with this abnormal switching!!) Per SOp Shipp See 796299,302 exclude 794712 | March | 2012 | 2012Q3 | 2012 | ZN711:PA21 | ZN188:PA43 | ZN00188/000043 | SYDNEY | UG | Not Veg | 2012-03-08 | N | 187.5992 | N | 11 | N | N | 1.1101 | 39.4971 | 217564.9947
| 514:18141 | 7 | 86.6759 | 62.87 | 12.3823 | 62.87 | 19038 | 4284 | 794891 | 2012-03-08 13:41 | 2012-03-08 16:17 | 156 | 11kV | 6897 | 64 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.1648 Enfield P-13 "S.35902 Telopea Hume" Fdr tripped on: RELAYS: Translay and EFI SIGNALS: 11kV trip, Zone Earth and TX.3 GE REMARKS: UG Fault. 11kv UG fault from ZN.1648 Enfield P-13 to S.7815 Braidwood Hume. | March | 2012 | 2012Q3 | 2012 | ZN1648:PA13 | ZN4853:PA22 | ZN04853/000022 | STRATHFIELD | UG | Not Veg | 2012-03-08 | N | 107.7656 | N | 11 | N | N | 1.1101 | 39.4971 | 5040.1242
| 514:18156 | 4 | 0.32679 | 62.87 | 0.081698 | 62.87 | 20271 | 18080 | 794985 | 2012-03-08 16:07 | 2012-03-08 17:34 | 87 | 11kV | 15399 | 189 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S35335 Royal North Hospital Panel 14 Tripped on O/C and Earth Fault, EFI and Fault Check. Cause: UG fault between S3601 S3646 S4064. See OMS 796112 796113 794985 | March | 2012 | 2012Q3 | 2012 | ZN35335:PA14 | ZN35335:PA14 | ZN35335/000014 | LANE COVE | UG | Not Veg | 2012-03-08 | N | 81.4762 | N | 11 | N | N | 1.1101 | 39.4971 | 11253.135
| 514:18160 | 2 | 0.99339 | #N/A | 0.49669 | 39.4971 | 20054 | 15642 | 794988 | 2012-03-08 16:18 | 2012-03-08 17:42 | 83.7833 | 11kV | 82390.55 | 1000 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV P-3 (S.9876, S.9850 etc FDR ex Zn.9118 Cronulla 11kv FDR from Recloser 35260 Pacific Cres East to S.9510 Bonnie Vale Camping Area isolated by DOp to remove tree off 11kv OH FDR. This interrupted a section of 11kV 35260 Pacific Cres East to AB 35526 due to defective section of 11kV FDR beyond AB 35526. ABNORMAL: Recloser 35756 Bundeena open & defective with Recloser 35005 Bundeena Liverpool closed. REMARKS: Interrupted for Safety reasons by DOp to remove tree off 11kV mains. | March | 2012 | 2012Q3 | 2012 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2012-03-08 | N | 82.3906 | N | 11 | N | N | 1.1101 | 39.4971 | 60208.5838
| ZN15004:PA1 | 1728 | 1324.1665 | 37.02 | 0.7663 | 37.02 | 19117 | 4734 | 794797 | 2012-03-08 12:06 | 2012-03-08 18:20 | 374 | 11kV | 6389 | 95 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | At Zn3472 Sefton P32 (Rookwood Dasea etc) tripped on A/n instant OC Remarks: Pole defective/failure. Broken Cross arm near AB3290 repaired by mains Related jobs: #796543, 796541, 796542, 796540, 794797 | March | 2012 | 2012Q3 | 2012 | ZN3472:PA32 | ZN35900:PA6 | ZN35900/000006 | CUMBERLAND | OH | Not Veg | 2012-03-08 | N | 67.2526 | N | 11 | N | N | 1.1101 | 39.4971 | 4668.8928
| ZN15004:PA3 | 1375 | 1152.62 | 32.38 | 0.83827 | 32.38 | 20284 | 18280 | 795113 | 2012-03-08 23:19 | 2012-03-09 00:22 | 63 | 11kV | 52336 | 866 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 11kv Pa26 tripped on EF Fault Check EFI EFI: S7224 S8174 Suspected cable fault between S8174 & S8531 See 796356,8 exclude 795113 | March | 2012 | 2012Q3 | 2012 | ZN188:PA26 | ZN188:PA26 | ZN00188/000026 | SYDNEY | UG | Not Veg | 2012-03-08 | N | 60.4342 | N | 11 | N | N | 1.1101 | 39.4971 | 38245.6051
| ZN15004:PA5 | 1749 | 1745.5438 | 31.47 | 0.99802 | 31.47 | 20001 | 14935 | 795124 | 2012-03-09 03:01 | 2012-03-09 05:18 | 137 | 11kV | 139795 | 1264 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | Unselected | N | At Zn116 Leichhardt: 11kv Pnl 47 "Macauley Norton fdr" tripped on A phase IOC and earth leakage with efi signal. Field efi operated at S35209, S703, S1477, S8238, S668, S2029, S1594 Remarks: 11kv end box blown on sw/B at S2645 (N/O) Difficult access (private lock/chain) to S1504 and S8326. Require security company at S154 for access. Related jobs: #796606, 796605, 796604, 795124 | March | 2012 | 2012Q3 | 2012 | ZN116:PA47 | ZN116:PA19 | ZN00116/000019 | INNER WEST | UG | Not Veg | 2012-03-09 | N | 110.5973 | N | 7 | N | N | 1.1101 | 39.4971 | 102158.0627
| ZN15004:PA9 | 1588 | 1188.0182 | 36.55 | 0.74812 | 36.55 | 18649 | 720 | 795122 | 2012-03-09 02:31 | 2012-03-09 07:09 | 278 | 11kV | 209606 | 2908 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S80 Chatswood Panel 32 tripped on B and C phase overcurrent. Cause; Tree on Mains between LB1733 and AB1994 tee S2385. See OMS 796130 796131 796130/131/129/125/159 | March | 2012 | 2012Q3 | 2012 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Veg | 2012-03-09 | N | 72.0791 | N | 7 | N | N | 1.1101 | 39.4971 | 153173.8825
| ZN12620:PA1 | 2751 | 1792.3896 | 31.39 | 0.65154 | 31.39 | 19901 | 13754 | 795490 | 2012-03-09 16:30 | 2012-03-09 17:20 | 50 | 11kV | 700 | 14 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 129992 B Phase A truck was reported to have snapped a service wire at 1630hrs. W Morgan found the damaged service had "flicked up" within safe working clearances of the 11kV. Sub 2268 had a full interruption to remove the service. There was no sign of contact between the 11kV and LV. No protection operation. Excluded OMS 795490 OMS 795966 | March | 2012 | 2012Q3 | 2012 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2012-03-09 | N | 50 | N | 7 | N | N | 1.1101 | 39.4971 | 511.5394
| ZN12620:PA10 | 1143 | 913.3581 | 36.4 | 0.79909 | 36.4 | 18935 | 3374 | 795496 | 2012-03-09 16:44 | 2012-03-09 18:15 | 91 | 11kV | 1820 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.12458 Pacific Cheero PT 1.1 - 20 Amp Roadside HDO operated (batch 2576 ABB) Fatigued fuse replaced | March | 2012 | 2012Q3 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-03-09 | N | 91 | N | 7 | N | N | 1.1101 | 39.4971 | 1330.0023
| ZN12620:PA11 | 1669 | 1346.9233 | 36.02 | 0.80702 | 36.02 | 19772 | 12545 | 795508 | 2012-03-09 17:02 | 2012-03-09 18:50 | 108 | 11kV | 108 | 1 | HV | Animal Other | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 129993 single phase Small burnt goanna found at base of pole. Excluded OMS 795508 OMS 795992 | March | 2012 | 2012Q3 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2012-03-09 | N | 108 | N | 7 | N | N | 1.1101 | 39.4971 | 78.9232
| ZN12620:PA13 | 394 | 303.6931 | 35.57 | 0.77079 | 35.57 | 19333 | 7553 | 795483 | 2012-03-09 16:21 | 2012-03-09 20:35 | 254 | 11kV | 254 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 129994 B Phase Burnt connection (tapping) at pole 9M-90017 on tee to sub 70463 leaving sub 70463 on two phases. No protection operated. Connection repaired and volts ok. Excluded OMS (heirarchy) 795483 OMS 795981 | March | 2012 | 2012Q3 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2012-03-09 | N | 254 | N | 7 | N | N | 1.1101 | 39.4971 | 185.6157
| ZN12620:PA2 | 515 | 348.8517 | 32.4 | 0.67738 | 32.4 | 20247 | 17743 | 795574 | 2012-03-09 22:05 | 2012-03-09 23:33 | 88 | 11kV | 56190 | 744 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 129995 2 fault operations C phase Overcurrent Excluded OMS 795574 OMS 796066, 796068, 796072, 796074, 796075 | March | 2012 | 2012Q3 | 2012 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2012-03-09 | N | 75.5242 | N | 7 | N | N | 1.1101 | 39.4971 | 41061.9947
| ZN12620:PA3 | 1121 | 908.0258 | 38.45 | 0.81001 | 38.45 | 19973 | 14648 | 795651 | 2012-03-10 13:55 | 2012-03-10 14:51 | 56 | 11kV | 4704 | 84 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | section of Pa19 ex S129 Hunters Hill PT2227 interrupted by DOp too remove large tree. See OMS 795701 795651 795675 | March | 2012 | 2012Q3 | 2012 | ZN129:PA19 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Veg | 2012-03-10 | N | 56 | N | 6 | N | N | 1.1101 | 39.4971 | 3437.5445
| ZN12620:PA7 | 2208 | 1703.4049 | 36.78 | 0.77147 | 36.78 | 20402 | 20156 | 795719 | 2012-03-10 14:45 | 2012-03-10 17:50 | 185 | 11kV | 2035 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120000 Isolated for emergency repair, wire off insulator on pole KQ-40068. Excluded OMS 795719 OMS 796022 | March | 2012 | 2012Q3 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-03-10 | N | 185 | N | 6 | N | N | 1.1101 | 39.4971 | 1487.118
| ZN12620:PA8 | 1271 | 1054.6375 | 34.01 | 0.82977 | 34.01 | 19469 | 8858 | 795639 | 2012-03-10 10:31 | 2012-03-10 18:40 | 489 | 11kV | 35809 | 181 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120007 2 fault operation 3 phase Overcurrent wire down at pole mn82209 Excluded OMS 795639, 795644, 795652, 795681, 795694, 795695, 795704 OMS 796241, 796245 | March | 2012 | 2012Q3 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-03-10 | N | 197.8398 | N | 6 | N | N | 1.1101 | 39.4971 | 26168.161
| ZN15015:PA15 | 640 | 586.3608 | 37.67 | 0.91619 | 37.67 | 19953 | 14281 | 795735 | 2012-03-10 16:35 | 2012-03-10 19:40 | 185 | 11kV | 4255 | 23 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 120008 3 phase interupted to replace pole falling it21706 oms 795735 & 795751 OMS 796234 | March | 2012 | 2012Q3 | 2012 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2012-03-10 | N | 185 | N | 6 | N | N | 1.1101 | 39.4971 | 3109.4285
| ZN15015:PA5 | 1624 | 1088.1456 | 34.8 | 0.67004 | 34.8 | 20371 | 19908 | 795752 | 2012-03-10 18:00 | 2012-03-10 20:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120009 C phase DOLF : 10 Amp Excluded OMS 795752 OMS 796152 | March | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-03-10 | N | 120 | N | 6 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN35400:PA101 | 1856 | 1463.7252 | 44.54 | 0.78865 | 44.54 | 19975 | 14657 | 795775 | 2012-03-10 21:09 | 2012-03-10 21:40 | 31 | 11kV | 64077 | 2067 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | At ZN.9037 Miranda P-8 "Alkaringa Rd" fdr tripped & reclosed, and locked out on. RELAYS: C phase IOC, EFI, Lockout, Timing SIGNALS: FIELD EFIs: S.9521, S.9292 ABNORMAL: SW/B at S.9494 Attunga Coolum closed and AB 35894 open & defective REMARKS: Anilmals/Birds. Possum on HV at PT.9427 Maroopna. | March | 2012 | 2012Q3 | 2012 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2012-03-10 | N | 31 | N | 6 | N | N | 1.1101 | 39.4971 | 46825.5816
| ZN35400:PA102 | 164 | 689.7053 | 50.35 | 4.2055 | 50.35 | 19037 | 4283 | 795873 | 2012-03-11 13:19 | 2012-03-11 14:00 | 41 | 11kV | 328 | 8 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 120010 B phase DOLF : 20 Amp dead birds Excluded OMS - incorrect sub - 795873 OMS 796282 (school sub) | March | 2012 | 2012Q3 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-03-11 | N | 41 | N | 3 | N | N | 1.1101 | 39.4971 | 239.6927
| ZN35400:PA103 | 158 | 237.2001 | #N/A | 1.5013 | 39.4971 | 19645 | 10738 | 795923 | 2012-03-11 20:27 | 2012-03-11 21:45 | 78 | 11kV | 390 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.12723 Mandalong Dick 0.8 - B phase HV 16Amo fuse blown HV fuse fatigue | March | 2012 | 2012Q3 | 2012 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2012-03-11 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 285.0005
| ZN35400:PA106 | 86 | 580.6122 | #N/A | 6.7513 | 39.4971 | 19292 | 7312 | 795924 | 2012-03-11 20:39 | 2012-03-11 23:06 | 146.8 | 11kV | 47858.9 | 496 | HV | Animal Flying Fox | Animal | DC-PT Transformer | Unplanned | Unselected | N | At ZN.9550 Gwawley Bay P-35 "Port Hacking Box #3" fdr tripped on: SIGNALS: 11kV Trip, Zone Earth, TX.1 grp Eth RELAYS: Earth Fault, EFI EFIs: S.9370 REMARKS: Bat contcated HV mains at PT.9519 Goodacre Av and stayed on HV equipment. Bat still alive so left 11kV FDR from SW/B at S.9370 Port hacking Box #3 to SW/A at S.9278 Gwawley Pde Tee PT.9159 isolated in LV //. | March | 2012 | 2012Q3 | 2012 | ZN9550:PA35 | ZN9550:PA9 | ZN09550/000009 | SUTHERLAND | OH | Not Veg | 2012-03-11 | N | 96.4897 | N | 3 | N | N | 1.1101 | 39.4971 | 34973.8725
| ZN35400:PA109 | 48 | 218.8309 | #N/A | 4.559 | 39.4971 | 19243 | 6478 | 796034 | 2012-03-12 08:09 | 2012-03-12 14:00 | 351 | 11kV | 94086 | 664 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Wamberal Zn Pnl.10 tripped on Earth Fault with EFI. Field EFI @ S.18824. OH down - 11kv on ground near AB45403. During the procedure of restoring P.10, Recloser 44607 Matcham North was opened via the WSOS program & indicated Open in the recloser window. It was also checked in the field by the DOp where it was showing open. However after a customer report to the DOp that the wires that had fallen were still jumping around intermittently the AB45403 was opened to isolate fallen wires. REC was tested on energising and still alive on 3 phases - defective, isolated and by-passed. | March | 2012 | 2012Q3 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2012-03-12 | N | 141.6958 | N | 1 | N | N | 1.1101 | 39.4971 | 68755.2737
| ZN35400:PA110 | 1885 | 1367.64 | 36.64 | 0.72554 | 36.64 | 19716 | 11961 | 796457 | 2012-03-13 01:30 | 2012-03-13 03:20 | 110 | 11kV | 11990 | 109 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120016 C Phase DOLF : 20 Amp No supply reported by HWC technician. Found DOLF down, probable fatigued fuse no fault found. | March | 2012 | 2012Q3 | 2012 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2012-03-13 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 8761.9384
| ZN35400:PA51 | 18 | 85.1851 | #N/A | 4.7325 | 39.4971 | 18699 | 1154 | 796757 | 2012-03-13 14:32 | 2012-03-13 15:45 | 72.8167 | 11kV | 107477.4 | 1476 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex P-7 "Terry Princes etc" FDR at ZN.10990 Arncliffe. 11kV roadside phase burnt at AB 31283 REMARKS: ABS - details below roadside phase burnt CC1: 22-"Refer to SOp" | March | 2012 | 2012Q3 | 2012 | ZN10990:PA7 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Not Veg | 2012-03-13 | N | 72.8167 | N | 2 | N | N | 1.1101 | 39.4971 | 78541.3139
| ZN35400:PA52 | 1975 | 1246.1598 | 34.6 | 0.63097 | 34.6 | 20076 | 15813 | 797289 | 2012-03-14 15:25 | 2012-03-14 17:00 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | DOLF replaced ( OMS job 797289 Excluded ) | March | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-03-14 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 69.4232
| ZN35400:PA53 | 608 | 366.3128 | #N/A | 0.60249 | 39.4971 | 19579 | 9730 | 797344 | 2012-03-14 14:26 | 2012-03-14 18:00 | 214 | 11kV | 4280 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120038 A phase DOLF :16 Amp. VOLTS =245 LOAD A=60 B = 72 C = 100.FUSE FATIGUE. A Phase DOLF fatigued , OMS REPORT NO 797344. | March | 2012 | 2012Q3 | 2012 | 501:48118 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2012-03-14 | N | 214 | N | 3 | N | N | 1.1101 | 39.4971 | 3127.6978
| ZN35400:PA56 | 174 | 557.7738 | #N/A | 3.2056 | 39.4971 | 20031 | 15361 | 797399 | 2012-03-14 21:05 | 2012-03-14 23:56 | 170.7167 | 11kV | 439590.3833 | 3665 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2602 Pa30 fdr tripped Relays: EF Fault Check EFI Singals: 11kv trip ZE Tx4 GE EFI: S46847 S8981 S2132 S8570 S3928 S8851 S4017 Abnormal: SwAS182 Clsoed "Telecom Botany Birrell" fdr S353 Open "Donald Birrell" fdr S353 Open Cause: 11kV UG Fault From S4017 to S3359 to S182 S1374-Dist1 in LV// at time. UGOH tail failed when Zn2602:Pa30 tripped See 797991,2,3,8027 exclude 797399,402,4,10,9,20,3 | March | 2012 | 2012Q3 | 2012 | ZN2602:PA30 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2012-03-14 | N | 119.9428 | N | 3 | N | N | 1.1101 | 39.4971 | 321239.6864
| ZN35400:PA59 | 109 | 839.9858 | #N/A | 7.7063 | 39.4971 | 19729 | 12044 | 797483 | 2012-03-15 09:09 | 2012-03-15 09:44 | 35 | 11kV | 52920 | 1512 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa14 CP491 fdr tripped on : Earth Leakage EFI EFI: CP491 S6574 S8695 S2870 Abnormal: S8695SwB Closed, S4556SwB Open, NB fontline fdr fault on Pa11 at Matraville Zone Cause: UG cable fault frokm S7870 to S4556. NB S4556 Interrupted due to fault on Pa11 at Matraville See DMA See 798101 exclude 797483 | March | 2012 | 2012Q3 | 2012 | ZN1788:PA14 | ZN1788:PA14 | ZN01788/000014 | RANDWICK | UG | Not Veg | 2012-03-15 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 38672.3751
| ZN35400:PA60 | 16 | 77.4593 | #N/A | 4.8412 | 39.4971 | 19923 | 14029 | 797847 | 2012-03-15 19:58 | 2012-03-15 20:55 | 57 | 11kV | 62760 | 1305 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At Zn129 Hunters Hill Panel 10 tripped on Earth Fault and Fault Check with EFI signal. Cause: Possum on UGOH at S5739 Parry Charles. See OMS 799233 799235 799848 | March | 2012 | 2012Q3 | 2012 | ZN129:PA10 | ZN129:PA49 | ZN00129/000049 | RYDE | OH | Not Veg | 2012-03-15 | N | 48.092 | N | 4 | N | N | 1.1101 | 39.4971 | 45863.1569
| ZN35400:PA61 | 307 | 540.2445 | #N/A | 1.7598 | 39.4971 | 19020 | 4196 | 797872 | 2012-03-15 23:32 | 2012-03-16 01:25 | 113 | 11kV | 31302 | 525 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S35500 Top Ryde Panel 32 Tripped on 50TABC, EFI, Cause: 11kV Cable fault between SWB at S8911 and Sw At S8532 See OMS 799346 799348 799354 797872 | March | 2012 | 2012Q3 | 2012 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2012-03-15 | N | 59.6229 | N | 4 | N | N | 1.1101 | 39.4971 | 22874.5783
| ZN35400:PA62 | 133 | 662.7566 | #N/A | 4.9831 | 39.4971 | 18906 | 3176 | 797871 | 2012-03-15 23:36 | 2012-03-16 02:31 | 175 | 11kV | 1400 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120051 Excluded OMS 797871 OMS 7978899 | March | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-03-15 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 1023.0787
| ZN35400:PA64 | 387 | 861.5514 | #N/A | 2.2262 | 39.4971 | 19493 | 9036 | 797893 | 2012-03-16 07:35 | 2012-03-16 10:10 | 155 | 11kV | 169151 | 1734 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12660 Woy Woy Pnl.10 tripped on B phase Earth Faut EFI down @ S.12696 & 12617 Suspect HV UG fault between S.12617 & LB49686 & S.12618 See OMS # 800041 800038 800039 | March | 2012 | 2012Q3 | 2012 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | UG | Not Veg | 2012-03-16 | N | 97.5496 | N | 5 | N | N | 1.1101 | 39.4971 | 123610.5617
| ZN35400:PA67 | 104 | 510.6632 | #N/A | 4.9102 | 39.4971 | 19367 | 7918 | 797879 | 2012-03-16 06:41 | 2012-03-16 11:45 | 304 | 11kV | 244576 | 1966 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 120060 2 Fault operations 3 Phase Earth fault ,overcurrent bird on pole ju 25612 cnr christo rd and hexham st new lambton. This is a tee off pole bird flashed across tee to main line, please investigate clearances Excluded oms 797928, 797929, 797930, 797927, 797879. OMS 798996,798995,798994,798993, | March | 2012 | 2012Q3 | 2012 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2012-03-16 | N | 124.4028 | N | 5 | N | N | 1.1101 | 39.4971 | 178728.927
| ZN35400:PA68 | 434 | 928.5074 | 42.27 | 2.1394 | 42.27 | 19684 | 11358 | 797963 | 2012-03-16 13:01 | 2012-03-16 13:55 | 54 | 11kV | 216 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120065 Section of 11kV fdr isolated to repair stranding conductors at pole FN-20002. Excluded OMS 797963 OMS 798964 | March | 2012 | 2012Q3 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-03-16 | N | 54 | N | 5 | N | N | 1.1101 | 39.4971 | 157.8464
| ZN35400:PA71 | 542 | 521.4087 | #N/A | 0.96201 | 39.4971 | 18972 | 3601 | 798533 | 2012-03-16 20:39 | 2012-03-16 21:40 | 61 | 11kV | 84674 | 1614 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | See 799039,40,1 Exclude 798533 Zn269 WAverley Pa16 fdr tripped on Relays- Translay EFI Signals - 11kV trip Ze Tx3 GE S339 Glenayr ave - Translay Remarks: UG cable fault from Pa16 to S339 tee to Tx2@S339 to S6942 to S977 See 799039,40 Exclude 798533 | March | 2012 | 2012Q3 | 2012 | ZN269:PA16 | ZN36800:PA33 | ZN36800/000033 | WAVERLEY | UG | Not Veg | 2012-03-16 | N | 52.4622 | N | 5 | N | N | 1.1101 | 39.4971 | 61877.2617
| ZN35400:PA72 | 268 | 440.9976 | #N/A | 1.6455 | 39.4971 | 19727 | 12033 | 798552 | 2012-03-16 23:55 | 2012-03-17 01:24 | 89 | 11kV | 118370 | 1330 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | At S1193 Lindfield Panel 16 Tripped on A and C phase IOC EFI and Lockout relay. Cause: Cables Twisted together Cnr Stanhope and Kardella Ave | March | 2012 | 2012Q3 | 2012 | ZN1193:PA16 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2012-03-16 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 86501.3047
| ZN35400:PA73 | 1191 | 1196.1148 | 44.73 | 1.0043 | 44.73 | 19983 | 14869 | 798564 | 2012-03-17 02:47 | 2012-03-17 04:05 | 78 | 11kV | 150354 | 2143 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S1068 Lidcombe Panel 12 "Percy Boorea" tripped on: A phase O/C & Earth Leakage EFI. Field EFI's S6550, S7343, S7011 Remarks: UG Fault. UG fault assumed. S7011 to S3460 to S1867 Related jobs: #800018,800016,800013, 798564 | March | 2012 | 2012Q3 | 2012 | ZN1068:PA12 | ZN167:PA13 | ZN00167/000013 | CUMBERLAND | UG | Not Veg | 2012-03-17 | N | 70.1605 | N | 7 | N | N | 1.1101 | 39.4971 | 109874.2685
| ZN35400:PA77 | 516 | 680.8363 | #N/A | 1.3195 | 39.4971 | 20154 | 16360 | 798571 | 2012-03-17 06:25 | 2012-03-17 07:40 | 75 | 11kV | 6300 | 84 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Rain Light | N | LID120070 oms-798571. Possum B phase 40 Amp DOLF Excluded job 798571 OMS 799029 | March | 2012 | 2012Q3 | 2012 | 210:8682 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Not Veg | 2012-03-17 | N | 75 | N | 7 | N | N | 1.1101 | 39.4971 | 4603.8542
| ZN35400:PA79 | 1029 | 1330.4558 | #N/A | 1.293 | 39.4971 | 19520 | 9188 | 798569 | 2012-03-17 05:48 | 2012-03-17 09:59 | 251 | 11kV | 17128 | 120 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 120069 4 fault operation C phase Overcurrent B & C Phase Wire sitting on x-arm of Pole 8M-30512. Excluded OMS 798569, 798596, 798584 OMS 799223, 799224 | March | 2012 | 2012Q3 | 2012 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2012-03-17 | N | 142.7333 | N | 7 | N | N | 1.1101 | 39.4971 | 12516.6372
| ZN35400:PA80 | 78 | 607.0753 | #N/A | 7.783 | 39.4971 | 20231 | 17395 | 798633 | 2012-03-17 09:09 | 2012-03-17 11:10 | 121 | 11kV | 121 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 120072 Single phase DOLF : 3 Amp Replaced both Excluded OMS 798633 (heirarchy) OMS 799160 | March | 2012 | 2012Q3 | 2012 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2012-03-17 | N | 121 | N | 7 | N | N | 1.1101 | 39.4971 | 88.4232
| ZN35400:PA81 | 2119 | 1721.2234 | 39.58 | 0.81228 | 39.58 | 19545 | 9563 | 798682 | 2012-03-17 10:52 | 2012-03-17 11:40 | 48 | 11kV | 48 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 120073 A phase DOLF : Excluded OMS 798682 (heirarchy) OMS 799152 | March | 2012 | 2012Q3 | 2012 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2012-03-17 | N | 48 | N | 7 | N | N | 1.1101 | 39.4971 | 35.077
| ZN35400:PA82 | 823 | 1802.7171 | 54.34 | 2.1904 | 54.34 | 19658 | 10969 | 798774 | 2012-03-17 18:39 | 2012-03-18 01:00 | 381 | 11kV | 27470 | 261 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 120075 3 fault operations CAR HIT POLE AK-40010 Wybong Rd section isolated to repair mains. Excluded OMS 798774 & 798776 OMS 799243, 799245 | March | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2012-03-17 | N | 105.249 | N | 7 | N | N | 1.1101 | 39.4971 | 20074.2658
| ZN35400:PA83 | 303 | 734.0925 | 48.26 | 2.4227 | 48.26 | 20005 | 14970 | 798795 | 2012-03-17 23:36 | 2012-03-18 01:04 | 88 | 11kV | 66044 | 1030 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Erina Zn Pnl.16 tripped on A & B phase Overcurrent - EFI (field EFi @ S.14330) Abnormal Switching: USL 42506 Open & Defective - REC 44986 Closed Cause not ascertained OMS # 800086 800087 800085 800089 800090 | March | 2012 | 2012Q3 | 2012 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-03-17 | N | 64.1204 | N | 7 | N | N | 1.1101 | 39.4971 | 48263.0072
| ZN35400:PA85 | 302 | 492.1722 | #N/A | 1.6297 | 39.4971 | 20261 | 17975 | 798818 | 2012-03-18 08:07 | 2012-03-18 15:00 | 413 | 11kV | 6302 | 37 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 120080 1 fault operation Crossarm Broken at Pole AJ- 80012. Protection Flags required. Excluded OMS 798818, 799263, 799266, 799275 | March | 2012 | 2012Q3 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2012-03-18 | N | 170.3243 | N | 2 | N | N | 1.1101 | 39.4971 | 4605.3157
| ZN35400:PA86 | 2 | 577.2417 | #N/A | 288.6208 | 39.4971 | 18817 | 2269 | 798935 | 2012-03-18 20:54 | 2012-03-18 22:45 | 111 | 11kV | 40437 | 436 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S35500 Top Ryde Panel 23 Tripped on earth fault with fault check and efi. Cause: Suspect UG cable fault between S7572 and S5838. See OMS 799284/285/307/309 797872//935/937/940 | March | 2012 | 2012Q3 | 2012 | ZN35500:PA23 | ZN35500:PA23 | ZN35500/000023 | RYDE | UG | Not Veg | 2012-03-18 | N | 92.7454 | N | 2 | N | N | 1.1101 | 39.4971 | 29550.1669
| ZN35400:PA88 | 422 | 915.5899 | 52.29 | 2.1696 | 52.29 | 20399 | 20107 | 798955 | 2012-03-19 06:49 | 2012-03-19 09:00 | 131.5 | 11kV | 3682 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120084 A & B phase DOLF : 20 Amp | March | 2012 | 2012Q3 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2012-03-19 | N | 131.5 | N | 6 | N | N | 1.1101 | 39.4971 | 2690.697
| ZN35400:PA89 | 149 | 591.8516 | #N/A | 3.9722 | 39.4971 | 19503 | 9094 | 799043 | 2012-03-19 09:37 | 2012-03-19 11:40 | 123 | 11kV | 87870 | 1934 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Rain Light | N | At ZN.10993 Hurstville North P-5 (Lyle St fdr) tripped & reclosed on: Relays: B phase earth fault, SEL relay, timing relays, Lockout, EFI. Field EFIs: N/A Signals: 11kV trip, TX.1 Grp Eth REMARKS: crane hit OH. Building site crane hit 11kV mains and brought mains down. Sit eis 11 Mashman St, Kingsgrove. Crane driver is Charlie Jabbour 0414 443 388 Buildform Construction Group. | March | 2012 | 2012Q3 | 2012 | ZN10993:PA5 | ZN10993:PA23 | ZN10993/000023 | BAYSIDE | OH | Not Veg | 2012-03-19 | N | 45.4343 | N | 6 | N | N | 1.1101 | 39.4971 | 64212.8043
| ZN35400:PA90 | 21 | 61.5877 | #N/A | 2.9327 | 39.4971 | 18946 | 3468 | 799094 | 2012-03-19 10:24 | 2012-03-19 13:10 | 166 | 11kV | 166 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120090 single phase DOLF : 10 Amp. Sub dolf also blown at sub 71242. Excluded OMS 799094 OMS 799600 | March | 2012 | 2012Q3 | 2012 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2012-03-19 | N | 166 | N | 6 | N | N | 1.1101 | 39.4971 | 121.3079
| ZN35400:PA94 | 36 | 326.6491 | #N/A | 9.0736 | 39.4971 | 19070 | 4465 | 799071 | 2012-03-19 10:01 | 2012-03-19 13:35 | 214 | 11kV | 41762 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 120088 3 fault operations 3 phase Earth fault Tree brought down mains at pole GW-57001. Excluded OMS 799071, 799077, 799082, 799086, 799174, 799179, 799211 OMS 799552, 799553 | March | 2012 | 2012Q3 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-03-19 | N | 131.7413 | N | 6 | N | N | 1.1101 | 39.4971 | 30518.4378
| ZN35400:PA95 | 673 | 858.0158 | 42.04 | 1.2749 | 42.04 | 19374 | 8005 | 799518 | 2012-03-19 22:32 | 2012-03-19 23:30 | 58 | 11kV | 33652 | 592 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S35500 Top Ryde Panel 18 tripped on Earth Fault, EFI, Fault Check and U/F Cause: 11kV feeder from S35500 Top Ryde to SW/A at S5352 failed. See OMS 799744 799520 799518 | March | 2012 | 2012Q3 | 2012 | ZN35500:PA18 | ZN35500:PA18 | ZN35500/000018 | RYDE | UG | Not Veg | 2012-03-19 | N | 56.8446 | N | 6 | N | N | 1.1101 | 39.4971 | 24591.889
| ZN35400:PA97 | 390 | 383.7784 | 46.15 | 0.98405 | 46.15 | 20193 | 16850 | 799527 | 2012-03-20 00:50 | 2012-03-20 02:55 | 125 | 11kV | 147213 | 1332 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S2400 Berowra Panel 22 tripped on O/C, E/F, EFI and Fault Check. OMS 799818 799819 799821 799822 See OMS 799818 799819 799821 799822 | March | 2012 | 2012Q3 | 2012 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2012-03-20 | N | 110.5203 | N | 3 | N | N | 1.1101 | 39.4971 | 107578.9184
| 524:33570 | 1361 | 1179.1492 | 39.93 | 0.86638 | 39.93 | 20370 | 19903 | 799521 | 2012-03-19 22:31 | 2012-03-20 11:16 | 765 | 11kV | 21420 | 28 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120094 3 fault operations Main down 5 span from RAGCB. Repairs to be complete in daylght | March | 2012 | 2012Q3 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2012-03-19 | N | 765 | N | 6 | N | N | 1.1101 | 39.4971 | 15653.1042
| 524:33572 | 572 | 1686.5084 | 37.87 | 2.9484 | 37.87 | 20038 | 15468 | 795454 | 2012-03-07 14:44 | 2012-03-20 12:30 | 18586 | 11kV | 18586 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | 7/3/12 12:09 Zn1788 Matraville Pa11 fdr tripped. UG cable fault btw Pa11 to S4556 to S6192 to S8708 to S6789 12:42 S4556 backfed from Pa14 13:58 Pa14 fdr tripped. UG cable fault btw S2870 to S4556. S4556 no supply due to UG faults on both sides of HV RMI and no parallel to LV side. Control room was advised cust moved out prior to outages. Only 1 NMI from S4556. | March | 2012 | 2012Q3 | 2012 |  |  |  |  | UG | Not Veg | 2012-03-07 | N | 18586 | N | 8 | N | N | 1.1101 | 39.4971 | 13582.1006
| 524:33574 | 64 | 72.7524 | 29.31 | 1.1368 | 29.31 | 20013 | 15029 | 799794 | 2012-03-20 13:06 | 2012-03-20 15:41 | 154.5333 | 11kV | 54134.7833 | 532 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120101 2 fault operation A & C phase Overcurrent, Instantaneous Overcurrent RAGCB 42067 closed at 1522hrs RAGCB 47688 closed at 1526hrs PLEASE PATROL FEEDER Excluded OMS 799789, 799794, 799803, 799807, 799809, 799810, 799812, 799831 OMS 800066, 800070, 800071, 800072, 800074, 800075, 800076 | March | 2012 | 2012Q3 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2012-03-20 | N | 101.7571 | N | 3 | N | N | 1.1101 | 39.4971 | 39560.103
| 524:33576 | 180 | 417.3768 | 41.35 | 2.3188 | 41.35 | 19455 | 8744 | 799860 | 2012-03-20 15:12 | 2012-03-20 18:15 | 183 | 11kV | 366 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120103 B phase DOLF : 10 Amp. Fuse Fatigue Excluded OMS 799860 OMS 799990 | March | 2012 | 2012Q3 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2012-03-20 | N | 183 | N | 3 | N | N | 1.1101 | 39.4971 | 267.462
| 524:33578 | 1301 | 1557.9602 | 35.62 | 1.1975 | 35.62 | 19593 | 9812 | 799978 | 2012-03-21 06:06 | 2012-03-21 09:15 | 189 | 11kV | 43915 | 275 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | Section of P16 Victoria Sydenham fdr from S5130 Railway Croydon via S5661 Palace Croydon to S8521 Fort Palace to S3121 Searle St Remarks: Vehcile hit kiosk. 19 Palace St Petersham. Interrupted by dop for safety Related jobs: #801001, 800006, 799978, 801183, 801184, 800997, 801003, 800990, 800989 | March | 2012 | 2012Q3 | 2012 | ZN262:PA16 | ZN262:PA16 | ZN00262/000016 | INNER WEST | Unknown | Not Veg | 2012-03-21 | N | 159.6909 | N | 5 | N | N | 1.1101 | 39.4971 | 32091.7867
| 524:33580 | 134 | 595.0516 | 44.33 | 4.4407 | 44.33 | 18953 | 3484 | 800022 | 2012-03-21 09:20 | 2012-03-21 10:15 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120107 A phase DOLF : 10 Amp Excluded OMS 800022 OMS 800457 | March | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-03-21 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 40.1924
| ZN36000:PA1 | 48 | 1770.1336 | #N/A | 36.8778 | 39.4971 | 18620 | 383 | 800115 | 2012-03-21 11:09 | 2012-03-21 11:45 | 36 | 11kV | 288 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120108 Single phase Repair stranding conductor | March | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-03-21 | N | 36 | N | 5 | N | N | 1.1101 | 39.4971 | 210.4619
| ZN36000:PA10 | 456 | 511.793 | 41.85 | 1.1224 | 41.85 | 19787 | 12684 | 800183 | 2012-03-21 13:41 | 2012-03-21 15:00 | 79 | 11kV | 74815 | 1705 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | AT S 2196 MILPERRA PANEL 25 TURVEY RIVER FEEDER TRIPPED ON (ELECTRONIC RELAY) A PHASE O/C NO EFI Remarks: TREE ON MAINS 13 BANKS ST MILPERA Related jobs: #800183, 800205, 800206, 800939, 800935, 801122 | March | 2012 | 2012Q3 | 2012 | ZN2196:PA25 | ZN2196:PA25 | ZN02196/000025 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-03-21 | N | 43.8798 | N | 5 | N | N | 1.1101 | 39.4971 | 54672.5953
| ZN36000:PA12 | 226 | 1100.4977 | 40.64 | 4.8695 | 40.64 | 19775 | 12570 | 800391 | 2012-03-22 01:31 | 2012-03-22 02:13 | 42 | 11kV | 113324 | 20172 | HV | Animal Possum | Animal | Busbar | Unplanned | Unselected | N | At Sydney East 9E4 Feeder CB tripped on IT Recieve No1 and No2 Protn. At S3425 Castle Cove 1B and 2B 11kV CBs opened, 4B auto closed, No1 Fault thrower closed. Relays: Tx2 A phase differential, TR3,4,6 Signals 132kV Trip, Battery Defect, No1,2,3 and 4 Tx No Volts At S180 Mosman 3A and 4A 11kV CB's opened 1A and 2A auto Closed. Cause: Possum on 11kV TX Busbar on No2 Tx Castle Cove See OMS 801705 701715 701714 701683 | March | 2012 | 2012Q3 | 2012 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | WILLOUGHBY | OH | Not Veg | 2012-03-22 | N | 5.6179 | N | 5 | N | N | 1.1101 | 39.4971 | 82813.8367
| ZN36000:PA17 | 3 | 42.2419 | #N/A | 14.0806 | 39.4971 | 18702 | 1177 | 800389 | 2012-03-22 01:22 | 2012-03-22 02:47 | 85 | 11kV | 16575 | 195 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S129 Hunters Hill Panel 27 Tripped Relays - C phase IOC and Overcurrent, EFI. Signals:11kV Trip, Zone Earth, Group Earth. Cause: DOp patrolled feeder but could not find anything | March | 2012 | 2012Q3 | 2012 | ZN129:PA27 | ZN129:PA51 | ZN00129/000051 | HUNTERS HILL | OH | Veg | 2012-03-22 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 12112.5211
| ZN36000:PA19 | 9 | 504.3167 | #N/A | 56.0352 | 39.4971 | 19699 | 11624 | 800415 | 2012-03-22 05:14 | 2012-03-22 09:25 | 251 | 11kV | 102221 | 1170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.10999 Kogarah P-16 "Jubilee Park" 11kV fdr tripped, reclosed, tripped and reclosed on: RELAYS: Basler 1.2.1 target, 50TBC, EFI SIGNALS: 11kV Trip, Zone Earth, Group Earth EFIs: S.10844, S.10983 REMARKS: Tree/branch on OH mains. Tree on 11kV near UGOH to S.10277 Princes Jubilee. Oatley mains on site to repair. | March | 2012 | 2012Q3 | 2012 | ZN10999:PA16 | ZN10999:PA16 | ZN10999/000016 | GEORGES RIVER | OH | Veg | 2012-03-22 | N | 87.3684 | N | 5 | N | N | 1.1101 | 39.4971 | 74700.0918
| ZN36000:PA2 | 479 | 628.7929 | 42.69 | 1.3127 | 42.69 | 18618 | 381 | 800371 | 2012-03-21 19:29 | 2012-03-22 10:00 | 871 | 11kV | 5292 | 8 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa5 fdr tripped Relays: OC relay trip EFI Signals: 11kV trip Tx5GE & ZE EFI: Nil Abnormal:S7639SwA closed S6192SwB Cause: 11kv fdr UG fault from Pa5 to S5931 to S7424 to S7639 failed See 801835,7,8 exclude 800371,5 | March | 2012 | 2012Q3 | 2012 | ZN1788:PA11 | ZN35700:PA10 | ZN35700/000010 | RANDWICK | UG | Not Veg | 2012-03-21 | N | 661.5 | N | 5 | N | N | 1.1101 | 39.4971 | 3867.2375
| ZN36000:PA22 | 14 | 86.1904 | #N/A | 6.1565 | 39.4971 | 18629 | 471 | 800405 | 2012-03-22 03:33 | 2012-03-22 10:30 | 417.2 | 11kV | 22111.6 | 53 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Sub 1504 PWD B phase HV Fuse blown (25A) Remarks: OH Down Possible grading issue or HV fuse fatigue | March | 2012 | 2012Q3 | 2012 | ZN116:PA47 | ZN116:PA19 | ZN00116/000019 | INNER WEST | OH | Not Veg | 2012-03-22 | N | 417.2 | N | 5 | N | N | 1.1101 | 39.4971 | 16158.5051
| ZN36000:PA24 | 1191 | 1373.2148 | 41.04 | 1.153 | 41.04 | 19535 | 9428 | 800625 | 2012-03-22 12:14 | 2012-03-22 18:26 | 372 | 11kV | 372 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 120127 single phase DOLF | March | 2012 | 2012Q3 | 2012 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2012-03-22 | N | 372 | N | 5 | N | N | 1.1101 | 39.4971 | 271.8466
| ZN36000:PA25 | 7 | 2667.54 | #N/A | 381.0771 | 39.4971 | 19396 | 8259 | 801016 | 2012-03-23 11:13 | 2012-03-23 12:35 | 82 | 11kV | 8688 | 150 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex peats Ridge zn Pnl.3 - REC 45071 Central Mangrove tripped on A & C phase overcurrent Unknown - Suspect branch See # 801797 801799 | March | 2012 | 2012Q3 | 2012 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2012-03-23 | N | 57.92 | N | 3 | N | N | 1.1101 | 39.4971 | 6348.9341
| ZN36000:PA26 | 547 | 883.6961 | #N/A | 1.6155 | 39.4971 | 19177 | 5271 | 801063 | 2012-03-23 12:31 | 2012-03-23 13:45 | 74 | 11kV | 31280 | 881 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3154 St Ives, Panel 17 Fdr CB tripped ,reclosed and locked out on C phase IOC and Timed OC, earth leakage, timing and lockout, efi.UG 11kV fault between Sw B @ S.7416 Sw A @ S.7417 and AB.2848 | March | 2012 | 2012Q3 | 2012 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | UG | Not Veg | 2012-03-23 | N | 35.5051 | N | 3 | N | N | 1.1101 | 39.4971 | 22858.5014
| ZN36000:PA4 | 887 | 1478.1597 | #N/A | 1.6665 | 39.4971 | 18681 | 984 | 801261 | 2012-03-23 17:18 | 2012-03-23 20:40 | 202.2667 | 11kV | 16381.7333 | 81 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Verbal Report that a bond had burnt off HV to S.46601 | March | 2012 | 2012Q3 | 2012 | ZN180:PA21 | ZN180:PA21 | ZN00180/000021 | MOSMAN | OH | Not Veg | 2012-03-23 | N | 202.2436 | N | 3 | N | N | 1.1101 | 39.4971 | 11971.2875
| ZN36000:PA6 | 1904 | 1628.6658 | 39.62 | 0.85539 | 39.62 | 19009 | 4142 | 801325 | 2012-03-24 02:21 | 2012-03-24 04:54 | 152.6667 | 11kV | 4617.2333 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120149 A phase DOLF : 10 Amp. Excluded OMS 801325, 801326 OMS 801639 | March | 2012 | 2012Q3 | 2012 | 231:8405 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2012-03-24 | N | 148.943 | N | 3 | N | N | 1.1101 | 39.4971 | 3374.1379
| ZN36000:PA7 | 2023 | 1732.1969 | 36.14 | 0.85625 | 36.14 | 19712 | 11860 | 801338 | 2012-03-24 08:00 | 2012-03-24 09:10 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120150 B phase DOLF : 10 Amp Excluded OMS (incorrect sub) 801338 OMS 801793 | March | 2012 | 2012Q3 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2012-03-24 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 51.1539
| ZN36000:PA8 | 65 | 726.328 | #N/A | 11.1743 | 39.4971 | 19346 | 7622 | 801322 | 2012-03-24 01:26 | 2012-03-24 09:50 | 504 | 11kV | 10009 | 177 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120147 3 fault operations Sectionaliser OHM down adjcent pole FT-50473 | March | 2012 | 2012Q3 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-03-24 | N | 56.548 | N | 3 | N | N | 1.1101 | 39.4971 | 7314.282
| ZN342:PA15 | 68 | 909.8575 | #N/A | 13.3803 | 39.4971 | 19256 | 6589 | 802234 | 2012-03-26 11:22 | 2012-03-26 14:45 | 203 | 11kV | 203 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 120175 B Phase DOLF : 10 Amp Staff reported they had been to this site recently for blown dolfs so suspected faulty 11kV surge arrestors. Due to their suspicions all surge arrestors were changed. Excluded OMS 801831 | March | 2012 | 2012Q3 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2012-03-26 | N | 203 | N | 2 | N | N | 1.1101 | 39.4971 | 148.3464
| ZN342:PA16 | 1016 | 1545.4358 | #N/A | 1.5211 | 39.4971 | 18742 | 1456 | 802113 | 2012-03-26 17:24 | 2012-03-26 18:11 | 47 | 11kV | 44039 | 937 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S80 Chatswood Panel 25 Tripped Cause: Branch on mains at 22 Roslyn St, Lane Cove North. Gore Hill mains to inspect and refer for future tree trimming See OMS 802268 802117 802116 802113 | March | 2012 | 2012Q3 | 2012 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2012-03-26 | N | 47 | N | 2 | N | N | 1.1101 | 39.4971 | 32182.4023
| ZN342:PA17 | 1798 | 1460.7812 | 39.97 | 0.81245 | 39.97 | 19153 | 4942 | 802175 | 2012-03-27 01:51 | 2012-03-27 06:20 | 269 | 11kV | 235671 | 1134 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 120181 See SI 20875 Fdr offloaded due to voltage issues when Wollombi Gen failed to start Excluded OMS # 802175, 802181 is part of this outage. - Paragraph 3 | March | 2012 | 2012Q3 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | Unknown | Not Veg | 2012-03-27 | N | 207.8228 | N | 2 | N | N | 1.1101 | 39.4971 | 172221.4157
| ZN342:PA18 | 1518 | 1984.3962 | 41.76 | 1.3072 | 41.76 | 19198 | 5670 | 802483 | 2012-03-27 15:06 | 2012-03-27 16:55 | 109 | 11kV | 1526 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120192 A phase DOLF : 16 Amp | March | 2012 | 2012Q3 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-03-27 | N | 109 | N | 2 | N | N | 1.1101 | 39.4971 | 1115.1558
| ZN342:PA21 | 715 | 1117.6649 | #N/A | 1.5632 | 39.4971 | 20007 | 14983 | 802597 | 2012-03-28 04:04 | 2012-03-28 05:08 | 64 | 11kV | 75072 | 1173 | HV | Animal Other | Animal | UGOH | Unplanned | Unselected | N | At S965 Pennant Hills 11kV OCB panel 42 tripped on Relays: Basler Relay 50TABC (IOC) Cause: DOp Patrolled - Suspect UGOH flashed over (possible animal) tee off to S7537 Newline Castle. Linesman to inspect in daylight hours. | March | 2012 | 2012Q3 | 2012 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Not Veg | 2012-03-28 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 54860.4034
| ZN342:PA22 | 2611 | 1459.2505 | 37.18 | 0.55889 | 37.18 | 19512 | 9145 | 802719 | 2012-03-28 05:37 | 2012-03-28 07:26 | 109 | 11kV | 94684 | 1171 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120196 2 Fault operations Earth fault | March | 2012 | 2012Q3 | 2012 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2012-03-28 | N | 80.8574 | N | 7 | N | N | 1.1101 | 39.4971 | 69192.2745
| ZN342:PA23 | 1363 | 1490.9407 | 39.85 | 1.0939 | 39.85 | 20106 | 16033 | 802623 | 2012-03-28 07:54 | 2012-03-28 08:42 | 48 | 11kV | 57586 | 1263 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At Zn1287 Revesby the 11kv "Hodgkinson Cres" feeder Pnl 11 has tripped. Signals: 11kv trip, ZE, GE Relays: B ph OC, C ph Timed and IOC, EFI, FC, Timer, LO Field EFI's: NIL Remarks: Suspected UG Fault between Panel 11 @ Zn 1287 Revesby and Sub 4452 Hodkinson Cres SW/A Related jobs: #802623, 803178 | March | 2012 | 2012Q3 | 2012 | ZN1287:PA11 | ZN1287:PA11 | ZN01287/000011 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-03-28 | N | 45.5946 | N | 7 | N | N | 1.1101 | 39.4971 | 42082.1503
| ZN342:PA24 | 1004 | 1106.5511 | 43.56 | 1.1021 | 43.56 | 19516 | 9173 | 802611 | 2012-03-28 06:31 | 2012-03-28 16:07 | 576 | 11kV | 177456 | 370 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 120202 1 fault operation Earth fault ote 1 minute interruption beyond 47754 from 1540 to 1541 due to ABS 40205 being unsafe to operate while energised. Faults were manins on X-arm at pole IQ-11502 and a links 40464 falling apart and beeding to be replaced. Excluded OMS 802611, 802731 OMS 803192, 803193, 803194, 803197, 803198, 803199 | March | 2012 | 2012Q3 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-03-28 | N | 479.6108 | N | 7 | N | N | 1.1101 | 39.4971 | 129679.6107
| ZN342:PA26 | 2657 | 2373.547 | 41.29 | 0.89332 | 41.29 | 19197 | 5631 | 802990 | 2012-03-28 16:14 | 2012-03-28 17:00 | 46 | 11kV | 46 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120209 A Phase DOLF : 10 Amp excluded OMS 802990 OMS 803140 | March | 2012 | 2012Q3 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-03-28 | N | 46 | N | 7 | N | N | 1.1101 | 39.4971 | 33.6154
| ZN342:PA27 | 346 | 314.7909 | #N/A | 0.9098 | 39.4971 | 20120 | 16110 | 803058 | 2012-03-28 20:10 | 2012-03-28 21:20 | 69.85 | 11kV | 3003.55 | 43 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse | Unplanned | Unselected | N | LID 120213 B phase DOLF : 16 Amp. Note the B phase fuse that blew was only a 10 amp fuse, however records show it should have been a 16 amp fuse, so it was replaced with the correct 16 amp fuse. Excluded OMS 803058, 803059, 803064, 803065 OMS 803060 | March | 2012 | 2012Q3 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2012-03-28 | N | 69.85 | N | 7 | N | N | 1.1101 | 39.4971 | 2194.9058
| ZN342:PA28 | 1269 | 1127.5362 | 39.99 | 0.88852 | 39.99 | 20281 | 18198 | 803070 | 2012-03-28 21:13 | 2012-03-28 21:57 | 44 | 11kV | 74272 | 1688 | HV | Animal Possum | Animal | Pole | Unplanned | Unselected | N | LID 120214 2 fault operations Earth fault Dead possum pole HW-60221 Lakeview Rd Excluded OMS 803070, 803071, 803072, 803074 OMS 803094 | March | 2012 | 2012Q3 | 2012 | 260:33347 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2012-03-28 | N | 44 | N | 7 | N | N | 1.1101 | 39.4971 | 54275.7869
| ZN342:PA33 | 547 | 799.1109 | #N/A | 1.4609 | 39.4971 | 19802 | 12812 | 803141 | 2012-03-29 09:00 | 2012-03-29 10:20 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 120219 Phase A 16 A DOLF - No Cause Found | March | 2012 | 2012Q3 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-03-29 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 116.9233
| ZN342:PA35 | 850 | 345.632 | 34.2 | 0.40663 | 34.2 | 20002 | 14936 | 803209 | 2012-03-29 10:30 | 2012-03-29 11:41 | 71 | 11kV | 107423 | 1513 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Zone Pa14 fdr tripped Relays-ACph IOC EFI Signals-Ze Tx4GE 11kv Trip EFI-CP491 S6574 S2870 Abnormal-S8695SwB closed, S4556SwA Open S4556 is interupted but there is only minor load. Matter has been referred to customer supply. (Refer defective on Pa11 Matraville) 11kV UG fdr fault from S2870SwA to S4556. S4556 supply not restored as HV fault on other side of RMI and LV no parrallel. Mater refered to John Koutsounadis See 803782 exclude 803209,13,693 | March | 2012 | 2012Q3 | 2012 | ZN1788:PA14 | ZN1788:PA14 | ZN01788/000014 | RANDWICK | UG | Not Veg | 2012-03-29 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 78501.56
| 509:33395 | 925 | 607.2691 | 34.09 | 0.65651 | 34.09 | 19721 | 12001 | 803324 | 2012-03-29 13:35 | 2012-03-29 14:07 | 32 | 11kV | 224 | 7 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 120223 A Phase DOLF : 10 Amp | March | 2012 | 2012Q3 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-03-29 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 163.6926
| 509:33397 | 403 | 347.1162 | 37.37 | 0.86133 | 37.37 | 19818 | 12944 | 803299 | 2012-03-29 13:10 | 2012-03-29 16:45 | 215 | 11kV | 3225 | 15 | HV | Animal Insect | Animal | Pole | Unplanned | Unselected | N | LID 120222 Feeder Section isolated - pole in danger of falling due to white ants | March | 2012 | 2012Q3 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2012-03-29 | N | 215 | N | 4 | N | N | 1.1101 | 39.4971 | 2356.7349
| 509:33399 | 1036 | 771.9524 | 32.12 | 0.74513 | 32.12 | 18905 | 3154 | 803082 | 2012-03-30 03:01 | 2012-03-30 05:55 | 174 | 11kV | 9222 | 53 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At PT.15829 the centre phase HDO fuse operated - possum found at base of pole opposite #40 Merrilee Cres | March | 2012 | 2012Q3 | 2012 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2012-03-30 | N | 174 | N | 4 | N | N | 1.1101 | 39.4971 | 6739.1656
| ZN12630:PA1 | 474 | 389.7417 | 36.54 | 0.82224 | 36.54 | 18775 | 1915 | 803537 | 2012-03-30 08:05 | 2012-03-30 10:05 | 120 | 11kV | 1080 | 9 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | At CP1835 Caravan Plessey HV DO (Road Side) blown Cause: Suspect lightning strike See OMS 804636, 803537, 803556 | March | 2012 | 2012Q3 | 2012 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2012-03-30 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 789.2321
| ZN12630:PA10 | 322 | 1076.9486 | 47.28 | 3.3446 | 47.28 | 19820 | 12959 | 803871 | 2012-03-30 18:03 | 2012-03-30 18:59 | 55.8833 | 11kV | 6015.7833 | 118 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 120240 A phase DOLF : 40 Amp Fallen tree branch found | March | 2012 | 2012Q3 | 2012 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Veg | 2012-03-30 | N | 50.9812 | N | 4 | N | N | 1.1101 | 39.4971 | 4396.157
| ZN12630:PA11 | 245 | 319.3929 | 39.55 | 1.3036 | 39.55 | 19759 | 12456 | 803917 | 2012-03-30 22:00 | 2012-03-30 23:25 | 85 | 11kV | 4080 | 48 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 120242 section opened to make repairs at pole JT-40108 | March | 2012 | 2012Q3 | 2012 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2012-03-30 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 2981.5437
| ZN12630:PA13 | 97 | 227.9197 | 42.65 | 2.3497 | 42.65 | 18966 | 3547 | 804061 | 2012-03-31 18:22 | 2012-03-31 20:46 | 144 | 11kV | 25968 | 182 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120254 A-B trip siemens relay fdr patroled no cause found. Excluded OMS 804061 | March | 2012 | 2012Q3 | 2012 | 512:48048 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2012-03-31 | N | 142.6813 | N | 1 | N | N | 1.1101 | 39.4971 | 18976.6485
| ZN12630:PA3 | 429 | 654.4192 | 49.61 | 1.5255 | 49.61 | 18641 | 699 | 804118 | 2012-04-01 09:56 | 2012-04-01 11:55 | 119 | 11kV | 714 | 6 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 120258 single phase DOLF : 10 Amp | April | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-04-01 | N | 119 | N | 3 | N | N | 1.1101 | 39.4971 | 521.7701
| ZN12630:PA6 | 8 | 50.8963 | #N/A | 6.362 | 39.4971 | 19471 | 8881 | 804178 | 2012-04-01 16:29 | 2012-04-01 18:10 | 101 | 11kV | 303 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | @ PT 14257 HUE HUE MOUNTAIN 0.5 Footpath HVDO fuse operated. Cause: Fuse fatigue See OMS 804320 and 804178 | April | 2012 | 2012Q4 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2012-04-01 | N | 101 | N | 3 | N | N | 1.1101 | 39.4971 | 221.4235
| ZN12630:PA8 | 368 | 1083.199 | 51.22 | 2.9435 | 51.22 | 18983 | 3842 | 804186 | 2012-04-01 17:37 | 2012-04-01 19:35 | 118 | 11kV | 93494 | 994 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Rain Wind Storm | N | At ZN.9550 Gwawley Bay P-43 "Gwawley Bay Aux No.2" fdr tripped & reclosed on: RELAYS: A & C phase OC, with EFI. SIGNALS: FIELD EFIs: S.48722, 9073 REMARKS: Lightning. Lightning strike at AB.355513. Bond burnt off roadside phase. | April | 2012 | 2012Q4 | 2012 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2012-04-01 | N | 94.0584 | N | 3 | N | N | 1.1101 | 39.4971 | 68322.6576
| 222:33596 | 1214 | 1438.0047 | 47.05 | 1.1845 | 47.05 | 18614 | 334 | 804242 | 2012-04-02 04:54 | 2012-04-02 06:10 | 76 | 11kV | 836 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120262 A & C phase DOLF : 10 Amp | April | 2012 | 2012Q4 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2012-04-02 | N | 76 | N | 5 | N | N | 1.1101 | 39.4971 | 610.9241
| 222:33597 | 664 | 495.9168 | 35.63 | 0.74686 | 35.63 | 18674 | 916 | 804234 | 2012-04-02 04:44 | 2012-04-02 07:23 | 159 | 11kV | 41480 | 370 | HV | Animal Flying Fox | Animal | UGOH | Unplanned | Rain Light | N | LID 120261 2 fault operations 3 phase Overcurrent Flying Fox on UGOH SUrge Arrester at Tocal Homestead Sub 29150. Requires Rachem Covers to insulate arrestors etc Excluded 804234 | April | 2012 | 2012Q4 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-04-02 | N | 112.1081 | N | 5 | N | N | 1.1101 | 39.4971 | 30312.3605
| 222:33600 | 1047 | 682.3916 | 34.22 | 0.65176 | 34.22 | 19557 | 9622 | 804445 | 2012-04-02 10:57 | 2012-04-02 11:36 | 39 | 11kV | 42978 | 1102 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At Sub 874 Concord 11KV fdr Pnl 25 "S3374 Mepunga St" tripped on B phase O/C and EFI Remarks: UG cable damaged. Pole gang digging Cnr Concord Rd and Uralla St concord. Related jobs: #804461, 804464, 804445, 804832 | April | 2012 | 2012Q4 | 2012 | ZN874:PA25 | ZN874:PA4 | ZN00874/000004 | CANADA BAY | UG | Not Veg | 2012-04-02 | N | 39 | N | 5 | N | N | 1.1101 | 39.4971 | 31407.0548
| 222:33601 | 798 | 576.2198 | 34.22 | 0.72208 | 34.22 | 19881 | 13577 | 804403 | 2012-04-02 10:28 | 2012-04-02 11:45 | 76.55 | 11kV | 5014.1667 | 73 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn711 Blackwattle Bay Pa31 fdr tripped Signals:5kV trip ZE No4GE Relays: Cph TImed OC EL EFI EFI: Nil Contractor error caused failure. Contractor hit cable on corner of pyrmont and quarry streets. See 804914 GIS 804960 Exclude 804403,16,9,23,32 | April | 2012 | 2012Q4 | 2012 | ZN711:PA31 | ZN7481:PA12 | ZN07481/000012 | SYDNEY | UG | Not Veg | 2012-04-02 | N | 68.6872 | N | 5 | N | N | 1.1101 | 39.4971 | 3664.2051
| 222:33602 | 947 | 1307.9635 | 40.52 | 1.3812 | 40.52 | 18744 | 1490 | 804459 | 2012-04-02 11:06 | 2012-04-02 12:15 | 68.7 | 11kV | 3091.5 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120266 B Phase DOLF : 40 Amp readings 246 volts 130, 150 & 180 amps | April | 2012 | 2012Q4 | 2012 | 224:80332 | 224:80332 | ZN00224/080332 | LAKE MACQUARIE | OH | Veg | 2012-04-02 | N | 68.7 | N | 5 | N | N | 1.1101 | 39.4971 | 2259.177
| ZN965:PA13 | 584 | 436.1083 | 26.99 | 0.74676 | 26.99 | 19696 | 11576 | 805057 | 2012-04-03 12:51 | 2012-04-03 14:38 | 107 | 11kV | 108712 | 1016 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120289 1 fault operation B & C phase Overcurrent. RAGCB auto reclose OFF for SI 21479 | April | 2012 | 2012Q4 | 2012 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2012-04-03 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 79443.5231
| ZN965:PA15 | 1177 | 1200.1437 | 31.42 | 1.0197 | 31.42 | 20288 | 18544 | 805064 | 2012-04-03 13:04 | 2012-04-03 17:15 | 251 | 11kV | 15922 | 95 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120286 Feeder isolated & earthed to repair low 11kV mains (2.5m above ground) at BEASHELL sub 54509. Excluded OMS 805064, 805099, 805140 | April | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-04-03 | N | 167.6 | N | 3 | N | N | 1.1101 | 39.4971 | 11635.328
| ZN965:PA17 | 1170 | 1307.3282 | 35.19 | 1.1174 | 35.19 | 19504 | 9099 | 805283 | 2012-04-03 22:34 | 2012-04-04 00:15 | 101 | 11kV | 202 | 2 | HV | Animal Flying Fox | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 120293 A phase DOLF : 10 Amp. Dead bat found Excluded OMS 805283 | April | 2012 | 2012Q4 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-04-03 | N | 101 | N | 3 | N | N | 1.1101 | 39.4971 | 147.6156
| ZN965:PA2 | 545 | 517.2351 | 29.99 | 0.94906 | 29.99 | 18859 | 2638 | 805298 | 2012-04-04 07:22 | 2012-04-04 08:25 | 63 | 11kV | 441 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120300 B phase DOLF : 63 Amp | April | 2012 | 2012Q4 | 2012 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | OH | Veg | 2012-04-04 | N | 63 | N | 2 | N | N | 1.1101 | 39.4971 | 322.2698
| ZN965:PA20 | 919 | 805.6484 | 30.14 | 0.87666 | 30.14 | 19647 | 10774 | 805327 | 2012-04-04 08:25 | 2012-04-04 09:10 | 45 | 11kV | 54810 | 1218 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Wind | N | LID 120299 fdr opened by S.O. Opened for safety reasons - door blown off kiosk Government Rd switching cubicle Excluded oms # 805327 & 805321 also see report # 120298 | April | 2012 | 2012Q4 | 2012 | 238:34151 | 238:34136 | ZN00238/034136 | MAITLAND | UG | Not Veg | 2012-04-04 | N | 45 | N | 2 | N | N | 1.1101 | 39.4971 | 40053.5314
| ZN965:PA21 | 709 | 824.849 | 35.82 | 1.1634 | 35.82 | 19234 | 6341 | 805739 | 2012-04-05 00:12 | 2012-04-05 00:35 | 23 | 11kV | 1403 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120316 2 fault operations reclosed OK Excluded OMS 805739 | April | 2012 | 2012Q4 | 2012 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2012-04-05 | N | 23 | N | 5 | N | N | 1.1101 | 39.4971 | 1025.271
| ZN965:PA22 | 594 | 394.3648 | 43.77 | 0.66391 | 43.77 | 19327 | 7524 | 805742 | 2012-04-05 05:38 | 2012-04-05 09:50 | 252 | 11kV | 206640 | 820 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | HV bond off Section of 11kV Feeder from S46834 to LV861 Ex Panel 21 Meadowbank. See OMS 807766 805742 805769 | April | 2012 | 2012Q4 | 2012 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Not Veg | 2012-04-05 | N | 252 | N | 5 | N | N | 1.1101 | 39.4971 | 151006.4172
| ZN965:PA24 | 1117 | 869.6691 | 30.49 | 0.77858 | 30.49 | 18851 | 2570 | 805874 | 2012-04-05 10:00 | 2012-04-05 12:20 | 140 | 11kV | 280 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | 10A DOLF blown Faulty arrestor Weather Fine : Record withdrawn No. 805874 | April | 2012 | 2012Q4 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2012-04-05 | N | 140 | N | 5 | N | N | 1.1101 | 39.4971 | 204.6157
| ZN965:PA26 | 930 | 949.0245 | 36.7 | 1.0205 | 36.7 | 18964 | 3544 | 806002 | 2012-04-05 13:49 | 2012-04-05 15:05 | 76 | 11kV | 4788 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | 2 fault operations on recloser Bat found on mains. Weather Fine . : Record withdrawn No. 806002 | April | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-04-05 | N | 76 | N | 5 | N | N | 1.1101 | 39.4971 | 3498.9292
| ZN965:PA28 | 1051 | 812.2406 | 28.47 | 0.77283 | 28.47 | 19271 | 6798 | 805903 | 2012-04-05 10:51 | 2012-04-05 16:20 | 329 | 11kV | 4277 | 13 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 120326 C Phase DOLF : 10 Amp. faulty LAS replaced Excluded oms # 805903 | April | 2012 | 2012Q4 | 2012 | 230:34051 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2012-04-05 | N | 329 | N | 5 | N | N | 1.1101 | 39.4971 | 3125.5054
| ZN965:PA29 | 760 | 580.706 | 30.26 | 0.76409 | 30.26 | 18920 | 3233 | 806177 | 2012-04-06 08:05 | 2012-04-06 09:35 | 90 | 11kV | 270 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | Replaced 16A DOLF Previous Storm Record Withdrawn OMS 806177 | April | 2012 | 2012Q4 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2012-04-06 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 197.308
| ZN965:PA3 | 1224 | 1606.4178 | 40.86 | 1.3124 | 40.86 | 20328 | 19341 | 806250 | 2012-04-06 16:38 | 2012-04-06 18:30 | 112 | 11kV | 20384 | 182 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 120332 2 fault operations single phase Earth fault Bird found at base of pole FQ-54715. | April | 2012 | 2012Q4 | 2012 | 512:48048 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Not Veg | 2012-04-06 | N | 112 | N | 2 | N | N | 1.1101 | 39.4971 | 14896.026
| ZN965:PA30 | 59 | 1390.027 | #N/A | 23.5598 | 39.4971 | 20335 | 19388 | 806286 | 2012-04-07 02:58 | 2012-04-07 03:55 | 57 | 11kV | 19215 | 383 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.3154 St Ives, Panel 22 Fdr CB tripped, reclosed and tripped on A phase IOC and timed OC, reclose timing and lockout elays, 11kV trip. Tree O/S #45 Roma St growing into mains | April | 2012 | 2012Q4 | 2012 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Veg | 2012-04-07 | N | 50.1697 | N | 6 | N | N | 1.1101 | 39.4971 | 14041.7553
| ZN965:PA33 | 820 | 726.8719 | 30.43 | 0.88643 | 30.43 | 18881 | 2907 | 807083 | 2012-04-07 13:44 | 2012-04-07 16:16 | 152 | 11kV | 13043 | 120 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Lid 120334 4 fault operations C phase Overcurrent Tree on 11kV mains at Pole JV-90090. | April | 2012 | 2012Q4 | 2012 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2012-04-07 | N | 108.6917 | N | 6 | N | N | 1.1101 | 39.4971 | 9531.4397
| ZN965:PA35 | 983 | 978.7241 | 30.41 | 0.99565 | 30.41 | 19879 | 13571 | 806356 | 2012-04-07 15:25 | 2012-04-07 17:30 | 125 | 11kV | 2375 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV OH interrupted for safety. Bundled LV pulled down by trees, poles required reraking | April | 2012 | 2012Q4 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2012-04-07 | N | 125 | N | 6 | N | N | 1.1101 | 39.4971 | 1735.5799
| ZN965:PA37 | 505 | 1009.0215 | #N/A | 1.9981 | 39.4971 | 20211 | 17140 | 806374 | 2012-04-07 15:26 | 2012-04-07 19:30 | 244.1333 | 11kV | 78226.7833 | 892 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.14144 Wamberal, Panel 4 FDr CB tripped on B and C phase OC, 11kV trip. Tree branch on OH mains which also caused a secondary fault burning bond near UG/OH | April | 2012 | 2012Q4 | 2012 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-04-07 | N | 87.6982 | N | 6 | N | N | 1.1101 | 39.4971 | 57165.826
| ZN965:PA38 | 731 | 1034.4652 | 38.79 | 1.4151 | 38.79 | 19995 | 14911 | 807101 | 2012-04-07 19:12 | 2012-04-07 19:33 | 21 | 11kV | 16422 | 782 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120335 Feeder interrupted to make temporary repairs to ABS 18016 (tapping burnt-off and partially welded to ABS contact). Tasman Mine complained about fluctuating volts prior to finding faulty ABS (unable to contact mine when faulty ABS found). ABS 12880 closed & ABS 3165 closed at time of interruption. | April | 2012 | 2012Q4 | 2012 | 216:10728 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Not Veg | 2012-04-07 | N | 21 | N | 6 | N | N | 1.1101 | 39.4971 | 12000.7132
| ZN965:PA39 | 493 | 390.5333 | 25.81 | 0.79216 | 25.81 | 19154 | 4943 | 806413 | 2012-04-07 21:57 | 2012-04-07 22:47 | 50 | 11kV | 81500 | 1630 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Panel 18 Tripped and reclosed on Relays: A and C phase IOC, Timing Relay, Fault Check, EFI and Lockout Signals: 11kV trip. Group Earth, Tx2 and Zone Earth Abnormal Switching: S47944 SWB closed, SWA Open. Cause: Possum Across HV UGOH near AB264 See OMS 809581/809539/806416. 806413/414/417/419/420/421/422 | April | 2012 | 2012Q4 | 2012 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Not Veg | 2012-04-07 | N | 50 | N | 6 | N | N | 1.1101 | 39.4971 | 59557.7962
| ZN965:PA4 | 1126 | 980.4757 | 28.56 | 0.87076 | 28.56 | 20004 | 14966 | 806444 | 2012-04-08 07:54 | 2012-04-08 08:42 | 48 | 11kV | 96 | 2 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn 1610 Homebush Bay, 11kV Pnl 16 "Holker Asia fdr" tripped on e/fault with efi and group earth signal Remarks: UG Fault. Cable fault between Zn 1610 (Pnl 16) to S8045 Holker Asia (sw F) Related jobs: #806444, 807082 | April | 2012 | 2012Q4 | 2012 | ZN1610:PA16 | ZN1610:PA16 | ZN01610/000016 | PARRAMATTA | UG | Not Veg | 2012-04-08 | N | 48 | N | 27 | Y | Y | 1.1101 | 39.4971 | 70.154
| ZN965:PA42 | 1144 | 879.3944 | 31.98 | 0.7687 | 31.98 | 19454 | 8736 | 806449 | 2012-04-08 08:18 | 2012-04-08 10:05 | 107 | 11kV | 107 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | Replaced 10A DOLF Bird. Volts = 245. Record withdrawn OMS # 806449 | April | 2012 | 2012Q4 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2012-04-08 | N | 107 | N | 27 | Y | Y | 1.1101 | 39.4971 | 78.1924
| ZN965:PA43 | 1028 | 1071.1326 | 35.71 | 1.042 | 35.71 | 18976 | 3639 | 806516 | 2012-04-08 17:51 | 2012-04-08 18:45 | 54 | 11kV | 1188 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | A and B phase 16 Amp DOLF's Electrical Storm Record withdrawn OMS 806516 | April | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-04-08 | N | 54 | N | 27 | Y | Y | 1.1101 | 39.4971 | 868.1554
| ZN965:PA44 | 469 | 400.7611 | 30.67 | 0.8545 | 30.67 | 18979 | 3800 | 806521 | 2012-04-08 18:05 | 2012-04-08 19:00 | 55 | 11kV | 880 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | B and C phase DOLF's blown 20 Amp Electrical Storm Record withdrawn OMS 806521 | April | 2012 | 2012Q4 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2012-04-08 | N | 55 | N | 27 | Y | Y | 1.1101 | 39.4971 | 643.078
| ZN965:PA46 | 1135 | 937.6613 | 28.37 | 0.82613 | 28.37 | 19749 | 12421 | 806554 | 2012-04-08 19:03 | 2012-04-08 19:43 | 40 | 11kV | 103320 | 2583 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 120366 1 fault operation, B & C phase Overcurrent Please patrol feeder. Refer OMS Job No. 806554. patroled suspect lightning strike | April | 2012 | 2012Q4 | 2012 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2012-04-08 | N | 40 | N | 27 | Y | Y | 1.1101 | 39.4971 | 75503.2086
| ZN965:PA47 | 1170 | 1390.3713 | 41.61 | 1.1884 | 41.61 | 18941 | 3422 | 806553 | 2012-04-08 19:04 | 2012-04-08 19:43 | 39 | 11kV | 43914 | 1126 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 120369 1 fault operation, A & B phase, Overcurrent bat found during feeder patrol. | April | 2012 | 2012Q4 | 2012 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2012-04-08 | N | 39 | N | 27 | Y | Y | 1.1101 | 39.4971 | 32091.056
| ZN965:PA6 | 1075 | 1165.4885 | 39.13 | 1.0842 | 39.13 | 20305 | 19020 | 806519 | 2012-04-08 18:00 | 2012-04-08 19:45 | 105 | 11kV | 210 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Lightning | N | B Phase 10 Amp DOLF Electrical Storm Record Withdrawn OMS 806519 | April | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-04-08 | N | 105 | N | 27 | Y | Y | 1.1101 | 39.4971 | 153.4618
| ZN965:PA8 | 1194 | 960.7452 | 30.47 | 0.80464 | 30.47 | 19351 | 7644 | 807705 | 2012-04-08 18:15 | 2012-04-08 20:35 | 140 | 11kV | 980 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | B and C phase DOLF's 20 Amp blown Electrical Storm | April | 2012 | 2012Q4 | 2012 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2012-04-08 | N | 140 | N | 27 | Y | Y | 1.1101 | 39.4971 | 716.1551
| ZN35700:PA1 | 639 | 1206.6713 | 45.34 | 1.8884 | 45.34 | 20396 | 20064 | 806540 | 2012-04-08 19:00 | 2012-04-08 20:50 | 110 | 11kV | 220 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 120380 Single phase DOLF : 10 Amp Excluded OMS 806540 | April | 2012 | 2012Q4 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2012-04-08 | N | 110 | N | 27 | Y | Y | 1.1101 | 39.4971 | 160.7695
| ZN35700:PA10 | 500 | 626.0346 | 43.01 | 1.2521 | 43.01 | 18732 | 1394 | 806564 | 2012-04-08 19:27 | 2012-04-08 20:56 | 89 | 11kV | 118385 | 1642 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At Zn4545 Meadowbank Panel 44 Tripped on and and C phase timed O/C. Cause Not ascertained - Suspect weather related. See OMS 807881 807882 806564. | April | 2012 | 2012Q4 | 2012 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Veg | 2012-04-08 | N | 72.0981 | N | 27 | Y | Y | 1.1101 | 39.4971 | 86512.2662
| ZN35700:PA12 | 32 | 419.9969 | #N/A | 13.1249 | 39.4971 | 19044 | 4346 | 806576 | 2012-04-08 19:41 | 2012-04-08 20:58 | 77 | 11kV | 106876 | 1388 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 120382 2 fault operations B & C phase Overcurrent Tree on mains at Pole TB-50442. OMS Job No. 806602. | April | 2012 | 2012Q4 | 2012 | 230:34051 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2012-04-08 | N | 77 | N | 27 | Y | Y | 1.1101 | 39.4971 | 78101.8285
| ZN35700:PA13 | 29 | 2855.7953 | 40.88 | 98.4757 | 40.88 | 18739 | 1430 | 806644 | 2012-04-08 20:50 | 2012-04-08 21:40 | 50 | 11kV | 250 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | A and B phase 40 Amp DOLF's blown Cause animals or birds Record Withdrawn OMS 806644 | April | 2012 | 2012Q4 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2012-04-08 | N | 50 | N | 27 | Y | Y | 1.1101 | 39.4971 | 182.6926
| ZN35700:PA14 | 13 | 1108.6656 | #N/A | 85.282 | 39.4971 | 20349 | 19568 | 806543 | 2012-04-08 18:57 | 2012-04-08 22:05 | 188 | 11kV | 564 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120384 B & C phase DOLF : 10 Amp | April | 2012 | 2012Q4 | 2012 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | UG | Not Veg | 2012-04-08 | N | 188 | N | 27 | Y | Y | 1.1101 | 39.4971 | 412.1546
| ZN35700:PA19 | 51 | 121.836 | #N/A | 2.3889 | 39.4971 | 18705 | 1185 | 806525 | 2012-04-08 18:17 | 2012-04-08 22:10 | 233 | 11kV | 699 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 120385 B phase 10 Amp DOLF blown Lightning storm | April | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-04-08 | N | 233 | N | 27 | Y | Y | 1.1101 | 39.4971 | 510.8086
| ZN35700:PA8 | 2 | 29.7872 | #N/A | 14.8936 | 39.4971 | 19805 | 12852 | 806513 | 2012-04-08 17:20 | 2012-04-08 22:45 | 325 | 11kV | 325 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | Replaced 10A DOLF Electrical Storm Record Withdrawn OMS 806513 | April | 2012 | 2012Q4 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-04-08 | N | 325 | N | 27 | Y | Y | 1.1101 | 39.4971 | 237.5004
| ZN35900:PA1 | 1806 | 1246.6569 | 35.74 | 0.69029 | 35.74 | 19565 | 9659 | 806569 | 2012-04-08 19:36 | 2012-04-08 23:02 | 206 | 11kV | 184428 | 1252 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | At Zn195 Pymble Panel 9 Tripped and Locked out on Signals: 11kV Trip, Group Earth and Zone Earth. Relays: A and Cphase Timed O/C, EFI and Fault Check. Cause: At AB779 Footpath Bond Burnt Off AB3231 Centre Phase Bond Burnt Off PT71 Foot Path HVDO fuse blown. Lightning See OMS 807054 807057 807058 807056 806569 | April | 2012 | 2012Q4 | 2012 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Not Veg | 2012-04-08 | N | 147.3067 | N | 27 | Y | Y | 1.1101 | 39.4971 | 134774.5427
| ZN35900:PA10 | 13 | 1015.1139 | #N/A | 78.0857 | 39.4971 | 19114 | 4721 | 806538 | 2012-04-08 18:49 | 2012-04-08 23:30 | 281 | 11kV | 2810 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 120390 B phase DOLF : 10 Amp excluded OMS 806538 | April | 2012 | 2012Q4 | 2012 | 512:48047 | 512:83733 | ZN00512/083733 | CESSNOCK | UG | Not Veg | 2012-04-08 | N | 281 | N | 27 | Y | Y | 1.1101 | 39.4971 | 2053.4651
| ZN35900:PA11 | 19 | 1073.5451 | 49.81 | 56.5024 | 49.81 | 20122 | 16122 | 806582 | 2012-04-08 19:49 | 2012-04-08 23:40 | 231 | 11kV | 116461 | 672 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Electrical Storm | N | At S3425 Castle Cove Pa28 Issabella Eastern Smith Tripped reclosed tripped and locked out on Relays: OC and IOC with EFI Timing relay lockout Fault Check 11kV Trip Cause: Endbox failure at S35197 See OMS 807889 807905 807906 809808 806652 | April | 2012 | 2012Q4 | 2012 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | UG | Not Veg | 2012-04-08 | N | 173.3051 | N | 27 | Y | Y | 1.1101 | 39.4971 | 85106.2638
| ZN35900:PA12 | 73 | 111.5208 | 63.22 | 1.5277 | 63.22 | 20141 | 16248 | 806636 | 2012-04-08 19:39 | 2012-04-09 00:04 | 265 | 11kV | 143601 | 587 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Recloser 527 tripped and locked out on IOC trip - lightning Storm at the time | April | 2012 | 2012Q4 | 2012 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2012-04-08 | N | 244.6354 | N | 27 | Y | Y | 1.1101 | 39.4971 | 104939.3753
| ZN35900:PA14 | 4 | 494.2454 | 61.68 | 123.5613 | 61.68 | 19616 | 10372 | 806580 | 2012-04-08 19:46 | 2012-04-09 00:35 | 289 | 11kV | 334208 | 1273 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | At S1193 Lindfield Panel 7 tripped, reclosed tripped amd locked out on C phase O/C Earth Fault and EFI. Lockout and Timing. Cause: Lightning Storm. See OMS 807151 807163 807160 708158 806580 | April | 2012 | 2012Q4 | 2012 | ZN1193:PA7 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Veg | 2012-04-08 | N | 262.5357 | N | 27 | Y | Y | 1.1101 | 39.4971 | 244229.3489
| ZN35900:PA15 | 55 | 195.1376 | 55.71 | 3.548 | 55.71 | 19599 | 9828 | 806687 | 2012-04-08 22:10 | 2012-04-09 01:00 | 170 | 11kV | 170 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 120393 A phase DOLF : 16 Amp Excluded OMS 806687 CSR logged to incorrect sub | April | 2012 | 2012Q4 | 2012 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | UG | Not Veg | 2012-04-08 | N | 170 | N | 27 | Y | Y | 1.1101 | 39.4971 | 124.231
| ZN35900:PA16 | 130 | 618.0797 | 48.13 | 4.7545 | 48.13 | 19513 | 9146 | 806550 | 2012-04-08 18:47 | 2012-04-09 01:10 | 383 | 11kV | 239240 | 1284 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | N | LID 120374 5 fault operations 3 phase Earth fault, Overcurrrent Lightning strike on UG/OH at Berry Park WWPS sub 55015. See Report 120381 & 120387 Feeder Abnormally Configured - part of Wallalong Feeder connected at time of event - see OMS 807501 | April | 2012 | 2012Q4 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2012-04-08 | N | 186.324 | N | 27 | Y | Y | 1.1101 | 39.4971 | 174829.5356
| ZN35900:PA17 | 1830 | 1394.366 | 30.43 | 0.76195 | 30.43 | 20046 | 15554 | 806578 | 2012-04-08 19:45 | 2012-04-09 01:25 | 340 | 11kV | 195980 | 637 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | At S.15011 Beacon Hill, Panel 8 Fdr CB tripped on earth fault with efi, zone earth, 11kV trip. Field efi's down at S.16265, S.17140, S.16921, S.16691, S.16229, S.15180, S.16907 and S.16228. Suspect lightning arrestor at UG/OH at S.15963. Tried back unsuccesfully three times. | April | 2012 | 2012Q4 | 2012 | ZN15011:PA8 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Not Veg | 2012-04-08 | N | 307.6609 | N | 27 | Y | Y | 1.1101 | 39.4971 | 143216.4036
| ZN35900:PA2 | 1707 | 1232.6469 | 33.4 | 0.72211 | 33.4 | 20178 | 16702 | 807411 | 2012-04-08 18:26 | 2012-04-09 02:47 | 501 | 11kV | 64442 | 208 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 120394 4 fault operations Earth fault, Overcurrent 11kv main on ground beyond ABS 40353. Repairs completed. OMS 806528 Also see report 120395. | April | 2012 | 2012Q4 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-04-08 | N | 309.8173 | N | 27 | Y | Y | 1.1101 | 39.4971 | 47092.3129
| ZN35900:PA20 | 1044 | 967.1505 | 41.35 | 0.92639 | 41.35 | 18582 | 88 | 806719 | 2012-04-09 04:30 | 2012-04-09 06:00 | 90 | 11kV | 450 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | C phase 10 Amp DOLF blown Electrical storm Record Withdrawn OMS 806719 | April | 2012 | 2012Q4 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-04-09 | N | 90 | N | 13 | N | N | 1.1101 | 39.4971 | 328.8467
| ZN35900:PA22 | 5 | 102.5236 | 46.85 | 20.5047 | 46.85 | 18902 | 3136 | 806721 | 2012-04-09 05:46 | 2012-04-09 06:26 | 40 | 11kV | 120 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 120398 A phase DOLF : 3 Amp Excluded OMS 806721 | April | 2012 | 2012Q4 | 2012 | 512:48047 | 512:83733 | ZN00512/083733 | CESSNOCK | UG | Not Veg | 2012-04-09 | N | 40 | N | 13 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN35900:PA23 | 1171 | 1138.2677 | 37.72 | 0.97205 | 37.72 | 20087 | 15883 | 806720 | 2012-04-09 04:39 | 2012-04-09 06:38 | 119 | 11kV | 238 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 120399 A phase DOLF : 10 Amp excluded OMS 806720 - heirarchy | April | 2012 | 2012Q4 | 2012 | 512:48047 | 512:83733 | ZN00512/083733 | CESSNOCK | UG | Not Veg | 2012-04-09 | N | 119 | N | 13 | N | N | 1.1101 | 39.4971 | 173.9234
| ZN35900:PA24 | 1715 | 1334.9823 | 31.77 | 0.77842 | 31.77 | 18792 | 2071 | 806726 | 2012-04-09 06:38 | 2012-04-09 07:20 | 42.3167 | 11kV | 253.9 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 120401 A & B phase DOLF : 20 Amp | April | 2012 | 2012Q4 | 2012 | 526:34641 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2012-04-09 | N | 42.3167 | N | 13 | N | N | 1.1101 | 39.4971 | 185.5426
| ZN35900:PA25 | 562 | 867.0053 | 34.49 | 1.5427 | 34.49 | 19312 | 7360 | 806743 | 2012-04-09 07:36 | 2012-04-09 08:55 | 79 | 11kV | 79 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | A+C Line DOLF's blown also Both DOLFs at sub 52818 also found blown & replaced - 10A. OMS # 806743 | April | 2012 | 2012Q4 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Veg | 2012-04-09 | N | 79 | N | 13 | N | N | 1.1101 | 39.4971 | 57.7309
| ZN35900:PA3 | 522 | 1188.9285 | 39.59 | 2.2776 | 39.59 | 18795 | 2090 | 806714 | 2012-04-09 01:44 | 2012-04-09 10:40 | 536 | 11kV | 33768 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At PT.39 Waterhouse Torrens - 11kV Footpath side 31.5K BB HDO fuse operated - cause unknown | April | 2012 | 2012Q4 | 2012 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2012-04-09 | N | 536 | N | 13 | N | N | 1.1101 | 39.4971 | 24676.6584
| ZN35900:PA4 | 1232 | 1045.0782 | 39.69 | 0.84828 | 39.69 | 19895 | 13716 | 806742 | 2012-04-09 07:27 | 2012-04-09 10:45 | 198 | 11kV | 396 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 120403 A phase DOLF : 3 Amp Arrestors replaced under A/P. Volts = 245. Amps = 15. Excluded OMS # 806742 | April | 2012 | 2012Q4 | 2012 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2012-04-09 | N | 198 | N | 13 | N | N | 1.1101 | 39.4971 | 289.3851
| ZN35900:PA6 | 335 | 512.1095 | 38.73 | 1.5287 | 38.73 | 19829 | 13011 | 806722 | 2012-04-09 06:05 | 2012-04-09 14:20 | 495 | 11kV | 990 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 120405 A phase DOLF : 10 Amp transformer changed excluded OMS 806722 | April | 2012 | 2012Q4 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | UG | Not Veg | 2012-04-09 | N | 495 | N | 13 | N | N | 1.1101 | 39.4971 | 723.4628
| ZN35900:PA7 | 6 | 296.6021 | #N/A | 49.4337 | 39.4971 | 19086 | 4553 | 806756 | 2012-04-09 07:57 | 2012-04-09 14:33 | 395.6167 | 11kV | 1170.6833 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120408 C phase DOLF 10A blown No cause found Weather Fine : Record withdrawn OMS # 806756. | April | 2012 | 2012Q4 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2012-04-09 | N | 390.2278 | N | 13 | N | N | 1.1101 | 39.4971 | 855.5009
| ZN2310:PA10 | 1754 | 1458.1756 | #N/A | 0.83134 | 39.4971 | 18969 | 3590 | 806770 | 2012-04-09 08:29 | 2012-04-09 16:00 | 451 | 11kV | 451 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | Record withdrawn OMS # 806770. 10A Dolf A phase Previous Storm | April | 2012 | 2012Q4 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | UG | Not Veg | 2012-04-09 | N | 451 | N | 13 | N | N | 1.1101 | 39.4971 | 329.5775
| ZN2310:PA14 | 1947 | 1429.1833 | 37.83 | 0.73404 | 37.83 | 19295 | 7315 | 806894 | 2012-04-09 16:02 | 2012-04-09 16:13 | 11 | 11kV | 11770 | 1070 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Feeder 34141 Tripped . Fdr on non auto for restoration of emergency work earth left on at sub 55015. Record withdrawn oms # 806894 : Weather Fine | April | 2012 | 2012Q4 | 2012 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2012-04-09 | N | 11 | N | 13 | N | N | 1.1101 | 39.4971 | 8601.1688
| ZN2310:PA15 | 2401 | 2012.5702 | 40.38 | 0.83822 | 40.38 | 19713 | 11861 | 806828 | 2012-04-09 10:38 | 2012-04-09 17:00 | 382 | 11kV | 382 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | 10A DOLF Replaced Electrical Storm Record Withdrawn No. 806828 | April | 2012 | 2012Q4 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2012-04-09 | N | 382 | N | 13 | N | N | 1.1101 | 39.4971 | 279.1543
| ZN2310:PA18 | 1162 | 1038.4381 | #N/A | 0.89366 | 39.4971 | 19041 | 4301 | 806577 | 2012-04-08 19:35 | 2012-04-09 17:20 | 1305 | 11kV | 293605 | 1038 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | At S847 Hornsby panel 44 tripped reclosed tripped and locked out on A and C phase IOC and Timed O/C, Timing, Fault Check, Lockout and EFI. Signals: Zone Earth Tx3 Group Earth. Tx3 Protn UV. Cause: 2 Bays of 11kV OH down due and Pole snapped From S4837 to LB2694. See OMS 809624 809627 809629 809628 see excluded 806577/581/586/600/609/710/736/876. | April | 2012 | 2012Q4 | 2012 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Not Veg | 2012-04-08 | N | 282.8565 | N | 27 | Y | Y | 1.1101 | 39.4971 | 214557.8741
| ZN2310:PA19 | 1623 | 1075.7312 | 33.44 | 0.6628 | 33.44 | 19008 | 4134 | 806590 | 2012-04-08 19:40 | 2012-04-09 18:40 | 1380 | 11kV | 752749 | 1121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.3154 St Ives, Panel 5 Fdr CB tripped on C phase timed OC, 11kV trip. ^ spans of 11kV OH mains down from LB.1175 to S.35365 | April | 2012 | 2012Q4 | 2012 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2012-04-08 | N | 671.4978 | N | 27 | Y | Y | 1.1101 | 39.4971 | 550086.7669
| ZN2310:PA2 | 450 | 259.8578 | 31.21 | 0.57746 | 31.21 | 20019 | 15095 | 806681 | 2012-04-08 19:40 | 2012-04-09 18:57 | 1397 | 11kV | 379627 | 769 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | At S.3154 St Ives, Panel 12 Fdr CB tripped on A phase timed OC, 11kV trip, #3 group earth, Zone Earth. 6 bays of 11kV OH mains down from AB.1855 to AB.60 tee to PT.1500 and PT.2361. Trees and lightning storm | April | 2012 | 2012Q4 | 2012 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2012-04-08 | N | 493.6632 | N | 27 | Y | Y | 1.1101 | 39.4971 | 277420.2145
| ZN2310:PA21 | 1601 | 1347.7062 | 37.99 | 0.84179 | 37.99 | 20311 | 19064 | 806950 | 2012-04-09 22:07 | 2012-04-09 23:45 | 98 | 11kV | 6076 | 62 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | At PT.9636 Bimnadeen Ave centre phase HDO fuse operated. Ex P-30 "S.48721 Gwawley Bay Aux No.1" fdr from ZN.9550 Gwawley Bay REMARKS Animlas, Possum found at base of pole, HV fuse carrier damaged requires T'Con replacement. | April | 2012 | 2012Q4 | 2012 | ZN9550:PA30 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | OH | Not Veg | 2012-04-09 | N | 98 | N | 13 | N | N | 1.1101 | 39.4971 | 4440.1616
| ZN2310:PA23 | 1824 | 1150.1821 | 32.55 | 0.63058 | 32.55 | 20391 | 20045 | 806965 | 2012-04-10 05:18 | 2012-04-10 09:11 | 232.5333 | 11kV | 1645.65 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120418 A & B phase DOLF : 20 Amp. | April | 2012 | 2012Q4 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2012-04-10 | N | 205.7063 | N | 6 | N | N | 1.1101 | 39.4971 | 1202.5925
| ZN2310:PA24 | 1281 | 1009.5261 | 35.12 | 0.78808 | 35.12 | 19742 | 12357 | 807010 | 2012-04-10 07:50 | 2012-04-10 09:25 | 95 | 11kV | 7790 | 82 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At CP1617 Church St A phase 31.5 Amp HV fuse blown interrupting S1961 Lyndhurst Crescent Cause: Customer in OMS 807010 reported tree branch fell through mains. See OMS 807011 807010 807018 CC1: 22-"Refer to SOp" | April | 2012 | 2012Q4 | 2012 | ZN129:PA8 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Veg | 2012-04-10 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 5692.7022
| ZN2310:PA25 | 854 | 570.0511 | 35.47 | 0.66751 | 35.47 | 19853 | 13354 | 807074 | 2012-04-10 09:17 | 2012-04-10 10:35 | 78 | 11kV | 78 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 120419 A phase DOLF : 10 Amp Volts = 247. Excluded OMS # 807074 | April | 2012 | 2012Q4 | 2012 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2012-04-10 | N | 78 | N | 6 | N | N | 1.1101 | 39.4971 | 57.0001
| ZN2310:PA29 | 702 | 420.733 | #N/A | 0.59933 | 39.4971 | 19553 | 9610 | 807254 | 2012-04-10 10:57 | 2012-04-10 11:52 | 55 | 11kV | 40366 | 808 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.12660 Woy Woy, Panel 11 Fdr CB tripped, reclosed and locked out on A phase IOC and timed OC. O/S #357 Orange Grove Rd tree branch removed by D.Op | April | 2012 | 2012Q4 | 2012 | ZN12660:PA11 | ZN12660:PA11 | ZN12660/000011 | CENTRAL COAST | OH | Veg | 2012-04-10 | N | 49.9579 | N | 6 | N | N | 1.1101 | 39.4971 | 29498.2822
| ZN2310:PA3 | 22 | 1272.5895 | #N/A | 57.845 | 39.4971 | 18600 | 249 | 807494 | 2012-04-10 15:06 | 2012-04-10 15:51 | 45 | 11kV | 63200 | 1476 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.12570 Avoca, Panel 12 Fdr CB tripped on C phase IOC and timed OC, 11kV trip. Tree branch on OH in Chapman St | April | 2012 | 2012Q4 | 2012 | ZN12570:PA12 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2012-04-10 | N | 42.8184 | N | 6 | N | N | 1.1101 | 39.4971 | 46184.6959
| ZN2310:PA30 | 849 | 506.4603 | 33 | 0.59654 | 33 | 19241 | 6437 | 807465 | 2012-04-10 14:39 | 2012-04-10 16:50 | 131 | 11kV | 786 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 120444 A phase DOLF : 10 Amp | April | 2012 | 2012Q4 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | UG | Not Veg | 2012-04-10 | N | 131 | N | 6 | N | N | 1.1101 | 39.4971 | 574.3856
| ZN2310:PA4 | 2967 | 1897.167 | 33.36 | 0.63942 | 33.36 | 20353 | 19597 | 807665 | 2012-04-11 03:54 | 2012-04-11 05:00 | 66 | 11kV | 11352 | 172 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.12690 Berkeley Vale, Panel 17 Fdr CB tripped on a,B and C phase OC, efi, 11kV trip, #13 Tx group earth. Field efi down at S.14827. Customer arcing at PT.14130 - suspect possum across HV OH | April | 2012 | 2012Q4 | 2012 | ZN12690:PA17 | ZN12690:PA17 | ZN12690/000017 | CENTRAL COAST | OH | Not Veg | 2012-04-11 | N | 66 | N | 7 | N | N | 1.1101 | 39.4971 | 8295.7068
| ZN2310:PA8 | 1439 | 909.25 | 40.05 | 0.63186 | 40.05 | 20269 | 18046 | 807668 | 2012-04-11 05:46 | 2012-04-11 06:50 | 64 | 11kV | 64 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120430 A phase DOLF : 10 Amp suspected fatigue excluded OMS 807668 | April | 2012 | 2012Q4 | 2012 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2012-04-11 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 46.7693
| ZN2310:PA9 | 5 | 251.7579 | #N/A | 50.3516 | 39.4971 | 19584 | 9735 | 807687 | 2012-04-11 06:54 | 2012-04-11 11:10 | 256 | 11kV | 256 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | Replaced A phase 10 amp DOLF No cause found unplanned LID 120436 : Record withdrawn OMS 807687 | April | 2012 | 2012Q4 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2012-04-11 | N | 256 | N | 7 | N | N | 1.1101 | 39.4971 | 187.0772
| ZN195:PA10 | 843 | 947.138 | 31.08 | 1.1235 | 31.08 | 19309 | 7354 | 807950 | 2012-04-11 12:31 | 2012-04-11 16:20 | 229 | 11kV | 228532 | 2296 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN2635 Epping Panel 10 tripped reclosed tripped and locked out on Relays: B phase Overcurrent, Timing relay, Lockout relay. Signals: 11kV Trip. Field EFIs - None. Cause: Tree branch on Mains near LV1904 Mains on Ground Adjacent to LB1966 See OMS 809474 809484 809472 809502 807971 807962 807961 | April | 2012 | 2012Q4 | 2012 | ZN2635:PA10 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | OH | Veg | 2012-04-11 | N | 99.5348 | N | 7 | N | N | 1.1101 | 39.4971 | 167004.445
| ZN195:PA11 | 805 | 862.827 | 39.33 | 1.0718 | 39.33 | 18828 | 2356 | 808091 | 2012-04-11 15:25 | 2012-04-11 16:40 | 75 | 11kV | 4050 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | A & B phase 20 Amp DOLF's replaced No cause found Unplanned LID 120445 | April | 2012 | 2012Q4 | 2012 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2012-04-11 | N | 75 | N | 7 | N | N | 1.1101 | 39.4971 | 2959.6205
| ZN195:PA22 | 358 | 527.6707 | 45.47 | 1.4739 | 45.47 | 19768 | 12529 | 808164 | 2012-04-11 16:40 | 2012-04-11 18:40 | 120 | 11kV | 720 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Record Withdrawn OMS # 808164. No protection operation, interruption was required to perform repairs. Staff found the tie had broken holding one 11kV conductor to its insulator. The cable had already caused burning on the 11kV cross arm that the cable had fallen onto. The cross arm had to be repalced as well as the cable re-attached to the insulator. Unplanned outage LID 120447 | April | 2012 | 2012Q4 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-04-11 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 526.1548
| ZN195:PA23 | 713 | 911.7324 | 38.04 | 1.2787 | 38.04 | 20430 | 20321 | 808241 | 2012-04-12 03:12 | 2012-04-12 05:18 | 126.2833 | 11kV | 41547.2167 | 329 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Tree branch on mains (A and B phases) in Cicada Glen near Walter caused Recloser 22381 to trip CC1: 22-"Refer to SOp" FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | April | 2012 | 2012Q4 | 2012 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2012-04-12 | N | 126.2833 | N | 5 | N | N | 1.1101 | 39.4971 | 30361.4805
| ZN195:PA25 | 783 | 943.6545 | 36.36 | 1.2052 | 36.36 | 18985 | 3869 | 808242 | 2012-04-12 03:50 | 2012-04-12 06:40 | 170 | 11kV | 213010 | 1678 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN.9700 Kirrawee 11kv fdr P-23 "S.9819 Talara Kingsway" RELAYS: 51 ABC, EFI SIGNALS: 11kV Trip, TX.3 Grp Eth, Zn Eth EFI: S.9819, S.9812, S.9813, S.9312, & S.9469 REMARKS: DOp has patrolled nothing found | April | 2012 | 2012Q4 | 2012 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Veg | 2012-04-12 | N | 126.9428 | N | 5 | N | N | 1.1101 | 39.4971 | 155661.4253
| ZN195:PA28 | 902 | 1087.7107 | 37.26 | 1.2059 | 37.26 | 19104 | 4658 | 808229 | 2012-04-11 22:26 | 2012-04-12 07:50 | 564 | 11kV | 10152 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At PT.15065 the footpath side 31.5 HDO fuse operated - cause unknown | April | 2012 | 2012Q4 | 2012 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2012-04-11 | N | 564 | N | 7 | N | N | 1.1101 | 39.4971 | 7418.7822
| ZN195:PA29 | 1122 | 1204.7423 | 35.82 | 1.0737 | 35.82 | 18597 | 233 | 808252 | 2012-04-12 06:23 | 2012-04-12 10:04 | 220.65 | 11kV | 4633.65 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | rplaced blown dolf on L/F42036 LID 120450 A phase DOLF : 5 Amp CC1: 06-"Urgent - O.H Mains - No others" | April | 2012 | 2012Q4 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-04-12 | N | 220.65 | N | 5 | N | N | 1.1101 | 39.4971 | 3386.1348
| ZN195:PA3 | 304 | 729.9562 | 47.89 | 2.4012 | 47.89 | 20377 | 19957 | 808520 | 2012-04-12 13:42 | 2012-04-12 18:09 | 267 | 11kV | 1066.9 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120462 C phase DOLF : 10 Amp Excluded OMS 808520 - GIS correction | April | 2012 | 2012Q4 | 2012 | 526:34640 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2012-04-12 | N | 266.725 | N | 5 | N | N | 1.1101 | 39.4971 | 779.6591
| ZN195:PA30 | 1250 | 1262.8561 | 34.85 | 1.0103 | 34.85 | 19494 | 9047 | 808709 | 2012-04-12 21:12 | 2012-04-12 22:55 | 103 | 11kV | 252520 | 2840 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington Pa26 fdr tripped on Relay- OC,EF Signal-11kV trip, Tx4GE EFI-Nil (Frontline fault) Cause: 11kV UG fault btw Pa26 to S8252 to S6899 to S778 See 808815,7,8 exclude 808709 | April | 2012 | 2012Q4 | 2012 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2012-04-12 | N | 88.9155 | N | 5 | N | N | 1.1101 | 39.4971 | 184534.1679
| ZN195:PA4 | 1078 | 940.1203 | 43.35 | 0.8721 | 43.35 | 18698 | 1139 | 808880 | 2012-04-13 10:48 | 2012-04-13 12:20 | 92 | 11kV | 184 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120470 A phase DOLF : 10 Amp possible fuse fatigue Excluded OMS 808800 | April | 2012 | 2012Q4 | 2012 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2012-04-13 | N | 92 | N | 4 | N | N | 1.1101 | 39.4971 | 134.4618
| ZN195:PA8 | 338 | 443.3288 | 50.15 | 1.3116 | 50.15 | 20296 | 18813 | 808736 | 2012-04-13 06:54 | 2012-04-13 12:40 | 346 | 11kV | 23386 | 152 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120471 3 fault operations A & B Phase Earth fault A & B ph mains down adj Pole AJ-20590 | April | 2012 | 2012Q4 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2012-04-13 | N | 153.8553 | N | 4 | N | N | 1.1101 | 39.4971 | 17089.799
| ZN195:PA9 | 1318 | 1319.5602 | 32.59 | 1.0012 | 32.59 | 19961 | 14467 | 809477 | 2012-04-13 13:01 | 2012-04-13 19:45 | 404 | 11kV | 5775 | 55 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | At ZN12650 West Gostford, Recloser 44604 on feeder 1 tripped and locked out(Relays OC, LO) Cause: Broken Crossarm O/S #692 Dog Trap road Somersby | April | 2012 | 2012Q4 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-04-13 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 4220.1997
| 239:82127 | 125 | 159.3332 | 52.68 | 1.2747 | 52.68 | 18769 | 1868 | 809059 | 2012-04-13 15:45 | 2012-04-14 00:28 | 523 | 11kV | 64616.3 | 321 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 120475 2 fault operations Earth fault Tip truck hit mains adj pole FT-93178. Staff encountered site access issues. Excluded OMS 809064 | April | 2012 | 2012Q4 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2012-04-13 | N | 201.2969 | N | 4 | N | N | 1.1101 | 39.4971 | 47219.6862
| 239:82128 | 61 | 97.8656 | 64.76 | 1.6044 | 64.76 | 18717 | 1243 | 809184 | 2012-04-14 07:35 | 2012-04-14 10:12 | 157 | 11kV | 55849.75 | 829 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120476 2 fault operations A & B phase Overcurrent Hot joint on LV at sub 71532, feeder restored successfully see LID Report 120477. Excluded OMS No. 809184. | April | 2012 | 2012Q4 | 2012 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2012-04-14 | N | 67.37 | N | 2 | N | N | 1.1101 | 39.4971 | 40813.35
| 239:82129 | 1462 | 1041.3499 | 33.2 | 0.71228 | 33.2 | 18574 | 59 | 809267 | 2012-04-14 12:53 | 2012-04-14 14:00 | 67.0833 | 11kV | 3689.5833 | 55 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 120484 section isolated to repair xarm at pole MG-40076 | April | 2012 | 2012Q4 | 2012 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2012-04-14 | N | 67.0833 | N | 2 | N | N | 1.1101 | 39.4971 | 2696.2387
| 239:82131 | 193 | 308.8421 | 47.57 | 1.6002 | 47.57 | 18736 | 1422 | 809345 | 2012-04-15 07:09 | 2012-04-15 08:30 | 81 | 11kV | 162 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120488 single phase LLC found disconnected Excluded OMS 809345 | April | 2012 | 2012Q4 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-04-15 | N | 81 | N | 2 | N | N | 1.1101 | 39.4971 | 118.3848
| 239:82132 | 955 | 728.5201 | 32.45 | 0.76285 | 32.45 | 18572 | 57 | 809416 | 2012-04-15 20:21 | 2012-04-16 05:56 | 575.4333 | 11kV | 575.4333 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120493 single phase DOLF : 10 Amp Excluded OMS 809416 logged to incorrect sub. | April | 2012 | 2012Q4 | 2012 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | UG | Not Veg | 2012-04-15 | N | 575.4333 | N | 2 | N | N | 1.1101 | 39.4971 | 420.5097
| 239:82133 | 1324 | 944.0993 | 31.61 | 0.71307 | 31.61 | 19300 | 7323 | 809510 | 2012-04-16 09:13 | 2012-04-16 09:55 | 42 | 11kV | 1504 | 36 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.14143 Somersby Pnl.21 tripped on E/F, EFI Section of 11kV UG feeder from S.18108 Gindurra Chivers 0.1 (sw/B) to S.18052 Chovers Gindurra (sw/A) damaged by Contractor Bolte Civic, on Gindurra Rd near Chivers Rd Somersby. See 811721 811723 | April | 2012 | 2012Q4 | 2012 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | UG | Not Veg | 2012-04-16 | N | 41.7778 | N | 2 | N | N | 1.1101 | 39.4971 | 1099.0788
| 239:82136 | 1503 | 1061.9685 | 32.65 | 0.70657 | 32.65 | 18631 | 510 | 809644 | 2012-04-16 10:46 | 2012-04-16 12:31 | 105 | 11kV | 1575 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120497 Feeder isolated to repair unravelling/stranding 11kV conductor near pole DV-91012. | April | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-04-16 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 1150.9635
| 264:81231 | 291 | 1123.8357 | 46.14 | 3.862 | 46.14 | 20387 | 20033 | 809992 | 2012-04-17 07:28 | 2012-04-17 08:55 | 87 | 11kV | 2414.85 | 28 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | At PT 2142 Murrua Princess Juliana Footpath Phase blown Cause: Fuse fatigue See 810037 | April | 2012 | 2012Q4 | 2012 | ZN3154:PA12 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Not Veg | 2012-04-17 | N | 86.2446 | N | 9 | N | N | 1.1101 | 39.4971 | 1764.7012
| 264:81232 | 837 | 1175.7183 | 41.77 | 1.4047 | 41.77 | 18704 | 1184 | 810002 | 2012-04-17 08:09 | 2012-04-17 09:15 | 66 | 11kV | 66 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120508 Single phase DOLF : 10 Amp Excluded OMS 810002 TX VOLTS 242 | April | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-04-17 | N | 66 | N | 9 | N | N | 1.1101 | 39.4971 | 48.2309
| 264:81236 | 1868 | 1418.9773 | 32.19 | 0.75962 | 32.19 | 20075 | 15812 | 809979 | 2012-04-17 06:37 | 2012-04-17 11:35 | 298 | 11kV | 16540 | 94 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Wamberal Zone Pnl.10 - REC 44607 matcham Nth tripped, reclosed tripped and locked out on OC trip and IOC trip 1 Phase of 11kV down on the groundin Wanbina Rd beyond LK42162. Also burnt off bond at 285 Matcham Rd near PT11815. see #810588 810587 | April | 2012 | 2012Q4 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2012-04-17 | N | 175.9574 | N | 9 | N | N | 1.1101 | 39.4971 | 12086.9442
| 264:81238 | 581 | 732.7736 | 46.7 | 1.2612 | 46.7 | 19922 | 14021 | 810184 | 2012-04-17 11:56 | 2012-04-17 12:20 | 24 | 11kV | 24 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 120514 A & B phase DOLF : 10 Amp Operator found DOLFs blown at sub. | April | 2012 | 2012Q4 | 2012 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | UG | Not Veg | 2012-04-17 | N | 24 | N | 9 | N | N | 1.1101 | 39.4971 | 17.5385
| 264:81240 | 597 | 797.3545 | 41.81 | 1.3356 | 41.81 | 19745 | 12397 | 810201 | 2012-04-17 11:44 | 2012-04-17 12:49 | 65 | 11kV | 8060 | 124 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV panel 3 Hornsby Recloser 3203 Ferndale Nicholas Tripped. Cause:Tree branch on mains O/S 72 Hinemoa See OMS 810201 810216 | April | 2012 | 2012Q4 | 2012 | ZN847:PA2 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Veg | 2012-04-17 | N | 65 | N | 9 | N | N | 1.1101 | 39.4971 | 5890.0103
| 264:81241 | 1316 | 1209.0869 | 39.97 | 0.91876 | 39.97 | 20390 | 20042 | 810319 | 2012-04-17 14:31 | 2012-04-17 15:34 | 63 | 11kV | 17073 | 271 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12600 Lisarow Pnl. 12 tripped on C Phase timed overcurrent Dop patrolled cause not ascertained | April | 2012 | 2012Q4 | 2012 | ZN12600:PA12 | ZN12600:PA12 | ZN12600/000012 | CENTRAL COAST | OH | Veg | 2012-04-17 | N | 63 | N | 9 | N | N | 1.1101 | 39.4971 | 12476.4448
| 264:81244 | 1531 | 1129.9322 | 32.08 | 0.73804 | 32.08 | 19343 | 7613 | 810324 | 2012-04-17 14:43 | 2012-04-17 16:45 | 122 | 11kV | 610 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 120516 single phase sub isolated to replace trans lead Excluded oms 810324 | April | 2012 | 2012Q4 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2012-04-17 | N | 122 | N | 9 | N | N | 1.1101 | 39.4971 | 445.77
| ZN1287:PA11 | 1479 | 1113.867 | 31.47 | 0.75312 | 31.47 | 18963 | 3543 | 810492 | 2012-04-17 20:07 | 2012-04-17 21:15 | 68 | 11kV | 20828 | 317 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 120517 2 fault operations 3 phase Earth fault | April | 2012 | 2012Q4 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-04-17 | N | 65.7035 | N | 9 | N | N | 1.1101 | 39.4971 | 15220.4881
| ZN1287:PA12 | 935 | 701.656 | 29.63 | 0.75043 | 29.63 | 19948 | 14243 | 810505 | 2012-04-17 21:22 | 2012-04-17 23:40 | 138 | 11kV | 64480 | 975 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Unselected | N | Zn.12660 Woy Woy Pnl.6 tripped, reclosed, tripped & locked out on earth fault, lockout, timing, EFI Field EFI @ S.18564 Possum found across lightning arrestors on UGOH to S.14409 in Jirramba St near Centennial. Pole # WW1583. Lightning arrestors are damaged and require replacement - have been cut away and feeder placed back into service see # 810603 810605 | April | 2012 | 2012Q4 | 2012 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2012-04-17 | N | 66.1333 | N | 9 | N | N | 1.1101 | 39.4971 | 47120.0822
| ZN1287:PA15 | 1966 | 1587.8076 | 30.3 | 0.80763 | 30.3 | 18975 | 3607 | 810525 | 2012-04-18 03:09 | 2012-04-18 06:10 | 181 | 11kV | 236115 | 1543 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S.2196 Milperra, Panel 5 "Marigold Amour No4" 11kv feeder, tripped, reclosed and locked out on; C phase O/L, lo Alarms: 11kv trip Remarks: Tree/branch on OH Mains. 15 Broe Ave, removed by Dop Related jobs: #810641, 810646, 810650, 810532, 810525 | April | 2012 | 2012Q4 | 2012 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-04-18 | N | 153.0233 | N | 12 | N | N | 1.1101 | 39.4971 | 172545.8778
| ZN1287:PA16 | 607 | 557.5679 | 44.79 | 0.91856 | 44.79 | 20428 | 20313 | 810534 | 2012-04-18 04:46 | 2012-04-18 06:45 | 119 | 11kV | 6783 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | PT11160 Waratah Denver - Foot path phase HDO fuse blown 31.5A Cause not ascertained see # 811327 811325 (GIS) | April | 2012 | 2012Q4 | 2012 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2012-04-18 | N | 119 | N | 12 | N | N | 1.1101 | 39.4971 | 4956.8163
| ZN1287:PA17 | 1292 | 1205.5531 | 37.14 | 0.93309 | 37.14 | 20047 | 15565 | 810552 | 2012-04-18 07:00 | 2012-04-18 09:00 | 120 | 11kV | 150304 | 1333 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn2400 Berowra Panel 22 tripped on A and B phase Overcurrent Tree on mains at 661 Pacific Highway Mt Colah. See OMS 811753 811755 810552 810555 | April | 2012 | 2012Q4 | 2012 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2012-04-18 | N | 112.7562 | N | 12 | N | N | 1.1101 | 39.4971 | 109837.73
| ZN1287:PA18 | 261 | 665.0205 | 57.68 | 2.548 | 57.68 | 19338 | 7583 | 810800 | 2012-04-18 11:06 | 2012-04-18 13:00 | 114 | 11kV | 570 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | N | LID 120523 C phase DOLF : 63 Amp Volts = 242. Amps = 30 Excluded OMS # 810800 | April | 2012 | 2012Q4 | 2012 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | UG | Not Veg | 2012-04-18 | N | 114 | N | 12 | N | N | 1.1101 | 39.4971 | 416.5392
| ZN1287:PA19 | 385 | 422.2118 | #N/A | 1.0967 | 39.4971 | 19270 | 6758 | 811546 | 2012-04-18 13:40 | 2012-04-18 14:10 | 30 | 11kV | 60 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | Unplanned Outage LID 120527 No protection operations. Section isolated to remedy low mains at pole DN-60001. No OMS # | April | 2012 | 2012Q4 | 2012 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-04-18 | N | 30 | N | 12 | N | N | 1.1101 | 39.4971 | 43.8462
| ZN1287:PA2 | 783 | 822.2544 | #N/A | 1.0501 | 39.4971 | 19894 | 13708 | 810918 | 2012-04-18 13:14 | 2012-04-18 14:55 | 101 | 11kV | 46965 | 465 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn877 Hornsby Section of Panel 5 Recloser 2378 Dural Pacific tripped on IOC and OC. Cause: Tree on Mains - Removed by dop See OMS 810918 810919 810921 | April | 2012 | 2012Q4 | 2012 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Veg | 2012-04-18 | N | 101 | N | 12 | N | N | 1.1101 | 39.4971 | 34320.6368
| ZN1287:PA20 | 48 | 24.8498 | 29.66 | 0.5177 | 29.66 | 20229 | 17370 | 810845 | 2012-04-18 11:56 | 2012-04-18 15:15 | 199 | 11kV | 144105 | 2165 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12610 Long Jetty Pnl.22 tripped, reclosed, tripped and locked out on A phase OC, EF. Tree branch outside 122 Swadling st. Damaged USL43077 see 811337 811338 | April | 2012 | 2012Q4 | 2012 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Veg | 2012-04-18 | N | 66.5612 | N | 12 | N | N | 1.1101 | 39.4971 | 105307.6836
| ZN1287:PA21 | 1685 | 1299.7479 | 32.43 | 0.77136 | 32.43 | 19371 | 7972 | 810986 | 2012-04-18 14:14 | 2012-04-18 15:36 | 82 | 11kV | 13858 | 169 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn.14144 Wamberal Pnl.2 -REC 44946 Kunarra Rd tripped, reclosed, tripped and locked out on Earth Trip See 811373 811376 | April | 2012 | 2012Q4 | 2012 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2012-04-18 | N | 82 | N | 12 | N | N | 1.1101 | 39.4971 | 10127.0177
| ZN1287:PA22 | 981 | 670.0457 | 34.84 | 0.68302 | 34.84 | 19411 | 8383 | 811258 | 2012-04-18 22:46 | 2012-04-19 00:20 | 94 | 11kV | 85236 | 907 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2568 St Peters 11kV OCB Pa19 fdr tripped on: Relays - Bph O/C Earth Leakage EFI Fault Check EFI - S35080 Signals - 11kV trip ZE Tx4GE Cause: 11kV fdr UG fault from SwB@S35080 to SwA@S5795 to S2166 See 812815,9 exclude 811258 | April | 2012 | 2012Q4 | 2012 | ZN2568:PA19 | ZN2568:PA19 | ZN02568/000019 | INNER WEST | UG | Not Veg | 2012-04-18 | N | 93.9757 | N | 12 | N | N | 1.1101 | 39.4971 | 62287.9548
| ZN1287:PA23 | 944 | 949.214 | 40.59 | 1.0055 | 40.59 | 19773 | 12548 | 811260 | 2012-04-18 22:57 | 2012-04-19 01:00 | 123 | 11kV | 3567 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | PT12798 Geoffrey Wyong 0.1 - Footpath Phase HDO blew 20A Cause not ascertained | April | 2012 | 2012Q4 | 2012 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Veg | 2012-04-18 | N | 123 | N | 12 | N | N | 1.1101 | 39.4971 | 2606.6584
| ZN1287:PA24 | 574 | 1613.6014 | 39.08 | 2.8112 | 39.08 | 19767 | 12527 | 811294 | 2012-04-19 06:14 | 2012-04-19 07:12 | 58 | 11kV | 75342 | 1299 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn.12690 berkeley Vale Pnl.12 tripped, reclosed, tripped and locked out on A & C phase timed overcurrent. DOp found dead bird at tee to LK42802 at Pole WY31914. DOp reports bonding at pole requires attention ASAP | April | 2012 | 2012Q4 | 2012 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2012-04-19 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 55057.7114
| ZN1287:PA3 | 1640 | 1230.3878 | 31.18 | 0.75024 | 31.18 | 19660 | 11015 | 811358 | 2012-04-19 08:10 | 2012-04-19 11:54 | 224 | 11kV | 1344 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120534 No protection operations. fdr isolated to repair tapping to sub 72182 under A/P. Excluded OMS # 811358 | April | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-04-19 | N | 224 | N | 6 | N | N | 1.1101 | 39.4971 | 982.1556
| ZN1287:PA4 | 1011 | 866.5118 | 31.09 | 0.85708 | 31.09 | 20339 | 19404 | 811552 | 2012-04-19 10:30 | 2012-04-19 13:10 | 160 | 11kV | 8640 | 54 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S4455 Pacific Bloomsbury 400A fuse blown on A and B phase of distributor 3. Cause: Tree branch on Mains see OMS 812927/811543/811538 | April | 2012 | 2012Q4 | 2012 | ZN195:PA22 | ZN195:PA22 | ZN00195/000022 | KU-RING-GAI | OH | Veg | 2012-04-19 | N | 160 | N | 6 | N | N | 1.1101 | 39.4971 | 6313.8572
| ZN1287:PA5 | 1178 | 1021.3087 | 34.01 | 0.86699 | 34.01 | 19200 | 5783 | 811195 | 2012-04-18 19:37 | 2012-04-19 13:15 | 1058 | 11kV | 19096 | 32 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S 17014, supply lost on section of 11kV feeder Cause: Broken crossarm | April | 2012 | 2012Q4 | 2012 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Veg | 2012-04-18 | N | 596.75 | N | 12 | N | N | 1.1101 | 39.4971 | 13954.7936
| ZN1287:PA6 | 914 | 653.3237 | 32.38 | 0.7148 | 32.38 | 19954 | 14282 | 810909 | 2012-04-18 13:08 | 2012-04-19 15:00 | 1552 | 11kV | 45579 | 780 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn.14143 Somersby Pnl.17 tripped on A & B phase Overcurrent Abnormal Switching: AB 45422 CLOSED - Sw A @ S.18052 OPENED Tree in Vittasalos Rd near Howes Rd brought down 1 bay of 11kV mains. Feeder isolated and earthed + permits issued. See # 812702 812703 | April | 2012 | 2012Q4 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-04-18 | N | 58.4346 | N | 12 | N | N | 1.1101 | 39.4971 | 33307.7888
| ZN10995:PA1 | 2087 | 1474.5742 | 32.69 | 0.70655 | 32.69 | 19709 | 11794 | 811801 | 2012-04-19 15:55 | 2012-04-19 17:30 | 95 | 11kV | 1900 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Wyong Zn Pnl.12 - Autolinks 44778 interrupted for safety Lineworker required 11kV CCT to be isolated + Earthed to safely remove tree off mains | April | 2012 | 2012Q4 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-04-19 | N | 95 | N | 6 | N | N | 1.1101 | 39.4971 | 1388.464
| ZN10995:PA12 | 1359 | 1073.9847 | 33.64 | 0.79028 | 33.64 | 19984 | 14872 | 811920 | 2012-04-20 00:24 | 2012-04-20 01:30 | 66 | 11kV | 858 | 13 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN2466 Flemington, Panel 39 tripped on: EF, SC and Signalled: EFI, Fault check, TX.3 Group Earth Remarks: 11KV feeder from ZN2466 Flemington to S6911 Figtree Alpha Related jobs: #811987, 811920 | April | 2012 | 2012Q4 | 2012 | ZN2466:PA39 | ZN1610:PA8 | ZN01610/000008 | PARRAMATTA | UG | Not Veg | 2012-04-20 | N | 66 | N | 6 | N | N | 1.1101 | 39.4971 | 627.0011
| ZN10995:PA13 | 1401 | 1128.8822 | 34.14 | 0.80577 | 34.14 | 19318 | 7437 | 811896 | 2012-04-19 20:27 | 2012-04-20 03:00 | 393 | 11kV | 3740 | 24 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Light | N | @ZN3472 Sefton Panel 39 "Dasea rook" feeder. Relay operatins: - A & C phase overcurrent, EFI Signals: Zone Earth, TX2 Groupe Earth, 11kv trip and battery defect Remarks: @Sub 2831 Muir Dasea No2 11kv end boxes lown and all sub doors blown open. Related jobs: #811896, 811901, 812033, 812034, 812032 | April | 2012 | 2012Q4 | 2012 | ZN3472:PA39 | ZN35900:PA10 | ZN35900/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-04-19 | N | 155.8333 | N | 6 | N | N | 1.1101 | 39.4971 | 2733.0817
| ZN10995:PA2 | 2453 | 1906.0424 | 37.67 | 0.77703 | 37.67 | 20113 | 16083 | 811925 | 2012-04-20 02:46 | 2012-04-20 04:30 | 104 | 11kV | 155616 | 1649 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ZN874 Concord Panel 18 tripped on EF, EFI Remarks: UG Fault. UG Fault on 11kv feeder from S3303 Shipham Brewer to S513 Wellbank warbrick to S2479 Ian Parade to S2099 shackle corm. Related jobs: #811925, 811977, 811976 | April | 2012 | 2012Q4 | 2012 | ZN874:PA18 | ZN874:PA18 | ZN00874/000018 | CANADA BAY | UG | Not Veg | 2012-04-20 | N | 94.3699 | N | 6 | N | N | 1.1101 | 39.4971 | 113719.5829
| ZN10995:PA5 | 1517 | 1342.7574 | 40.63 | 0.88514 | 40.63 | 19523 | 9200 | 811928 | 2012-04-20 05:06 | 2012-04-20 07:40 | 154 | 11kV | 8624 | 56 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11160 Waratah Denver - Foot path phase HDO fuse blown (31.5A) Fuse Fatigue | April | 2012 | 2012Q4 | 2012 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Not Veg | 2012-04-20 | N | 154 | N | 6 | N | N | 1.1101 | 39.4971 | 6302.1648
| ZN10995:PA6 | 1930 | 1311.3993 | 37.69 | 0.67948 | 37.69 | 18661 | 771 | 811935 | 2012-04-20 06:56 | 2012-04-20 08:35 | 99 | 11kV | 4950 | 50 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | PT14672 Roper Blueridge 0.1 - roadside HDO fuse blown Surge arrestor blown | April | 2012 | 2012Q4 | 2012 | ZN14892:PA6 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2012-04-20 | N | 99 | N | 6 | N | N | 1.1101 | 39.4971 | 3617.314
| ZN10995:PA7 | 2186 | 1353.0461 | 33.83 | 0.61896 | 33.83 | 18802 | 2166 | 811936 | 2012-04-20 07:03 | 2012-04-20 09:30 | 147 | 11kV | 735 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120545 Fuse carrier burnt up. Replaced OK Excluded OMS # 811936 | April | 2012 | 2012Q4 | 2012 | 526:34640 | 526:34640 | ZN00526/034640 | SINGLETON | OH | Not Veg | 2012-04-20 | N | 147 | N | 6 | N | N | 1.1101 | 39.4971 | 537.1163
| ZN10995:PA8 | 668 | 1073.1373 | 60.1 | 1.6065 | 60.1 | 18763 | 1784 | 811913 | 2012-04-19 22:14 | 2012-04-20 13:45 | 931 | 11kV | 30066 | 153 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120542 3 fault operations Sensitive Earth fault Tapperell sub 52338 left isolated. Repairs to wiring to be completed in business hours (nailed pole) | April | 2012 | 2012Q4 | 2012 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2012-04-19 | N | 196.5098 | N | 6 | N | N | 1.1101 | 39.4971 | 21971.346
| ZN10998:PA1 | 502 | 295.1754 | #N/A | 0.588 | 39.4971 | 20134 | 16193 | 812131 | 2012-04-20 11:15 | 2012-04-20 14:30 | 195 | 11kV | 28485 | 550 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | 11kv fdr pa35 fdr Ex S630 Masct tripped relays-Aph O/L EFI Signals-11kv trip ZE No6GE EFI- S5957 11kv RMI failure at S5957 caught on fire. See 812994,7,8 Exclude 812121,31 | April | 2012 | 2012Q4 | 2012 | ZN630:PA35 | ZN340:PA35 | ZN00340/000035 | BAYSIDE | Unknown | Not Veg | 2012-04-20 | N | 51.7909 | N | 6 | N | N | 1.1101 | 39.4971 | 20815.9978
| ZN10998:PA10 | 2032 | 1426.5639 | 42.51 | 0.70205 | 42.51 | 19330 | 7528 | 812385 | 2012-04-21 07:39 | 2012-04-21 10:05 | 146 | 11kV | 876 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120550 B phase DOLF : 10 Amp A - 255V 2A, B -248V 23A, C - 250V 7A. Excluded OMS 812385. | April | 2012 | 2012Q4 | 2012 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | UG | Not Veg | 2012-04-21 | N | 146 | N | 6 | N | N | 1.1101 | 39.4971 | 640.155
| ZN10998:PA13 | 1244 | 1456.3701 | 36.72 | 1.1707 | 36.72 | 20102 | 16001 | 813064 | 2012-04-21 18:40 | 2012-04-21 19:20 | 40 | 11kV | 40 | 1 | HV | 3rd Party Action | 3rd Party Impact | 3rd Party Asset | Unplanned | Unselected | N | S5201 Paddingotn Pa28 Left fdr operated on Aph O/C following a fault on the customers switchgear. Customers installation fault | April | 2012 | 2012Q4 | 2012 |  |  |  |  | Unknown | Not Veg | 2012-04-21 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 29.2308
| ZN10998:PA16 | 644 | 371.4224 | 45.05 | 0.57674 | 45.05 | 18893 | 3046 | 812509 | 2012-04-21 17:00 | 2012-04-21 20:50 | 230 | 11kV | 460 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 120561 A phase DOLF : 5 Amp faulty lightning arrestor | April | 2012 | 2012Q4 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2012-04-21 | N | 230 | N | 6 | N | N | 1.1101 | 39.4971 | 336.1544
| ZN10998:PA17 | 2059 | 1582.0929 | 33.09 | 0.76838 | 33.09 | 19232 | 6330 | 812535 | 2012-04-21 20:20 | 2012-04-21 21:19 | 59.1 | 11kV | 69974.4 | 1184 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At ZN.10994 Mortdale, P-9 "Station the Strad' fdr tripped on: RELAYS: 50 TAB, 50 TN EFI SIGNALS: 11kV trip. REMARKS: Animals/Birds. Possum on HV UGOH to AB30078 | April | 2012 | 2012Q4 | 2012 | ZN10994:PA9 | ZN10994:PA9 | ZN10994/000009 | GEORGES RIVER | OH | Not Veg | 2012-04-21 | N | 59.1 | N | 6 | N | N | 1.1101 | 39.4971 | 51135.2276
| ZN10998:PA18 | 1363 | 1074.0714 | 37.98 | 0.78802 | 37.98 | 19279 | 7168 | 812536 | 2012-04-21 20:22 | 2012-04-21 22:11 | 109 | 11kV | 51539 | 485 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Zone Pa11 fdr tripped on Earth Leakage ACph IOC & EFI Zone Earth No4GE 11kvTrip EFI- Nil EFI failed to operate @S4556 UG cable fault btw S4556 to S2870. S2870 HAZ RMI. LV// required to extend cutout beyond HAZ for test & repaire. Switching tag left @S2870 See 813088,9,90,97 GIS 813111 Exclude 812536,40 | April | 2012 | 2012Q4 | 2012 | ZN1788:PA11 | ZN35700:PA10 | ZN35700/000010 | RANDWICK | UG | Not Veg | 2012-04-21 | N | 106.266 | N | 6 | N | N | 1.1101 | 39.4971 | 37663.1811
| ZN10998:PA19 | 947 | 847.6966 | #N/A | 0.89514 | 39.4971 | 19133 | 4852 | 812548 | 2012-04-21 23:09 | 2012-04-22 03:41 | 272 | 11kV | 378046 | 1613 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | At ZN.9118 Cronulla P-3 "Binaville Ave" fdr tripped, reclosed, tripped and locked on: RELAYS: A phase timed O/C, timing relay, lockout relay, & EFI SIGNALS: 11kV trip, Zn Earth, TX.1 Grp Eth FIELD EFIs: S.9876, S.9848 ABNORMAL: Rec 35005 Bundeena Liverpool is closed, AB 35520 is opened REMARKS: Pole defective/Failure. Top of UGOH pole in Woolooware Rd near Rutherland Ave Burraneer broke off causing the HV mains to fall into LV mains. | April | 2012 | 2012Q4 | 2012 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2012-04-21 | N | 234.3745 | N | 6 | N | N | 1.1101 | 39.4971 | 276264.8663
| ZN10998:PA2 | 877 | 729.0942 | 35.22 | 0.83135 | 35.22 | 19527 | 9296 | 812583 | 2012-04-22 08:44 | 2012-04-22 10:30 | 106.25 | 11kV | 106.25 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT2077 Galston Swains No1 11kV fuse operated on A phase Cause: Fuse fatigue. See OMS 812895 812583 | April | 2012 | 2012Q4 | 2012 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-04-22 | N | 106.25 | N | 2 | N | N | 1.1101 | 39.4971 | 77.6444
| ZN10998:PA24 | 627 | 569.6893 | #N/A | 0.9086 | 39.4971 | 18774 | 1913 | 812686 | 2012-04-22 22:16 | 2012-04-23 00:43 | 147 | 11kV | 89491 | 663 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn.14144 Wamberal Pnl.10 tripped on B & C phase OC, EFI Possible tree brnach in Brooks St. See 812718 812719 812720 | April | 2012 | 2012Q4 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2012-04-22 | N | 134.9789 | N | 2 | N | N | 1.1101 | 39.4971 | 65397.3833
| ZN10998:PA25 | 836 | 465.6572 | 38.28 | 0.55701 | 38.28 | 18854 | 2591 | 812715 | 2012-04-23 07:35 | 2012-04-23 08:30 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120571 A phase DOLF : 31 Amp excluded OMS 812715 | April | 2012 | 2012Q4 | 2012 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | UG | Not Veg | 2012-04-23 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 40.1924
| ZN10998:PA26 | 929 | 853.5684 | 46.15 | 0.9188 | 46.15 | 19766 | 12501 | 812775 | 2012-04-23 08:48 | 2012-04-23 14:30 | 342 | 11kV | 1212 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 120573 Single phase DOLF : 10 Amp Excluded OMS 812775 | April | 2012 | 2012Q4 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-04-23 | N | 202 | N | 3 | N | N | 1.1101 | 39.4971 | 885.6939
| ZN10998:PA28 | 1121 | 739.622 | 40.04 | 0.65979 | 40.04 | 20324 | 19253 | 813005 | 2012-04-23 12:51 | 2012-04-23 15:00 | 129 | 11kV | 8127 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | N | LID 120575 C phase DOLF : 31 Amp 242 volts. 64, 27, 115 amps Excluded oms 813005 | April | 2012 | 2012Q4 | 2012 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | UG | Not Veg | 2012-04-23 | N | 129 | N | 3 | N | N | 1.1101 | 39.4971 | 5938.9719
| ZN10998:PA29 | 1622 | 1317.0128 | 43.47 | 0.81197 | 43.47 | 19960 | 14464 | 813260 | 2012-04-24 02:30 | 2012-04-24 04:50 | 140 | 11kV | 15680 | 112 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT12231 Government Omega - B & C phase fuses blown 31.5A Possum see 813283 GIS (813285 813284) | April | 2012 | 2012Q4 | 2012 | ZN12590:PA6 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2012-04-24 | N | 140 | N | 6 | N | N | 1.1101 | 39.4971 | 11458.4815
| ZN10998:PA3 | 1237 | 834.5255 | 33.57 | 0.67464 | 33.57 | 20091 | 15901 | 813267 | 2012-04-24 06:25 | 2012-04-24 08:40 | 135 | 11kV | 1620 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT46693 The Ridgeway Timber - Footpath side 16K HVDO open Fuse fatigue - failed at crimp point | April | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2012-04-24 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 1183.8482
| ZN10998:PA31 | 1727 | 1189.5354 | 46.09 | 0.68879 | 46.09 | 18637 | 568 | 813321 | 2012-04-24 09:07 | 2012-04-24 11:00 | 113 | 11kV | 1130 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120584 C Phase 5A Line Fuse - no cause found | April | 2012 | 2012Q4 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-04-24 | N | 113 | N | 6 | N | N | 1.1101 | 39.4971 | 825.7707
| ZN10998:PA32 | 1481 | 1528.5493 | 38.1 | 1.0321 | 38.1 | 19779 | 12610 | 813468 | 2012-04-24 12:40 | 2012-04-24 16:00 | 200 | 11kV | 200 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120590 No protection operation 11kV dropper lead broken off at top of B Phase DOLF | April | 2012 | 2012Q4 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2012-04-24 | N | 200 | N | 6 | N | N | 1.1101 | 39.4971 | 146.1541
| ZN10998:PA5 | 584 | 322.8563 | 30.75 | 0.55284 | 30.75 | 19113 | 4702 | 813382 | 2012-04-24 10:22 | 2012-04-24 17:34 | 432 | 11kV | 156757 | 1593 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 120587 & 120588 Hazemeyer unit failed at the Rutherford Rd Switching cubicle, blowing the door of the switching cubicle open at the time the Hazemeyer unit failed. Note sub 71820 McLintock Dr had to be placed in LV parallel to restore supply volts 247V 248v 250V at LV board after being placed in LV parallell. | April | 2012 | 2012Q4 | 2012 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | UG | Not Veg | 2012-04-24 | N | 98.4036 | N | 6 | N | N | 1.1101 | 39.4971 | 114553.3921
| ZN10998:PA8 | 1059 | 1393.7577 | 41.97 | 1.3161 | 41.97 | 19740 | 12341 | 813590 | 2012-04-24 15:28 | 2012-04-24 19:45 | 257 | 11kV | 17052 | 192 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 120592 3 fault operations B phase Sensitive Earth Fault B phase OHM down between poles CN-90147 & MD-30388 | April | 2012 | 2012Q4 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-04-24 | N | 88.8125 | N | 6 | N | N | 1.1101 | 39.4971 | 12461.0987
| ZN10998:PA9 | 771 | 641.4962 | 43.06 | 0.83203 | 43.06 | 18750 | 1613 | 815081 | 2012-04-25 11:15 | 2012-04-25 13:05 | 110 | 11kV | 156266 | 1433 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 120597 Bph tapping burnt off line side of ABS 1492. Excluded OMS No. 813782 | April | 2012 | 2012Q4 | 2012 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2012-04-25 | N | 109.0482 | N | 7 | N | N | 1.1101 | 39.4971 | 114194.5837
| ZN36100:PA1 | 880 | 1081.8507 | 41.39 | 1.2294 | 41.39 | 19678 | 11192 | 813821 | 2012-04-25 14:06 | 2012-04-25 14:40 | 34.05 | 11kV | 87917.1 | 2582 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120598 No Protection operation. 11kV Tapping off at UGOH on pole KU-41158. Feeder switched to isolate problem - repairs arranged for Thursday 26/4/12 | April | 2012 | 2012Q4 | 2012 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2012-04-25 | N | 34.05 | N | 7 | N | N | 1.1101 | 39.4971 | 64247.2236
| ZN36100:PA12 | 1312 | 1370.7075 | 31.13 | 1.0447 | 31.13 | 18710 | 1212 | 813736 | 2012-04-25 05:04 | 2012-04-25 15:20 | 616 | 11kV | 11088 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 12095 Single Phase 10A Line DOLF 11kV Mains off pole GS-44587 & on ground | April | 2012 | 2012Q4 | 2012 | 507:80925 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2012-04-25 | N | 616 | N | 7 | N | N | 1.1101 | 39.4971 | 8102.7834
| ZN36100:PA13 | 498 | 1333.9193 | 37.36 | 2.6786 | 37.36 | 18646 | 717 | 813792 | 2012-04-25 11:40 | 2012-04-25 15:20 | 220 | 11kV | 1760 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 120596 Feeder Section Isolated to repair 11kV main off crossarm at Jarrett Sub 52134 Section beyond Line Fuse 41300 already off at this time - see OMS 814064 | April | 2012 | 2012Q4 | 2012 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Not Veg | 2012-04-25 | N | 220 | N | 7 | N | N | 1.1101 | 39.4971 | 1286.1561
| ZN36100:PA15 | 766 | 807.1567 | 30.88 | 1.0537 | 30.88 | 19147 | 4908 | 813859 | 2012-04-25 16:22 | 2012-04-25 17:55 | 93 | 11kV | 204816 | 2308 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | At Zn3922 Drummoyne 11KV Panel 5, "Byrnes Manning" Feeder, has tripped on. Signals: GE, ZE and 11KV trip. Relays: Aph timed, EFI, FC. Field EFI's: Sub 36165, Sub 7583, Sub 7681, Sub 7682, Sub 7683 Remarks: UG fault. Between Sw/B @ Sub 7683 Margaret Warayama and Sw/A @ Sub 8614 Yara Margaret Related jobs: #813859, 815544, 815543 | April | 2012 | 2012Q4 | 2012 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2012-04-25 | N | 88.7418 | N | 7 | N | N | 1.1101 | 39.4971 | 149673.4918
| ZN36100:PA16 | 608 | 679.2748 | 34.82 | 1.1172 | 34.82 | 19035 | 4267 | 813869 | 2012-04-25 18:05 | 2012-04-25 19:18 | 73 | 11kV | 219 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120599 section isolated to repair "A" phase open circuit at pole MT-10363 Excluded OMS 813869 | April | 2012 | 2012Q4 | 2012 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2012-04-25 | N | 73 | N | 7 | N | N | 1.1101 | 39.4971 | 160.0387
| ZN36100:PA19 | 2593 | 1405.9365 | 31.13 | 0.5422 | 31.13 | 19996 | 14913 | 813873 | 2012-04-25 21:08 | 2012-04-25 21:49 | 41 | 11kV | 1785 | 861 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 120600 Fdr off loaded to open faulty ABS 40293 Excluded OMS 813873 | April | 2012 | 2012Q4 | 2012 | 502:48010 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2012-04-25 | N | 2.0732 | N | 7 | N | N | 1.1101 | 39.4971 | 1304.4254
| ZN36100:PA2 | 1128 | 884.6629 | 35.55 | 0.78428 | 35.55 | 18940 | 3418 | 814024 | 2012-04-26 10:10 | 2012-04-26 10:50 | 40 | 11kV | 360 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120603 C phase DOLF : 20 Amp | April | 2012 | 2012Q4 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2012-04-26 | N | 40 | N | 2 | N | N | 1.1101 | 39.4971 | 263.0774
| ZN36100:PA20 | 1052 | 916.4606 | 31.22 | 0.87116 | 31.22 | 19293 | 7313 | 814087 | 2012-04-26 11:30 | 2012-04-26 13:00 | 90 | 11kV | 3870 | 43 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matravile Pa16 fdr tripped on Earth Fault EFI Alarms 11kv trip Ze No4GE EFI-S8139 S5211 S5022 S6134 S455 S492 S8535 S8536 Cause - Cable fault suspected to be caused by stake hit into ground cnr Simblist and Friendship Rd Port Botany See 814475 GIS 814089 Exclude 814087,95,102,12 | April | 2012 | 2012Q4 | 2012 | ZN1788:PA16 | ZN35700:PA13 | ZN35700/000013 | RANDWICK | UG | Not Veg | 2012-04-26 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 2828.0819
| ZN36100:PA21 | 1567 | 1127.9263 | 31.47 | 0.7198 | 31.47 | 18759 | 1738 | 814355 | 2012-04-27 08:14 | 2012-04-27 09:30 | 76 | 11kV | 13832 | 182 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120611 burnt off tapping Newcastle Rd x Albert St | April | 2012 | 2012Q4 | 2012 | 258:80775 | 258:80775 | ZN00258/080775 | NEWCASTLE | OH | Not Veg | 2012-04-27 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 10108.0176
| ZN36100:PA23 | 982 | 846.7648 | 30.96 | 0.86229 | 30.96 | 20185 | 16759 | 814398 | 2012-04-27 09:34 | 2012-04-27 11:50 | 136 | 11kV | 408 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120617 Single phase DOLF : 10 Amp. excluded OMS 814398 | April | 2012 | 2012Q4 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2012-04-27 | N | 136 | N | 3 | N | N | 1.1101 | 39.4971 | 298.1544
| ZN36100:PA25 | 2073 | 1359.2254 | #N/A | 0.65568 | 39.4971 | 19620 | 10390 | 814448 | 2012-04-27 10:48 | 2012-04-27 15:30 | 282 | 11kV | 20743 | 325 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | @Zn1610 Homebush Bay Panel 17 "Sub 8920 Perkins Spitz" feeder tripped. Relays:I/T receive, EFI. Signals - 11KV trip, EFI, TX2 Group earth. @Sub 1191 Suttor St (2F2) Relays: No 1 TX C phase diff, I/T send Remarks: Transformer failure. Due to character limitation for more information please ask for outage report from network security. Related jobs: #814439, 815569, 815572, 814448, 815570 | April | 2012 | 2012Q4 | 2012 | ZN1610:PA17 | ZN1610:PA17 | ZN01610/000017 | PARRAMATTA | UG | Not Veg | 2012-04-27 | N | 63.8246 | N | 3 | N | N | 1.1101 | 39.4971 | 15158.3726
| ZN36100:PA27 | 779 | 1253.5287 | 36.87 | 1.6092 | 36.87 | 18701 | 1176 | 814665 | 2012-04-28 00:37 | 2012-04-28 02:13 | 96 | 11kV | 97632 | 1017 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | At S847 Hornsby Panel 46 tripped on Relays: A and C phase Timed and IOC, B phase Timed , Timing Relay, Lockout and Fault Check with FI. Signals: 11kV Trip, Zone Earth and No3 Tx Group Earth, Tx3 UV. Cause Possum on PT2192. | April | 2012 | 2012Q4 | 2012 | ZN847:PA46 | ZN847:PA46 | ZN00847/000046 | HORNSBY | OH | Not Veg | 2012-04-28 | N | 96 | N | 4 | N | N | 1.1101 | 39.4971 | 71346.5859
| ZN36100:PA5 | 1490 | 1340.3653 | 33.54 | 0.89957 | 33.54 | 19649 | 10821 | 814672 | 2012-04-28 07:58 | 2012-04-28 08:12 | 14 | 11kV | 196 | 14 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV from LB45058 to LB41248 interrupted by DOp PT/Section of feeder interrupted to allow branch to be removed from HV mains | April | 2012 | 2012Q4 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2012-04-28 | N | 14 | N | 4 | N | N | 1.1101 | 39.4971 | 143.231
| ZN36100:PA6 | 2215 | 1623.3984 | 40.88 | 0.73291 | 40.88 | 19886 | 13618 | 814701 | 2012-04-28 09:28 | 2012-04-28 10:45 | 77 | 11kV | 35180 | 460 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9900 Menai P-5 "Gould Windle' fdr opened on Earth Fault: RELAYS: Earth fault SIGNALS: 11kV Trip, TX.1 Group Earth, Zone Earth, FIELD EFIs: S.9912 REMARKS: UG Fault. UG cable fault S.9012 Gould Windle to S.9015 Windle place. Sw/B closed at S.9526 Hall Bradman. Haz RMIs at S.9912 and S.9015, LV// required for both DCs for Tester/Jointer work. | April | 2012 | 2012Q4 | 2012 | ZN9900:PA5 | ZN9900:PA5 | ZN09900/000005 | SUTHERLAND | UG | Not Veg | 2012-04-28 | N | 76.4783 | N | 4 | N | N | 1.1101 | 39.4971 | 25708.5064
| ZN36100:PA7 | 805 | 616.7327 | 38.46 | 0.76613 | 38.46 | 19630 | 10493 | 814840 | 2012-04-28 20:29 | 2012-04-28 21:00 | 30.9 | 11kV | 1977.6 | 64 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | PT12864 Thomas Walker Platypus - Foot Path & Centre Phase HDOs ruptured Low IR. Possum | April | 2012 | 2012Q4 | 2012 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2012-04-28 | N | 30.9 | N | 4 | N | N | 1.1101 | 39.4971 | 1445.1718
| ZN36100:PA8 | 792 | 1365.6476 | 34.74 | 1.7243 | 34.74 | 19028 | 4245 | 814879 | 2012-04-29 10:20 | 2012-04-29 13:40 | 200.4333 | 11kV | 801.7333 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 120631 section isolated to repair faulty crossarm at pole 4L-30001. | April | 2012 | 2012Q4 | 2012 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2012-04-29 | N | 200.4333 | N | 1 | N | N | 1.1101 | 39.4971 | 585.8831
| 526:34633 | 118 | 103.0465 | 36.46 | 0.87328 | 36.46 | 20204 | 17026 | 815074 | 2012-04-30 09:47 | 2012-04-30 12:00 | 133 | 11kV | 20482 | 154 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S5595 Kitchener Frere 630A fuse blown on on C phase of distributor 1. Cause: Cable Fault See OMS 815083 815074 | April | 2012 | 2012Q4 | 2012 | ZN965:PA8 | ZN965:PA8 | ZN00965/000008 | HORNSBY | UG | Not Veg | 2012-04-30 | N | 133 | N | 5 | N | N | 1.1101 | 39.4971 | 14967.6415
| 526:34635 | 31 | 55.5714 | 45.88 | 1.7926 | 45.88 | 20172 | 16570 | 815278 | 2012-04-30 13:44 | 2012-04-30 15:20 | 96 | 11kV | 197170 | 3518 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S 36300 Balgowlah North Pa11 Feeder tripped. relays Basler timed earth, fault, EFI Cause: Suspect underground fault on 11kv feeder See 815568 815532 815536 and withdrawn records 815278 815298 815305 | April | 2012 | 2012Q4 | 2012 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2012-04-30 | N | 56.046 | N | 5 | N | N | 1.1101 | 39.4971 | 144086.0205
| 526:34636 | 126 | 491.7478 | 50.56 | 3.9028 | 50.56 | 18982 | 3841 | 815317 | 2012-04-30 14:31 | 2012-04-30 16:45 | 134 | 11kV | 267.5667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 120638 A phase DOLF : 10 Amp. | April | 2012 | 2012Q4 | 2012 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | UG | Not Veg | 2012-04-30 | N | 133.7833 | N | 5 | N | N | 1.1101 | 39.4971 | 195.5298
| 526:34637 | 167 | 464.6744 | 50.09 | 2.7825 | 50.09 | 18930 | 3354 | 815400 | 2012-04-30 16:48 | 2012-04-30 20:10 | 202 | 11kV | 284320 | 1459 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S 36300 Balgowlah North Pa11 Feeder tripped. relays Basler OC, Earth Fault, EFI Cause: Suspect underground fault on 11kv feeder See 815696 815700 815705 815400 | April | 2012 | 2012Q4 | 2012 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | UG | Not Veg | 2012-04-30 | N | 194.8732 | N | 5 | N | N | 1.1101 | 39.4971 | 207772.67
| 526:34639 | 265 | 319.0905 | 42.17 | 1.2041 | 42.17 | 19676 | 11179 | 815502 | 2012-05-01 06:30 | 2012-05-01 08:15 | 105 | 11kV | 420 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 120648 Single phase DOLF : 10 Amp TREE BRANCH ON ARRESTOR. VOLTS = 243 LOAD = 10A Excluded OMS REPORT NO 815502. | May | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2012-05-01 | N | 105 | N | 7 | N | N | 1.1101 | 39.4971 | 306.9236
| 526:34640 | 167 | 1244.8422 | 50.58 | 7.4541 | 50.58 | 19941 | 14198 | 815443 | 2012-04-30 17:38 | 2012-05-01 11:35 | 1077 | 11kV | 47721 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Section fo Berowa Pa11. recloser 1238 Milson Passage tripped reclosed tripped and locke dout on A and C phase O/C Cause Feeder patrolled by Hornsby OH and Nothing found. See OMS 816492 816491 815443 | April | 2012 | 2012Q4 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2012-04-30 | N | 822.7759 | N | 5 | N | N | 1.1101 | 39.4971 | 34873.0993
| 526:34641 | 795 | 440.0318 | 28.46 | 0.5535 | 28.46 | 18608 | 280 | 815647 | 2012-05-01 10:40 | 2012-05-01 11:35 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120651 C phase DOLF : 10 Amp Excluded OMS REPORT NO 815647. VOLTS = 247 | May | 2012 | 2012Q4 | 2012 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2012-05-01 | N | 55 | N | 7 | N | N | 1.1101 | 39.4971 | 40.1924
| 526:34643 | 460 | 371.9143 | 35.12 | 0.80851 | 35.12 | 19966 | 14626 | 815923 | 2012-05-01 16:02 | 2012-05-01 17:45 | 103 | 11kV | 9373 | 91 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1765 Sutton Ida B phase HV drop out fuse blown. Cause: Fuse fatigue. See OMS 816459 816365 | May | 2012 | 2012Q4 | 2012 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2012-05-01 | N | 103 | N | 7 | N | N | 1.1101 | 39.4971 | 6849.5119
| 526:34644 | 2 | 6.9403 | 29.27 | 3.4701 | 29.27 | 20439 | 20412 | 815670 | 2012-05-01 11:07 | 2012-05-01 18:35 | 448 | 11kV | 148585 | 1451 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S2400 Berowra Panel 21 tripped reclosed tripped and locked out on Relays: Tripe LED, EFI trip, EFI, Reclose lockout, E/F check. Signals: 11kV trip, ZOne Earth, Tx2 Group Earth Cause: UGOH to S2896 Failed. See OMS 816504 816506 815670 | May | 2012 | 2012Q4 | 2012 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | Unknown | Unknown | 2012-05-01 | N | 102.4018 | N | 7 | N | N | 1.1101 | 39.4971 | 108581.5355
| 811:74234 | 261 | 239.8188 | 44.67 | 0.91885 | 44.67 | 18831 | 2366 | 815966 | 2012-05-01 17:30 | 2012-05-01 18:45 | 75 | 11kV | 525 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 120654 interupted section of fdr for emergency repair to crossarm at pole fp-90704 Excluded oms 815966 | May | 2012 | 2012Q4 | 2012 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-05-01 | N | 75 | N | 7 | N | N | 1.1101 | 39.4971 | 383.6545
| ZN35335:PA14 | 187 | 1163.9538 | 43.15 | 6.2244 | 43.15 | 18909 | 3190 | 815998 | 2012-05-01 22:02 | 2012-05-01 23:10 | 68 | 11kV | 66264 | 1065 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At ZN.10994 Mortdale 11kV fdr P-3 "Mi Mi Street" feeder tripped on: RELAYS: Earth Fault, EFI SIGNALS: 11kV trip, TX.2 Grp Eth FIELD EFIs: S.47566, S.10647 & S.10162 REMARKS: Animals/Birds. Possum on 11kV UGOH in Louisa Rd. | May | 2012 | 2012Q4 | 2012 | ZN10994:PA3 | ZN10994:PA3 | ZN10994/000003 | GEORGES RIVER | OH | Not Veg | 2012-05-01 | N | 62.2197 | N | 7 | N | N | 1.1101 | 39.4971 | 48423.7767
| ZN35335:PA16 | 199 | 824.0557 | #N/A | 4.141 | 39.4971 | 19457 | 8770 | 816009 | 2012-05-01 22:59 | 2012-05-02 02:15 | 196 | 11kV | 7644 | 39 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120655 A Phase DOLF : 16 Amp Excluded OMS 816009 | May | 2012 | 2012Q4 | 2012 | 230:34047 | 230:81440 | ZN00230/081440 | PORT STEPHENS | UG | Not Veg | 2012-05-01 | N | 196 | N | 7 | N | N | 1.1101 | 39.4971 | 5586.0097
| ZN35335:PA17 | 7 | 617.8447 | #N/A | 88.2635 | 39.4971 | 18616 | 369 | 816015 | 2012-05-02 04:42 | 2012-05-02 05:35 | 53 | 11kV | 1007 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | PT13670 Barinya Meadow - Centre Phase 20K Drop Out fuse Operated Cause not ascertained | May | 2012 | 2012Q4 | 2012 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2012-05-02 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 735.8859
| ZN35335:PA2 | 3 | 62.1251 | #N/A | 20.7084 | 39.4971 | 19405 | 8350 | 816135 | 2012-05-02 10:13 | 2012-05-02 11:11 | 58 | 11kV | 73788 | 1296 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.1648 Enfield P-15 "Tangarra St" Fdr tripped on: RELAYS: A phase IOC, A phase Time O/C and EFI SIGNALS: 11kV trip, Zone Earth and TX.3 GE REMARKS: UG Fault. Suspected 11kv UG fault from S.2013 Tangarra St to S.3134 Mitchell Stanley. Note: Compound filled end box at S.2013 Tangarra. LV // required. | May | 2012 | 2012Q4 | 2012 | ZN1648:PA15 | ZN4853:PA2 | ZN04853/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-05-02 | N | 56.9352 | N | 4 | N | N | 1.1101 | 39.4971 | 53922.094
| ZN35335:PA4 | 3 | 536.493 | #N/A | 178.831 | 39.4971 | 18777 | 1918 | 816036 | 2012-05-02 07:24 | 2012-05-02 12:50 | 326 | 11kV | 180894 | 917 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 120656 2 fault operations Broken xarm at pole & wires down. High into Low Voltage mains Excluded OMS 816036 | May | 2012 | 2012Q4 | 2012 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2012-05-02 | N | 197.2672 | N | 4 | N | N | 1.1101 | 39.4971 | 132191.9997
| ZN35335:PA6 | 6 | 126.0986 | #N/A | 21.0164 | 39.4971 | 18962 | 3532 | 816509 | 2012-05-03 08:50 | 2012-05-03 08:57 | 7 | 11kV | 546 | 78 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 120671 Emergency isolation to isolate sparking UGOH. Excluded OMS 816457 | May | 2012 | 2012Q4 | 2012 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | Unknown | Unknown | 2012-05-03 | N | 7 | N | 6 | N | N | 1.1101 | 39.4971 | 399.0007
| ZN35335:PA8 | 2 | 33.2308 | #N/A | 16.6154 | 39.4971 | 19551 | 9598 | 816479 | 2012-05-03 08:04 | 2012-05-03 09:48 | 104 | 11kV | 138184 | 1355 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn965 Pennant Hills Panel 46 Tripped reclosed tripped and locked out on Relays: Earth Fault, EFI, Timing and Lockout. Signals: 11kV Trip and No3 Group Earth Cause: 11kV UG fault from S5842 New Farm Cherrybrook to S792 Purchase Newline. See OMS 817641 817644 816479 | May | 2012 | 2012Q4 | 2012 | ZN965:PA46 | ZN965:PA46 | ZN00965/000046 | HORNSBY | UG | Not Veg | 2012-05-03 | N | 101.9808 | N | 6 | N | N | 1.1101 | 39.4971 | 100980.7915
| 511:29869 | 97 | 237.2934 | 61.79 | 2.4463 | 61.79 | 18921 | 3282 | 816463 | 2012-05-03 07:16 | 2012-05-03 10:45 | 209.0833 | 11kV | 1254.5 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 120672 B & C phase DOLF : 20 Amp | May | 2012 | 2012Q4 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2012-05-03 | N | 209.0833 | N | 6 | N | N | 1.1101 | 39.4971 | 916.7516
| 511:29872 | 81 | 867.6202 | 58.29 | 10.7114 | 58.29 | 19867 | 13449 | 816919 | 2012-05-03 11:45 | 2012-05-03 12:50 | 65 | 11kV | 1105 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV feeder from Somersby Zn Pnl.17 isolated from USL41965 to USL 41266 to AB45443 to AB 43180 tee PT13020, PT14214 & PT11331. Large tree snapped and rested against the HV mains, DOP isolated to allow removal by linesman see 816920 816921 816919 | May | 2012 | 2012Q4 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-05-03 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 807.5014
| 511:29873 | 1731 | 1193.0814 | 33.06 | 0.68924 | 33.06 | 20334 | 19372 | 816559 | 2012-05-03 09:56 | 2012-05-03 14:20 | 264 | 11kV | 252469 | 3764 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S 15006 Dee Why West Zone panel 12 tripped off on IOC, Earth Fault, Frame leakage and EFI, Cause: Contractor cut in section of conduit and cable in Campbell Pde near Time & Tide Hotel. Section of 11kV Feeder from S15670 Time & Tide to S15889 Lynwood Av 69 to S16547 Ilikai Fisher. See 816974, 816559 | May | 2012 | 2012Q4 | 2012 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | UG | Not Veg | 2012-05-03 | N | 67.0747 | N | 6 | N | N | 1.1101 | 39.4971 | 184496.8986
| 511:29874 | 142 | 475.2698 | #N/A | 3.347 | 39.4971 | 18577 | 70 | 816852 | 2012-05-03 17:44 | 2012-05-03 20:40 | 176 | 11kV | 704 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120677 No protection operations. Sub isolated to replace burnt LV lead under A/P. Excluded OMS 816852 | May | 2012 | 2012Q4 | 2012 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2012-05-03 | N | 176 | N | 6 | N | N | 1.1101 | 39.4971 | 514.4624
| 511:29876 | 781 | 636.1349 | 35.61 | 0.81451 | 35.61 | 18684 | 1009 | 816915 | 2012-05-04 06:53 | 2012-05-04 09:10 | 137.3333 | 11kV | 3982.6667 | 29 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT12524 Anchor Beachcomber - Roadside HV fuse blown 31.5A Fatigue | May | 2012 | 2012Q4 | 2012 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2012-05-04 | N | 137.3333 | N | 1 | N | N | 1.1101 | 39.4971 | 2910.4153
| 511:29877 | 1234 | 1488.3289 | 41.96 | 1.2061 | 41.96 | 19246 | 6486 | 817277 | 2012-05-05 01:46 | 2012-05-05 02:56 | 70 | 11kV | 41160 | 588 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | Section of 11kV feeder from AB42757 was interrupted due to vandals bending the operating arm of the AB causing it to open | May | 2012 | 2012Q4 | 2012 | ZN12590:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Not Veg | 2012-05-05 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 30078.514
| 511:29878 | 1218 | 1123.3658 | 40.68 | 0.9223 | 40.68 | 20410 | 20199 | 817345 | 2012-05-05 10:58 | 2012-05-05 12:45 | 107 | 11kV | 100285 | 1085 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2568 St Peters Zn Pa9 fdr tripped Relays- Earth Fault, Fault Check, EFI Signals-11kv trip, Ze, #2 GE EFI-S1481 S131 S8927 Cause-UG Fault. Suspect UG 11kV fault btw SwB S8927 to SwA S47256 See 817770,4,7,8 exclude 817345,7,8 | May | 2012 | 2012Q4 | 2012 | ZN2568:PA9 | ZN2568:PA9 | ZN02568/000009 | INNER WEST | UG | Not Veg | 2012-05-05 | N | 92.4286 | N | 4 | N | N | 1.1101 | 39.4971 | 73285.3201
| 511:29880 | 1466 | 1734.0247 | 45.25 | 1.1828 | 45.25 | 19164 | 5139 | 817438 | 2012-05-05 22:07 | 2012-05-06 00:30 | 143 | 11kV | 73680 | 526 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Section of 11kV feeder Ex Peats Ridge Zn Pnl.2 - REC 45189 Cooks Peats Ridge 0.5 tripped / reclosed / tripped & locked out on: O/C and 3 Phase O/C Mains patrolled and found clear See OMS # 817619 817621 817622 817624 | May | 2012 | 2012Q4 | 2012 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2012-05-05 | N | 140.076 | N | 4 | N | N | 1.1101 | 39.4971 | 53843.1708
| ZN10997:PA1 | 985 | 702.1876 | 30.92 | 0.71288 | 30.92 | 18932 | 3360 | 817445 | 2012-05-05 23:30 | 2012-05-06 01:48 | 138 | 11kV | 4686 | 2220 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Lake Munmorah Pnl.7 tripped and reclosed on B Phase O/C Car hit pole near 10 Colongra Bay Rd see 817633 817632 (outage to PT12722) | May | 2012 | 2012Q4 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2012-05-05 | N | 2.1108 | N | 4 | N | N | 1.1101 | 39.4971 | 3424.3906
| ZN10997:PA11 | 705 | 741.5107 | 36.09 | 1.0518 | 36.09 | 19285 | 7239 | 817460 | 2012-05-06 07:42 | 2012-05-06 08:16 | 34 | 11kV | 13223 | 1046 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 120703 2 fault operations C phase Overcurrent Fdr flashed over at ABS 40656 low fixed clearance please repair Fdr flashed over at ABS 40656 due to fault on Fdr 48057 | May | 2012 | 2012Q4 | 2012 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | OH | Not Veg | 2012-05-06 | N | 12.6415 | N | 1 | N | N | 1.1101 | 39.4971 | 9662.9784
| ZN10997:PA12 | 1394 | 976.4324 | 32.28 | 0.70045 | 32.28 | 18730 | 1357 | 817888 | 2012-05-07 14:27 | 2012-05-07 16:30 | 123 | 11kV | 861 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120712 B phase DOLF : 10 Amp DOLF carrier burnt up. Excluded OMS# 817888 | May | 2012 | 2012Q4 | 2012 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2012-05-07 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 629.1934
| ZN10997:PA2 | 2573 | 1573.0901 | 32.54 | 0.61138 | 32.54 | 19052 | 4373 | 817957 | 2012-05-07 16:24 | 2012-05-07 17:31 | 67 | 11kV | 113641 | 1870 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Somersby Zon Pnl.12 tripped, reclosed, tripped and locked out on: O/C & E/F, EFI Field EFIs operating up to and including S.14219 11kV UG cable fault from S14223 to S14219 See 818072 818070 | May | 2012 | 2012Q4 | 2012 | ZN14143:PA12 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2012-05-07 | N | 60.7706 | N | 4 | N | N | 1.1101 | 39.4971 | 83045.491
| ZN10997:PA5 | 883 | 614.0819 | 30.74 | 0.69545 | 30.74 | 18944 | 3442 | 818053 | 2012-05-07 22:55 | 2012-05-08 01:00 | 124.8833 | 11kV | 1248.8333 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120713 A phase DOLF : 31 Amp. | May | 2012 | 2012Q4 | 2012 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-05-07 | N | 124.8833 | N | 4 | N | N | 1.1101 | 39.4971 | 912.6106
| ZN10997:PA7 | 1411 | 1133.7184 | 36.9 | 0.80349 | 36.9 | 19360 | 7786 | 818050 | 2012-05-07 22:41 | 2012-05-08 11:35 | 774.05 | 11kV | 13158.85 | 17 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 120715 A phase DOLF : 20 Amp Possum at sub 52619. 11kV mains down between poles HS-53306 & HS-53307. CC1: 22-"Refer to SOp" | May | 2012 | 2012Q4 | 2012 | 507:80923 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Not Veg | 2012-05-07 | N | 774.05 | N | 4 | N | N | 1.1101 | 39.4971 | 9616.0995
| ZN10997:PA8 | 256 | 205.4131 | 35.7 | 0.8024 | 35.7 | 19321 | 7464 | 818761 | 2012-05-09 11:53 | 2012-05-09 13:10 | 77 | 11kV | 10857 | 141 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | PT13168 Bonnieview Lord - HDO fuse operated HV crossarm holding the HDO's broke causing fuse to open GIS: 819037 819038 819040 840618 | May | 2012 | 2012Q4 | 2012 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Not Veg | 2012-05-09 | N | 77 | N | 2 | N | N | 1.1101 | 39.4971 | 7933.9754
| ZN9015:PA1 | 2 | 47.7428 | 41.08 | 23.8714 | 41.08 | 19476 | 8917 | 818979 | 2012-05-09 20:04 | 2012-05-10 01:15 | 311 | 11kV | 349191 | 2220 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn.12590 Lake Munmorah Pnl.7 tripped & reclosed on: Trip Flag O/C 01 Car hit pole 11 kV feeder between AB40027 to AB44001 tee PT12990. DOp found USL40256 roadside phase link blown open and damaged. Interrupted Pnl.7 @ 2251 to allow DOp to open USL40256 and Closed Pnl.7 @ 2255. See # 819046 819047 819052 819051 | May | 2012 | 2012Q4 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2012-05-09 | N | 157.2932 | N | 2 | N | N | 1.1101 | 39.4971 | 255178.4834
| 813:89055 | 577 | 667.712 | 54 | 1.1572 | 54 | 19611 | 10324 | 819016 | 2012-05-10 06:16 | 2012-05-10 11:30 | 314.2667 | 11kV | 15858.9167 | 52 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120741 ap issued to repair tapping at pole CN-60043 Note: Supply interrupted by DOP at 0930, quality of supply calls reporting Low Volts and brown outs began at 06:15 | May | 2012 | 2012Q4 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-05-10 | N | 304.9792 | N | 5 | N | N | 1.1101 | 39.4971 | 11589.2285
| 813:89058 | 19 | 37.498 | 41.35 | 1.9736 | 41.35 | 20268 | 18044 | 819161 | 2012-05-10 11:03 | 2012-05-10 12:00 | 57 | 11kV | 36879 | 647 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14144 Wamberal P10 tripped on E/F Contractor error caused failure - On central Coast hwy near Brookes Hills Rd, Contractor excavator hit mains reported to Rob North to follow up. | May | 2012 | 2012Q4 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2012-05-10 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 26950.0855
| 813:89059 | 283 | 508.2098 | 49.89 | 1.7958 | 49.89 | 20301 | 18965 | 819193 | 2012-05-10 11:54 | 2012-05-10 12:52 | 58 | 11kV | 63684 | 1098 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn12570 Avoca Pnl.16 from AB43567 - Roadside bond off | May | 2012 | 2012Q4 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2012-05-10 | N | 58 | N | 5 | N | N | 1.1101 | 39.4971 | 46538.3888
| 813:89061 | 655 | 609.55 | 40.13 | 0.93061 | 40.13 | 19424 | 8490 | 819305 | 2012-05-10 13:40 | 2012-05-10 15:00 | 80 | 11kV | 880 | 11 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | Unselected | N | LID 120750 11kV Fdr isolated for emergency condemned pole replacement. Excluded OMS 819305 | May | 2012 | 2012Q4 | 2012 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-05-10 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 643.078
| 813:89062 | 848 | 793.1793 | 30.16 | 0.93535 | 30.16 | 18579 | 84 | 819377 | 2012-05-10 15:24 | 2012-05-10 17:04 | 99.65 | 11kV | 1123.1333 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120751 B phase DOLF : 10 Amp 243 Volt approx 25 Amp per phaase | May | 2012 | 2012Q4 | 2012 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | UG | Not Veg | 2012-05-10 | N | 86.3949 | N | 5 | N | N | 1.1101 | 39.4971 | 820.7527
| 813:89063 | 1074 | 996.231 | 31.54 | 0.92759 | 31.54 | 18803 | 2168 | 819777 | 2012-05-11 16:24 | 2012-05-11 19:20 | 176 | 11kV | 1232 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120763 Fuse Holder burnt up. excluded OMS No. 819777 | May | 2012 | 2012Q4 | 2012 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2012-05-11 | N | 176 | N | 2 | N | N | 1.1101 | 39.4971 | 900.3093
| 813:89065 | 718 | 727.2672 | 30.8 | 1.0129 | 30.8 | 19807 | 12862 | 819841 | 2012-05-11 20:55 | 2012-05-11 21:55 | 60 | 11kV | 19020 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 120764 1 fault operation 3 phase Overcurrent Branch across 11kv between poles GW-50127 & GW-50128. Please inspect during daylight Excluded oms 819843 | May | 2012 | 2012Q4 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-05-11 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 13899.255
| ZN3472:PA11 | 466 | 884.0905 | 50.99 | 1.8972 | 50.99 | 18667 | 848 | 819850 | 2012-05-12 03:01 | 2012-05-12 03:55 | 54 | 11kV | 48438 | 897 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S35500 Top Ryde Panel 31 trupped on A and C phase overcurrent with EFI on Pa31R Cause: Possum caused flash over at PT1421 Whiteside Parklands. | May | 2012 | 2012Q4 | 2012 | ZN35500:PA31 | ZN35500:PA31 | ZN35500/000031 | RYDE | OH | Not Veg | 2012-05-12 | N | 54 | N | 3 | N | N | 1.1101 | 39.4971 | 35397.0617
| ZN3472:PA12 | 1697 | 1003.0823 | 22.88 | 0.59109 | 22.88 | 20372 | 19914 | 819865 | 2012-05-12 08:07 | 2012-05-12 11:05 | 178 | 11kV | 30438 | 171 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S1179 Houston rd Cph 60Amp Reyrolle JOS 1025 fuse operated. Cause: TX has no oil in conservator, leaking from various location on tx LV// S7395 Barker Houston, N/O Dist2 LV Links 8248, 8140 See 820446 GIS 820449,54,533 exclude 819865,6,9,83,96 | May | 2012 | 2012Q4 | 2012 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | UG | Not Veg | 2012-05-12 | N | 178 | N | 3 | N | N | 1.1101 | 39.4971 | 22243.1926
| ZN3472:PA15 | 184 | 412.249 | 48.86 | 2.2405 | 48.86 | 20083 | 15876 | 819952 | 2012-05-12 14:37 | 2012-05-12 15:30 | 53 | 11kV | 58823 | 1211 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At ZN.9900 Menai P-1 "S.9002 Raine Marsden, S.9930 North Brooks Morton etc" fdr tripped on RHS fdr: RELAYS: B phase O/C recloser 7 lockout relays SIGNALS: FIELD EFIs: Nil REMARKS: Other - details provided. Neutral conductor in contact with HV. | May | 2012 | 2012Q4 | 2012 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | OH | Not Veg | 2012-05-12 | N | 48.5739 | N | 3 | N | N | 1.1101 | 39.4971 | 42986.1134
| ZN3472:PA16 | 69 | 1004.3536 | 48.36 | 14.5558 | 48.36 | 20085 | 15879 | 820008 | 2012-05-13 07:37 | 2012-05-13 09:36 | 119 | 11kV | 109327 | 956 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S2400 Berowra Panel 26 tripped on B and C phase IOC. Cause not ascertained for outage See OMS 820839/853/835 820008 820009 | May | 2012 | 2012Q4 | 2012 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2012-05-13 | N | 114.3588 | N | 4 | N | N | 1.1101 | 39.4971 | 79892.947
| ZN3472:PA17 | 1617 | 1308.0673 | 34.82 | 0.80895 | 34.82 | 18794 | 2085 | 820004 | 2012-05-13 07:16 | 2012-05-13 09:42 | 145.9833 | 11kV | 2288.9333 | 26 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120775 A phase DOLF broken on line side. Repaired live line. | May | 2012 | 2012Q4 | 2012 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2012-05-13 | N | 88.0359 | N | 4 | N | N | 1.1101 | 39.4971 | 1672.685
| ZN3472:PA18 | 55 | 154.3152 | 57.29 | 2.8057 | 57.29 | 19221 | 6128 | 820032 | 2012-05-13 10:08 | 2012-05-13 10:41 | 33 | 11kV | 76907 | 2403 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12690 Berkeley vale Pnl.19 tripped on A & C phase OC Abnormal Switching: LB43329 Closed - AB42592 Open & Defective Tree branch contact See 820867 820874 | May | 2012 | 2012Q4 | 2012 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2012-05-13 | N | 32.0046 | N | 4 | N | N | 1.1101 | 39.4971 | 56201.3672
| ZN3472:PA20 | 1256 | 1310.0398 | 34.62 | 1.043 | 34.62 | 19051 | 4365 | 820070 | 2012-05-13 12:01 | 2012-05-13 15:00 | 179 | 11kV | 25764 | 233 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 44995 Kulnura Tripped & locked out Tree brought down OH adjacent to PT13281 see # 820888 820889 | May | 2012 | 2012Q4 | 2012 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2012-05-13 | N | 110.5751 | N | 4 | N | N | 1.1101 | 39.4971 | 18827.5713
| ZN3472:PA22 | 934 | 1277.2092 | 42.09 | 1.3675 | 42.09 | 19733 | 12101 | 820547 | 2012-05-14 14:38 | 2012-05-14 16:53 | 135.2 | 11kV | 3359.25 | 39 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT2452 Burns Wahroonga Roadside Phase HDO fuse operated. Cause: Fuse fatigue. See OMS 822493/575/579/564/602/592/547/580/563/646/553/589/548. | May | 2012 | 2012Q4 | 2012 | ZN1673:PA43 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Not Veg | 2012-05-14 | N | 86.1346 | N | 1 | N | N | 1.1101 | 39.4971 | 2454.8408
| ZN3472:PA27 | 1983 | 1625.3459 | 32.61 | 0.81964 | 32.61 | 18612 | 305 | 820794 | 2012-05-15 07:42 | 2012-05-15 13:45 | 363 | 11kV | 9294 | 74 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 120788 1 fault operation 3 phase Overcurrent Crane hit LV mains adjacent to pole DP-70088. Repaired under A/P. | May | 2012 | 2012Q4 | 2012 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2012-05-15 | N | 125.5946 | N | 1 | N | N | 1.1101 | 39.4971 | 6791.7811
| ZN3472:PA28 | 1299 | 1680.7334 | 36.31 | 1.2939 | 36.31 | 18885 | 2957 | 821704 | 2012-05-16 23:05 | 2012-05-16 23:30 | 25 | 11kV | 1925 | 77 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 120812 C phase DOLF : 31 Amp Possum on transformer 252 Volts Excluded OMS 821704 | May | 2012 | 2012Q4 | 2012 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Not Veg | 2012-05-16 | N | 25 | N | 1 | N | N | 1.1101 | 39.4971 | 1406.7332
| ZN3472:PA29 | 841 | 833.5347 | 40.69 | 0.99112 | 40.69 | 18613 | 318 | 821706 | 2012-05-17 02:31 | 2012-05-17 04:24 | 113 | 11kV | 55950 | 510 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.20 tripped on A & B phase Overcurrent Cause not ascertained see 823115 823115 | May | 2012 | 2012Q4 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2012-05-17 | N | 109.7059 | N | 2 | N | N | 1.1101 | 39.4971 | 40886.6098
| ZN3472:PA30 | 2036 | 1799.2508 | 33.93 | 0.88372 | 33.93 | 19864 | 13412 | 822125 | 2012-05-17 17:58 | 2012-05-17 19:55 | 117 | 11kV | 213439 | 1880 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S72 Five Dock panel 14 "S8715 MWS&DB Martin St No2" etc feeder tripped on Leakage efi. Alarms 11kv trip zone earth No4 gorup earth. Field efi's operated S8715 Remarks: UG Fault11kv feeder failed S8715 MWS & DB Martin St to CP521 Allen Burfitt to 36106 Beeson Tebbutt. Related jobs: #822125, 822289, 822288 | May | 2012 | 2012Q4 | 2012 | ZN72:PA14 | ZN35555:PA2 | ZN35555/000002 | INNER WEST | UG | Not Veg | 2012-05-17 | N | 113.5314 | N | 2 | N | N | 1.1101 | 39.4971 | 155974.9258
| ZN3472:PA33 | 1933 | 1161.1541 | 23.94 | 0.6007 | 23.94 | 19930 | 14101 | 822177 | 2012-05-18 00:20 | 2012-05-18 01:27 | 67 | 11kV | 225589 | 3487 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S262 Marrickville Panel 7 'S5630 Despointes Syd' Feeder tripped on Relays - B phase time O/C, EFI, Fault Check Signals - 11kv trip, ZE, TX4 GE ABNORMAL: SW/A OPEN @ S8521, SW B CLOSED @ S5650, SW B CLOSED @ CP85, SW A OPEN @ S5095, SW A OPEN @ CP521, SW B CLOSED @ S2647 Remarks: UG Fault. 11KV UG feeder fault from Panel 7 @ S262 Marrickville to S5630 Despointes Syd Related jobs: #822181, 822180, 822179, 822178, 822177, 822314, 822312, 822305 | May | 2012 | 2012Q4 | 2012 | ZN262:PA7 | ZN262:PA7 | ZN00262/000007 | INNER WEST | UG | Not Veg | 2012-05-18 | N | 64.6943 | N | 7 | N | N | 1.1101 | 39.4971 | 164853.7875
| ZN3472:PA34 | 592 | 906.7935 | 52.39 | 1.5317 | 52.39 | 19497 | 9061 | 822504 | 2012-05-18 14:33 | 2012-05-18 16:15 | 102 | 11kV | 1734 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | REC 45010 Palmgrove tripped on SEF Cause not ascertained | May | 2012 | 2012Q4 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-05-18 | N | 102 | N | 7 | N | N | 1.1101 | 39.4971 | 1267.1561
| ZN3472:PA35 | 427 | 1299.1814 | 50.19 | 3.0426 | 50.19 | 19379 | 8036 | 822568 | 2012-05-18 15:56 | 2012-05-18 16:33 | 37 | 11kV | 11655 | 315 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44999 Warner tripped on IOC Tree branch in vicinity 72 Boyce Road | May | 2012 | 2012Q4 | 2012 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2012-05-18 | N | 37 | N | 7 | N | N | 1.1101 | 39.4971 | 8517.1302
| ZN3472:PA8 | 1189 | 994.939 | 33.98 | 0.83679 | 33.98 | 20310 | 19060 | 822632 | 2012-05-18 17:43 | 2012-05-18 19:08 | 85 | 11kV | 29964.65 | 353 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | Ex Zn167 Auburn (panel 13) "S3943 Hall Dartbrook" feeder. At S3221 MAcquarie Raw 11kV RMI HV C Phase 71A OQFRN fuse found blown. Remarks: Possible fuse fatigue.Dop has not taken load readings. Related jobs: #824567, 822628, 822632 | May | 2012 | 2012Q4 | 2012 | ZN1068:PA29 | ZN36000:PA24 | ZN36000/000024 | CUMBERLAND | UG | Not Veg | 2012-05-18 | N | 84.8857 | N | 7 | N | N | 1.1101 | 39.4971 | 21897.2824
| 513:83493 | 946 | 1515.8064 | 37.22 | 1.6023 | 37.22 | 20158 | 16384 | 822613 | 2012-05-18 14:00 | 2012-05-18 19:25 | 325 | 11kV | 650 | 2 | HV | Vandalism | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 120835 Single phase DOLF : 10 Amp The stay wire was cut off around ground level and contacted the DOLF dropper cable. The damage was spotted by Ausgrid staff (B LINDSAY) performing an inspection. Excluded OMS 822613 | May | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-05-18 | N | 325 | N | 7 | N | N | 1.1101 | 39.4971 | 475.0008
| 513:83495 | 963 | 808.3384 | 35.01 | 0.8394 | 35.01 | 18751 | 1614 | 822626 | 2012-05-18 17:36 | 2012-05-18 23:10 | 334 | 11kV | 8759 | 97 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn.12590 lake Munmorah Pnl.1 tripped on A & C phase IOC and timed with EFI Vehicle hit pole WH157 vicinity Pacific Hwy at Chain Valley See 823128 823129 823130 | May | 2012 | 2012Q4 | 2012 | ZN12590:PA1 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2012-05-18 | N | 90.299 | N | 7 | N | N | 1.1101 | 39.4971 | 6400.8189
| 513:83497 | 299 | 338.1837 | 45.47 | 1.131 | 45.47 | 18740 | 1437 | 822694 | 2012-05-18 23:04 | 2012-05-19 | 56 | 11kV | 95564 | 1899 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12640 Umina Pnl.2 tripped & reclosed on A + B timed OC, EFI Bond burnt off @ AB41313 (Centre Phase) | May | 2012 | 2012Q4 | 2012 | ZN12640:PA2 | ZN12640:PA2 | ZN12640/000002 | CENTRAL COAST | OH | Not Veg | 2012-05-18 | N | 50.3233 | N | 7 | N | N | 1.1101 | 39.4971 | 69835.3525
| 513:83500 | 281 | 285.5541 | 39.63 | 1.0162 | 39.63 | 19442 | 8573 | 822743 | 2012-05-19 09:19 | 2012-05-19 10:20 | 61 | 11kV | 76674 | 1434 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 120841 2 fault operations A & B phase Overcurrent Regiment Rd Switching Cubicle 38575 failure. UGOH at pole HR-21110 also damaged. Excluded OMS# 822754 & 822747 | May | 2012 | 2012Q4 | 2012 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | Unknown | Unknown | 2012-05-19 | N | 53.4686 | N | 2 | N | N | 1.1101 | 39.4971 | 56031.0977
| 513:83502 | 202 | 164.9082 | 39.76 | 0.81638 | 39.76 | 20103 | 16011 | 822739 | 2012-05-19 09:16 | 2012-05-19 13:35 | 259 | 11kV | 154472 | 2929 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.15006 Dee Why West, Panel 9 Fdr CB tripped on 11kV trip, zone earth, Aand B phase IOC. Field efi's down at S.16792, S.17031, S.16733, S.16734 and S.16559.Magpie brought down one span of 11kV OH from PT.15330 | May | 2012 | 2012Q4 | 2012 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | OH | Not Veg | 2012-05-19 | N | 52.7388 | N | 2 | N | N | 1.1101 | 39.4971 | 112883.5814
| 513:83503 | 755 | 907.984 | 38.92 | 1.2026 | 38.92 | 18901 | 3124 | 822909 | 2012-05-20 07:46 | 2012-05-20 09:30 | 104 | 11kV | 208 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 120850 Single phase DOLF : 10 Amp | May | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2012-05-20 | N | 104 | N | 3 | N | N | 1.1101 | 39.4971 | 152.0003
| 513:83504 | 520 | 981.0469 | 39.29 | 1.8866 | 39.29 | 19434 | 8535 | 823000 | 2012-05-20 18:16 | 2012-05-20 19:54 | 98 | 11kV | 46997 | 510 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14891 Pnl.20 tripped on A + B phase iOC Cause not ascertained - DOp patrolled feeder after report of flash in Mountain Rd but could not find anything. Suspects tree branch as there is a lot of overhanging trees in Mountain Rd. Would have been off for 10 seconds if recloser @ zone was still auto - see further interrupted for bond failure see 823149 823151 823153 823152 | May | 2012 | 2012Q4 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2012-05-20 | N | 92.151 | N | 3 | N | N | 1.1101 | 39.4971 | 34344.0214
| 523:33500 | 209 | 199.5261 | 25.77 | 0.95467 | 25.77 | 19259 | 6623 | 823033 | 2012-05-20 22:14 | 2012-05-20 23:35 | 81 | 11kV | 1296 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of pnl.20 Ex Wyong Zn interrupted from LB47304 Interrupted by DOp to allow reapir of bonds after feeder fault | May | 2012 | 2012Q4 | 2012 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2012-05-20 | N | 81 | N | 3 | N | N | 1.1101 | 39.4971 | 947.0786
| 523:33501 | 767 | 693.9207 | 25.12 | 0.90472 | 25.12 | 18630 | 506 | 823431 | 2012-05-21 14:20 | 2012-05-21 16:20 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120861 C phase DOLF : 10 Amp Excluded OMS 823431 | May | 2012 | 2012Q4 | 2012 |  |  |  |  | UG | Not Veg | 2012-05-21 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 87.6925
| 523:33503 | 759 | 609.9975 | 22.74 | 0.80369 | 22.74 | 20032 | 15368 | 823441 | 2012-05-21 14:35 | 2012-05-21 17:30 | 175 | 11kV | 175 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120862 B Phase dist fuse : 100 Amp Excluded OMS 823441 | May | 2012 | 2012Q4 | 2012 |  |  |  |  | UG | Not Veg | 2012-05-21 | N | 175 | N | 2 | N | N | 1.1101 | 39.4971 | 127.8848
| 523:33505 | 898 | 775.4164 | 22.44 | 0.86349 | 22.44 | 18927 | 3349 | 823610 | 2012-05-22 06:45 | 2012-05-22 07:24 | 39 | 11kV | 30849 | 791 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Tree branch on mains near AB.20330 removed by ZD.Op. AT S.15003 Brookvale, Panel 8 Fdr CB tripped on B and C phase IOC. | May | 2012 | 2012Q4 | 2012 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Veg | 2012-05-22 | N | 39 | N | 3 | N | N | 1.1101 | 39.4971 | 22543.5393
| 523:33507 | 581 | 476.5497 | 23.03 | 0.82022 | 23.03 | 18779 | 1922 | 823891 | 2012-05-22 13:10 | 2012-05-22 13:40 | 30 | 11kV | 720 | 24 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 120867 Isolation to repair Broken crossarm brace at pole GU-33130 | May | 2012 | 2012Q4 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2012-05-22 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 526.1548
| 523:33508 | 523 | 991.3442 | 48.84 | 1.8955 | 48.84 | 19687 | 11386 | 823847 | 2012-05-22 12:12 | 2012-05-22 14:49 | 156.7167 | 11kV | 576.7167 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120868 B & C phase DOLF : 20 Amp Excluded OMS 823847 | May | 2012 | 2012Q4 | 2012 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2012-05-22 | N | 72.0896 | N | 3 | N | N | 1.1101 | 39.4971 | 421.4475
| 523:33509 | 485 | 450.0599 | 28.31 | 0.92796 | 28.31 | 19585 | 9737 | 824432 | 2012-05-23 17:30 | 2012-05-23 21:30 | 240 | 11kV | 480 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 120882 NO PROTECTION OPERATED.TRANSFORMER CHANGED UNDER ACCESS PERMIT. Excluded OMS 824432 | May | 2012 | 2012Q4 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2012-05-23 | N | 240 | N | 1 | N | N | 1.1101 | 39.4971 | 350.7698
| 523:33511 | 278 | 180.9129 | 21.77 | 0.65077 | 21.77 | 18772 | 1886 | 824796 | 2012-05-24 13:48 | 2012-05-24 15:04 | 76 | 11kV | 95228 | 1253 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S195 Pymble panel 9 tripped on B phase Timed O/C Cause: Tree branch removed form 11kV OH Near PT2038 Wattle Kananga | May | 2012 | 2012Q4 | 2012 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Veg | 2012-05-24 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 69589.8136
| ZN14143:PA10 | 58 | 84.2756 | 49.68 | 1.453 | 49.68 | 19736 | 12147 | 825193 | 2012-05-24 15:15 | 2012-05-24 16:30 | 75 | 11kV | 1350 | 18 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Section of Pnl.1 ex peats Ridge Zn -feeder interrupted from LB4056 to AB40267 Car hit pole (reported by OH mains) adjacent AB40267 caused 11kV ties onto pin insulators to fail | May | 2012 | 2012Q4 | 2012 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2012-05-24 | N | 75 | N | 6 | N | N | 1.1101 | 39.4971 | 986.5402
| ZN14143:PA12 | 114 | 544.79 | 40.46 | 4.7789 | 40.46 | 19484 | 8989 | 824955 | 2012-05-24 19:15 | 2012-05-24 21:35 | 140 | 11kV | 83405 | 1345 | HV | Animal Possum | Animal | DC PT | Unplanned | Rain Light | N | At S2400 Berowra Panel 22 Opened on Ie>>B, It>>B, EFI, Earth F/C. 11kV Trip. PT1400 Northumberland Landra Surge Diverters blown due to possum. See OMS 826119 826122 826121. 824982/955/978/983 | May | 2012 | 2012Q4 | 2012 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2012-05-24 | N | 62.0112 | N | 6 | N | N | 1.1101 | 39.4971 | 60949.914
| ZN14143:PA14 | 126 | 856.7239 | 62.1 | 6.7994 | 62.1 | 18995 | 3960 | 824984 | 2012-05-24 19:34 | 2012-05-24 21:50 | 136.3167 | 11kV | 4685.85 | 39 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Unselected | N | At PT.9505 Shackel Beach, centre phase HDO 31.5. Tree branch on PT. | May | 2012 | 2012Q4 | 2012 | ZN9900:PA13 | ZN9252:PA25 | ZN09252/000025 | SUTHERLAND | OH | Veg | 2012-05-24 | N | 120.15 | N | 6 | N | N | 1.1101 | 39.4971 | 3424.281
| ZN14143:PA16 | 2256 | 1718.1174 | #N/A | 0.76158 | 39.4971 | 19925 | 14067 | 825017 | 2012-05-24 21:30 | 2012-05-25 00:27 | 177.2167 | 11kV | 13331.05 | 83 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | Telco cable appears to came in contact with OH mains, cleared and restored supply, the DOp found LV?? link #404 in suspected for area upgrades, that extended the custs affected. | May | 2012 | 2012Q4 | 2012 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2012-05-24 | N | 160.6151 | N | 6 | N | N | 1.1101 | 39.4971 | 9741.9381
| ZN14143:PA17 | 807 | 886.3279 | 43.18 | 1.0983 | 43.18 | 18656 | 743 | 825036 | 2012-05-25 02:28 | 2012-05-25 04:00 | 92 | 11kV | 5980 | 65 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 120891 B Phase DOLF : 20 Amp. DOLF element fatigue. Load readings: 47, 18 & 60A; 251V. Excluded OMS Job No. 825036. | May | 2012 | 2012Q4 | 2012 | 230:34047 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2012-05-25 | N | 92 | N | 5 | N | N | 1.1101 | 39.4971 | 4370.0076
| ZN14143:PA21 | 141 | 429.9856 | 56.8 | 3.0495 | 56.8 | 19264 | 6671 | 825039 | 2012-05-25 03:32 | 2012-05-25 04:55 | 83 | 11kV | 54877 | 824 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn.14144 Wamberal Pnl.4 tripped on B & C phase O/C Cause not ascertained see 825201 825203 825200 825199 | May | 2012 | 2012Q4 | 2012 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-05-25 | N | 66.5983 | N | 5 | N | N | 1.1101 | 39.4971 | 40102.493
| ZN14143:PA5 | 93 | 1721.0975 | 50.14 | 18.5064 | 50.14 | 18695 | 1109 | 824894 | 2012-05-24 16:00 | 2012-05-25 10:25 | 1105 | 11kV | 1105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 120895 B phase DOLF : 10 Amp Tx Volts: Aph - 249V, Bph - 249V, Cph - 249V Excluded OMS No. 824894.- customer has multiple subs | May | 2012 | 2012Q4 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2012-05-24 | N | 1105 | N | 6 | N | N | 1.1101 | 39.4971 | 807.5014
| ZN14143:PA6 | 35 | 1563.7807 | 61.11 | 44.6794 | 61.11 | 20260 | 17955 | 825428 | 2012-05-25 17:39 | 2012-05-25 21:05 | 206 | 11kV | 42436 | 206 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LB2423 Opened By DOp Ex Panel 11 Brooklyn. Cause : Interrupted by DOp - Defective X arm on 11kV Bare Mains to ABC join rotted through and about to fall. See OMS 826012 825428 | May | 2012 | 2012Q4 | 2012 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2012-05-25 | N | 206 | N | 5 | N | N | 1.1101 | 39.4971 | 31010.9771
| ZN14143:PA8 | 32 | 356.5808 | 63.87 | 11.1431 | 63.87 | 20412 | 20212 | 825506 | 2012-05-25 22:37 | 2012-05-25 23:37 | 60 | 11kV | 61040 | 1043 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At ZN.9245 Engadine P-14 "old Princes Station FDR" tripped on: RELAYS: A & C phase IOC, E/L EFI, Reclose time delay, lockout SIGNALS: EFIs: REMARKS: Animals/Birds. Possum on UGOH cnr Cambai & Anzac ave | May | 2012 | 2012Q4 | 2012 | ZN9245:PA14 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Not Veg | 2012-05-25 | N | 58.5235 | N | 5 | N | N | 1.1101 | 39.4971 | 44606.2316
| ZN2568:PA14 | 1516 | 2894.8489 | 41.6 | 1.9095 | 41.6 | 18871 | 2774 | 825512 | 2012-05-26 02:48 | 2012-05-26 04:17 | 89 | 11kV | 142938 | 1896 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.12580 Erina Pnl.1 tripped on A 7 C phase IOC. Field EFI S.11628 Cause not ascertained see 826022 826020 | May | 2012 | 2012Q4 | 2012 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Veg | 2012-05-26 | N | 75.3892 | N | 5 | N | N | 1.1101 | 39.4971 | 104454.8744
| ZN2568:PA15 | 1 | 0 | #N/A | 0 | 39.4971 | 19945 | 14209 | 825514 | 2012-05-26 05:06 | 2012-05-26 06:34 | 88 | 11kV | 78871 | 1185 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | UG Cable Fault in section of 11kv fdr from S3813SwB to S36016SwA At Zn2602 Clovelly Pa31 fdr tripped on: Relays- Bph O/C EFI Fault CHeck EFI- S1803 S3813 Signals- 11kv trip See 826147,54 exclude 825514 | May | 2012 | 2012Q4 | 2012 | ZN2602:PA31 | ZN2602:PA35 | ZN02602/000035 | WAVERLEY | UG | Not Veg | 2012-05-26 | N | 66.5578 | N | 5 | N | N | 1.1101 | 39.4971 | 57636.6005
| ZN2568:PA16 | 1609 | 786.7358 | 34.57 | 0.48896 | 34.57 | 20088 | 15884 | 825491 | 2012-05-25 20:31 | 2012-05-26 08:30 | 719 | 11kV | 38474 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 120903 & 120904 1 fault operation B & C phase Earth fault Mains down at Pole GN-70019. Sw 42034 tripped when ABS 48662 was closed following repairs to feeder. Mains found down at the original site & at Pole GN-80010. | May | 2012 | 2012Q4 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-05-25 | N | 549.6286 | N | 5 | N | N | 1.1101 | 39.4971 | 28115.6644
| ZN2568:PA17 | 138 | 467.9334 | 60.59 | 3.3908 | 60.59 | 19718 | 11976 | 825627 | 2012-05-26 12:25 | 2012-05-26 15:01 | 156 | 11kV | 41028 | 263 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of PAnel 18 ex Zn2400 Berowra Recloser 555 Arcadia Park Tripped . Cause: Tree on OH mains in Bloodwood Rd near Arcadia. See OMS 826031 825627 825628 825631 | May | 2012 | 2012Q4 | 2012 | ZN2400:PA18 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2012-05-26 | N | 156 | N | 5 | N | N | 1.1101 | 39.4971 | 29982.0523
| ZN2568:PA18 | 4 | 3.045 | #N/A | 0.76126 | 39.4971 | 20267 | 18032 | 825708 | 2012-05-26 17:20 | 2012-05-26 18:05 | 45 | 11kV | 5490 | 122 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | Section of 11kV feeder ex Pnl.7 (Lake Munmorah) AB44494 found unlocked and opened | May | 2012 | 2012Q4 | 2012 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2012-05-26 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 4011.9301
| ZN2568:PA19 | 1075 | 1987.9206 | 45.19 | 1.8492 | 45.19 | 19521 | 9189 | 825756 | 2012-05-26 23:30 | 2012-05-27 00:36 | 66 | 11kV | 45408 | 688 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Wyong pnl.12 tripped on O/C with EFI - Field EFi @ S158360 & S47409 REC40075 & REC44753 By-Passed & defective Cause not ascertained Note: no auto reclosing on Feeder | May | 2012 | 2012Q4 | 2012 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-05-26 | N | 66 | N | 5 | N | N | 1.1101 | 39.4971 | 33182.8271
| ZN2568:PA20 | 44 | 1025.6025 | #N/A | 23.3091 | 39.4971 | 19970 | 14636 | 825764 | 2012-05-27 06:30 | 2012-05-27 07:35 | 65 | 11kV | 2340 | 36 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 120912 B Phase DOLF : 31.5 Amp Fuse fatigue Excluded OMS 825764, 825766 | May | 2012 | 2012Q4 | 2012 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2012-05-27 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 1710.003
| ZN2568:PA21 | 1887 | 1487.0607 | 40.44 | 0.78806 | 40.44 | 18755 | 1641 | 825860 | 2012-05-27 12:41 | 2012-05-27 15:35 | 174 | 11kV | 4176 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120918 B & C phase DOLF : 31.5 Amp Excluded OMS 825860 & 826863 | May | 2012 | 2012Q4 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-05-27 | N | 174 | N | 2 | N | N | 1.1101 | 39.4971 | 3051.6976
| ZN2568:PA22 | 726 | 348.907 | 37.68 | 0.48059 | 37.68 | 19173 | 5235 | 816239 | 2012-05-02 13:40 | 2012-05-27 21:00 | 36440 | 11kV | 523792 | 2234 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | Section of 11kv fdr pa44 Ex Zn3155 Double Bay Zn From S1568 to S1605 to S35572 Relays- @S1568 suspected ITR send, No access to S1568 safety issue @S189 ITR Receive @S1605 ITR Receive Pa44@Zn3155 opened by AOp @ 1344 after report from field staff working at S1568 Cause-Flashover/Arcing Remarks-Whilst Ausgrid TCon's were screening LV Board for futur work, equipment insulation failure caused flashover at S1568. See 817843,4,6,7,8,9 LV// 817819,20,5,8,31,7 exclude 816239,48,380,1,2,3,4,5,6,407,12,68,530 | May | 2012 | 2012Q4 | 2012 | ZN3155:PA44 | ZN3155:PA44 | ZN03155/000044 | WOOLLAHRA | UG | Not Veg | 2012-05-02 | N | 234.4637 | N | 4 | N | N | 1.1101 | 39.4971 | 382771.7444
| ZN2568:PA25 | 396 | 921.5164 | 48.17 | 2.3271 | 48.17 | 20348 | 19552 | 826476 | 2012-05-28 17:31 | 2012-05-28 21:30 | 239 | 11kV | 45918 | 308 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Report Smoke from S2559. Instructed DOp to Open S2973SwB @1830 & Isolate section of 11kv fdr from S2973SwB via RMI at S2559 to S4797 Section of Pa39 fdr at Zn2568 St Peters Transformer Tail Defective See 826763,5 Exclude 826476,80,91 | May | 2012 | 2012Q4 | 2012 | ZN2568:PA39 | ZN2568:PA39 | ZN02568/000039 | INNER WEST | UG | Not Veg | 2012-05-28 | N | 149.0844 | N | 1 | N | N | 1.1101 | 39.4971 | 33555.52
| ZN2568:PA26 | 2763 | 1803.1473 | 39.91 | 0.6526 | 39.91 | 18749 | 1586 | 826562 | 2012-05-29 05:50 | 2012-05-29 11:50 | 360 | 11kV | 1800 | 5 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | PT12168 Bushells Peats Ridge 0.1 - Road & Centre phase 16A HDo replaced Tree branch on OH mains removed by DOp | May | 2012 | 2012Q4 | 2012 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2012-05-29 | N | 360 | N | 5 | N | N | 1.1101 | 39.4971 | 1315.3869
| ZN2568:PA27 | 1477 | 2166.5662 | 42.08 | 1.4669 | 42.08 | 18961 | 3515 | 826828 | 2012-05-29 11:50 | 2012-05-29 17:00 | 310 | 11kV | 310 | 1 | HV | Vandalism | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | LID 120933 3 phase outage Vandalism Earths stolen sub isolated to repair. | May | 2012 | 2012Q4 | 2012 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | Unknown | Not Veg | 2012-05-29 | N | 310 | N | 5 | N | N | 1.1101 | 39.4971 | 226.5389
| ZN2568:PA28 | 265 | 781.823 | #N/A | 2.9503 | 39.4971 | 18575 | 63 | 826996 | 2012-05-29 16:08 | 2012-05-29 21:45 | 337 | 11kV | 13581 | 93 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Ex Pnl.2 Lisarow Zn - REC 41708 Tapler Rd - Tripped , reclosed, tripped and locked out on Earth Leakage Abnormal Switching: REC41708 CLOSED - REC 41066 OPEN & DEFECTIVE Vehicle hit pole o/s 89 Macdonald Rd. see 827169 827170 | May | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2012-05-29 | N | 146.0323 | N | 5 | N | N | 1.1101 | 39.4971 | 9924.5942
| ZN2568:PA29 | 1836 | 1450.8121 | 43.54 | 0.7902 | 43.54 | 19811 | 12882 | 827120 | 2012-05-29 22:08 | 2012-05-29 22:28 | 20 | 11kV | 800 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120939 Fdr reclosed OK Please patrol. Excluded oms-827120. | May | 2012 | 2012Q4 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-05-29 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 584.6164
| ZN2568:PA31 | 920 | 451.1472 | #N/A | 0.49038 | 39.4971 | 19597 | 9822 | 827119 | 2012-05-29 22:05 | 2012-05-30 01:07 | 182 | 11kV | 134729 | 751 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | REC 45138 Yeramba Illalong tripped on A & B phase OC, IOC & lockout PT11705 Bambara Kullaroo is defective - seems HVDOs dont grade with REC 45138 see 827172 827171 | May | 2012 | 2012Q4 | 2012 | ZN12590:PA6 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2012-05-29 | N | 179.3995 | N | 5 | N | N | 1.1101 | 39.4971 | 98455.9794
| ZN2568:PA32 | 2416 | 1524.1083 | 38.4 | 0.63084 | 38.4 | 18911 | 3192 | 827127 | 2012-05-30 01:40 | 2012-05-30 02:20 | 40 | 11kV | 28924 | 751 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | REC 45138 Yeramba Illalong tripped on A + B phase OC, IOC and lockout The section of 11kV fdr between LK41801 and PT11705 has an intermitent phase to phase fault (tracking) see 827174 827173 | May | 2012 | 2012Q4 | 2012 | ZN12590:PA6 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2012-05-30 | N | 38.514 | N | 5 | N | N | 1.1101 | 39.4971 | 21136.8061
| ZN2568:PA33 | 53 | 306.1229 | #N/A | 5.7759 | 39.4971 | 19118 | 4735 | 827227 | 2012-05-30 09:29 | 2012-05-30 12:29 | 180 | 11kV | 180 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 120948 A & B phase DOLF : 31 Amp excluded OMS 827227 | May | 2012 | 2012Q4 | 2012 | 234:14291 | 264:81238 | ZN00264/081238 | PORT STEPHENS | UG | Not Veg | 2012-05-30 | N | 180 | N | 5 | N | N | 1.1101 | 39.4971 | 131.5387
| ZN2568:PA38 | 790 | 910.2255 | 59.43 | 1.1522 | 59.43 | 20060 | 15687 | 827374 | 2012-05-30 12:30 | 2012-05-30 16:15 | 225 | 11kV | 2850 | 30 | HV | Staff Other | Utility Process Issue | Pole | Unplanned | Unselected | N | LID 120956 3 fault operations Pole 7E-80058 fell over when boring for replacement pole. excluded OMS 827374 | May | 2012 | 2012Q4 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-05-30 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 2082.6959
| ZN2568:PA39 | 1038 | 970.3273 | 48.09 | 0.9348 | 48.09 | 20086 | 15881 | 827604 | 2012-05-30 20:23 | 2012-05-30 22:00 | 97 | 11kV | 9021 | 93 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT10164 Banksia Short defective Road Side HV Drop out assembly 50K. Fuse equipment - details below. Defective HV fuse carrier Related jobs: #827611, 827612, 827951, 827604 | May | 2012 | 2012Q4 | 2012 | ZN10996:PA9 | ZN10998:PA8 | ZN10998/000008 | BAYSIDE | OH | Not Veg | 2012-05-30 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 6592.2807
| ZN2568:PA40 | 363 | 518.7799 | 48.54 | 1.4291 | 48.54 | 20280 | 18170 | 827615 | 2012-05-30 20:31 | 2012-05-30 22:16 | 105 | 11kV | 11532 | 110 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn874 Concord: Panel 12 "S.2834" Nullawarra Curra" feeder tripped on Relays: Translay, I/T Receive, EFI Signals: 11kv trip, No.3 Tx, GE, ZE At S5417 Hospital Rd "SW/A" tripped on: I/T Send, No.1 HVC EFI. Note no other flags operated Remarks: UG fault. 11KV feeeder failed from Sub874 Concord (Panel 12) to S.2834 Nullawarra Curra SW.A Related jobs: #827620, 827615, 827739, 827737, 827733 | May | 2012 | 2012Q4 | 2012 | ZN874:PA12 | ZN874:PA12 | ZN00874/000012 | CANADA BAY | UG | Not Veg | 2012-05-30 | N | 104.8364 | N | 5 | N | N | 1.1101 | 39.4971 | 8427.2455
| ZN2568:PA42 | 409 | 625.0593 | 44.38 | 1.5283 | 44.38 | 20395 | 20057 | 827632 | 2012-05-31 00:53 | 2012-05-31 02:10 | 77 | 11kV | 82313 | 1069 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120958 2 fault operations B & C phase Overcurrent Excluded OMS 827632 | May | 2012 | 2012Q4 | 2012 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2012-05-31 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 60151.9126
| ZN2568:PA6 | 23 | 1672.3747 | 40.52 | 72.7119 | 40.52 | 19375 | 8006 | 829003 | 2012-05-31 04:00 | 2012-05-31 11:27 | 447 | 11kV | 447 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 120957 Trip & Reclose - refer to OMS 829002 1 fault operation Earth fault 2 x 11kV tappings blown at pole GW-90001 feed to Sanitarium. Suspect UG cable fault. Excluded OMS 827634 | May | 2012 | 2012Q4 | 2012 |  |  |  | LAKE MACQUARIE | OH | Not Veg | 2012-05-31 | N | 447 | N | 3 | N | N | 1.1101 | 39.4971 | 326.6544
| ZN2568:PA7 | 298 | 2882.3279 | #N/A | 9.6722 | 39.4971 | 18599 | 244 | 827834 | 2012-05-31 12:00 | 2012-05-31 17:00 | 300 | 11kV | 2400 | 8 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 120967 A & C phase DOLF : 10 Amp L.V reported down truck hit pole ir-33417 Refer to related records 827834 and 827850 | May | 2012 | 2012Q4 | 2012 | 238:34141 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2012-05-31 | N | 300 | N | 3 | N | N | 1.1101 | 39.4971 | 1753.8492
| ZN2568:PA8 | 4 | 1716.824 | #N/A | 429.206 | 39.4971 | 18857 | 2624 | 829177 | 2012-06-01 12:40 | 2012-06-01 13:40 | 60 | 11kV | 840 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 120975 section isolated to repair fault at GU-84509 | June | 2012 | 2012Q4 | 2012 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2012-06-01 | N | 60 | N | 1 | N | N | 1.1101 | 39.4971 | 613.8472
| ZN2568:PA9 | 1235 | 1272.7583 | 39.57 | 1.0306 | 39.57 | 19003 | 4052 | 829182 | 2012-06-02 08:24 | 2012-06-02 09:00 | 36 | 11kV | 15840 | 440 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 120989 1 fault operation Sw 50797 on non-auto reclose for planned work at the time of tripping. | June | 2012 | 2012Q4 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-06-02 | N | 36 | N | 3 | N | N | 1.1101 | 39.4971 | 11575.4048
| ZN3154:PA10 | 1013 | 1036.4879 | 31.04 | 1.0232 | 31.04 | 19914 | 13925 | 828556 | 2012-06-02 00:55 | 2012-06-02 10:03 | 548 | 11kV | 75624 | 138 | HV | Fire (non-electrical) | Adverse Weather/Environment | 3rd Party Asset | Unplanned | Unselected | N | S.2141 Allen Cant off P-30 interrupted by DOp at remote ends due to factory wall collapse on S.2141 Allen Cant. Interrupted for Safety Reasons. Due to wall collapse on substation, during factory fire. | June | 2012 | 2012Q4 | 2012 | ZN690:PA30 | ZN690:PA30 | ZN00690/000030 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2012-06-02 | N | 548 | N | 3 | N | N | 1.1101 | 39.4971 | 55263.7887
| ZN3154:PA11 | 814 | 929.0705 | 33.6 | 1.1414 | 33.6 | 20036 | 15409 | 828752 | 2012-06-02 21:26 | 2012-06-02 22:25 | 59 | 11kV | 1018 | 32 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 15001 BEACON HILL Pnl 10 "S.16679 Rodborough Rd 14A, S16857 Frenches hurdis No.2".Recloser REC.21779 Oxford brooker Tripped and reclosed. HV fuse operated at PT 16378 Oxford Weardon. Restored via lv parallel due to access issues requires EWP EFI's on feeder and on panel 10 reset. Signals @ REC 21799:OC,IOC. Possum at PT 16378 Oxford Wearden.HV centre phase fuse reqiures replacement, EWP required restored via lv paralell Refer 829339 and 830485 | June | 2012 | 2012Q4 | 2012 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2012-06-02 | N | 31.8125 | N | 3 | N | N | 1.1101 | 39.4971 | 743.9244
| ZN3154:PA12 | 700 | 915.326 | 38.98 | 1.3076 | 38.98 | 19632 | 10497 | 828761 | 2012-06-03 00:56 | 2012-06-03 02:40 | 104 | 11kV | 3380 | 62 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 120993 1 fault operation Sensitive Earth Fault Replaced B phase DOLF & arrestor sub 51075. Isolated switchboard to dairy, main sw burnt up, customer to get contractor. Excluded OMS 828761 | June | 2012 | 2012Q4 | 2012 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2012-06-03 | N | 54.5161 | N | 4 | N | N | 1.1101 | 39.4971 | 2470.0043
| ZN3154:PA13 | 634 | 701.1233 | 30.36 | 1.1059 | 30.36 | 19887 | 13625 | 828760 | 2012-06-03 01:00 | 2012-06-03 02:50 | 110 | 11kV | 3630 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Section of Pnl.2 Lisarow from LB40866 to REC41066 interrupted for safety reasons Abnormal Switching: REC41708 CLOSED - REC41066 OPENED Isolated for safety due to 11kV conductor being in contact with pole | June | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2012-06-03 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 2652.6969
| ZN3154:PA14 | 435 | 447.2666 | 30.03 | 1.0282 | 30.03 | 20306 | 19023 | 828788 | 2012-06-03 07:00 | 2012-06-03 09:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 120995 Single phase DOLF : 10 Amp Excluded OMS 828788 | June | 2012 | 2012Q4 | 2012 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2012-06-03 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 87.6925
| ZN3154:PA16 | 1012 | 1119.685 | 31.47 | 1.1064 | 31.47 | 19909 | 13870 | 828769 | 2012-06-03 06:42 | 2012-06-03 10:30 | 228 | 11kV | 1925 | 15 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 120994 and 120996 A phase DOLF : 10 Amp, Single phase DOLF : 10 Amp FAULTY ARRESTOR.RENEWED. Refer OMS 829203, 829203 Excluded OMS REPORT NO 828769, 829191 | June | 2012 | 2012Q4 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-06-03 | N | 128.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 1406.7332
| ZN3154:PA17 | 905 | 963.3425 | 30.35 | 1.0645 | 30.35 | 18711 | 1220 | 829080 | 2012-06-04 10:09 | 2012-06-04 12:50 | 161 | 11kV | 389076 | 4460 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121003 1 fault operation C phase Overcurrent; Sensitive Earth Fault Large gum tree down across 11kV mains 5 span down, HV into LV. A/R was OFF for planned work at the time of the fault. | June | 2012 | 2012Q4 | 2012 | 232:11459 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2012-06-04 | N | 87.2368 | N | 6 | N | N | 1.1101 | 39.4971 | 284325.265
| ZN3154:PA18 | 1258 | 1463.7554 | 32.25 | 1.1636 | 32.25 | 19092 | 4585 | 829121 | 2012-06-04 10:48 | 2012-06-04 12:50 | 122 | 11kV | 110690 | 1076 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Chamhaven Zn Pnl.21 tripped on A Ph timed O/C, earth fault, EFI, Fault Check Field EFIs: S14236 14501 14577 14578 Suspect UG cable fault from 11kV USL44068 to CP44585 to S14584 tee PT14001 See 829630 829631 829633 | June | 2012 | 2012Q4 | 2012 | ZN14892:PA21 | ZN14892:PA21 | ZN14892/000021 | CENTRAL COAST | UG | Not Veg | 2012-06-04 | N | 102.8717 | N | 6 | N | N | 1.1101 | 39.4971 | 80888.9872
| ZN3154:PA19 | 788 | 1023.3404 | 34.91 | 1.2987 | 34.91 | 18971 | 3597 | 828956 | 2012-06-04 06:18 | 2012-06-04 14:45 | 507 | 11kV | 50269 | 241 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 121002 3 fault operations B & C Phase Earth fault MAINS ON GROUND ADJ ABS48523. Excluded OMS REPORT NO 828993. | June | 2012 | 2012Q4 | 2012 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2012-06-04 | N | 208.5851 | N | 6 | N | N | 1.1101 | 39.4971 | 36735.1025
| ZN3154:PA22 | 816 | 889.028 | 33.16 | 1.0895 | 33.16 | 18858 | 2630 | 829414 | 2012-06-04 15:27 | 2012-06-04 18:10 | 163 | 11kV | 323967 | 2370 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | @16:37 Long Jetty Zone Pnl.20 tripped on IOC, SEL After switching to restore Pnl.11 11kV OH bond burnt bringing down mains to the ground between AB41104 and AB45005 See 829672 829673 + 829541 829677 | June | 2012 | 2012Q4 | 2012 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2012-06-04 | N | 136.6949 | N | 6 | N | N | 1.1101 | 39.4971 | 236745.5282
| ZN3154:PA23 | 507 | 541.5091 | 30.74 | 1.0681 | 30.74 | 20440 | 20424 | 829479 | 2012-06-04 16:37 | 2012-06-04 19:50 | 193 | 11kV | 41569 | 918 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | @16:37 Long Jetty Zone Pnl.20 tripped on IOC, SEL After switching to restore Pnl.11 11kV OH bond burnt bringing down mains to the ground between AB41104 and AB45005 See 829672 829673 + 829541 829677 | June | 2012 | 2012Q4 | 2012 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2012-06-04 | N | 45.2821 | N | 6 | N | N | 1.1101 | 39.4971 | 30377.3991
| ZN3154:PA24 | 1018 | 907.6134 | 34.26 | 0.89157 | 34.26 | 19058 | 4398 | 829563 | 2012-06-04 21:16 | 2012-06-04 22:45 | 89 | 11kV | 24531 | 343 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Erina Zone P16L - REC46673 Terrigal Penrose - tripped & reclosed & tripped on IOC Cause not ascertained See 829889 829898 829902 | June | 2012 | 2012Q4 | 2012 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-06-04 | N | 71.519 | N | 6 | N | N | 1.1101 | 39.4971 | 17926.5313
| ZN3154:PA25 | 609 | 515.3391 | 32.15 | 0.84621 | 32.15 | 18748 | 1584 | 829573 | 2012-06-05 02:54 | 2012-06-05 04:00 | 66 | 11kV | 47916 | 726 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9900 Menai P-20 "S.9350 McMahon Allison", fdr tripped on: RELAYS: Earth fault, EFI SIGNALS: 11kV trip, Z eth, GE No.2 FIELD EFIs: Nil REMARKS: UG Fault. 11kv UG Fault from ZN.9900 Menai P-20 to S,9350 McMahon Allison. | June | 2012 | 2012Q4 | 2012 | ZN9900:PA20 | ZN9900:PA20 | ZN09900/000020 | SUTHERLAND | UG | Not Veg | 2012-06-05 | N | 66 | N | 27 | Y | Y | 1.1101 | 39.4971 | 35015.5995
| ZN3154:PA3 | 328 | 384.6193 | 33.52 | 1.1726 | 33.52 | 18799 | 2126 | 830093 | 2012-06-05 16:22 | 2012-06-05 17:44 | 82 | 11kV | 127311 | 1581 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Zn931 Darlinghurst Pa25 11kv CB tripped on: Relays: Intertrip Recieve Cause: Tx Failure on Differential Fault S1565 #1Tx See 831605,6 Exclude 830093 | June | 2012 | 2012Q4 | 2012 | ZN931:PA25 | ZN931:PA25 | ZN00931/000025 | SYDNEY | UG | Not Veg | 2012-06-05 | N | 80.5256 | N | 27 | Y | Y | 1.1101 | 39.4971 | 93035.1238
| ZN3154:PA4 | 1220 | 1155.4172 | 31.29 | 0.94706 | 31.29 | 19162 | 5072 | 830144 | 2012-06-05 16:39 | 2012-06-05 17:46 | 67.4333 | 11kV | 120015.7167 | 2265 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 121015 tapping off at abs 7898. abs 7898 opened & Sw 35559 closed no protection operation also see report # 121018 / OMS 831346 Excluded oms # 830144 | June | 2012 | 2012Q4 | 2012 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2012-06-05 | N | 52.9871 | N | 27 | Y | Y | 1.1101 | 39.4971 | 87703.9459
| ZN3154:PA5 | 1180 | 963.2377 | 31.01 | 0.8163 | 31.01 | 18694 | 1087 | 830178 | 2012-06-05 16:42 | 2012-06-05 18:16 | 94 | 11kV | 210331 | 2250 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Wind | N | At S.36300 Balgowlah North, 11kV Fdr CB tripped on A and C phase IOC, 11kV trip, zone earth. Suspect trees in wind storm. Note:- 11kV has no auto reclose functionality | June | 2012 | 2012Q4 | 2012 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Veg | 2012-06-05 | N | 93.4804 | N | 27 | Y | Y | 1.1101 | 39.4971 | 153703.6911
| ZN3154:PA6 | 472 | 893.7622 | 47.41 | 1.8936 | 47.41 | 18615 | 353 | 830228 | 2012-06-05 16:58 | 2012-06-05 18:30 | 91.5667 | 11kV | 91.5667 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REFER JOB#830070 COMMENTS. CC1: 04-"Non Urgent - refer to OH Mains" | June | 2012 | 2012Q4 | 2012 | ZN9118:PA26 | ZN9118:PA26 | ZN09118/000026 | SUTHERLAND | OH | Veg | 2012-06-05 | N | 91.5667 | N | 27 | Y | Y | 1.1101 | 39.4971 | 66.9142
| 228:7486 | 3 | 3.8537 | 40.08 | 1.2846 | 40.08 | 19045 | 4358 | 830358 | 2012-06-05 17:25 | 2012-06-05 18:44 | 79 | 11kV | 98911 | 1263 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | At S129 Hunters Hill Panel 24 tripped on C phase O/C and Timing Cause Not ascertained for outage - Mains to Patrol in Daylight. See OMS 831256 831252 830358 | June | 2012 | 2012Q4 | 2012 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2012-06-05 | N | 78.3143 | N | 27 | Y | Y | 1.1101 | 39.4971 | 72281.2414
| 228:7487 | 1094 | 601.4313 | 34.49 | 0.54975 | 34.49 | 20218 | 17166 | 830429 | 2012-06-05 17:40 | 2012-06-05 19:29 | 109 | 11kV | 10464 | 96 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | RECLOSER 20852 TRIPPED ON OC WITH LOCKOUT | June | 2012 | 2012Q4 | 2012 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2012-06-05 | N | 109 | N | 27 | Y | Y | 1.1101 | 39.4971 | 7646.7826
| 228:7490 | 1590 | 899.594 | 35.12 | 0.56578 | 35.12 | 18974 | 3606 | 830292 | 2012-06-05 17:09 | 2012-06-05 19:38 | 149 | 11kV | 205340 | 1599 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Wind | N | aT s.15002 pANEL 6 fDR cb TRIPPED ON a PHASE TIMED oc, FRAME LEAKAGE, EFI, FAULT CHECK #2 tX, fIELD EFI'S DOWN AT s.16441, s.16903 | June | 2012 | 2012Q4 | 2012 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | UG | Not Veg | 2012-06-05 | N | 128.4178 | N | 27 | Y | Y | 1.1101 | 39.4971 | 150056.4155
| 228:7491 | 779 | 554.7469 | 36.56 | 0.71213 | 36.56 | 18956 | 3496 | 830273 | 2012-06-05 17:57 | 2012-06-05 19:45 | 108 | 11kV | 104257 | 1087 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Zn.14892 Charmhaven Pnl.13 tripped on O/C trip Due to storm see 831333 831335 831337 | June | 2012 | 2012Q4 | 2012 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 95.9126 | N | 27 | Y | Y | 1.1101 | 39.4971 | 76187.9405
| ZN4853:PA11 | 370 | 579.4713 | #N/A | 1.5661 | 39.4971 | 18761 | 1765 | 831346 | 2012-06-05 19:40 | 2012-06-05 19:45 | 5 | 11kV | 2545 | 509 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 121018 no protection operation abs 572 opened to cut away tapping at abs 7898 see report # 121015 / OMS 831332 | June | 2012 | 2012Q4 | 2012 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2012-06-05 | N | 5 | N | 27 | Y | Y | 1.1101 | 39.4971 | 1859.8109
| ZN4853:PA15 | 1825 | 1561.5044 | #N/A | 0.85562 | 39.4971 | 19671 | 11111 | 830519 | 2012-06-05 18:15 | 2012-06-05 20:20 | 125 | 11kV | 212250 | 1698 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | REC 41873 Woolana Woodlawn triped on O/C trip Wild Weather | June | 2012 | 2012Q4 | 2012 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 125 | N | 27 | Y | Y | 1.1101 | 39.4971 | 155106.0397
| ZN4853:PA17 | 846 | 778.5061 | #N/A | 0.92022 | 39.4971 | 19539 | 9489 | 830485 | 2012-06-05 18:01 | 2012-06-05 20:36 | 155 | 11kV | 143704 | 1115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Zn.12610 Long Jetty pnl.18 tripped on B & C Phase IOC Due to wild weather - 11kV OH saging neat PT46144 see 831768 831771 831773 831776 | June | 2012 | 2012Q4 | 2012 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 128.8825 | N | 27 | Y | Y | 1.1101 | 39.4971 | 105014.6446
| ZN4853:PA2 | 1764 | 1153.5494 | #N/A | 0.65394 | 39.4971 | 19433 | 8534 | 830514 | 2012-06-05 18:05 | 2012-06-05 21:20 | 195 | 11kV | 160614 | 1074 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12620 noraville Pnl.10 tripped on B Ph O/C Tree branch on 11kV mains between AB4326 abd AB43258 tee PT12474 See 831790 831791 831795 | June | 2012 | 2012Q4 | 2012 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 149.5475 | N | 27 | Y | Y | 1.1101 | 39.4971 | 117371.9739
| ZN4853:PA26 | 427 | 1073.3036 | #N/A | 2.5136 | 39.4971 | 19451 | 8718 | 830450 | 2012-06-05 17:47 | 2012-06-05 21:20 | 213 | 11kV | 56329 | 571 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121017 2 fault operations Tree branch on mains adjacent pole KR-10064 Winston Rd Eagleton. HV mains into LV mains. Sw 42321 opened following fault, closed at 1945 when comms finally returned. please patrol Excluded OMS 830450 & 830709 | June | 2012 | 2012Q4 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-06-05 | N | 98.6497 | N | 27 | Y | Y | 1.1101 | 39.4971 | 41163.5718
| ZN4853:PA7 | 18 | 407.7172 | #N/A | 22.651 | 39.4971 | 20423 | 20263 | 830329 | 2012-06-05 17:19 | 2012-06-05 21:46 | 267 | 11kV | 363363 | 2106 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Zn.12660 Woy Woy Pnl.5 tripped on: A Phase Timed O/C Abnormal switching: CP49100 BYPASSED - Sw6613 @ S14569 CLOSED - AB43575 OPEN Weather related no exact cause see 831248 831251 831250 831263 831265 831262 831258 | June | 2012 | 2012Q4 | 2012 | ZN12660:PA5 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 172.537 | N | 27 | Y | Y | 1.1101 | 39.4971 | 265534.963
| ZN4853:PA8 | 187 | 353.4921 | #N/A | 1.8903 | 39.4971 | 19588 | 9747 | 830775 | 2012-06-05 20:05 | 2012-06-05 22:51 | 165.6833 | 11kV | 132173.9333 | 798 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At 2226 hours, terrey Hills Panel 4 Fdr CB tripped and locked out on SE, 11kV trip. A bond was burnt off at AB.20435 (secondary issue). A unfound sequence 2 x HV fuses blown at F.21414. Large tree branch brought down HV near PT.15361. {Note: SE did not operate at Recloser 21350 | June | 2012 | 2012Q4 | 2012 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2012-06-05 | N | 165.6315 | N | 27 | Y | Y | 1.1101 | 39.4971 | 96588.812
| ZN901:PA10 | 418 | 657.8756 | 40.97 | 1.5739 | 40.97 | 19127 | 4834 | 830914 | 2012-06-05 22:17 | 2012-06-05 23:13 | 56 | 11kV | 64491 | 1219 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Tree branch brought down OH Spotter reported 11kv resting on LV at 73 Como rd. Section of 11kv from AB35830 to AB35914 to S49508SwA See 832678,80 exclude 830914 | June | 2012 | 2012Q4 | 2012 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2012-06-05 | N | 52.9048 | N | 27 | Y | Y | 1.1101 | 39.4971 | 47128.1206
| ZN901:PA2 | 166 | 744.4005 | #N/A | 4.4843 | 39.4971 | 20165 | 16454 | 830410 | 2012-06-05 17:38 | 2012-06-05 23:45 | 367 | 11kV | 226919 | 1956 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.18 tripped on B Phase O/C EFI OH resting on cross arm - High into Low near PT18326 II required see 832165 832166 832168 | June | 2012 | 2012Q4 | 2012 | ZN12570:PA18 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Not Veg | 2012-06-05 | N | 116.0118 | N | 27 | Y | Y | 1.1101 | 39.4971 | 165825.7122
| ZN901:PA26 | 703 | 1156.1783 | #N/A | 1.6446 | 39.4971 | 20228 | 17366 | 830812 | 2012-06-05 20:29 | 2012-06-06 01:00 | 271 | 11kV | 137641 | 1489 | HV | 3rd Party Vehicle | 3rd Party Impact | UGOH | Unplanned | Rain Wind Storm | N | @Zn10999 Pa10 fdr tripped, reclosed & locked out on; Alarms:11kv trip Cause: Vehicle hit pole. Section of 11kv from LB30021 to AB3085 tee S10767 damaged when vehicle hit pole at Stoney Creek rd & Preddys rd See 832648,50,1 Exclude 830812,21,39 | June | 2012 | 2012Q4 | 2012 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | UG | Not Veg | 2012-06-05 | N | 92.4385 | N | 27 | Y | Y | 1.1101 | 39.4971 | 100583.9831
| ZN901:PA27 | 2543 | 1396.2873 | #N/A | 0.54907 | 39.4971 | 19301 | 7327 | 830616 | 2012-06-06 00:38 | 2012-06-06 02:30 | 112 | 11kV | 117382 | 1381 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC.44936 Bently tripped / reclosed / tripped and locked out on O/C 11kV wire on ground line side and adjacent to REC44397 alan St. Feeder from AB40343 to REC44397 isolated. Further interruption beyond REC44397 at same time see #83295. Extended outage to S12804 - A & B phase fuse blown (415V) restored @ 10:20 #832247 see 832208 832211 832213 832235 | June | 2012 | 2012Q4 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-06-06 | N | 84.9978 | N | 11 | N | N | 1.1101 | 39.4971 | 85779.3034
| ZN901:PA29 | 690 | 664.9535 | #N/A | 0.9637 | 39.4971 | 20153 | 16359 | 830840 | 2012-06-05 20:41 | 2012-06-06 03:08 | 387 | 11kV | 31897 | 1501 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12590 lake Munmorah Pnl.2 tripped on A Ph IOC and timed O/C, EFI , EF Wild weather - tree down 11kV into the LV around AB44591 abd LB44808 tee PT14567 see 831840 831839 831841 | June | 2012 | 2012Q4 | 2012 | ZN12590:PA2 | ZN13000:PA10 | ZN13000/000010 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 21.2505 | N | 27 | Y | Y | 1.1101 | 39.4971 | 23309.3868
| ZN901:PA3 | 16 | 844.8575 | #N/A | 52.8036 | 39.4971 | 19972 | 14647 | 830848 | 2012-06-05 21:18 | 2012-06-06 04:00 | 402 | 11kV | 22914 | 57 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Unselected | N | PT12558 Albert Mulhall - footpath phase HVDO fuse blown BBLAS 31.5K Bouganvillia bush in proximity of lightning arrestors. tree trimming required | June | 2012 | 2012Q4 | 2012 | ZN12640:PA8 | ZN12640:PA8 | ZN12640/000008 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 402 | N | 27 | Y | Y | 1.1101 | 39.4971 | 16744.8754
| ZN901:PA31 | 2422 | 1722.2882 | #N/A | 0.7111 | 39.4971 | 19752 | 12436 | 830987 | 2012-06-06 01:51 | 2012-06-06 04:30 | 159 | 11kV | 73980 | 897 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 121022 3 fault operations 3 phase Overcurrent; Earth fault Tree on 11kV mains near Ballantrae St sub 13275 at Pole JV-41471. | June | 2012 | 2012Q4 | 2012 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Veg | 2012-06-06 | N | 82.4749 | N | 11 | N | N | 1.1101 | 39.4971 | 54062.402
| ZN901:PA36 | 190 | 433.6726 | #N/A | 2.2825 | 39.4971 | 18725 | 1301 | 832392 | 2012-06-06 07:48 | 2012-06-06 08:36 | 48 | 11kV | 51156 | 1199 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | REC 40185 tripped on O/C Tree branch on mains see 832392 832394 | June | 2012 | 2012Q4 | 2012 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Veg | 2012-06-06 | N | 42.6656 | N | 11 | N | N | 1.1101 | 39.4971 | 37383.296
| ZN901:PA38 | 1496 | 1249.7094 | #N/A | 0.83537 | 39.4971 | 20347 | 19538 | 831139 | 2012-06-06 03:50 | 2012-06-06 09:00 | 310 | 11kV | 67609 | 927 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn.12620 Noraville Pnl.2 tripped on Earth Faiult timed. Abnormal Switching: LB40214 closed to feeder LB44808 (open for lake munmorah DMA from LB44808 to AB44591) 11kV wire down from AB43175 to teee off to links41323. While returning adjacent feeder to service after repairs, panel 2 tripped due to another wire down and DOp opened AB43175 to isolate. @4:18 REC40178 tripped on O/C and SEL - 11kv on ground beyond recloser 40178 see 832351 832357 832347 | June | 2012 | 2012Q4 | 2012 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2012-06-06 | N | 72.9331 | N | 11 | N | N | 1.1101 | 39.4971 | 49406.6631
| ZN901:PA7 | 863 | 480.1132 | #N/A | 0.55633 | 39.4971 | 19537 | 9453 | 830571 | 2012-06-05 18:00 | 2012-06-06 09:54 | 954 | 11kV | 152640 | 160 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kV feeder from AB 31328 to AB 31021 middle phase bond burnt off at AB 31328. ex ZN.10991 Blakehurst P-1 "Woids Ave" feeder. Bond. At AB 31328 middle phase bond burnt off. | June | 2012 | 2012Q4 | 2012 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2012-06-05 | N | 954 | N | 27 | Y | Y | 1.1101 | 39.4971 | 111544.8099
| ZN901:PA8 | 130 | 848.033 | #N/A | 6.5233 | 39.4971 | 19951 | 14258 | 830049 | 2012-06-05 16:00 | 2012-06-06 10:00 | 1080 | 11kV | 195362.3 | 1357 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn9700 Kirrawee Pa20 11kv fdr tripped, reclsoed & locked out on; ABphase O/C, timer, LO; Alarms: 11kv trip Cause: Tree branch on OH Mains. At UGOH adjacent S9352 See 832613,4 Exclude 830049,92 | June | 2012 | 2012Q4 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2012-06-05 | N | 143.9663 | N | 27 | Y | Y | 1.1101 | 39.4971 | 142765.0066
| ZN901:PA9 | 577 | 952.5566 | 45.95 | 1.6509 | 45.95 | 18850 | 2565 | 831032 | 2012-06-06 | 2012-06-06 10:30 | 630 | 11kV | 28260 | 287 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC41845 tripped and locked out on SEF 11kV wire on ground in tee to PT11410 beyond links 41345. see 832285 832286 | June | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2012-06-06 | N | 98.4669 | N | 11 | N | N | 1.1101 | 39.4971 | 20651.5745
| 223:14393 | 1134 | 732.9327 | 31.82 | 0.64633 | 31.82 | 19498 | 9082 | 830604 | 2012-06-05 18:26 | 2012-06-06 10:30 | 964 | 11kV | 52694 | 96 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44937 Alan St tripped / reclosed twice and locked out on IOC Tree brought down 11kV feeder on ground one span from REC44937. Isolated from load links at RC44937 to LB40624 to Links 42939. | June | 2012 | 2012Q4 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-06-05 | N | 548.8958 | N | 27 | Y | Y | 1.1101 | 39.4971 | 38507.221
| 223:14394 | 1522 | 871.4494 | 31.92 | 0.57257 | 31.92 | 18665 | 789 | 831409 | 2012-06-06 09:47 | 2012-06-06 10:49 | 62 | 11kV | 5828 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REC 44607 tripped & locked out X2 on IOC trip Tree branch 2 bays nth of PT14718 | June | 2012 | 2012Q4 | 2012 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2012-06-06 | N | 62 | N | 11 | N | N | 1.1101 | 39.4971 | 4258.9305
| 223:14395 | 1663 | 855.1812 | 34.15 | 0.51424 | 34.15 | 19540 | 9495 | 830378 | 2012-06-05 17:29 | 2012-06-06 11:45 | 1096 | 11kV | 121147 | 527 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | At S.15014 Mona Vale, Panel 18 Fdr CB tripped on efi, fault check, zone earth, group earth, 11kV trip. Field efi's down at S.16489 and S.16147. HV down into LV O/S #66 Annam Rd Bayview | June | 2012 | 2012Q4 | 2012 | ZN15014:PA18 | ZN15014:PA18 | ZN15014/000018 | NORTHERN BEACHES | OH | Not Veg | 2012-06-05 | N | 229.8805 | N | 27 | Y | Y | 1.1101 | 39.4971 | 88530.6544
| 223:14397 | 1250 | 973.3257 | 32.98 | 0.77866 | 32.98 | 19467 | 8839 | 830979 | 2012-06-06 01:00 | 2012-06-06 11:50 | 650 | 11kV | 106154 | 233 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REC44995 Kulnurra tripped & locked out X3 on O/C trip Tree branch on george downes nr greta rd see 832382 832383 | June | 2012 | 2012Q4 | 2012 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2012-06-06 | N | 455.5966 | N | 11 | N | N | 1.1101 | 39.4971 | 77574.2122
| 223:14398 | 859 | 1158.4357 | 42.87 | 1.3486 | 42.87 | 19449 | 8669 | 831547 | 2012-06-06 11:05 | 2012-06-06 12:50 | 105 | 11kV | 630 | 6 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 121025 Single phase section isolated to repair pole 7F-40053 | June | 2012 | 2012Q4 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-06-06 | N | 105 | N | 11 | N | N | 1.1101 | 39.4971 | 460.3854
| 223:14399 | 143 | 97.9413 | 34.26 | 0.6849 | 34.26 | 19427 | 8497 | 831676 | 2012-06-06 12:32 | 2012-06-06 13:15 | 43 | 11kV | 817 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | PT12010 - roadside phase HDO operated cause not ascertained See 832406 832405 | June | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2012-06-06 | N | 43 | N | 11 | N | N | 1.1101 | 39.4971 | 597.0395
| 230:81432 | 983 | 717.9141 | 37.87 | 0.73033 | 37.87 | 20437 | 20396 | 830952 | 2012-06-05 23:41 | 2012-06-06 13:50 | 849 | 11kV | 313163 | 1889 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At S2400 Berowra Panel 15 tripped on B and Cphase O/C Cause: 11kV Mains into LV mains. See OMS 832293 832296 832295 832324 831080/030/963/962/960/956/952 | June | 2012 | 2012Q4 | 2012 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Not Veg | 2012-06-05 | N | 165.7824 | N | 27 | Y | Y | 1.1101 | 39.4971 | 228850.2837
| 230:81434 | 1342 | 1146.948 | 34.29 | 0.85466 | 34.29 | 19800 | 12792 | 832159 | 2012-06-05 22:58 | 2012-06-06 15:25 | 987 | 11kV | 38710 | 961 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S.15013 Terrey Hills, Panel 6 Fdr CB tripped on SEL whilst trying to restore Panel 4 via AB.25104. Cause initially was tree brought down OH near PT.1536.Two fuses blown at F.21414. AB.20435 burnt bond (a secondary issue). | June | 2012 | 2012Q4 | 2012 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2012-06-05 | N | 40.281 | N | 27 | Y | Y | 1.1101 | 39.4971 | 28288.1262
| 230:81438 | 555 | 385.75 | 33.35 | 0.69504 | 33.35 | 18806 | 2194 | 832156 | 2012-06-06 05:00 | 2012-06-06 16:35 | 695 | 11kV | 695 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Wind | N | At CP.1623, the A and B phase 90 amp fuses replaced for a fault on Customers asset | June | 2012 | 2012Q4 | 2012 |  |  |  | NORTHERN BEACHES | Unknown | Not Veg | 2012-06-06 | N | 695 | N | 11 | N | N | 1.1101 | 39.4971 | 507.8855
| 230:81440 | 1651 | 1025.9103 | 28.57 | 0.62139 | 28.57 | 19929 | 14100 | 832142 | 2012-06-07 03:09 | 2012-06-07 04:28 | 79 | 11kV | 109968 | 1392 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.9118 Cronulla P-24 "S.9062 St Andrews Pl" tripped on: RELAYS: EFI, O/C timed E/F SIGNALS: 11kV trip, No.2 Group Eth, Zone Eth REMARKS: UG Fault. UG cable fault N.9118 Cronulla P-24 "S.9062 St Andrews Pl" to S.9062 St Andrews Pl. UG cable damage. | June | 2012 | 2012Q4 | 2012 | ZN9118:PA24 | ZN9118:PA24 | ZN09118/000024 | SUTHERLAND | UG | Not Veg | 2012-06-07 | N | 79 | N | 2 | N | N | 1.1101 | 39.4971 | 80361.3709
| 235:2120 | 714 | 732.578 | 39.65 | 1.026 | 39.65 | 18796 | 2094 | 832127 | 2012-06-06 21:47 | 2012-06-07 10:15 | 748 | 11kV | 8228 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11441 Cromarty Hill Nth Scenice - Centre phase HDO holder assembly broken repiared by T/Con | June | 2012 | 2012Q4 | 2012 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2012-06-06 | N | 748 | N | 11 | N | N | 1.1101 | 39.4971 | 6012.7797
| 235:2123 | 1384 | 1508.9256 | 43.09 | 1.0903 | 43.09 | 19116 | 4729 | 832683 | 2012-06-07 16:28 | 2012-06-07 18:50 | 142 | 11kV | 5668 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 121038 B phase Sensitive Earth Fault Tree fell over into mains at pole DQ-30022, breaking one tie from 11kV insulator that had to be re-attached. | June | 2012 | 2012Q4 | 2012 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-06-07 | N | 76.5946 | N | 2 | N | N | 1.1101 | 39.4971 | 4142.0072
| 235:2124 | 939 | 730.4641 | 31.15 | 0.77792 | 31.15 | 19183 | 5407 | 832802 | 2012-06-08 07:43 | 2012-06-08 09:00 | 77 | 11kV | 122397 | 1666 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At ZN.9700 Kirrawee 11kV P-20 "The Belmont Cook fdr", tripped on: RELAYS: SEF SIGNALS: 11kv trip FIELD EFIs: Nil ABNORMAL: Sw A S.9196 Presidnet Eton closed. Sw B S.9323 Flora Eton opened. REMARKS: Bond. AB 35136 has roadside bond burnt off. | June | 2012 | 2012Q4 | 2012 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2012-06-08 | N | 73.4676 | N | 2 | N | N | 1.1101 | 39.4971 | 89444.1175
| 235:2728 | 334 | 244.2687 | 33.87 | 0.73134 | 33.87 | 19907 | 13833 | 833211 | 2012-06-08 21:28 | 2012-06-09 01:15 | 227.05 | 11kV | 23257.7333 | 206 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At ZN.10901 Alexander Laycock A phase LV braid from TX to LV board has gone HR. Transformer tail defective. | June | 2012 | 2012Q4 | 2012 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | UG | Not Veg | 2012-06-08 | N | 112.9016 | N | 2 | N | N | 1.1101 | 39.4971 | 16996.0655
| 235:2857 | 312 | 267.8883 | 34.45 | 0.85862 | 34.45 | 19354 | 7683 | 833307 | 2012-06-09 03:47 | 2012-06-09 11:34 | 467 | 11kV | 42647 | 211 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121054 2 fault operations B phase Earth fault 11Kv main down between pole GQ-47486 & GQ-47487 accross dam. | June | 2012 | 2012Q4 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-06-09 | N | 202.1185 | N | 5 | N | N | 1.1101 | 39.4971 | 31165.1697
| 235:8684 | 143 | 800.5226 | 48.92 | 5.5981 | 48.92 | 19013 | 4163 | 833306 | 2012-06-09 02:20 | 2012-06-09 16:05 | 825 | 11kV | 72722 | 442 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121051 3 fault operations A phase Overcurrent OC at Sw 50797. 11kV wires down at sub 12937 A-phase EF check at Sw 81208. | June | 2012 | 2012Q4 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-06-09 | N | 164.5294 | N | 5 | N | N | 1.1101 | 39.4971 | 53143.0927
| 235:8685 | 115 | 87.5586 | 49.16 | 0.76138 | 49.16 | 20355 | 19780 | 833419 | 2012-06-09 12:28 | 2012-06-09 16:20 | 232 | 11kV | 232 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121058 Single phase DOLF : 5 Amp excluded OMS (heirarchy) 833419 | June | 2012 | 2012Q4 | 2012 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-06-09 | N | 232 | N | 5 | N | N | 1.1101 | 39.4971 | 169.5388
| 502:48001 | 307 | 196.9502 | #N/A | 0.64153 | 39.4971 | 19383 | 8108 | 833494 | 2012-06-09 17:41 | 2012-06-09 18:56 | 75 | 11kV | 20947 | 1033 | HV | Overload | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Unselected | N | REC45189 Cooks Peats Ridge 0.5 tripped on overload. Abnormal Switching: Bypass Closed @ REC44961 and AB43233 Open/Defective Overload due to abnormal switching see 834481 834480 734478 | June | 2012 | 2012Q4 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-06-09 | N | 20.2778 | N | 5 | N | N | 1.1101 | 39.4971 | 15307.4498
| 502:48002 | 207 | 159.3023 | 38.87 | 0.76958 | 38.87 | 19704 | 11714 | 833548 | 2012-06-09 23:58 | 2012-06-10 01:06 | 68 | 11kV | 117267 | 1735 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.12660 Woy Woy Pnl.10 tripped and locked out on ABC phase IOC, EFI Field EFI @ S12696 Possum caused flashover on UGOH to S14713. No damage see 834502 834503 | June | 2012 | 2012Q4 | 2012 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Not Veg | 2012-06-09 | N | 67.589 | N | 5 | N | N | 1.1101 | 39.4971 | 85695.2648
| 502:48004 | 1442 | 1092.5384 | 32.25 | 0.75765 | 32.25 | 20326 | 19314 | 833555 | 2012-06-10 02:02 | 2012-06-10 04:15 | 133 | 11kV | 183033 | 1869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN.398 Dulwich Hill P-15 "Victoria Clissold fdr" tripped. RELAYS: A phase ins, EFI EFIs: S.5048, S.2583, REMARKS: UG Fault. UG cable fault in section of 11kV feeder from SW B at S,2583 Victporia Robert to SW A at S.8972 Park ln Shepherd tee S.5067 Robert Rose. | June | 2012 | 2012Q4 | 2012 | ZN398:PA15 | ZN398:PA15 | ZN00398/000015 | INNER WEST | UG | Not Veg | 2012-06-10 | N | 97.931 | N | 3 | N | N | 1.1101 | 39.4971 | 133755.1178
| 502:48008 | 793 | 510.97 | 33.48 | 0.64435 | 33.48 | 19959 | 14447 | 833636 | 2012-06-10 10:28 | 2012-06-10 12:05 | 97 | 11kV | 65863 | 679 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kV feeder ex S1193 Lindfield Panel 16 AB1063 found burnt off on footpath side. See OMS 834623 833636 | June | 2012 | 2012Q4 | 2012 | ZN1193:PA16 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2012-06-10 | N | 97 | N | 3 | N | N | 1.1101 | 39.4971 | 48130.7378
| 502:48009 | 119 | 145.8916 | 36.03 | 1.226 | 36.03 | 18764 | 1785 | 833631 | 2012-06-10 10:18 | 2012-06-10 12:20 | 122 | 11kV | 5734 | 47 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11004 Sydney Ocean Beach -C phase 3.15A hDO fuse blown Batch of 31.5A fuses have been mixed with 3.15A fuse. Operators SUPT notified to resolve | June | 2012 | 2012Q4 | 2012 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2012-06-10 | N | 122 | N | 3 | N | N | 1.1101 | 39.4971 | 4190.2381
| 502:48010 | 1560 | 971.0794 | 33.22 | 0.62249 | 33.22 | 19952 | 14261 | 834137 | 2012-06-11 20:18 | 2012-06-11 20:52 | 34 | 11kV | 5134 | 151 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S167 Auburn Panel 11 "Beaconsfield silver" 11KV feeder tripped on; EF, EFC, EFI Alarms; 11kv trip, TX 3 GE No field EFI's operated Remarks: UG Fault. Suspect UG Cable fault from S.167 Auburn (Panel 11) to S.1923 Beaconsfield Silver (Sw/B) Related jobs: #834137, 834312 | June | 2012 | 2012Q4 | 2012 | ZN167:PA11 | ZN167:PA11 | ZN00167/000011 | PARRAMATTA | UG | Not Veg | 2012-06-11 | N | 34 | N | 2 | N | N | 1.1101 | 39.4971 | 3751.7758
| ZN15013:PA1 | 342 | 736.2203 | #N/A | 2.1527 | 39.4971 | 19130 | 4843 | 834168 | 2012-06-12 00:48 | 2012-06-12 01:30 | 42 | 11kV | 30492 | 726 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Unselected | N | At ZN.9550 Gwawley Bay P-36 "LB47770 etc" fdr tripped on: SIGNALS: 11kV Trip, Zone Earth, TX.3 grp Eth RELAYS: 50TB, 50TN, EFI REMARKS: Lightning / Surge Arrestor. Possum commited suicide at UGOH to S.9875 damaging centre phase LA. | June | 2012 | 2012Q4 | 2012 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2012-06-12 | N | 42 | N | 7 | N | N | 1.1101 | 39.4971 | 22282.6542
| ZN15013:PA10 | 626 | 823.9104 | 42.23 | 1.3162 | 42.23 | 18869 | 2750 | 835022 | 2012-06-12 04:23 | 2012-06-12 06:20 | 117 | 11kV | 96230 | 869 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S965 Pennant Hills panel 26 tripped on Relays: EF, timing, lockout and efi. Cause: UG fault between S6153 and S2696 and S4988 See OMS 385022, 835023, 835025, 835024 | June | 2012 | 2012Q4 | 2012 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2012-06-12 | N | 110.7365 | N | 7 | N | N | 1.1101 | 39.4971 | 70322.0457
| ZN15013:PA12 | 148 | 938.2282 | #N/A | 6.3394 | 39.4971 | 18918 | 3223 | 834214 | 2012-06-12 07:09 | 2012-06-12 07:55 | 46.4833 | 11kV | 2928.45 | 63 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Unselected | N | PT13494 Lexing tone Avoca - Footpath phase HDO blown 31.5A Stick on TX | June | 2012 | 2012Q4 | 2012 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Veg | 2012-06-12 | N | 46.4833 | N | 7 | N | N | 1.1101 | 39.4971 | 2140.0249
| ZN15013:PA2 | 68 | 322.6307 | #N/A | 4.7446 | 39.4971 | 20411 | 20200 | 834175 | 2012-06-12 03:07 | 2012-06-12 08:26 | 319 | 11kV | 218779 | 949 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S1195 Lindfield Panel 9 tripped and reclosed on relays A phase O/C, LO and EFI. Signals: 11kV Trip, Zone Earth and No1 Group Earth. Cause: Tree branhes between LB1427 and LB1278. Based on operator comments bond blown at CP1427 See OMS 835209 835207 834181/185/178/180/183/175/182/176 | June | 2012 | 2012Q4 | 2012 | ZN1193:PA9 | ZN1193:PA21 | ZN01193/000021 | KU-RING-GAI | OH | Veg | 2012-06-12 | N | 230.5364 | N | 7 | N | N | 1.1101 | 39.4971 | 159877.2403
| ZN15013:PA4 | 872 | 1475.2227 | 39.52 | 1.6918 | 39.52 | 20128 | 16166 | 834095 | 2012-06-11 18:00 | 2012-06-12 09:00 | 900 | 11kV | 28800 | 32 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | PT18484 pacific Ashbrook - Experienced low volts due to defective AB abnormal switching. Switching: AB43233 Open/Defective - REC44961 by-passed - TCAT18836 by-passed due to peak load Volts restored via restoring TCAT18836 | June | 2012 | 2012Q4 | 2012 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-06-11 | N | 900 | N | 2 | N | N | 1.1101 | 39.4971 | 21046.1905
| ZN15013:PA6 | 231 | 360.9913 | 32.84 | 1.5627 | 32.84 | 18924 | 3318 | 834462 | 2012-06-12 10:45 | 2012-06-12 11:30 | 44.5667 | 11kV | 33736.9667 | 757 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121064 No protection operation. Tapping off at ABS 20855 CC1: 22-"Refer to SOp" | June | 2012 | 2012Q4 | 2012 | 260:33347 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2012-06-12 | N | 44.5667 | N | 7 | N | N | 1.1101 | 39.4971 | 24653.9802
| ZN15013:PA8 | 141 | 1340.7622 | 43.16 | 9.509 | 43.16 | 20189 | 16823 | 834170 | 2012-06-12 01:31 | 2012-06-12 11:50 | 619 | 11kV | 100720 | 571 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID 121062 1 fault operation Sensitive Earth Fault Tree brought down 11kV mains at LF 18465. | June | 2012 | 2012Q4 | 2012 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-06-12 | N | 176.3923 | N | 7 | N | N | 1.1101 | 39.4971 | 73603.2053
| 238:34136 | 1783 | 1308.9588 | 35.41 | 0.73413 | 35.41 | 20373 | 19915 | 834842 | 2012-06-12 17:30 | 2012-06-12 21:00 | 210 | 11kV | 3360 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV feeder interrupted by DOp for emergency cut out from Auto Link 47645 Tree about to fall on HV distributor | June | 2012 | 2012Q4 | 2012 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-06-12 | N | 210 | N | 7 | N | N | 1.1101 | 39.4971 | 2455.3889
| 238:34137 | 280 | 611.7656 | #N/A | 2.1849 | 39.4971 | 18914 | 3211 | 835191 | 2012-06-13 11:32 | 2012-06-13 13:10 | 98 | 11kV | 4606 | 47 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT46696 Ena Quarang - Footpath phase HDO fell open Didnt fail - fell out | June | 2012 | 2012Q4 | 2012 | ZN12570:PA9 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Not Veg | 2012-06-13 | N | 98 | N | 2 | N | N | 1.1101 | 39.4971 | 3365.9289
| 238:34138 | 821 | 454.7326 | 31.45 | 0.55388 | 31.45 | 19654 | 10894 | 835325 | 2012-06-13 13:52 | 2012-06-13 15:37 | 105 | 11kV | 1890 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 121075 2 fault operations C phase Earth fault Excluded OMS 835325 | June | 2012 | 2012Q4 | 2012 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2012-06-13 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 1381.1563
| 238:34140 | 450 | 186.311 | 31.75 | 0.41402 | 31.75 | 20114 | 16084 | 835913 | 2012-06-14 13:57 | 2012-06-14 17:40 | 222.9167 | 11kV | 2229.1667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121088 Single phase DOLF : 5 Amp CC1: 22-"Refer to SOp" | June | 2012 | 2012Q4 | 2012 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-06-14 | N | 222.9167 | N | 1 | N | N | 1.1101 | 39.4971 | 1629.0093
| 238:34141 | 1100 | 548.5185 | 31.52 | 0.49865 | 31.52 | 19580 | 9731 | 836092 | 2012-06-15 00:36 | 2012-06-15 02:00 | 84 | 11kV | 5208 | 62 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | At PT1108 Finlay Mawson middle and roadside HVDO fuse operated Cause: Possum on HV fuse assembly See OMS 837728 837722 836092 836097 | June | 2012 | 2012Q4 | 2012 | ZN2635:PA1 | ZN2635:PA43 | ZN02635/000043 | PARRAMATTA | OH | Not Veg | 2012-06-15 | N | 84 | N | 5 | N | N | 1.1101 | 39.4971 | 3805.8528
| 238:34143 | 1323 | 835.0162 | 30.68 | 0.63115 | 30.68 | 19193 | 5582 | 836993 | 2012-06-15 09:00 | 2012-06-15 09:20 | 20 | 11kV | 2200 | 110 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | LID 121093 3 phase interruption SI 23175 request indicated interuption , cust not notified. | June | 2012 | 2012Q4 | 2012 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2012-06-15 | N | 20 | N | 5 | N | N | 1.1101 | 39.4971 | 1607.6951
| 238:34144 | 525 | 1415.0684 | 58.64 | 2.6954 | 58.64 | 20239 | 17515 | 836159 | 2012-06-15 09:27 | 2012-06-15 10:20 | 53 | 11kV | 73063 | 1386 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @Zn10997 Sans Souci Pa12 "Calreville Ave" fdr tripped on: Relays: SEF Signals: 11kv trip Cause: AB31158 has an open bond on footpath side outgoing feeder See 837324,6 Exclude 836159,81 | June | 2012 | 2012Q4 | 2012 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | OH | Not Veg | 2012-06-15 | N | 52.715 | N | 5 | N | N | 1.1101 | 39.4971 | 53392.2854
| 238:34147 | 71 | 41.6781 | 30.7 | 0.58701 | 30.7 | 19199 | 5782 | 836278 | 2012-06-15 11:38 | 2012-06-15 13:05 | 87 | 11kV | 42108 | 484 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 121094 2 fault operations 3 phase Overcurrent; Earth fault truck hit pole ah 50996 Kelly st x Joan Scone Excluded OMS 836278; 836283; 836284; 836294 | June | 2012 | 2012Q4 | 2012 | 813:89059 | 813:89059 | ZN00813/089059 | UPPER HUNTER | OH | Not Veg | 2012-06-15 | N | 87 | N | 5 | N | N | 1.1101 | 39.4971 | 30771.2844
| 238:34148 | 153 | 39.9893 | 33.92 | 0.26137 | 33.92 | 19384 | 8135 | 836358 | 2012-06-15 13:38 | 2012-06-15 14:30 | 52 | 11kV | 12844 | 247 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 121095 3 phase Overcurrent; Earth fault UGOH termination blown up at pole JT-91797. Excluded OMS 836358 & 836369. | June | 2012 | 2012Q4 | 2012 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | Unknown | Unknown | 2012-06-15 | N | 52 | N | 5 | N | N | 1.1101 | 39.4971 | 9386.0164
| 238:34150 | 689 | 1381.7922 | 50.77 | 2.0055 | 50.77 | 18942 | 3429 | 836537 | 2012-06-16 00:35 | 2012-06-16 02:00 | 85 | 11kV | 20910 | 246 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | @S1440 Fuse ruptured tripping RMI Tx Tee off Cause: End Box Fault, Tx1 failed See 837331 exclude 836537 | June | 2012 | 2012Q4 | 2012 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2012-06-16 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 15280.4113
| 238:34151 | 1109 | 647.8556 | 30.67 | 0.58418 | 30.67 | 19412 | 8385 | 836669 | 2012-06-16 14:27 | 2012-06-16 19:44 | 317 | 11kV | 75122 | 895 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | @Zn10996 Rockdale Zone Pa10 LB31264 fdr tripped, reclosed and locked out on Earth Leakage, Timing and Lockout relays, EFI. Cause: OH resting on cross arm, 11kv pulled away from insulator near LB31116 on General Holmes Dr. See 837335,6,7 Exclude 836669 PT10779 interrupted for safety due to OH resting on cross arm See 837339 exclude 836708 | June | 2012 | 2012Q4 | 2012 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2012-06-16 | N | 83.9352 | N | 2 | N | N | 1.1101 | 39.4971 | 54896.9419
| 204:82689 | 1077 | 1057.5147 | 42.99 | 0.98191 | 42.99 | 20287 | 18542 | 836746 | 2012-06-17 00:06 | 2012-06-17 02:00 | 114 | 11kV | 7752 | 68 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Rain Light | N | LID 121102 A phase DOLF : 31 Amp possum at pole IU-81527, 3rd time in 12 months possum at this pole please make repairs asap. Excluded OMS 836746 | June | 2012 | 2012Q4 | 2012 | 214:8670 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Not Veg | 2012-06-17 | N | 114 | N | 2 | N | N | 1.1101 | 39.4971 | 5664.933
| 204:82691 | 1306 | 741.55 | 41.27 | 0.5678 | 41.27 | 19413 | 8386 | 837381 | 2012-06-17 12:50 | 2012-06-17 12:58 | 8 | 11kV | 7104 | 888 | HV | Staff Operation | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | @Zn10996 Rockdale 11kv Pa10 fdr tripped Relays: EFI, Bph timed OC Signals: Tx1 GE 11kv Prot EFI's: S10109 Abnormal: Pt10050 in LV//. S10402 Sw/B closed, S10402 Sw/A opened Cuase: UG Fault. Yesterday a fault occured on this fdr. A wire was found on Xarm and was repaired today was being RTS at time DOp closed LV31116 the feeder tripped. | June | 2012 | 2012Q4 | 2012 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | UG | Not Veg | 2012-06-17 | N | 8 | N | 2 | N | N | 1.1101 | 39.4971 | 5191.3937
| 204:82697 | 1595 | 802.467 | 35.27 | 0.50311 | 35.27 | 19425 | 8491 | 837083 | 2012-06-18 10:09 | 2012-06-18 13:14 | 185 | 11kV | 11100 | 60 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT18648 patonga Bay - Roadside phase 11kV HDO ruptured Fuse Fatigue see 837612 837613 | June | 2012 | 2012Q4 | 2012 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2012-06-18 | N | 185 | N | 2 | N | N | 1.1101 | 39.4971 | 8111.5526
| 204:82699 | 989 | 1242.7154 | 47.85 | 1.2565 | 47.85 | 20431 | 20351 | 837548 | 2012-06-18 23:07 | 2012-06-19 01:25 | 138 | 11kV | 191544 | 1388 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11KV Panel 10 'AB31314 Etc" feeder frin S10999 KOGARAH @ AB31314 Centre Phase Bond Burnt Off Remarks: Bond. 11KV HV Bond Burnt Off @ AB31314 Related jobs: #837545, 837548, 837549, 837857 | June | 2012 | 2012Q4 | 2012 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Not Veg | 2012-06-18 | N | 138 | N | 2 | N | N | 1.1101 | 39.4971 | 139974.7056
| 204:82701 | 415 | 473.028 | 42.98 | 1.1398 | 42.98 | 19195 | 5589 | 837842 | 2012-06-19 13:17 | 2012-06-19 15:15 | 118 | 11kV | 118 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121130 B phase DOLF : 63 Amp Load: Aph - 40A, Bph - 80A, Cph - 80A. Volts: 248V Excluded OMS No. 837842 | June | 2012 | 2012Q4 | 2012 | 260:33344 | 239:82128 | ZN00239/082128 | LAKE MACQUARIE | OH | Veg | 2012-06-19 | N | 118 | N | 2 | N | N | 1.1101 | 39.4971 | 86.2309
| 204:82703 | 484 | 293.1636 | 41.35 | 0.60571 | 41.35 | 19230 | 6275 | 837935 | 2012-06-19 15:40 | 2012-06-19 16:26 | 46 | 11kV | 2352.8333 | 52 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT48611 Boyce Waner - HV fuse blown Footpath side 63Amp HDO Fuse fatigue See 83935 838120 CC1: 22-"Refer to SOp" | June | 2012 | 2012Q4 | 2012 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2012-06-19 | N | 45.2468 | N | 2 | N | N | 1.1101 | 39.4971 | 1719.3812
| 204:82705 | 1179 | 1069.5005 | 49.33 | 0.90713 | 49.33 | 20291 | 18667 | 838438 | 2012-06-20 15:43 | 2012-06-20 15:53 | 10 | 11kV | 7266 | 786 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121137 B & C phase overcurrent B phase on ABS 1417 burnt up. Excluded OMS No. 838438 + 838538 | June | 2012 | 2012Q4 | 2012 | 210:8682 | 210:83465 | ZN00210/083465 | NEWCASTLE | OH | Not Veg | 2012-06-20 | N | 9.2443 | N | 2 | N | N | 1.1101 | 39.4971 | 5309.7785
| 204:82708 | 22 | 413.7699 | 64.41 | 18.8077 | 64.41 | 18856 | 2596 | 838129 | 2012-06-20 09:16 | 2012-06-20 16:20 | 424 | 11kV | 38584 | 91 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT482 Graylind Wesson 31.5A fuse blown on B phase . Cause: Fuse Fatigue. 838656 838129 | June | 2012 | 2012Q4 | 2012 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Not Veg | 2012-06-20 | N | 424 | N | 2 | N | N | 1.1101 | 39.4971 | 28196.0492
| 204:82710 | 309 | 296.8379 | 51.93 | 0.96064 | 51.93 | 19459 | 8785 | 838563 | 2012-06-21 06:56 | 2012-06-21 08:20 | 84.45 | 11kV | 11316.3 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121139 B phase DOLF : 31 Amp | June | 2012 | 2012Q4 | 2012 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | UG | Not Veg | 2012-06-21 | N | 84.45 | N | 3 | N | N | 1.1101 | 39.4971 | 8269.6183
| 204:82711 | 13 | 27.3976 | #N/A | 2.1075 | 39.4971 | 18891 | 3012 | 838550 | 2012-06-21 06:18 | 2012-06-21 09:05 | 167 | 11kV | 35023.5 | 210 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121140 A Phase line tapping burnt off at stockton rsl sub pole Excluded oms 838568 | June | 2012 | 2012Q4 | 2012 | 228:7491 | 228:85415 | ZN00228/085415 | NEWCASTLE | OH | Not Veg | 2012-06-21 | N | 166.7786 | N | 3 | N | N | 1.1101 | 39.4971 | 25594.1408
| 412:83247 | 1 | 0 | #N/A | 0 | 39.4971 | 19719 | 11997 | 838654 | 2012-06-21 10:00 | 2012-06-21 11:35 | 94.6333 | 11kV | 88955.3333 | 940 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1673 Turramyurra Panel 13 Tripped on B phase IOC and Earth Fault with EFI. Cause: Cable failed in Jointing Pit O/S Zn Sub | June | 2012 | 2012Q4 | 2012 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | UG | Not Veg | 2012-06-21 | N | 94.6333 | N | 3 | N | N | 1.1101 | 39.4971 | 65005.9339
| 265:81641 | 45 | 363.2987 | 60.69 | 8.0733 | 60.69 | 20400 | 20113 | 839028 | 2012-06-22 06:46 | 2012-06-22 09:35 | 169.45 | 11kV | 2880.65 | 17 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121154 Burnt off tapping Pole ES-33403 (2nd pole beyond LF 40416) Isolated from LF 40416 for repairs. | June | 2012 | 2012Q4 | 2012 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2012-06-22 | N | 169.45 | N | 4 | N | N | 1.1101 | 39.4971 | 2105.0941
| 265:81645 | 41 | 274.5215 | 61.32 | 6.6956 | 61.32 | 18879 | 2899 | 839221 | 2012-06-22 11:39 | 2012-06-22 12:44 | 65 | 11kV | 6045 | 93 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC41708 Tapley Road tripped on timed OC Abnormal: REC41708 Closed - REC 41066 OPEN & Defective Tree branch on mains | June | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2012-06-22 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 4417.5077
| 265:81648 | 191 | 1207.452 | 49.85 | 6.3217 | 49.85 | 20386 | 20028 | 839486 | 2012-06-22 17:42 | 2012-06-22 19:00 | 78 | 11kV | 212626 | 2817 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Wyong Pnl.10 tripped on SEF Abnormal: Sw B @ S18367 CLOSED - AB41511 Open & Defective Bond burnt off at 11kV UGOH to Sw A @ S.14857 See840126 840122 841047 (GIS) | June | 2012 | 2012Q4 | 2012 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2012-06-22 | N | 75.4796 | N | 4 | N | N | 1.1101 | 39.4971 | 155380.8094
| 265:81649 | 44 | 400.3278 | 61.25 | 9.0984 | 61.25 | 18654 | 740 | 839524 | 2012-06-22 19:56 | 2012-06-22 20:46 | 50 | 11kV | 24972 | 511 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn711 Blackwattle Bay Pa23 fdr trippe don AC ph IOC EFI Cause: UG Fault See 840101,4 exclude 839524,9 | June | 2012 | 2012Q4 | 2012 | ZN711:PA23 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2012-06-22 | N | 48.8689 | N | 4 | N | N | 1.1101 | 39.4971 | 18248.8011
| 265:81651 | 153 | 286.8231 | 43.81 | 1.8747 | 43.81 | 18668 | 849 | 839550 | 2012-06-23 00:06 | 2012-06-23 01:15 | 69 | 11kV | 2208 | 32 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121168 A phase DOLF : 31 Amp Broken (not blown) fuse replaced, OK as left. Excluded OMS No 839550. | June | 2012 | 2012Q4 | 2012 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-06-23 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 1613.5413
| 525:34580 | 2 | 7.0379 | 68.29 | 3.519 | 68.29 | 19278 | 7164 | 840199 | 2012-06-23 08:00 | 2012-06-23 08:04 | 4 | 11kV | 7196 | 1799 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | @ZN10994 Mortdale 11kv fdr pa11 tripped on SEL Field EFI's NIL Tripped while switching AB31056 Defective. Could not be fully closed See 844122,3 exclude 840199,204 | June | 2012 | 2012Q4 | 2012 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2012-06-23 | N | 4 | N | 6 | N | N | 1.1101 | 39.4971 | 5258.6246
| 525:34586 | 2 | 0.32852 | 79.37 | 0.16426 | 79.37 | 19122 | 4757 | 839580 | 2012-06-23 08:20 | 2012-06-23 09:48 | 88 | 11kV | 131629 | 1500 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.12590 lakel Munmorah Pnl.3 Tripped on C phase timed & inst - lockout Cause not ascertained - pnl 3 did not reclosed due to open circuit solenoid fuses. Replaced by Dop see 840157 840158 | June | 2012 | 2012Q4 | 2012 | ZN12590:PA3 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Veg | 2012-06-23 | N | 87.7527 | N | 6 | N | N | 1.1101 | 39.4971 | 96190.5908
| 242:81532 | 914 | 636.3562 | 26.55 | 0.69623 | 26.55 | 19328 | 7526 | 839695 | 2012-06-23 13:51 | 2012-06-23 17:40 | 229 | 11kV | 1374 | 6 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 121174 A phase DOLF : 20 Amp. fallen private lv mains isolated at taps at pole IR-42624 Excluded oms 839695 | June | 2012 | 2012Q4 | 2012 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2012-06-23 | N | 229 | N | 6 | N | N | 1.1101 | 39.4971 | 1004.0787
| 242:81533 | 17 | 66.49 | 60.6 | 3.9112 | 60.6 | 18822 | 2303 | 839750 | 2012-06-23 17:46 | 2012-06-23 19:00 | 74 | 11kV | 76622 | 1147 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3154 St Ives, Panel 13 Fdr CB tripped on B phase OC and IOC, earth fault, efi, #1 group earth, zone earth, 11kV trip. Field efi's down at S.4609 and S.7266. UG cable fault in section of 11kV between S.7266 and S.8458 | June | 2012 | 2012Q4 | 2012 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | UG | Not Veg | 2012-06-23 | N | 66.8021 | N | 6 | N | N | 1.1101 | 39.4971 | 55993.0976
| 242:81535 | 1580 | 1416.574 | 44.27 | 0.89657 | 44.27 | 20124 | 16134 | 839746 | 2012-06-23 17:41 | 2012-06-23 22:05 | 264.2167 | 11kV | 2377.95 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121175 B & C Phase DOLF : 31 Amp HV reported down section isolated to repair 11 kv mains | June | 2012 | 2012Q4 | 2012 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-06-23 | N | 264.2167 | N | 6 | N | N | 1.1101 | 39.4971 | 1737.7357
| 242:81538 | 1036 | 691.5006 | 24.94 | 0.66747 | 24.94 | 19938 | 14154 | 839874 | 2012-06-24 12:44 | 2012-06-24 14:00 | 76 | 11kV | 13528 | 178 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | AT ZN 10999 ROCKDALE, SECTION OF 11KV FEEDER, EX PANEL 22L 'AB 30017', FROM Sw/B @ SUB 10007 ILIFFE REGENT TO N/O AB 30042 HAS BEEN DE-ENERGISED TO ALLOW FOR EMERGENCY REPAIR. INSULATOR FAILED WIRE ON CROSSARM HAD BEGAN TO BURN THROUGH CROSSARM. | June | 2012 | 2012Q4 | 2012 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Not Veg | 2012-06-24 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 9885.8634
| 242:81539 | 2207 | 1637.5253 | 28.95 | 0.74197 | 28.95 | 20264 | 18013 | 839873 | 2012-06-24 12:36 | 2012-06-24 15:55 | 199 | 11kV | 597 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 121184 A phase DOLF : 10 AMp Arrestor changed under A/P Excluded OMS # 839873 | June | 2012 | 2012Q4 | 2012 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2012-06-24 | N | 199 | N | 3 | N | N | 1.1101 | 39.4971 | 436.27
| 242:81541 | 1726 | 1191.0477 | 33.11 | 0.69006 | 33.11 | 19868 | 13450 | 839903 | 2012-06-24 15:19 | 2012-06-25 11:30 | 1211 | 11kV | 28463 | 152 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121186 3 fault operations 3 phase Earth fault Conductor broken at pole 9G-90032. No customers off affected area. Left isolated for repair in daylight Excluded OMS # 839903 | June | 2012 | 2012Q4 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-06-24 | N | 187.2566 | N | 3 | N | N | 1.1101 | 39.4971 | 20799.9209
| ZN35500:PA14 | 76 | 1090.6196 | 46.41 | 14.3503 | 46.41 | 19358 | 7738 | 840568 | 2012-06-25 20:06 | 2012-06-25 21:50 | 104 | 11kV | 208 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121192 Single phase DOLF : 10 Amp | June | 2012 | 2012Q4 | 2012 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-06-25 | N | 104 | N | 1 | N | N | 1.1101 | 39.4971 | 152.0003
| ZN35500:PA15 | 161 | 342.0761 | #N/A | 2.1247 | 39.4971 | 19244 | 6479 | 840619 | 2012-06-26 07:17 | 2012-06-26 08:07 | 50 | 11kV | 6400 | 128 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 41020 tripped and locked out on B phase Overcurrent tree branch on 11kV mains near PT864 | June | 2012 | 2012Q4 | 2012 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2012-06-26 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 4676.9312
| ZN35500:PA16 | 1471 | 877.0129 | 33.41 | 0.5962 | 33.41 | 19265 | 6675 | 840671 | 2012-06-26 09:15 | 2012-06-26 11:10 | 115 | 11kV | 15065 | 131 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 121199 Isolated to repair links 1268 that failed during planned switching on job SINO-22788 (OMS 841375) | June | 2012 | 2012Q4 | 2012 | 232:11459 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2012-06-26 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 11009.0577
| ZN35500:PA18 | 1470 | 1059.2642 | 38.59 | 0.72059 | 38.59 | 19171 | 5229 | 840993 | 2012-06-26 14:39 | 2012-06-26 16:10 | 91 | 11kV | 180611 | 2467 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12660 Woy Woy Pnl.14 tripped on A phase iOC and A Phase time O/C Small tree branch on mains near AB41632 See 841283 841292 841293 GIS: 841285 841299 | June | 2012 | 2012Q4 | 2012 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2012-06-26 | N | 73.2108 | N | 5 | N | N | 1.1101 | 39.4971 | 131985.1917
| ZN35500:PA19 | 358 | 1001.7957 | #N/A | 2.7983 | 39.4971 | 18896 | 3090 | 841018 | 2012-06-26 15:13 | 2012-06-26 16:35 | 81.65 | 11kV | 6205.4 | 76 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | PT12656 - roadside HDO blown 31.5Amp Cockatoo came into contact with HDO. PT interrupted to replace HDO. CC1: 22-"Refer to SOp" | June | 2012 | 2012Q4 | 2012 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2012-06-26 | N | 81.65 | N | 5 | N | N | 1.1101 | 39.4971 | 4534.7233
| ZN35500:PA20 | 91 | 704.7093 | #N/A | 7.7441 | 39.4971 | 19077 | 4491 | 841046 | 2012-06-26 16:00 | 2012-06-26 17:22 | 82 | 11kV | 136250 | 1735 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.1 tripped on C Phase O/C and C phase times O/C Abnormal Switching: LB45097 Closed - AB43760 Open Underground cable fault from Avoca zone Pnl.1 to S12664 | June | 2012 | 2012Q4 | 2012 | ZN12570:PA1 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | UG | Not Veg | 2012-06-26 | N | 78.5303 | N | 5 | N | N | 1.1101 | 39.4971 | 99567.4813
| ZN35500:PA22 | 1090 | 712.8018 | 30.41 | 0.65395 | 30.41 | 19128 | 4841 | 841198 | 2012-06-27 07:36 | 2012-06-27 09:04 | 88 | 11kV | 98174 | 1178 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills Panel 42 tripped on Earth Fault with EFI. Cable fault failed in Excavated pitt Cnr Castle Hill RD and Franklin Rd. See OMS 841883 841887 841199 841198 841198 841199 | June | 2012 | 2012Q4 | 2012 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | UG | Not Veg | 2012-06-27 | N | 83.3396 | N | 6 | N | N | 1.1101 | 39.4971 | 71742.6636
| ZN35500:PA23 | 396 | 905.864 | 42.47 | 2.2875 | 42.47 | 19741 | 12350 | 841215 | 2012-06-27 08:26 | 2012-06-27 09:10 | 44 | 11kV | 85248 | 2017 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At S10994 Mortdale Zn P12 Mortdale Aux No2 fdr tripped on SEL Remarks: other details provided. AB30799 failed Related jobs# 841215, 841841, 841840 | June | 2012 | 2012Q4 | 2012 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2012-06-27 | N | 42.2647 | N | 6 | N | N | 1.1101 | 39.4971 | 62296.724
| ZN35500:PA24 | 1248 | 749.8848 | 34.18 | 0.60087 | 34.18 | 19689 | 11418 | 841272 | 2012-06-27 09:57 | 2012-06-27 10:15 | 18 | 11kV | 9324 | 518 | HV | Staff Operation | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Unselected | N | CP64824 Deepwater Holly ex Pa33 Castle Cove Intellirupter 64824 sef was left auto during switching of disconnect 289829 Abnromal Switching CP62055 Closed SwA open At S4760. CP62053 Closed SWAOpen At S35369. S5367 Supplied Via LV parallel. Abnormal Switching for Disconnect 289829 See OMS 845937 841272 841274 841281. | June | 2012 | 2012Q4 | 2012 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2012-06-27 | N | 18 | N | 6 | N | N | 1.1101 | 39.4971 | 6813.7042
| ZN35500:PA26 | 486 | 1070.4421 | 47.08 | 2.2026 | 47.08 | 19245 | 6481 | 841593 | 2012-06-27 15:19 | 2012-06-27 16:17 | 58 | 11kV | 4002 | 69 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | iR 44797 Boudi -Triped / Reclosed / Tripped & locked out on O/C Customer cut tree branch coming into contact with HV | June | 2012 | 2012Q4 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2012-06-27 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 2924.5436
| ZN35500:PA27 | 873 | 854.4151 | 34.21 | 0.97871 | 34.21 | 19672 | 11122 | 841603 | 2012-06-27 15:36 | 2012-06-27 18:50 | 194 | 11kV | 194 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | Unselected | N | LID 121212 A phase DOLF : 10 Amp sub isolated to lower tap position Excluded OMS 841603 | June | 2012 | 2012Q4 | 2012 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2012-06-27 | N | 194 | N | 6 | N | N | 1.1101 | 39.4971 | 141.7695
| ZN35500:PA28 | 1879 | 1332.777 | 31.12 | 0.7093 | 31.12 | 19290 | 7274 | 841700 | 2012-06-27 21:14 | 2012-06-27 23:08 | 114 | 11kV | 329817 | 3272 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S80 Chatswood Panel 32 Tripped on A and B phase O/C, EF, EFI Cause: Suspect Cable fault from S80 Panel 32 to S2486 to S5279 to S1649. See OMS 843779 841700 841712 843779 | June | 2012 | 2012Q4 | 2012 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | UG | Not Veg | 2012-06-27 | N | 100.7998 | N | 6 | N | N | 1.1101 | 39.4971 | 241020.5356
| ZN35500:PA30 | 129 | 916.4547 | #N/A | 7.1043 | 39.4971 | 20034 | 15376 | 841753 | 2012-06-28 07:50 | 2012-06-28 09:30 | 100 | 11kV | 31700 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID 121222 2 fault operations 3 phase Overcurrent; Earth fault Trip & L/O Tree near mains beyond 11kV links 15761. Please arrange full patrol beyond Martinsville recloser and tree trimming where required. | June | 2012 | 2012Q4 | 2012 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-06-28 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 23165.425
| ZN35500:PA31 | 1022 | 1299.2256 | 40.15 | 1.2713 | 40.15 | 19653 | 10886 | 841845 | 2012-06-28 10:16 | 2012-06-28 13:20 | 184 | 11kV | 128590 | 1872 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | @ZN35800 Bankstown - 11kv Panel No.14 "Sub 4168 & Sub 5773" feeder tripped. Relays: A phase IOC, Earth Fault & EFI Signals: 11kv trip, No.12 Group earth Field EFI's: Nil Remarks: End box fault. 11kv end box failure @ Sub 5773 Hixson Archer Related jobs: #841845, 842006, 841852 | June | 2012 | 2012Q4 | 2012 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2012-06-28 | N | 68.6912 | N | 5 | N | N | 1.1101 | 39.4971 | 93969.7792
| ZN35500:PA32 | 549 | 1341.7145 | 42.73 | 2.4439 | 42.73 | 20208 | 17090 | 841935 | 2012-06-28 12:13 | 2012-06-28 14:35 | 142 | 11kV | 2734 | 865 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121225 B & C phase HV HRC fuse : 31 Amp also see 842268 Excluded OMS 841935 | June | 2012 | 2012Q4 | 2012 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | UG | Not Veg | 2012-06-28 | N | 3.1607 | N | 5 | N | N | 1.1101 | 39.4971 | 1997.9266
| ZN35500:PA34 | 321 | 562.3369 | 50.88 | 1.7518 | 50.88 | 18663 | 776 | 842053 | 2012-06-28 12:30 | 2012-06-28 17:20 | 290 | 11kV | 580 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 121227 C phase DOLF : 16 Amp Excluded OMS 842053 | June | 2012 | 2012Q4 | 2012 | 512:48047 | 512:83733 | ZN00512/083733 | MAITLAND | UG | Not Veg | 2012-06-28 | N | 290 | N | 5 | N | N | 1.1101 | 39.4971 | 423.8469
| ZN35500:PA35 | 633 | 861.6215 | 44.97 | 1.3612 | 44.97 | 18844 | 2512 | 842141 | 2012-06-28 19:54 | 2012-06-29 04:00 | 486 | 11kV | 334510 | 2442 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At Zn.12570 Avoca Panel 16 Fdr CB tripped on SEF, and efi with 11kV trip signal - 11kV OH down near PT.13495 | June | 2012 | 2012Q4 | 2012 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2012-06-28 | N | 136.982 | N | 5 | N | N | 1.1101 | 39.4971 | 244450.0416
| ZN35500:PA36 | 1717 | 1152.8665 | 31.01 | 0.67144 | 31.01 | 18980 | 3818 | 842617 | 2012-06-30 08:59 | 2012-06-30 10:08 | 69 | 11kV | 47955 | 695 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S10996 Rockdale section of P10 'LB31264 etc' fdr from AB30119 Remarks: Open circuit. Roadside bond ab30119 Related jobs: #842607, 843048, 842617, 842629 | June | 2012 | 2012Q4 | 2012 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2012-06-30 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 35044.0996
| 270:83583 | 611 | 388.8673 | 31.97 | 0.63644 | 31.97 | 18709 | 1203 | 842687 | 2012-06-30 12:32 | 2012-06-30 14:15 | 103 | 11kV | 2678 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Pt1723 Duneba Nabiac 400A fuse blown on A B and C phase of distributor 1. Cause: Tree trimming in area O/S No5 Duneba Trees fell onto mains. Cleared by OH. See OMS 844177 842692 842688 842687 842690 842689 | June | 2012 | 2012Q4 | 2012 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2012-06-30 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 1957.0034
| 270:83584 | 316 | 715.5521 | 55.29 | 2.2644 | 55.29 | 19063 | 4419 | 842750 | 2012-06-30 17:24 | 2012-06-30 18:45 | 81 | 11kV | 3159 | 39 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121243 3 phase fault 3 fault operations Overcurrent CLOSED BACK ON, NO FAULT REPORTED PLEASE PATROL FEEDER FROM SW 74616. Excluded OMS REPORT NO 842750. | June | 2012 | 2012Q4 | 2012 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-06-30 | N | 81 | N | 3 | N | N | 1.1101 | 39.4971 | 2308.504
| 270:83586 | 600 | 824.0435 | 40.75 | 1.3734 | 40.75 | 19507 | 9112 | 842458 | 2012-06-29 14:50 | 2012-07-02 13:10 | 4220 | 11kV | 305756 | 1226 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Unselected | N | At S9245 Engadine Panel 8 (S9279 Numantia Copeland Fdr) tripped, reclosed and locked out on: Relays - A phase time overcurrent, Lockout, EFI, Signals - 11kv trip, #1 Group earth Field EFI's: Nil Remarks: lightning/ surge arrestor. Surge arrestor blown near AB35964 Related jobs: #842883, 842477, 842458, 843777, 843773, 843771 | June | 2012 | 2012Q4 | 2012 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2012-06-29 | N | 249.3931 | N | 1 | N | N | 1.1101 | 39.4971 | 223437.4665
| 270:83587 | 1241 | 1122.8283 | 33.61 | 0.90478 | 33.61 | 17605 | 10078 | 843133 | 2012-07-02 12:02 | 2012-07-02 14:00 | 118 | 11kV | 55598 | 602 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Rec 2479 Delhi River Tripped and Locked out on O/C Trip. Cause Not ascertained for HV interruptions. S5068 Found to be in LV parallel at the time of interruption See OMS 844304 844302 844303 | July | 2012 | 2013Q1 | 2013 | ZN1193:PA1 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2012-07-02 | N | 92.3555 | N | 6 | N | N | 1.1101 | 39.4971 | 40629.3785
| 270:83590 | 1304 | 866.6211 | 31.88 | 0.66459 | 31.88 | 17710 | 11648 | 843248 | 2012-07-02 14:01 | 2012-07-02 14:35 | 34 | 11kV | 51476 | 1514 | HV | 3rd Party Vehicle | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | LID 121250 3 Phase interruption; No protection operated. Truck ripped handle OFF ABS 17448 the impact opening the switch causing the outage. The ABS can not be used and requires replacement or total re-build as the DO advises the upper operating mechanisms and damaged as well as the handle and operating rod. Excluded OMS 843248 & 843270 | July | 2012 | 2013Q1 | 2013 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2012-07-02 | N | 34 | N | 6 | N | N | 1.1101 | 39.4971 | 37617.1425
| 270:83591 | 1303 | 895.6486 | 40.33 | 0.68737 | 40.33 | 16605 | 700 | 843066 | 2012-07-02 11:04 | 2012-07-02 15:00 | 236 | 11kV | 236 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121252 Single phase DOLF : 5 Amp Excluded OMS 843066 | July | 2012 | 2013Q1 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-07-02 | N | 236 | N | 6 | N | N | 1.1101 | 39.4971 | 172.4618
| 270:83593 | 712 | 517.0147 | 31.56 | 0.72614 | 31.56 | 17943 | 13498 | 843375 | 2012-07-02 16:49 | 2012-07-02 17:40 | 51.3833 | 11kV | 3905.1333 | 76 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | At PT.12656 the roadside and centre phase HDO fuse operated - bird found at base of pole | July | 2012 | 2013Q1 | 2013 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2012-07-02 | N | 51.3833 | N | 6 | N | N | 1.1101 | 39.4971 | 2853.7563
| 270:83594 | 754 | 1048.6669 | 47.12 | 1.3908 | 47.12 | 17294 | 7031 | 843195 | 2012-07-02 12:59 | 2012-07-02 22:00 | 541 | 11kV | 23345 | 188 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 121251 2 fault operations 3 phase Overcurrent Local residents suggested to the operators that a tree removal company was removing dead trees to sell as firewood. The residents speaking to the operator thought nobody had engaged the tree trimmer for work.. When the operator arrived he found a massive tree had fallen through the 11kV and brought down mains between pole HV-20279 then ten spans towards ABS 2360. Excluded OMS 843195, 843216 & 843250 | July | 2012 | 2013Q1 | 2013 | 225:33670 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2012-07-02 | N | 124.1755 | N | 6 | N | N | 1.1101 | 39.4971 | 17059.8374
| ZN1673:PA1 | 1649 | 2243.5078 | 34.15 | 1.3605 | 34.15 | 18099 | 15785 | 843451 | 2012-07-02 23:21 | 2012-07-03 01:15 | 114 | 11kV | 5016 | 44 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121253 B phase DOLF : 31 Amp Burnt up DOLF replaced OK. As left 237V - 92A, 147A & 121A. Excluded OMS No's 843451 & 843453. | July | 2012 | 2013Q1 | 2013 | 238:34141 | 508:82576 | ZN00508/082576 | PORT STEPHENS | UG | Not Veg | 2012-07-02 | N | 114 | N | 6 | N | N | 1.1101 | 39.4971 | 3665.5449
| ZN1673:PA11 | 622 | 608.4709 | 31.55 | 0.97825 | 31.55 | 16955 | 3275 | 843489 | 2012-07-03 07:53 | 2012-07-03 08:50 | 57 | 11kV | 456 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | Ex Panel 24 Chatswood. S6968 Katherine Victoria Trpped due to Low Gas on No2 RMI. Note Parallel Trip Coils. See OMS 844297 843489 | July | 2012 | 2013Q1 | 2013 | ZN80:PA24 | ZN80:PA24 | ZN00080/000024 | WILLOUGHBY | UG | Not Veg | 2012-07-03 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 333.2314
| ZN1673:PA13 | 936 | 1054.0513 | 31.62 | 1.1261 | 31.62 | 17477 | 8570 | 843637 | 2012-07-03 10:54 | 2012-07-03 12:10 | 76 | 11kV | 4180 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | OMS # 843637. DOLF was found to have fallen from the carrier and was found hanging, the fuse had not blown, cause for fuse falling out unknown. VOLTS A phase 255 Volts B phase 255 Volts C phase 255 volts AMPS A phase 420 AMPS B phase 160 AMPS C phase 220 AMPS refer to related job 843637 | July | 2012 | 2013Q1 | 2013 | 202:34253 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2012-07-03 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 3054.6207
| ZN1673:PA14 | 1032 | 1344.7895 | 40.22 | 1.3031 | 40.22 | 17564 | 9508 | 843673 | 2012-07-03 08:30 | 2012-07-03 17:20 | 530 | 11kV | 6050 | 25 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 121262 Isolation for continued repair work on mains damaged by anonymous tree trimming company. No OMS number. No protection operation. Job continuing repairs of mains damaged by tee trimmer wo damaged 10 spans of mains | July | 2012 | 2013Q1 | 2013 | 225:33670 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2012-07-03 | N | 242 | N | 3 | N | N | 1.1101 | 39.4971 | 4421.1616
| ZN1673:PA18 | 1189 | 1060.1333 | 30.28 | 0.89162 | 30.28 | 17111 | 4498 | 844073 | 2012-07-04 09:30 | 2012-07-04 11:35 | 125 | 11kV | 13500 | 108 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kV Panel 18 ex Panel S2400 Berowra. Section interrupted to allow emergency repairs to AB2295. See OMS 844520 844073 | July | 2012 | 2013Q1 | 2013 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2012-07-04 | N | 125 | N | 4 | N | N | 1.1101 | 39.4971 | 9865.4018
| ZN1673:PA19 | 524 | 877.9812 | 33.07 | 1.6755 | 33.07 | 17411 | 8052 | 844231 | 2012-07-04 14:20 | 2012-07-04 20:50 | 390 | 11kV | 53440 | 3064 | HV | 3rd Party Action | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S35500 Top Ryde Panel 28 interrupted for safet Section of 11kV from AB937 to AB1563 to S47157 tee PT46720 Isolated for safety. Car Hit pole CNR of Smalls and Zola St Ryde. HV and LV and Pole damaged. See OMS 844673 844677 844678 844676 844231 At S47157 Warren Fawcett 400A fuse blown on A B and C phase of distributor 4. see OMS 844668 844460 844440 | July | 2012 | 2013Q1 | 2013 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2012-07-04 | N | 17.4413 | N | 4 | N | N | 1.1101 | 39.4971 | 39052.3758
| ZN1673:PA2 | 810 | 1014.3528 | 31.12 | 1.2523 | 31.12 | 16942 | 3184 | 844468 | 2012-07-04 20:56 | 2012-07-04 23:20 | 144 | 11kV | 576 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121285 Fuse: 63 Amp Found DOLF down, probable fuse fatigue. Replaced OK. Refer related OMS no. 844468. | July | 2012 | 2013Q1 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-07-04 | N | 144 | N | 4 | N | N | 1.1101 | 39.4971 | 420.9238
| ZN1673:PA20 | 8 | 1515.8154 | #N/A | 189.4769 | 39.4971 | 17347 | 7454 | 844434 | 2012-07-04 18:14 | 2012-07-04 23:45 | 331 | 11kV | 993 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT.14143 the centre phase 16 amp HDO fuse found open possible fatigue | July | 2012 | 2013Q1 | 2013 | ZN14143:PA17 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Not Veg | 2012-07-04 | N | 331 | N | 4 | N | N | 1.1101 | 39.4971 | 725.6551
| ZN1673:PA21 | 1437 | 1404.3698 | 34.94 | 0.97729 | 34.94 | 17572 | 9601 | 845088 | 2012-07-06 10:33 | 2012-07-06 11:35 | 62 | 11kV | 186 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121307 C phase DOLF : 10 Amp Tx Volts: A,B & C ph = 250V excluded OMS 845088 | July | 2012 | 2013Q1 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-07-06 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 135.9233
| ZN1673:PA6 | 1168 | 1256.3501 | 31.47 | 1.0756 | 31.47 | 16821 | 2162 | 845144 | 2012-07-06 12:08 | 2012-07-06 14:30 | 142 | 11kV | 142 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121311 A phase DOLF : 10 Amp. Excluded OMS 845144 | July | 2012 | 2013Q1 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-07-06 | N | 142 | N | 3 | N | N | 1.1101 | 39.4971 | 103.7694
| ZN1673:PA7 | 1041 | 1251.8727 | 34.64 | 1.2026 | 34.64 | 17162 | 5207 | 845402 | 2012-07-06 22:49 | 2012-07-06 23:42 | 53 | 11kV | 46762 | 912 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn129 Hunters Hill Panel 5 tripped on Signals: 11kV Trip and Group Earth No1 Relays: EFI, FC, OC, EF element Cause: Suspect UG cable fault between S3395 Ryde Martin and S3996 Abigail Figtree. See OMS 846888 846889 845402 | July | 2012 | 2013Q1 | 2013 | ZN129:PA5 | ZN129:PA39 | ZN00129/000039 | HUNTERS HILL | UG | Not Veg | 2012-07-06 | N | 51.2741 | N | 3 | N | N | 1.1101 | 39.4971 | 34172.2904
| ZN1673:PA9 | 455 | 759.7565 | 36.62 | 1.6698 | 36.62 | 16609 | 726 | 845407 | 2012-07-07 00:36 | 2012-07-07 07:25 | 409 | 11kV | 206545 | 505 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of 11kV Feeder ex Panel 17L AB1884 Footpath Side Blade HR - Causing Open circuit and low volts on distributor centres See OMS 845407/411/412/413/417/418/419 | July | 2012 | 2013Q1 | 2013 | ZN2635:PA17 | ZN2635:PA38 | ZN02635/000038 | HORNSBY | OH | Not Veg | 2012-07-07 | N | 409 | N | 3 | N | N | 1.1101 | 39.4971 | 150936.994
| ZN12640:PA1 | 782 | 775.9879 | 34.74 | 0.99231 | 34.74 | 16850 | 2333 | 845427 | 2012-07-07 08:21 | 2012-07-07 11:00 | 159 | 11kV | 159 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121316 A phase DOLF : 5 Amp Excluded OMS 845427 | July | 2012 | 2013Q1 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-07-07 | N | 159 | N | 3 | N | N | 1.1101 | 39.4971 | 116.1925
| ZN12640:PA10 | 1587 | 1157.0818 | 30.21 | 0.7291 | 30.21 | 17457 | 8381 | 845596 | 2012-07-07 18:58 | 2012-07-07 21:30 | 152 | 11kV | 44333 | 484 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | @ZN262 Marrickville 11kv OCB panel 29 "S-284 Mitchell St" Feeder tripped on: Relays: B phase timed O/C. Fault Check. Signals: 11kv trip, group earth, Zone Earth. Field EFI's: S-284 Mitchell St Remarks: Simultaneous fault - End box fault @ S-6076 Far Thompson and Transformer fault @ S-284 Mitchell St. Related jobs: #845607, 845605, 845596, 846072, 846070, 846064 | July | 2012 | 2013Q1 | 2013 | ZN262:PA29 | ZN262:PA29 | ZN00262/000029 | INNER WEST | UG | Not Veg | 2012-07-07 | N | 91.5971 | N | 3 | N | N | 1.1101 | 39.4971 | 32397.2488
| ZN12640:PA12 | 1311 | 1107.7482 | 35.97 | 0.84496 | 35.97 | 16878 | 2538 | 845699 | 2012-07-08 14:36 | 2012-07-08 15:41 | 65 | 11kV | 79885 | 1229 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12640 Unima Panel 19 11kV LB40712 Roadside Bond burnt off See OMS 847213 845708 847214 845699 845214 | July | 2012 | 2013Q1 | 2013 | ZN12640:PA19 | ZN12640:PA14 | ZN12640/000014 | CENTRAL COAST | OH | Not Veg | 2012-07-08 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 58377.6018
| ZN12640:PA13 | 2059 | 1379.6699 | 30.57 | 0.67007 | 30.57 | 17920 | 13315 | 845722 | 2012-07-08 16:36 | 2012-07-08 18:07 | 91 | 11kV | 113997 | 1426 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3472 Sefton Panel 33 (S.2771 Wrights York Fdr) tripped. Relays: Trip, Alarm, O/C, EFI, E/F, EFI relay. Signals: - 11kv trip, Zone earth, Batt defect. Field EFI's: S2771, S4295, S3921, S1920, S2705 Remarks: UG Fault. Fault in 11kv UG feeder between SwA at S.2705 Vaughn St and Sw B at S2664 Chiswick Cumb Related jobs: #845730, 845727, 845722, 846164, 846163, 846168, 846162 | July | 2012 | 2013Q1 | 2013 | ZN3472:PA33 | ZN3472:PA33 | ZN03472/000033 | CUMBERLAND | UG | Not Veg | 2012-07-08 | N | 79.9418 | N | 2 | N | N | 1.1101 | 39.4971 | 83305.6453
| ZN12640:PA14 | 1835 | 1129.0966 | 36.1 | 0.61531 | 36.1 | 18499 | 19887 | 846036 | 2012-07-09 12:22 | 2012-07-09 14:55 | 153 | 11kV | 3366 | 22 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | PT9188 Cowan Scylla Dist No.2 "Cowan St North" Phase: C Fuse: 400A Remarks: UG cable damaged by contractor. Related jobs: #846372, 846092, 846036 | July | 2012 | 2013Q1 | 2013 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | UG | Not Veg | 2012-07-09 | N | 153 | N | 1 | N | N | 1.1101 | 39.4971 | 2459.7735
| ZN12640:PA2 | 1391 | 854.7331 | 29.77 | 0.61447 | 29.77 | 17747 | 11927 | 846463 | 2012-07-10 10:21 | 2012-07-10 14:02 | 221 | 11kV | 40388.8667 | 183 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT10201 Alston Laycock Foothpath HDO 50 amp found blown. Section of Panel No.2 "USL 30438" feeder ex Sub 10993 Hurstville North. Fuse Failure Subs to M&R Pt 10201 | July | 2012 | 2013Q1 | 2013 | ZN10993:PA2 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Not Veg | 2012-07-10 | N | 220.7042 | N | 3 | N | N | 1.1101 | 39.4971 | 29514.9925
| ZN12640:PA4 | 1363 | 1084.8027 | 33.31 | 0.79589 | 33.31 | 18523 | 20073 | 846672 | 2012-07-10 13:54 | 2012-07-10 18:56 | 301.7167 | 11kV | 1849.7167 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121339 B phase DOLF : 16 Amp Excluded OMS 846672 & 846689 | July | 2012 | 2013Q1 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-07-10 | N | 184.9717 | N | 3 | N | N | 1.1101 | 39.4971 | 1351.7184
| ZN12640:PA5 | 1545 | 977.0442 | 30.89 | 0.63239 | 30.89 | 17946 | 13581 | 846865 | 2012-07-10 23:26 | 2012-07-11 00:25 | 59 | 11kV | 101725 | 1823 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S874 Concord: 11kv feeder panel No.22 "Norman Majors" feeder tripped. Relays: B phase E/F, EFI Signals: Zone earth, No1 grp earth, 11kv trip. Field EFIs: Nil Remarks: UG fault.Front line feeder failure from S874 Concord: 11 kv feeder panel No22 to S4153 Norman Majors (SWA), LV// in at time of a failure, bringing down LV mains in Bent St Nr Wellbank. Outage report upon request available. Related jobs: #846872, 847449, 846868, 846865, 847432, 847430 | July | 2012 | 2013Q1 | 2013 | ZN874:PA22 | ZN874:PA22 | ZN00874/000022 | CANADA BAY | UG | Not Veg | 2012-07-10 | N | 55.8009 | N | 3 | N | N | 1.1101 | 39.4971 | 74337.6296
| ZN12640:PA7 | 1739 | 1034.1699 | 37.65 | 0.59469 | 37.65 | 17581 | 9672 | 846868 | 2012-07-11 00:52 | 2012-07-11 09:35 | 523 | 11kV | 38179 | 73 | HV | Overload LV Parallel | Utility Process Issue | Feeder/Distributor U/G | Unplanned | Unselected | N | S5975 Correys Majors Dist No2 "Majors Bay Rd E UG & Ellis St OH" Phase: AB Fuse: 400A Remarks: LV parallel (during feeder trip). LV dist fault caused by trip on pnl22 Concord. Created 3 phase short circuit on dist 2 ex S5975 LV UG cable(See DMA). Faulty cable isolated, no customers affected. OH LV network restored via LV// 14674 and 20712 0915 11/07/2012 Related jobs: #846872, 847449, 846868, 846865, 847432, 847430 | July | 2012 | 2013Q1 | 2013 | ZN874:PA17 | ZN874:PA17 | ZN00874/000017 | CANADA BAY | UG | Not Veg | 2012-07-11 | N | 523 | N | 7 | N | N | 1.1101 | 39.4971 | 27900.0871
| ZN12640:PA8 | 1002 | 916.1437 | 39.82 | 0.91432 | 39.82 | 18096 | 15755 | 846873 | 2012-07-11 03:40 | 2012-07-11 09:55 | 375 | 11kV | 3375 | 9 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 121247 B Phase DOLF : 16 Amp. Excluded OMS REPORT NO 846873. M.BROWN TO PATROL. FOUND FAULTY STAY WIRE AT SUB 71524. | July | 2012 | 2013Q1 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-07-11 | N | 375 | N | 7 | N | N | 1.1101 | 39.4971 | 2466.3505
| ZN14144:PA1 | 1218 | 1012.555 | 33.79 | 0.83133 | 33.79 | 17164 | 5223 | 846929 | 2012-07-11 08:47 | 2012-07-11 11:18 | 150.6167 | 11kV | 10934.3667 | 77 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 121346 A phase DOLF : 20 Amp. Replace faulty transformer | July | 2012 | 2013Q1 | 2013 | 213:33774 | 213:33774 | ZN00213/033774 | NEWCASTLE | UG | Not Veg | 2012-07-11 | N | 142.0048 | N | 7 | N | N | 1.1101 | 39.4971 | 7990.5127
| ZN14144:PA10 | 695 | 1091.9974 | 34.48 | 1.5712 | 34.48 | 17277 | 6846 | 846880 | 2012-07-11 06:31 | 2012-07-11 11:54 | 323 | 11kV | 70788 | 822 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 121349 2 fault operations A & B phase Overcurrent; Instantaneous Earth fault Excluded OMS REPORT NO 846895 & 846880 FAULTY ARRESTORS ON OGOH AT SUB 70004 BIRRELL ST. | July | 2012 | 2013Q1 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2012-07-11 | N | 86.1168 | N | 7 | N | N | 1.1101 | 39.4971 | 51729.7825
| ZN14144:PA2 | 1036 | 1009.4684 | 30.62 | 0.97439 | 30.62 | 16669 | 1052 | 847099 | 2012-07-11 11:49 | 2012-07-11 13:00 | 71 | 11kV | 71 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121351 A phase DOLF : 16 Amp. Fatigued fuse. Readings as left 12A, 13A, 11A 240V Excluded OMS 847099 | July | 2012 | 2013Q1 | 2013 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2012-07-11 | N | 71 | N | 7 | N | N | 1.1101 | 39.4971 | 51.8847
| ZN14144:PA4 | 855 | 606.3586 | 31.38 | 0.70919 | 31.38 | 17956 | 13712 | 846965 | 2012-07-11 09:18 | 2012-07-11 15:05 | 347 | 11kV | 41640 | 120 | HV | Overload LV Parallel | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | At S5305 Phillip Princes 400A fuse blown on A phase of distributor 2. Cause: S5305 PhillipPrincess Distributor 1 has been defective since 05/11/11. Distributor 1 and 2 in parallel See OMS 849070 846965 | July | 2012 | 2013Q1 | 2013 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | UG | Not Veg | 2012-07-11 | N | 347 | N | 7 | N | N | 1.1101 | 39.4971 | 30429.2838
| ZN14144:PA5 | 306 | 337.8455 | 31.98 | 1.1041 | 31.98 | 18497 | 19864 | 847355 | 2012-07-11 22:33 | 2012-07-11 23:45 | 72 | 11kV | 63552 | 937 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn.35500 Top Ryde, the 11kV Panel 34 Fdr CB tripped on earth fault, efi, 11kV trip, #3 group eartrh. Field efi operated at S.35596. 11kV UG cable fault between S.35596, S.2115 and tee S.5264 | July | 2012 | 2013Q1 | 2013 | ZN35500:PA34 | ZN35500:PA36 | ZN35500/000036 | RYDE | UG | Not Veg | 2012-07-11 | N | 67.825 | N | 7 | N | N | 1.1101 | 39.4971 | 46441.9271
| ZN14144:PA7 | 1048 | 826.8311 | 33.3 | 0.78896 | 33.3 | 17279 | 6882 | 847381 | 2012-07-12 07:49 | 2012-07-12 08:43 | 54 | 11kV | 102708 | 1902 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121360 A phase A PHASE TAPPING ON ABS 40391 (FEEDER SIDE) BURNT OFF.FEEDER ABNORMAL ABS 40008 CLOSED.ABS40140 OPEN. Excluded OMS 847379, 847381, 847396, 847400 | July | 2012 | 2013Q1 | 2013 | 503:48078 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Not Veg | 2012-07-12 | N | 54 | N | 1 | N | N | 1.1101 | 39.4971 | 75055.977
| ZN14144:PA8 | 478 | 396.4873 | 32.8 | 0.82947 | 32.8 | 16505 | 29 | 847818 | 2012-07-13 00:57 | 2012-07-13 01:11 | 14 | 11kV | 6888 | 492 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | The roadside bond burnt off at USL.42262 | July | 2012 | 2013Q1 | 2013 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2012-07-13 | N | 14 | N | 1 | N | N | 1.1101 | 39.4971 | 5033.5472
| ZN36800:PA31 | 3354 | 2191.6115 | 34.76 | 0.65343 | 34.76 | 17306 | 7134 | 848276 | 2012-07-14 09:33 | 2012-07-14 10:52 | 79 | 11kV | 103282.2333 | 1308 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | At ZN35800 Bankstown, 11kv Pnl 1 "Gow Gibson" fdr tripped on B phase IOC Remarks: Other - details provided. Balloon caused flashover vicinity PT1739 High Northam Related jobs: #848665, 848276 | July | 2012 | 2013Q1 | 2013 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-07-14 | N | 78.962 | N | 1 | N | N | 1.1101 | 39.4971 | 75475.6098
| ZN36800:PA32 | 359 | 177.14 | #N/A | 0.49343 | 39.4971 | 17147 | 4976 | 848412 | 2012-07-15 00:51 | 2012-07-15 03:50 | 179 | 11kV | 127354 | 1544 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Sub2196 Milperra Panel 5 "Marigold Armour No.4" feeder tripped, reclosed, tripped and locked out on: Relays: C phase OC, Lock out relay and EFI Signals: 11kv trip Field EFI's: Nil Remarks: Tree/branch on OH mains. Large tree branch on OH mains outside No.3 Lemnos St Milperra Related jobs: #848588, 848589, 848412, 848413, 848414 | July | 2012 | 2013Q1 | 2013 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-07-15 | N | 82.4832 | N | 2 | N | N | 1.1101 | 39.4971 | 93066.5469
| ZN36800:PA33 | 1774 | 1320.8234 | 40.02 | 0.74455 | 40.02 | 17890 | 13053 | 848517 | 2012-07-15 17:47 | 2012-07-15 19:14 | 86.4833 | 11kV | 518.9 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121372 A & C phase DOLF : 20 Amp | July | 2012 | 2013Q1 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2012-07-15 | N | 86.4833 | N | 2 | N | N | 1.1101 | 39.4971 | 379.1968
| ZN36800:PA35 | 148 | 233.4623 | #N/A | 1.5774 | 39.4971 | 16751 | 1623 | 848568 | 2012-07-16 06:18 | 2012-07-16 08:15 | 117 | 11kV | 160590 | 1555 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN4545 Meadowbank Panel 25 Tripped on Relays: Earth Fault With EFI. Signals: Zone Earth, Group Earth and 11kV trip. Cause: Front Line feeder fault. See OMS 849288 849289 848568 | July | 2012 | 2013Q1 | 2013 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | UG | Not Veg | 2012-07-16 | N | 103.2733 | N | 5 | N | N | 1.1101 | 39.4971 | 117354.4354
| ZN36800:PA36 | 871 | 507.9456 | 33.72 | 0.58318 | 33.72 | 17200 | 5896 | 848755 | 2012-07-16 11:48 | 2012-07-16 17:10 | 322 | 11kV | 104006 | 323 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kv feeder panel No12 'Victoria Mitchell' Ex S9252 Jannali 11kv centre phase bond burnt off at AB35216 Bond 11kv centre phase bond burnt off at AB35216 (Jannali Sht 2 D/7) | July | 2012 | 2013Q1 | 2013 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2012-07-16 | N | 322 | N | 5 | N | N | 1.1101 | 39.4971 | 76004.5171
| ZN36800:PA39 | 2256 | 1335.9011 | #N/A | 0.59215 | 39.4971 | 18285 | 17335 | 848939 | 2012-07-16 16:20 | 2012-07-16 17:40 | 79.6 | 11kV | 15044.4 | 189 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 121383 3 phase isolation Insulator pin pulled through X-arm, Mains held up by tapping. | July | 2012 | 2013Q1 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-07-16 | N | 79.6 | N | 5 | N | N | 1.1101 | 39.4971 | 10994.0038
| ZN36800:PA40 | 3017 | 2043.1882 | 34.41 | 0.67723 | 34.41 | 16968 | 3348 | 849030 | 2012-07-16 20:23 | 2012-07-16 21:19 | 56 | 11kV | 62720 | 1120 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.3154 St Ives, Panel 5 Fdr CB tripped on C phASE ioc AND TIMED oc, EFI, 11Kv TRIP, ZONE EARTH, #1 tX gROUP EARTH. - CAUSE UNKNOWN | July | 2012 | 2013Q1 | 2013 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2012-07-16 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 45833.9261
| ZN36800:PA42 | 649 | 366.2195 | 33.84 | 0.56428 | 33.84 | 17491 | 8715 | 849044 | 2012-07-16 22:01 | 2012-07-17 02:30 | 269 | 11kV | 4828 | 190 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121384 1 fault operation DOLF : 31 Amp Recloser flag : Earth fault Sect 42007 Locked out LF 40945 blown B phase 2 phases on the ground between poles CN-90135 & CN-90136. Near SUB 53472 Excluded OMS 849044 | July | 2012 | 2013Q1 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-07-16 | N | 25.4105 | N | 5 | N | N | 1.1101 | 39.4971 | 3528.16
| ZN36800:PA43 | 2172 | 1521.7854 | 38.27 | 0.70064 | 38.27 | 17540 | 9060 | 849311 | 2012-07-17 12:36 | 2012-07-17 19:10 | 394 | 11kV | 8670 | 105 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 121399 1 fault operation single phase Sensitive earth fault Mains down Adj. pole GR-82007,Tree cut down over mains. Excluded OMS# 849311 & 849326. | July | 2012 | 2013Q1 | 2013 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2012-07-17 | N | 82.5714 | N | 3 | N | N | 1.1101 | 39.4971 | 6335.7803
| ZN36800:PA46 | 1101 | 789.559 | 40.45 | 0.71713 | 40.45 | 17515 | 8932 | 849487 | 2012-07-17 20:00 | 2012-07-17 20:30 | 30 | 11kV | 4320 | 144 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Section of 11kv feeder panel No.8 "Jannali" feeder Ex S.9252 Jannali From S.9540 Toronto Buller No2 (SW B) tee PT 9435 Buller St to AB 35131 Dop Interrupted supply @ 2000 to PT 9435 to allow for Emergency repairs failed insulator above PT Insulator Failed Dop Interrupted supply @ 2000 to PT 9435 to allow for Emergency repairs failed insulator above PT. | July | 2012 | 2013Q1 | 2013 | ZN9252:PA8 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2012-07-17 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 3156.9286
| ZN36800:PA47 | 173 | 253.4486 | 40.92 | 1.465 | 40.92 | 17333 | 7343 | 849511 | 2012-07-17 22:31 | 2012-07-18 01:15 | 164 | 11kV | 275890 | 2284 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Sub 2310 Punchbowl Zn Panel #34 labelled "Slyvester King George etc" tripped on C phase O/C. EFI 11kv trip #5 TX GE Field EFI's. S3106, S36008, S48550, S2198, S3616, S3105, CP2134 Remarks: UG Fault, suspected UG Fault in tee off from CP2154 to S35162. (Also Suspect S3543 Dist 1 in LV// with S48550 Dist 1) Related jobs: #849519, 849516, 849515, 849511, 849600, 849601, 849596 | July | 2012 | 2013Q1 | 2013 | ZN2310:PA34 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-07-17 | N | 120.7925 | N | 3 | N | N | 1.1101 | 39.4971 | 201612.2746
| ZN36800:PA49 | 999 | 871.5959 | 41.84 | 0.87247 | 41.84 | 17404 | 8009 | 849523 | 2012-07-18 05:45 | 2012-07-18 07:15 | 90 | 11kV | 37170 | 413 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | The RHS phase open circuited at the 11kV UG/OH ex S.16951 | July | 2012 | 2013Q1 | 2013 | ZN15011:PA8 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | Unknown | Unknown | 2012-07-18 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 27162.7397
| ZN36800:PA50 | 1397 | 1041.7333 | 35.03 | 0.74569 | 35.03 | 18106 | 15837 | 849560 | 2012-07-18 08:00 | 2012-07-18 09:00 | 60 | 11kV | 6120 | 102 | HV | Staff Other | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | LID 121410 no protection operation see SI 20670 customers at sub 42752 not notified of interruption | July | 2012 | 2013Q1 | 2013 | 218:7476 | 261:81865 | ZN00261/081865 | LAKE MACQUARIE | UG | Not Veg | 2012-07-18 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 4472.3155
| ZN36800:PA53 | 970 | 590.7369 | 36 | 0.60901 | 36 | 16641 | 898 | 849522 | 2012-07-18 01:13 | 2012-07-18 10:45 | 572 | 11kV | 37746 | 126 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121401 2 fault operations Earth fault 2 wires down off pole GQ-32603. Auto Links 49146 did not see fault Excluded OMS 849522 | July | 2012 | 2013Q1 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-07-18 | N | 299.5714 | N | 5 | N | N | 1.1101 | 39.4971 | 27583.6635
| ZN36800:PA54 | 1491 | 1053.7422 | 31.76 | 0.70674 | 31.76 | 18335 | 17758 | 849666 | 2012-07-18 12:20 | 2012-07-18 12:35 | 15 | 11kV | 15 | 1 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 121414 Isolated section to cut away damaged L/As pole NB-10087 Thurlow Ave. See report 121402; OMS 849549, 850035, 850044 Please replace L/As pole NB-10087 Excluded OMS 849666 | July | 2012 | 2013Q1 | 2013 | 232:33409 | 242:81535 | ZN00242/081535 | PORT STEPHENS | OH | Not Veg | 2012-07-18 | N | 15 | N | 5 | N | N | 1.1101 | 39.4971 | 10.9616
| ZN36800:PA56 | 1169 | 834.6486 | 35.2 | 0.71399 | 35.2 | 17507 | 8864 | 849975 | 2012-07-18 19:03 | 2012-07-18 20:29 | 86 | 11kV | 18576 | 216 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121417 2 fault operations A & B phase Overcurrent Sw 34637 Prot A & B ph O/C. Excluded OMS# 849975 & 849990. | July | 2012 | 2013Q1 | 2013 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2012-07-18 | N | 86 | N | 5 | N | N | 1.1101 | 39.4971 | 13574.7929
| ZN36800:PA57 | 5 | 73.5186 | #N/A | 14.7037 | 39.4971 | 17971 | 13924 | 849969 | 2012-07-19 07:25 | 2012-07-19 08:13 | 48 | 11kV | 4464 | 93 | HV | 3rd Party Vehicle | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | Handle of AB.40910 was damaged and opened after being hit by truck. | July | 2012 | 2013Q1 | 2013 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2012-07-19 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 3262.1595
| ZN36800:PA58 | 2213 | 1473.8094 | 35.79 | 0.66598 | 35.79 | 17558 | 9352 | 850130 | 2012-07-19 10:14 | 2012-07-19 11:55 | 101 | 11kV | 101 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121429 C phase DOLF : 16 Amp Fuse Fatigue Excluded OMS 850130 | July | 2012 | 2013Q1 | 2013 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2012-07-19 | N | 101 | N | 5 | N | N | 1.1101 | 39.4971 | 73.8078
| ZN12650:PA1 | 1741 | 1394.1856 | 31.28 | 0.8008 | 31.28 | 16549 | 312 | 850320 | 2012-07-19 15:40 | 2012-07-19 17:39 | 118.6667 | 11kV | 198.55 | 2 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 121432 B Phase DOLF : 10 Amp. Dead Bird found at sub. Tx Volts = 244V Load: Aph - 10A, Bph - 4A, Cph - 0A | July | 2012 | 2013Q1 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2012-07-19 | N | 99.275 | N | 5 | N | N | 1.1101 | 39.4971 | 145.0945
| ZN12650:PA10 | 748 | 767.8113 | 43.87 | 1.0265 | 43.87 | 16910 | 2995 | 850282 | 2012-07-19 14:33 | 2012-07-19 18:30 | 237 | 11kV | 3318 | 14 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121433 B phase DOLF : 40 Amp 11kV Section isolated to replace burnt up DOLF & Carrier 72027 Wallarah Rd sub. See LID report # 121434. OMS 851453 | July | 2012 | 2013Q1 | 2013 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2012-07-19 | N | 237 | N | 5 | N | N | 1.1101 | 39.4971 | 2424.6965
| ZN12650:PA12 | 2090 | 1628.4789 | 34.96 | 0.77918 | 34.96 | 17309 | 7169 | 850431 | 2012-07-19 20:20 | 2012-07-19 21:45 | 85 | 11kV | 9597.6 | 113 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 121435 A phase DOLF : 20 Amp. Load readings: 246V; 110/120/110A. | July | 2012 | 2013Q1 | 2013 | 232:11459 | 242:81539 | ZN00242/081539 | PORT STEPHENS | UG | Not Veg | 2012-07-19 | N | 84.9345 | N | 5 | N | N | 1.1101 | 39.4971 | 7013.643
| ZN12650:PA13 | 1888 | 1469.1715 | 38.58 | 0.77816 | 38.58 | 16872 | 2500 | 850521 | 2012-07-20 10:07 | 2012-07-20 12:32 | 145 | 11kV | 5495 | 47 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | At S.16408 Manly Wharf RMCB tripped on low gas | July | 2012 | 2013Q1 | 2013 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | Unknown | Not Veg | 2012-07-20 | N | 116.9149 | N | 2 | N | N | 1.1101 | 39.4971 | 4015.5839
| ZN12650:PA14 | 812 | 1382.1435 | 45.79 | 1.7021 | 45.79 | 18005 | 14234 | 850808 | 2012-07-20 23:57 | 2012-07-21 05:00 | 303 | 11kV | 606 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121445 A phase Burnt-off 11kV lead at Baxter sub 51814. excluded OMS Job No. 850808. | July | 2012 | 2013Q1 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-07-20 | N | 303 | N | 2 | N | N | 1.1101 | 39.4971 | 442.8469
| ZN12650:PA16 | 157 | 789.2668 | 40.11 | 5.0272 | 40.11 | 17169 | 5275 | 850904 | 2012-07-21 11:08 | 2012-07-21 13:23 | 135 | 11kV | 277047 | 2147 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S12570 Avoca Panel 6 tripped on C phase IOC and Timed. Cause Not ascertained for outage See OMS 852469 /476/747/853100 850910/904 | July | 2012 | 2013Q1 | 2013 | ZN12570:PA6 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Veg | 2012-07-21 | N | 129.0391 | N | 3 | N | N | 1.1101 | 39.4971 | 202457.7761
| ZN12650:PA17 | 2346 | 2353.6498 | 39.88 | 1.0033 | 39.88 | 17227 | 6246 | 850993 | 2012-07-21 18:24 | 2012-07-21 19:18 | 54 | 11kV | 74068 | 1592 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121450 229:34983 Dipped fdr for safety to by pass Medowie reg No1. LID 121449 1 fault operation Sensitive Earth Fault Sw 19722 tripped on SEF, B phase incoming Link 18313 load side burnt off at Medowie Reg No 1. Reg isolated and bypassed. also see report 121450 | July | 2012 | 2013Q1 | 2013 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2012-07-21 | N | 46.5251 | N | 3 | N | N | 1.1101 | 39.4971 | 54126.7098
| ZN12650:PA19 | 287 | 411.9031 | 49.31 | 1.4352 | 49.31 | 17574 | 9617 | 851032 | 2012-07-22 03:39 | 2012-07-22 05:08 | 89 | 11kV | 90508 | 1076 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn269 Waverley 11kV Pa18 Fdr tripped on: Re;ays-Earth Leakage timmed, EFI Field EFI's-S3265S3697S1738S6177 Signals-11kv trip, Zone Earth, Tx1 Group Earth, Tx2 Group Earth Cause: UG Fault Suspect cable on 11kv fdr from S6177 to S1858 tee to S4590 tee to S7783 See 851496,9 exclude 851032 | July | 2012 | 2013Q1 | 2013 | ZN269:PA18 | ZN36800:PA46 | ZN36800/000046 | WAVERLEY | UG | Not Veg | 2012-07-22 | N | 84.1152 | N | 8 | N | N | 1.1101 | 39.4971 | 66140.5769
| ZN12650:PA2 | 414 | 776.1804 | 64.05 | 1.8748 | 64.05 | 18319 | 17675 | 851031 | 2012-07-22 02:35 | 2012-07-22 05:15 | 160 | 11kV | 68945 | 616 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn8000 Macquarie Park Panel 38 11kV VCB tripped on Relays: OC with EFI. Cause: Suspect 11kV cable fault from SWB at S7225 Duracell Talavera to SWB at S5887 Talavera Texas tee tee S3763 Talavera Lane Cove. See OMS 851031/623/624 852027 851031 | July | 2012 | 2013Q1 | 2013 | ZN8000:PA38 | ZN8000:PA38 | ZN08000/000038 | RYDE | UG | Not Veg | 2012-07-22 | N | 111.9237 | N | 8 | N | N | 1.1101 | 39.4971 | 50382.9725
| ZN12650:PA20 | 1614 | 1169.7936 | 36.4 | 0.72478 | 36.4 | 16567 | 424 | 857038 | 2012-07-22 05:35 | 2012-07-22 09:10 | 215 | 11kV | 267524 | 1707 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @Zn9252 Janalli 11kv OCB Panel 2 "S-9690 Toronto Buller" etc Feeder tripped out: Relays: SEL Lockout Field EFIs: NIL Signals: 11kv trip Remarks: Bond. HR Connection at AB35571 Related jobs: #857038, 857039, 857040 | July | 2012 | 2013Q1 | 2013 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2012-07-22 | N | 156.7217 | N | 8 | N | N | 1.1101 | 39.4971 | 195498.6486
| ZN12650:PA21 | 65 | 274.5483 | 52.17 | 4.2238 | 52.17 | 17999 | 14187 | 851092 | 2012-07-22 11:15 | 2012-07-22 12:10 | 55 | 11kV | 220 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121455 A phase DOLF : 31 Amp excluded OMS 851092 | July | 2012 | 2013Q1 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2012-07-22 | N | 55 | N | 8 | N | N | 1.1101 | 39.4971 | 160.7695
| ZN12650:PA3 | 1155 | 1653.4694 | 39.7 | 1.4316 | 39.7 | 17942 | 13489 | 851021 | 2012-07-21 21:33 | 2012-07-22 13:50 | 977 | 11kV | 1954 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 121451 A phase DOLF : 10 Amp Replaced faulty transformer Excluded OMS 851021 | July | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-07-21 | N | 977 | N | 3 | N | N | 1.1101 | 39.4971 | 1427.9256
| ZN12650:PA5 | 144 | 1213.0816 | #N/A | 8.4242 | 39.4971 | 18460 | 19193 | 851119 | 2012-07-22 13:44 | 2012-07-22 15:30 | 106 | 11kV | 212 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121461 A phase DOLF : 10 Amp | July | 2012 | 2013Q1 | 2013 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | UG | Not Veg | 2012-07-22 | N | 106 | N | 8 | N | N | 1.1101 | 39.4971 | 154.9233
| ZN12650:PA6 | 1324 | 1639.8487 | 42.34 | 1.2386 | 42.34 | 16655 | 966 | 851135 | 2012-07-22 14:46 | 2012-07-22 15:48 | 62 | 11kV | 72286 | 1253 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | At S195 Pymble Panel 9 Tripped on A phase Overcurrent Alarms: 11kV Trip and Tx2 Group Earth Cause: AB2302 Failed Explosively. See OMS 851493 851486 851135 | July | 2012 | 2013Q1 | 2013 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Not Veg | 2012-07-22 | N | 57.6903 | N | 8 | N | N | 1.1101 | 39.4971 | 52824.4767
| ZN12650:PA8 | 181 | 238.6581 | #N/A | 1.3186 | 39.4971 | 17448 | 8307 | 851215 | 2012-07-22 21:36 | 2012-07-22 23:20 | 104 | 11kV | 148156 | 1440 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn269 Waverley 11kv fdr Pa9 tripped on: Relays-Cph O/C, EFI Signals: 11kv trip, Zone Earth, Tx2 & Tx3 Group Earth Field EFI-S4051 S2188 S35262 Cause: Fault Suspect 11kv Cable fault from S2188 to S183 to S2537 See 851512,4 Exclude 851215 | July | 2012 | 2013Q1 | 2013 | ZN269:PA9 | ZN36100:PA6 | ZN36100/000006 | WAVERLEY | UG | Not Veg | 2012-07-22 | N | 102.8861 | N | 8 | N | N | 1.1101 | 39.4971 | 108268.0349
| ZN12650:PA9 | 1305 | 1633.6113 | 44.29 | 1.2518 | 44.29 | 16603 | 664 | 852452 | 2012-07-23 04:29 | 2012-07-23 06:30 | 121 | 11kV | 8349 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN14891 Wyong 11kV Recloser Dickson Tripped on IOC. Cause: Suspect Branch on OH in Dickson Rd. | July | 2012 | 2013Q1 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2012-07-23 | N | 121 | N | 3 | N | N | 1.1101 | 39.4971 | 6101.2029
| 229:34983 | 429 | 1168.6327 | 37.26 | 2.7241 | 37.26 | 18256 | 17108 | 851149 | 2012-07-22 17:16 | 2012-07-23 10:45 | 1049 | 11kV | 8230 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121463 3 fault operations Feeder isolated following earlier Trip & reclose. Found main down from Sw 42066 to pole HQ-61555 Sw 42066 tripped on try back. Trip & Reclose OMS 851405 | July | 2012 | 2013Q1 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2012-07-22 | N | 433.1579 | N | 8 | N | N | 1.1101 | 39.4971 | 6014.2413
| 229:34986 | 81 | 76.0492 | 34.25 | 0.93888 | 34.25 | 18067 | 15470 | 851428 | 2012-07-23 10:28 | 2012-07-23 11:45 | 77 | 11kV | 7469 | 97 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of Panel 22 Berowra Tripped AB956 Opend and Defective AB1161 is Closed. AB269 Fell Apart during Disconnect 295636 Cause: Dop interrupted PT2178 and PT2217 From AB 1212 to allow staff to make temporary repairs and Tie back bonds on both sides of AB269 See OMS 852387 852385 851428 851466 | July | 2012 | 2013Q1 | 2013 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2012-07-23 | N | 77 | N | 3 | N | N | 1.1101 | 39.4971 | 5458.1249
| 229:34989 | 14 | 17.0473 | #N/A | 1.2177 | 39.4971 | 17484 | 8647 | 851291 | 2012-07-23 08:28 | 2012-07-23 17:30 | 542 | 11kV | 1084 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121471 B phase B Phase LL Lead disconnected from top of DOLF at Sub 51769 BEH Irrigation. No Prot Op Excluded OMS 851291 | July | 2012 | 2013Q1 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-07-23 | N | 542 | N | 3 | N | N | 1.1101 | 39.4971 | 792.1552
| 229:34992 | 38 | 176.6927 | 43.27 | 4.6498 | 43.27 | 18220 | 16786 | 851828 | 2012-07-24 03:28 | 2012-07-24 04:27 | 59 | 11kV | 1298 | 22 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn 2466 Flemington - 11kv Panel No.32 "Sub 8125 Birnie Par No.3" feeder tripped. Relays: Earth fault, fault check. Signals: 11kv trip, Zone earth, No.3 Group Earth. Field EFI's: Nil Remarks: 11KV UG Fault from Zn2466 Flemington Panel No.32 to Sub 8125 Birnie Par No.3 Related jobs: #8518528, 851938 | July | 2012 | 2013Q1 | 2013 | ZN2466:PA32 | ZN2466:PA6 | ZN02466/000006 | CUMBERLAND | UG | Not Veg | 2012-07-24 | N | 59 | N | 7 | N | N | 1.1101 | 39.4971 | 948.5401
| 229:34995 | 696 | 1030.7203 | 44.74 | 1.4809 | 44.74 | 17905 | 13166 | 851833 | 2012-07-24 06:31 | 2012-07-24 09:00 | 149 | 11kV | 149 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | AT ZN 9245 ENGADINE A SECTION OF 11KV FEEDER "SUB 9668" EX PANEL 10, AT CP 9240 ENGADINE PUMP STATION TO HVC, LHS PHASE HDO HAS BLOWN CAUSE NOT ASCERTAINED NOTHING FOUND. | July | 2012 | 2013Q1 | 2013 |  |  |  | SUTHERLAND | OH | Veg | 2012-07-24 | N | 149 | N | 7 | N | N | 1.1101 | 39.4971 | 108.8848
| ZN12660:PA10 | 1822 | 1375.8668 | 34.44 | 0.75514 | 34.44 | 16870 | 2472 | 851987 | 2012-07-24 11:22 | 2012-07-24 12:22 | 60 | 11kV | 119879 | 2042 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.12570 Avoca, 11kV Fdr CB tripped on A phase IOC and timed OC. 11kV trip. | July | 2012 | 2013Q1 | 2013 | ZN12570:PA12 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2012-07-24 | N | 58.7067 | N | 7 | N | N | 1.1101 | 39.4971 | 87604.0374
| ZN12660:PA11 | 762 | 694.0379 | 33.59 | 0.91081 | 33.59 | 17096 | 4372 | 851999 | 2012-07-24 11:24 | 2012-07-24 13:41 | 137 | 11kV | 144735.6833 | 1125 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn2466 Flemington Panel 20 John Hastings tripped on: Relays - EFI and fault check relay. Signals - 11kv trip Remarks: UG cable damgaged by contractor. UG cable damaged due to core holes along feeder trench by contractor. Auburn city council rang with details. (OMS Flemington Panel 20,27 & Lidcombe Pnl 12 is incorrect, have added to sharepoint) Related jobs: #852009, 852005, 851999, 851996, 852459, 852462, 852470, 852477, 852479 | July | 2012 | 2013Q1 | 2013 | ZN1068:PA12 | ZN2466:PA20 | ZN02466/000020 | CUMBERLAND | UG | Not Veg | 2012-07-24 | N | 128.6539 | N | 7 | N | N | 1.1101 | 39.4971 | 105768.5684
| ZN12660:PA13 | 666 | 1083.0505 | 45.86 | 1.6262 | 45.86 | 18494 | 19842 | 852231 | 2012-07-24 17:35 | 2012-07-24 18:40 | 65 | 11kV | 4054.7 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At PT.11543 the footpath 31.5 amp HDO fuse blown - cause unknown CC1: 22-"Refer to SOp" | July | 2012 | 2013Q1 | 2013 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Veg | 2012-07-24 | N | 64.3603 | N | 7 | N | N | 1.1101 | 39.4971 | 2963.0552
| ZN12660:PA14 | 1263 | 942.6299 | 34.35 | 0.74634 | 34.35 | 16898 | 2880 | 852103 | 2012-07-24 14:13 | 2012-07-24 21:15 | 422 | 11kV | 1688 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121490 Single phase DOLF : 3 Amp 252 Volts Excluded OMS 852103 | July | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2012-07-24 | N | 422 | N | 7 | N | N | 1.1101 | 39.4971 | 1233.5406
| ZN12660:PA16 | 971 | 711.6167 | 35.04 | 0.73287 | 35.04 | 16615 | 754 | 852277 | 2012-07-24 20:38 | 2012-07-24 21:35 | 56.8833 | 11kV | 48020.8833 | 1143 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Centre phase of Load Break Switch 26232 open circuited | July | 2012 | 2013Q1 | 2013 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2012-07-24 | N | 42.013 | N | 7 | N | N | 1.1101 | 39.4971 | 35092.2452
| ZN12660:PA17 | 1323 | 940.6637 | 33.56 | 0.71101 | 33.56 | 17591 | 9776 | 852317 | 2012-07-25 01:30 | 2012-07-25 02:10 | 40 | 11kV | 4000 | 100 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 121492 B phase DOLF : 40 Amp DEAD POSSUM FOUND AT BASE OF POLE. 248V, 76A, 100A, 227A. Excluded OMS# 852317 | July | 2012 | 2013Q1 | 2013 | 218:7478 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2012-07-25 | N | 40 | N | 4 | N | N | 1.1101 | 39.4971 | 2923.082
| ZN12660:PA5 | 281 | 151.5972 | 32.21 | 0.53949 | 32.21 | 18041 | 14997 | 852486 | 2012-07-25 10:49 | 2012-07-25 11:50 | 61 | 11kV | 6703.7333 | 110 | HV | 3rd Party Action | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | @S1409 ODEA AVE 11kv RMI tee off to Tx found open. Open Air Sub. Scaffolding has just been erected around sub perimeter. See 852486 GIS 853232 Exclude 852521,9 | July | 2012 | 2013Q1 | 2013 | ZN188:PA16 | ZN188:PA42 | ZN00188/000042 | SYDNEY | UG | Not Veg | 2012-07-25 | N | 60.943 | N | 4 | N | N | 1.1101 | 39.4971 | 4898.8906
| ZN12660:PA6 | 474 | 341.7639 | 29.43 | 0.72102 | 29.43 | 17511 | 8907 | 852780 | 2012-07-25 20:30 | 2012-07-26 08:30 | 720 | 11kV | 720 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 121503 Sub isolated to install LV fuses to comply to standard 30A LVF installed | July | 2012 | 2013Q1 | 2013 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | UG | Not Veg | 2012-07-25 | N | 720 | N | 4 | N | N | 1.1101 | 39.4971 | 526.1548
| ZN12660:PA8 | 1320 | 962.8914 | 37.33 | 0.72946 | 37.33 | 18341 | 17804 | 852685 | 2012-07-25 16:27 | 2012-07-26 11:30 | 1143 | 11kV | 11583 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 121502 3 fault operations Single phase Earth fault Report of Tree Bringing down mains. Excluded OMS 852685, 852715, 852722, 852769, 853054 | July | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-07-25 | N | 297 | N | 4 | N | N | 1.1101 | 39.4971 | 8464.5148
| ZN14891:PA1 | 950 | 1737.0992 | 47.72 | 1.8285 | 47.72 | 17403 | 7998 | 853502 | 2012-07-26 08:30 | 2012-07-26 11:30 | 180 | 11kV | 1440 | 8 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Sub 52971 mains cut away at pole CV-53676. Col Chapman toarrange repairs to fallen mains 1st thing Friday morning. Refer 853054 Also refer prev event - 853495 | July | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-07-26 | N | 180 | N | 1 | N | N | 1.1101 | 39.4971 | 1052.3095
| ZN14891:PA10 | 1744 | 1096.1324 | 32.34 | 0.62852 | 32.34 | 17527 | 8998 | 853450 | 2012-07-27 05:33 | 2012-07-27 07:15 | 102 | 11kV | 816 | 8 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | Unselected | N | At S6968 Katherine Victoria No1 and No2 TX RMCB tripped. (Parallel Trip Coils) Relays on No2 Protn Panel - Low Gas and Protection Trip Indicators Cause: Low Gas in No2 Caused Parallel Trip on Both Txs. See OMS 855091 853450 | July | 2012 | 2013Q1 | 2013 | ZN80:PA24 | ZN80:PA24 | ZN00080/000024 | WILLOUGHBY | Unknown | Unknown | 2012-07-27 | N | 102 | N | 6 | N | N | 1.1101 | 39.4971 | 596.3087
| ZN14891:PA12 | 728 | 734.3625 | 34.65 | 1.0087 | 34.65 | 17557 | 9308 | 853598 | 2012-07-27 10:54 | 2012-07-27 12:58 | 124 | 11kV | 62635.0333 | 508 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Section of 11kv Pa42 fdr Ex Zn2602 Clovelly @S2919 Randwick Racecourse SwD tripped on Aph timed O/C with an EFI EFI operated @ Zn2602 Clovelly See 853598 GIS 854323,43,69 Exclude 853604,6,36,40 | July | 2012 | 2013Q1 | 2013 | ZN2602:PA42 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2012-07-27 | N | 123.2973 | N | 6 | N | N | 1.1101 | 39.4971 | 45771.8349
| ZN14891:PA14 | 590 | 1159.2479 | 56.03 | 1.9648 | 56.03 | 17859 | 12774 | 853625 | 2012-07-27 11:16 | 2012-07-27 13:36 | 140 | 11kV | 115997 | 1181 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At S187 Crows Nest Panel 17 Tripped on Relays: A B and C Phase Earth Fault EFI and Fault Check. Abnormal Switching: Feeder defective between S1391 and S4726 and S8545. Cause: Contract Cable Layers Dug Up 11kV Feeders between S1033 and S1391 and S3496 See OMS 855318 855319 853625 | July | 2012 | 2013Q1 | 2013 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2012-07-27 | N | 98.2193 | N | 6 | N | N | 1.1101 | 39.4971 | 84767.1863
| ZN14891:PA16 | 1819 | 1408.7519 | 32.55 | 0.77447 | 32.55 | 18217 | 16735 | 853678 | 2012-07-27 12:43 | 2012-07-27 14:26 | 102.8333 | 11kV | 2262.3333 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121522 Single phase 11kV Fdr isolated for emergency repairs to low 11kV OHM at Congewai sub 50517. | July | 2012 | 2013Q1 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-07-27 | N | 102.8333 | N | 6 | N | N | 1.1101 | 39.4971 | 1653.2465
| ZN14891:PA17 | 1631 | 842.9497 | 31.26 | 0.51683 | 31.26 | 18279 | 17278 | 853847 | 2012-07-27 17:54 | 2012-07-27 18:53 | 58.9167 | 11kV | 2571.55 | 56 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121523 B phase DOLF : 40 Amp Fatigued fuse B phase DOLF. | July | 2012 | 2013Q1 | 2013 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2012-07-27 | N | 45.9205 | N | 6 | N | N | 1.1101 | 39.4971 | 1879.2129
| ZN14891:PA19 | 256 | 490.7115 | 44.47 | 1.9168 | 44.47 | 17589 | 9773 | 853852 | 2012-07-27 17:54 | 2012-07-27 19:45 | 111 | 11kV | 111 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121525 No protection operated, the fuse and carrier had corroded/rusted and caused a high resistance connection. Excluded OMS (times) 853852 | July | 2012 | 2013Q1 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-07-27 | N | 111 | N | 6 | N | N | 1.1101 | 39.4971 | 81.1155
| ZN14891:PA20 | 555 | 1133.5439 | 39.62 | 2.0424 | 39.62 | 16963 | 3341 | 853894 | 2012-07-28 07:17 | 2012-07-28 08:40 | 83 | 11kV | 63927 | 1060 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At S965 Pennant Hills Panel 43 tripped on A abd C phase Overcurrent With EFI Cause: Surge arrestor on UGOH O/S 19 Eucalypus Failed explosively See OMS 854261 854262 854263 853907 853894 | July | 2012 | 2013Q1 | 2013 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | OH | Not Veg | 2012-07-28 | N | 60.3085 | N | 1 | N | N | 1.1101 | 39.4971 | 46715.9661
| ZN14891:PA21 | 725 | 803.7209 | 37.96 | 1.1086 | 37.96 | 16992 | 3512 | 854066 | 2012-07-29 00:28 | 2012-07-29 02:20 | 112 | 11kV | 11648 | 104 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT2007 Lovell Hollis 50A Centre Phase HDO operated. Cause: Fuse fatiguie. See OMS 855087 854066/068 | July | 2012 | 2013Q1 | 2013 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2012-07-29 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 8512.0148
| ZN14891:PA3 | 25 | 247.128 | 41.31 | 9.8851 | 41.31 | 16842 | 2297 | 854085 | 2012-07-29 08:09 | 2012-07-29 13:45 | 336.2833 | 11kV | 3026.55 | 9 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121529 11kV main on ground near pole JR-84101. Backfed from sub 9759 no prot operation. (cow killed) | July | 2012 | 2013Q1 | 2013 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2012-07-29 | N | 336.2833 | N | 3 | N | N | 1.1101 | 39.4971 | 2211.7135
| ZN14891:PA5 | 1421 | 1526.7459 | 36.91 | 1.0744 | 36.91 | 17765 | 12043 | 854392 | 2012-07-29 15:04 | 2012-07-29 15:54 | 50 | 11kV | 69300 | 1386 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pa17 fdr tripped on: translay EarthLeakage EFI Field EFI's Nil Cause: UG Fault Suspected Cable fault front line See 854392 exclude 854164 | July | 2012 | 2013Q1 | 2013 | ZN1788:PA17 | ZN1788:PA17 | ZN01788/000017 | BAYSIDE | UG | Not Veg | 2012-07-29 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 50642.396
| ZN14891:PA6 | 221 | 1013.097 | 63.26 | 4.5841 | 63.26 | 16853 | 2341 | 854371 | 2012-07-30 10:21 | 2012-07-30 11:40 | 79 | 11kV | 1046 | 266 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 121536 C Phase DOLF : 40 Amp. Crow across HV at Bronte Rd. sub 5733 Excluded OMS 854371, 854376, 854383, 854418 | July | 2012 | 2013Q1 | 2013 | 208:72 | 257:81999 | ZN00257/081999 | NEWCASTLE | OH | Not Veg | 2012-07-30 | N | 3.9323 | N | 4 | N | N | 1.1101 | 39.4971 | 764.3859
| ZN14891:PA8 | 1381 | 851.2883 | 30.92 | 0.61643 | 30.92 | 17504 | 8857 | 854693 | 2012-07-30 18:30 | 2012-07-30 19:47 | 77 | 11kV | 246939 | 3207 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 121544 3 fault operations A & C phases Overcurrent faulty section of UGM between Sw 34260 & ABS 43864 Excluded oms # 854693 & 854700 | July | 2012 | 2013Q1 | 2013 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | UG | Not Veg | 2012-07-30 | N | 77 | N | 4 | N | N | 1.1101 | 39.4971 | 180455.7377
| ZN14891:PA9 | 1353 | 1119.2924 | 35.43 | 0.82727 | 35.43 | 17764 | 12042 | 854735 | 2012-07-30 20:31 | 2012-07-30 23:55 | 204 | 11kV | 238676 | 2712 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At Zn.15008 Harbord, Panel 7 Fdr CB tripped, reclosed and locked outr on IOC, lockout, timing, earth fault check, zone earth and 11kV trip. At corner of Albert Ave and Soldiers Ave Freshwater near USL.22917 conductor failed | July | 2012 | 2013Q1 | 2013 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2012-07-30 | N | 88.0074 | N | 4 | N | N | 1.1101 | 39.4971 | 174417.381
| ZN188:PA1 | 999 | 741.8621 | 49.14 | 0.7426 | 49.14 | 16932 | 3119 | 854764 | 2012-07-30 22:59 | 2012-07-31 00:01 | 62 | 11kV | 2976 | 48 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1561 Derwent Daly 31.5A fuse operated/. Cause: Fuse fatigue See OMS 855618 854764 | July | 2012 | 2013Q1 | 2013 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Not Veg | 2012-07-30 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 2174.773
| ZN188:PA10 | 2221 | 1970.6397 | 39.17 | 0.88728 | 39.17 | 18160 | 16135 | 854767 | 2012-07-31 01:48 | 2012-07-31 02:40 | 52 | 11kV | 3172 | 61 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 121547 C Phase DOLF : 20 Amp Found possum at sub. Load readings: 25/30/45A; 253V. Excluded OMS Job No. 854767. | July | 2012 | 2013Q1 | 2013 | 221:11894 | 221:11894 | ZN00221/011894 | LAKE MACQUARIE | OH | Not Veg | 2012-07-31 | N | 52 | N | 2 | N | N | 1.1101 | 39.4971 | 2318.004
| ZN188:PA13 | 83 | 262.2892 | #N/A | 3.1601 | 39.4971 | 17804 | 12440 | 854770 | 2012-07-31 02:50 | 2012-07-31 04:01 | 71 | 11kV | 110821 | 1971 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2310 Punchbowl Pnl33 "Sefton" tripped. Relays: Earth Fault, EFI Signals: No.5 Tx group earth, 11KV trip Field EFI's: S4125, S4012, S3289, S35230 Remarks: UG faul. 11kv feeder between S.35230 Wangee Punchbowl No.2 and S.4013 Wangee punchbowl failed. Related jobs: #854770, 854802, 854801 | July | 2012 | 2013Q1 | 2013 | ZN2310:PA33 | ZN2310:PA15 | ZN02310/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-07-31 | N | 56.2258 | N | 2 | N | N | 1.1101 | 39.4971 | 80984.7181
| ZN188:PA14 | 309 | 215.4433 | #N/A | 0.69723 | 39.4971 | 17980 | 14115 | 855311 | 2012-08-01 08:30 | 2012-08-01 10:35 | 125 | 11kV | 336.5833 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121563 C phase dist fuse : 100 Amp Sub isolated LVF Fuse & holder replaced due to ageing. As left 249V, 250V & 242V. 5A, 5a & 40A Cass No. 735681. Excluded OMS 855311 | August | 2012 | 2013Q1 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2012-08-01 | N | 112.1944 | N | 2 | N | N | 1.1101 | 39.4971 | 245.9652
| ZN188:PA15 | 465 | 567.386 | 44.67 | 1.2202 | 44.67 | 16984 | 3450 | 855693 | 2012-08-01 17:58 | 2012-08-01 19:00 | 62.0333 | 11kV | 2295.2333 | 37 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121571 B phase DOLF : 20 Amp. | August | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2012-08-01 | N | 62.0333 | N | 2 | N | N | 1.1101 | 39.4971 | 1677.2888
| ZN188:PA16 | 1117 | 640.36 | 38.17 | 0.57329 | 38.17 | 16743 | 1537 | 855746 | 2012-08-02 02:53 | 2012-08-02 04:55 | 122 | 11kV | 154286 | 1896 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S.12580 Erina, Panel 1 Fdr CB tripped on B and C phase OC, 11kV trip. Field efi's down at S.18318, S.18217, S.18864, S.18865 and S.11628. 11kV UG/OH from USL.40390 defective. PE to investigate the non operation of recloser | August | 2012 | 2013Q1 | 2013 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | Unknown | Unknown | 2012-08-02 | N | 81.3745 | N | 2 | N | N | 1.1101 | 39.4971 | 112747.6581
| ZN188:PA17 | 2489 | 1622.9104 | 39.88 | 0.65203 | 39.88 | 17947 | 13588 | 856063 | 2012-08-02 15:03 | 2012-08-02 16:46 | 103 | 11kV | 231618 | 2792 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn269 Waverley Zone Pa19 tripped on Cph IOC Bph timed EFI Pa26 tripped on EF EFI EFI's S4280 S7971 S4507 S48624 S7207 S35303 S8831 S2229 S1990 ABNORMAL:@S84 fdr 'S2229 etc' closed see D&R 288088/290440 Cause: UG Cable Fault btw Pa19 to S1990 See 857492,5,6 Exclude 856063,78 | August | 2012 | 2013Q1 | 2013 | ZN269:PA19 | ZN36100:PA25 | ZN36100/000025 | WAVERLEY | UG | Not Veg | 2012-08-02 | N | 82.9577 | N | 2 | N | N | 1.1101 | 39.4971 | 169259.6028
| ZN188:PA18 | 290 | 439.5695 | #N/A | 1.5158 | 39.4971 | 18066 | 15469 | 856197 | 2012-08-03 00:23 | 2012-08-03 01:25 | 62 | 11kV | 8356 | 135 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7900 Campbell St Pa17 tripped on Earth Fault, Earth Fault check relay, EFI Signals: Overcurrnet and Earth Fault Pickup, overcurrent timeout, earth fualt timeout EFI 11kv trip Cause: UG Fault Note: Sydney Water digging in front of zone. Front Line Feeder Fault See 857535,8 Exclude 856197 | August | 2012 | 2013Q1 | 2013 | ZN7900:PA17 | ZN7900:PA20 | ZN07900/000020 | SYDNEY | UG | Not Veg | 2012-08-03 | N | 61.8963 | N | 3 | N | N | 1.1101 | 39.4971 | 6106.3183
| ZN188:PA2 | 629 | 564.8357 | 44.3 | 0.89799 | 44.3 | 16924 | 3064 | 856208 | 2012-08-03 07:37 | 2012-08-03 10:25 | 168 | 11kV | 168 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121582 B phase DOLF : 10 Amp. Excluded OMS 856208 no cause found | August | 2012 | 2013Q1 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2012-08-03 | N | 168 | N | 3 | N | N | 1.1101 | 39.4971 | 122.7694
| ZN188:PA21 | 1560 | 1090.3846 | 43.83 | 0.69896 | 43.83 | 16849 | 2317 | 880473 | 2012-08-03 20:53 | 2012-08-03 22:36 | 103 | 11kV | 27192 | 264 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N |  | August | 2012 | 2013Q1 | 2013 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2012-08-03 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 19871.1116
| ZN188:PA22 | 67 | 505.1353 | 39.76 | 7.5393 | 39.76 | 16731 | 1418 | 856665 | 2012-08-04 11:10 | 2012-08-04 13:50 | 160 | 11kV | 46440 | 713 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn10993 Hurstville Nth Pa7 tripped on ACph O/C REclose time delay lockout UGOH Fault Short Cicruit 11kV UGOH to S10903 COmmercial West Utilux failed See 857684,5 Exclude 856664,5 | August | 2012 | 2013Q1 | 2013 | ZN10993:PA7 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | Unknown | Unknown | 2012-08-04 | N | 65.1332 | N | 2 | N | N | 1.1101 | 39.4971 | 33936.9823
| ZN188:PA25 | 56 | 88.8225 | #N/A | 1.5861 | 39.4971 | 16747 | 1566 | 856721 | 2012-08-04 19:09 | 2012-08-04 21:00 | 111 | 11kV | 13256.5333 | 120 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | Ex Zn1788 Matraville Zn Ex Pa8 @S2640 BCph JOS 1025 40amp fuses operated Govt Bus hit kiosk See 856721 GIS 857556 Exclude 856723,4,6 | August | 2012 | 2013Q1 | 2013 | ZN1788:PA8 | ZN1788:PA61 | ZN01788/000061 | RANDWICK | Unknown | Not Veg | 2012-08-04 | N | 110.4711 | N | 2 | N | N | 1.1101 | 39.4971 | 9687.4836
| ZN188:PA26 | 1289 | 1834.1202 | 43.98 | 1.4229 | 43.98 | 17987 | 14139 | 856879 | 2012-08-06 00:42 | 2012-08-06 02:05 | 83 | 11kV | 198239 | 2463 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Zn398 Dulwich Hill Pa8 tripped on Relays-Electronic-DOp unable to read Signals-11kV trip, ZE, TX1 GE No field EFI operated Cause- End Box Fault See 857702 exclude 856879,880 | August | 2012 | 2013Q1 | 2013 | ZN398:PA8 | ZN398:PA2 | ZN00398/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-08-06 | N | 80.4868 | N | 2 | N | N | 1.1101 | 39.4971 | 144867.2141
| ZN188:PA27 | 217 | 1073.6775 | 42.99 | 4.9478 | 42.99 | 16553 | 332 | 856917 | 2012-08-06 07:55 | 2012-08-06 08:02 | 7 | 11kV | 5789 | 827 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121612/01 & 121612/02 IR 50797 Trip on overload - load transfer during switching on SI 24187. | August | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2012-08-06 | N | 7 | N | 2 | N | N | 1.1101 | 39.4971 | 4230.4305
| ZN188:PA28 | 143 | 668.0128 | #N/A | 4.6714 | 39.4971 | 16642 | 909 | 857793 | 2012-08-07 20:09 | 2012-08-07 21:39 | 90 | 11kV | 67617 | 901 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At Zn.14892 Charmhaven, Panel 1 Fdr CB tripped on SEF, reclosing lockout and timing relay operated. Bond burnt off the 11kV USL#42035 | August | 2012 | 2013Q1 | 2013 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | OH | Not Veg | 2012-08-07 | N | 75.0466 | N | 1 | N | N | 1.1101 | 39.4971 | 49412.5092
| ZN188:PA29 | 40 | 1043.9261 | #N/A | 26.0982 | 39.4971 | 17394 | 7909 | 857832 | 2012-08-08 07:43 | 2012-08-08 09:15 | 92 | 11kV | 644 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121625 B phase DOLF : 20 Amp top of fuse holder burnt off, fuse holder replaced Excluded oms 857832/857783 | August | 2012 | 2013Q1 | 2013 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2012-08-08 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 470.6162
| ZN188:PA3 | 915 | 761.2345 | 44.1 | 0.83195 | 44.1 | 18084 | 15655 | 858005 | 2012-08-08 11:02 | 2012-08-08 12:36 | 93.8167 | 11kV | 278.7667 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121627 No protection operations. Operator found DOLF dislodged from carrier. Replaced OK. Volts = 256. Excluded OMS # 858005 | August | 2012 | 2013Q1 | 2013 | 203:8090 | 204:82701 | ZN00204/082701 | NEWCASTLE | OH | Not Veg | 2012-08-08 | N | 92.9222 | N | 3 | N | N | 1.1101 | 39.4971 | 203.7145
| ZN188:PA30 | 185 | 312.4279 | #N/A | 1.6888 | 39.4971 | 16824 | 2182 | 858295 | 2012-08-08 23:01 | 2012-08-09 00:15 | 74 | 11kV | 148 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121636 Single phase DOLF : 10 Amp Fatigued fuse. Readings as left 24A @ 243V Excluded OMS 858295 | August | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2012-08-08 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 108.154
| ZN188:PA31 | 592 | 953.8321 | #N/A | 1.6112 | 39.4971 | 17823 | 12518 | 858489 | 2012-08-09 10:56 | 2012-08-09 12:45 | 108.9667 | 11kV | 8608.3667 | 79 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | N | LID 121641 Feeder isolated for emergency pole & xarm replacement. Poles 5H-70060 & 5H-70061. Emergency switching request 24411. | August | 2012 | 2013Q1 | 2013 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2012-08-09 | N | 108.9667 | N | 3 | N | N | 1.1101 | 39.4971 | 6290.7405
| ZN188:PA32 | 860 | 635.1916 | 46.28 | 0.73859 | 46.28 | 17595 | 9806 | 858575 | 2012-08-09 12:46 | 2012-08-09 13:50 | 64 | 11kV | 53056 | 829 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | LID 121643 2 fault operations A & B phase Instantaneous Earth fault; Instataneous Overcurrent Contractor hit cable outside Thornton sub. Excluded OMS No's 858575 & 858582. | August | 2012 | 2013Q1 | 2013 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | UG | Not Veg | 2012-08-09 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 38771.7599
| ZN188:PA33 | 264 | 643.6177 | 49.16 | 2.4379 | 49.16 | 16981 | 3440 | 858846 | 2012-08-09 22:45 | 2012-08-10 00:11 | 86 | 11kV | 145914 | 2012 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15009 Manly, 11kV Panel CB "1R" tripped on Basler relay Earth fault, Fault Check, efi, 11kV signal, zone earth. UG/OH shorted suspect possum | August | 2012 | 2013Q1 | 2013 | ZN15009:PA1 | ZN15009:PA1 | ZN15009/000001 | NORTHERN BEACHES | OH | Not Veg | 2012-08-09 | N | 72.5219 | N | 3 | N | N | 1.1101 | 39.4971 | 106629.6475
| ZN188:PA34 | 144 | 117.3996 | #N/A | 0.81528 | 39.4971 | 17335 | 7356 | 858971 | 2012-08-10 10:25 | 2012-08-10 12:00 | 95 | 11kV | 146858 | 2131 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | Unselected | Y | @Zn9700 Kirrawee 11kv Pa17 fdr tripped on Earth fault Signals: EFI operated at S9048 S9587 S9838 S9807 Cause:UG Cable damaged by staff. Remarks: 11kv cable damaged cnr forest and gymea bay road between S9807 via PT9262 to AB35356 See 863443 Restore 863444,5 Exclude 858971 | August | 2012 | 2013Q1 | 2013 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | UG | Not Veg | 2012-08-10 | N | 68.9151 | N | 8 | N | N | 1.1101 | 39.4971 | 107319.4948
| ZN188:PA37 | 2250 | 1160.4255 | 36.45 | 0.51574 | 36.45 | 18396 | 18408 | 859058 | 2012-08-10 11:29 | 2012-08-10 12:19 | 50 | 11kV | 51750 | 1035 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | Y | Sub 847 HOrnsby Panel 44 "Haldane Health etc" feeder tripped, reclosed, tripped and locked out on: Relays: A and C Phase IOC, Lockout, Reclose timing, Fault check. Signals: 11KV trip., Zone earth, Group 3 Earth Field EFI's: S35146, S8975, S47937, S4837 Remarks: Tree/branch on OH mains. Outside 53 Dudley Ave Related jobs: #859058, 859074, 859108, 859072, 859063, 861304 | August | 2012 | 2013Q1 | 2013 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Veg | 2012-08-10 | Y | 50 | N | 8 | N | Y | 1.1101 | 39.4971 | 37817.3736
| ZN188:PA38 | 1038 | 696.6218 | 35.09 | 0.67112 | 35.09 | 17808 | 12460 | 859099 | 2012-08-10 11:43 | 2012-08-10 13:13 | 90 | 11kV | 189630 | 2107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | @Zn10995 Riverwood 11kv Pa7 tripped on Cph timed overcurrent and lock out Cuase: Tree branch on mains Remarks: Branch on mains vicinity $10124 See 863458 exclude 859099 | August | 2012 | 2013Q1 | 2013 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Veg | 2012-08-10 | Y | 90 | N | 8 | N | Y | 1.1101 | 39.4971 | 138576.0109
| ZN188:PA4 | 661 | 668.6892 | 45.07 | 1.0116 | 45.07 | 17017 | 3796 | 859257 | 2012-08-10 12:25 | 2012-08-10 13:37 | 72 | 11kV | 115335 | 1732 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | At 12570 Avoca Panel 1 Tripped, reclosed, tripped and locked out on Relays: Earth Fault, Lockout, Timing and EFI. Cause: Not ascertained. See OMS 864476 864480 864479 859257 | August | 2012 | 2013Q1 | 2013 | ZN12570:PA1 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2012-08-10 | Y | 66.5906 | N | 8 | N | Y | 1.1101 | 39.4971 | 84283.4162
| ZN188:PA41 | 6 | 1039.9101 | #N/A | 173.3183 | 39.4971 | 17368 | 7632 | 858873 | 2012-08-10 07:41 | 2012-08-10 13:46 | 365 | 11kV | 72195 | 233 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | Y | LID 121652 C phase Overcurrent; Earth fault CB 8089 OP/CL/OP C phase O/C & EF CB 91144 OP A&C O/C CABLE FAULT into Sw 30369. Taps burnt off ABS 19324 Wires down pole JU-30058 excluded OMS 858945 | August | 2012 | 2013Q1 | 2013 | 203:8089 | 204:82703 | ZN00204/082703 | NEWCASTLE | UG | Not Veg | 2012-08-10 | N | 309.8498 | N | 8 | N | N | 1.1101 | 39.4971 | 52757.9766
| ZN188:PA42 | 737 | 1123.9 | #N/A | 1.525 | 39.4971 | 17498 | 8803 | 859071 | 2012-08-10 11:44 | 2012-08-10 14:01 | 137 | 11kV | 12661.2667 | 93 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | At Sub 4037 Cavil Ave B phase 40amp HV fuse operated. Failed to trip TX Section Panel No.11 "Norton Queen" ex sub 398 Cavill Ave Remarks: weathers related See 859092 GIS 863488 Exclude 859155,463 | August | 2012 | 2013Q1 | 2013 | ZN398:PA11 | ZN398:PA11 | ZN00398/000011 | INNER WEST | OH | Veg | 2012-08-10 | N | 136.1427 | N | 8 | N | N | 1.1101 | 39.4971 | 9252.4802
| ZN188:PA43 | 991 | 944.4157 | 39.23 | 0.95299 | 39.23 | 18061 | 15432 | 870880 | 2012-08-10 12:23 | 2012-08-10 14:18 | 115 | 11kV | 1035 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | TREES PUSHING WIRES AND NOW NO POWER AT 68 AND 66 ALSO WITHOUT POWER No further information available, calls received from 55,66 and 68 Rainbow PDE advising no supply (calls attached to OMS 859244 - Feeder Outage which began at 14:18 and confirmed via SCADA), appears there was a minor disst outage prior to the feeder outage which these customers were also a part o.f | August | 2012 | 2013Q1 | 2013 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2012-08-10 | Y | 115 | N | 8 | N | Y | 1.1101 | 39.4971 | 756.3475
| ZN188:PA44 | 1345 | 1110.7864 | 46.66 | 0.82586 | 46.66 | 16502 | 14 | 859137 | 2012-08-10 11:55 | 2012-08-10 15:00 | 185 | 11kV | 78154 | 698 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At S.15002 Narrabeen Panel 4 Fdr CB trippped A and C phase OC, A phase IOC, 11kV trip. | August | 2012 | 2013Q1 | 2013 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Veg | 2012-08-10 | Y | 111.9685 | N | 8 | N | Y | 1.1101 | 39.4971 | 57112.638
| ZN188:PA45 | 506 | 644.8432 | 46.6 | 1.2744 | 46.6 | 16596 | 596 | 859395 | 2012-08-10 12:52 | 2012-08-10 15:12 | 140 | 11kV | 235653 | 1897 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 121655 2 fault operations A & C phases Overcurrent Excluded OMS 859395 branches removed form mains at sub 26216 by dop | August | 2012 | 2013Q1 | 2013 | 232:33413 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Veg | 2012-08-10 | Y | 124.224 | N | 8 | N | Y | 1.1101 | 39.4971 | 172208.2618
| ZN188:PA5 | 67 | 543.0452 | #N/A | 8.1052 | 39.4971 | 17578 | 9643 | 864489 | 2012-08-10 13:39 | 2012-08-10 15:12 | 93 | 11kV | 52009 | 1732 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | Y | At Zn12570 Avoca Panel 11 Feeder Tripped on Relays: C phase Timed O/C Field EFI's = Nil Cause: 11kV Oh feeder from AB43516 to AB43514 to PT12784 0.3 found detached from insulators and resting on crossarms near PT12784 See OMS 864489 864490 864491 | August | 2012 | 2013Q1 | 2013 | ZN12570:PA1 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2012-08-10 | Y | 30.0283 | N | 8 | N | Y | 1.1101 | 39.4971 | 38006.6432
| ZN188:PA6 | 64 | 218.6474 | #N/A | 3.4164 | 39.4971 | 16698 | 1221 | 859642 | 2012-08-10 14:01 | 2012-08-10 15:16 | 75 | 11kV | 64500 | 860 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At S80 Chatswood Panel 25 tripped on A and B phase O/C Lockout and timing relay. Signals: 11kV Trip. Tree branch on OH mains near Epping Moore See OMS 863930 859642 | August | 2012 | 2013Q1 | 2013 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2012-08-10 | N | 75 | N | 8 | N | N | 1.1101 | 39.4971 | 47134.6976
| ZN188:PA9 | 619 | 605.1213 | 49.07 | 0.97758 | 49.07 | 17656 | 10861 | 859596 | 2012-08-10 13:56 | 2012-08-10 15:27 | 91 | 11kV | 163618 | 1798 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 121657 3 phase fault branch removed from mains cnr bay rd and quigley st bolton point Excluded oms 859596 & 859721 | August | 2012 | 2013Q1 | 2013 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2012-08-10 | Y | 91 | N | 8 | N | Y | 1.1101 | 39.4971 | 119567.2085
[7 empty] | 16839 | 2245 | 859580 | 2012-08-10 13:49 | 2012-08-10 15:45 | 116 | 11kV | 1972 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | CP45010 Palmgrove Tripped on overcurrent Cause: Tree branch found on 11kV OH at PT12434 Ourimbah Footes. See OMS 864457 859508 860029 | August | 2012 | 2013Q1 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-08-10 | Y | 116 | N | 8 | N | Y | 1.1101 | 39.4971 | 1441.0794
[7 empty] | 18230 | 16884 | 859759 | 2012-08-10 14:33 | 2012-08-10 16:15 | 101.7833 | 11kV | 4885.6 | 48 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At PT1257 Namoi Place 400A fuse blown on B and C phase of distributor 2. Cause: Tree branch brought wires down. See OMS 859759/791/795/987/897 | August | 2012 | 2013Q1 | 2013 | ZN1193:PA7 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Veg | 2012-08-10 | Y | 101.7833 | N | 8 | N | Y | 1.1101 | 39.4971 | 3570.2524
[7 empty] | 17512 | 8911 | 863852 | 2012-08-10 13:01 | 2012-08-10 16:24 | 203 | 11kV | 182613 | 927 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Recloser 20397 tripped and locked out on IOC. Large tree on 11kV below recloser 20397 | August | 2012 | 2013Q1 | 2013 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2012-08-10 | Y | 196.9935 | N | 8 | N | Y | 1.1101 | 39.4971 | 133448.1942
[7 empty] | 16550 | 317 | 859592 | 2012-08-10 14:01 | 2012-08-10 16:50 | 169.4333 | 11kV | 9149.4 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | Weather related. Unknown See 859592 exclude 860004,28 | August | 2012 | 2013Q1 | 2013 | ZN35600:PA20 | ZN35600:PA20 | ZN35600/000020 | RANDWICK | OH | Veg | 2012-08-10 | N | 169.4333 | N | 8 | N | N | 1.1101 | 39.4971 | 6686.1117
[7 empty] | 16928 | 3089 | 859114 | 2012-08-10 11:52 | 2012-08-10 16:52 | 300 | 11kV | 21900 | 73 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y |  | August | 2012 | 2013Q1 | 2013 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Veg | 2012-08-10 | Y | 300 | N | 8 | N | Y | 1.1101 | 39.4971 | 16003.8741
[7 empty] | 17898 | 13124 | 859244 | 2012-08-10 14:18 | 2012-08-10 16:57 | 159 | 11kV | 149193 | 1050 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | At Sub 10994 Mortdale Panel No.21 Opened & Locked out on A & B phaseIOC, timing lockout & reclose relays & IEF Remarks: Weather related. Large tree branch on 11KV OH Beattie & Balmoral Sts Related jobs: #860233, 859244, 863327, 863332, 863336, 863337 | August | 2012 | 2013Q1 | 2013 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2012-08-10 | Y | 142.0886 | N | 8 | N | Y | 1.1101 | 39.4971 | 109025.844
[7 empty] | 17344 | 7403 | 859880 | 2012-08-10 14:47 | 2012-08-10 17:00 | 133 | 11kV | 240464 | 1808 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 121660 1 fault operation | August | 2012 | 2013Q1 | 2013 | 260:33344 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Veg | 2012-08-10 | Y | 133 | N | 8 | N | Y | 1.1101 | 39.4971 | 175723.9987
[7 empty] | 17332 | 7342 | 859283 | 2012-08-10 12:48 | 2012-08-10 17:00 | 252 | 11kV | 65652 | 432 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | Development works. GIS connectivity incorrect due to capital works. Outage has been simulated. AT S.15005 Belrose Panel 2 Fdr CB tripped on LHS Band C phase OC, efi, 11kV trip. Cause unknown - wind storm at the time Refer to related records 866697, 866695, 866691 and 866692 | August | 2012 | 2013Q1 | 2013 | ZN15012:PA8 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Veg | 2012-08-10 | Y | 151.9722 | N | 8 | N | Y | 1.1101 | 39.4971 | 47976.5452
[7 empty] | 17161 | 5192 | 866750 | 2012-08-10 16:22 | 2012-08-10 17:00 | 38 | 11kV | 20178 | 531 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | Development works. GIS connectivity incorrect due to capital works. Outage has been simulated. AT S.15005 Belrose Panel 2 Fdr CB tripped on LHS Band C phase OC, efi, 11kV trip. Cause unknown - wind storm at the time, refer to related record 866752 | August | 2012 | 2013Q1 | 2013 | ZN15011:PA8 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Veg | 2012-08-10 | Y | 38 | N | 8 | N | Y | 1.1101 | 39.4971 | 14745.4872
[7 empty] | 17514 | 8931 | 866744 | 2012-08-10 16:22 | 2012-08-10 17:00 | 38 | 11kV | 3420 | 90 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Unselected | Y | Development works. GIS connectivity incorrect due to capital works. Outage has been simulated. AT S.15005 Belrose Panel 2 Fdr CB tripped on LHS Band C phase OC, efi, 11kV trip. Cause unknown - wind storm at the time | August | 2012 | 2013Q1 | 2013 | ZN15011:PA8 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Not Veg | 2012-08-10 | Y | 38 | N | 8 | N | Y | 1.1101 | 39.4971 | 2499.2351
[7 empty] | 16925 | 3065 | 862387 | 2012-08-10 15:42 | 2012-08-10 17:01 | 79 | 11kV | 97486 | 1234 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Wind | Y | LID 121661/01 M De Vries - J Brewer Car hit pole at sub 767 Richardson Rd. DOP checked OK, Feeder restored. | August | 2012 | 2013Q1 | 2013 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2012-08-10 | Y | 79 | N | 8 | N | Y | 1.1101 | 39.4971 | 71239.8934
[7 empty] | 16706 | 1250 | 859323 | 2012-08-10 13:18 | 2012-08-10 17:25 | 247 | 11kV | 33345 | 135 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At S742 Calvert Spencer HV fuse blown on B phase. Cause: Tree/branch on OH Mains and UGOH. See OMS 862966 862035 859452 | August | 2012 | 2013Q1 | 2013 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | OH | Veg | 2012-08-10 | Y | 247 | N | 8 | N | Y | 1.1101 | 39.4971 | 24367.5425
[7 empty] | 17410 | 8049 | 859452 | 2012-08-10 16:23 | 2012-08-10 17:25 | 62 | 11kV | 3286 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At S8728 Craiglands Vale 400A fuse blown on A and B phase of distributor 2. Cause: Tree on OH Mains Removed and restored by Dop See OMS 862960 859452 | August | 2012 | 2013Q1 | 2013 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | OH | Veg | 2012-08-10 | Y | 62 | N | 8 | N | Y | 1.1101 | 39.4971 | 2401.3119
[7 empty] | 17400 | 7954 | 859332 | 2012-08-10 12:43 | 2012-08-10 17:40 | 297 | 11kV | 182507 | 781 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | Y | Recloser 35005 Bundeena Liverpool opened & lockoued out Section of Pa11 Ex S9118 Abnormal: AB35526 Open Recloser 35005 Closed see DMA Cause: Weather related Remarks: Wind causing 11k OH to clash on secnion of feeder between AB35595, AB35265 tee S9922 (in LV//) See 863597 restore 863598 exclude 859332,553,990 | August | 2012 | 2013Q1 | 2013 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2012-08-10 | N | 233.6837 | N | 8 | N | N | 1.1101 | 39.4971 | 133370.7326
[7 empty] | 17563 | 9492 | 860152 | 2012-08-10 15:47 | 2012-08-10 18:03 | 136 | 11kV | 60514 | 475 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | @Zn10990 Arncliffe Pa5 Opened & Locked Out on Sensitive Earth, Cph IOC & Timedl, Lockout Cause: Weather related Remarks: Large branch on 11kv OH btw S10800 to S10742 to AB31316 See 863666,8 GIS 864012 Exclude 860152,293 | August | 2012 | 2013Q1 | 2013 | ZN10990:PA5 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | OH | Veg | 2012-08-10 | N | 127.3979 | N | 8 | N | N | 1.1101 | 39.4971 | 44221.8463
[7 empty] | 17037 | 3964 | 859936 | 2012-08-10 15:15 | 2012-08-10 18:40 | 205 | 11kV | 5945 | 29 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | Y | At S4438 Kelray Salisbury 400A fuse blown on A phase of distributor 2 Cause: OH cables twisted together. See OMS 864103 859950 | August | 2012 | 2013Q1 | 2013 | ZN847:PA44 | ZN847:PA31 | ZN00847/000031 | HORNSBY | OH | Not Veg | 2012-08-10 | Y | 205 | N | 8 | N | Y | 1.1101 | 39.4971 | 4344.4307
[7 empty] | 16647 | 937 | 860432 | 2012-08-10 17:51 | 2012-08-10 18:50 | 59 | 11kV | 92925 | 1575 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | Y | Panel 7 Fdr CB opened by S.Op to prevent overload condition as a result of S10 33kV Feeder failure | August | 2012 | 2013Q1 | 2013 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Not Veg | 2012-08-10 | Y | 59 | N | 8 | N | Y | 1.1101 | 39.4971 | 67906.8492
[7 empty] | 18286 | 17341 | 859890 | 2012-08-10 14:57 | 2012-08-10 18:55 | 238 | 11kV | 42045 | 233 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | Recloser CP44995 Kulnurra Tripped On IOC. Cause Not ascertcertained See OMS 866266/267/270/271/272/273 859890 | August | 2012 | 2013Q1 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2012-08-10 | Y | 180.4506 | N | 8 | N | Y | 1.1101 | 39.4971 | 30725.2459
[7 empty] | 17269 | 6796 | 859361 | 2012-08-10 12:57 | 2012-08-10 19:55 | 418 | 11kV | 118395 | 1601 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | Y | LID 121670 2 fault operations HV into LV at sub 9548 excluded OMS 859390 | August | 2012 | 2013Q1 | 2013 | 260:33353 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2012-08-10 | Y | 73.9507 | N | 8 | N | Y | 1.1101 | 39.4971 | 86519.5739
[7 empty] | 17592 | 9780 | 859719 | 2012-08-10 14:14 | 2012-08-10 19:55 | 341 | 11kV | 65713 | 757 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | Ex Zn12570 Avoca Panel 16 McMasters Beach Fdr Recloser CCp45133 Mc Masters Beach Tripped onA Phase O/C Cause; First Patrol DOp found 11kV OH. DOp found 11kV Mains down near PT13787 Ligntning arrestors defective and cut away at PT13787. See OMS 864557 864592 859719 | August | 2012 | 2013Q1 | 2013 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2012-08-10 | Y | 86.8071 | N | 8 | N | Y | 1.1101 | 39.4971 | 48021.1222
[7 empty] | 17289 | 6983 | 860498 | 2012-08-10 17:01 | 2012-08-10 20:10 | 189 | 11kV | 376866 | 1994 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | Abnormally Switched XPS into Hunters Hill Zone was due to be put back tonight after 2300hrs. ABNORMAL: Closed @ S5263 Gregory Morrison OPEN @S61464 Arnold Frederick. Remarks: Storm. Hunters Hill Zone Fdr "812" fault all of Hunter Hill Zone off. Section Pn24Left/Sub 61646 Related jobs: #860873, 860498, 861331, 861323 | August | 2012 | 2013Q1 | 2013 | ZN35500:PA24 | ZN129:PA49 | ZN00129/000049 | RYDE | OH | Veg | 2012-08-10 | N | 189 | N | 8 | N | N | 1.1101 | 39.4971 | 275402.5571
[7 empty] | 17556 | 9293 | 859974 | 2012-08-10 15:14 | 2012-08-10 21:30 | 376 | 11kV | 120972 | 1572 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | Y | Zone 847 Hornsby Panel 18 "Carrington Pacific" fdr tripped on Relays: A and C phase Instantaneous + timed, lock out relay A phase timing relay. Signals: 11kv trip Remarks: tree/branch on OH mains. Tree on 11kv mains near PT 1828 Bundanoon Binnari Related jobs: #859974, 860727, 860676, 861283, 861285 | August | 2012 | 2013Q1 | 2013 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2012-08-10 | Y | 76.9542 | N | 8 | N | Y | 1.1101 | 39.4971 | 88402.7695
[7 empty] | 16947 | 3245 | 860810 | 2012-08-10 19:30 | 2012-08-10 22:00 | 150 | 11kV | 39900 | 266 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | Y | LID 121671 section isolated to repair pole excluded oms 860810 | August | 2012 | 2013Q1 | 2013 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Not Veg | 2012-08-10 | Y | 150 | N | 8 | N | Y | 1.1101 | 39.4971 | 29157.7431
[7 empty] | 17566 | 9528 | 859608 | 2012-08-10 17:53 | 2012-08-10 22:17 | 264 | 11kV | 181220 | 1306 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | At S.15006 Dee Why West Panel 13 tripped on A and B phase OC, fault check and SEF, 11kV trip. 11kV on ground at corner of Suffolk and Northfolk St Collaroy | August | 2012 | 2013Q1 | 2013 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2012-08-10 | Y | 138.7596 | N | 8 | N | Y | 1.1101 | 39.4971 | 132430.2309
[7 empty] | 17143 | 4825 | 859353 | 2012-08-10 12:04 | 2012-08-11 00:40 | 756.3667 | 11kV | 58942.0667 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Tree branch was removed from OH mains in The Pinnacle | August | 2012 | 2013Q1 | 2013 | ZN15004:PA3 | ZN15004:PA9 | ZN15004/000009 | NORTHERN BEACHES | OH | Veg | 2012-08-10 | Y | 755.6675 | N | 8 | N | Y | 1.1101 | 39.4971 | 43073.1238
[7 empty] | 17571 | 9593 | 860205 | 2012-08-10 16:04 | 2012-08-11 01:30 | 566 | 11kV | 19468 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | ex Panel 2 Peats Ridge Recloser 44945 Tripped and Locked Out. Cause: Tree branch on OH mains on OH near AB44208. See OMS 856459 856459 865466 860205 | August | 2012 | 2013Q1 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2012-08-10 | Y | 367.3208 | N | 8 | N | Y | 1.1101 | 39.4971 | 14226.6402
[7 empty] | 17836 | 12593 | 860805 | 2012-08-10 22:00 | 2012-08-11 05:45 | 465 | 11kV | 10824 | 76 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Section of Panel 2 interrupted from LB41249 due to HV ABC conductors hanging low. Cause: Tree branch on Mains See OMS 865808 860944 | August | 2012 | 2013Q1 | 2013 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2012-08-10 | Y | 142.4211 | N | 8 | N | Y | 1.1101 | 39.4971 | 7909.8599
[7 empty] | 16783 | 1942 | 861071 | 2012-08-11 08:11 | 2012-08-11 10:20 | 129 | 11kV | 8461 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Interruppter 44797 tripped on fault - tree branch on OH near PT.14539 | August | 2012 | 2013Q1 | 2013 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2012-08-11 | N | 122.6232 | N | 11 | N | N | 1.1101 | 39.4971 | 6183.0492
[7 empty] | 18053 | 15373 | 866962 | 2012-08-11 10:05 | 2012-08-11 10:20 | 15 | 11kV | 10485 | 699 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Interruppter 44797 tripped on fault - tree branch on OH near PT.14539 initially, on restoration a secondary device Recloser 45133 tripped | August | 2012 | 2013Q1 | 2013 | ZN12570:PA16 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2012-08-11 | N | 15 | N | 11 | N | N | 1.1101 | 39.4971 | 7662.1287
[7 empty] | 17626 | 10436 | 861181 | 2012-08-11 09:42 | 2012-08-11 10:24 | 42 | 11kV | 39480 | 940 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 121680 2 Fault Operations Phase C , Overcurrent Weather or Electrical Storm Conductor HV reported down Tree branch stuck in mains Glenelg st x Port Stephens St. Related to OMS 861181 | August | 2012 | 2013Q1 | 2013 | 234:2001 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2012-08-11 | N | 42 | N | 11 | N | N | 1.1101 | 39.4971 | 28850.8195
[7 empty] | 16602 | 660 | 860912 | 2012-08-10 20:54 | 2012-08-11 10:30 | 815.9 | 11kV | 815.9 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | CC1: 06-"Urgent - O.H Mains - No others" | August | 2012 | 2013Q1 | 2013 | ZN2310:PA25 | ZN2310:PA21 | ZN02310/000021 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-08-10 | Y | 815.9 | N | 8 | N | Y | 1.1101 | 39.4971 | 596.2357
[7 empty] | 17139 | 4730 | 862820 | 2012-08-10 18:50 | 2012-08-11 11:15 | 985 | 11kV | 21830 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | LID 121668 2 fault operations single phase Earth fault TREE ON MAINS AT POLE CV-53673 UPPER YANGO. Excluded OMS 860786 | August | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-08-10 | Y | 559.7436 | N | 8 | N | Y | 1.1101 | 39.4971 | 15952.7201
[7 empty] | 16643 | 917 | 861277 | 2012-08-11 11:15 | 2012-08-11 13:10 | 115 | 11kV | 345 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121681 HV DROPPER LEAD BROKEN AT TOP OFF DOLF. | August | 2012 | 2013Q1 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-08-11 | N | 115 | N | 11 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 18357 | 17897 | 861386 | 2012-08-11 13:15 | 2012-08-11 13:50 | 35 | 11kV | 4480 | 128 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 121682 Sub isolated for safety to repair several sevices & LV mains with tree damage. LH & RH Circuits are apparently joined together, please rectify. Excluded OMS No.s 859771 & 861386. | August | 2012 | 2013Q1 | 2013 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2012-08-11 | N | 35 | N | 11 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 17489 | 8685 | 860911 | 2012-08-10 20:51 | 2012-08-11 13:50 | 1019 | 11kV | 4706 | 18 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | Y | LID 121673 2 fault operations single phase Earth fault FAULTY ARRESTOR AT SUB 52825.FOUND WITH BRIDGES IN DOLF REPLACED WITH 10 Amp FUSES. Excluded OMS 860911 | August | 2012 | 2013Q1 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2012-08-10 | Y | 261.4444 | N | 8 | N | Y | 1.1101 | 39.4971 | 3439.006
[7 empty] | 18138 | 16015 | 860765 | 2012-08-10 18:30 | 2012-08-11 14:20 | 1190 | 11kV | 142800 | 120 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 121675 Weather or Electrical storm LV reported down Related to OMS 860765 Sub isolated to make safe LV OHM down. | August | 2012 | 2013Q1 | 2013 | 232:33411 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Not Veg | 2012-08-10 | Y | 1190 | N | 8 | N | Y | 1.1101 | 39.4971 | 104354.0281
[7 empty] | 18298 | 17438 | 860875 | 2012-08-11 07:13 | 2012-08-11 16:30 | 557 | 11kV | 8355 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | LID 121684 Phase A - Fuse size 10 Amp Weather or Electrical Storm Fuses (incorrect operation) related to OMS 861031 | August | 2012 | 2013Q1 | 2013 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2012-08-11 | N | 557 | N | 11 | N | N | 1.1101 | 39.4971 | 6105.5876
[7 empty] | 17218 | 6112 | 861531 | 2012-08-11 16:15 | 2012-08-11 17:40 | 85 | 11kV | 340 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 121685 Repairs to droppers at sub 2755 Weather or Electrical storm excluded OMS 861054 | August | 2012 | 2013Q1 | 2013 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2012-08-11 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 18213 | 16716 | 861658 | 2012-08-11 19:35 | 2012-08-11 20:33 | 58 | 11kV | 94540 | 1630 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LIS 121686 2 fault operations C phase Overcurrent BRANCH ON 11KV OHM POLE IU-92249 Excluded OMS 861658 | August | 2012 | 2013Q1 | 2013 | 218:7482 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | OH | Veg | 2012-08-11 | N | 58 | N | 11 | N | N | 1.1101 | 39.4971 | 69087.0435
[7 empty] | 16563 | 379 | 861723 | 2012-08-11 21:53 | 2012-08-11 23:09 | 76 | 11kV | 56696 | 746 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S.14143 Somersby, Panel 17 Fdr CB tripped on B phase IOC, efi, #2 group earth. | August | 2012 | 2013Q1 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-08-11 | N | 76 | N | 11 | N | N | 1.1101 | 39.4971 | 41431.7646
[7 empty] | 16776 | 1870 | 862800 | 2012-08-12 01:53 | 2012-08-12 03:12 | 79 | 11kV | 25912 | 328 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Recloser 22381 tripped and locked out on IOC. Tree branch on OH near PT.15061 | August | 2012 | 2013Q1 | 2013 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2012-08-12 | N | 79 | N | 3 | N | N | 1.1101 | 39.4971 | 18935.7253
[7 empty] | 18290 | 17365 | 861751 | 2012-08-11 23:59 | 2012-08-12 05:14 | 315.2667 | 11kV | 269379.2667 | 2243 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | At S.36300 Balgowlah North, Panel 3 Fdr CB tripped on earth leakage, efi. Broken cross arm O/S #12 Moore St, Clontarf. HV into LV.Abnormal switching:- At S.17102 Sw 'A' Closed Sw 'B' open. S.17040 Sw B is open - Panel 1 at Manly defective | August | 2012 | 2013Q1 | 2013 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2012-08-11 | N | 120.0978 | N | 11 | N | N | 1.1101 | 39.4971 | 196854.4227
[7 empty] | 17241 | 6420 | 862013 | 2012-08-12 18:07 | 2012-08-12 18:20 | 13 | 11kV | 1534 | 118 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | D.Op interrupted supply to allow the safe removal of tree branch from 11kV O/S #456 Terrigal Drive , Terrigal | August | 2012 | 2013Q1 | 2013 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-08-12 | N | 13 | N | 3 | N | N | 1.1101 | 39.4971 | 1121.002
[7 empty] | 17217 | 6103 | 862019 | 2012-08-12 21:30 | 2012-08-12 23:35 | 125 | 11kV | 1875 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 121692 No protection operation. Fdr isolated to repair 11kV main & replace xarm at pole KR-40115. Excluded OMS 862019 | August | 2012 | 2013Q1 | 2013 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2012-08-12 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 1370.1947
[7 empty] | 17088 | 4323 | 862117 | 2012-08-13 02:13 | 2012-08-13 03:34 | 81 | 11kV | 5844 | 74 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn8000 Macquarie Park panel 20 tripped on IOC, Timed OC EF, EFI Fault Check. Cause: 11kV UG cable fault from S7959 to S7066. See OMS864131 864132 862117 | August | 2012 | 2013Q1 | 2013 | ZN8000:PA20 | ZN8000:PA20 | ZN08000/000020 | RYDE | UG | Not Veg | 2012-08-13 | N | 78.973 | N | 3 | N | N | 1.1101 | 39.4971 | 4270.6228
[7 empty] | 18115 | 15880 | 861576 | 2012-08-11 17:31 | 2012-08-13 15:25 | 2754 | 11kV | 139332 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Rec 1238 Milson Paggage Tripped off. Section of 11kV feeder panel No 11" Brooklyn" Ex S2400 Berowra Zn 11 KV Down, refer to related jobs 861576, 861578, 872889 and 872894 | August | 2012 | 2013Q1 | 2013 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2012-08-11 | N | 2402.2759 | N | 11 | N | N | 1.1101 | 39.4971 | 101819.716
[7 empty] | 17122 | 4578 | 862603 | 2012-08-13 15:43 | 2012-08-13 16:55 | 72 | 11kV | 10800 | 150 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 121698 C phase Feeder was interrupted for emergency repairs as Cph on ABS 74718 was burning up. Excluded oms 862603 | August | 2012 | 2013Q1 | 2013 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2012-08-13 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 7892.3215
[7 empty] | 17917 | 13270 | 862668 | 2012-08-13 17:19 | 2012-08-13 19:00 | 101 | 11kV | 404 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121699 A & B phase DOLF : 10 AMp Excluded OMS 862668 & 862670 | August | 2012 | 2013Q1 | 2013 | 502:48010 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Veg | 2012-08-13 | N | 101 | N | 3 | N | N | 1.1101 | 39.4971 | 295.2313
[7 empty] | 16808 | 2113 | 863366 | 2012-08-14 14:30 | 2012-08-14 14:40 | 10 | 11kV | 30 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121707 3 phase interruption interupted to check if HV fuses or links installed in fuse carrier. | August | 2012 | 2013Q1 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2012-08-14 | N | 10 | N | 1 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 16701 | 1238 | 863266 | 2012-08-15 05:45 | 2012-08-15 07:20 | 95 | 11kV | 5415 | 57 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At PT2218 Linden Way 50A centre phase HVDO operated. Cause: Possum found at the base of pole No apparent damage caused See OMS 864307 864308 863279 863266 | August | 2012 | 2013Q1 | 2013 | ZN3425:PA44 | ZN3425:PA44 | ZN03425/000044 | WILLOUGHBY | OH | Not Veg | 2012-08-15 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 3957.1223
[7 empty] | 18509 | 19963 | 863485 | 2012-08-15 11:14 | 2012-08-15 13:23 | 128.5667 | 11kV | 128.5667 | 1 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | Replaced blown dolf on sub 53322 c phase 10A | August | 2012 | 2013Q1 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-08-15 | N | 128.5667 | N | 5 | N | N | 1.1101 | 39.4971 | 93.9527
[7 empty] | 17894 | 13081 | 863830 | 2012-08-15 12:00 | 2012-08-15 13:40 | 100 | 11kV | 100 | 1 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 121714 Single phase DOLF : 10 Amp Mark Jordan in Singleton issued Job to H Verden. Cause - Possom | August | 2012 | 2013Q1 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-08-15 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 16660 | 999 | 863568 | 2012-08-15 16:15 | 2012-08-15 17:20 | 65 | 11kV | 65 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 121715 Single phase DOLF : 10 Amp | August | 2012 | 2013Q1 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-08-15 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 17159 | 5167 | 863794 | 2012-08-15 21:05 | 2012-08-15 21:50 | 45 | 11kV | 38475 | 855 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15014 Mona Vale, 11kV Panel 22 Fdr CB tripped on A phase IOC, efi, fault check, #1 Tx fault check. Field efi's operated at S.16761, S.16817, S.16695 and S.16699. Possum on HV UG/OH to tee to S.16248 esxcludes OMS 863796 | August | 2012 | 2013Q1 | 2013 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Not Veg | 2012-08-15 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 28116.3952
[7 empty] | 17815 | 12486 | 863808 | 2012-08-16 06:53 | 2012-08-16 07:16 | 23 | 11kV | 61801 | 2687 | HV | Staff Other | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | Panel 12 circuit breaker at S.10999 Kogarah opened via DNMS. Remarks: staff error. Panel 12 at S10999 Kogarah inadvertantly opened while making S/E and Reclose N/A Related jobs: #866567, 866566, 866562, 863808, 863814, 863818, 863820, 863821, 863823 | August | 2012 | 2013Q1 | 2013 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | Unknown | Not Veg | 2012-08-16 | N | 23 | N | 4 | N | N | 1.1101 | 39.4971 | 45162.348
[7 empty] | 16771 | 1786 | 863934 | 2012-08-16 10:06 | 2012-08-16 11:41 | 95 | 11kV | 760 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121720 B phase DOLF : 10 Amp | August | 2012 | 2013Q1 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-08-16 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 555.3856
[7 empty] | 17033 | 3941 | 864199 | 2012-08-16 16:33 | 2012-08-16 17:22 | 49 | 11kV | 517 | 13 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15001 Brookvale, Panel 17 Fdr CB tripped on earth fault, efi, fault check, 11kV trip. UG cable failed between S.15001, S.16316 and S.16629 | August | 2012 | 2013Q1 | 2013 | ZN15001:PA17 | ZN15001:PA2 | ZN15001/000002 | NORTHERN BEACHES | UG | Not Veg | 2012-08-16 | N | 39.7692 | N | 4 | N | N | 1.1101 | 39.4971 | 377.8084
[7 empty] | 18368 | 18079 | 864247 | 2012-08-16 18:27 | 2012-08-16 20:49 | 142 | 11kV | 26975 | 310 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 121721 / 722. 3 Fault operations, A & B phases. Intelliruptor; Overcurrent. Car into pole JP-86504. Pole broken, 4 span HV & LV mains down between poles JP-86502 & JP-86506. Refer: OMS 864348 No protection operations. Section off loaded for switching. Refer: OMS 864347 This section back fed from CE NTWK via 27673 commencing at 20:49 til approx 06:40 then normal supply returned at 06:50 excluded OMS # 864247; 864252; 864266; 864271; 864272; 864283; 864284; 864285; 864286;864298; 864302; | August | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-08-16 | N | 87.0161 | N | 4 | N | N | 1.1101 | 39.4971 | 19712.5344
[7 empty] | 17089 | 4330 | 864296 | 2012-08-17 05:19 | 2012-08-17 07:35 | 136 | 11kV | 136 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At Sub 5509 Stubbs Adderley, ex Panel 20 'Station Par' Feeder from Zn 167 Auburn, The No.2 Tx 'B' phase 11kv fuse has blown Remarks: fuse fatigue. fuse type 75A OEFMA Related jobs: #865535, 864296 | August | 2012 | 2013Q1 | 2013 |  |  |  |  | OH | Not Veg | 2012-08-17 | N | 136 | N | 12 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 17068 | 4178 | 864508 | 2012-08-17 12:16 | 2012-08-17 13:10 | 54 | 11kV | 51516 | 954 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kv Panel 12 'Miller Bil No.1' feeder @ Zn1290 Leightonfield. 11KV Bond has burnt off @ AB 21 Remarks: Burnt Bond @ AB21 Related jobs: #864508, 864559, 865498 | August | 2012 | 2013Q1 | 2013 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-08-17 | N | 54 | N | 12 | N | N | 1.1101 | 39.4971 | 37646.3733
[7 empty] | 17948 | 13615 | 864565 | 2012-08-17 12:49 | 2012-08-17 14:36 | 107 | 11kV | 123050 | 1150 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | At S10990 Arncliffe panel 11 (S.10136 Station Wollongong fdr) tripped, reclosed and locked out. Relays: C phase O/C, Inst and timed O/C, timing, lockout, EFI Signals : 11kv trip Field EFIs: Nil Remarks: 11kv C phase bond on UGOH outside No98 station st on associated section of feeder from S10990 Arncliffe (panel No 11) to S10136 Station Wollongong SW A Related jobs: #865575, 865577, 865580, 864579, 864565, 864574, 864653 | August | 2012 | 2013Q1 | 2013 | ZN10990:PA11 | ZN10998:PA5 | ZN10998/000005 | BAYSIDE | OH | Not Veg | 2012-08-17 | N | 107 | N | 12 | N | N | 1.1101 | 39.4971 | 89921.3106
[7 empty] | 18517 | 20015 | 864513 | 2012-08-17 12:19 | 2012-08-17 14:56 | 157 | 11kV | 2041 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 121744 C phase DOLF : 10 Amp ause not found suspect wind Excluded oms 864513 | August | 2012 | 2013Q1 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-08-17 | N | 157 | N | 12 | N | N | 1.1101 | 39.4971 | 1491.5026
[7 empty] | 18186 | 16458 | 864593 | 2012-08-17 13:19 | 2012-08-17 15:42 | 143 | 11kV | 76170 | 769 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S.3154 St Ives, Panel 12 Fdr CB tripped on C phase OC, timing and 1kV trip. Cause unknown | August | 2012 | 2013Q1 | 2013 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2012-08-17 | N | 99.0507 | N | 12 | N | N | 1.1101 | 39.4971 | 55662.7894
[7 empty] | 18125 | 15931 | 864817 | 2012-08-17 15:34 | 2012-08-17 18:00 | 146 | 11kV | 378 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | AEx Zn12650 West Gosford No1 Dog Trap Rd Feeder Section of 11kV OH found on ground Beyond CP43922. Isolated for safety. CSupply restored via MG's (Protection to investigate SEL did not trip) See OMS 865230 866137 864817 864903 | August | 2012 | 2013Q1 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-08-17 | N | 126 | N | 12 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 16965 | 3344 | 864595 | 2012-08-17 13:23 | 2012-08-17 19:10 | 346.65 | 11kV | 11439.45 | 33 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121748 A phase burnt off tapping on ugoh to sub 71621 CC1: 06-"Urgent - O.H Mains - No others" | August | 2012 | 2013Q1 | 2013 | 813:89063 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2012-08-17 | N | 346.65 | N | 12 | N | N | 1.1101 | 39.4971 | 8359.6127
[7 empty] | 17263 | 6673 | 865744 | 2012-08-17 18:11 | 2012-08-17 19:35 | 84 | 11kV | 1428 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 121749 B & C phase DOLF : 20 Amp 40799 cursory patrol carried out suspect wind | August | 2012 | 2013Q1 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2012-08-17 | N | 84 | N | 12 | N | N | 1.1101 | 39.4971 | 1043.5403
[7 empty] | 16911 | 3005 | 864847 | 2012-08-17 16:38 | 2012-08-17 20:07 | 209 | 11kV | 74259 | 368 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121750 3 fault operations 3 phase Overcurrent branch on 11kV ohm at pole ir 71564 os 13 tocal rd. Dop reports mains look ok but suggests OHM check in daylight. Excluded oms 864847 | August | 2012 | 2013Q1 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2012-08-17 | N | 201.7908 | N | 12 | N | N | 1.1101 | 39.4971 | 54266.2869
[7 empty] | 17862 | 12819 | 864586 | 2012-08-17 13:08 | 2012-08-17 20:37 | 449 | 11kV | 75404 | 238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121752 2 fault operations 3 phase Overcurrent tree brought wires down adj tee to molines sub 52669 Excluded OMS 864586 | August | 2012 | 2013Q1 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2012-08-17 | N | 316.8235 | N | 12 | N | N | 1.1101 | 39.4971 | 55103.0192
[7 empty] | 18554 | 20367 | 864469 | 2012-08-17 11:36 | 2012-08-17 23:30 | 714 | 11kV | 85888 | 526 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Section of 11kV feeder Panel 2 ex Zn12630 Peats Ridge Tripped Rec45189 Cooks Peats Ridge Tripped on overcurrent Wires down vicinity PT13480 Popran Ferry due to High Winds. See OMS 866000 866002 864892 864644 864469 | August | 2012 | 2013Q1 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2012-08-17 | N | 163.2852 | N | 12 | N | N | 1.1101 | 39.4971 | 62764.4171
[7 empty] | 17756 | 11979 | 864963 | 2012-08-18 08:18 | 2012-08-18 10:10 | 111.6333 | 11kV | 9433.3833 | 86 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121756 3 fault operations 3 phase Overcurrent Operator removed tree from mains at pole KR-10086 Excluded OMS # 864963 | August | 2012 | 2013Q1 | 2013 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Veg | 2012-08-18 | N | 109.6905 | N | 9 | N | N | 1.1101 | 39.4971 | 6893.6383
[7 empty] | 17631 | 10547 | 864582 | 2012-08-17 13:07 | 2012-08-18 12:50 | 1423 | 11kV | 65423 | 623 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S35370 Galston Panel 8 Tripped on A and C phase O/C EFI, Reclose Lockout with 11kV Trip. Cause: Large tree came down on 11kV and LV. Both sets of wires down. Section of 11kV Isolated between CP64 and CP65 See OMS 867105 867117 867120 867119 864582 864939 | August | 2012 | 2013Q1 | 2013 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2012-08-17 | N | 105.0128 | N | 12 | N | N | 1.1101 | 39.4971 | 47809.1987
[7 empty] | 16626 | 797 | 865013 | 2012-08-18 10:06 | 2012-08-18 14:45 | 279 | 11kV | 1674 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 121762 LL lead broken off at DOLF Excluded OMS 865013 | August | 2012 | 2013Q1 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-08-18 | N | 279 | N | 9 | N | N | 1.1101 | 39.4971 | 1223.3098
[7 empty] | 17532 | 9017 | 865101 | 2012-08-18 13:17 | 2012-08-18 15:30 | 133 | 11kV | 218240 | 1906 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2473 North Sydney Panel 21 Tripped on Relays: A phase O/C EFI Signals: 11kV trip Field EFI's Cause: Cable fault from S2920 To S4433 to S2336 See OMS 870477 870479 870651 865101 | August | 2012 | 2013Q1 | 2013 | ZN2473:PA21 | ZN35400:PA52 | ZN35400/000052 | NORTH SYDNEY | UG | Not Veg | 2012-08-18 | N | 114.5016 | N | 9 | N | N | 1.1101 | 39.4971 | 159483.355
[7 empty] | 16858 | 2391 | 865006 | 2012-08-18 09:54 | 2012-08-18 16:13 | 379 | 11kV | 484.0667 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 121760 A phase LL lead burnt/broken off at DOLF Excluded OMS 865006 | August | 2012 | 2013Q1 | 2013 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2012-08-18 | N | 242.0333 | N | 9 | N | N | 1.1101 | 39.4971 | 353.7416
[7 empty] | 17330 | 7338 | 865140 | 2012-08-18 15:31 | 2012-08-18 16:28 | 57 | 11kV | 7752 | 136 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | Bond burnt off section panel 20 "Bay St East" fdr Rockdale before tee off to AB 31007 Remarks: Bond off cnr pole of West Botany St and Bay Rd See 870878 Exclude 865140,8 | August | 2012 | 2013Q1 | 2013 | ZN10996:PA20 | ZN10998:PA24 | ZN10998/000024 | BAYSIDE | OH | Not Veg | 2012-08-18 | N | 57 | N | 9 | N | N | 1.1101 | 39.4971 | 5664.933
[7 empty] | 18403 | 18494 | 865203 | 2012-08-18 19:03 | 2012-08-18 19:13 | 10 | 11kV | 11740 | 1174 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 121768 no protection operation, abs 16408 hot joint, feeder opened off at Sw 6420 to make abs 16408 open. Excluded oms # 865203 | August | 2012 | 2013Q1 | 2013 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2012-08-18 | N | 10 | N | 9 | N | N | 1.1101 | 39.4971 | 8579.2457
[7 empty] | 17569 | 9560 | 867207 | 2012-08-18 19:36 | 2012-08-18 20:44 | 68 | 11kV | 81536 | 1399 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | At S187 Crows Nest Panel 7 Feeder Tripped on Relays: Panel 7R B phase IOC, EFI,Fault Check. Panels IT send Signals: 11kV trip Zone Earth Cause: 11kV feeder fault from Panel 7 at S187 Crows Nest to S47880 Albany Oxley No1 ti S6347 Willoughby Lane No2. Note: S1691#2 Was in parallel with panel 7 at the time of interruption See OMS 867207 867225 865217 865221 865231 | August | 2012 | 2013Q1 | 2013 | ZN187:PA7 | ZN187:PA10 | ZN00187/000010 | NORTH SYDNEY | UG | Not Veg | 2012-08-18 | N | 58.2816 | N | 9 | N | N | 1.1101 | 39.4971 | 59584.1039
[7 empty] | 18098 | 15778 | 865225 | 2012-08-18 20:17 | 2012-08-18 21:15 | 58 | 11kV | 3364 | 58 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Section of Panel 13 ex Sub11408 Charmhaven At S11516 Tosca Minnamurra 31.5A roadside HDO blown. Cause: Dead Possum found at base of PT. See OMS 866700 866505 866506 866507 865228/225/230/229 | August | 2012 | 2013Q1 | 2013 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Not Veg | 2012-08-18 | N | 58 | N | 9 | N | N | 1.1101 | 39.4971 | 2458.312
[7 empty] | 17793 | 12353 | 865213 | 2012-08-18 19:20 | 2012-08-19 00:16 | 296 | 11kV | 12533 | 84 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 121770 11kV wire down adj pole IQ 61322 adj sub 50440 Steggles sub. Sect of fdr interupted by aop oms 865213, blown tapping found after restoration necessitatiing longer outage of 2 subs. + OMS No. 865265. 2 damaged tappings repaired Live Line at pole IQ-61318. All restored 0830hrs | August | 2012 | 2013Q1 | 2013 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2012-08-18 | N | 149.2024 | N | 9 | N | N | 1.1101 | 39.4971 | 9158.7467
[7 empty] | 17624 | 10344 | 865257 | 2012-08-19 00:25 | 2012-08-19 04:02 | 217 | 11kV | 125900 | 744 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S3425 Castle Cove Panel 28 Eastern Valley Soutyh Feeder opened and reclosed on C phase IOC - A phase IOC and Timed O/C Relay - Lockout - EFI and Fault Check. Cause: Suspect UGOH or RMI defective at S35197 Parnoo Neerim See OMS 872643/648/651/650 See excluded OMS 865257 | August | 2012 | 2013Q1 | 2013 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | Unknown | Unknown | 2012-08-19 | N | 169.2204 | N | 4 | N | N | 1.1101 | 39.4971 | 92004.0066
[7 empty] | 17198 | 5876 | 865265 | 2012-08-19 02:15 | 2012-08-19 08:30 | 375 | 11kV | 375 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | 2 damaged tappings repaired Live Line at pole IQ-61318. All restored 0830hrs Refer to 865655 customer affected by previous event also = 11 KV wire down at pole IQ61322 | August | 2012 | 2013Q1 | 2013 |  |  |  |  | OH | Not Veg | 2012-08-19 | N | 375 | N | 4 | N | N | 1.1101 | 39.4971 | 274.0389
[7 empty] | 17811 | 12468 | 865379 | 2012-08-19 19:37 | 2012-08-19 20:46 | 68.8667 | 11kV | 275.4667 | 4 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 121772 Single phase DOLF : 10 Amp possum on sub CC1: 22-"Refer to SOp" | August | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2012-08-19 | N | 68.8667 | N | 4 | N | N | 1.1101 | 39.4971 | 201.3029
[7 empty] | 18536 | 20191 | 865395 | 2012-08-19 22:18 | 2012-08-20 00:25 | 127 | 11kV | 635 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121773 C phase DOLF : 10 Amp DOLF Carrier broken. Fuse & carrier replaced. Excluded OMS No.865395. | August | 2012 | 2013Q1 | 2013 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2012-08-19 | N | 127 | N | 4 | N | N | 1.1101 | 39.4971 | 464.0393
[7 empty] | 18117 | 15893 | 865408 | 2012-08-20 07:30 | 2012-08-20 09:32 | 122 | 11kV | 244 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121775 A phase DOLF : 10 AMp Excluded OMS 865408 | August | 2012 | 2013Q1 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-08-20 | N | 122 | N | 3 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 17960 | 13751 | 865691 | 2012-08-20 12:33 | 2012-08-20 13:15 | 42 | 11kV | 420 | 10 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 121780 C phase DOLF : 20 Amp Excluded OMS No. 865691 246V each ph | August | 2012 | 2013Q1 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-08-20 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 17887 | 13018 | 865829 | 2012-08-20 15:19 | 2012-08-20 16:38 | 79 | 11kV | 47972 | 778 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At S.12570 Avoca, Panel 34 Fdr CB tripped, reclosed and locked out on 50TA, A phase IOC, efi, 11kV trip. At PT.13939 the lightning arrestors failed | August | 2012 | 2013Q1 | 2013 | ZN12570:PA15 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2012-08-20 | N | 61.6607 | N | 3 | N | N | 1.1101 | 39.4971 | 35056.5227
[7 empty] | 18559 | 20414 | 865970 | 2012-08-21 06:17 | 2012-08-21 15:45 | 568 | 11kV | 113959 | 1846 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 121782 3 fault operations A & C phase Overcurrent Cable fault near UG/OH Pole IV-31455. | August | 2012 | 2013Q1 | 2013 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | UG | Not Veg | 2012-08-21 | N | 61.7329 | N | 2 | N | N | 1.1101 | 39.4971 | 83277.876
[7 empty] | 17749 | 11941 | 866483 | 2012-08-21 22:33 | 2012-08-22 00:40 | 127 | 11kV | 381 | 3 | HV | 3rd Party Action | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | LID 121797 Vandalism stolen vehicle set alight beside sub 55657 Richie Rd No.2 catching said sub alight as well and destroying it. Excluded oms # 866483 sub 55657 found set on fire | August | 2012 | 2013Q1 | 2013 | 525:34586 | 525:34586 | ZN00525/034586 | CESSNOCK | UG | Not Veg | 2012-08-21 | N | 127 | N | 2 | N | N | 1.1101 | 39.4971 | 278.4236
[7 empty] | 17423 | 8136 | 866859 | 2012-08-22 15:44 | 2012-08-22 16:45 | 61 | 11kV | 50617 | 904 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.14892 Charmhaven Panel 1 Fdr CB tripped and locked out on 50N earth fault, efi, reclosing timing and lockout relays, fault check, Field efi's operated at S.18361, S.18320, S.18105, S.18081, S.14946, S.14899 | August | 2012 | 2013Q1 | 2013 | ZN14892:PA1 | ZN14892:PA1 | ZN14892/000001 | CENTRAL COAST | UG | Not Veg | 2012-08-22 | N | 55.9923 | N | 3 | N | N | 1.1101 | 39.4971 | 36989.4107
[7 empty] | 18300 | 17468 | 866934 | 2012-08-22 20:12 | 2012-08-22 21:18 | 66 | 11kV | 1188 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121811 B phase DOLF : 10 Amp Excluded OMS 866934, 866935 FUSE ELEMENT BROKE VOLTS = 246 AMPS = 15-23-41 | August | 2012 | 2013Q1 | 2013 | 243:80081 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2012-08-22 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 868.1554
[7 empty] | 17758 | 11984 | 866938 | 2012-08-22 21:40 | 2012-08-22 22:55 | 75.4167 | 11kV | 1357.5 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121812 C phase DOLF : 16 Amp Cause not found CC1: 22-"Refer to SOp" | August | 2012 | 2013Q1 | 2013 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | UG | Not Veg | 2012-08-22 | N | 75.4167 | N | 3 | N | N | 1.1101 | 39.4971 | 992.021
[7 empty] | 18383 | 18257 | 867203 | 2012-08-23 12:59 | 2012-08-23 14:00 | 61.0667 | 11kV | 61.0667 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Unplanned | Wind | N | Restored. CC1: 06-"Urgent - O.H Mains - No others" | August | 2012 | 2013Q1 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | Unknown | Unknown | 2012-08-23 | N | 61.0667 | N | 36 | Y | Y | 1.1101 | 39.4971 | 44.6257
[7 empty] | 17178 | 5531 | 867180 | 2012-08-23 12:31 | 2012-08-23 14:11 | 100 | 11kV | 10600 | 106 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Recloser 559 Cobah Tripped on O/C Ex Panel 18 Berowra Waters from CP2400 Berowra Cause not ascertaine for outage CC1: 22-"Refer to SOp" | August | 2012 | 2013Q1 | 2013 | ZN2400:PA18 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2012-08-23 | N | 100 | N | 36 | Y | Y | 1.1101 | 39.4971 | 7746.1674
[7 empty] | 17085 | 4303 | 867232 | 2012-08-23 13:14 | 2012-08-23 14:20 | 66 | 11kV | 39732 | 602 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Recloser CP2749 River Tripped on O/C Weather Related - Cause Not ascertained | August | 2012 | 2013Q1 | 2013 | ZN1193:PA1 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Veg | 2012-08-23 | N | 66 | N | 36 | Y | Y | 1.1101 | 39.4971 | 29034.9737
[7 empty] | 18473 | 19442 | 867243 | 2012-08-23 13:29 | 2012-08-23 14:35 | 66 | 11kV | 112662 | 1707 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @ZN9252 Jannali Pa2 fdr tripped reclosed and locked out on Cph and sealing contactor, reclose timing and lockout relay Remarks-Rival st kareela, removed by mains See 868415 exclude 867243 | August | 2012 | 2013Q1 | 2013 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Veg | 2012-08-23 | N | 66 | N | 36 | Y | Y | 1.1101 | 39.4971 | 82330.0666
[7 empty] | 17892 | 13075 | 867234 | 2012-08-23 14:45 | 2012-08-23 15:11 | 26 | 11kV | 104 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | N | LID 121826 C phase DOLF : 63 Amp Excluded OMS 867278 & 867234 | August | 2012 | 2013Q1 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-08-23 | N | 26 | N | 36 | Y | Y | 1.1101 | 39.4971 | 76.0001
[7 empty] | 16988 | 3464 | 867286 | 2012-08-23 13:45 | 2012-08-23 15:17 | 92 | 11kV | 96692 | 1051 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @Zn10994 Mortdale Pa21 11kv fdr tripped on Alarms-IOC and E/F Refer to related records 867467 and 867286 See 868410 exclude 867286 | August | 2012 | 2013Q1 | 2013 | ZN10994:PA21 | ZN10994:PA21 | ZN10994/000021 | GEORGES RIVER | OH | Veg | 2012-08-23 | N | 92 | N | 36 | Y | Y | 1.1101 | 39.4971 | 70659.6617
[7 empty] | 16720 | 1323 | 867221 | 2012-08-23 13:06 | 2012-08-23 15:58 | 172 | 11kV | 172848 | 1131 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At S1673 Turramurra Panel 18 tripped on A and B phase IOC Signals: 11kV Trip Cause not ascertained for outage . | August | 2012 | 2013Q1 | 2013 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2012-08-23 | N | 152.8276 | N | 36 | Y | Y | 1.1101 | 39.4971 | 126312.2202
[7 empty] | 17555 | 9291 | 867200 | 2012-08-23 12:55 | 2012-08-23 16:00 | 185 | 11kV | 10450 | 252 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 121819 2 fault operations 3 phase Earth fault 11kV wire down cnr Waddells lane x NEH Singleton Excluded OMS 867200; 867211 & 867231 | August | 2012 | 2013Q1 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-08-23 | N | 41.4683 | N | 36 | Y | Y | 1.1101 | 39.4971 | 7636.5518
[7 empty] | 17476 | 8561 | 867435 | 2012-08-23 14:08 | 2012-08-23 16:20 | 132 | 11kV | 8184 | 62 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | At PT1108 Finlay Mawson Footpath Phase 31.5A HV fuse operated Cause: Broken LV cross arm in redgrove ave. See OMS 870385 867984 867435 867395 | August | 2012 | 2013Q1 | 2013 | ZN2635:PA1 | ZN2635:PA43 | ZN02635/000043 | PARRAMATTA | OH | Not Veg | 2012-08-23 | N | 132 | N | 36 | Y | Y | 1.1101 | 39.4971 | 5980.6258
[7 empty] | 17171 | 5311 | 867208 | 2012-08-23 14:00 | 2012-08-23 16:30 | 150 | 11kV | 750 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 121823 C phase DOLF : 20 Amp | August | 2012 | 2013Q1 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2012-08-23 | N | 150 | N | 36 | Y | Y | 1.1101 | 39.4971 | 548.0779
[7 empty] | 18237 | 16941 | 867618 | 2012-08-23 15:06 | 2012-08-23 17:05 | 119.3667 | 11kV | 119.3667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | N | LID 121828 B & C phase DOLF : 10 Amp. | August | 2012 | 2013Q1 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-08-23 | N | 119.3667 | N | 36 | Y | Y | 1.1101 | 39.4971 | 87.2296
[7 empty] | 18089 | 15691 | 867419 | 2012-08-23 14:10 | 2012-08-23 17:06 | 176 | 11kV | 309323 | 2319 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | @Zn10995 Riverwood Pa2 fdr tripped reclosed and locked out on Aph inst/timed oc, reclose time and lockout relay tree/branch on OH Mains near PT10434 removed by mains See 868421,3,5 exclude 867419,845 | August | 2012 | 2013Q1 | 2013 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Veg | 2012-08-23 | N | 133.3864 | N | 36 | Y | Y | 1.1101 | 39.4971 | 226044.1249
[7 empty] | 18165 | 16231 | 867340 | 2012-08-23 13:51 | 2012-08-23 17:24 | 213 | 11kV | 36717 | 341 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Recloser 527 Catherine Paul tripped on IOC, OC and lockout. Tree branch brought down two phase of OH Abnormal Switching: AB436 Closed and AB 1388 Open and defective | August | 2012 | 2013Q1 | 2013 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2012-08-23 | N | 107.6745 | N | 36 | Y | Y | 1.1101 | 39.4971 | 26831.7006
[7 empty] | 17760 | 11995 | 867229 | 2012-08-23 13:41 | 2012-08-23 17:30 | 229 | 11kV | 326493 | 1609 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S1673 Turramurra Panel 11 tripped on Relays: A B and Cphase IOC and reclose Signals: 11kV Trip Cauee: 11kV feeder from AB2538 to AB2226 to AB358 Tee PT1431 Isolated. Large Tree on HV See OMS 871248/251/250/249 876303 867991 | August | 2012 | 2013Q1 | 2013 | ZN1673:PA11 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2012-08-23 | N | 202.9167 | N | 36 | Y | Y | 1.1101 | 39.4971 | 238591.4545
[7 empty] | 17040 | 3970 | 867589 | 2012-08-23 14:54 | 2012-08-23 18:40 | 226 | 11kV | 20668 | 143 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121825 Tree blown onto mains at pole MG-90193. Bph 11kV OHM broke and fell on ground. Sw 43402 Tripped on 3phase OC prot. & reclosed. Sw 43402 Tripped & Locked out on Bph Earth Fault. 11kV into LV. Blew Bph & Cph LVF at forest Road sub 20328. Excluded OMS 867589 | August | 2012 | 2013Q1 | 2013 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2012-08-23 | N | 144.5315 | N | 36 | Y | Y | 1.1101 | 39.4971 | 15103.5648
[7 empty] | 17437 | 8223 | 868347 | 2012-08-23 17:40 | 2012-08-23 18:42 | 62 | 11kV | 3906 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 121831 2 fault operations 3 phase Overcurrent | August | 2012 | 2013Q1 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-08-23 | N | 62 | N | 36 | Y | Y | 1.1101 | 39.4971 | 2854.3896
[7 empty] | 17231 | 6289 | 867487 | 2012-08-23 14:36 | 2012-08-23 19:50 | 314 | 11kV | 282628 | 1234 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Panel 15 Tripped on Relays: B and C phase IOC and E/F Signals: 11kV Trip, Zone Earth, Tx 3 Group Earth. Cause: Tree branch brought down O/H Mains down adjacent PT1668 See OMS 870690/693/695 867487 | August | 2012 | 2013Q1 | 2013 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2012-08-23 | N | 229.034 | N | 36 | Y | Y | 1.1101 | 39.4971 | 206536.2063
[7 empty] | 17362 | 7578 | 867929 | 2012-08-23 17:50 | 2012-08-23 20:05 | 135 | 11kV | 675 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 121835 Single phase | August | 2012 | 2013Q1 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2012-08-23 | N | 135 | N | 36 | Y | Y | 1.1101 | 39.4971 | 493.2701
[7 empty] | 18155 | 16117 | 867960 | 2012-08-23 18:17 | 2012-08-23 20:20 | 123 | 11kV | 80258 | 769 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Zn.12570 Avoca ex Pnl.2 - REC 44982 Bensville has tripped / reclosed / tripped and locked out on OC trip, Lock Out Storm - no cause found see 872625 872627 872624 | August | 2012 | 2013Q1 | 2013 | ZN12570:PA2 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2012-08-23 | N | 104.3667 | N | 36 | Y | Y | 1.1101 | 39.4971 | 58650.1792
[7 empty] | 17419 | 8124 | 867671 | 2012-08-23 15:18 | 2012-08-23 20:35 | 317 | 11kV | 25497 | 233 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Zn12630 Peats Ridge section of 11kV feeder ex Panel 1. recloser CP44995 Kulnurra has tripped on SEL and LO Cause: wires dowb between AB42452 and LB44238 See OMS 868577 868578 867671 | August | 2012 | 2013Q1 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2012-08-23 | N | 109.4292 | N | 36 | Y | Y | 1.1101 | 39.4971 | 18632.4556
[7 empty] | 18123 | 15917 | 867836 | 2012-08-23 20:25 | 2012-08-23 20:43 | 18 | 11kV | 270 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121836 Tree across 11kv OHM at sub 20621 LF 20926 did not blow. Excluded oms 867982, 867836 | August | 2012 | 2013Q1 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-08-23 | N | 18 | N | 36 | Y | Y | 1.1101 | 39.4971 | 197.308
[7 empty] | 17545 | 9137 | 867958 | 2012-08-23 18:16 | 2012-08-23 20:55 | 158.55 | 11kV | 1109.85 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 121855 C phase DOLF : 10 Amp. Volts = 252, 252, 252 CC1: 06-"Urgent - O.H Mains - No others" | August | 2012 | 2013Q1 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2012-08-23 | N | 158.55 | N | 36 | Y | Y | 1.1101 | 39.4971 | 811.0456
[7 empty] | 17552 | 9163 | 868057 | 2012-08-23 20:35 | 2012-08-23 21:15 | 40.1167 | 11kV | 40.1167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 121838 Single phase DOLF : 10 Amp | August | 2012 | 2013Q1 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2012-08-23 | N | 40.1167 | N | 36 | Y | Y | 1.1101 | 39.4971 | 29.3161
[7 empty] | 18303 | 17493 | 867946 | 2012-08-23 18:03 | 2012-08-23 21:25 | 202 | 11kV | 2020 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 121839 A & B phase DOLF : 5 Amp Excluded OMS 867996 | August | 2012 | 2013Q1 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2012-08-23 | N | 202 | N | 36 | Y | Y | 1.1101 | 39.4971 | 1476.1564
[7 empty] | 16986 | 3453 | 867989 | 2012-08-23 18:52 | 2012-08-23 21:30 | 158 | 11kV | 9164 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | No LID report found Opened to clear tree from LV | August | 2012 | 2013Q1 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-08-23 | N | 158 | N | 36 | Y | Y | 1.1101 | 39.4971 | 6696.7809
[7 empty] | 16961 | 3317 | 867332 | 2012-08-23 13:52 | 2012-08-23 21:47 | 475 | 11kV | 353875 | 745 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | recloser CP46113 Fiddens Wharf tripped on O/C Cause: Large Tree removed from 11kV mains near AB241 See OMS 867332/868029 | August | 2012 | 2013Q1 | 2013 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2012-08-23 | N | 475 | N | 36 | Y | Y | 1.1101 | 39.4971 | 258601.4125
[7 empty] | 18496 | 19857 | 867199 | 2012-08-23 12:50 | 2012-08-23 21:50 | 540 | 11kV | 32166 | 192 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Zn12630 Peats Ridge section of 11kV feeder Recloser CP45013 tripped reclosed tripped and locked out Relays: O/C Trip and Lockout At Tee OFf to PT47195 Wise ferry Lavender 5.7 tree brought down 11kV See OMS 868583 868584 868589 868590 868588 867218 867199 | August | 2012 | 2013Q1 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2012-08-23 | N | 167.5312 | N | 36 | Y | Y | 1.1101 | 39.4971 | 23505.9641
[7 empty] | 17822 | 12516 | 867959 | 2012-08-23 18:14 | 2012-08-23 23:00 | 286 | 11kV | 13442 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 121834 1 fault operation Overcurrent | August | 2012 | 2013Q1 | 2013 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2012-08-23 | N | 286 | N | 36 | Y | Y | 1.1101 | 39.4971 | 9823.0171
[7 empty] | 18390 | 18300 | 867919 | 2012-08-23 17:37 | 2012-08-23 23:00 | 323 | 11kV | 12004 | 64 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 121833 1 fault operation mains down 2 span beyond 11kV links 74568 | August | 2012 | 2013Q1 | 2013 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2012-08-23 | N | 187.5625 | N | 36 | Y | Y | 1.1101 | 39.4971 | 8772.1691
[7 empty] | 18029 | 14703 | 867400 | 2012-08-23 14:10 | 2012-08-23 23:30 | 560.4833 | 11kV | 3923.3833 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 121840 HV droper BURNT OFF CC1: 22-"Refer to SOp" | August | 2012 | 2013Q1 | 2013 | 234:2001 | 264:81232 | ZN00264/081232 | MAITLAND | OH | Not Veg | 2012-08-23 | N | 560.4833 | N | 36 | Y | Y | 1.1101 | 39.4971 | 2867.0928
[7 empty] | 16757 | 1683 | 867523 | 2012-08-23 14:35 | 2012-08-23 23:56 | 561 | 11kV | 56100 | 100 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | Ex Panel 25 Chatswood -Bond burnt of At AB2964. See OMS 871223/867523/882/952/969 | August | 2012 | 2013Q1 | 2013 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Not Veg | 2012-08-23 | N | 561 | N | 36 | Y | Y | 1.1101 | 39.4971 | 40996.2253
[7 empty] | 17205 | 5955 | 867236 | 2012-08-23 13:26 | 2012-08-24 01:00 | 694 | 11kV | 40014 | 311 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S14143 Somersby Panel 10 Tripped reclosed tripped and locked out\ Relays: A B and C phase Overcurrent Cause Tree Brough Down 11kV OH mains near PT13019 Mt Penang Pacific See OMS 867236 868567 868569, 873556 and 873557 | August | 2012 | 2013Q1 | 2013 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Veg | 2012-08-23 | N | 128.6624 | N | 36 | Y | Y | 1.1101 | 39.4971 | 29241.051
[7 empty] | 17790 | 12346 | 867509 | 2012-08-23 14:30 | 2012-08-24 01:25 | 654.7 | 11kV | 45829 | 70 | HV | Arcing | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S7262 Ganmain Road. 400A fuse blown on C phase of distributor 2. Cause: Based on customere calls suspect distributor 1 2 and 3 were in parallel at the time of interruption. CR report has Flashover/Arching as trigger of event | August | 2012 | 2013Q1 | 2013 | ZN195:PA11 | ZN195:PA11 | ZN00195/000011 | KU-RING-GAI | OH | Not Veg | 2012-08-23 | N | 654.7 | N | 36 | Y | Y | 1.1101 | 39.4971 | 33490.4815
[7 empty] | 17329 | 7331 | 867289 | 2012-08-23 13:40 | 2012-08-24 01:30 | 710 | 11kV | 160154 | 1452 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S2635 Epping Panel 21 Tripped on Relays: A and C phase IOC, Timed O/C, Fault Check relay and EFI. Large Tree brought down HV and LV mains tee to PT2443. See OMS 870407/409/411 867289 | August | 2012 | 2013Q1 | 2013 | ZN2635:PA21 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Veg | 2012-08-23 | N | 110.2989 | N | 36 | Y | Y | 1.1101 | 39.4971 | 117035.8195
[7 empty] | 18054 | 15386 | 868595 | 2012-08-23 16:38 | 2012-08-24 01:40 | 542 | 11kV | 21070 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Zn14891 Wyong Section of 11kV ex Panel 5 Recloser Cp45016 Dickson has tripped reclosed tripped and locked out on O?C trip and LO Cause: Tree branch brought down OH See OMS 868595 868597 867828 867862 | August | 2012 | 2013Q1 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2012-08-23 | N | 305.3623 | N | 36 | Y | Y | 1.1101 | 39.4971 | 15397.3345
[7 empty] | 17509 | 8880 | 868096 | 2012-08-24 02:24 | 2012-08-24 03:43 | 79 | 11kV | 29467 | 373 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV Panel 12 Wyong Recloser 50630 Yarramalong Chandler 00.1 Tripped . Cause: Tree branch on mains near PT12809 | August | 2012 | 2013Q1 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-08-24 | N | 79 | N | 10 | N | N | 1.1101 | 39.4971 | 21533.6145
[7 empty] | 17691 | 11478 | 868111 | 2012-08-24 05:50 | 2012-08-24 08:42 | 172 | 11kV | 1376 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Rec 47302 Hue Hue Sparks 0.1 interrupted again @ 0709 to effect repairs to bond. Burnt bond near USL 42977 discovered after issues with restoring gas generator (872640). Also see 872636 | August | 2012 | 2013Q1 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2012-08-24 | N | 172 | N | 10 | N | N | 1.1101 | 39.4971 | 1005.5402
[7 empty] | 17937 | 13440 | 868182 | 2012-08-24 08:20 | 2012-08-24 09:15 | 55 | 11kV | 110 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121845 C phase DOLF : 10 Amp | August | 2012 | 2013Q1 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | UG | Not Veg | 2012-08-24 | N | 55 | N | 10 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 18481 | 19576 | 868102 | 2012-08-24 03:57 | 2012-08-24 10:14 | 377 | 11kV | 101826 | 1258 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn195 Pymble Panel 11 Tripped reclosed tripped and locked out on A phase IOC and Timed Abnormal Switching: Zp1370 Closed AB358 Opened. Cause: 11kV feeder from S4143 to S4142 to S4618 to S5340. Cause: See OMS 871336 871337 871888 868102 | August | 2012 | 2013Q1 | 2013 | ZN195:PA11 | ZN195:PA11 | ZN00195/000011 | KU-RING-GAI | UG | Not Veg | 2012-08-24 | N | 80.9428 | N | 10 | N | N | 1.1101 | 39.4971 | 74411.4374
[7 empty] | 16917 | 3031 | 868305 | 2012-08-24 09:58 | 2012-08-24 11:15 | 77.1 | 11kV | 1542 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121849 LOW 11KV MAINS BETWEEN POLES 6L-30011 & 6L-30010. | August | 2012 | 2013Q1 | 2013 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2012-08-24 | N | 77.1 | N | 10 | N | N | 1.1101 | 39.4971 | 1126.8481
[7 empty] | 16774 | 1865 | 868095 | 2012-08-24 02:06 | 2012-08-24 11:41 | 575 | 11kV | 25300 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex West Gosford Zn pnl.1 - REC 44853 Ourimbah Bumble tripped / reclosed / tripped and locked out on OC trip and Lock out Mains down between LB43544to LB 44060 | August | 2012 | 2013Q1 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-08-24 | N | 575 | N | 10 | N | N | 1.1101 | 39.4971 | 18488.4938
[7 empty] | 18226 | 16868 | 870634 | 2012-08-24 14:20 | 2012-08-24 14:35 | 15 | 11kV | 405 | 27 | HV | Arcing | Equipment Failure | Bond | Unplanned | Unselected | N | AB.26215 has arcing bonds. temporary repairs after D.Op interrupted supply to two dc's | August | 2012 | 2013Q1 | 2013 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2012-08-24 | N | 15 | N | 10 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 17657 | 10893 | 867298 | 2012-08-23 13:42 | 2012-08-24 15:40 | 1558 | 11kV | 37319 | 237 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | CP428 ex Bayfield Rd Tripped reclosed tripped and locked out on O/C and EF Abnormal Switching CP554 Open LB406 Closed Cause: Large tree on PT2150 Brought HV into LV - LV mains down. See OMS 87360/609/613 | August | 2012 | 2013Q1 | 2013 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2012-08-23 | N | 157.4641 | N | 36 | Y | Y | 1.1101 | 39.4971 | 27271.6245
[7 empty] | 17334 | 7352 | 868518 | 2012-08-24 04:41 | 2012-08-24 17:47 | 786 | 11kV | 166862 | 465 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Wind | N | At S3425 Castle Cove Panel 28Tripped and reclosed on A B and C phase IOC with Lockout, Timing and EFI. IR49995 Holly Kendal also Tripped (Based on Customer Calls Assumed Locked out) Abnromal Switching: LB1396 and LB62052 Open - LB 62055 Closed (S35197 Parnoo Nerim in LV parallel) Cause: Weather Related + Surge Arrestor Blown at UGOH to S444 Allard Ave. See OMS 872321/322/324/323 868110/113/114/382/126/531/560/580/602 | August | 2012 | 2013Q1 | 2013 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2012-08-24 | N | 358.843 | N | 10 | N | N | 1.1101 | 39.4971 | 121937.828
[7 empty] | 17260 | 6643 | 868633 | 2012-08-24 15:55 | 2012-08-24 20:18 | 263 | 11kV | 167328 | 1175 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 121859 4 fault operations C phase Translay Suspected U/G Cable fault at front end of Feeder. Faulty Transformer 19426, blew up during feeder restoration. CB 6539 (Cap Bank) tripped simultaneously, Cap Bank appears to be damaged due to voltage spike, isolated for work. Excluded OMS No.s 868633, 868638 & 868698. | August | 2012 | 2013Q1 | 2013 | 222:2014 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | UG | Not Veg | 2012-08-24 | N | 142.4068 | N | 10 | N | N | 1.1101 | 39.4971 | 122278.3671
[7 empty] | 17045 | 3991 | 869185 | 2012-08-25 08:45 | 2012-08-25 08:55 | 10 | 11kV | 40 | 4 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | LID 121864 A phase DOLF : 63 Amp replaced incorrect size fuse installed in emergency | August | 2012 | 2013Q1 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-08-25 | N | 10 | N | 5 | N | N | 1.1101 | 39.4971 | 29.2308
[7 empty] | 17715 | 11682 | 868741 | 2012-08-24 20:17 | 2012-08-25 12:19 | 961.65 | 11kV | 8860.1833 | 42 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | Unselected | N | LID 121860 Pillar IR-40033 burnt up. Isolated at SP-IR-40031. C phase 400A LVF 28269 also replaced. | August | 2012 | 2013Q1 | 2013 | 503:48078 | 532:83314 | ZN00532/083314 | MAITLAND | UG | Not Veg | 2012-08-24 | N | 210.9567 | N | 10 | N | N | 1.1101 | 39.4971 | 6474.7606
[7 empty] | 17888 | 13030 | 869190 | 2012-08-25 11:40 | 2012-08-25 13:10 | 90 | 11kV | 90 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121869 ap issued to repair mains from t off to sub 75475 | August | 2012 | 2013Q1 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-08-25 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 18011 | 14329 | 868927 | 2012-08-25 19:36 | 2012-08-25 20:35 | 59 | 11kV | 2006 | 34 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT.11890 the footpath side HV dropper fuse assembly failed. | August | 2012 | 2013Q1 | 2013 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2012-08-25 | N | 59 | N | 5 | N | N | 1.1101 | 39.4971 | 1465.9256
[7 empty] | 17067 | 4173 | 868919 | 2012-08-25 19:35 | 2012-08-25 21:00 | 85 | 11kV | 8415 | 99 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | See interruption 868919 for interruption for Panel 13 @Noraville, Section of 11kV of Panel 13 interrupted to restore supply from Lake Munmorah (Does Not Phase) . Vehicle Hit pole outside 61 Main road Toukley. PT 13145 Main cross 0.5 partly restored via LV// also refer 868919, 868920, 868921, 868923, 868924, 868930, 868931, 868932, 868936 | August | 2012 | 2013Q1 | 2013 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | OH | Not Veg | 2012-08-25 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 6149.4338
[7 empty] | 17112 | 4509 | 868957 | 2012-08-26 08:20 | 2012-08-26 09:50 | 89.8167 | 11kV | 9071.4833 | 101 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121876 C phase DOLF : 40 Amp Fatigue | August | 2012 | 2013Q1 | 2013 | 260:33347 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Not Veg | 2012-08-26 | N | 89.8167 | N | 4 | N | N | 1.1101 | 39.4971 | 6629.1725
[7 empty] | 17000 | 3548 | 869010 | 2012-08-26 12:26 | 2012-08-26 13:15 | 49 | 11kV | 392 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | lid 121878 1 FAULT OPERATION 3 PHASE Overcurrent, Earth fault System was abnormal due to DSI 24578. Sw 18137 Reclose function was OFF due to DSI 24578. | August | 2012 | 2013Q1 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-08-26 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 286.462
[7 empty] | 17759 | 11993 | 869018 | 2012-08-26 13:34 | 2012-08-26 15:30 | 115.8 | 11kV | 6021.6 | 52 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121880 Fuse carrier had worked loose in wind. | August | 2012 | 2013Q1 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-08-26 | N | 115.8 | N | 4 | N | N | 1.1101 | 39.4971 | 4400.4077
[7 empty] | 17168 | 5243 | 869028 | 2012-08-26 14:33 | 2012-08-26 16:34 | 121.4167 | 11kV | 9591.9167 | 79 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | LID 121881 DOLF's left out when restoring supply after switching in area, sub blacked out when interconnictions opened. | August | 2012 | 2013Q1 | 2013 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | UG | Not Veg | 2012-08-26 | N | 121.4167 | N | 4 | N | N | 1.1101 | 39.4971 | 7009.4898
[7 empty] | 16537 | 259 | 870310 | 2012-08-25 09:55 | 2012-08-27 14:00 | 3125 | 11kV | 6250 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121868 3 phase interruption metering point lv cables damaged sub isolated for repairs on 27.8.12 | August | 2012 | 2013Q1 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2012-08-25 | N | 3125 | N | 5 | N | N | 1.1101 | 39.4971 | 4567.3157
[7 empty] | 18364 | 18019 | 870113 | 2012-08-28 17:20 | 2012-08-28 18:30 | 70.3333 | 11kV | 3235.3333 | 46 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At PT.14043, the footpath phase 31.5 amp fuse operated after possum contacted OH mains at PT.14043 | August | 2012 | 2013Q1 | 2013 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2012-08-28 | N | 70.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 2364.2862
[7 empty] | 18040 | 14973 | 870150 | 2012-08-28 19:39 | 2012-08-28 20:32 | 53 | 11kV | 50721 | 957 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn9073 Miranda 11kv Pa2 "Sylvania Heights" Fdr @AB35854 Centre Phase bond burnt off Relays-EFI@Zn9073 EFI's-UGOH Pole Sylvania rd nr Garnet rd Cause: Bond LV// tracking system reports PT9939 Dist 2 fed from PT9593. Link 915 links in. DAROS#283513 See 870270 LV// 870271 Exclude 870150,8,62,66,72,3,4 | August | 2012 | 2013Q1 | 2013 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2012-08-28 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 37065.4108
[7 empty] | 17803 | 12439 | 870186 | 2012-08-28 20:57 | 2012-08-28 21:21 | 24 | 11kV | 28752 | 1198 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 121903 C phase Overcurrent, Earth fault Possum found at pole JU-43957 | August | 2012 | 2013Q1 | 2013 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | OH | Not Veg | 2012-08-28 | N | 24 | N | 4 | N | N | 1.1101 | 39.4971 | 21011.1136
[7 empty] | 16501 | 12 | 870215 | 2012-08-28 21:13 | 2012-08-29 11:00 | 826.8 | 11kV | 5787.6 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Burnt off bond at Link 41502 CC1: 22-"Refer to SOp" | August | 2012 | 2013Q1 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2012-08-28 | N | 826.8 | N | 4 | N | N | 1.1101 | 39.4971 | 4229.4074
[7 empty] | 18003 | 14229 | 870581 | 2012-08-29 20:25 | 2012-08-29 22:30 | 125 | 11kV | 22954.25 | 184 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | S8011 Truscott Batchelor Distributors 1,2,3,4 Phase: ABC Fuse: 400A Remarks: Vehicle hit kiosk. Kiosk housing and LV boards damaged and have to be replaced @ Sub 8011 Truscott batchelor. Supply restored via LV// Related jobs: #870790, 870581, 870584, 870585 CC1: 22-"Refer to SOp" | August | 2012 | 2013Q1 | 2013 | ZN2196:PA5 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | Unknown | Not Veg | 2012-08-29 | N | 124.7514 | N | 3 | N | N | 1.1101 | 39.4971 | 16774.2889
[7 empty] | 16802 | 2070 | 870596 | 2012-08-29 22:46 | 2012-08-30 00:45 | 119 | 11kV | 9296 | 850 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Recloser 49100 Tripped and reclosed on IOC and OVC timing relay. Auto links 46371 tripped cause not ascertained due to gullys and cliffs | August | 2012 | 2013Q1 | 2013 | ZN12660:PA5 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Veg | 2012-08-29 | N | 10.9365 | N | 3 | N | N | 1.1101 | 39.4971 | 6793.2426
[7 empty] | 18267 | 17193 | 870911 | 2012-08-30 01:58 | 2012-08-30 04:00 | 122 | 11kV | 7076 | 58 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 3288 City South 43/44KK feeder tripped on: Relays - 44K Earth Fault, B &C phase IOC Signals: KLM & GHJ Group Earths, Trip Bus "A" 11kv. Abnormal: 43/44M feeder is out of service Remarks: Suspect 11kV UG fault on 43/44K feeder from City South. At Sub 1022 Goulburn & Elizabeth Sts the 44K Network protector did not open. Fuses has blown on NP causing interruption. | August | 2012 | 2013Q1 | 2013 | ZN3288:PA43 44KLM | ZN931:PA1 | ZN00931/000001 | SYDNEY | UG | Not Veg | 2012-08-30 | N | 122 | N | 3 | N | N | 1.1101 | 39.4971 | 5170.9321
[7 empty] | 16882 | 2581 | 870603 | 2012-08-30 01:55 | 2012-08-30 08:10 | 375 | 11kV | 4875 | 13 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Fuse Batch ABB2587 | August | 2012 | 2013Q1 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-08-30 | N | 375 | N | 3 | N | N | 1.1101 | 39.4971 | 3562.5062
[7 empty] | 18104 | 15825 | 870592 | 2012-08-29 21:42 | 2012-08-30 14:00 | 978 | 11kV | 81006 | 126 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 121914 1 fault operation A phase Overcurrent Mains down between 49146 & sub 924. Excluded OMS No 870592 | August | 2012 | 2013Q1 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-08-29 | N | 642.9048 | N | 3 | N | N | 1.1101 | 39.4971 | 59196.7955
[7 empty] | 16717 | 1314 | 865227 | 2012-08-30 17:47 | 2012-08-30 18:00 | 13 | 11kV | 1716 | 132 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | AB.44110 has a high resistance connection on the footpath side | August | 2012 | 2013Q1 | 2013 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2012-08-30 | N | 13 | N | 3 | N | N | 1.1101 | 39.4971 | 1254.0022
[7 empty] | 17175 | 5393 | 871426 | 2012-08-31 16:10 | 2012-08-31 17:25 | 75 | 11kV | 42825 | 571 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 121931 B & C Phase The post insulators at ABS 40258 failed earlier today, it could not be repaired safely using live line procedures. This required an insterruption to remove the cracked insulators and bridge out the air break switch No protection operation. | August | 2012 | 2013Q1 | 2013 | 504:48034 | 522:83129 | ZN00522/083129 | CESSNOCK | OH | Not Veg | 2012-08-31 | N | 75 | N | 2 | N | N | 1.1101 | 39.4971 | 31295.2469
[7 empty] | 18222 | 16822 | 871424 | 2012-08-31 16:30 | 2012-08-31 18:10 | 100 | 11kV | 1500 | 15 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | LID 121932 UGM damaged by civil work Section interrupted to break taps to isolate faulty UGM | August | 2012 | 2013Q1 | 2013 | 264:81240 | 265:81651 | ZN00265/081651 | PORT STEPHENS | UG | Not Veg | 2012-08-31 | N | 100 | N | 2 | N | N | 1.1101 | 39.4971 | 1096.1558
[7 empty] | 17421 | 8130 | 871667 | 2012-09-01 18:36 | 2012-09-01 19:29 | 53 | 11kV | 65083 | 1327 | HV | Arcing | Equipment Failure | O/H Link | Unplanned | Wind | N | Zn.12610 Long Jetty Pnl.22 tripped, reclosed and locked out on E/F & C phase IOC, Lock Out Abnormal Switching: AB40271 Open & Defective - AB40376 Closed USL 40764 was arcing, sparking and glowing then flashed over see 872184 872185 | September | 2012 | 2013Q1 | 2013 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Not Veg | 2012-09-01 | N | 49.0452 | N | 4 | N | N | 1.1101 | 39.4971 | 47560.7368
[7 empty] | 18224 | 16863 | 871668 | 2012-09-01 18:18 | 2012-09-01 19:40 | 82 | 11kV | 49974 | 681 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn3155 Double Bay Pa16 11kv fdr tripped Relays: EF, FC and EFI Signals:Ze, No1TxGe, 11kvtrip and battery defect EFI: Nil Cause: Ug Fault Remarks: Fault between S2214 Sw/A and S36083 Sw/A See 872000,1,3 Exclude 871668,71 | September | 2012 | 2013Q1 | 2013 | ZN3155:PA16 | ZN3155:PA16 | ZN03155/000016 | WOOLLAHRA | UG | Not Veg | 2012-09-01 | N | 73.3833 | N | 4 | N | N | 1.1101 | 39.4971 | 36519.5252
[7 empty] | 17015 | 3729 | 871675 | 2012-09-01 18:48 | 2012-09-01 23:35 | 287 | 11kV | 287 | 1 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121937 A phase DOLF : 31 Amp Excluded OMS 871675 Volts 250 | September | 2012 | 2013Q1 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2012-09-01 | N | 287 | N | 4 | N | N | 1.1101 | 39.4971 | 209.7311
[7 empty] | 18158 | 16131 | 871514 | 2012-09-01 23:20 | 2012-09-02 00:15 | 55 | 11kV | 2695 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121933 A phase DOLF : 31 Amp excluded oms 871514, 871516, 871517 | September | 2012 | 2013Q1 | 2013 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2012-09-01 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 1969.4265
[7 empty] | 18527 | 20096 | 871836 | 2012-09-03 01:33 | 2012-09-03 04:30 | 177 | 11kV | 19824 | 112 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | At PT458 Welby St 11kV Middle Phase HV fuse blown Cause: Centre phase fuse fallen apart. See OMS 875083 871838 871836 | September | 2012 | 2013Q1 | 2013 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Not Veg | 2012-09-03 | N | 177 | N | 4 | N | N | 1.1101 | 39.4971 | 14486.7945
[7 empty] | 17207 | 5993 | 871917 | 2012-09-03 09:10 | 2012-09-03 10:50 | 99.8333 | 11kV | 8785.3333 | 88 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121939 A phase DOLF : 20 Amp Fuse carrier broke due to fatigue. TX volts: Aph - 250V, Bph - 247V, Cph - 250V TX load: Aph - 20A, Bph - 50A, Cph - 10A | September | 2012 | 2013Q1 | 2013 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2012-09-03 | N | 99.8333 | N | 4 | N | N | 1.1101 | 39.4971 | 6420.0625
[7 empty] | 17100 | 4406 | 872410 | 2012-09-03 16:20 | 2012-09-03 16:30 | 10 | 11kV | 10 | 1 | HV | Staff Other | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | LID 121943 3 phase interruption No OMS number, Paul Morgan advised we were supplying greater than 260 volts per phase due to a recent tap change during work on the transformer. Tap changed to tap 1 at 11495 Volts. Open circuit volts are now 243 Volts. No protection operated. | September | 2012 | 2013Q1 | 2013 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | UG | Not Veg | 2012-09-03 | N | 10 | N | 4 | N | N | 1.1101 | 39.4971 | 7.3077
[7 empty] | 17338 | 7368 | 872240 | 2012-09-03 16:06 | 2012-09-03 23:30 | 444 | 11kV | 218694 | 1722 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 121945 1 fault operation Sensitive Earth Fault Car hit Pole HW-70718. Pole replaced. Excluded OMS Job No. 872233. | September | 2012 | 2013Q1 | 2013 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2012-09-03 | N | 127 | N | 4 | N | N | 1.1101 | 39.4971 | 159815.1248
[7 empty] | 17390 | 7883 | 872503 | 2012-09-04 11:11 | 2012-09-04 13:55 | 164 | 11kV | 164 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 121955 Excluded OMS No. 872503 Fuse carrier burnt up. tap change carried out to reduce no load volts from 257 to 245 | September | 2012 | 2013Q1 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2012-09-04 | N | 164 | N | 4 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 16983 | 3448 | 872838 | 2012-09-04 18:10 | 2012-09-04 19:00 | 50 | 11kV | 750 | 15 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | LID 121960 See Report 121932/ OMS 871850 Subs interrupted to restore repaired cable. | September | 2012 | 2013Q1 | 2013 | 264:81240 | 265:81651 | ZN00265/081651 | PORT STEPHENS | UG | Not Veg | 2012-09-04 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 548.0779
[7 empty] | 17850 | 12723 | 872694 | 2012-09-04 15:50 | 2012-09-04 19:31 | 221 | 11kV | 85088 | 827 | HV | Excavation 3rd Party | 3rd Party Impact | 3rd Party Asset | Unplanned | Unselected | N | LID 121957 gas mains dug up by excavator causing large fire and lv mains to fall section isolated so fire brigade could dowse flames AP issued to repair 11kv mains | September | 2012 | 2013Q1 | 2013 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | UG | Not Veg | 2012-09-04 | N | 102.8875 | N | 4 | N | N | 1.1101 | 39.4971 | 62179.8007
[7 empty] | 16572 | 487 | 872770 | 2012-09-04 18:43 | 2012-09-04 20:08 | 84.55 | 11kV | 8125.2833 | 107 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121961 A phase DOLF : 40 Amp volts 253/ph load 196, 188, 118 | September | 2012 | 2013Q1 | 2013 | 503:48016 | 532:83314 | ZN00532/083314 | MAITLAND | UG | Not Veg | 2012-09-04 | N | 75.9372 | N | 4 | N | N | 1.1101 | 39.4971 | 5937.7174
[7 empty] | 16763 | 1730 | 872810 | 2012-09-05 01:44 | 2012-09-05 02:20 | 36 | 11kV | 2052 | 57 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At PT2475 Dalrymply Moola - Roadside 31.5A HVDO fuse operated Possum on OH. See OMS 875075 872810 | September | 2012 | 2013Q1 | 2013 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | WILLOUGHBY | OH | Not Veg | 2012-09-05 | N | 36 | N | 11 | N | N | 1.1101 | 39.4971 | 1499.5411
[7 empty] | 16868 | 2453 | 872991 | 2012-09-05 11:15 | 2012-09-05 12:24 | 69 | 11kV | 104121 | 1509 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121966 remove tree branch at pole GW-50003 Martinsville Rd Cooranbong. Excluded OMS 872991 | September | 2012 | 2013Q1 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-09-05 | N | 69 | N | 11 | N | N | 1.1101 | 39.4971 | 76088.5558
[7 empty] | 18434 | 18959 | 873434 | 2012-09-05 12:25 | 2012-09-05 12:43 | 18 | 11kV | 18 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 121967 High sub volts reported, tap changed. 258V down to 245V. | September | 2012 | 2013Q1 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-09-05 | N | 18 | N | 11 | N | N | 1.1101 | 39.4971 | 13.1539
[7 empty] | 18025 | 14616 | 873127 | 2012-09-05 14:29 | 2012-09-05 15:00 | 30.6833 | 11kV | 3191.0667 | 104 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | LID 121971 dolfs open on sub 50660 Gillies on SI 24793 for live line not restored on RSI 24793 | September | 2012 | 2013Q1 | 2013 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | UG | Not Veg | 2012-09-05 | N | 30.6833 | N | 11 | N | N | 1.1101 | 39.4971 | 2331.9374
[7 empty] | 17019 | 3809 | 873103 | 2012-09-05 13:54 | 2012-09-05 15:15 | 81 | 11kV | 63627 | 1074 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12620 Noraville pnl.10 tripped on B + C phase OC Tree branch on mains outside 6 Sonoma Rd Budgewoi. see 874797 874796 | September | 2012 | 2013Q1 | 2013 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Veg | 2012-09-05 | N | 59.243 | N | 11 | N | N | 1.1101 | 39.4971 | 46496.7349
[7 empty] | 18068 | 15481 | 873035 | 2012-09-05 12:27 | 2012-09-05 16:50 | 263 | 11kV | 1052 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 121976 B Phase DOLF : 20 Amp Excluded OMS 873035 10 A SUB FUSE ALSO REPLACED | September | 2012 | 2013Q1 | 2013 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2012-09-05 | N | 263 | N | 11 | N | N | 1.1101 | 39.4971 | 768.7706
[7 empty] | 17135 | 4692 | 873110 | 2012-09-05 13:58 | 2012-09-05 18:20 | 262 | 11kV | 15343 | 66 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 121977 1 fault operation single phase Overcurrent RECLOSE WAS OFF FOR S1 23906 Excluded OMS 873110 | September | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-09-05 | N | 232.4697 | N | 11 | N | N | 1.1101 | 39.4971 | 11212.2119
[7 empty] | 16512 | 82 | 873278 | 2012-09-05 19:13 | 2012-09-05 20:52 | 99 | 11kV | 60124 | 663 | HV | Animal Bird | Animal | Air Break Switch | Unplanned | Unselected | N | LID 121979 1 fault operation 3 phase Earth fault DEAD BIRD FOUND AT BASE OF ABS 4644 Excluded OMS 873278 | September | 2012 | 2013Q1 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-09-05 | N | 90.6848 | N | 11 | N | N | 1.1101 | 39.4971 | 43936.8458
[7 empty] | 17654 | 10837 | 873290 | 2012-09-05 20:25 | 2012-09-06 00:52 | 267 | 11kV | 10417 | 71 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12630 Peats Ridge Pnl.1 - REC 44994 mangrove Creek tripped / reclosed and locked out on OC Tree outside 650 Kyola Rd fell on mains. see 874799 874800 | September | 2012 | 2013Q1 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2012-09-05 | N | 146.7183 | N | 11 | N | N | 1.1101 | 39.4971 | 7612.4364
[7 empty] | 17323 | 7283 | 873301 | 2012-09-05 23:16 | 2012-09-06 01:03 | 107 | 11kV | 97756 | 950 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3154 St Ives, Panel 16 Fdr CB tripped on B phase OC and earth fault, Zone earth, 11kV trip. Field efi's down at S.7413, S.7414, S.4621, S.4791, S.477 and S.464 Section of 11kV UG cable defective between S.464 and S.465 | September | 2012 | 2013Q1 | 2013 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | UG | Not Veg | 2012-09-05 | N | 102.9011 | N | 11 | N | N | 1.1101 | 39.4971 | 71437.2015
[7 empty] | 18463 | 19197 | 873147 | 2012-09-05 14:48 | 2012-09-06 03:00 | 732 | 11kV | 43636 | 233 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Wind | N | LID 121981 Carrington prot: C-phase OC & timed earth fault. PWC loader prot: C-phase directional OC. 11kV failure at Darling Street sub 28182. Excluded OMS Job Nos. 873147 & 873245. | September | 2012 | 2013Q1 | 2013 | 203:8089 | 204:82703 | ZN00204/082703 | NEWCASTLE | UG | Not Veg | 2012-09-05 | N | 187.279 | N | 11 | N | N | 1.1101 | 39.4971 | 31887.9018
[7 empty] | 16676 | 1100 | 873310 | 2012-09-06 05:03 | 2012-09-06 07:10 | 126.9 | 11kV | 8756.1 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 121985 C phase DOLF : 40 Amp. Reading as left 150A, 28A, 66A @ 249V. OMS 873310 | September | 2012 | 2013Q1 | 2013 | 220:8687 | 220:8687 | ZN00220/008687 | LAKE MACQUARIE | UG | Not Veg | 2012-09-06 | N | 126.9 | N | 13 | N | N | 1.1101 | 39.4971 | 6398.6996
[7 empty] | 17458 | 8384 | 873307 | 2012-09-06 04:35 | 2012-09-06 08:00 | 205 | 11kV | 90294 | 1291 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At Zn129 Hunters Hill Panel 12 Tripped on C phase sealing end contactor, EFI, Frame leakage and fault check. Cause: Possum on 11kV UGOH O/S No7 Garling St Lane Cove. See OMS 875527/530/531 873307/308 | September | 2012 | 2013Q1 | 2013 | ZN129:PA12 | ZN129:PA56 | ZN00129/000056 | LANE COVE | OH | Not Veg | 2012-09-06 | N | 69.9411 | N | 13 | N | N | 1.1101 | 39.4971 | 65984.192
[7 empty] | 16672 | 1079 | 873410 | 2012-09-06 10:30 | 2012-09-06 10:45 | 15 | 11kV | 915 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | N | LID 121992 C phase DOLF : 31 Amp Excluded OMS 873410 | September | 2012 | 2013Q1 | 2013 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | UG | Not Veg | 2012-09-06 | N | 15 | N | 13 | N | N | 1.1101 | 39.4971 | 668.655
[7 empty] | 16588 | 567 | 875168 | 2012-09-06 10:30 | 2012-09-06 12:35 | 125 | 11kV | 125 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 121996 Broken LLC dropper | September | 2012 | 2013Q1 | 2013 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2012-09-06 | N | 125 | N | 13 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 16920 | 3041 | 873449 | 2012-09-06 10:21 | 2012-09-06 12:45 | 144 | 11kV | 432 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 121998 No protection operation, broken 11kV tapping to DOLF 16844. Excluded oms 873449 | September | 2012 | 2013Q1 | 2013 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | OH | Not Veg | 2012-09-06 | N | 144 | N | 13 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 17380 | 7740 | 873303 | 2012-09-06 01:50 | 2012-09-06 14:18 | 748 | 11kV | 25731 | 133 | HV | Fire (non-electrical) | Adverse Weather/Environment | Pole | Unplanned | Unselected | N | LID 121984 3 phase interruption No protection operations. Feeder isolated to extinguish fire in tree adjacent pole AF-30047. Tree requires urgent trimming - touching mains in wind Excluded OMS # 873305 & 873303 | September | 2012 | 2013Q1 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2012-09-06 | N | 193.4662 | N | 13 | N | N | 1.1101 | 39.4971 | 18803.4559
[7 empty] | 17316 | 7218 | 873497 | 2012-09-06 11:30 | 2012-09-06 14:32 | 182 | 11kV | 2002 | 11 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 122001 No protection operation. 11kV main on xarm pole KQ-40077 & broken ties pole KQ-40078. | September | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-09-06 | N | 182 | N | 13 | N | N | 1.1101 | 39.4971 | 1463.0026
[7 empty] | 17700 | 11519 | 873355 | 2012-09-06 08:33 | 2012-09-06 14:34 | 361 | 11kV | 54518 | 342 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 121986 3 fault operations C phase Instantaneous Overcurrent | September | 2012 | 2013Q1 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-09-06 | N | 159.4094 | N | 13 | N | N | 1.1101 | 39.4971 | 39840.1464
[7 empty] | 18557 | 20393 | 874809 | 2012-09-06 11:30 | 2012-09-06 15:13 | 223 | 11kV | 4237 | 19 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 121997 This sub was isolated as its LV feeds into the access permit area requied to remove trees from Pole GW-90366. See unplanned report 121986. Excluded OMS 873355. | September | 2012 | 2013Q1 | 2013 | 243:80081 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2012-09-06 | N | 223 | N | 13 | N | N | 1.1101 | 39.4971 | 3096.2746
[7 empty] | 17788 | 12335 | 873707 | 2012-09-06 16:20 | 2012-09-06 18:50 | 150 | 11kV | 600 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122003 B & C Phase switch fuses : 25 Amp sub interconnected from LVF 38414. Excluded OMS 873722 | September | 2012 | 2013Q1 | 2013 | 513:48058 | 513:83504 | ZN00513/083504 | SINGLETON | UG | Not Veg | 2012-09-06 | N | 150 | N | 13 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 16573 | 488 | 873656 | 2012-09-06 14:54 | 2012-09-06 23:59 | 545 | 11kV | 545 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 122006 A phase LL Clamp off in wind. Excluded oms-873656 | September | 2012 | 2013Q1 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-09-06 | N | 545 | N | 13 | N | N | 1.1101 | 39.4971 | 398.2699
[7 empty] | 17830 | 12544 | 876217 | 2012-09-06 23:12 | 2012-09-07 00:48 | 96 | 11kV | 80352 | 837 | HV | Animal Possum | Animal | Bond | Unplanned | Unselected | N | LID 122005 Sw 34260 opened by SOp. 11kV tapping off at pole KU-41168 affecting 5 subs. | September | 2012 | 2013Q1 | 2013 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2012-09-06 | N | 96 | N | 13 | N | N | 1.1101 | 39.4971 | 58718.8716
[7 empty] | 17453 | 8352 | 873810 | 2012-09-06 20:50 | 2012-09-07 02:34 | 344 | 11kV | 192825 | 2430 | HV | Animal Possum | Animal | Bond | Unplanned | Unselected | N | LID 122004 1 fault operation Overcurrent, Earth fault I-E, TI ABC. Dead possum found on HV. 3 x 11kV taps blown at UGOH pole JU-61270. | September | 2012 | 2013Q1 | 2013 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2012-09-06 | N | 79.3519 | N | 13 | N | N | 1.1101 | 39.4971 | 140910.8226
[7 empty] | 16904 | 2922 | 873850 | 2012-09-07 05:54 | 2012-09-07 07:40 | 105.7833 | 11kV | 7193.2667 | 68 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11994 Kalua Aloha - Centre Phase 16K HDO fuse fatigued CC1: 22-"Refer to SOp" | September | 2012 | 2013Q1 | 2013 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2012-09-07 | N | 105.7833 | N | 15 | N | N | 1.1101 | 39.4971 | 5256.6271
[7 empty] | 17213 | 6064 | 873836 | 2012-09-07 04:05 | 2012-09-07 08:25 | 260 | 11kV | 161831 | 1350 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 122007 1 fault operation c phase Earth fault, Overcurrent HV into LV neutral at pole IV-21639 caused by possum. | September | 2012 | 2013Q1 | 2013 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2012-09-07 | N | 119.8748 | N | 15 | N | N | 1.1101 | 39.4971 | 118261.3216
[7 empty] | 17847 | 12682 | 874903 | 2012-09-07 10:38 | 2012-09-07 11:20 | 42 | 11kV | 42 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 122012 A phase DOLF : 20 Amp Broken fuse carrier replaced. Readings as left 40A, 46A, 54A @ 245V. | September | 2012 | 2013Q1 | 2013 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2012-09-07 | N | 42 | N | 15 | N | N | 1.1101 | 39.4971 | 30.6924
[7 empty] | 17520 | 8965 | 874167 | 2012-09-07 14:13 | 2012-09-07 15:50 | 97 | 11kV | 22698 | 234 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | AT S.15013 TERREY HILLS,PANEL 6 FDR CB TRIPPED, RECLOSED AND TRIPPED, LOCKED OUT ON A AND CPHASE IOC AND TIMED OC, LOCKOUT RELAY AND TIMIMG 11kV TRIP. NO FIELD EFI'S. TREES IN LAROOL ST AND AUMUNA ST. ABNORMAL SWITCHING LB.25194 CLOSED AND AB.26217 | September | 2012 | 2013Q1 | 2013 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2012-09-07 | N | 97 | N | 15 | N | N | 1.1101 | 39.4971 | 16587.0289
[7 empty] | 18139 | 16018 | 874264 | 2012-09-07 15:31 | 2012-09-07 16:04 | 33 | 11kV | 42636 | 1292 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122017 A & B phase Overcurrent tree branch on mains at pole IV-50308 Tallawalla Rd removed and fdr restored Excluded OMS 874264 | September | 2012 | 2013Q1 | 2013 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2012-09-07 | N | 33 | N | 15 | N | N | 1.1101 | 39.4971 | 31157.1313
[7 empty] | 17620 | 10325 | 874164 | 2012-09-07 14:14 | 2012-09-07 16:05 | 111 | 11kV | 38244 | 525 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zb.14891 Wyong Pnl.21 tripped on 51n Fault Check operation (basler) 11kv OH mains betwwen AB41445 and USL41291 had come away frm pin insulator on pole and landed on ground causing fault. see 874966 874969 | September | 2012 | 2013Q1 | 2013 | ZN14891:PA21 | ZN14891:PA17 | ZN14891/000017 | CENTRAL COAST | OH | Not Veg | 2012-09-07 | N | 72.8457 | N | 15 | N | N | 1.1101 | 39.4971 | 27947.5872
[7 empty] | 17084 | 4294 | 874200 | 2012-09-07 14:38 | 2012-09-07 16:20 | 101.75 | 11kV | 1831.5 | 18 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | PT1797 Lockinvar Rosemount 400A fuse blown on B phase of distributor 2. Cause: LV mains in Locinvar Place 1 Span west of PT1797 are clasing together in strong winds. Mains to re tension and add spreader bar to mains. | September | 2012 | 2013Q1 | 2013 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Not Veg | 2012-09-07 | N | 101.75 | N | 15 | N | N | 1.1101 | 39.4971 | 1338.4062
[7 empty] | 18334 | 17755 | 874127 | 2012-09-07 13:49 | 2012-09-07 16:46 | 177 | 11kV | 56109 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122015 2 fault operations Earth fault, Sw 13793 OP/CL/OP tree branch pole GV-70215 NEAR SUB 9909, cleared by DOP Excluded OMS 874127, 874153 | September | 2012 | 2013Q1 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-09-07 | N | 177 | N | 15 | N | N | 1.1101 | 39.4971 | 41002.8023
[7 empty] | 17580 | 9660 | 874110 | 2012-09-07 13:42 | 2012-09-07 17:55 | 253 | 11kV | 146896 | 1027 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 122021 2 fault operations B phase Earth fault 11KV MAINS DOWN TO SUB 52273 THOMAS ST GILLESTON HTS.11KV MAINS INTO LV MAINS .PREMISES INSPECTED BY ON CALL STAFF. Excluded OMS 874110, 874142 & 874219 | September | 2012 | 2013Q1 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2012-09-07 | N | 143.0341 | N | 15 | N | N | 1.1101 | 39.4971 | 107347.2641
[7 empty] | 18091 | 15720 | 874377 | 2012-09-07 17:39 | 2012-09-07 19:12 | 92.3667 | 11kV | 92.3667 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | OK on arrival - no further infromation available | September | 2012 | 2013Q1 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-09-07 | N | 92.3667 | N | 15 | N | N | 1.1101 | 39.4971 | 67.4988
[7 empty] | 16586 | 561 | 874254 | 2012-09-07 15:22 | 2012-09-07 20:05 | 283 | 11kV | 11886 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122022 B phase DOLF : 15 Amp excluded OMS 874254 | September | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-09-07 | N | 283 | N | 15 | N | N | 1.1101 | 39.4971 | 8685.9382
[7 empty] | 16980 | 3419 | 874358 | 2012-09-07 17:20 | 2012-09-07 20:37 | 197 | 11kV | 310506 | 2094 | HV | Animal Possum | Animal | UGOH | Unplanned | Wind | N | At S.15008 Harbord, Panel 9 Fdr CB tripped, reclosed and tripped on A and C phase OC, lockout and timing relays, 11kv TRIP, BATTERY DEFECTField efi's nil. UG/OH to S.16026 reported dead possum | September | 2012 | 2013Q1 | 2013 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2012-09-07 | N | 148.2837 | N | 15 | N | N | 1.1101 | 39.4971 | 226908.6264
[7 empty] | 18181 | 16429 | 874442 | 2012-09-07 21:05 | 2012-09-07 22:30 | 85 | 11kV | 170 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 122023 A phase DOLF : 10 Amp Excluded OMS 874442 Protection Equipment Fuses (incorrect operation). oms-874442 | September | 2012 | 2013Q1 | 2013 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2012-09-07 | N | 85 | N | 15 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 18204 | 16644 | 874378 | 2012-09-07 23:29 | 2012-09-07 23:43 | 14 | 11kV | 2534 | 181 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | AEx Zn 2400 Berowra Panel 18 LB 62018 Was opened for safety to remove tree resting against CCT near LB62108 See OMS 874457 874378 | September | 2012 | 2013Q1 | 2013 | ZN2400:PA18 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2012-09-07 | N | 14 | N | 15 | N | N | 1.1101 | 39.4971 | 1851.7725
[7 empty] | 18239 | 16981 | 874434 | 2012-09-07 19:50 | 2012-09-08 11:00 | 910 | 11kV | 910 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122025 A phase LLC connecting subs 70419 and 70420 to the main line has worked loose and fallen away. No protection operated. Excluded OMS # 874434. | September | 2012 | 2013Q1 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-09-07 | N | 910 | N | 15 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 17117 | 4544 | 874507 | 2012-09-08 09:32 | 2012-09-08 12:30 | 178 | 11kV | 178 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122026 A phase dropper Live line lead ahd becoem detached. Excluded OMS 874507 | September | 2012 | 2013Q1 | 2013 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2012-09-08 | N | 178 | N | 1 | N | N | 1.1101 | 39.4971 | 130.0771
[7 empty] | 17177 | 5522 | 874760 | 2012-09-09 19:49 | 2012-09-09 20:55 | 66 | 11kV | 1584 | 24 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 122036 B phase DOLF : 20 Amp ELEMENT FATIGUE. VOLTS = 241. Excluded OMS REPORT NO 874760 | September | 2012 | 2013Q1 | 2013 | 813:89063 | 813:89065 | ZN00813/089065 | UPPER HUNTER | OH | Not Veg | 2012-09-09 | N | 66 | N | 1 | N | N | 1.1101 | 39.4971 | 1157.5405
[7 empty] | 18542 | 20271 | 874786 | 2012-09-10 01:52 | 2012-09-10 03:01 | 69 | 11kV | 10143 | 147 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn901 Surry Hills 11kv fdr Pa2 "Regent Queen etc" fdr tripped on Relays: E/F EFI EFI's: Nil Remarks: UG cable fault in section of 11kv fdr from Zn901 Surry Hills to S8413 Sw/A to S8958 Sw/A to S112 Sw/D See 875422 exclude 874786 | September | 2012 | 2013Q1 | 2013 | ZN901:PA2 | ZN901:PA2 | ZN00901/000002 | SYDNEY | UG | Not Veg | 2012-09-10 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 7412.2052
[7 empty] | 18194 | 16560 | 875440 | 2012-09-10 18:45 | 2012-09-10 19:54 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122047 C phase DOLF : 10 Amp | September | 2012 | 2013Q1 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2012-09-10 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 18435 | 18961 | 875273 | 2012-09-10 17:56 | 2012-09-10 21:30 | 214 | 11kV | 159495 | 1091 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S187 Crows Nest Panel 13 Tripped on Panel 13L EF, Tripped on Relays: Panel 13L, EF, TRIP LED, EFI, Fault Check. Signals: 11kV Trip and Zone Earth Cause: 11kV cable Fault. Based on Customer calls suspect S8448#2 and S8420#2 were in parallel with panel 13 at the time of interruption See OMS 875595/599/600 875661 875271 | September | 2012 | 2013Q1 | 2013 | ZN187:PA13 | ZN187:PA13 | ZN00187/000013 | NORTH SYDNEY | UG | Not Veg | 2012-09-10 | N | 146.1916 | N | 3 | N | N | 1.1101 | 39.4971 | 116554.2417
[7 empty] | 17483 | 8626 | 875634 | 2012-09-11 14:09 | 2012-09-11 15:58 | 109 | 11kV | 172724 | 1772 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn9245 Engadine Pa10 tripped on Aph IOC EFI EFI-S9007 Cuase: Not ascertained Remarks: Tree trimmers working mountain rd area would not admit fault Custs (address 37 & 38 Engadine Ave Engadine) report Branch on Dist Wires See 875890,2,3 Exclude 875634,7,42,63 | September | 2012 | 2013Q1 | 2013 | ZN9245:PA10 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Veg | 2012-09-11 | N | 97.474 | N | 3 | N | N | 1.1101 | 39.4971 | 126221.6047
[7 empty] | 16773 | 1860 | 875726 | 2012-09-11 17:31 | 2012-09-11 19:40 | 129 | 11kV | 44767 | 409 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.14891 Wyong Pnl.14 tripped on SEF, EFI Cause not ascertained see 876783 876784 876785 | September | 2012 | 2013Q1 | 2013 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Veg | 2012-09-11 | N | 109.4548 | N | 3 | N | N | 1.1101 | 39.4971 | 32714.4032
[7 empty] | 18524 | 20074 | 875745 | 2012-09-11 20:15 | 2012-09-11 21:20 | 65 | 11kV | 1560 | 24 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122065 section isolated for repairs at sub 27616 | September | 2012 | 2013Q1 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-09-11 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 1140.002
[7 empty] | 17889 | 13038 | 875784 | 2012-09-12 05:14 | 2012-09-12 09:05 | 231 | 11kV | 203095 | 2255 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.14892 Charmhaven Pnl.21 tripped on Earth Fault, Overcurrent, Fault Check Underground feeder fault between S.14584 to CP44585 to LB44068 tee PT14001 P3 failed while attempting to restore p21 # 876214 see 876210 876211 876212 876213 | September | 2012 | 2013Q1 | 2013 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | UG | Not Veg | 2012-09-12 | N | 90.0643 | N | 5 | N | N | 1.1101 | 39.4971 | 148415.8357
[7 empty] | 17166 | 5236 | 875971 | 2012-09-12 11:27 | 2012-09-12 12:18 | 51 | 11kV | 54491 | 1308 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | At S.15005 Dee Why West, Panel 13 Fdr CB tripped on earth fault with 11kV trip, zpone earth, efi, fault check, field efi's down at S.47595 and S.15777. Footpath side lightning arrestor failed at UG/OH | September | 2012 | 2013Q1 | 2013 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2012-09-12 | N | 41.6598 | N | 5 | N | N | 1.1101 | 39.4971 | 39820.4156
[7 empty] | 16817 | 2153 | 876099 | 2012-09-12 15:16 | 2012-09-12 16:30 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122083 single phase DOLF : 10 Amp Excluded OMS 876099 | September | 2012 | 2013Q1 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2012-09-12 | N | 74 | N | 5 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 16516 | 94 | 876196 | 2012-09-12 22:13 | 2012-09-12 23:22 | 69 | 11kV | 37191 | 539 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 46673 tripped and locked out on IOC and Timed O/C Tree branch fell onot mains O/S 14 Chetwynd Rd | September | 2012 | 2013Q1 | 2013 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-09-12 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 27178.0859
[7 empty] | 16781 | 1934 | 876257 | 2012-09-13 09:07 | 2012-09-13 10:07 | 60 | 11kV | 6180 | 103 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122094 2 fault operations B & C phase Overcurrent Excluded OMS 876257 | September | 2012 | 2013Q1 | 2013 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-09-13 | N | 60 | N | 12 | N | N | 1.1101 | 39.4971 | 4516.1617
[7 empty] | 16600 | 617 | 877010 | 2012-09-13 10:13 | 2012-09-13 12:30 | 137 | 11kV | 14111 | 103 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122096 1 fault operation B & C phase | September | 2012 | 2013Q1 | 2013 | 803:74013 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-09-13 | N | 137 | N | 12 | N | N | 1.1101 | 39.4971 | 10311.9026
[7 empty] | 16683 | 1121 | 876230 | 2012-09-13 08:14 | 2012-09-13 12:48 | 274 | 11kV | 36782 | 262 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 122087, 122097, 122097 2 fault operations C phase Earth fault Cph OHM down at pole 8K-60334. Refer to related records 876996, 876997, 876998, 876999, 877002 and 877003 Excluded OMS No. 876230, 876274 | September | 2012 | 2013Q1 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2012-09-13 | N | 140.3893 | N | 12 | N | N | 1.1101 | 39.4971 | 26879.2007
[7 empty] | 16812 | 2134 | 876198 | 2012-09-12 22:23 | 2012-09-13 13:32 | 909 | 11kV | 204913 | 521 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122085 2 fault operations Earth fault 11kV mains down near Pole IR-12219. | September | 2012 | 2013Q1 | 2013 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2012-09-12 | N | 393.3071 | N | 5 | N | N | 1.1101 | 39.4971 | 149744.3765
[7 empty] | 17133 | 4685 | 876599 | 2012-09-13 16:33 | 2012-09-13 17:21 | 48 | 11kV | 30192 | 629 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of Pnl 10 Ex Noraville beyond USL43994 Roadside phase bond failed @ pole BU3684 (Cnr Brandon & Scenic) | September | 2012 | 2013Q1 | 2013 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2012-09-13 | N | 48 | N | 12 | N | N | 1.1101 | 39.4971 | 22063.4231
[7 empty] | 17101 | 4407 | 876645 | 2012-09-13 17:06 | 2012-09-13 18:17 | 70.55 | 11kV | 12667.5 | 600 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn.12690 Berkeley Vale Pnl.3 tripped & reclosed on: Spajj 140 relay - L1, Trip, Timing, LO, EFI REC 41630 Keren Bundilla - Tripped / reclosed & locked out on O/L trip, lockout Tree on Mains B & C phase between AB44498 tee PT14432 - removed by DOp see 877987 877990 | September | 2012 | 2013Q1 | 2013 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Veg | 2012-09-13 | N | 21.1125 | N | 12 | N | N | 1.1101 | 39.4971 | 9257.0354
[7 empty] | 17063 | 4153 | 876639 | 2012-09-13 17:00 | 2012-09-13 18:20 | 80 | 11kV | 1200 | 15 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 122104 Linesman found pole GU-54502 leaning over 45deg. Isolated from Lk 41275 for repair. | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2012-09-13 | N | 80 | N | 12 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 18145 | 16055 | 876685 | 2012-09-13 17:58 | 2012-09-13 18:36 | 38 | 11kV | 25954 | 716 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn8100 GreenSquare pan 20 tripped on Aph Overcurrent & EF Cause: UG Fault Remarks: UG fault between S5203Sw/A to S6326Sw/B. Note EFI does not operate at S5203 reported previously subs to repair See 876797,9,800 GIS 876809,10 exclude 876685,93,704 | September | 2012 | 2013Q1 | 2013 | ZN8100:PA20 | ZN384:PA68 | ZN00384/000068 | SYDNEY | UG | Not Veg | 2012-09-13 | N | 36.2486 | N | 12 | N | N | 1.1101 | 39.4971 | 18966.4177
[7 empty] | 18289 | 17364 | 876659 | 2012-09-13 17:25 | 2012-09-13 18:38 | 73 | 11kV | 1533 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | N | LID 122105 B phase DOLF : 10 Amp | September | 2012 | 2013Q1 | 2013 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | UG | Not Veg | 2012-09-13 | N | 73 | N | 12 | N | N | 1.1101 | 39.4971 | 1120.2712
[7 empty] | 16973 | 3377 | 876640 | 2012-09-13 17:06 | 2012-09-13 22:45 | 339 | 11kV | 14736 | 64 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11014 Daley Empire Bay - B phase HDO assembly failed see 876927 for secondary outage to PT13414 to make repairs | September | 2012 | 2013Q1 | 2013 | ZN12660:PA14 | ZN12660:PA5 | ZN12660/000005 | CENTRAL COAST | OH | Not Veg | 2012-09-13 | N | 230.25 | N | 12 | N | N | 1.1101 | 39.4971 | 10768.6342
[7 empty] | 18464 | 19204 | 876710 | 2012-09-13 19:10 | 2012-09-14 00:05 | 295 | 11kV | 1770 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | PT13338 - Roadside 16A HDO fuse operated weather realted - Wind & rain see 878051 GIS 878053 | September | 2012 | 2013Q1 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2012-09-13 | N | 295 | N | 12 | N | N | 1.1101 | 39.4971 | 1293.4638
[7 empty] | 16715 | 1308 | 876698 | 2012-09-13 18:22 | 2012-09-14 00:15 | 353 | 11kV | 706 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 122107 Broken LL dropper Excluded OMS 876698 | September | 2012 | 2013Q1 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-09-13 | N | 353 | N | 12 | N | N | 1.1101 | 39.4971 | 515.924
[7 empty] | 18541 | 20270 | 876884 | 2012-09-13 14:05 | 2012-09-14 11:39 | 1293.7833 | 11kV | 130055 | 1362 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122101/02 3 fault operations C phase Earth fault BCE line diff both ends tree hit fdr at pole JS 60131 | September | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2012-09-13 | N | 95.4883 | N | 12 | N | N | 1.1101 | 39.4971 | 95040.358
[7 empty] | 17233 | 6300 | 876993 | 2012-09-14 13:59 | 2012-09-14 14:55 | 56 | 11kV | 3360 | 60 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 Zetland Pa33 Epson rd fdr tripped on Earth Fault with fault check & EFI Cause: Not Ascertained Remarks: Suspected developing cable fault See 878164 exclude 876993 | September | 2012 | 2013Q1 | 2013 | ZN188:PA33 | ZN188:PA33 | ZN00188/000033 | RANDWICK | UG | Not Veg | 2012-09-14 | N | 56 | N | 2 | N | N | 1.1101 | 39.4971 | 2455.3889
[7 empty] | 18525 | 20085 | 876942 | 2012-09-14 12:36 | 2012-09-14 21:19 | 523 | 11kV | 138114 | 1818 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 122118 2 fault operations Earth fault Broken cross arm & pole fire at pole KS-60003. Excluded oms-876942 & 876969. | September | 2012 | 2013Q1 | 2013 | 229:34989 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Not Veg | 2012-09-14 | N | 75.9703 | N | 2 | N | N | 1.1101 | 39.4971 | 100929.6375
[7 empty] | 18546 | 20326 | 877150 | 2012-09-15 09:42 | 2012-09-15 12:00 | 137.9833 | 11kV | 827.9 | 6 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 122120 3 phase interruption SECTION ISOLATED TO REPLACE POLE Excluded OMS 877150 | September | 2012 | 2013Q1 | 2013 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Not Veg | 2012-09-15 | N | 137.9833 | N | 2 | N | N | 1.1101 | 39.4971 | 605.0049
[7 empty] | 17844 | 12657 | 877268 | 2012-09-15 18:10 | 2012-09-15 19:34 | 84 | 11kV | 12432 | 148 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At Sub 482 Dickson Ave B phase is Open Circuit on the LV side of Transformer Remarks: open circuit. Tx Open circuit B phase on LV end. Related jobs: #877545, 877268 | September | 2012 | 2013Q1 | 2013 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | BURWOOD | UG | Not Veg | 2012-09-15 | N | 84 | N | 2 | N | N | 1.1101 | 39.4971 | 9084.9389
[7 empty] | 17339 | 7373 | 877293 | 2012-09-16 00:06 | 2012-09-16 01:12 | 66 | 11kV | 42797 | 937 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.8 tripped and reclosed on B & C phase OC Bond burnt off between PT13554 and AB41187 see 878110 878111 | September | 2012 | 2013Q1 | 2013 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2012-09-16 | N | 45.6745 | N | 3 | N | N | 1.1101 | 39.4971 | 31274.7853
[7 empty] | 17356 | 7509 | 877302 | 2012-09-16 06:16 | 2012-09-16 09:05 | 169 | 11kV | 20787 | 123 | HV | Animal Possum | Animal | DC Transformer | Unplanned | Unselected | N | Ex Panel 31 S1829 Rydale Sixth PT1120 Maida Blaxland 11kV Amp Footpath Drop out fuse operated. Cause: Possum on Tx Tank. See OMS 877439 877302 877304. | September | 2012 | 2013Q1 | 2013 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | PARRAMATTA | OH | Not Veg | 2012-09-16 | N | 169 | N | 3 | N | N | 1.1101 | 39.4971 | 15190.5265
[7 empty] | 16694 | 1178 | 877360 | 2012-09-16 12:02 | 2012-09-16 13:06 | 64 | 11kV | 59840 | 935 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3154 St Ives, Panel 10 Fdr CB tripped on A phase timed OC with an efi, zone earth, 11kV trip. No field efi's operated. Cable fault in frontline cable. | September | 2012 | 2013Q1 | 2013 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | UG | Not Veg | 2012-09-16 | N | 64 | N | 3 | N | N | 1.1101 | 39.4971 | 43729.307
[7 empty] | 17461 | 8402 | 877420 | 2012-09-17 01:17 | 2012-09-17 03:00 | 103 | 11kV | 206 | 2 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 122129 B phase DOLF : 10 Amp Possum found at base of UG/OH pole. | September | 2012 | 2013Q1 | 2013 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-09-17 | N | 103 | N | 19 | N | N | 1.1101 | 39.4971 | 150.5387
[7 empty] | 18214 | 16717 | 877569 | 2012-09-17 10:07 | 2012-09-17 16:19 | 372 | 11kV | 744 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 122133 B phase dist fuse sub isolated to replace lv fuse assembly Excluded oms 877569 | September | 2012 | 2013Q1 | 2013 | 510:48164 | 508:82579 | ZN00508/082579 | DUNGOG | OH | Not Veg | 2012-09-17 | N | 372 | N | 19 | N | N | 1.1101 | 39.4971 | 543.6933
[7 empty] | 18249 | 17071 | 877772 | 2012-09-17 17:40 | 2012-09-17 19:27 | 107 | 11kV | 5242 | 55 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122149 3 phase isolation stranding on 11kV ohm adj sub 51262 interupted for repair Excluded OMS 877772 | September | 2012 | 2013Q1 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-09-17 | N | 95.3091 | N | 19 | N | N | 1.1101 | 39.4971 | 3830.699
[7 empty] | 16779 | 1898 | 877875 | 2012-09-17 18:45 | 2012-09-17 20:19 | 94 | 11kV | 4350 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122151 3 fault operations 3 phase Overcurrent | September | 2012 | 2013Q1 | 2013 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2012-09-17 | N | 92.5532 | N | 19 | N | N | 1.1101 | 39.4971 | 3178.8517
[7 empty] | 17304 | 7127 | 878218 | 2012-09-17 18:16 | 2012-09-17 21:09 | 173 | 11kV | 30275 | 175 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122153 3 fault operations 3 phase Earth fault LID 122153 ## suspect did not grade with sub dolf see report 122156/OMS 878217 | September | 2012 | 2013Q1 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-09-17 | N | 173 | N | 19 | N | N | 1.1101 | 39.4971 | 22124.077
[7 empty] | 16627 | 816 | 877878 | 2012-09-17 18:16 | 2012-09-17 21:09 | 173 | 11kV | 1730 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122155 B phase DOLF : 5 Amp Excluded OMS 877878 | September | 2012 | 2013Q1 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-09-17 | N | 173 | N | 19 | N | N | 1.1101 | 39.4971 | 1264.233
[7 empty] | 17193 | 5813 | 877903 | 2012-09-17 20:08 | 2012-09-17 21:10 | 62 | 11kV | 5596 | 93 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn.12600 Lisarow Pnl.5 tripped on C phase O/C, EFI UGOH to S.12462 Albany Int Pacific No 2 broken away due to fault in Under Ground section see 879517 879515 | September | 2012 | 2013Q1 | 2013 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | UG | Not Veg | 2012-09-17 | N | 60.172 | N | 19 | N | N | 1.1101 | 39.4971 | 4089.3917
[7 empty] | 16856 | 2370 | 877886 | 2012-09-17 19:30 | 2012-09-17 21:22 | 112.45 | 11kV | 216.7667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122157 Single phase DOLF : 10 Amp. Excluded OMD 877886 | September | 2012 | 2013Q1 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2012-09-17 | N | 108.3833 | N | 19 | N | N | 1.1101 | 39.4971 | 158.4067
[7 empty] | 18385 | 18260 | 877873 | 2012-09-17 18:43 | 2012-09-17 21:35 | 172 | 11kV | 516 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122158 C phase DOLF : 10 Amp Excluded OMS 877873 | September | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | UG | Not Veg | 2012-09-17 | N | 172 | N | 19 | N | N | 1.1101 | 39.4971 | 377.0776
[7 empty] | 17326 | 7308 | 877881 | 2012-09-17 19:21 | 2012-09-17 21:49 | 148 | 11kV | 3404 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122159 C phase DOLF : 20 Amp Excluded oms 877881. 877905, 877917 | September | 2012 | 2013Q1 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-09-17 | N | 148 | N | 19 | N | N | 1.1101 | 39.4971 | 2487.5428
[7 empty] | 16811 | 2129 | 877904 | 2012-09-17 20:09 | 2012-09-17 21:55 | 106 | 11kV | 318 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | PT18804 Tuggerah McDonalds - Roadside HDO blown 20A Lightning | September | 2012 | 2013Q1 | 2013 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2012-09-17 | N | 106 | N | 19 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 16594 | 594 | 877888 | 2012-09-17 20:00 | 2012-09-17 23:31 | 211 | 11kV | 3798 | 18 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122162 Sectionaliser | September | 2012 | 2013Q1 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-09-17 | N | 211 | N | 19 | N | N | 1.1101 | 39.4971 | 2775.4664
[7 empty] | 17902 | 13149 | 877894 | 2012-09-17 19:44 | 2012-09-17 23:55 | 251 | 11kV | 1004 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 122160 3 phase DOLF : 10 Amp 11kv surge arrestor failed on sub 52276 Excluded oms 877894. | September | 2012 | 2013Q1 | 2013 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2012-09-17 | N | 251 | N | 19 | N | N | 1.1101 | 39.4971 | 733.6936
[7 empty] | 17771 | 12090 | 877901 | 2012-09-17 20:02 | 2012-09-18 01:35 | 333 | 11kV | 1332 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122163 B & C phase DOLF : 20 Amp Excluded OMS 877901 | September | 2012 | 2013Q1 | 2013 | 524:33576 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2012-09-17 | N | 333 | N | 19 | N | N | 1.1101 | 39.4971 | 973.3863
[7 empty] | 17612 | 10173 | 877940 | 2012-09-18 03:10 | 2012-09-18 03:32 | 22 | 11kV | 44792 | 2036 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Panel #16 Tripped on A and C phase OC. EFI all field EFIs #3GE and ZE 11kv trip. Two seperate cable faults: 1) section of 11kv feeder from S502 SWB to S885 SWA to S839 SWB 2) section of 11kv feed from S49061 SWB to S46971 SWA tee to Sub 2656. See interruptions forms for Pa20 at 0059, Pa16 at 0211 and Pa16 at 0310. Related jobs: #879169, 877945, 877944, 877943, 877942, 877941, 877940, 879203 | September | 2012 | 2013Q1 | 2013 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2012-09-18 | N | 22 | N | 20 | Y | Y | 1.1101 | 39.4971 | 32732.6725
[7 empty] | 16931 | 3103 | 877884 | 2012-09-17 19:27 | 2012-09-18 04:25 | 538 | 11kV | 2152 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122165 B phase DOLF : 10 Amp Excluded OMS 877884 | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-09-17 | N | 538 | N | 19 | N | N | 1.1101 | 39.4971 | 1572.6181
[7 empty] | 17787 | 12315 | 877930 | 2012-09-18 00:59 | 2012-09-18 04:50 | 231 | 11kV | 241749 | 1652 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ Sub 398 Dulwich Hill Zn Panel #20 tripped on Bassler 50TAC ZE #GE. EFI and all field EFIs except S502 which did not operate. Remarks: two separate cable faults. 1) section of 11kv feeder from S502 SWB to S885 SWA to S839 SWB 2) section of 11kv feed from S49061 SWB to S46971 SWA tee to S2656. See interruption forms Pa16 at 0211, Pa16 at 0310 and Pa16 at 0401. Related jobs: #877930, 879172, 879173, 879178, 879179, 879171, 879169 | September | 2012 | 2013Q1 | 2013 | ZN398:PA20 | ZN398:PA20 | ZN00398/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-09-18 | N | 146.3372 | N | 20 | Y | Y | 1.1101 | 39.4971 | 176663.0388
[7 empty] | 16540 | 270 | 877918 | 2012-09-17 20:58 | 2012-09-18 05:15 | 497 | 11kV | 994 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122166 C phase DOLF : 10 Amp Excluded OMS 877918 | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-09-17 | N | 497 | N | 19 | N | N | 1.1101 | 39.4971 | 726.3859
[7 empty] | 18048 | 15270 | 877879 | 2012-09-17 18:55 | 2012-09-18 06:20 | 685 | 11kV | 32077 | 160 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122140 4 fault operations A & C phase Overcurrent; Earth fault Mains found down Between pole ER94984 and Moon Mountain Sub 52384 | September | 2012 | 2013Q1 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2012-09-17 | N | 200.4812 | N | 19 | N | N | 1.1101 | 39.4971 | 23440.9255
[7 empty] | 16768 | 1753 | 877955 | 2012-09-18 06:01 | 2012-09-18 07:40 | 99 | 11kV | 9009 | 91 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | The centre phase 40K HDO fuse operated due to fatigue | September | 2012 | 2013Q1 | 2013 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Not Veg | 2012-09-18 | N | 99 | N | 20 | Y | Y | 1.1101 | 39.4971 | 6583.5115
[7 empty] | 17251 | 6551 | 877950 | 2012-09-18 05:17 | 2012-09-18 08:15 | 178 | 11kV | 1780 | 10 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | At PT9014 Darrangan Princes, A section of Panel 8 Fdr "Sub 9279 Numantia Copeland" from Engadine Zone. HDO centre phase operation: 40 K HDO batch? Remarks: Animals/Birds. Possum came in contact with HV fuse. Related jobs: #877950, 877977, 878717 | September | 2012 | 2013Q1 | 2013 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2012-09-18 | N | 178 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1300.7715
[7 empty] | 16621 | 788 | 877949 | 2012-09-18 04:56 | 2012-09-18 09:10 | 254 | 11kV | 15748 | 62 | HV | Vegetation Blow/Fall In | Vegetation | Fuse | Unplanned | Unselected | N | PT12112 Wycombe Hastings - Footpath phase HDO found open Possibly knocked open by falling tree branch found on ground under PT GIS:878571 | September | 2012 | 2013Q1 | 2013 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-09-18 | N | 254 | N | 20 | Y | Y | 1.1101 | 39.4971 | 11508.1739
[7 empty] | 18126 | 15935 | 877893 | 2012-09-17 19:44 | 2012-09-18 11:00 | 916.3667 | 11kV | 3665.4667 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 122164 A phase DOLF : 5 Amp AP ISSUED TO REPLACE A PHASE LA CC1: 22-"Refer to SOp" | September | 2012 | 2013Q1 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-09-17 | N | 916.3667 | N | 19 | N | N | 1.1101 | 39.4971 | 2678.6149
[7 empty] | 17938 | 13455 | 878009 | 2012-09-18 11:00 | 2012-09-18 11:30 | 30 | 11kV | 60 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 122182 Single phase DOLF | September | 2012 | 2013Q1 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | UG | Not Veg | 2012-09-18 | N | 30 | N | 20 | Y | Y | 1.1101 | 39.4971 | 43.8462
[7 empty] | 18077 | 15564 | 877922 | 2012-09-17 21:33 | 2012-09-18 13:45 | 972 | 11kV | 230981 | 1955 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Lightning | N | Zn.12570 Avoca Pnl.35 tripped on A & B phase trip. Section of 11kV CCT down on ground beyond USL45430 to PT18027. See 878600 878601 878602 878603 878604 878605 | September | 2012 | 2013Q1 | 2013 | ZN12570:PA35 | ZN12570:PA35 | ZN12570/000035 | CENTRAL COAST | OH | Not Veg | 2012-09-17 | N | 118.1488 | N | 19 | N | N | 1.1101 | 39.4971 | 168794.102
[7 empty] | 18156 | 16118 | 877968 | 2012-09-18 06:29 | 2012-09-18 14:17 | 468.35 | 11kV | 14204.5833 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 122185 SECTION ISOLATED TO REPAIR MAINS at Pole ET 51634 | September | 2012 | 2013Q1 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2012-09-18 | N | 430.4419 | N | 20 | Y | Y | 1.1101 | 39.4971 | 10380.2905
[7 empty] | 18367 | 18061 | 878013 | 2012-09-18 11:50 | 2012-09-18 15:00 | 190 | 11kV | 2090 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 122187 3 phase isolation Mains down at pole HY 30082, burnt off tapping at 11kV links 40937 Excluded OMS 878013 | September | 2012 | 2013Q1 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-09-18 | N | 190 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1527.3104
[7 empty] | 17817 | 12492 | 878158 | 2012-09-18 10:45 | 2012-09-18 18:17 | 452 | 11kV | 790.0833 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 122183 SUB ISOLATED TO REPLACE TX Excluded OMS 878158/878425 | September | 2012 | 2013Q1 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | UG | Not Veg | 2012-09-18 | N | 395.0417 | N | 20 | Y | Y | 1.1101 | 39.4971 | 577.3696
[7 empty] | 17929 | 13401 | 878481 | 2012-09-18 18:27 | 2012-09-18 19:40 | 72.9 | 11kV | 13986.4 | 193 | HV | Staff Other | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | S2236 Learmonth St Dist 1,2,3,4 Phase: ABC Fuse: 400A Remarks: staff error. Lineworker removed LV// prior to Dop restoring centre. Dop called away to emergency work. Related jobs: #878479, 878481 | September | 2012 | 2013Q1 | 2013 | ZN72:PA31 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | OH | Not Veg | 2012-09-18 | N | 72.4684 | N | 20 | Y | Y | 1.1101 | 39.4971 | 10220.8486
[7 empty] | 18421 | 18848 | 877967 | 2012-09-18 06:26 | 2012-09-18 20:25 | 839 | 11kV | 839 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 122172 Single phase DOLF : 10 Amp FAULTY SUB REPLACED Excluded oms 877967 | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-09-18 | N | 839 | N | 20 | Y | Y | 1.1101 | 39.4971 | 613.1165
[7 empty] | 18037 | 14895 | 878452 | 2012-09-18 17:41 | 2012-09-18 20:51 | 190 | 11kV | 4280 | 47 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 122199 4 fault operations 3 phase Overcurrent 11kv OHM has found contacting crossarm and evidence of burning through.temp repair be ll crew Excluded OMS 878452 | September | 2012 | 2013Q1 | 2013 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2012-09-18 | N | 91.0638 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3127.6978
[7 empty] | 16940 | 3179 | 878522 | 2012-09-18 20:05 | 2012-09-18 22:14 | 129 | 11kV | 189450 | 1695 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122200 1 fault operation 3 phase Sensitive Earth Fault Faulty sub 52962 | September | 2012 | 2013Q1 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2012-09-18 | N | 111.7699 | N | 20 | Y | Y | 1.1101 | 39.4971 | 138444.4722
[7 empty] | 16901 | 2905 | 878486 | 2012-09-18 18:34 | 2012-09-18 22:25 | 231 | 11kV | 1386 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122202 A phase DOLF : 20 Amp Excluded OMS 878486 | September | 2012 | 2013Q1 | 2013 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2012-09-18 | N | 231 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1012.8479
[7 empty] | 18294 | 17413 | 878490 | 2012-09-18 18:46 | 2012-09-18 22:48 | 242 | 11kV | 242 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122203 A phase DOLF : 10 Amp Excluded OMS 878490 | September | 2012 | 2013Q1 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | UG | Not Veg | 2012-09-18 | N | 242 | N | 20 | Y | Y | 1.1101 | 39.4971 | 176.8465
[7 empty] | 17237 | 6363 | 878446 | 2012-09-18 17:34 | 2012-09-18 23:20 | 346 | 11kV | 378957 | 2330 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2835 Burwood Panel 23 'Wentworth Hornsey' Feeder has tripped, Signals: 11kv trip, No.4 Tx GE, Relays: EF, EFI and FC Field EFI's: S48182 Remarks: UG fault. At sub 136 Syme Ave one of the 11kv tails has burnt up. Related jobs: #878489, 878476, 878473, 878451, 878446, 878692, 878693, 878687, 878684, 878679 | September | 2012 | 2013Q1 | 2013 | ZN2835:PA23 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2012-09-18 | N | 162.6425 | N | 20 | Y | Y | 1.1101 | 39.4971 | 276930.5983
[7 empty] | 18121 | 15915 | 878506 | 2012-09-18 19:37 | 2012-09-18 23:35 | 238 | 11kV | 1428 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122204 B phase DOLF : 25 Amp Excluded OMS 878506 & 878511 | September | 2012 | 2013Q1 | 2013 | 526:34641 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Veg | 2012-09-18 | N | 238 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1043.5403
[7 empty] | 16518 | 99 | 878504 | 2012-09-18 19:36 | 2012-09-19 00:10 | 274 | 11kV | 274 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 122205 A phase DOLF : 10 Amp Excluded OMS 878504 | September | 2012 | 2013Q1 | 2013 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | UG | Not Veg | 2012-09-18 | N | 274 | N | 20 | Y | Y | 1.1101 | 39.4971 | 200.2311
[7 empty] | 17099 | 4399 | 878516 | 2012-09-18 21:29 | 2012-09-19 01:15 | 226 | 11kV | 4294 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 122206 3 phase DOLF : 20 Amp Excluded OMS 878516, 878537, 878538 | September | 2012 | 2013Q1 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2012-09-18 | N | 226 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3137.9285
[7 empty] | 17690 | 11464 | 878268 | 2012-09-18 12:35 | 2012-09-19 07:05 | 1110 | 11kV | 1110 | 1 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Previous Storm | N | LID 122186 UGOH at pole FR-72004 Rothbury Estate Winery faulty. UGOH been replaced. Power restored and Volts checked OK. VISI Break 49221 left Open Locked & DT'd as DOP could not check rotation. No one on site. Rotation checked with customer and visi break closed at 0705 hours on 19/9/2012 by Darren McPhail. Excluded OMS 878196 & 878332. | September | 2012 | 2013Q1 | 2013 | 526:34636 | 526:34640 | ZN00526/034640 | CESSNOCK | Unknown | Unknown | 2012-09-18 | N | 1110 | N | 20 | Y | Y | 1.1101 | 39.4971 | 811.1553
[7 empty] | 17845 | 12662 | 878555 | 2012-09-19 06:12 | 2012-09-19 08:05 | 113 | 11kV | 678 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 122211 A phase DOLF : 10 Amp A phase fuse carrier burnt through and failed. Excluded OMS # 878555 & 878556. | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2012-09-19 | N | 113 | N | 10 | N | N | 1.1101 | 39.4971 | 495.4624
[7 empty] | 17128 | 4627 | 878583 | 2012-09-19 08:00 | 2012-09-19 10:10 | 130 | 11kV | 90159 | 902 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At Zn.965 Pennant Hills Feeder tripped reclosed and locked Relays Earth Fault, EFI, Timing and Lockout Signals: 11Kv Trip No1 Group Earth, Zone Earth See OMS 879120 879122 879123 879124 | September | 2012 | 2013Q1 | 2013 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | UG | Not Veg | 2012-09-19 | N | 99.9545 | N | 10 | N | N | 1.1101 | 39.4971 | 65885.538
[7 empty] | 17378 | 7734 | 878634 | 2012-09-19 09:14 | 2012-09-19 12:30 | 196 | 11kV | 26460 | 135 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 122217 B phase DOLF : 10 Amp. Surge arrestor had failed. Excluded OMS 878634 & 878756 | September | 2012 | 2013Q1 | 2013 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2012-09-19 | N | 196 | N | 10 | N | N | 1.1101 | 39.4971 | 19336.1876
[7 empty] | 16860 | 2400 | 878589 | 2012-09-19 08:14 | 2012-09-19 12:45 | 271 | 11kV | 271 | 1 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 122220 C phase DOLF : 10 Amp Cause possum had contacted HV. | September | 2012 | 2013Q1 | 2013 | 512:48047 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2012-09-19 | N | 271 | N | 10 | N | N | 1.1101 | 39.4971 | 198.0388
[7 empty] | 17832 | 12577 | 878570 | 2012-09-19 07:40 | 2012-09-19 13:43 | 362.5833 | 11kV | 717.2333 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 122223 B phase DOLF : 10 Amp Lightning Arrestor Excluded OMS 878570 | September | 2012 | 2013Q1 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-09-19 | N | 358.6167 | N | 10 | N | N | 1.1101 | 39.4971 | 524.133
[7 empty] | 17931 | 13416 | 878864 | 2012-09-19 13:46 | 2012-09-19 14:29 | 43 | 11kV | 26113 | 646 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Fdr Pa36 tripped Relays: Earth Fault, Cph, OC, EFI, 11kv trip, Zone Earth, #2 Group Earth Field EFI's S35216 Cause: UG Fault btw S8906 to S8624 See 879134,5 Exclude 878864 | September | 2012 | 2013Q1 | 2013 | ZN1788:PA36 | ZN1788:PA69 | ZN01788/000069 | RANDWICK | UG | Not Veg | 2012-09-19 | N | 40.4226 | N | 10 | N | N | 1.1101 | 39.4971 | 19082.6102
[7 empty] | 17933 | 13418 | 878662 | 2012-09-19 09:51 | 2012-09-19 14:30 | 279 | 11kV | 1116 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 122219 Single phase DOLF : 10 Amp Lightning arrestor Excluded OMS 878662 & 878730 | September | 2012 | 2013Q1 | 2013 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Not Veg | 2012-09-19 | N | 279 | N | 10 | N | N | 1.1101 | 39.4971 | 815.5399
[7 empty] | 17393 | 7897 | 878553 | 2012-09-19 05:15 | 2012-09-19 16:30 | 675 | 11kV | 13102 | 190 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122207 Trip & reclose 2 fault operations Earth fault See OMS 879095 - Camberwell sectionaliser L/O | September | 2012 | 2013Q1 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-09-19 | N | 68.9579 | N | 10 | N | N | 1.1101 | 39.4971 | 9574.5552
[7 empty] | 18000 | 14188 | 878582 | 2012-09-19 08:06 | 2012-09-19 18:27 | 621.1667 | 11kV | 2402.8333 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 122227 A & C phase DOLF : 10 Amp Faulty Transformer. Excluded OMS 878582 Job was attributed to 50806 Alder sub in OMS but 27681 Lewis sub was the faulty Tx. | September | 2012 | 2013Q1 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2012-09-19 | N | 600.7083 | N | 10 | N | N | 1.1101 | 39.4971 | 1755.9197
[7 empty] | 16769 | 1758 | 879031 | 2012-09-19 19:44 | 2012-09-19 21:30 | 106 | 11kV | 212 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | PT13620 Wise Ferry Lavender 3.4 - 16A HDO fuse operated 2 x Lightning arrestors cut away by DOp | September | 2012 | 2013Q1 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2012-09-19 | N | 106 | N | 10 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 18271 | 17207 | 879059 | 2012-09-20 06:50 | 2012-09-20 09:20 | 150 | 11kV | 300 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 122229 A & B phase DOLF : 10 Amp Bird on Trans Excluded OMS No. 879059 | September | 2012 | 2013Q1 | 2013 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2012-09-20 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 16504 | 28 | 879196 | 2012-09-20 10:00 | 2012-09-20 15:05 | 305 | 11kV | 3660 | 12 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 122236 Section isolated to repair defective crossarm. | September | 2012 | 2013Q1 | 2013 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Not Veg | 2012-09-20 | N | 305 | N | 4 | N | N | 1.1101 | 39.4971 | 2674.62
[7 empty] | 18534 | 20186 | 879204 | 2012-09-20 11:01 | 2012-09-20 15:45 | 283.5833 | 11kV | 8223.9167 | 29 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122238 section of fdr isolated to replace pole KS-30072 | September | 2012 | 2013Q1 | 2013 | 229:34983 | 233:82818 | ZN00233/082818 | PORT STEPHENS | OH | Not Veg | 2012-09-20 | N | 283.5833 | N | 4 | N | N | 1.1101 | 39.4971 | 6009.7957
[7 empty] | 18415 | 18756 | 879461 | 2012-09-20 19:07 | 2012-09-20 20:20 | 73 | 11kV | 73 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122244 B phase DOLF : 10 Amp Excluded OMS report 879461 Volts =248 Amps =12 | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-09-20 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 53.3462
[7 empty] | 17236 | 6358 | 879603 | 2012-09-21 10:14 | 2012-09-21 13:46 | 212 | 11kV | 4028 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122253 Emergency isolation to repair low 11kV OHM at pole KQ-80039 | September | 2012 | 2013Q1 | 2013 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2012-09-21 | N | 212 | N | 4 | N | N | 1.1101 | 39.4971 | 2943.5436
[7 empty] | 17093 | 4350 | 879833 | 2012-09-21 17:18 | 2012-09-21 17:50 | 32 | 11kV | 1664 | 52 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122257 C phase DOLF : 31 Amp. Excluded OMS 879833 | September | 2012 | 2013Q1 | 2013 | 503:48011 | 528:83020 | ZN00528/083020 | MAITLAND | UG | Not Veg | 2012-09-21 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 1216.0021
[7 empty] | 18163 | 16192 | 879814 | 2012-09-21 08:30 | 2012-09-21 20:20 | 710 | 11kV | 4260 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 122255 C phase During reconnection switching # 24813 this 11kV link broke when the operator tried to close it. These were very old links and the porcelain bottom half (load side) of the link snapped off. This interruption meant that subs beyond link 41665 were still interrupted after supply was restored to all subs on the line side of these links. No protection operated. Replaced 11kV Links 41665, Excluded OMS 879814 | September | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-09-21 | N | 710 | N | 4 | N | N | 1.1101 | 39.4971 | 3113.0824
[7 empty] | 18349 | 17867 | 879873 | 2012-09-21 20:52 | 2012-09-21 22:10 | 78 | 11kV | 78 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122258 A phase DOLF : 10 Amp. Readings as left 252V @ 2A, 2A, 2A. Excluded OMS 879873 | September | 2012 | 2013Q1 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-09-21 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 18420 | 18821 | 879879 | 2012-09-22 07:00 | 2012-09-22 08:10 | 70 | 11kV | 210 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122261 B phase DOLF : 10 Amp | September | 2012 | 2013Q1 | 2013 | 243:80075 | 243:80075 | ZN00243/080075 | CENTRAL COAST | UG | Not Veg | 2012-09-22 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 17697 | 11502 | 879885 | 2012-09-22 00:58 | 2012-09-22 10:30 | 572 | 11kV | 2860 | 5 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At PT11371 Pacific Ashbrooke 0.7 16A HDO fuse operated. Cause: Possum found at base of pole. See OMS 808241 879885 | September | 2012 | 2013Q1 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-09-22 | N | 572 | N | 5 | N | N | 1.1101 | 39.4971 | 2090.0036
[7 empty] | 17195 | 5865 | 879977 | 2012-09-22 15:21 | 2012-09-22 16:28 | 67 | 11kV | 4153 | 79 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn630 Mascot 11kv fdr Pa9 tripped Relays:E/F, EFI Signals: 11kv trip, Group2Earth, Zone Earth EFI-s36138 Refer Subs Nrmal and standby supply available, unable to operate LV C/O from Standby to normal Cause: UG FAult Remarks: 11kv fdr fault in section from S36138Sw/B to S7135Sw/B to S7754 to S6626 Note Request EFI tpo be fitted at S6626 Airport Centre No1 to assist with fault location See 880198,99,200 Exclude 879977 | September | 2012 | 2013Q1 | 2013 | ZN630:PA9 | ZN8100:PA37 | ZN08100/000037 | BAYSIDE | UG | Not Veg | 2012-09-22 | N | 52.5696 | N | 5 | N | N | 1.1101 | 39.4971 | 3034.8899
[7 empty] | 18248 | 17069 | 879983 | 2012-09-22 16:00 | 2012-09-22 18:00 | 120 | 11kV | 34080 | 284 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 122267 11kV links 40464 failed while restoring SI 24905. Emergency replacement carried out. Excluded OMS report #879983. & 879911 | September | 2012 | 2013Q1 | 2013 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-09-22 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 24904.6588
[7 empty] | 17384 | 7827 | 879889 | 2012-09-22 05:17 | 2012-09-22 18:40 | 803 | 11kV | 15065 | 113 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122260 4 fault operations, 3 phase, Earth fault section isolated to repair mains at P. AH-5239 Excluded oms 879889 & 878894 | September | 2012 | 2013Q1 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-09-22 | N | 133.3186 | N | 5 | N | N | 1.1101 | 39.4971 | 11009.0577
[7 empty] | 18561 | 20437 | 880012 | 2012-09-23 03:14 | 2012-09-23 04:40 | 86 | 11kV | 8428 | 98 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | At PT12188 Cornex Burilla all 3 HDO's operated 31.5A Possum found on PT Based on Customer calls suspect S11253#2 // with ABOVE SUB Sww OMS 880260 880264 880016/13/15/14/12 | September | 2012 | 2013Q1 | 2013 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2012-09-23 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 6158.9338
[7 empty] | 16566 | 418 | 880085 | 2012-09-23 13:18 | 2012-09-23 15:40 | 142 | 11kV | 568 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13755 Parukala Wise Ferry 1.2 HV fuse blown on Footpath Phase. Cause: Fuse fatigue. | September | 2012 | 2013Q1 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2012-09-23 | N | 142 | N | 3 | N | N | 1.1101 | 39.4971 | 415.0776
[7 empty] | 16658 | 978 | 880118 | 2012-09-23 18:47 | 2012-09-23 22:30 | 223 | 11kV | 446 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122272 LL Clamps was not tightened correctly. Excluded OMS report # 880118 | September | 2012 | 2013Q1 | 2013 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2012-09-23 | N | 223 | N | 3 | N | N | 1.1101 | 39.4971 | 325.9236
[7 empty] | 17026 | 3857 | 880305 | 2012-09-24 11:30 | 2012-09-24 12:40 | 70 | 11kV | 87215 | 1294 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn116 Leichhardt - 11kv Panel No.47 "Sub 35209 Macauley Norton" feeder tripped. Relays: Earth fault, EFI, fault check relay Signals: 11kv trip, No.3 Group earth, Zone earth. Field EFI's: S35209, S49859, S703, S1477, S8238 Remarks: 11kv UG fault from Sub 8238 North William to Sub 668 William El. Related jobs: #881205, 881206, 881207, 880305, 880328 | September | 2012 | 2013Q1 | 2013 | ZN116:PA47 | ZN116:PA19 | ZN00116/000019 | INNER WEST | UG | Not Veg | 2012-09-24 | N | 67.3995 | N | 6 | N | N | 1.1101 | 39.4971 | 63734.1496
[7 empty] | 17074 | 4224 | 880291 | 2012-09-24 11:16 | 2012-09-24 13:00 | 104 | 11kV | 3016 | 29 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT11588 Beaufort Wycombe Roadside 31.5A HVDO fuse operated. Cause: Possible fuse fatigiue See OMS 880448 880291 880361 | September | 2012 | 2013Q1 | 2013 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2012-09-24 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 2204.0038
[7 empty] | 18180 | 16426 | 880471 | 2012-09-24 14:48 | 2012-09-24 16:38 | 110 | 11kV | 330 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 122283 A phase Fuse found open - closed OK - windy | September | 2012 | 2013Q1 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2012-09-24 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 18452 | 19132 | 880395 | 2012-09-24 13:15 | 2012-09-24 16:45 | 210 | 11kV | 15500 | 145 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7481 Darling Harbour 11kv fdr Pa19 Tripped Relays: Bph O/C E/F EFI EFI's S6421 S3044 Abnormal S6336 "Momnorail Western Bvld" Closed. S6332SwB Opened Cause: UG Fault Remarks:11kv UG fdr fault in section from S3044SwB to S3092SwB to S6488SwD See 880755,6,7 Exclude 880395,405,21 | September | 2012 | 2013Q1 | 2013 | ZN7481:PA19 | ZN7481:PA19 | ZN07481/000019 | SYDNEY | UG | Not Veg | 2012-09-24 | N | 106.8966 | N | 6 | N | N | 1.1101 | 39.4971 | 11326.9428
[7 empty] | 17593 | 9783 | 880577 | 2012-09-24 09:00 | 2012-09-24 17:10 | 490 | 11kV | 12740 | 26 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | LID 122284 dop missed line of switching to restore sub 5491 Bobs Farm North. Other subs in isolation area restored by 1544hrs. DQ | September | 2012 | 2013Q1 | 2013 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | UG | Not Veg | 2012-09-24 | N | 490 | N | 6 | N | N | 1.1101 | 39.4971 | 9310.0162
[7 empty] | 18508 | 19962 | 880331 | 2012-09-24 12:06 | 2012-09-24 20:00 | 474 | 11kV | 1422 | 3 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | N | LID 122285 B & C phase DOLF : 10 Amp Pole stay wire broke & caused DOLF to blow. Excluded OMS# 880331 | September | 2012 | 2013Q1 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-09-24 | N | 474 | N | 6 | N | N | 1.1101 | 39.4971 | 1039.1557
[7 empty] | 17606 | 10092 | 880775 | 2012-09-25 02:57 | 2012-09-25 03:36 | 39 | 11kV | 2340 | 60 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 Zetland Pa33 fdr tripped Relays: E/F Fault Check EFI Signals: 11kv trip, Zone Earth, No4 Group Earth UG Fault from Zn188 Zetland Pa33 to S8206 to S338 See 880775 exclude 880649,51 | September | 2012 | 2013Q1 | 2013 | ZN188:PA33 | ZN188:PA33 | ZN00188/000033 | RANDWICK | UG | Not Veg | 2012-09-25 | N | 39 | N | 5 | N | N | 1.1101 | 39.4971 | 1710.003
[7 empty] | 17234 | 6304 | 880648 | 2012-09-25 02:46 | 2012-09-25 03:49 | 63 | 11kV | 36540 | 580 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn9252 Jannali Pa7 fdr tripped on: Relays: Aph Instantaneous and tiomed , Earth Fault, EFI, Timing Relay and Lockout Relay Signals: Zone Earth, Tx3 Group Earth, 11kV trip Remarks: Possum at base of UGOH to S47850, Mains to check UGOH in daylight See 881630 exclude 880648 | September | 2012 | 2013Q1 | 2013 | ZN9252:PA7 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2012-09-25 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 26702.3543
[7 empty] | 17412 | 8060 | 880667 | 2012-09-25 07:36 | 2012-09-25 09:15 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 122295 A & B phase DOLF : 10 Amp Possible previous storm, irrigation pump only. Damaged meter. Excluded OMS No. 880667 | September | 2012 | 2013Q1 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | UG | Not Veg | 2012-09-25 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 18443 | 19037 | 880665 | 2012-09-25 09:09 | 2012-09-25 11:55 | 166 | 11kV | 166 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122296 Direct call from cust. Burnt off tapping pole MD-60696 Repaired live line | September | 2012 | 2013Q1 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2012-09-25 | N | 166 | N | 5 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 16966 | 3345 | 881003 | 2012-09-25 16:24 | 2012-09-25 16:55 | 30.95 | 11kV | 1671.3 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122298 A & B phase DOLF : 20 Amp | September | 2012 | 2013Q1 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2012-09-25 | N | 30.95 | N | 5 | N | N | 1.1101 | 39.4971 | 1221.3367
[7 empty] | 18102 | 15820 | 881086 | 2012-09-26 02:49 | 2012-09-26 03:44 | 55 | 11kV | 53130 | 966 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Recloser 20397 Pittwater Cabbage Tree, tripped and locked out on IOC and Timed OC. Possum on 11kV UG/OH adjacent S.16251 | September | 2012 | 2013Q1 | 2013 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Not Veg | 2012-09-26 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 38825.8369
[7 empty] | 18078 | 15568 | 881117 | 2012-09-26 08:00 | 2012-09-26 09:10 | 70 | 11kV | 210 | 3 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 122305 C phase DOLF : 10 Amp PIDGEON FOUND AT BOTTOM OF POLE VOLTS 250 LOAD 5 AMPS | September | 2012 | 2013Q1 | 2013 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2012-09-26 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 18400 | 18466 | 881092 | 2012-09-26 05:44 | 2012-09-26 10:54 | 310 | 11kV | 30070 | 97 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122302 1 fault operation 3 phase Earth fault ap issued to repair mains at pole EU-34099 dead pelican found at site Excluded oms 881092 | September | 2012 | 2013Q1 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-09-26 | N | 310 | N | 4 | N | N | 1.1101 | 39.4971 | 21974.2691
[7 empty] | 17053 | 4048 | 919092 | 2012-09-26 12:47 | 2012-09-26 13:55 | 68 | 11kV | 14004 | 256 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 122311 2 fault operations Overcurrent; Earth fault Fdr 34837 is supplying Fdr 34843 via ABS 47462. Fdr 34843 opened in OMS. Backhoe dug up cable 14 Callistemon Cl. Excluded OMS 881317 & 881344 | September | 2012 | 2013Q1 | 2013 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | UG | Not Veg | 2012-09-26 | N | 54.7031 | N | 4 | N | N | 1.1101 | 39.4971 | 10233.7102
[7 empty] | 17694 | 11489 | 881520 | 2012-09-27 02:52 | 2012-09-27 05:15 | 143 | 11kV | 1716 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122315 C phase DOLF Delay in restoration-on call linesman not authorised to replace DOLF. Load readings: 247V; 75/12/65A. Excluded OMS Job No. 881520. | September | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | UG | Not Veg | 2012-09-27 | N | 143 | N | 3 | N | N | 1.1101 | 39.4971 | 1254.0022
[7 empty] | 17916 | 13267 | 881754 | 2012-09-27 13:06 | 2012-09-27 15:55 | 169 | 11kV | 16708 | 272 | HV | Staff Other | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | At S.12630 Peats Ridge, Panel 4 Fdr CB tripped on SEF, 11kV trip. 11kV OH on ground. Refer planned jobs 881947, 881949, 881957, 881958 reconductoring going on, suspect these planned outages triggered fault | September | 2012 | 2013Q1 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2012-09-27 | N | 61.4265 | N | 3 | N | N | 1.1101 | 39.4971 | 12209.7136
[7 empty] | 17893 | 13077 | 881902 | 2012-09-27 19:14 | 2012-09-27 21:50 | 156 | 11kV | 1716 | 11 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | @S6236 Tx2 tripped. Cause: Tx2 failure See 883183 exclude 881902 | September | 2012 | 2013Q1 | 2013 | ZN690:PA15 | ZN690:PA15 | ZN00690/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-09-27 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 1254.0022
[7 empty] | 17076 | 4247 | 881924 | 2012-09-28 01:38 | 2012-09-28 02:48 | 70 | 11kV | 4200 | 60 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | At PT1803 Waninga Aldous The Roadside HDO fuse has blown. Cause: Burnt possum at Base of PT See OMS 882872 881924 881925 | September | 2012 | 2013Q1 | 2013 | ZN847:PA22 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2012-09-28 | N | 70 | N | 12 | N | N | 1.1101 | 39.4971 | 3069.2361
[7 empty] | 17994 | 14176 | 882077 | 2012-09-28 11:20 | 2012-09-28 12:23 | 63 | 11kV | 1638 | 26 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 122339 Emergency pole replacement - JP 76545 Storks Rd, Glen Oak | September | 2012 | 2013Q1 | 2013 | 264:81240 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2012-09-28 | N | 63 | N | 12 | N | N | 1.1101 | 39.4971 | 1197.0021
[7 empty] | 17011 | 3679 | 882069 | 2012-09-28 12:13 | 2012-09-28 13:30 | 77 | 11kV | 77 | 1 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | CC1: 22-"Refer to SOp" | September | 2012 | 2013Q1 | 2013 | ZN15012:PA4 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2012-09-28 | N | 77 | N | 12 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 18308 | 17532 | 882194 | 2012-09-28 14:03 | 2012-09-28 15:21 | 78 | 11kV | 78 | 1 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Wind | N | LID 122342 A phase DOLF : 10 Amp Dead Bird found at sub. TX Volts: Aph - 250V, Bph - 250V, Cph - 252V Excluded OMS No. 882194 | September | 2012 | 2013Q1 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-09-28 | N | 78 | N | 12 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 16939 | 3175 | 882188 | 2012-09-28 13:50 | 2012-09-28 16:45 | 175 | 11kV | 105489 | 810 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | @ zone 15002 Narrabeen panel 8 tripped on Relays: B phase Earth fault , frame leakage fault check, EFI zone earth 11kV trip Flash over on 11kV UGOH near AB 26122 | September | 2012 | 2013Q1 | 2013 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | Unknown | Unknown | 2012-09-28 | N | 130.2333 | N | 12 | N | N | 1.1101 | 39.4971 | 77088.2498
[7 empty] | 18064 | 15447 | 882288 | 2012-09-28 18:15 | 2012-09-28 18:45 | 30 | 11kV | 31770 | 1059 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.12570 Avoca, Panel 9 Fdr CB tripped, reclosed, tripped and locked out on A phase IOC and timed OC, 11kV trip. Tree Branch fell into HV mains near PT.12467 | September | 2012 | 2013Q1 | 2013 | ZN12570:PA9 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Veg | 2012-09-28 | N | 30 | N | 12 | N | N | 1.1101 | 39.4971 | 23216.5789
[7 empty] | 17397 | 7933 | 882303 | 2012-09-28 18:38 | 2012-09-28 19:25 | 47 | 11kV | 10481 | 223 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2835 Burwood - 11kv Panel No.21 "Sub 2081 ADA coles" feeder tripped. Relays: Translay, EFI, Fault check. Signals: 11kv trip, No.2 Group Earth, Zone Earth. Field EFI's: Sub 35650, Sub 48009 @Sub 243 Broughton St: Sw B tripped on Translay. Remarks: UG fault. 11KV fault from Zn2835 Burwood Panel No.21 to Sub 2081 Ada Coles. Caltex service supply point is not present in OMS and is not accounted for Related jobs: #883389, 883388, 882307, 882306, 882303 | September | 2012 | 2013Q1 | 2013 | ZN2835:PA21 | ZN2835:PA21 | ZN02835/000021 | CANADA BAY | UG | Not Veg | 2012-09-28 | N | 47 | N | 12 | N | N | 1.1101 | 39.4971 | 7659.2057
[7 empty] | 17842 | 12649 | 882300 | 2012-09-28 19:10 | 2012-09-28 20:15 | 65 | 11kV | 2600 | 40 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122346 11kV OHM isolated to repair stranding conductor at pole HS-43333. Excluded OMS No. 882300 | September | 2012 | 2013Q1 | 2013 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2012-09-28 | N | 65 | N | 12 | N | N | 1.1101 | 39.4971 | 1900.0033
[7 empty] | 17481 | 8598 | 882139 | 2012-09-28 12:13 | 2012-09-28 20:20 | 487 | 11kV | 57272 | 1151 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | A.OP opened Panel 8 ex S.15012 Killarney for safety after car hit pole near 11kV USL.24837 | September | 2012 | 2013Q1 | 2013 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2012-09-28 | N | 49.7585 | N | 12 | N | N | 1.1101 | 39.4971 | 41852.6884
[7 empty] | 17642 | 10710 | 882274 | 2012-09-28 17:04 | 2012-09-28 21:10 | 246 | 11kV | 1230 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122345 A phase Live Line Clamp 11kV dropper burnt off. Sub isolated for LL crew to repair. Excluded OMS 882274 | September | 2012 | 2013Q1 | 2013 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2012-09-28 | N | 246 | N | 12 | N | N | 1.1101 | 39.4971 | 898.8477
[7 empty] | 17870 | 12867 | 882327 | 2012-09-28 21:16 | 2012-09-28 22:50 | 94 | 11kV | 282 | 3 | HV | Animal Goanna | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | LID 122347 Single phase DOLF : 10 Amp Dead goanna at sub. Excluded OMS 882327. | September | 2012 | 2013Q1 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2012-09-28 | N | 94 | N | 12 | N | N | 1.1101 | 39.4971 | 206.0773
[7 empty] | 17737 | 11852 | 882346 | 2012-09-28 22:30 | 2012-09-28 23:52 | 81.6167 | 11kV | 15099.0833 | 185 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Stolen vehicle hit AB.40898 pole causing to open and damaging blades and contacts | September | 2012 | 2013Q1 | 2013 | ZN12610:PA22 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2012-09-28 | N | 81.6167 | N | 12 | N | N | 1.1101 | 39.4971 | 11033.9648
[7 empty] | 18467 | 19220 | 882365 | 2012-09-29 03:51 | 2012-09-29 11:22 | 451 | 11kV | 11283 | 47 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 122352 3 fault operations Overcurrent pole FS-12935 11kV mains off pin on cross arm on two phases. Light rain during outage. cust reports car hit pole approx 4 mths ago. DQ | September | 2012 | 2013Q1 | 2013 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2012-09-29 | N | 240.0638 | N | 7 | N | N | 1.1101 | 39.4971 | 8245.2836
[7 empty] | 17855 | 12746 | 882450 | 2012-09-29 12:56 | 2012-09-29 14:00 | 64 | 11kV | 128 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 122355 Single phase Live Line Clamp Sub isolated to repair LL Clamp that was found off. Excluded OMS No. 882450 | September | 2012 | 2013Q1 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-09-29 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 93.5386
[7 empty] | 18370 | 18089 | 882462 | 2012-09-29 13:14 | 2012-09-29 16:20 | 186 | 11kV | 9347 | 1577 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby 11KV tripped And closed on O/C Timing Relay lockout relay fault check with efi. Trees on OH O/S 10 Montview Pde See OMS 882932 882934 882462-466-467-469 | September | 2012 | 2013Q1 | 2013 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2012-09-29 | N | 5.9271 | N | 7 | N | N | 1.1101 | 39.4971 | 6830.5119
[7 empty] | 16696 | 1214 | 882492 | 2012-09-29 14:36 | 2012-09-29 17:15 | 158.3167 | 11kV | 12507.0167 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At PT9628 Sylvania Matoong. Footpath phase 31.5A HDO Operated Cause: Tree/branch on OH Mains at 27 Matong Place CC1: 22-"Refer to SOp" | September | 2012 | 2013Q1 | 2013 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Veg | 2012-09-29 | N | 158.3167 | N | 7 | N | N | 1.1101 | 39.4971 | 9139.7589
[7 empty] | 17801 | 12423 | 882513 | 2012-09-29 16:35 | 2012-09-29 18:19 | 103.5167 | 11kV | 136434.2 | 2351 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.12650 West Gosford, Panel 17 Fdr CB tripped on "17L" IOC with efi, 11kV trip, zone earth. Field efi's down at s.18185 AND s.12341. HDO fuse blown at PT.13104 - cause unknown - Fdr Prot'n/Auto Close Non auto | September | 2012 | 2013Q1 | 2013 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Veg | 2012-09-29 | N | 58.0324 | N | 7 | N | N | 1.1101 | 39.4971 | 99702.0892
[7 empty] | 17975 | 14023 | 882458 | 2012-09-29 13:09 | 2012-09-29 20:01 | 412 | 11kV | 32411 | 216 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 122356 2 fault operations Earth fault 1 phase off 11kV OHM down at poles GQ-57475, GQ-55402 & GQ-55403. Excluded OMS No. 882458 + 882460 | September | 2012 | 2013Q1 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2012-09-29 | N | 150.0509 | N | 7 | N | N | 1.1101 | 39.4971 | 23685.0028
[7 empty] | 18475 | 19498 | 883207 | 2012-09-29 20:43 | 2012-09-29 20:52 | 9 | 11kV | 1179 | 131 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122360 Switching error on restoration of LID Unplanned outage 122356/ OMS 883201 | September | 2012 | 2013Q1 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2012-09-29 | N | 9 | N | 7 | N | N | 1.1101 | 39.4971 | 861.5784
[7 empty] | 16877 | 2531 | 882648 | 2012-09-30 20:46 | 2012-09-30 21:20 | 34 | 11kV | 29138 | 857 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At AB 20521 centre phase load side bond burnt off | September | 2012 | 2013Q1 | 2013 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2012-09-30 | N | 34 | N | 2 | N | N | 1.1101 | 39.4971 | 21293.191
[7 empty] | 18446 | 19074 | 882647 | 2012-09-30 20:44 | 2012-09-30 23:50 | 185.9 | 11kV | 185.9 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S49253 Seaview Victoria No.2 RMI Transformer switch tripped 2x120HFNA 80amp fuse blown Cause: Tx failure 11kv/415v transformer in kiosk appears to have failed. Permit left for T/Con. See 883208 GIS 882647 | September | 2012 | 2013Q1 | 2013 | ZN398:PA19 | ZN398:PA19 | ZN00398/000019 | INNER WEST | UG | Not Veg | 2012-09-30 | N | 185.9 | N | 2 | N | N | 1.1101 | 39.4971 | 135.8502
[7 empty] | 16503 | 21 | 882665 | 2012-10-01 00:19 | 2012-10-01 05:15 | 296 | 11kV | 21016 | 71 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 122364 Section isolated to replace pole AK-61404 damaged by vehicle. No protection operation. Excluded OMS 882665 | October | 2012 | 2013Q2 | 2013 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2012-10-01 | N | 296 | N | 5 | N | N | 1.1101 | 39.4971 | 15357.8729
[7 empty] | 18218 | 16738 | 882749 | 2012-10-01 12:47 | 2012-10-01 13:44 | 57.3833 | 11kV | 2232.45 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122368 B phase DOLF : 50 Amp Volts = 248. Amps = 170, 200, 190. Excluded OMS 882749, 882753, 882754 & 882761 | October | 2012 | 2013Q2 | 2013 | 208:72 | 257:81999 | ZN00257/081999 | NEWCASTLE | UG | Not Veg | 2012-10-01 | N | 53.1536 | N | 5 | N | N | 1.1101 | 39.4971 | 1631.4086
[7 empty] | 17886 | 13005 | 882766 | 2012-10-01 14:54 | 2012-10-01 16:11 | 77 | 11kV | 170090 | 2300 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn10994 Mortdale Pa20 fdr opened & locked out on IOC, recloser lockout & EFI EFI's - S10535 UG Cable fault btw s10535 & S10423 See 883220,1 GIS 883228 Exclude 882766,7 | October | 2012 | 2013Q2 | 2013 | ZN10994:PA20 | ZN10994:PA20 | ZN10994/000020 | GEORGES RIVER | UG | Not Veg | 2012-10-01 | N | 73.9522 | N | 5 | N | N | 1.1101 | 39.4971 | 124296.7552
[7 empty] | 16530 | 165 | 882824 | 2012-10-01 21:52 | 2012-10-01 23:01 | 69 | 11kV | 111642 | 1618 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.12640 Umina, Panel 7 Fdr CB tripped, reclosed and locked out on A and B phase OC, reclose timing and lockout relays. DOP patrolled feeder and area where reports of explosions were and could not find anything CC1: 22-"Refer to SOp" | October | 2012 | 2013Q2 | 2013 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Veg | 2012-10-01 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 81584.6807
[7 empty] | 18229 | 16880 | 882797 | 2012-10-01 21:27 | 2012-10-02 00:48 | 201 | 11kV | 187037 | 3267 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At Zn35500 Top Ryde Panel 28 Tripped on A B and C phase IOC. Cause: Possum came into contact with UGOH near S47772. See OMS 883056-059-060-064-063-067 882797 | October | 2012 | 2013Q2 | 2013 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2012-10-01 | N | 57.2504 | N | 5 | N | N | 1.1101 | 39.4971 | 136681.1229
[7 empty] | 17659 | 10924 | 884267 | 2012-10-02 09:14 | 2012-10-02 10:50 | 96 | 11kV | 8256 | 86 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn4990 City Central Panel 55H/56H tripped on: - Relays: - IO Earth fault/No6 low earth fault Remarks: UG fault. Cable fault Related jobs: #884285, 884287, 884267 | October | 2012 | 2013Q2 | 2013 | ZN4990:PA55 56GHJ | ZN4990:PA55 56GHJ | ZN04990/55 56GHJ | SYDNEY | UG | Not Veg | 2012-10-02 | N | 96 | N | 3 | N | N | 1.1101 | 39.4971 | 6033.2413
[7 empty] | 17145 | 4916 | 883293 | 2012-10-02 15:46 | 2012-10-02 16:40 | 54 | 11kV | 4428 | 82 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122377 C phase DOLF : 20 Amp Low volts due to blown C Phase DOLF. Fuse blew on inrush when section energised. Excluded OMS 882293 & OMS 883304 | October | 2012 | 2013Q2 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | UG | Not Veg | 2012-10-02 | N | 54 | N | 3 | N | N | 1.1101 | 39.4971 | 3235.8518
[7 empty] | 18409 | 18643 | 883365 | 2012-10-02 22:31 | 2012-10-03 09:00 | 629 | 11kV | 808521 | 1386 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn4990 City Central 55/56 G Interrupted by Aop for repairs on 55/56 H&J. See separate DMAs on 55/56H feeder and 55/56J feeder and 55A feeder and 55/56F pilot. Remarks: Cable fault on 55H feeder also caused damage to 55/56 G&J and 55A feeder and 55/56F pilot. The 55/56 G feeder was interrupted to effectivly repair the 55/56H & J feeder/pilots. Related jobs: #884318, 884315, 884313, 884310, 884312, 884320, 884325, 884327, 884328, 884326, 884322, 884306, 883365 | October | 2012 | 2013Q2 | 2013 | ZN4990:PA55 56GHJ | ZN4990:PA55 56GHJ | ZN04990/55 56GHJ | SYDNEY | UG | Not Veg | 2012-10-02 | N | 583.3485 | N | 3 | N | N | 1.1101 | 39.4971 | 590843.2995
[7 empty] | 16529 | 154 | 883574 | 2012-10-03 11:37 | 2012-10-03 11:55 | 18 | 11kV | 4572 | 254 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122389 Operating error occured during reconnect SI 25396 Contributing factor was a false SCADA indication - indicating closed whilst actually open Excluded OMS report # 883574. | October | 2012 | 2013Q2 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2012-10-03 | N | 18 | N | 5 | N | N | 1.1101 | 39.4971 | 3341.0827
[7 empty] | 18008 | 14283 | 883579 | 2012-10-03 11:52 | 2012-10-03 14:44 | 172 | 11kV | 85344 | 1513 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 122390 & LID 122391 2 fault operations B & C phase Overcurrent; Earth fault UGOH failed on pole IT-93014 Also DOLF at sub 12281 had defective contacts RTS 13:15 during this outage. Excluded OMS 883579, 883584, 883585, 883586, 883587, 883589 & 883594 | October | 2012 | 2013Q2 | 2013 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | Unknown | Unknown | 2012-10-03 | N | 56.4071 | N | 5 | N | N | 1.1101 | 39.4971 | 62366.878
[7 empty] | 17116 | 4531 | 883809 | 2012-10-03 18:21 | 2012-10-03 19:55 | 94 | 11kV | 94 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122393 Single phase DOLF : 10 Amp Excluded OMS 883809 | October | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-10-03 | N | 94 | N | 5 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 16543 | 279 | 883812 | 2012-10-03 18:28 | 2012-10-03 20:45 | 137 | 11kV | 137 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122395 Single phase LL Clamp dislodged from Mains. No Protection Operation Excluded OMS 883812 | October | 2012 | 2013Q2 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-10-03 | N | 137 | N | 5 | N | N | 1.1101 | 39.4971 | 100.1156
[7 empty] | 16946 | 3244 | 883828 | 2012-10-03 22:17 | 2012-10-04 01:23 | 186 | 11kV | 135413 | 1699 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kV Panel No1 ex S14068 Noraville Aux Bat across 11kV brought down main adjacent AB42404 883974/975/976 883828 883829 | October | 2012 | 2013Q2 | 2013 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2012-10-03 | N | 79.7016 | N | 5 | N | N | 1.1101 | 39.4971 | 98955.8264
[7 empty] | 17242 | 6438 | 883833 | 2012-10-04 05:06 | 2012-10-04 07:05 | 119 | 11kV | 13090 | 110 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | At PT1193 Bouvardia St, (ex panel 38 'AB 893, S.5076 Highclere Punch' Fdr) replaced footpath phase BBLAS 31.5 amp HV drop out fuse. Signals: Zone earth, Tx5 Group earth Remarks: At PT1193 Bouvardia St, suspect animal on Tx bushing as shroud on Tx connection missing and centre phase Tx shroud displaced. Note that PT pole is also condemned. Related jobs: #883833, 886423 | October | 2012 | 2013Q2 | 2013 | ZN2310:PA38 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-10-04 | N | 119 | N | 3 | N | N | 1.1101 | 39.4971 | 9565.7859
[7 empty] | 18028 | 14678 | 884217 | 2012-10-04 19:25 | 2012-10-04 20:15 | 50 | 11kV | 8150 | 163 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | At S4225 Forster Orchard 400A fuse blown on A and C phase of distributor 1. At S4225 Forster Orchard 400A fuse blown on A and C phase of distributor 2 Cause: Celco Cable Hit OH. Truck Hit Optus wire - Clashing distributor See OMS 887005-887007-887011 884217/217/219 | October | 2012 | 2013Q2 | 2013 | ZN4545:PA44 | ZN4545:PA35 | ZN04545/000035 | RYDE | OH | Not Veg | 2012-10-04 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 5955.7796
[7 empty] | 17358 | 7550 | 884223 | 2012-10-04 19:41 | 2012-10-04 21:22 | 101 | 11kV | 101 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 122407 A phase DOLF : 10 Amp Fuse fatigue Excluded OMS 884223 | October | 2012 | 2013Q2 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-10-04 | N | 101 | N | 3 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 18354 | 17891 | 884408 | 2012-10-05 12:28 | 2012-10-05 14:35 | 127 | 11kV | 381 | 3 | HV | Overload | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | S.6459 Boorea Nyrang No.1 all three RMCB's tripped. Ex panel 15 "Carter Australia" fdr Relays - No.1 Supply BBOC relay operated. Remarks: overload. Customer drawing excessive load from the No.1 supply. Referred. Related jobs: #884408, 884982, 884980 | October | 2012 | 2013Q2 | 2013 | ZN2466:PA15 | ZN1068:PA19 | ZN01068/000019 | CUMBERLAND | Unknown | Not Veg | 2012-10-05 | N | 127 | N | 3 | N | N | 1.1101 | 39.4971 | 278.4236
[7 empty] | 18480 | 19567 | 884506 | 2012-10-05 16:00 | 2012-10-05 17:00 | 60 | 11kV | 1920 | 32 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Section of Pnl.5 Wyong interupted between LK43590 to LK43695 for safety reason To allow OH mains to tie in 11kV sitting on cross arm and replace 2 broken insulators. | October | 2012 | 2013Q2 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2012-10-05 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 1403.0794
[7 empty] | 17795 | 12356 | 884550 | 2012-10-05 19:28 | 2012-10-05 20:20 | 52 | 11kV | 5876 | 113 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | At PT2400 Meadowbank Darwin the centre phase 11kV HDO blown. Possum at PT2400 Meadowbank Darwin no apparent damage to wires. See OMS 887181 887182 884550 884553 884559 | October | 2012 | 2013Q2 | 2013 | ZN4545:PA25 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Not Veg | 2012-10-05 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 4294.0075
[7 empty] | 17194 | 5862 | 884592 | 2012-10-06 08:51 | 2012-10-06 09:50 | 59 | 11kV | 26770 | 521 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S195 Pymble Panel 22 Panel 22 Tripped on Relays: EF- EFI - Fault Check. 11kV UG cable fault from S6925 Pacific Mona to S4455 Pacific Boomsbury. See OMS 886055 886057 884592 | October | 2012 | 2013Q2 | 2013 | ZN195:PA22 | ZN195:PA10 | ZN00195/000010 | KU-RING-GAI | UG | Not Veg | 2012-10-06 | N | 51.382 | N | 6 | N | N | 1.1101 | 39.4971 | 19562.7264
[7 empty] | 16989 | 3499 | 884636 | 2012-10-06 12:40 | 2012-10-06 13:00 | 20 | 11kV | 980 | 49 | HV | Equipment Failed in Service | Equipment Failure | Pillar | Unplanned | Unselected | N | LID 122421 3 phase Isolation Pillar HR-62746 found damaged. | October | 2012 | 2013Q2 | 2013 | 501:48118 | 528:83011 | ZN00528/083011 | MAITLAND | UG | Not Veg | 2012-10-06 | N | 20 | N | 6 | N | N | 1.1101 | 39.4971 | 716.1551
[7 empty] | 17699 | 11514 | 884638 | 2012-10-06 12:16 | 2012-10-06 13:10 | 54 | 11kV | 116298 | 2377 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn3155 Double Bay Pa23 tripped Relays: bph OC E/F, Fault Check, EFI Siganls: 11kv trip, tx3 group earth, Zone earth EFI's S48928 S2816 Causde: UG Fault Remarks: section of 11kv u?G fdr btw S2816 Sw/B and S8234 Sw/A failed See 885013,5 exclude 884638 | October | 2012 | 2013Q2 | 2013 | ZN3155:PA23 | ZN3155:PA40 | ZN03155/000040 | WOOLLAHRA | UG | Not Veg | 2012-10-06 | N | 48.9264 | N | 6 | N | N | 1.1101 | 39.4971 | 84987.1482
[7 empty] | 17095 | 4371 | 884666 | 2012-10-06 15:14 | 2012-10-06 16:04 | 50 | 11kV | 62500 | 1250 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 15 tripped reclosed tripped and locked out on A and C phase O/C, Timing and lockout relay. Tree branch on mains o/s 15 Cobran Rd Cheltenman - Removed By Dop. See OMS 887125 887124 884679/673/671/670668/666 Based on customer calls suspect S4971#3 was in parallel with Panel 15 at the time of interruption. | October | 2012 | 2013Q2 | 2013 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2012-10-06 | N | 50 | N | 6 | N | N | 1.1101 | 39.4971 | 45673.1566
[7 empty] | 17097 | 4386 | 884684 | 2012-10-06 15:21 | 2012-10-06 17:05 | 104 | 11kV | 4784 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S35802 Young Chilton supply mannually interrupted on A B and Cphase of idstributor 1. Cause: Interrupted so lineworker could remove tree branch from mains in Chilton Pde near Davidson Ave Warrawee. See OMS 887115 884685/683/686/684/687. | October | 2012 | 2013Q2 | 2013 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | OH | Veg | 2012-10-06 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 3496.0061
[7 empty] | 17598 | 9820 | 884717 | 2012-10-06 21:02 | 2012-10-07 01:10 | 248 | 11kV | 1984 | 8 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT11507 - Centre and Footpath Phase 20A Drop out Fuses operated Possum on PT | October | 2012 | 2013Q2 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2012-10-06 | N | 248 | N | 6 | N | N | 1.1101 | 39.4971 | 1449.8487
[7 empty] | 17124 | 4616 | 884741 | 2012-10-07 07:35 | 2012-10-07 12:00 | 264.7167 | 11kV | 3441.3167 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122426 Single phase LLC dropper broken at pole 8H-20056. | October | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-10-07 | N | 264.7167 | N | 5 | N | N | 1.1101 | 39.4971 | 2514.8127
[7 empty] | 17211 | 6060 | 884792 | 2012-10-07 12:17 | 2012-10-07 14:41 | 144 | 11kV | 16848 | 117 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 122429 Small grass fire started. Follows earlier T & R Fdr 35193 see report 122424/OMS 885025 Isolated to repair broken xarm pole MD-90922 | October | 2012 | 2013Q2 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2012-10-07 | N | 144 | N | 5 | N | N | 1.1101 | 39.4971 | 12312.0215
[7 empty] | 17846 | 12678 | 884803 | 2012-10-07 13:20 | 2012-10-07 17:48 | 268 | 11kV | 1072 | 4 | HV | Fire (non-electrical) | Adverse Weather/Environment | Pole | Unplanned | Unselected | N | LID 122427 Single phase Pole VP-70231 replaced after bushfire damage. Excluded OMS No 884808. | October | 2012 | 2013Q2 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2012-10-07 | N | 268 | N | 5 | N | N | 1.1101 | 39.4971 | 783.386
[7 empty] | 18055 | 15391 | 885165 | 2012-10-07 19:05 | 2012-10-07 20:25 | 80 | 11kV | 1600 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong Pnl.5 - Section of 11kV feeder from REC4511 to LB45100 interrupted for safety CCT resting on crossarm reported by Wyong On call | October | 2012 | 2013Q2 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2012-10-07 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 1169.2328
[7 empty] | 17748 | 11937 | 884854 | 2012-10-07 21:23 | 2012-10-07 22:34 | 71 | 11kV | 148881 | 2136 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12610 Long Jetty Pnl.13 tripped on Earth Fault Abnormal: AB41135 CLOSED - AB40898 OPEN UG cable fault between Long Jetty Zone and USL44363 | October | 2012 | 2013Q2 | 2013 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | UG | Not Veg | 2012-10-07 | N | 69.7008 | N | 5 | N | N | 1.1101 | 39.4971 | 108797.8436
[7 empty] | 18299 | 17460 | 884895 | 2012-10-08 08:06 | 2012-10-08 09:21 | 75 | 11kV | 2400 | 33 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | @Zn1788 Matraville Pa21 fdr tripped Relays: Earth Fault, EFI Signals: 11kv trip, Tx3 Group Earth EFI's S7169 (incorrect indication) Cause: UG Cable damaged by contractor Remarks: ASP Damaged HV cable on crner Botany Rd and McCauley st Port Botany 11kv fdr from Zn1788Pa21 to S7169 Sw/A to S5180 Sw/A to S48354 Sw/B See 885542,5 Exlude 884895 | October | 2012 | 2013Q2 | 2013 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | UG | Not Veg | 2012-10-08 | N | 72.7273 | N | 2 | N | N | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 17107 | 4483 | 884966 | 2012-10-08 09:09 | 2012-10-08 11:35 | 146 | 11kV | 292 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | L<ID 122437 B & C phase DOLF : 20 Amp Excluded OMS 884966 | October | 2012 | 2013Q2 | 2013 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | UG | Not Veg | 2012-10-08 | N | 146 | N | 2 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 16756 | 1660 | 885781 | 2012-10-09 16:39 | 2012-10-09 17:28 | 48.85 | 11kV | 75131.3 | 1538 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Unselected | N | At S.15005 Belrose Panel 8 Fdr Cb tripped on B and C pghase IOC, 11kV trip. No foiled efi's operated. Cause unknown | October | 2012 | 2013Q2 | 2013 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Veg | 2012-10-09 | N | 48.85 | N | 4 | N | N | 1.1101 | 39.4971 | 54903.738
[7 empty] | 16546 | 302 | 885727 | 2012-10-09 14:59 | 2012-10-09 18:00 | 181 | 11kV | 543 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122453 A phase DOLF : 10 Amp Excluded OMS 885727 | October | 2012 | 2013Q2 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | UG | Not Veg | 2012-10-09 | N | 181 | N | 4 | N | N | 1.1101 | 39.4971 | 396.8084
[7 empty] | 18465 | 19208 | 885796 | 2012-10-09 17:11 | 2012-10-09 18:30 | 79 | 11kV | 22752 | 288 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Sectiion of Panel 10 @ Umina Zone isolated from S18775 Sw/B to AB42060 to AB43812 Defeective Air Break switch tracking down pole. | October | 2012 | 2013Q2 | 2013 | ZN12640:PA10 | ZN12640:PA10 | ZN12640/000010 | CENTRAL COAST | OH | Not Veg | 2012-10-09 | N | 79 | N | 4 | N | N | 1.1101 | 39.4971 | 16626.4905
[7 empty] | 17877 | 12912 | 885800 | 2012-10-09 17:18 | 2012-10-09 18:34 | 75.9167 | 11kV | 406.55 | 7 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 122455 A phase DOLF : 20 Amp. BIRD ON ARRESTOR. VOLTS = 247 | October | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2012-10-09 | N | 58.0786 | N | 4 | N | N | 1.1101 | 39.4971 | 297.0947
[7 empty] | 16618 | 781 | 886493 | 2012-10-10 12:10 | 2012-10-10 12:25 | 15 | 11kV | 330 | 22 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 122469 generator failed 5 minutes after being connected in planned switching SINO 25362 or OMS 886756 Aggreko Generator failed unexpectedly after taking load on planned switching beyond 40460 | October | 2012 | 2013Q2 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | Unknown | Not Veg | 2012-10-10 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 16929 | 3095 | 885977 | 2012-10-10 10:03 | 2012-10-10 18:00 | 477 | 11kV | 18297 | 241 | HV | Staff Other | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | LID 122465 Staff cut incorrect cable | October | 2012 | 2013Q2 | 2013 | 243:80077 | 243:80077 | ZN00243/080077 | LAKE MACQUARIE | UG | Not Veg | 2012-10-10 | N | 75.9212 | N | 4 | N | N | 1.1101 | 39.4971 | 13370.9079
[7 empty] | 17500 | 8842 | 886313 | 2012-10-10 18:15 | 2012-10-10 19:13 | 58 | 11kV | 1786 | 39 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S874 Concord P23 Pomeroy Underwood fdr tripped on B phase OC & Earth Fault, EFI EFIs @ S35117, S1024, S3907, S6564 ABNORMALS: SWP @ S3906 DJS Homebush No.1 closed, SWA @ S35176 Pomeroy Underwood open programmed outage #298710 Remarks: cause not ascertained. Suspect ug fault. Related jobs: #886313, 886323, 887138, 887136 | October | 2012 | 2013Q2 | 2013 | ZN874:PA16 | ZN36000:PA12 | ZN36000/000012 | CANADA BAY | UG | Not Veg | 2012-10-10 | N | 45.7949 | N | 4 | N | N | 1.1101 | 39.4971 | 1305.1561
[7 empty] | 18324 | 17719 | 887873 | 2012-10-11 08:45 | 2012-10-11 09:05 | 20 | 11kV | 440 | 22 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122477 During SI L0559 Congewai Gen tripped after Synchronising to the network and also blew LF 40460. | October | 2012 | 2013Q2 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-10-11 | N | 20 | N | 7 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 16798 | 2030 | 886358 | 2012-10-11 04:22 | 2012-10-11 09:45 | 323 | 11kV | 45262 | 466 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 2378 Dural Pacific Tripped Reclosed Tripped and locked out on IOC Cause: 11kV down in LV near PT1797 See OMS 887188 887190 887192 | October | 2012 | 2013Q2 | 2013 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Not Veg | 2012-10-11 | N | 97.1288 | N | 7 | N | N | 1.1101 | 39.4971 | 33076.1346
[7 empty] | 17466 | 8481 | 886398 | 2012-10-11 08:19 | 2012-10-11 10:55 | 156 | 11kV | 312 | 2 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 122484 Single phase DOLF : 10 Amp Dead possum found at sub. Excluded OMS 886398 | October | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-10-11 | N | 156 | N | 7 | N | N | 1.1101 | 39.4971 | 228.0004
[7 empty] | 17775 | 12121 | 886664 | 2012-10-11 12:10 | 2012-10-11 14:55 | 165 | 11kV | 495 | 3 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 122487 3 phase interruption No protection operated, interruption was for safety to issue an access permit and remove the tree fallen onto the 11kV at pole OR-70047 Fenningham island Rd. Excluded OMS 886461 | October | 2012 | 2013Q2 | 2013 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2012-10-11 | N | 165 | N | 7 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 18398 | 18450 | 886751 | 2012-10-11 15:07 | 2012-10-11 16:17 | 70 | 11kV | 1750 | 25 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 Meadowbank Panel 9 Tripped on B phase earth leakage- EFI- Fault Check Cag Relay. Cause: Front Line Feeder failure See OMS 886952 886751 | October | 2012 | 2013Q2 | 2013 | ZN4545:PA9 | ZN4545:PA9 | ZN04545/000009 | CANADA BAY | UG | Not Veg | 2012-10-11 | N | 70 | N | 7 | N | N | 1.1101 | 39.4971 | 1278.8484
[7 empty] | 18154 | 16112 | 886776 | 2012-10-11 15:52 | 2012-10-11 19:05 | 193 | 11kV | 5597 | 29 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 122490 B phase DOLF : 16 Amp L.V. reported down Excluded OMS 886780 & 886776 | October | 2012 | 2013Q2 | 2013 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | UG | Not Veg | 2012-10-11 | N | 193 | N | 7 | N | N | 1.1101 | 39.4971 | 4090.1225
[7 empty] | 17524 | 8986 | 886848 | 2012-10-11 18:29 | 2012-10-11 20:40 | 131 | 11kV | 21484 | 164 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Ex Pnl.2 Peats Ridge - 11kV feeder isolated from AB42632 to AB43179 - rest of feeder interrupted 11kV cross arm split and 11kV insultor not secure near PT47195. Reported to control room by portfolio Manager Steve Cawley repairs done immdiately | October | 2012 | 2013Q2 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2012-10-11 | N | 131 | N | 7 | N | N | 1.1101 | 39.4971 | 15699.8735
[7 empty] | 17206 | 5958 | 886154 | 2012-10-10 13:37 | 2012-10-12 04:10 | 2313 | 11kV | 39510.4333 | 257 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 122474 Fault. Section isolated. to be tested 11/10/12. Excluded OMS # 886154 | October | 2012 | 2013Q2 | 2013 | 240:34843 | 240:34843 | ZN00240/034843 | NEWCASTLE | UG | Not Veg | 2012-10-10 | N | 153.7371 | N | 4 | N | N | 1.1101 | 39.4971 | 28873.0593
[7 empty] | 17519 | 8964 | 887929 | 2012-10-12 08:05 | 2012-10-12 08:20 | 15 | 11kV | 330 | 22 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 122501 Congewai generator failed, exact cause of the generator failure unknown. | October | 2012 | 2013Q2 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | Unknown | Not Veg | 2012-10-12 | N | 15 | N | 3 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 18292 | 17372 | 887202 | 2012-10-12 14:26 | 2012-10-12 17:55 | 209 | 11kV | 8875 | 74 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of pnl.8 Wyong - REC 48425 Kangy Angy tripped on SEF Tree brought down wires at PT11272 see 887686 887687 | October | 2012 | 2013Q2 | 2013 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Veg | 2012-10-12 | N | 119.9324 | N | 3 | N | N | 1.1101 | 39.4971 | 6485.5882
[7 empty] | 17897 | 13110 | 887309 | 2012-10-12 17:32 | 2012-10-12 19:15 | 103 | 11kV | 824 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122510 B & C phase DOLF : 10 Amp Excluded OMS 887309 & 887313 | October | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-10-12 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 602.1549
[7 empty] | 17354 | 7497 | 887506 | 2012-10-14 01:08 | 2012-10-14 01:42 | 34 | 11kV | 4318 | 127 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | AT PT1423 Pellisier Delange interrupted by DOp due to ugoh failure Cause: See Related Meadowbank Panel 17 feeder trip. UGOH failure 887657-654-512-517-506 | October | 2012 | 2013Q2 | 2013 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | Unknown | Unknown | 2012-10-14 | N | 34 | N | 3 | N | N | 1.1101 | 39.4971 | 3155.467
[7 empty] | 16582 | 546 | 887516 | 2012-10-14 04:32 | 2012-10-14 05:07 | 35 | 11kV | 41895 | 1197 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.19 tripped on A & B phase IOC (19R leg) Fruit bat on mains outside 32 Lakedge Ave - No reclose on panel | October | 2012 | 2013Q2 | 2013 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2012-10-14 | N | 35 | N | 3 | N | N | 1.1101 | 39.4971 | 30615.6303
[7 empty] | 18269 | 17195 | 887535 | 2012-10-14 08:56 | 2012-10-14 09:50 | 54 | 11kV | 4266 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122525 3 fault operation B & C phase Overcurrent Excluded OMS 887535 & 887537 | October | 2012 | 2013Q2 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2012-10-14 | N | 54 | N | 3 | N | N | 1.1101 | 39.4971 | 3117.467
[7 empty] | 17685 | 11392 | 887612 | 2012-10-15 04:31 | 2012-10-15 06:03 | 92 | 11kV | 46307 | 504 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn931 Darlinghurst 11kv OCB Pa13 fdr tripped on: Relays-Zn Earth, Group Earth, Earth, Earth Fault, EFI EFI's- Nil Signals-11kv trip Cause: UG Fault Remarks: Suspect 11kv fdr fault from S35244Sw/B to S8948Sw/A to S3302Sw/A See 887740,4 exclude 887612 | October | 2012 | 2013Q2 | 2013 | ZN931:PA13 | ZN931:PA13 | ZN00931/000013 | WOOLLAHRA | UG | Not Veg | 2012-10-15 | N | 91.879 | N | 5 | N | N | 1.1101 | 39.4971 | 33839.7898
[7 empty] | 17959 | 13735 | 887616 | 2012-10-15 05:54 | 2012-10-15 07:20 | 86 | 11kV | 154221 | 1886 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S15014 Mona Vale Panel 19 Tripped on Relays: Earth Fault Field EFI's - None. NO EFI fitted at S15225 Cause: UG cable fault between S15225 Darley Barrenjoey to S16696 Darley Stanley See OMS 887807 887809 887810 | October | 2012 | 2013Q2 | 2013 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | UG | Not Veg | 2012-10-15 | N | 81.7715 | N | 5 | N | N | 1.1101 | 39.4971 | 112700.1581
[7 empty] | 18522 | 20066 | 887617 | 2012-10-15 06:34 | 2012-10-15 08:09 | 95 | 11kV | 1140 | 12 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT11180 Hunts Greta 16Amp HV fuse blown Possum found at base of pole | October | 2012 | 2013Q2 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2012-10-15 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 833.0784
[7 empty] | 17955 | 13706 | 899701 | 2012-10-15 07:43 | 2012-10-15 08:24 | 41 | 11kV | 76260 | 1860 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S15014 Mona Vale Section of Panel 11 From Rec20397 Pittwater Cabbage Tree lost supply Cause: Bond off UGOH from S16490 to REc20397 Pittwater See OMS 887822 | October | 2012 | 2013Q2 | 2013 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Not Veg | 2012-10-15 | N | 41 | N | 5 | N | N | 1.1101 | 39.4971 | 55728.5587
[7 empty] | 17770 | 12088 | 888102 | 2012-10-15 23:43 | 2012-10-16 01:05 | 82 | 11kV | 63793 | 937 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12690 Berkeley Vale Pnl.6 tripped & reclosed on Earth Fault EFI reclose timing Primary cause not ascterained. However, fault current burnt off bond footpath phase off USL43476 see 888643 888642 | October | 2012 | 2013Q2 | 2013 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2012-10-15 | N | 68.0822 | N | 5 | N | N | 1.1101 | 39.4971 | 46618.0428
[7 empty] | 18318 | 17649 | 888122 | 2012-10-16 07:53 | 2012-10-16 09:40 | 107 | 11kV | 321 | 3 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 122545 Single phase DOLF : 10 Amp Burnt possum at Base of pole 243Volts Excluded OMS # 888122 & 888123 | October | 2012 | 2013Q2 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2012-10-16 | N | 107 | N | 7 | N | N | 1.1101 | 39.4971 | 234.5773
[7 empty] | 18253 | 17091 | 888199 | 2012-10-16 09:27 | 2012-10-16 10:45 | 78 | 11kV | 9828 | 126 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | HV A phase fuse blwn. DOp Brooks suspects defective TX Work Permit left for T/COn See 890282 exclude 888199 | October | 2012 | 2013Q2 | 2013 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | UG | Not Veg | 2012-10-16 | N | 78 | N | 7 | N | N | 1.1101 | 39.4971 | 7182.0125
[7 empty] | 17590 | 9775 | 888160 | 2012-10-16 08:42 | 2012-10-16 12:25 | 223 | 11kV | 223 | 1 | HV | Animal Other | Animal | Stay Wire | Unplanned | No Weather Impact | N | LID 122553 single phase Broken Stay. Repaired by Bruce Blackadder repaired stay due to cows rubbing and causing it to fail | October | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2012-10-16 | N | 223 | N | 7 | N | N | 1.1101 | 39.4971 | 162.9618
[7 empty] | 18151 | 16097 | 888112 | 2012-10-16 06:54 | 2012-10-16 13:39 | 405 | 11kV | 60103 | 673 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122549 B phase Burnt off B phase tapping at pole IR-12224 Excluded OMS 888112, 888119, 888385 & 888392 | October | 2012 | 2013Q2 | 2013 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2012-10-16 | N | 89.3061 | N | 7 | N | N | 1.1101 | 39.4971 | 43921.4997
[7 empty] | 16737 | 1498 | 888442 | 2012-10-16 13:28 | 2012-10-16 14:12 | 44 | 11kV | 87231 | 1993 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @Zn10990 Arncliffe Pa2 tripped on: Relays: OC A Phase Signals: Nil Cause: Not Ascertained Remarks: Cause not found. Mains to Patrol See 888830,2 Exlude 888442 | October | 2012 | 2013Q2 | 2013 | ZN10990:PA2 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Veg | 2012-10-16 | N | 43.7687 | N | 7 | N | N | 1.1101 | 39.4971 | 63745.8419
[7 empty] | 16977 | 3397 | 888219 | 2012-10-16 09:45 | 2012-10-16 20:00 | 614.6667 | 11kV | 45678 | 171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S5299 Fontenoy Tuckwell 400A fuse blown on A B and C phase of distributor 3 At S5299 Fontenoy Tuckwell supply manually interrupted on A B and Cphase of distributor 2 and 4 See OMS 890244 888219 888579 | October | 2012 | 2013Q2 | 2013 | ZN8000:PA19 | ZN8000:PA19 | ZN08000/000019 | RYDE | UG | Not Veg | 2012-10-16 | N | 267.1228 | N | 7 | N | N | 1.1101 | 39.4971 | 33380.1351
[7 empty] | 16630 | 850 | 888631 | 2012-10-16 23:59 | 2012-10-17 01:25 | 86 | 11kV | 5418 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S5250 Morshead Sturdee 400A fuse blown on A and B phase of distributor 2 see OMS 889266 888631 | October | 2012 | 2013Q2 | 2013 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2012-10-16 | N | 86 | N | 7 | N | N | 1.1101 | 39.4971 | 3959.3146
[7 empty] | 17405 | 8011 | 888653 | 2012-10-17 08:07 | 2012-10-17 13:45 | 338.45 | 11kV | 1823.45 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122571 11kV tapping burnt off at pole MD-90675 tee to subs 46734 & 47592 Excluded OMS 888653 | October | 2012 | 2013Q2 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2012-10-17 | N | 202.6056 | N | 5 | N | N | 1.1101 | 39.4971 | 1332.5235
[7 empty] | 17840 | 12638 | 889028 | 2012-10-17 15:35 | 2012-10-17 16:35 | 60 | 11kV | 21900 | 365 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Interrupted by DOp for emergency repairs to 11kv adj PT10217 Cambridge Forest See 889734 exclude 889028 | October | 2012 | 2013Q2 | 2013 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2012-10-17 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 16003.8741
[7 empty] | 16956 | 3280 | 888804 | 2012-10-17 10:53 | 2012-10-17 17:20 | 387 | 11kV | 427433 | 1994 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 122569 Cable fault | October | 2012 | 2013Q2 | 2013 | 232:11455 | 232:33409 | ZN00232/033409 | PORT STEPHENS | UG | Not Veg | 2012-10-17 | N | 214.3596 | N | 5 | N | N | 1.1101 | 39.4971 | 312355.4293
[7 empty] | 17235 | 6309 | 888879 | 2012-10-17 12:21 | 2012-10-17 18:14 | 353 | 11kV | 49420 | 140 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Wind Strong | N | LID 122570 1 fault operation, Earth fault; Sensitive Earth fault see T&R 122568 (OMS 889189) also Contract tree trimmers felled a tree onto mains adjacent pole AS-60023 Putty Rd. Prot SE/F, E/F 12Amps. | October | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-10-17 | N | 353 | N | 5 | N | N | 1.1101 | 39.4971 | 36114.6784
[7 empty] | 17982 | 14126 | 889055 | 2012-10-17 16:55 | 2012-10-17 18:53 | 118 | 11kV | 86489 | 902 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S2365 Epping Panel 12 Tripped on Relays: Earth Fault, Frame Leakage, Fault Check and EFI Signals: 11kV Trip, TX1, Group Earth and Zone Earth. See OMS 891171 -172-173-176-207 | October | 2012 | 2013Q2 | 2013 | ZN2635:PA12 | ZN965:PA39 | ZN00965/000039 | PARRAMATTA | OH | Veg | 2012-10-17 | N | 95.8858 | N | 5 | N | N | 1.1101 | 39.4971 | 63203.6102
[7 empty] | 18112 | 15855 | 889115 | 2012-10-18 00:13 | 2012-10-18 01:42 | 89 | 11kV | 106514 | 1317 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | @Zn10991 Blakehurst Pa6 tripped, reclosed and locked out Relays-Cph Inst and Timed O/C, Lock out, Reclose relay, EFI Siganls:11kv trip Cause: Animals/Birds Remarks:Possum on HV UGOH btw AB30120 and tee to S10560. Possible damage to insulators. Pa6 ex Blakeuhurst Zone. See 889744,5,6 Exclude 889115 | October | 2012 | 2013Q2 | 2013 | ZN10991:PA6 | ZN10991:PA6 | ZN10991/000006 | GEORGES RIVER | OH | Not Veg | 2012-10-18 | N | 80.8762 | N | 3 | N | N | 1.1101 | 39.4971 | 77837.2896
[7 empty] | 16668 | 1044 | 890382 | 2012-10-18 11:10 | 2012-10-18 12:10 | 60 | 11kV | 780 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 122583 Single phase Cross arm pole 9F-90069 broken. | October | 2012 | 2013Q2 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2012-10-18 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 570.001
[7 empty] | 18404 | 18519 | 889536 | 2012-10-18 18:55 | 2012-10-18 19:10 | 15 | 11kV | 1950 | 130 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 122593 Sub interrupted for restoration after 11kV UGM cable repairs Removing Generator related to OMS 889357 | October | 2012 | 2013Q2 | 2013 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | UG | Not Veg | 2012-10-18 | N | 15 | N | 3 | N | N | 1.1101 | 39.4971 | 1425.0025
[7 empty] | 16785 | 1953 | 889572 | 2012-10-19 07:45 | 2012-10-19 09:35 | 110 | 11kV | 110 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 122595 B phase DOLF : 10 Amp FUSE FATIGUE Excluded OMS REPORT NO 889572. | October | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-10-19 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 17692 | 11486 | 889742 | 2012-10-19 11:38 | 2012-10-19 12:06 | 28 | 11kV | 17948 | 641 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn874 Concord 11kv VCB panel 3 "S8757 George Conway No.2" FDR tripped on: Relays: Timmed earth fault, EFI Field EFI's: 8757, 8758, 3122 Signals: 11kv trip, Zone Earth, No.4 group earth Remarks: UG fault. Suspect 11kv feeder fault from S3122 George Mena no.1 SW-B to S-3385 Rothwell Conway. Related jobs: #889742, 889761, 891160 | October | 2012 | 2013Q2 | 2013 | ZN874:PA3 | ZN874:PA26 | ZN00874/000026 | CANADA BAY | UG | Not Veg | 2012-10-19 | N | 28 | N | 6 | N | N | 1.1101 | 39.4971 | 13115.869
[7 empty] | 18333 | 17753 | 889842 | 2012-10-19 14:34 | 2012-10-19 15:26 | 52 | 11kV | 33800 | 650 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn9035 Caringbah Pa2 Fdr tripped on Earht Leakage Time O/L Lockout EFI Suspected HV UG Fault From S9035 to S9796 to S9450 See 890285 exclude 889842 | October | 2012 | 2013Q2 | 2013 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | UG | Not Veg | 2012-10-19 | N | 52 | N | 6 | N | N | 1.1101 | 39.4971 | 24700.0431
[7 empty] | 17713 | 11677 | 889904 | 2012-10-19 16:26 | 2012-10-19 17:30 | 64 | 11kV | 3648 | 57 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 122609 1 fault operation A phase Earth fault During RSI 25184 Surge arrestor failed at UGOH pole IS-22345. Excluded OMD 889904 | October | 2012 | 2013Q2 | 2013 | 235:2120 | 238:34150 | ZN00238/034150 | MAITLAND | OH | Not Veg | 2012-10-19 | N | 64 | N | 6 | N | N | 1.1101 | 39.4971 | 2665.8508
[7 empty] | 16700 | 1234 | 889921 | 2012-10-19 17:13 | 2012-10-19 17:51 | 38 | 11kV | 20558 | 541 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Pnl.16L Erina - REC 46673 Terrigal Penrose tripped on IOC Tree removed near PT12104 | October | 2012 | 2013Q2 | 2013 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-10-19 | N | 38 | N | 6 | N | N | 1.1101 | 39.4971 | 15023.18
[7 empty] | 16679 | 1116 | 889862 | 2012-10-19 17:23 | 2012-10-19 18:15 | 52 | 11kV | 780 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 122608 Tree on fdr near pole MN 41019 section isolated for repairs Excluded OMS 889862 & 889923 | October | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-10-19 | N | 52 | N | 6 | N | N | 1.1101 | 39.4971 | 570.001
[7 empty] | 17150 | 5009 | 890112 | 2012-10-21 00:12 | 2012-10-21 01:31 | 79 | 11kV | 56406 | 714 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | At S187 Crows Nest Panel 28 tripped Cause; Suspect Faulty relay. | October | 2012 | 2013Q2 | 2013 | ZN187:PA28 | ZN187:PA28 | ZN00187/000028 | NORTH SYDNEY | Unknown | Not Veg | 2012-10-21 | N | 79 | N | 2 | N | N | 1.1101 | 39.4971 | 41219.8411
[7 empty] | 17436 | 8222 | 890200 | 2012-10-21 20:02 | 2012-10-22 02:48 | 406 | 11kV | 123270 | 335 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122619 3 fault operations A & C phase Earth fault; Overcurrent 2 phase 11kV mains down between poles DR-40145 & DR-40143. Replaced under AP. 10A B ph DOLF replaced sub 27937. Volts = 242. Excluded OMS 890200; 890212 | October | 2012 | 2013Q2 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-10-21 | N | 367.9701 | N | 2 | N | N | 1.1101 | 39.4971 | 90082.0802
[7 empty] | 18047 | 15232 | 890220 | 2012-10-22 02:34 | 2012-10-22 03:00 | 26 | 11kV | 26 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Transformer | Unplanned | Unselected | N | EX ZN 1285 Greenacre Park Pnl's 30&36 @ S-3413 Hume Shellcote No.2 "Transformer tripped on B phase O/C Remarks: @S3413 Hume Shellcote No.2 Transformer found tripped off. Clearance given to Dop by customer (PRIMO SMALLGOODS) to restore supply. Related jobs: #890220, 891254 | October | 2012 | 2013Q2 | 2013 | ZN1285:PA36 | ZN37100:PA15 | ZN37100/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-10-22 | N | 26 | N | 18 | N | N | 1.1101 | 39.4971 | 19
[7 empty] | 17824 | 12521 | 891087 | 2012-10-22 12:36 | 2012-10-22 13:32 | 56 | 11kV | 38360 | 685 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S3154 st ives 11kv trip zone earth tx 1 group earth tree branch fell onto mains adjacent to S.5187 #890484,#890496,#890505 | October | 2012 | 2013Q2 | 2013 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2012-10-22 | N | 56 | N | 18 | N | N | 1.1101 | 39.4971 | 28032.3566
[7 empty] | 17328 | 7328 | 890650 | 2012-10-22 14:55 | 2012-10-22 15:54 | 59 | 11kV | 5428 | 92 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | REC 44937 Allan St tripped and locked out on B & C phase overcurrent Weather related - trees | October | 2012 | 2013Q2 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-10-22 | N | 59 | N | 18 | N | N | 1.1101 | 39.4971 | 3966.6223
[7 empty] | 17388 | 7861 | 890638 | 2012-10-22 14:53 | 2012-10-22 16:23 | 90 | 11kV | 74340 | 826 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn.14144 Wamberal Pnl.4 tripped on B & C phase Overcurrent Weather related | October | 2012 | 2013Q2 | 2013 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-10-22 | N | 90 | N | 18 | N | N | 1.1101 | 39.4971 | 54325.4793
[7 empty] | 16900 | 2894 | 890652 | 2012-10-22 15:04 | 2012-10-22 16:57 | 112.75 | 11kV | 107450.75 | 953 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S2400 Berowra Panel 26 Tripped on Relays: A phase IOC Signals 11kV Trip - Zone Earth and Tx2 Group Earth. Cause: Tree ins Contact with HV adjacent PT1600 | October | 2012 | 2013Q2 | 2013 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2012-10-22 | N | 112.75 | N | 18 | N | N | 1.1101 | 39.4971 | 78521.8388
[7 empty] | 18176 | 16370 | 890725 | 2012-10-22 15:46 | 2012-10-22 17:19 | 93 | 11kV | 91553 | 1133 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | REC 45140 Pinnaroo Collendina tripped, reclosed and locked out on Overcurrent and IOC weather related see 891184 891182 | October | 2012 | 2013Q2 | 2013 | ZN12590:PA3 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Veg | 2012-10-22 | N | 80.8058 | N | 18 | N | N | 1.1101 | 39.4971 | 66904.232
[7 empty] | 18347 | 17852 | 890501 | 2012-10-22 16:26 | 2012-10-22 18:28 | 122 | 11kV | 19012 | 169 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122635 Operator found a very burnt up piece of bamboo across all three phases near the R Donkin pole sub. As the fault was beyond the Hue Hue road Recloser and it also tripped the Zone sub Sw 80075 it appears the protection did not grade in this instance. Excluded OMS 890501 | October | 2012 | 2013Q2 | 2013 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2012-10-22 | N | 112.497 | N | 18 | N | N | 1.1101 | 39.4971 | 13893.4088
[7 empty] | 17998 | 14185 | 890612 | 2012-10-22 14:29 | 2012-10-22 18:30 | 240.7 | 11kV | 3369.8 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122643 B phase DOLF : 31 Amp CC1: 22-"Refer to SOp" | October | 2012 | 2013Q2 | 2013 | 503:48011 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Veg | 2012-10-22 | N | 240.7 | N | 18 | N | N | 1.1101 | 39.4971 | 2462.5504
[7 empty] | 16599 | 616 | 890845 | 2012-10-22 16:56 | 2012-10-22 18:34 | 98.4667 | 11kV | 157842.0667 | 1603 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122641 Emergency isolation to remove tree limb from OHM. CC1: 22-"Refer to SOp" | October | 2012 | 2013Q2 | 2013 | 260:33353 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Veg | 2012-10-22 | N | 98.4667 | N | 18 | N | N | 1.1101 | 39.4971 | 115346.3268
[7 empty] | 17071 | 4201 | 890738 | 2012-10-22 15:55 | 2012-10-22 19:38 | 223 | 11kV | 166328 | 1702 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Zn.12650 West Gosford Pnl.1 tripped, reclosed and tripped on Lockout & timing, SEF, B & C phase O/C, EFI Abnormal: REC44936 OPEN and by-passed 11kV mains down on LV see 891192 891194 891195 | October | 2012 | 2013Q2 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-10-22 | N | 97.725 | N | 18 | N | N | 1.1101 | 39.4971 | 121547.5966
[7 empty] | 17073 | 4220 | 890911 | 2012-10-22 17:45 | 2012-10-22 19:50 | 125 | 11kV | 2375 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122647 A phase dist fuse : 315 Amp Trees in growing through LV. LH LVF. Excluded OMS 890911 | October | 2012 | 2013Q2 | 2013 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | OH | Veg | 2012-10-22 | N | 125 | N | 18 | N | N | 1.1101 | 39.4971 | 1735.5799
[7 empty] | 18363 | 18002 | 890873 | 2012-10-22 17:15 | 2012-10-22 20:35 | 200 | 11kV | 2200 | 11 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 122638 3 phase isolation Damaged stay wire at pole SF 80469 off NEH. Inadequate clearance to make repairs. | October | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2012-10-22 | N | 200 | N | 18 | N | N | 1.1101 | 39.4971 | 1607.6951
[7 empty] | 18203 | 16616 | 890695 | 2012-10-22 15:22 | 2012-10-22 20:47 | 325 | 11kV | 10725 | 33 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122648 3 phase Trees blown onto mains Excluded OMS 890762 & 890695 | October | 2012 | 2013Q2 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2012-10-22 | N | 325 | N | 18 | N | N | 1.1101 | 39.4971 | 7837.5137
[7 empty] | 16814 | 2138 | 891320 | 2012-10-22 17:21 | 2012-10-22 20:50 | 209 | 11kV | 6171 | 39 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122650 3 fault operations 3 phase Tree into mains beyond 41292 | October | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-10-22 | N | 158.2308 | N | 18 | N | N | 1.1101 | 39.4971 | 4509.5848
[7 empty] | 16604 | 691 | 891104 | 2012-10-22 15:50 | 2012-10-22 22:00 | 370 | 11kV | 25160 | 68 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122644 2 fault operations Large tree on OHM. Excluded OMS 890730, 890747, 890772 | October | 2012 | 2013Q2 | 2013 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2012-10-22 | N | 370 | N | 18 | N | N | 1.1101 | 39.4971 | 18386.1859
[7 empty] | 17247 | 6521 | 890771 | 2012-10-22 16:13 | 2012-10-23 00:20 | 487 | 11kV | 232797 | 1811 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 122642 2 fault operations Large trees on OHM two locations, High into low at sub 3198. Excluded OMS 890771,890778,890782, 890783, 890975, 891049 | October | 2012 | 2013Q2 | 2013 | 243:80084 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2012-10-22 | N | 128.5461 | N | 18 | N | N | 1.1101 | 39.4971 | 170121.1813
[7 empty] | 16595 | 595 | 890799 | 2012-10-22 16:33 | 2012-10-23 02:31 | 597.2167 | 11kV | 65232.4 | 318 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122646 2 fault operations | October | 2012 | 2013Q2 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-10-22 | N | 205.1333 | N | 18 | N | N | 1.1101 | 39.4971 | 47669.9139
[7 empty] | 17222 | 6224 | 890849 | 2012-10-22 16:57 | 2012-10-23 10:30 | 1053 | 11kV | 338595 | 1846 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 122634 2 fault operations 3 phase Note HV mains contacted LV mains,at pole IV-30534 in Bayview Rd, both HV and LV mains had fallen and the neutral conductor was broken. Sub 6401 had supply restored much later as all premises supplied from this sub had to be checked for safety following the LV and HV coming into contact. Excluded OMS 891033, 890849, 890693, 890073 | October | 2012 | 2013Q2 | 2013 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2012-10-22 | N | 183.4209 | N | 18 | N | N | 1.1101 | 39.4971 | 247435.2391
[7 empty] | 17443 | 8260 | 891308 | 2012-10-23 11:03 | 2012-10-23 11:53 | 50 | 11kV | 2750 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44604 Dog Trap Road Opened & locked out on A & B phase O/C branch removed from 11kV OH adjacent PT12576 | October | 2012 | 2013Q2 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-10-23 | N | 50 | N | 3 | N | N | 1.1101 | 39.4971 | 2009.6189
[7 empty] | 16666 | 1037 | 891655 | 2012-10-23 22:03 | 2012-10-23 23:35 | 92 | 11kV | 7544 | 82 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 122673 C phase DOLF : 20 Amp No cause found, probable fuse fatigue. Fuse replaced OK. Excluded OMS No. 891655 & 891657. | October | 2012 | 2013Q2 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2012-10-23 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 5512.9327
[7 empty] | 17812 | 12481 | 891644 | 2012-10-23 21:00 | 2012-10-24 01:50 | 290 | 11kV | 70808 | 745 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14143 Somersby Pnl.17 tripped on: A and B phase O/C Tree branch brought down OH see 891907 891908 | October | 2012 | 2013Q2 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2012-10-23 | N | 95.0443 | N | 3 | N | N | 1.1101 | 39.4971 | 51744.3979
[7 empty] | 18320 | 17681 | 892267 | 2012-10-24 10:12 | 2012-10-24 10:16 | 4 | 11kV | 6152 | 1538 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.15005 Belrose, Panel 8 Fdr CB tripped on SEL due to staff error. SEL should have been NA during the transfer of 11dc's from Panel 2R (close LB.24418 and open USL.21362 | October | 2012 | 2013Q2 | 2013 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2012-10-24 | N | 4 | N | 8 | N | N | 1.1101 | 39.4971 | 4495.7001
[7 empty] | 16539 | 269 | 891769 | 2012-10-24 06:43 | 2012-10-24 10:56 | 253.4 | 11kV | 5130.3 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122682 B Phase DOLF FUSE FATIGUE VOLTS 247, 250, 250 LOAD 114, 15 10 | October | 2012 | 2013Q2 | 2013 | 229:34989 | 233:82815 | ZN00233/082815 | PORT STEPHENS | UG | Not Veg | 2012-10-24 | N | 244.3 | N | 8 | N | N | 1.1101 | 39.4971 | 3749.0719
[7 empty] | 16580 | 536 | 892249 | 2012-10-24 05:14 | 2012-10-24 13:45 | 511 | 11kV | 20030 | 98 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122692 Steel Mains unstranding to 52242 Jackson sub. One trip as Reclose Function OFF for Total Fire Ban. Excluded OMS 892249 & 892288 | October | 2012 | 2013Q2 | 2013 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2012-10-24 | N | 204.3878 | N | 8 | N | N | 1.1101 | 39.4971 | 14637.3332
[7 empty] | 17254 | 6578 | 900274 | 2012-10-24 09:35 | 2012-10-24 14:50 | 315 | 11kV | 139384 | 449 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 122680 C phase Overcurrent FEEDER TRIPPED WHEN OPENING ABS 226 ON SI 25753 CABLE BOX POLE JU34509 DAMAGED | October | 2012 | 2013Q2 | 2013 | 203:8085 | 204:82699 | ZN00204/082699 | NEWCASTLE | OH | Not Veg | 2012-10-24 | N | 310.4321 | N | 8 | N | N | 1.1101 | 39.4971 | 101857.7161
[7 empty] | 17375 | 7703 | 892078 | 2012-10-24 14:45 | 2012-10-24 18:09 | 204 | 11kV | 227376 | 1134 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn3922 Drummoyne Panel 2 "Edenholme Rd" ect feeder tripped on:- Relays: C phase overcurrent, EFI and fault check Signals: 11kv trip, Zone earth and group earth. Remarks: UG fault. due to faulty EFI @ Sub 48988 Little Arthur and misleading protection information. Fault had to be found progressively. Underground cable fault between sub 48988 Little Arthur and Sub 1460 Elliot St. Related jobs: #892078, 892304, 892303 | October | 2012 | 2013Q2 | 2013 | ZN3922:PA2 | ZN3922:PA2 | ZN03922/000002 | INNER WEST | UG | Not Veg | 2012-10-24 | N | 200.5079 | N | 8 | N | N | 1.1101 | 39.4971 | 166159.6743
[7 empty] | 17653 | 10810 | 892163 | 2012-10-24 17:00 | 2012-10-24 18:15 | 75 | 11kV | 300 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122689 A phase DOLF : 10 Amp Excluded OMS 892163 | October | 2012 | 2013Q2 | 2013 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | UG | Not Veg | 2012-10-24 | N | 75 | N | 8 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 18550 | 20350 | 892209 | 2012-10-24 16:30 | 2012-10-24 20:20 | 230 | 11kV | 920 | 4 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | LID 122690 Customer MSB on fire Excluded OMS 892209 | October | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | Unknown | Not Veg | 2012-10-24 | N | 230 | N | 8 | N | N | 1.1101 | 39.4971 | 672.3089
[7 empty] | 18148 | 16070 | 897611 | 2012-10-24 21:29 | 2012-10-25 00:23 | 174 | 11kV | 1398 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | RE48045 Myoora Chilkes GCC tripped / reclosed and locked out on Earth Fault. UG fault. Dop suggests it will take all day to cut an entrance to worksite. He is unable to get close enough for a detailed report of damage except that he can see 2 Surge diverters blown on 1 of the UGOHs closes to PT 12510. And damage to UGOH near USL 43659. See 897611 897613 | October | 2012 | 2013Q2 | 2013 | ZN14143:PA17 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | UG | Not Veg | 2012-10-24 | N | 139.8 | N | 8 | N | N | 1.1101 | 39.4971 | 1021.6172
[7 empty] | 16994 | 3514 | 892250 | 2012-10-25 06:00 | 2012-10-25 09:14 | 194.45 | 11kV | 777.8 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122697 Single phase Patrolled before retrying Line DOLF due to Total Fire Ban | October | 2012 | 2013Q2 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2012-10-25 | N | 194.45 | N | 4 | N | N | 1.1101 | 39.4971 | 568.3933
[7 empty] | 17451 | 8323 | 892614 | 2012-10-25 17:05 | 2012-10-25 17:46 | 41 | 11kV | 37770 | 955 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn398DulwichHill Pa11 Labelled "Norton Queen" tripped on Relays-Earth Fault, EFI Signals: 11kv trip, Tx1 Group Earth, Tx3 Group Earth, Zone Earth EFI's S1942 S6625 Cause: UG Fault Remarks:Section of 11kv fdr from S1942 Sw/B to S4158 Sw/A is defective See 892842,4 exclude 892614 | October | 2012 | 2013Q2 | 2013 | ZN398:PA11 | ZN398:PA11 | ZN00398/000011 | INNER WEST | UG | Not Veg | 2012-10-25 | N | 39.5497 | N | 4 | N | N | 1.1101 | 39.4971 | 27601.202
[7 empty] | 16960 | 3310 | 892649 | 2012-10-25 18:18 | 2012-10-25 19:04 | 45.65 | 11kV | 18474.6167 | 578 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of Zn4545 meadowbank Panel 24 Bond Burnt off AB254 See OMS 895649 892650 | October | 2012 | 2013Q2 | 2013 | ZN4545:PA24 | ZN35500:PA16 | ZN35500/000016 | RYDE | OH | Not Veg | 2012-10-25 | N | 31.963 | N | 4 | N | N | 1.1101 | 39.4971 | 13500.705
[7 empty] | 16867 | 2451 | 892684 | 2012-10-25 22:17 | 2012-10-25 23:08 | 51 | 11kV | 63087 | 1237 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | @Sub 1287 Revesby Zn Panel #17 labelled Hinemoa St tripped reclosed tripped and locked out on C phase IOC and timed OC lockout/timing relay 11kv trip Remarks: animals/birds bats Related jobs: #893024, 892697, 892691, 892690, 892689, 892688, 892687, 892686, 892685, 892684, 893416 | October | 2012 | 2013Q2 | 2013 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-10-25 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 46102.1188
[7 empty] | 16665 | 1029 | 892711 | 2012-10-26 06:25 | 2012-10-26 08:40 | 135 | 11kV | 270 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122710 single phase DOLF : 2 Amp excluded OMS 892711 | October | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-10-26 | N | 135 | N | 1 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 17479 | 8580 | 893106 | 2012-10-27 04:58 | 2012-10-27 05:42 | 44 | 11kV | 2530 | 62 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S3472 Sefton Panel 16 Park Regents Park Feeder tripped on : A Phase O/C E/L fault check Field EFI's : S6641, S6948 Remarks: UG fault, UF cable fault Related jobs: #893106, 893430, 893429 | October | 2012 | 2013Q2 | 2013 | ZN3472:PA16 | ZN3472:PA16 | ZN03472/000016 | CUMBERLAND | UG | Not Veg | 2012-10-27 | N | 40.8065 | N | 2 | N | N | 1.1101 | 39.4971 | 1848.8494
[7 empty] | 17751 | 11956 | 893202 | 2012-10-27 16:52 | 2012-10-27 20:48 | 236 | 11kV | 146787 | 1598 | HV | Fire (non-electrical) | Adverse Weather/Environment | 3rd Party Asset | Unplanned | Unselected | N | @Zn1788 Matraville Pa32 fdr opened on Bph OC, EFI's operated- S47859 Cause: Fire Remarks: Fence on fire which engulfed kiosk S35452 Fdr isolated from S47859 to S8960 to S35091 See 893436,7,8,9 GIS 893445,556,72,86 Exclude 893202,5,6,12,4,5,9,22,7 | October | 2012 | 2013Q2 | 2013 | ZN1788:PA32 | ZN1788:PA43 | ZN01788/000043 | RANDWICK | Unknown | Not Veg | 2012-10-27 | N | 91.8567 | N | 2 | N | N | 1.1101 | 39.4971 | 107267.6101
[7 empty] | 17521 | 8966 | 893280 | 2012-10-28 13:01 | 2012-10-28 13:55 | 54 | 11kV | 88031 | 1641 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | @ s15015 North Head Panel 5 manly Hospital Tripped on :SEF protection Usl 22305 One phase links failed #893282,893280,893540,893539 | October | 2012 | 2013Q2 | 2013 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | OH | Not Veg | 2012-10-28 | N | 53.6447 | N | 2 | N | N | 1.1101 | 39.4971 | 64330.4583
[7 empty] | 17903 | 13158 | 893289 | 2012-10-28 16:45 | 2012-10-28 18:02 | 77 | 11kV | 2926 | 38 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 122732 nil protection. tree fell on OHM adj sub 52870 interupted to remove tree Excluded oms 893331/893289 | October | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-10-28 | N | 77 | N | 2 | N | N | 1.1101 | 39.4971 | 2138.2345
[7 empty] | 17784 | 12290 | 893354 | 2012-10-29 00:09 | 2012-10-29 01:43 | 94 | 11kV | 48774 | 561 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S965. Pennant Hills Panel 22 feeder tripped on Relays: Earth Fault & EFI. Signals: 11kV Trip, Tx3 Group Earth. Cause not ascertained 893449 893452 | October | 2012 | 2013Q2 | 2013 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | OH | Veg | 2012-10-29 | N | 86.9412 | N | 3 | N | N | 1.1101 | 39.4971 | 35642.6006
[7 empty] | 17576 | 9635 | 893359 | 2012-10-29 04:45 | 2012-10-29 08:10 | 205 | 11kV | 410 | 2 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 122737 Single phase DOLF : 10 Amp Excluded OMS 893359 | October | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-10-29 | N | 205 | N | 3 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 17967 | 13829 | 893620 | 2012-10-29 11:58 | 2012-10-29 14:30 | 152 | 11kV | 152 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122739 B phase DOLF : 10 Amp Tx Volts: Aph - 242V, Bph - 242V, Cph - 242V Excluded OMS No. 893620 | October | 2012 | 2013Q2 | 2013 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | UG | Not Veg | 2012-10-29 | N | 152 | N | 3 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 16510 | 73 | 893862 | 2012-10-30 05:40 | 2012-10-30 07:00 | 80 | 11kV | 4160 | 52 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122745 A & B phase DOLF : 31 Amp Readings as left 150A, 110A, 120A @ 248V Excluded OMS 893862, 893864. SEE REPORT 122745. | October | 2012 | 2013Q2 | 2013 | 216:10728 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | UG | Not Veg | 2012-10-30 | N | 80 | N | 2 | N | N | 1.1101 | 39.4971 | 3040.0053
[7 empty] | 17838 | 12626 | 893975 | 2012-10-30 09:36 | 2012-10-30 11:30 | 114 | 11kV | 228 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122755 A & B phase DOLF : 10 Amp Excluded OMS 893975 | October | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-10-30 | N | 114 | N | 2 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 17781 | 12262 | 894670 | 2012-10-31 15:24 | 2012-10-31 15:40 | 16 | 11kV | 13616 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12600 Lisarow Pnl.13 tripped on Minor Trip LED SEF EFI (Recloser is NA) Tree branch on open condutor near LB40982 | October | 2012 | 2013Q2 | 2013 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2012-10-31 | N | 16 | N | 6 | N | N | 1.1101 | 39.4971 | 9950.1712
[7 empty] | 17698 | 11513 | 894646 | 2012-10-31 14:52 | 2012-10-31 16:56 | 124 | 11kV | 145226.6167 | 1282 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | AT Zn4545 MEadowbank Panel 35 Tripped, reclosed tripped and locked out on IOC and EFI, Fault Check, Timing and Reclose Relays. Cause: 11kV UG feeder damaged from S1712 Graf Ave to S8545 Graf Anthony to S3073 West Anthony See OMS 869049 894322 894646 894648 894656 894719 | October | 2012 | 2013Q2 | 2013 | ZN4545:PA35 | ZN4545:PA35 | ZN04545/000035 | RYDE | UG | Not Veg | 2012-10-31 | N | 113.2813 | N | 6 | N | N | 1.1101 | 39.4971 | 106127.328
[7 empty] | 18083 | 15632 | 894651 | 2012-10-31 15:01 | 2012-10-31 17:20 | 139 | 11kV | 73980 | 950 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S1193 Lindfield Panel 21 Tripped, Reclosed Tripped and Locked out on Relays: A phase O/C and IOC, Earth Fault, EFI, Timing and Lockout relays. Signals: 11kV Trip Cause: Tree branch on OH mains in Shirley Rd See OMS 896253 896251 896245 894651 894663 | October | 2012 | 2013Q2 | 2013 | ZN1193:PA21 | ZN1193:PA21 | ZN01193/000021 | KU-RING-GAI | OH | Veg | 2012-10-31 | N | 77.8737 | N | 6 | N | N | 1.1101 | 39.4971 | 54062.402
[7 empty] | 18418 | 18786 | 894723 | 2012-10-31 16:39 | 2012-10-31 18:25 | 106 | 11kV | 212 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122772 C phase DOLF : 16 Amp Excluded OMS No. 894723 Tx Volts - 240V | October | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-10-31 | N | 106 | N | 6 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 17719 | 11715 | 894769 | 2012-10-31 21:58 | 2012-10-31 22:05 | 7 | 11kV | 11458 | 1747 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | REC47818 Wilfred Barrett Terilbah (ex Pnl.1 @ Noraville) tripped on OC Trip Staff Error - Operator closed wrong switch see 894835 894834 | October | 2012 | 2013Q2 | 2013 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | Unknown | Not Veg | 2012-10-31 | N | 6.5587 | N | 6 | N | N | 1.1101 | 39.4971 | 8373.1684
[7 empty] | 17327 | 7326 | 894777 | 2012-10-31 22:14 | 2012-10-31 23:20 | 66 | 11kV | 147239 | 2410 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn10999 Kogarah Pa24 fdr tripped Signals-1kv trip Relays Aph Overcurrent, earth fault EFI's S10182 Cause: Cause not ascertained Remarks: DOp patrolled fdr and checked repored causes but could not find anything Cust report pole top transformer exploded in area See 894903,4,5 LV// 894912,3 Exclude 894777,8,9,81 | October | 2012 | 2013Q2 | 2013 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | OH | Veg | 2012-10-31 | N | 61.095 | N | 6 | N | N | 1.1101 | 39.4971 | 107597.9184
[7 empty] | 17635 | 10609 | 895069 | 2012-11-01 14:38 | 2012-11-01 15:37 | 59 | 11kV | 63130 | 1070 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | LID 122784 3 phase interruption Fdr 80340 de-energised to put out fire at pole sub 12382. Section isolated to replace pole & sub. Excluded OMS 895069 | November | 2012 | 2013Q2 | 2013 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2012-11-01 | N | 59 | N | 2 | N | N | 1.1101 | 39.4971 | 46133.542
[7 empty] | 17648 | 10742 | 895181 | 2012-11-01 18:59 | 2012-11-01 20:10 | 71 | 11kV | 17892 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 122786 E/F Prot operation 197A. Reclose off for total fire ban. PLEASE PATROL FDR up to Reclosers. Excluded OMS# 895183. | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-11-01 | N | 71 | N | 2 | N | N | 1.1101 | 39.4971 | 13074.9459
[7 empty] | 18365 | 18026 | 895392 | 2012-11-02 11:28 | 2012-11-02 12:03 | 35 | 11kV | 15190 | 434 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At Sub 1850 Bass Hill Panel No.14 "AB 2579" feeder opened on SEL 11KV trip Remarks: Air break switch. Bond off @ AB2579. suspect S3517 Dist 3 was in parallel with S36110 Dist 2 Related jobs: #895384, 895395, 895392, 896294, 896293 | November | 2012 | 2013Q2 | 2013 | ZN1850:PA14 | ZN1850:PA45 | ZN01850/000045 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-11-02 | N | 35 | N | 2 | N | N | 1.1101 | 39.4971 | 11100.404
[7 empty] | 16767 | 1748 | 896312 | 2012-11-02 15:20 | 2012-11-02 16:21 | 61 | 11kV | 1647 | 27 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S1290 Leightonfield Panel #16 'Christina Rd feeder Tripped & Reclosed on; Leakage - SEL - Lockout Remarks: Vehicle hit pole. Truck reversed into HV UGOH pole damaging pole & Burning Roadside bond off | November | 2012 | 2013Q2 | 2013 | ZN1290:PA16 | ZN1290:PA16 | ZN01290/000016 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-11-02 | N | 61 | N | 2 | N | N | 1.1101 | 39.4971 | 1203.579
[7 empty] | 17995 | 14179 | 897328 | 2012-11-03 04:46 | 2012-11-03 07:20 | 154 | 11kV | 29695 | 315 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | Recloser CP630 Cressy Wellington Tripped Reclosed Tripped and Locked out on IOC and Earth Fault Cause: Lightning Arrestors defective in section below AB1116. See OMS 897328 897329 | November | 2012 | 2013Q2 | 2013 | ZN35500:PA34 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2012-11-03 | N | 94.2698 | N | 2 | N | N | 1.1101 | 39.4971 | 21700.2301
[7 empty] | 17160 | 5170 | 896319 | 2012-11-03 18:29 | 2012-11-03 19:25 | 56 | 11kV | 10528 | 188 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 122802 1 fault operation B phase Overcurrent Fdr 82285 Bph O/C, Trans 1 Aprot Multitrip - TR2 slave, 11kV BBP Multitrip Main & Slave. Sw's 82286,82284,82287,82286,82285 & 82283 ALL opened at 1829hrs. Possible Prot malgrade - Please Investigate. CABLE TESTS REQUIRED. Excluded OMS# 895837. | November | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2012-11-03 | N | 56 | N | 2 | N | N | 1.1101 | 39.4971 | 7693.5519
[7 empty] | 17183 | 5569 | 895893 | 2012-11-04 08:54 | 2012-11-04 10:20 | 85.8167 | 11kV | 1973.7833 | 23 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 122806 B phase DOLF : 20 Amp Party paraphernalia ( baloons & streamers ) on overhead mains. | November | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-11-04 | N | 85.8167 | N | 5 | N | N | 1.1101 | 39.4971 | 1442.3826
[7 empty] | 17978 | 14050 | 895956 | 2012-11-04 17:34 | 2012-11-04 18:25 | 51 | 11kV | 1989 | 39 | HV | Staff Other | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | @S5704 Hickson Pottinger switching error on 11kv RMI Remarks: City feeder re-development 61/62 GHJ 35/37 KLM. Error during switching @ S-5704 Hickson Pottinger due to confusion of labelling on 62J HV RMI and was not labelled as per labelling standards. Related jobs: #896609, 895956 | November | 2012 | 2013Q2 | 2013 | ZN8700:PA61 62GHJ | ZN8700:PA63 64ABC | ZN08700/63 64ABC | SYDNEY | UG | Not Veg | 2012-11-04 | N | 51 | N | 5 | N | N | 1.1101 | 39.4971 | 1453.5025
[7 empty] | 16542 | 278 | 895958 | 2012-11-04 17:35 | 2012-11-04 19:55 | 140 | 11kV | 700 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14335 Wattle Tree Patter 0.6 - Footpath phase HDo blown 16Amp Fuse fatigue | November | 2012 | 2013Q2 | 2013 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2012-11-04 | N | 140 | N | 5 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 16746 | 1551 | 895979 | 2012-11-04 20:03 | 2012-11-04 22:15 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122810 A phase DOLF : 10 Amp Excluded OMS 895979 | November | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | UG | Not Veg | 2012-11-04 | N | 132 | N | 5 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 17553 | 9165 | 895993 | 2012-11-04 23:58 | 2012-11-05 02:45 | 167 | 11kV | 220254 | 1406 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 3 Tripped on Relays: A Phase IOC Signals: 11kV Trip, Zone Earth Cause: Bat Flew into 11kV Mains Tangling them near UGOH to PT1322. Cause: Bat Flew into 11kV Mains Tangling them near UGOH to PT1322. See OMS 897949 897952 897953 987954 | November | 2012 | 2013Q2 | 2013 | ZN129:PA3 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Not Veg | 2012-11-04 | N | 156.6529 | N | 5 | N | N | 1.1101 | 39.4971 | 160955.1268
[7 empty] | 17924 | 13370 | 895997 | 2012-11-05 04:19 | 2012-11-05 05:00 | 41 | 11kV | 3321 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122816 A phase DOLF : 31 Amp Excluded OMS 895997 | November | 2012 | 2013Q2 | 2013 | 220:8689 | 220:8689 | ZN00220/008689 | LAKE MACQUARIE | UG | Not Veg | 2012-11-05 | N | 41 | N | 7 | N | N | 1.1101 | 39.4971 | 2426.8888
[7 empty] | 18329 | 17739 | 896001 | 2012-11-05 05:25 | 2012-11-05 06:05 | 40 | 11kV | 7520 | 188 | HV | Equipment Failed in Service | Equipment Failure | Busbar | Unplanned | No Weather Impact | N | LID 122817 Faulty relay at Sw 82285, S Atchison / N Hussey to replace Excluded OMS 896001 | November | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | Unknown | Not Veg | 2012-11-05 | N | 40 | N | 7 | N | N | 1.1101 | 39.4971 | 5495.3942
[7 empty] | 17506 | 8863 | 896000 | 2012-11-05 05:04 | 2012-11-05 08:53 | 229.4167 | 11kV | 47154.4 | 277 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 122818 C phase DOLF : 40 Amp Excluded OMS 896011 | November | 2012 | 2013Q2 | 2013 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2012-11-05 | N | 170.2325 | N | 7 | N | N | 1.1101 | 39.4971 | 34459.0447
[7 empty] | 18516 | 20005 | 896082 | 2012-11-05 09:09 | 2012-11-05 09:54 | 45 | 11kV | 1935 | 43 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 122825 2 fault operations, A & B phase Overcurrent Contract tree trimmers dropped branch on mains between poles IV-37090 & IV-37091 Lamington Drv. Refer J Riches for details. Excluded OMS 896082 | November | 2012 | 2013Q2 | 2013 | 217:33607 | 217:33607 | ZN00217/033607 | LAKE MACQUARIE | OH | Veg | 2012-11-05 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 1414.0409
[7 empty] | 17004 | 3600 | 896307 | 2012-11-05 13:46 | 2012-11-05 14:38 | 52 | 11kV | 7280 | 140 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 122831 2 fault operations A phase Overcurrent Excluded OMS 896307 | November | 2012 | 2013Q2 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2012-11-05 | N | 52 | N | 7 | N | N | 1.1101 | 39.4971 | 5320.0093
[7 empty] | 17492 | 8716 | 896563 | 2012-11-05 14:55 | 2012-11-05 16:05 | 70 | 11kV | 350 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 122832 No protection operated, interruption was required to replace 66kV insulators above this section of 11kV. | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-11-05 | N | 70 | N | 7 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 17930 | 13406 | 896458 | 2012-11-05 17:04 | 2012-11-05 20:15 | 191.1167 | 11kV | 2675.6333 | 14 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122834 A phase No protection operated, cause of partial outage was a burnt 11Kv tapping at pole ES-61606. | November | 2012 | 2013Q2 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2012-11-05 | N | 191.1167 | N | 7 | N | N | 1.1101 | 39.4971 | 1955.2739
[7 empty] | 17818 | 12498 | 896766 | 2012-11-06 12:00 | 2012-11-06 13:17 | 77 | 11kV | 49126 | 638 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn1648 Enfield Pa4 fdr tripped Relays: E/F, EFI Signals: 11kv trip, Tx1 Group Earth, Zone Earth EFI's: Nil Section of 11kv UG fault fdr between Zn1648 Enfeild and S2638 Cross High failed. See 897316 exclude 896766 | November | 2012 | 2013Q2 | 2013 | ZN1648:PA4 | ZN4853:PA17 | ZN04853/000017 | STRATHFIELD | UG | Not Veg | 2012-11-06 | N | 77 | N | 8 | N | N | 1.1101 | 39.4971 | 35899.8318
[7 empty] | 18255 | 17098 | 896827 | 2012-11-06 13:30 | 2012-11-06 14:11 | 41 | 11kV | 17138 | 418 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | AB45022 footpath line side bond has burnt off - ex long jetty zone Pnl.25 see 897147 for interruption on pnl.25 @ 1411 | November | 2012 | 2013Q2 | 2013 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2012-11-06 | N | 41 | N | 8 | N | N | 1.1101 | 39.4971 | 12523.9449
[7 empty] | 17315 | 7212 | 897147 | 2012-11-06 14:11 | 2012-11-06 14:15 | 4 | 11kV | 1232 | 308 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Foot path line side bond on AB45022 has burnt off. See separate iterruption at 1330, refer to 897146 | November | 2012 | 2013Q2 | 2013 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2012-11-06 | N | 4 | N | 8 | N | N | 1.1101 | 39.4971 | 900.3093
[7 empty] | 18377 | 18179 | 896890 | 2012-11-06 15:04 | 2012-11-06 15:39 | 35 | 11kV | 18200 | 520 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.262 Marrickville 11kv trip Zone Earth TX3 group earth. Panel 40 The Ruby St fdr tripped on B ph leakage EFI fault check. No field EFI's Remarks: UG fault. Suspect frontline fdr fault. Related jobs: #896890, 897124 | November | 2012 | 2013Q2 | 2013 | ZN262:PA40 | ZN262:PA40 | ZN00262/000040 | INNER WEST | UG | Not Veg | 2012-11-06 | N | 35 | N | 8 | N | N | 1.1101 | 39.4971 | 13300.0232
[7 empty] | 17736 | 11849 | 896880 | 2012-11-06 15:02 | 2012-11-06 16:55 | 113 | 11kV | 3616 | 32 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT48785 Empire Bay Awinya 0.9 - Road side HDO 31.5K fuse operated Fuse fatigue see 897165 897164(GIS) | November | 2012 | 2013Q2 | 2013 | ZN12660:PA5 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2012-11-06 | N | 113 | N | 8 | N | N | 1.1101 | 39.4971 | 2642.4661
[7 empty] | 17191 | 5760 | 897024 | 2012-11-06 20:25 | 2012-11-06 21:37 | 72 | 11kV | 132684 | 1962 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2602 Clovelly Pa30 fdr tripped Signals-trip, zone earth, GRoup Earth Relays: EF EFI Fault check EFI: S464847 S8981 S2132 S8570 See 897263,4 LV// 897292 Exclude 897024,7,30,46 | November | 2012 | 2013Q2 | 2013 | ZN2602:PA30 | ZN36800:PA58 | ZN36800/000058 | WAVERLEY | UG | Not Veg | 2012-11-06 | N | 67.6269 | N | 8 | N | N | 1.1101 | 39.4971 | 96961.5537
[7 empty] | 17488 | 8681 | 897012 | 2012-11-06 19:08 | 2012-11-06 21:55 | 167 | 11kV | 333.4667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122845 Single phase DOLF : 10 Amp Excluded OMS 897012 | November | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82574 | ZN00508/082574 | PORT STEPHENS | UG | Not Veg | 2012-11-06 | N | 166.7333 | N | 8 | N | N | 1.1101 | 39.4971 | 243.6876
[7 empty] | 16575 | 505 | 897025 | 2012-11-06 20:32 | 2012-11-06 22:15 | 103 | 11kV | 65611 | 637 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn847 Section of 11kV Panel 18 Ab2730 Burnt Off. See OMS 897300 897025 | November | 2012 | 2013Q2 | 2013 | ZN847:PA18 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2012-11-06 | N | 103 | N | 8 | N | N | 1.1101 | 39.4971 | 47946.5836
[7 empty] | 16555 | 356 | 897057 | 2012-11-07 03:05 | 2012-11-07 04:31 | 86 | 11kV | 127968 | 1488 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.12580 Erina Pnl.10 tripped on EFI Cause not ascertained | November | 2012 | 2013Q2 | 2013 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2012-11-07 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 93515.24
[7 empty] | 18235 | 16915 | 897438 | 2012-11-07 17:48 | 2012-11-07 19:41 | 113 | 11kV | 97801 | 953 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At S2400 Berowra Panel 26 Tripped on IOC Signals: 11kV Trip, Zone Earth, Group Earth, O/C Trip and EFI. Cause: Report of Lightning at 22 Easton Rd Berowra Heights. Feeder Patrolled and OK. See OMS 897859 897866 897438 897446 | November | 2012 | 2013Q2 | 2013 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2012-11-07 | N | 102.6243 | N | 3 | N | N | 1.1101 | 39.4971 | 71470.0862
[7 empty] | 17535 | 9028 | 897497 | 2012-11-07 20:19 | 2012-11-07 22:46 | 147 | 11kV | 10059 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC45016 Dickson tripped / reclosed / tripped and locked out on: OC Trip, IOC Trip Dop cleared stick from mains near LK42953. DOp found another stick had fallen on mains near LK44356. REC45016 interrupted @ 2237 to close LK43590 see 897601 897602 897603 | November | 2012 | 2013Q2 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2012-11-07 | N | 145.7826 | N | 3 | N | N | 1.1101 | 39.4971 | 7350.8205
[7 empty] | 17052 | 4042 | 897550 | 2012-11-08 01:11 | 2012-11-08 03:30 | 139 | 11kV | 141813 | 1467 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S3425 Castle Cove Feeder tripped and Reclosed on Relays: C Phase Timed O/C Lockout Timing DOp Patrolled OH and Nothing found - Mains to patrol in daylight hours Bond burnt off near LB445. See OMS 897550 897896 897898 | November | 2012 | 2013Q2 | 2013 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | WILLOUGHBY | OH | Not Veg | 2012-11-08 | N | 96.6687 | N | 4 | N | N | 1.1101 | 39.4971 | 103632.7576
[7 empty] | 17311 | 7188 | 897831 | 2012-11-08 12:51 | 2012-11-08 15:12 | 141 | 11kV | 148281 | 1463 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122870 1 fault operation Sensitive Earth fault Blown tapping ABS 11386. Requires new ABS. Excluded OMS 897831 | November | 2012 | 2013Q2 | 2013 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Not Veg | 2012-11-08 | N | 101.3541 | N | 4 | N | N | 1.1101 | 39.4971 | 108359.3813
[7 empty] | 17577 | 9637 | 898033 | 2012-11-08 17:32 | 2012-11-08 18:40 | 68 | 11kV | 98460 | 1800 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Lightning | N | @Zn9700 Kirrawee Pa20 tripped, reclosed, tripped and locked out on: Relays: A&B Phase OC, IOC, Lockout, Timing, EFI, Fault CHeck Signals:11kv trip, Group Earth, Zone Earth EFI:S9432 Cause: Lightning/ Surge Arrestor. Lightning strike at PT9141 damaged 2 surge arrestors See 899206,5,6 Exclude 898033,8,68 | November | 2012 | 2013Q2 | 2013 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | UG | Not Veg | 2012-11-08 | N | 54.7 | N | 4 | N | N | 1.1101 | 39.4971 | 71951.6639
[7 empty] | 17613 | 10223 | 898164 | 2012-11-09 00:02 | 2012-11-09 00:54 | 52 | 11kV | 63648 | 1224 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12580 Erina Pnl.16 tripped on 16R - A & B phase timed O/C Branch removed from HV near PT48048 | November | 2012 | 2013Q2 | 2013 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Veg | 2012-11-09 | N | 52 | N | 12 | N | N | 1.1101 | 39.4971 | 46512.0811
[7 empty] | 18502 | 19904 | 898032 | 2012-11-09 | 2012-11-09 01:45 | 105 | 11kV | 9309 | 152 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | LID 122881 Live Line Clamps at PoleAF-60051 Siezed. Need to be fixed before repairs can proceed along spur. See Report 122876/ OMS 898483 | November | 2012 | 2013Q2 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2012-11-09 | N | 61.2434 | N | 12 | N | N | 1.1101 | 39.4971 | 6802.7426
[7 empty] | 17352 | 7491 | 898183 | 2012-11-09 01:49 | 2012-11-09 03:02 | 73 | 11kV | 7935 | 1095 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC45092 Mannering Park tripped @ reclosed on IOC @PT13588 - Footpath Phase 31.5 A HDO operated - restored @3:02 Tree branch on removed from PT13588 see 899675 899674 | November | 2012 | 2013Q2 | 2013 | ZN12590:PA7 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Veg | 2012-11-09 | N | 7.2466 | N | 12 | N | N | 1.1101 | 39.4971 | 5798.664
[7 empty] | 17475 | 8556 | 898182 | 2012-11-09 02:07 | 2012-11-09 03:04 | 57 | 11kV | 116457 | 2185 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn690 Campsie Pa14 fdr tripped on Aph, Time, Earth Fault, EFI, Fault Check. Tx1 Fault Check 11kv trip, Zone Earth, Tx1 Group Earth EFI: S2322 S3337 Cause: UG Fault Remarks: 11kv underground fault from S33337Sw/B to S35327Sw/A Note:S3337 is a hazemyer RMI See 899231,3 Exclude 898182 | November | 2012 | 2013Q2 | 2013 | ZN690:PA14 | ZN690:PA14 | ZN00690/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-11-09 | N | 53.2984 | N | 12 | N | N | 1.1101 | 39.4971 | 85103.3407
[7 empty] | 17407 | 8029 | 898170 | 2012-11-09 00:37 | 2012-11-09 03:21 | 164 | 11kV | 65272 | 398 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Recloser CP3281 Bay Cooper Tripped and locked out Cause: Branch removed by DOp near PT2132 and AB298. See OMS 898170 898190. | November | 2012 | 2013Q2 | 2013 | ZN2400:PA18 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2012-11-09 | N | 164 | N | 12 | N | N | 1.1101 | 39.4971 | 47698.8524
[7 empty] | 18244 | 17004 | 898199 | 2012-11-09 04:30 | 2012-11-09 08:27 | 237 | 11kV | 690965 | 3547 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah North, Panel 11 Fdr CB tripped on 11R A and B phase OC, 11kV trip. Flying fox found adjacent PT.15479. Bonds burnt off 11kV UG/OH adjacent link 21220 | November | 2012 | 2013Q2 | 2013 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Not Veg | 2012-11-09 | N | 194.8027 | N | 12 | N | N | 1.1101 | 39.4971 | 504936.842
[7 empty] | 18014 | 14532 | 898299 | 2012-11-08 07:49 | 2012-11-09 09:13 | 1523.8667 | 11kV | 19734 | 78 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122859 33kV into 11kV OHM at pole KT-70124. Sw 3305 Prot. op. E/F & Diff prot. Sw 3349 Prot op. E/F & Diff prot. 11kv Sw 7490 no prot. op. | November | 2012 | 2013Q2 | 2013 | 228:7490 | 228:85413 | ZN00228/085413 | NEWCASTLE | OH | Not Veg | 2012-11-08 | N | 253 | N | 4 | N | N | 1.1101 | 39.4971 | 14421.0251
[7 empty] | 17486 | 8662 | 898218 | 2012-11-09 07:02 | 2012-11-09 09:50 | 168 | 11kV | 168 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122889 A phase DOLF : 10 Amp Excluded OMS 898218 | November | 2012 | 2013Q2 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | UG | Not Veg | 2012-11-09 | N | 168 | N | 12 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 17078 | 4259 | 898168 | 2012-11-09 00:30 | 2012-11-09 10:44 | 614 | 11kV | 16246 | 164 | HV | Arcing | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC44947 Gavenlock Rd - Tripped / reclosed / tripped / reclosed/ tripped & locked out on IOC Arcing/flashover on tee to PT12444. PT12444 interrupted MG required. see 899630 899629 899627 | November | 2012 | 2013Q2 | 2013 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2012-11-09 | N | 99.061 | N | 12 | N | N | 1.1101 | 39.4971 | 11872.0976
[7 empty] | 16562 | 375 | 898767 | 2012-11-09 22:31 | 2012-11-10 00:02 | 91 | 11kV | 67977 | 747 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.14143 Somersby Pnl.17 tripped on B & C phase IOC, EFI Possum on UGOH adjacent S14926 | November | 2012 | 2013Q2 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-11-09 | N | 91 | N | 12 | N | N | 1.1101 | 39.4971 | 49675.5866
[7 empty] | 17057 | 4083 | 898771 | 2012-11-09 22:45 | 2012-11-10 00:04 | 79 | 11kV | 152487 | 2004 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.10 tripped on A & B phase O/C and SEF Abnormal: AB41042 Closed - AB41878 OPEN & Defective Bat on 11kV near AB42404 and bond burnt off AB42638 | November | 2012 | 2013Q2 | 2013 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2012-11-09 | N | 76.0913 | N | 12 | N | N | 1.1101 | 39.4971 | 111433.002
[7 empty] | 17730 | 11811 | 898783 | 2012-11-10 01:57 | 2012-11-10 03:37 | 100 | 11kV | 170010 | 1796 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 122904 2 fault operations C phase Overcurrent; Earth fault Possum found at base of pole IV-19955 | November | 2012 | 2013Q2 | 2013 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Not Veg | 2012-11-10 | N | 94.6604 | N | 4 | N | N | 1.1101 | 39.4971 | 124238.2936
[7 empty] | 16589 | 570 | 898674 | 2012-11-09 16:51 | 2012-11-10 04:55 | 724 | 11kV | 225673 | 1132 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 122900 2 fault operations UGOH blown at pole CH-37008 | November | 2012 | 2013Q2 | 2013 | 223:14397 | 223:14397 | ZN00223/014397 | LAKE MACQUARIE | Unknown | Unknown | 2012-11-09 | N | 199.3578 | N | 12 | N | N | 1.1101 | 39.4971 | 164915.1722
[7 empty] | 16523 | 121 | 898778 | 2012-11-09 23:26 | 2012-11-10 05:25 | 359 | 11kV | 2879 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 45010 Palm Grove tripped on A & C phase OC, Earth Fault, lockout Branch on mains adjacent to LK43412 see 899789 899787 | November | 2012 | 2013Q2 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-11-09 | N | 169.3529 | N | 12 | N | N | 1.1101 | 39.4971 | 2103.8883
[7 empty] | 18187 | 16462 | 898833 | 2012-11-10 10:00 | 2012-11-10 11:15 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122909 B phase DOLF : 10 Amp Tx Volts: Aph - 251V, Bph - 251V, Cph - 251V Excluded OMS 898833 | November | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2012-11-10 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 17229 | 6276 | 898868 | 2012-11-10 13:32 | 2012-11-10 15:21 | 109 | 11kV | 90906 | 834 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 122912 1 fault operation Car hit pole HR-29004. LV Service damaged. A-E Overcurrent Flag. "SEF Lockout Alarm" operated then went to normal. Excluded OMS 898868; 898869; 898870 | November | 2012 | 2013Q2 | 2013 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Not Veg | 2012-11-10 | N | 109 | N | 4 | N | N | 1.1101 | 39.4971 | 66431.4235
[7 empty] | 17671 | 11059 | 898918 | 2012-11-10 22:13 | 2012-11-11 04:05 | 352 | 11kV | 135655 | 1111 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 122917 2 fault operations Overcurrent; Earth fault Car hit Pole HR-21143. HV into LV-premises checked OK. Excluded OMS Job Nos. 898918 & 898919. | November | 2012 | 2013Q2 | 2013 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2012-11-10 | N | 122.1017 | N | 4 | N | N | 1.1101 | 39.4971 | 99132.6729
[7 empty] | 17158 | 5159 | 898929 | 2012-11-11 02:16 | 2012-11-11 09:45 | 449 | 11kV | 27056 | 464 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At Zn12620 Noraville Panel 13 interrupted by AOp to provide isolation for the following sub S14534 Yaralla Beachcomber damaged by fire see OMS 900015 898929 | November | 2012 | 2013Q2 | 2013 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | UG | Not Veg | 2012-11-11 | N | 58.3103 | N | 4 | N | N | 1.1101 | 39.4971 | 19771.7268
[7 empty] | 17615 | 10244 | 898932 | 2012-11-11 06:49 | 2012-11-11 10:25 | 216 | 11kV | 1512 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Panel 37L Avoca Beach feeder from ZN12570 Avoca At PT18112 Townsend Avoca 1.0 11kV Roadside 20A fuse operated. Cause: Fuse fatigue See OMS 900000 898932 | November | 2012 | 2013Q2 | 2013 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2012-11-11 | N | 216 | N | 4 | N | N | 1.1101 | 39.4971 | 1104.925
[7 empty] | 17958 | 13722 | 898984 | 2012-11-11 13:58 | 2012-11-11 20:05 | 367 | 11kV | 82683 | 1219 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 122923 2 fault operations Earth fault Dead Magpie found at sub 50375 Soldier Settlement sub. 11kV Wires down at Pole HS-43360. Grass Fire involved. Flags Sw 80923 OC & EF (51N) + Lockout. Also Repaired 11kV L/F 41555. On DOLF was welded in. Excluded OMS 898984; 898987; 898990; 899002 | November | 2012 | 2013Q2 | 2013 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Not Veg | 2012-11-11 | N | 67.8285 | N | 4 | N | N | 1.1101 | 39.4971 | 60422.2977
[7 empty] | 16639 | 894 | 899032 | 2012-11-11 20:23 | 2012-11-12 02:45 | 382 | 11kV | 10097 | 75 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 122925 4 fault operations Earth fault Broken stay wire resting on 11kV at Pole DP-50003. Excluded OMS 899032, 899042 & 899044 | November | 2012 | 2013Q2 | 2013 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2012-11-11 | N | 134.6267 | N | 4 | N | N | 1.1101 | 39.4971 | 7378.5898
[7 empty] | 16729 | 1405 | 899367 | 2012-11-12 13:46 | 2012-11-12 16:09 | 143 | 11kV | 100386 | 702 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Ex Zn12610 Long Jetty Pnl.18 - Burnt off bail clamp @ 11kV UGPOH between S.12134 and LB47175. | November | 2012 | 2013Q2 | 2013 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | Unknown | Unknown | 2012-11-12 | N | 143 | N | 4 | N | N | 1.1101 | 39.4971 | 73359.1279
[7 empty] | 17907 | 13178 | 899419 | 2012-11-12 15:18 | 2012-11-12 16:12 | 54 | 11kV | 39096 | 724 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2602 Clovelly 11kv fdr pa10 fdr tripped on: Bph IOC Earth Fault EFI Fault Check EFI's:Nil Cause: UG Fault Remarks:Suspect Cable Failure from Zn2602 Clovelly to S713 to S2213 See 899580 exclude 899419 | November | 2012 | 2013Q2 | 2013 | ZN2602:PA10 | ZN36800:PA31 | ZN36800/000031 | RANDWICK | UG | Not Veg | 2012-11-12 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 28570.2037
[7 empty] | 18309 | 17533 | 899462 | 2012-11-12 16:30 | 2012-11-12 18:13 | 103 | 11kV | 66324 | 814 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn35370 Galston Panel 10 Tripped reclosed tripped and locked out on Relays: O/C (a and B phase), Reclose lockout and EFI. Large Tree branch removed Near PT1983 Galston Clarke Estate See OMS 902129 902133 899463 | November | 2012 | 2013Q2 | 2013 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2012-11-12 | N | 81.4791 | N | 4 | N | N | 1.1101 | 39.4971 | 48467.623
[7 empty] | 16922 | 3059 | 899404 | 2012-11-12 14:59 | 2012-11-12 23:25 | 506 | 11kV | 1012 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 122936 C phase burnt off at base of dolf at sub 51367 Excluded OMS 899404 (heirarchy) | November | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-11-12 | N | 506 | N | 4 | N | N | 1.1101 | 39.4971 | 739.5398
[7 empty] | 17928 | 13391 | 900578 | 2012-11-13 02:16 | 2012-11-13 03:43 | 87 | 11kV | 176978 | 2858 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Sn80 Chatswood Panel 30 Tripped on B and C phase IOC and Timed. Cause: Feeder patrolled OK - Suspect Branch contact mains - report of arcing wires near 155 River Rd. See OMS 900578 899546 | November | 2012 | 2013Q2 | 2013 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Veg | 2012-11-13 | N | 61.9237 | N | 3 | N | N | 1.1101 | 39.4971 | 129330.3024
[7 empty] | 17187 | 5720 | 900022 | 2012-11-13 19:27 | 2012-11-13 21:10 | 103 | 11kV | 92405 | 1462 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | @Zn3155 Double Bay 11kV Pa29 Opened on intertrip Recieve @S1859 fdr "Zn3155 Double Bay etc" Opened on Intertrip and REcieve @S1605 11kv OCB tripped on O/C and Intertrip Send Abnormal: S3176SwA Open S8394 No4 Close, S3045SwB Close S1605 HV CB Open Cause: Other details provided Unstable Protection, Vibration on clsoing See 900783,4,5 LV// 900807 Exclude 90022,3 | November | 2012 | 2013Q2 | 2013 | ZN3155:PA29 | ZN3155:PA29 | ZN03155/000029 | WOOLLAHRA | UG | Not Veg | 2012-11-13 | N | 63.2045 | N | 3 | N | N | 1.1101 | 39.4971 | 67526.8485
[7 empty] | 17625 | 10369 | 900043 | 2012-11-13 20:49 | 2012-11-14 01:10 | 261 | 11kV | 5742 | 22 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex ZN 2196 Milperra 11kv pnl 11 "S-7188 Green Marigold No.2" Feeder @S-2540 Daisy Car No.1 H.V TX isolator found tripped off. B phase HV OEFMA 75A fuse blown Remarks: cause not ascertained. Possible fuse fatigue. LV // found in see seperate interruption report Related jobs: #900043, 900044, 900045, 900230 | November | 2012 | 2013Q2 | 2013 | ZN2196:PA11 | ZN2196:PA11 | ZN02196/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-11-13 | N | 261 | N | 3 | N | N | 1.1101 | 39.4971 | 4196.0842
[7 empty] | 17951 | 13667 | 900487 | 2012-11-14 13:00 | 2012-11-14 18:15 | 315 | 11kV | 688 | 374 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Unselected | N | REcloser 50630 tripped and reclosed. Auto link 44779 operated on one leg only. Tree branch broke cross arm causing 11kV OH onto ground | November | 2012 | 2013Q2 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-11-14 | N | 1.8396 | N | 1 | N | N | 1.1101 | 39.4971 | 502.7701
[7 empty] | 16574 | 504 | 900709 | 2012-11-15 12:03 | 2012-11-15 16:35 | 272 | 11kV | 272 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 122983 Single phase DOLF : 10 Amp. Excluded OMS 900709 | November | 2012 | 2013Q2 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | UG | Not Veg | 2012-11-15 | N | 272 | N | 2 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 17462 | 8422 | 900830 | 2012-11-15 19:40 | 2012-11-15 20:50 | 69.6667 | 11kV | 1950.6667 | 28 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 122984 A phase A PHASE 11KV LINK 3737 FAULTY. ALL 3 LINKS CHANGED.GRASSFIRE STARTED ON 13/11/2012 AT THIS LOCATION BURNING OUT APPROX 5 ACRES.(2 HECTARES) | November | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-11-15 | N | 69.6667 | N | 2 | N | N | 1.1101 | 39.4971 | 1425.4897
[7 empty] | 16871 | 2489 | 901268 | 2012-11-16 19:04 | 2012-11-16 19:30 | 26 | 11kV | 20254 | 779 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.34 tripped on A & B phase IOC and Earth Fault Tree branch removed by DOp outside 72 Lake Shore Dr. | November | 2012 | 2013Q2 | 2013 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2012-11-16 | N | 26 | N | 2 | N | N | 1.1101 | 39.4971 | 14801.0258
[7 empty] | 18227 | 16871 | 901264 | 2012-11-16 18:48 | 2012-11-16 20:13 | 85 | 11kV | 2975 | 35 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn35370 Galston ex Panel 2 Autolink 367 Tree branch on OH mains adjacent PT1817 | November | 2012 | 2013Q2 | 2013 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2012-11-16 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 2174.0423
[7 empty] | 17480 | 8581 | 901339 | 2012-11-17 08:36 | 2012-11-17 11:45 | 188.5167 | 11kV | 942.5833 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 123005 A Taylor was doing earthing tests/maintenance and as part of his HAC used a proximity tester near the pole. From testing it appeared the pole was conductive so requested the sub me isolated to replace all insulators. No protection operated. | November | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-11-17 | N | 188.5167 | N | 3 | N | N | 1.1101 | 39.4971 | 688.8121
[7 empty] | 18013 | 14469 | 901348 | 2012-11-17 09:20 | 2012-11-17 12:00 | 160 | 11kV | 7360 | 46 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Planned LID 123000 Customers given insufficient notice Emergency replacement of 11kV air break switch | November | 2012 | 2013Q2 | 2013 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2012-11-17 | N | 160 | N | 3 | N | N | 1.1101 | 39.4971 | 5378.4709
[7 empty] | 17573 | 9605 | 901412 | 2012-11-17 18:18 | 2012-11-18 01:40 | 442 | 11kV | 15809 | 117 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 123006 2 fault operations Earth fault arro sub Sw 8684 Timed E/F. Car hit Pole JT-10098. 11kV fell into LV near Hexham South sub 8390-no customer damage. Excluded OMS Job Nos. 901412 & 901421-4. Cass Job Nos. 777117 & 777119. 33kV Fdr 3150 de-energised while LV & 11kV repaired. | November | 2012 | 2013Q2 | 2013 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2012-11-17 | N | 135.1197 | N | 3 | N | N | 1.1101 | 39.4971 | 11552.7509
[7 empty] | 18090 | 15716 | 901444 | 2012-11-18 06:50 | 2012-11-18 09:20 | 150 | 11kV | 300 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123011 A phase Live line connection had burnt away and was replaced. No protection operation associated with this job. Excluded OMS 901444 | November | 2012 | 2013Q2 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2012-11-18 | N | 150 | N | 2 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 17753 | 11959 | 901537 | 2012-11-18 21:57 | 2012-11-18 23:22 | 85 | 11kV | 62272 | 826 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.4 tripped on A & B phase OC Branch on mains at USL44812 see 902648 602646 | November | 2012 | 2013Q2 | 2013 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2012-11-18 | N | 75.3898 | N | 2 | N | N | 1.1101 | 39.4971 | 45506.5409
[7 empty] | 17228 | 6253 | 902668 | 2012-11-19 07:16 | 2012-11-19 07:20 | 4 | 11kV | 420 | 105 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.13000 lake Munmorah New Pnl.1 tripped on SEL Abnormal: AB43821 was closed and LK44436 Open Staff Error - Pnl.1 tripped during switching. protection on Pnl.1 Old was name N/A instead of Pnl.1 New | November | 2012 | 2013Q2 | 2013 | ZN12590:PA1 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2012-11-19 | N | 4 | N | 7 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 16976 | 3396 | 901568 | 2012-11-19 08:09 | 2012-11-19 10:05 | 116 | 11kV | 172229 | 1672 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2310 Punchbowl Panel 31 Roselands feeder tripped on: C PHASE IOC & EFI Remarks: UG fault. Underground cable fault. Related jobs: #901568, 902567 | November | 2012 | 2013Q2 | 2013 | ZN2310:PA31 | ZN35800:PA2 | ZN35800/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-11-19 | N | 103.0078 | N | 7 | N | N | 1.1101 | 39.4971 | 125859.8733
[7 empty] | 18002 | 14227 | 901953 | 2012-11-19 15:43 | 2012-11-19 16:20 | 36.8833 | 11kV | 17372.05 | 471 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 40075 Yarramalong tripped / reclosed and reclosed on B phase OC Tree on mains cleared by DOp | November | 2012 | 2013Q2 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2012-11-19 | N | 36.8833 | N | 7 | N | N | 1.1101 | 39.4971 | 12694.9818
[7 empty] | 17203 | 5934 | 901924 | 2012-11-19 14:57 | 2012-11-19 17:18 | 141 | 11kV | 101748 | 814 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Wind | N | At S35370 Galston Panel 10 Tripped on B and Cphase O/C Abnormal Switching: SW/A closed at S8401 Open at CP482 Cause: OH mains to patrol 906163 906165 906166 901924 | November | 2012 | 2013Q2 | 2013 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2012-11-19 | N | 124.9975 | N | 7 | N | N | 1.1101 | 39.4971 | 74354.4373
[7 empty] | 17869 | 12863 | 902024 | 2012-11-19 17:47 | 2012-11-19 18:18 | 31 | 11kV | 6293 | 231 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123026 2 fault operations 3 phase Overcurrent | November | 2012 | 2013Q2 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2012-11-19 | N | 27.2424 | N | 7 | N | N | 1.1101 | 39.4971 | 4598.7388
[7 empty] | 16938 | 3149 | 902032 | 2012-11-19 18:30 | 2012-11-19 20:10 | 100 | 11kV | 9600 | 96 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT18784 Mulloway Tarwhine - Footpath phase HDO Fuse Fatigued | November | 2012 | 2013Q2 | 2013 | ZN12590:PA4 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Not Veg | 2012-11-19 | N | 100 | N | 7 | N | N | 1.1101 | 39.4971 | 7015.3968
[7 empty] | 18458 | 19153 | 902074 | 2012-11-19 23:48 | 2012-11-20 01:37 | 109 | 11kV | 49508 | 600 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn.12600 lisarow Pnl.1 tripped on ABC phase Overcurrent, lockout and timing Possum on UGOH below S14833 (no efi Fitted) see 902710 902709 902708 | November | 2012 | 2013Q2 | 2013 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2012-11-19 | N | 82.5133 | N | 7 | N | N | 1.1101 | 39.4971 | 36178.9862
[7 empty] | 17918 | 13282 | 902107 | 2012-11-20 03:59 | 2012-11-20 04:34 | 35 | 11kV | 17960 | 898 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 123028 Pole JV-41493 fire. 33kV Fdr 3431 de-energised-no interruption. | November | 2012 | 2013Q2 | 2013 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2012-11-20 | N | 20 | N | 6 | N | N | 1.1101 | 39.4971 | 13124.6383
[7 empty] | 17679 | 11178 | 902103 | 2012-11-20 07:32 | 2012-11-20 08:55 | 83 | 11kV | 166 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123029 Single phase DOLF : 10 Amp Volts = 252 Volts Current = 31Amps | November | 2012 | 2013Q2 | 2013 |  |  |  |  | UG | Not Veg | 2012-11-20 | N | 83 | N | 6 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 16945 | 3209 | 902182 | 2012-11-20 09:37 | 2012-11-20 10:26 | 49 | 11kV | 8820 | 180 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.8 tripped on b phase Earth Faul, EFI Backhoe damaged cable from pnl.8 to S14124. Damage site on corner Racecourse Rd and Faunce St. | November | 2012 | 2013Q2 | 2013 | ZN12650:PA8 | ZN12650:PA8 | ZN12650/000008 | CENTRAL COAST | UG | Not Veg | 2012-11-20 | N | 49 | N | 6 | N | N | 1.1101 | 39.4971 | 6445.3959
[7 empty] | 18311 | 17554 | 902292 | 2012-11-20 11:59 | 2012-11-20 13:40 | 101 | 11kV | 1313 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123038 Single phase DOLF : 20 Amp Please patrol the feeder, W Walton reports these fuses have blown several times. Excluded OMS 902292 | November | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2012-11-20 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 959.5017
[7 empty] | 18152 | 16099 | 902387 | 2012-11-20 14:13 | 2012-11-20 16:30 | 137 | 11kV | 959 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 123040 C phase bad connection on fuse carrier Excluded OMS 902387 - | November | 2012 | 2013Q2 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2012-11-20 | N | 137 | N | 6 | N | N | 1.1101 | 39.4971 | 700.8089
[7 empty] | 18439 | 18978 | 902477 | 2012-11-20 16:51 | 2012-11-21 00:58 | 487 | 11kV | 78435 | 231 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 123043 2 fault operations Overcurrent 11kV tie off at Pole EE-60029. Excluded OMS 902477 | November | 2012 | 2013Q2 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2012-11-20 | N | 339.5455 | N | 6 | N | N | 1.1101 | 39.4971 | 57317.9846
[7 empty] | 17849 | 12704 | 902923 | 2012-11-21 17:25 | 2012-11-21 23:40 | 375 | 11kV | 4875 | 13 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | Ex Zn116 Leichhardt ZN pnl 45 "S-8189 Derbyshire William" feeder @S-5207 The Crescent Vic B phase top of LV board H.R connection. Remarks: interrupted for safely reasons. @S-5207 The Crescent Vic B phase top of L.V board H.R connection. Centre interrupted for safety Related jobs: #902923, 903049 | November | 2012 | 2013Q2 | 2013 | ZN116:PA45 | ZN116:PA1 | ZN00116/000001 | INNER WEST | UG | Not Veg | 2012-11-21 | N | 375 | N | 1 | N | N | 1.1101 | 39.4971 | 3562.5062
[7 empty] | 16788 | 1973 | 902997 | 2012-11-22 08:12 | 2012-11-22 12:15 | 243 | 11kV | 729 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123065 C phase Repair damaged LL Clamp at T-off pole 8O-30049 to sub 71642. Excluded OMS 902997 | November | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-11-22 | N | 243 | N | 2 | N | N | 1.1101 | 39.4971 | 532.7317
[7 empty] | 18376 | 18148 | 903190 | 2012-11-22 12:18 | 2012-11-22 14:02 | 104 | 11kV | 166646 | 1609 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 Meadowbank Panel 40Opened on Earth Fault, Fault Check Relay and EFI. Zone Earth and Group Earth Cause: UG cable fault between Pa40 at Zn4545 Meadowbank and SW/A at S47010 Anthony Betts. See OMS 904786 904790 904713 903184 | November | 2012 | 2013Q2 | 2013 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | UG | Not Veg | 2012-11-22 | N | 103.5712 | N | 2 | N | N | 1.1101 | 39.4971 | 121779.9816
[7 empty] | 18202 | 16615 | 903575 | 2012-11-23 18:15 | 2012-11-23 20:04 | 109 | 11kV | 8187 | 79 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 123069 2 fault operations Earth fault A phase DOLF : 20 Amp Replaced damaged Aph fuse & carrier at LF 40751. Excluded OMS No. 903575 & 903605 | November | 2012 | 2013Q2 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2012-11-23 | N | 103.6329 | N | 1 | N | N | 1.1101 | 39.4971 | 5982.8181
[7 empty] | 18346 | 17842 | 903608 | 2012-11-24 04:14 | 2012-11-24 05:50 | 96 | 11kV | 7200 | 75 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | PT11849 Charlton Rolls - Middle & roadside HDO's blown (40Amp) Possible animals/bird - DOp reports no wires down | November | 2012 | 2013Q2 | 2013 | ZN12610:PA22 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2012-11-24 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 5261.5476
[7 empty] | 18024 | 14612 | 904004 | 2012-11-24 11:43 | 2012-11-24 12:05 | 22 | 11kV | 858 | 39 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 123076 B phase section isolated to repair stranded mains pole GN-80038 to GN-80010 | November | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-11-24 | N | 22 | N | 5 | N | N | 1.1101 | 39.4971 | 627.0011
[7 empty] | 18526 | 20087 | 903666 | 2012-11-24 15:30 | 2012-11-24 16:02 | 32 | 11kV | 6240 | 195 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn7900 Capmbell St Tx2 Group Earth. 11kv trip Pa15 the belmore mary fdr tripped on Earth Fault with EFI See 903948 exclude 903666 | November | 2012 | 2013Q2 | 2013 | ZN7900:PA15 | ZN7900:PA15 | ZN07900/000015 | SYDNEY | UG | Not Veg | 2012-11-24 | N | 32 | N | 5 | N | N | 1.1101 | 39.4971 | 4560.008
[7 empty] | 17066 | 4166 | 903674 | 2012-11-24 16:46 | 2012-11-24 18:50 | 124 | 11kV | 124 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123080 Single phase DOLF : 10 mp excluded OMS 903674 | November | 2012 | 2013Q2 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-11-24 | N | 124 | N | 5 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 17911 | 13199 | 903689 | 2012-11-24 16:40 | 2012-11-24 22:00 | 320 | 11kV | 10695 | 231 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123077 Trip and reclose Sectionaliser operated. Earth fault; Overcurrent Line patrolled after lightning storm no damage found. Excluded OMS 903689. | November | 2012 | 2013Q2 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2012-11-24 | N | 46.2987 | N | 5 | N | N | 1.1101 | 39.4971 | 7815.5906
[7 empty] | 16823 | 2177 | 904100 | 2012-11-25 02:32 | 2012-11-25 06:00 | 208 | 11kV | 21424 | 103 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123088 2 fault operations Earth fault | November | 2012 | 2013Q2 | 2013 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2012-11-25 | N | 208 | N | 23 | Y | Y | 1.1101 | 39.4971 | 15656.0273
[7 empty] | 18129 | 15954 | 903712 | 2012-11-25 04:00 | 2012-11-25 07:00 | 180 | 11kV | 1800 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123091 3 phase DOLF : 16 Amp Excluded OMS 903712 | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-11-25 | N | 180 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 17746 | 11925 | 904153 | 2012-11-25 03:01 | 2012-11-25 08:05 | 304 | 11kV | 25048 | 255 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 123090 2 fault operations Sensitive Earth fault Replaced blown TX at sub 71720. Excluded OMS 903711 # | November | 2012 | 2013Q2 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2012-11-25 | N | 98.2275 | N | 23 | Y | Y | 1.1101 | 39.4971 | 18304.3396
[7 empty] | 18448 | 19103 | 903716 | 2012-11-25 05:54 | 2012-11-25 08:15 | 141 | 11kV | 241897 | 2465 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2568 St Peters Pa32 fdr tripped on: Relays: Earth Fault, EFI, Fault CHeck Signals: 11kv trip, Zone Earth, Group 4 Earth Field EFI's: S21 S6169 Cause: UG Fault Remarks: 11kv fdr fault btw S6169 Sw/B to S1690 Sw/A See 903964,5 LV// 903967 Exclude 903716,7,8,9,29,31,65 | November | 2012 | 2013Q2 | 2013 | ZN2568:PA32 | ZN2568:PA32 | ZN02568/000032 | SYDNEY | UG | Not Veg | 2012-11-25 | N | 98.1327 | N | 23 | Y | Y | 1.1101 | 39.4971 | 176771.1928
[7 empty] | 18168 | 16281 | 903720 | 2012-11-25 06:15 | 2012-11-25 10:12 | 237 | 11kV | 1896 | 8 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | REC 47302 - Hue Hue Sparks 0.1 11kV O/H down between REC 47302 Hue Hue Sparks 0.1 and LK 42977 Linesmen have repaired Earthing Conductor also stolen from REC 47302, Subs have replaced | November | 2012 | 2013Q2 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2012-11-25 | N | 237 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1385.5409
[7 empty] | 16913 | 3009 | 903727 | 2012-11-25 07:47 | 2012-11-25 11:40 | 233 | 11kV | 233 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123097 C phase DOLF : 10 Amp Excluded OMS 903727 246 Volts | November | 2012 | 2013Q2 | 2013 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | UG | Not Veg | 2012-11-25 | N | 233 | N | 23 | Y | Y | 1.1101 | 39.4971 | 170.2695
[7 empty] | 17582 | 9678 | 903725 | 2012-11-25 07:38 | 2012-11-25 12:55 | 317 | 11kV | 551 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123093 Single phase DOLF : 10 Amp Excluded OMS 903725 | November | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-11-25 | N | 183.6667 | N | 23 | Y | Y | 1.1101 | 39.4971 | 402.6545
[7 empty] | 17560 | 9454 | 903775 | 2012-11-25 11:13 | 2012-11-25 13:00 | 107 | 11kV | 88012 | 1566 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Zn10990 Arncliffe Pa7 fdr tripped, reclosed, tripped and locked out on Relays- E/L, Lockout, Timing, EFI Signals: 11kv trip, Zone Earth Field EFI's: S10688 S10612 Cause: Insulator Failed Remarks: 11kv fdr from AB31263 to AB30559 to AB31205 tedd S10723. See 904061,2,4 Exclude 903775,7,8,81 | November | 2012 | 2013Q2 | 2013 | ZN10990:PA7 | ZN10998:PA32 | ZN10998/000032 | BAYSIDE | OH | Not Veg | 2012-11-25 | N | 56.2018 | N | 23 | Y | Y | 1.1101 | 39.4971 | 64316.5737
[7 empty] | 18118 | 15902 | 903780 | 2012-11-25 11:35 | 2012-11-25 14:05 | 150 | 11kV | 5550 | 37 | HV | Overload LV Parallel | Utility Process Issue | O/H Link | Unplanned | Unselected | N | PT10276 Argyle Princes No1 Centre Phase HDO fuse blew but failed to drop out Ex Panel 12 fdr from Zn10990 Arncliffe Zone Cuase: Lv Parrallel (during feeder trip) Ramerks: See seaperate interrution report for panel 7 @ Arncliffe See 904069 Exlcude 903780,3 | November | 2012 | 2013Q2 | 2013 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | OH | Not Veg | 2012-11-25 | N | 150 | N | 23 | Y | Y | 1.1101 | 39.4971 | 4055.7763
[7 empty] | 16863 | 2431 | 903784 | 2012-11-25 14:15 | 2012-11-25 14:50 | 35 | 11kV | 35 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Previous Storm | N | LID 123101 Single phase TAP POSITION CHANGED TO POS 4 10725 TAP.NO LOAD VOLTS =242V. Excluded OMS 903784 | November | 2012 | 2013Q2 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | UG | Not Veg | 2012-11-25 | N | 35 | N | 23 | Y | Y | 1.1101 | 39.4971 | 25.577
[7 empty] | 18243 | 17001 | 903799 | 2012-11-25 13:45 | 2012-11-25 15:00 | 75 | 11kV | 150 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123102 B phase DOLF : 10 Amp VOLTS= 242,242,243 LOAD A=0 B= 18 C= 0 Excluded OMS REPORT NO 903799. | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-11-25 | N | 75 | N | 23 | Y | Y | 1.1101 | 39.4971 | 109.6156
[7 empty] | 17467 | 8484 | 903785 | 2012-11-25 11:50 | 2012-11-25 15:02 | 192 | 11kV | 70934 | 874 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 123100 2 fault operations Sensitive Earth fault Fdr abnormal for SI 26551 ABS 7622 CLOSED & ABS 1975 OPEN. Cut away faulty L/A at UGOH pole IV-40093. Requires replacement. Excluded OMS 903785 & 903787 | November | 2012 | 2013Q2 | 2013 | 225:33679 | 270:83594 | ZN00270/083594 | LAKE MACQUARIE | OH | Not Veg | 2012-11-25 | N | 81.1602 | N | 23 | Y | Y | 1.1101 | 39.4971 | 51836.475
[7 empty] | 18379 | 18183 | 903803 | 2012-11-25 15:30 | 2012-11-25 16:30 | 60 | 11kV | 60 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123103 C phase DOLF : 10 Amp Excluded OMS 903803 | November | 2012 | 2013Q2 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2012-11-25 | N | 60 | N | 23 | Y | Y | 1.1101 | 39.4971 | 43.8462
[7 empty] | 17283 | 6913 | 903817 | 2012-11-25 15:08 | 2012-11-25 16:58 | 110 | 11kV | 30030 | 273 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LOID 123105 C phase Overcurrent FEEDER PATROLLED BY ON CALL STAFF,NO FAULT FOUND.FEEDER NOT ABLE TO BE CLOSED ON BY ON CALL STAFF(NO APPROPRIATE OPERATING AUTHORITY)HAD TO WAIT FOR DO FROM NEWCASTLE.SEE REPORT NO 123108. | November | 2012 | 2013Q2 | 2013 | 501:48118 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2012-11-25 | N | 110 | N | 23 | Y | Y | 1.1101 | 39.4971 | 21945.0383
[7 empty] | 18027 | 14669 | 903821 | 2012-11-25 15:42 | 2012-11-25 17:27 | 105.2167 | 11kV | 5366.05 | 51 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123104 B & C phase DOLF : 32 Amp | November | 2012 | 2013Q2 | 2013 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2012-11-25 | N | 105.2167 | N | 23 | Y | Y | 1.1101 | 39.4971 | 3921.3511
[7 empty] | 16722 | 1346 | 903833 | 2012-11-25 16:50 | 2012-11-25 18:00 | 70 | 11kV | 70 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123106 A phase DOLF : 10 Amp Excluded OMS 903833 Volts = 236 | November | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-11-25 | N | 70 | N | 23 | Y | Y | 1.1101 | 39.4971 | 51.1539
[7 empty] | 16727 | 1395 | 903839 | 2012-11-25 15:08 | 2012-11-25 19:20 | 252 | 11kV | 3780 | 15 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 123108 C phase DOLF : 16 Amp FAULTY ARRESTOR AFTER STORM.SEE REPORT NO 123105. Excluded OMS REPORT NO 903839. | November | 2012 | 2013Q2 | 2013 | 501:48118 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2012-11-25 | N | 252 | N | 23 | Y | Y | 1.1101 | 39.4971 | 2762.3125
[7 empty] | 17105 | 4475 | 903854 | 2012-11-25 19:49 | 2012-11-25 20:45 | 55.8167 | 11kV | 5637.4833 | 101 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 123109 A & B phase DOLF : 40 Amp Magpie across 2 phases at substation 19429. Readings as left 120A, 140A, 110A @ 248V. | November | 2012 | 2013Q2 | 2013 | 260:33344 | 239:82128 | ZN00239/082128 | LAKE MACQUARIE | OH | Not Veg | 2012-11-25 | N | 55.8167 | N | 23 | Y | Y | 1.1101 | 39.4971 | 4119.7065
[7 empty] | 17579 | 9645 | 903842 | 2012-11-25 18:12 | 2012-11-25 21:54 | 221.9833 | 11kV | 11321.15 | 51 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123107 B & C phase DOLF : 32 Amp | November | 2012 | 2013Q2 | 2013 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2012-11-25 | N | 221.9833 | N | 23 | Y | Y | 1.1101 | 39.4971 | 8273.1625
[7 empty] | 16962 | 3320 | 903691 | 2012-11-25 18:30 | 2012-11-25 23:20 | 290 | 11kV | 580 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123085 Single phase DOLF : 10 Amp Excluded OMS 903691 | November | 2012 | 2013Q2 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2012-11-25 | N | 290 | N | 23 | Y | Y | 1.1101 | 39.4971 | 423.8469
[7 empty] | 16836 | 2231 | 903864 | 2012-11-25 21:06 | 2012-11-25 23:58 | 172 | 11kV | 172 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 123110 Single phase DOLF : 10 Amp Replaced L/A's. Excluded OMS 903864 | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-11-25 | N | 172 | N | 23 | Y | Y | 1.1101 | 39.4971 | 125.6925
[7 empty] | 17878 | 12920 | 903847 | 2012-11-25 19:15 | 2012-11-26 03:50 | 515 | 11kV | 515 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 123111 Single phase DOLF : 10 Amp Replaced faulty TX. Excluded OMS 903847 | November | 2012 | 2013Q2 | 2013 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | UG | Not Veg | 2012-11-25 | N | 515 | N | 23 | Y | Y | 1.1101 | 39.4971 | 376.3468
[7 empty] | 18167 | 16280 | 904809 | 2012-11-26 08:47 | 2012-11-26 08:53 | 6 | 11kV | 4782 | 797 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123113 1 fault operations 3 phase Overcurrent; Earth fault FDR 74118 TRIPPED WHILST SVT CABLE ON SI 26292A VIA ABS 43207. ABS OPENED AND FDR RESTORED | November | 2012 | 2013Q2 | 2013 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Veg | 2012-11-26 | N | 6 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3494.5446
[7 empty] | 17621 | 10332 | 903866 | 2012-11-25 23:06 | 2012-11-26 14:10 | 903.6 | 11kV | 46083.6 | 51 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 123112 B & C phase DOLF UG cable fault CC1: 22-"Refer to SOp" | November | 2012 | 2013Q2 | 2013 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | UG | Not Veg | 2012-11-25 | N | 903.6 | N | 23 | Y | Y | 1.1101 | 39.4971 | 33676.5356
[7 empty] | 17766 | 12046 | 904028 | 2012-11-26 11:53 | 2012-11-26 15:30 | 217 | 11kV | 21518 | 113 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Pnl 16 "S2035 Vernon Redmyre Etc" fdr pnl. At S2035 Vernon Redmyre C phase HV fuse SIBA 80 Amp failed (Possible fatigue) Remarks: Fuse Fatigue. Note in LV// at time of interruption. See seperate interruption for No 1 Dist @ Sub 6234 Related jobs: #905098, 904028 | November | 2012 | 2013Q2 | 2013 | ZN2835:PA16 | ZN2835:PA16 | ZN02835/000016 | STRATHFIELD | OH | Not Veg | 2012-11-26 | N | 190.4248 | N | 25 | Y | Y | 1.1101 | 39.4971 | 15724.7197
[7 empty] | 17082 | 4291 | 904137 | 2012-11-26 13:38 | 2012-11-26 15:31 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123121 Single phase DOLF : 10 Amp Excluded OMS 904137 | November | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-11-26 | N | 113 | N | 25 | Y | Y | 1.1101 | 39.4971 | 82.5771
[7 empty] | 18424 | 18860 | 904246 | 2012-11-26 15:17 | 2012-11-26 17:31 | 134 | 11kV | 30016 | 224 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123123 1 fault operation 3 phase Sensitive Earth Fault; Earth fault patrolled by a pople no cause found Excluded OMS 904246 | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-11-26 | N | 134 | N | 25 | Y | Y | 1.1101 | 39.4971 | 21934.8075
[7 empty] | 18019 | 14564 | 904277 | 2012-11-26 17:09 | 2012-11-26 19:10 | 121 | 11kV | 119415 | 1902 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S.15005 Belrose, Panel 2 Fdr CB tripped on B and C phase OC, 11kV trip. Tree branch on mains adjacent to PT.15449. Bond burnt off adjacent to link 22275 | November | 2012 | 2013Q2 | 2013 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Not Veg | 2012-11-26 | N | 62.7839 | N | 25 | Y | Y | 1.1101 | 39.4971 | 87264.9599
[7 empty] | 18245 | 17011 | 904281 | 2012-11-26 17:25 | 2012-11-26 19:50 | 145 | 11kV | 90697 | 953 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | At S2400 Berowra Panel 26 Tripped on Relays: A and B phase IOC and A and B phase Overcurrent EFI. Signals: 11kV Trip, Zone Earth, Group 2 Earth. Cause NOt found: Reports of large amounts of lightning in the area at the time of outage - Bond burnt off near PT. See OMS 904551 904555 904281 | November | 2012 | 2013Q2 | 2013 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Not Veg | 2012-11-26 | N | 95.17 | N | 25 | Y | Y | 1.1101 | 39.4971 | 66278.6925
[7 empty] | 18136 | 16007 | 904312 | 2012-11-26 18:26 | 2012-11-26 20:07 | 101 | 11kV | 9797 | 97 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123125 2 fault operations C phase Overcurrent cursory fdr patrol to ABS 74532. Full patrol required. No cause found Excluded oms 904312 | November | 2012 | 2013Q2 | 2013 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2012-11-26 | N | 101 | N | 25 | Y | Y | 1.1101 | 39.4971 | 7159.3586
[7 empty] | 16649 | 941 | 904344 | 2012-11-26 22:49 | 2012-11-26 23:05 | 16 | 11kV | 816 | 51 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 123185 3 phase interruption nil protection interupted for emergency repairs of x arm broken at sub 70128 Inglare Excluded oms 904344 ## | November | 2012 | 2013Q2 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2012-11-26 | N | 16 | N | 25 | Y | Y | 1.1101 | 39.4971 | 596.3087
[7 empty] | 17265 | 6746 | 904219 | 2012-11-26 18:28 | 2012-11-26 23:11 | 283 | 11kV | 50457 | 254 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Electrical Storm | N | LID 123184 3 fault operations 3 phase fault Sensitive Earth Fault; Earth fault Fault beyond ABS 27357 private OHM i Excluded OMS 904313 | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | Unknown | Not Veg | 2012-11-26 | N | 198.6496 | N | 25 | Y | Y | 1.1101 | 39.4971 | 36872.4874
[7 empty] | 18322 | 17706 | 904397 | 2012-11-26 21:20 | 2012-11-26 23:24 | 124 | 11kV | 1364 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123175 A phase DOLF : 10 Amp Excluded OMS 904397 | November | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-11-26 | N | 124 | N | 25 | Y | Y | 1.1101 | 39.4971 | 996.771
[7 empty] | 18486 | 19712 | 904369 | 2012-11-26 20:57 | 2012-11-26 23:34 | 157 | 11kV | 157 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123177 C Phase DOLF : 10 Amp note oms sub no incorrect (71027) Excluded oms 904369 | November | 2012 | 2013Q2 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2012-11-26 | N | 157 | N | 25 | Y | Y | 1.1101 | 39.4971 | 114.731
[7 empty] | 17688 | 11454 | 904356 | 2012-11-26 20:43 | 2012-11-26 23:42 | 179 | 11kV | 716 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123170 A & C phase DOLF : 5 Amp Excluded OMS 904356 & LID 123172 | November | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-11-26 | N | 179 | N | 25 | Y | Y | 1.1101 | 39.4971 | 523.2317
[7 empty] | 17056 | 4072 | 910998 | 2012-11-26 20:41 | 2012-11-27 00:25 | 224 | 11kV | 9849 | 483 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123178 A phase DOLF : 10 Amp Excluded OMS 904363 | November | 2012 | 2013Q2 | 2013 | 512:48048 | 526:34633 | ZN00526/034633 | CESSNOCK | UG | Not Veg | 2012-11-26 | N | 20.3913 | N | 25 | Y | Y | 1.1101 | 39.4971 | 7197.3587
[7 empty] | 18352 | 17889 | 904416 | 2012-11-26 21:46 | 2012-11-27 00:25 | 159.4333 | 11kV | 6855.6333 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123171 3 phase DOLF : 15 Amp | November | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-11-26 | N | 159.4333 | N | 25 | Y | Y | 1.1101 | 39.4971 | 5009.8946
[7 empty] | 18262 | 17148 | 904352 | 2012-11-26 20:39 | 2012-11-27 00:30 | 231 | 11kV | 231 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123180 A phase DOLF : 10 Amp Excluded OMS 904352 | November | 2012 | 2013Q2 | 2013 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | UG | Not Veg | 2012-11-26 | N | 231 | N | 25 | Y | Y | 1.1101 | 39.4971 | 168.808
[7 empty] | 18216 | 16734 | 904400 | 2012-11-26 21:10 | 2012-11-27 01:00 | 230 | 11kV | 173515 | 1169 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123168 2 fault operations 3 phase Overcurrent; Earth fault Lightning hit UGOH pole IR-70533. Crew replace L/A's. Excluded OMS 904435, 904400 | November | 2012 | 2013Q2 | 2013 | 238:34147 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Not Veg | 2012-11-26 | N | 148.4303 | N | 25 | Y | Y | 1.1101 | 39.4971 | 126799.6442
[7 empty] | 16514 | 90 | 910901 | 2012-11-26 20:05 | 2012-11-27 01:15 | 310 | 11kV | 310 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123182 Single phase Burnt up LV fuse assembly replaced Excluded oms 904341 & 910901 | November | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-11-26 | N | 310 | N | 25 | Y | Y | 1.1101 | 39.4971 | 226.5389
[7 empty] | 16682 | 1120 | 904297 | 2012-11-26 18:03 | 2012-11-27 03:00 | 537 | 11kV | 12351 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123187 B phase DOLF : 16 Amp Excluded OMS 904297, 904303 | November | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-11-26 | N | 537 | N | 25 | Y | Y | 1.1101 | 39.4971 | 9025.7465
[7 empty] | 16532 | 228 | 904359 | 2012-11-26 20:46 | 2012-11-27 03:55 | 429 | 11kV | 3003 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123183 A & B phase DOLF : 10 Amp tapping burnt off pole FP 50311 as well as blown fuses 48049 Excluded OMS 904359 | November | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-11-26 | N | 429 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2194.5038
[7 empty] | 16738 | 1509 | 904372 | 2012-11-26 21:26 | 2012-11-27 04:20 | 414 | 11kV | 4968 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123188 A & B phase DOLF : 10 Amp Excluded OMS 904372; 904404 | November | 2012 | 2013Q2 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-11-26 | N | 414 | N | 25 | Y | Y | 1.1101 | 39.4971 | 3630.4679
[7 empty] | 18547 | 20327 | 904798 | 2012-11-27 03:30 | 2012-11-27 04:30 | 60 | 11kV | 1260 | 21 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 123190 Isolated section to repair blown tappings at links 41287 see report 123189 | November | 2012 | 2013Q2 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2012-11-27 | N | 60 | N | 18 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 17126 | 4622 | 904425 | 2012-11-26 21:51 | 2012-11-27 04:30 | 399 | 11kV | 2793 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 123189 2 blown tappings at links 41287, also see report 123190 for another outage to isolate fdr to repair. Excluded oms 904460 | November | 2012 | 2013Q2 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2012-11-26 | N | 399 | N | 25 | Y | Y | 1.1101 | 39.4971 | 2041.042
[7 empty] | 17044 | 3989 | 904382 | 2012-11-26 21:10 | 2012-11-27 05:20 | 490 | 11kV | 8330 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123192 A & B phase DOLF : 20 Amp excluded OMS 904382, 904424 | November | 2012 | 2013Q2 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2012-11-26 | N | 490 | N | 25 | Y | Y | 1.1101 | 39.4971 | 6087.3183
[7 empty] | 17216 | 6081 | 904464 | 2012-11-27 04:10 | 2012-11-27 06:15 | 125 | 11kV | 213133 | 1877 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn35800 Bankstown - 11kv Panel No.14 "Sub 4168 & Sub 5773" feeder tripped. Relays: Earth Fault EFI. Signals: 11kv trip, No.12 Group Earth, Field EFI's: Sub 4168, Sub 5762 Remarks: UG fault. 11kv UG fault from AB 315 to AB 422 to Sw A @ Sub 7092 Stanley Leonard tee Sub 1278 Vimy St Related jobs: #904464, 904630, 904631, 904627 | November | 2012 | 2013Q2 | 2013 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-11-27 | N | 113.5498 | N | 18 | N | N | 1.1101 | 39.4971 | 155751.31
[7 empty] | 18461 | 19194 | 904390 | 2012-11-26 21:16 | 2012-11-27 06:45 | 569 | 11kV | 1707 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123193 Single phase DOLF : 10 Amp Excluded OMS 904390 | November | 2012 | 2013Q2 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | UG | Not Veg | 2012-11-26 | N | 569 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1247.4253
[7 empty] | 18422 | 18849 | 904484 | 2012-11-27 05:00 | 2012-11-27 07:35 | 155 | 11kV | 310 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123194 C phase DOLF : 10 Amp Excluded OMS 904484 | November | 2012 | 2013Q2 | 2013 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | UG | Not Veg | 2012-11-27 | N | 155 | N | 18 | N | N | 1.1101 | 39.4971 | 226.5389
[7 empty] | 16745 | 1550 | 904503 | 2012-11-27 06:33 | 2012-11-27 08:30 | 117 | 11kV | 351 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123197 B & C phase DOLF : 10 Amp Excluded OMS 9054503 | November | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | UG | Not Veg | 2012-11-27 | N | 117 | N | 18 | N | N | 1.1101 | 39.4971 | 256.5004
[7 empty] | 16702 | 1240 | 904473 | 2012-11-27 06:05 | 2012-11-27 08:31 | 146 | 11kV | 292 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123196 Single phase DOLF : 10 Amp Excluded OMS 904473 | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | UG | Not Veg | 2012-11-27 | N | 146 | N | 18 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 18150 | 16095 | 904500 | 2012-11-27 07:25 | 2012-11-27 09:35 | 130 | 11kV | 135174 | 1433 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.116 Leichhardt 11kv trip zone earth #2 group earth. Panel 34 the Balmain Derby fdr. Tripped on IOC EFI and fault check Remarks: Suspect cable fault between S4205 Campbell Perry and S1488 Mary Church Related jobs: #904534, 904506, 904505, 904500, 905161, 905159, 905163, 905152 | November | 2012 | 2013Q2 | 2013 | ZN116:PA34 | ZN116:PA12 | ZN00116/000012 | INNER WEST | UG | Not Veg | 2012-11-27 | N | 94.3294 | N | 18 | N | N | 1.1101 | 39.4971 | 98781.1722
[7 empty] | 18007 | 14256 | 905092 | 2012-11-26 20:38 | 2012-11-27 10:40 | 842 | 11kV | 6709 | 69 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123142 2 fault operations Trip & Lockout Blown Arrestor at Sub 54418 Roeth No. 2 sub. Sub replaced Prot Flags Required | November | 2012 | 2013Q2 | 2013 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2012-11-26 | N | 97.2319 | N | 25 | Y | Y | 1.1101 | 39.4971 | 4902.7393
[7 empty] | 17726 | 11785 | 905318 | 2012-11-27 10:40 | 2012-11-27 11:00 | 20 | 11kV | 20 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123205 3 phase Overcurrent DOP reports that the recloser is in extremely poor condition and needs to be assessed for replacement before it fails. The relay box is so rusted the relays can be seen from the ground, it is quite possible in heavy rain water is entering the control box. Please assess this recloser ASAP, the DOP thinks it will need to be replaced. | November | 2012 | 2013Q2 | 2013 |  |  |  | LAKE MACQUARIE | OH | Veg | 2012-11-27 | N | 20 | N | 18 | N | N | 1.1101 | 39.4971 | 14.6154
[7 empty] | 17156 | 5154 | 904498 | 2012-11-27 07:16 | 2012-11-27 11:45 | 269 | 11kV | 538 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123209 C phase DOLF : 40 Amp Excluded OMS 904498 | November | 2012 | 2013Q2 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | UG | Not Veg | 2012-11-27 | N | 269 | N | 18 | N | N | 1.1101 | 39.4971 | 393.1545
[7 empty] | 16577 | 514 | 904531 | 2012-11-27 08:23 | 2012-11-27 12:45 | 262 | 11kV | 786 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123215 B phase DOLF : 10 Amp Excluded OMS 904531 | November | 2012 | 2013Q2 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2012-11-27 | N | 262 | N | 18 | N | N | 1.1101 | 39.4971 | 574.3856
[7 empty] | 17693 | 11488 | 904512 | 2012-11-27 07:03 | 2012-11-27 13:20 | 377.25 | 11kV | 4506.1 | 16 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123210 DOLF : 10 Amp Lightning arrestors replaced under A/P. Excluded OMS 904512; 904723 | November | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-11-27 | N | 281.6313 | N | 18 | N | N | 1.1101 | 39.4971 | 3292.925
[7 empty] | 17944 | 13504 | 904699 | 2012-11-27 11:08 | 2012-11-27 14:05 | 177 | 11kV | 1239 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123218 C phase DOLF : 10 Amp SUB ISOLATED FOR REPAIR Excluded OMS No. 904699 | November | 2012 | 2013Q2 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2012-11-27 | N | 177 | N | 18 | N | N | 1.1101 | 39.4971 | 905.4247
[7 empty] | 16724 | 1374 | 904533 | 2012-11-27 12:00 | 2012-11-27 14:07 | 127 | 11kV | 127 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123217 C phase DOLF : 10 Amp AP ISSUED TO REPAIR BROKEN LIVE LINE LEAD TO DOLF Excluded OMS 904533 | November | 2012 | 2013Q2 | 2013 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | UG | Not Veg | 2012-11-27 | N | 127 | N | 18 | N | N | 1.1101 | 39.4971 | 92.8079
[7 empty] | 17351 | 7483 | 904460 | 2012-11-27 01:30 | 2012-11-27 14:45 | 795 | 11kV | 23300 | 48 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 123191 2 fault operations 3 span 11kv mains on ground . Oliver Sub 7579 Aph DOLF replaced. Back on at 1403hrs. Williams sub 51931 single phase DOLF replaced. Back on at 1445hrs. Excluded OMS 904460 & 905281 | November | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-11-27 | N | 485.4167 | N | 18 | N | N | 1.1101 | 39.4971 | 17026.9528
[7 empty] | 17025 | 3855 | 904826 | 2012-11-27 14:23 | 2012-11-27 15:18 | 55 | 11kV | 1789 | 34 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 1290 Leightonfield 11kv Fdr Pnl #10 "sub 1206 Christina Wood" Tripped on : B phase leakage EFI Field EFI's S1206 S5539 Remarks: Suspect UG cable failure. 11kv fdr failed from S5539 Woodville Rd to Sub 8425 Woodville Tangerine Related jobs: #904826, 905122, 905119 | November | 2012 | 2013Q2 | 2013 | ZN1290:PA10 | ZN1290:PA10 | ZN01290/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2012-11-27 | N | 52.6176 | N | 18 | N | N | 1.1101 | 39.4971 | 1307.3484
[7 empty] | 16558 | 367 | 904817 | 2012-11-27 14:18 | 2012-11-27 16:00 | 102 | 11kV | 9935.3333 | 98 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | At S.4265 the 11kV B phase OCIOM 40 amp 11kV fuse failed | November | 2012 | 2013Q2 | 2013 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | OH | Not Veg | 2012-11-27 | N | 101.381 | N | 18 | N | N | 1.1101 | 39.4971 | 7260.4486
[7 empty] | 18351 | 17888 | 913978 | 2012-11-26 21:02 | 2012-11-27 21:30 | 1468 | 11kV | 163162 | 1123 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123149 Earth wire into 11kV pole JR-72417 Raymond Terrace Rd Blown Lightning arrestors at sub 12449 Swan Reach Excluded OMS 904381; 904430; 904470, 905054, 905055, 905056, 905057, 905059, 905060, 905063, 905068, 905069, 904722. Also 910943, 910944, 910945, 910947, 910951, 910952, 910954, 910957, 910958, 910965, & 910968 | November | 2012 | 2013Q2 | 2013 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2012-11-26 | N | 145.2912 | N | 25 | Y | Y | 1.1101 | 39.4971 | 119233.9771
[7 empty] | 17782 | 12270 | 904929 | 2012-11-27 17:34 | 2012-11-27 21:45 | 251 | 11kV | 1004 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123230 B phase DOLF : 5 Amp Also Found Aph LVF (200A) blown at Crosbie sub 51461. Also OMS 904929 | November | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-11-27 | N | 251 | N | 18 | N | N | 1.1101 | 39.4971 | 733.6936
[7 empty] | 18470 | 19289 | 904968 | 2012-11-27 22:00 | 2012-11-27 23:50 | 110 | 11kV | 110 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 123236 No protection operation, Sub isolated to replace 11kV LA tracking to xarm. Excluded OMS 904968. | November | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-11-27 | N | 110 | N | 18 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 18188 | 16464 | 904973 | 2012-11-27 20:33 | 2012-11-28 01:10 | 277 | 11kV | 277 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123237 A Phase DOLF : 10 Amp readings as left 246V per phase. Excluded OMS 904973 | November | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2012-11-27 | N | 277 | N | 18 | N | N | 1.1101 | 39.4971 | 202.4234
[7 empty] | 17131 | 4636 | 905176 | 2012-11-28 09:21 | 2012-11-28 09:48 | 27 | 11kV | 9828 | 364 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Section of 11kV Panel 31 ex Zn Chatswood Reecloser CP530 Greville Tripped Cause: Lightning arrestor to PT1075 failed when energised from S5122 Kooba Kareela. Note DC's beyond S5122 were in LV parallel and were not interrupted. Abnormal switching:SWB closed at S5122 and SW B Open at S5128 See OMS 906200 905176 905187 | November | 2012 | 2013Q2 | 2013 | ZN80:PA31 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Not Veg | 2012-11-28 | N | 27 | N | 5 | N | N | 1.1101 | 39.4971 | 7182.0125
[7 empty] | 16515 | 91 | 905310 | 2012-11-28 11:41 | 2012-11-28 12:50 | 69.0833 | 11kV | 18307.0833 | 265 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser CP3280 Hunt Ave tripped reclosed tripped and locke dout on B and Cphase O/C Cause: Tree branch on 11 KV OH See OMS 905310 905343 | November | 2012 | 2013Q2 | 2013 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2012-11-28 | N | 69.0833 | N | 5 | N | N | 1.1101 | 39.4971 | 13378.2765
[7 empty] | 17661 | 10928 | 905507 | 2012-11-28 16:54 | 2012-11-28 20:08 | 194 | 11kV | 119378 | 683 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | LID 123255 4 fault operations, Earth fault Aust Meat Holdings sub beyond links 74336 has blown LAs - left Isolated - private sub. Message left on emergency contact No by A Regan. Excluded OMS# 905507 | November | 2012 | 2013Q2 | 2013 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | Unknown | Not Veg | 2012-11-28 | N | 174.7848 | N | 5 | N | N | 1.1101 | 39.4971 | 87237.9213
[7 empty] | 16749 | 1585 | 905545 | 2012-11-28 18:43 | 2012-11-28 21:52 | 189 | 11kV | 944.9833 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | At PT 12629 Goolara Nicklins - Footpath HDO 16a operated Lightning Strike | November | 2012 | 2013Q2 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2012-11-28 | N | 188.9967 | N | 5 | N | N | 1.1101 | 39.4971 | 690.5659
[7 empty] | 16608 | 711 | 905585 | 2012-11-29 06:03 | 2012-11-29 09:15 | 192 | 11kV | 4608 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123263 Single phase DOLF : | November | 2012 | 2013Q2 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2012-11-29 | N | 192 | N | 9 | N | N | 1.1101 | 39.4971 | 3367.3905
[7 empty] | 18164 | 16227 | 905564 | 2012-11-28 21:42 | 2012-11-29 11:45 | 843 | 11kV | 9198 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID123257 A Phase DOLF : 10 Amp Tree brought down 11kV main. Excluded OMS 905564, 905571 & 905805 | November | 2012 | 2013Q2 | 2013 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2012-11-28 | N | 353.7692 | N | 5 | N | N | 1.1101 | 39.4971 | 6721.6271
[7 empty] | 16708 | 1269 | 905595 | 2012-11-29 07:12 | 2012-11-29 11:50 | 278 | 11kV | 55600 | 200 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Transformer failed | November | 2012 | 2013Q2 | 2013 | ZN15006:PA1 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | UG | Not Veg | 2012-11-29 | N | 278 | N | 9 | N | N | 1.1101 | 39.4971 | 40630.8401
[7 empty] | 16888 | 2680 | 905705 | 2012-11-29 10:18 | 2012-11-29 13:00 | 162 | 11kV | 162 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123267 B phase DOLF : 10 Amp Excluded OMS 905705 | November | 2012 | 2013Q2 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2012-11-29 | N | 162 | N | 9 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 18350 | 17884 | 905773 | 2012-11-29 11:48 | 2012-11-29 13:27 | 98.6167 | 11kV | 1479.25 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 123265 Line inspector Pat Scully found a conductor with several damaged strands that had to be repaired immediately. No protection operated, isolation to allow repairs | November | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-11-29 | N | 98.6167 | N | 9 | N | N | 1.1101 | 39.4971 | 1080.9923
[7 empty] | 16612 | 736 | 905909 | 2012-11-29 15:46 | 2012-11-29 16:16 | 30 | 11kV | 12480 | 416 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123270 sw 50797 tripped on overload while suppling essential energy system via abs 27673 on SI L0650 | November | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-11-29 | N | 30 | N | 9 | N | N | 1.1101 | 39.4971 | 9120.0159
[7 empty] | 17275 | 6838 | 905920 | 2012-11-29 17:02 | 2012-11-29 19:50 | 168 | 11kV | 234375 | 2116 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.12660 Woy Woy Pnl.16 tripped on C phase timed OC Abnormal: AB41713 OPEN/Defective - Swb @ S48927 CLOSED Cause not ascertained - see 906716 906715 906177 906181 | November | 2012 | 2013Q2 | 2013 | ZN12660:PA14 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Veg | 2012-11-29 | N | 110.7632 | N | 9 | N | N | 1.1101 | 39.4971 | 171274.3371
[7 empty] | 16840 | 2270 | 905967 | 2012-11-29 18:46 | 2012-11-29 20:00 | 74 | 11kV | 55528 | 944 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S4545 Meadowbank Panel 17 Tripped and Locked out on No Cause Found - No protection relay operated howeverthe lack of reclose and operation of the lockout relay would suggest SEL. See OMS 906188 906191 905967 | November | 2012 | 2013Q2 | 2013 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Veg | 2012-11-29 | N | 58.822 | N | 9 | N | N | 1.1101 | 39.4971 | 40578.2246
[7 empty] | 18051 | 15346 | 905986 | 2012-11-29 21:01 | 2012-11-29 22:35 | 94 | 11kV | 5734 | 61 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11624 Yugari Empire Bay - 1 x Phase HDO operated Fuse fatigue GIS: 906192 906193 | November | 2012 | 2013Q2 | 2013 | ZN12660:PA14 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Not Veg | 2012-11-29 | N | 94 | N | 9 | N | N | 1.1101 | 39.4971 | 4190.2381
[7 empty] | 18348 | 17862 | 905993 | 2012-11-29 22:10 | 2012-11-29 22:54 | 44 | 11kV | 67364 | 1531 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | At Zn129 Hunters Hill 11kV OCB panel 3 Tripped on Relays: A phase O/C Timed, Fault Check and EFI. Signals: 11kV Trip No1 Tx Group Earth. Possum on 11kV UGOH O/S No4 Rocher Ave. Damaged pin insulator on Crossarm Above UGOH. See OMS908052 908056 908104 908101 905998 905996 905993 | November | 2012 | 2013Q2 | 2013 | ZN129:PA3 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Not Veg | 2012-11-29 | N | 44 | N | 9 | N | N | 1.1101 | 39.4971 | 49227.6243
[7 empty] | 18361 | 17991 | 906025 | 2012-11-30 08:28 | 2012-11-30 09:20 | 52 | 11kV | 52 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 123281 LV FUSE CARRIER DROPPED OUT IS LOOSE , OK SHORT TERM BUT NEEDS FIXING ASAP. NO PROTECTION OPERATED. Also refer OMS 906025 | November | 2012 | 2013Q2 | 2013 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2012-11-30 | N | 52 | N | 8 | N | N | 1.1101 | 39.4971 | 38.0001
[7 empty] | 18211 | 16711 | 907315 | 2012-11-30 13:30 | 2012-11-30 13:40 | 10 | 11kV | 420 | 42 | HV | Staff Other | Utility Process Issue | O/H Link | Unplanned | Unselected | N | Autolink 46841 operated - ex Pnl.5 Peats Ridge Zone Failed after ineefective repair D/R #305221 - see Planned OMS job 907266 | November | 2012 | 2013Q2 | 2013 | ZN12630:PA5 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2012-11-30 | N | 10 | N | 8 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 17072 | 4217 | 906227 | 2012-11-30 13:24 | 2012-11-30 15:50 | 146 | 11kV | 36028 | 260 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15013 Terrey Hills, Panel 1 Fdr CB tripped on earth fault, fault check, efi, 11kV trip, zone earth. Field efi down at S.16790. 11kV UG cable fault from S.16790 to S.16638 | November | 2012 | 2013Q2 | 2013 | ZN15013:PA1 | ZN15013:PA1 | ZN15013/000001 | NORTHERN BEACHES | UG | Not Veg | 2012-11-30 | N | 138.5692 | N | 8 | N | N | 1.1101 | 39.4971 | 26328.1998
[7 empty] | 17272 | 6808 | 906228 | 2012-11-30 15:44 | 2012-11-30 16:26 | 42 | 11kV | 50274 | 1197 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.40 tripped / reclosed and locked out on A & B inst and OC. Tree branch on empire bay drive near Cochrone St. see 907319 907326 (GIS) | November | 2012 | 2013Q2 | 2013 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2012-11-30 | N | 42 | N | 8 | N | N | 1.1101 | 39.4971 | 36738.7564
[7 empty] | 17794 | 12355 | 906385 | 2012-11-30 18:33 | 2012-11-30 19:55 | 82.0333 | 11kV | 6152.5 | 75 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123295 2 Faualt operations, Earth Fault, Tripped when DOLFS put in at sut 54144 (refer LID 123308, OMS 906375) | November | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2012-11-30 | N | 82.0333 | N | 8 | N | N | 1.1101 | 39.4971 | 4496.0655
[7 empty] | 17482 | 8624 | 906395 | 2012-11-30 21:20 | 2012-11-30 22:43 | 83 | 11kV | 59562 | 743 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | The roadside bond at AB.2229 burnt off, causing low volts. At 2120 hours the Panel 11 Fdr CB tripped on SEL, 11kV trip, zone earth, #1 group earth. | November | 2012 | 2013Q2 | 2013 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Not Veg | 2012-11-30 | N | 80.1642 | N | 8 | N | N | 1.1101 | 39.4971 | 43526.1528
[7 empty] | 17716 | 11683 | 906440 | 2012-11-30 21:15 | 2012-12-01 00:05 | 170 | 11kV | 850 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123315 Fuse: 40Amp Line DOLF, also refer related record 906440 | November | 2012 | 2013Q2 | 2013 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2012-11-30 | N | 170 | N | 8 | N | N | 1.1101 | 39.4971 | 621.1549
[7 empty] | 17197 | 5875 | 911032 | 2012-11-30 20:41 | 2012-12-01 04:10 | 449 | 11kV | 10776 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123318 B & C phase DOLF : 40Amp Excluded OMS 906426 | November | 2012 | 2013Q2 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2012-11-30 | N | 449 | N | 8 | N | N | 1.1101 | 39.4971 | 7874.783
[7 empty] | 16786 | 1956 | 906477 | 2012-12-01 02:28 | 2012-12-01 08:10 | 342 | 11kV | 684 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 123319 Single phase DOLF : 10 Amp Dead Cockatoo at base of sub pole. 2 x 10A Dolfs blown Excluded OMS # 906477 | December | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2012-12-01 | N | 342 | N | 17 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 17409 | 8035 | 906528 | 2012-12-01 09:21 | 2012-12-01 10:55 | 93.6667 | 11kV | 4027.6667 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 123320 Stranded Mains Adjacent Pole FN-60074 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-12-01 | N | 93.6667 | N | 17 | N | N | 1.1101 | 39.4971 | 2943.3
[7 empty] | 17173 | 5316 | 906472 | 2012-12-01 00:24 | 2012-12-01 11:20 | 656 | 11kV | 1312 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123324 Single phase DOLF : 10 Amp Excluded OMS 906472 | December | 2012 | 2013Q2 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | UG | Not Veg | 2012-12-01 | N | 656 | N | 17 | N | N | 1.1101 | 39.4971 | 958.7709
[7 empty] | 16545 | 297 | 906482 | 2012-12-01 05:52 | 2012-12-01 12:15 | 383.2333 | 11kV | 1103.2333 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Pnl 13 Kurnell - AB35004 interrupted at 0915 hrs for safety reasons PT 9064 require LV fuse assembly and Tx tails replaced | December | 2012 | 2013Q2 | 2013 | ZN9301:PA13 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2012-12-01 | N | 220.6467 | N | 17 | N | N | 1.1101 | 39.4971 | 806.2104
[7 empty] | 17303 | 7126 | 906561 | 2012-12-01 11:21 | 2012-12-01 12:55 | 94 | 11kV | 94 | 1 | HV | Animal Frog | Animal | DC Not Transformer | Unplanned | Previous Storm | N | LID 123326 Single phase DOLF : 10 Amp Frog Excluded OMS 906561 | December | 2012 | 2013Q2 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-12-01 | N | 94 | N | 17 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 18489 | 19817 | 906619 | 2012-12-01 15:33 | 2012-12-01 16:38 | 65 | 11kV | 69640 | 2085 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10995 Riverwood - Pnl 1 - Tripped, reclosed and locked out on A phase IOC, EF, LO, Timer, EFI 11kV UGOH to S 10792 Baumans HIghland failed explosively. LV// links for S 10792: 564, 2775, 2774, 67, 2773. see 908772 908759(GIS) 908774 | December | 2012 | 2013Q2 | 2013 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | Unknown | Unknown | 2012-12-01 | N | 33.4005 | N | 17 | N | N | 1.1101 | 39.4971 | 50890.858
[7 empty] | 18275 | 17246 | 906629 | 2012-12-01 16:29 | 2012-12-01 17:35 | 66 | 11kV | 18546 | 281 | HV | Animal Bird | Animal | Recloser / Sectionaliser | Unplanned | Unselected | N | S 10996 Rockdale - Pnl 20 "Bruce West Botany" C Phase IOC, Timed and LO Magpie located and removed from USL 30760 | December | 2012 | 2013Q2 | 2013 | ZN10996:PA20 | ZN10998:PA24 | ZN10998/000024 | BAYSIDE | OH | Not Veg | 2012-12-01 | N | 66 | N | 17 | N | N | 1.1101 | 39.4971 | 13552.8698
[7 empty] | 17724 | 11761 | 906685 | 2012-12-01 19:13 | 2012-12-01 22:15 | 182 | 11kV | 7819.7 | 43 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S4425 Orana Mona Vale 400A fuse blown on A B and C phase of distributor 1. Cause: UG cable fault in UGOH A and C phase fault. See OMS 906685 906684 | December | 2012 | 2013Q2 | 2013 | ZN195:PA11 | ZN195:PA11 | ZN00195/000011 | KU-RING-GAI | UG | Not Veg | 2012-12-01 | N | 181.8535 | N | 17 | N | N | 1.1101 | 39.4971 | 5714.4061
[7 empty] | 16632 | 852 | 908811 | 2012-12-01 21:07 | 2012-12-01 23:24 | 137 | 11kV | 13015 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123339 2 Fault operations Earth fault | December | 2012 | 2013Q2 | 2013 | 231:8405 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2012-12-01 | N | 137 | N | 17 | N | N | 1.1101 | 39.4971 | 9510.9781
[7 empty] | 16841 | 2294 | 906668 | 2012-12-01 18:27 | 2012-12-01 23:50 | 323 | 11kV | 1615 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123348 C phase DOLF : 20 Amp Excluded OMS 906668 | December | 2012 | 2013Q2 | 2013 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2012-12-01 | N | 323 | N | 17 | N | N | 1.1101 | 39.4971 | 1180.1944
[7 empty] | 18183 | 16439 | 906717 | 2012-12-01 21:04 | 2012-12-01 23:50 | 166.1833 | 11kV | 1163.2833 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123345 3 phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-12-01 | N | 166.1833 | N | 17 | N | N | 1.1101 | 39.4971 | 850.0931
[7 empty] | 17926 | 13383 | 906769 | 2012-12-01 23:45 | 2012-12-02 01:35 | 110 | 11kV | 6370 | 65 | HV | Overload LV Parallel | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | At S35707 Tiree Woolwich 400A fuse blown on A and B phase of distributor 3. At S 2294 Weil Park 400A fuse blown on A and Cphase of distributor 1. Cause: Above distributors were LV parallel and Parallel failed. See OMS 906771 907177 706769 CC1: 22-"Refer to SOp" | December | 2012 | 2013Q2 | 2013 | ZN129:PA4 | ZN129:PA34 | ZN00129/000034 | HUNTERS HILL | OH | Not Veg | 2012-12-01 | N | 98 | N | 17 | N | N | 1.1101 | 39.4971 | 4655.0081
[7 empty] | 16876 | 2515 | 906765 | 2012-12-01 23:26 | 2012-12-02 02:30 | 184 | 11kV | 184 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123354 C Phase DOLF : 10 Amp Excluded OMS 906765 | December | 2012 | 2013Q2 | 2013 | 510:48164 | 508:82576 | ZN00508/082576 | PORT STEPHENS | UG | Not Veg | 2012-12-01 | N | 184 | N | 17 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 17854 | 12740 | 906725 | 2012-12-01 21:24 | 2012-12-02 03:45 | 381 | 11kV | 2667 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123358 A phase DOLF 10 Amp Excluded OMS 906725 | December | 2012 | 2013Q2 | 2013 | 238:34141 | 264:81240 | ZN00264/081240 | PORT STEPHENS | UG | Not Veg | 2012-12-01 | N | 381 | N | 17 | N | N | 1.1101 | 39.4971 | 1948.9649
[7 empty] | 16818 | 2155 | 909082 | 2012-12-02 02:20 | 2012-12-02 06:20 | 240 | 11kV | 12960 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123352 1 fault operation | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-12-02 | N | 240 | N | 22 | Y | Y | 1.1101 | 39.4971 | 9470.7857
[7 empty] | 18161 | 16156 | 906850 | 2012-12-02 08:41 | 2012-12-02 09:06 | 25 | 11kV | 16138 | 967 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.8 tripped and locked out on A & B phase IOC, EFI @PT11511 - ABC phase fuses blown Abnormal: SwB @ S18204 CLOSED - AB42968 OPEN Kookaburra found dead at base of PT11511. - Note: Protection on Pnl.8 was Non-auto at time due to swtiching. see also 907352 | December | 2012 | 2013Q2 | 2013 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Not Veg | 2012-12-02 | N | 16.6887 | N | 22 | Y | Y | 1.1101 | 39.4971 | 11793.1744
[7 empty] | 18518 | 20019 | 906812 | 2012-12-02 06:25 | 2012-12-02 09:20 | 175 | 11kV | 4200 | 24 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1568 Galston Guides Roadside 31.5A fuse operated Cause: Fuse fatigue See OMS 907200 907197 906812/831/837/843/862 | December | 2012 | 2013Q2 | 2013 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2012-12-02 | N | 175 | N | 22 | Y | Y | 1.1101 | 39.4971 | 3069.2361
[7 empty] | 17406 | 8017 | 909186 | 2012-12-02 06:47 | 2012-12-02 09:30 | 163 | 11kV | 489 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123367 A & B Phase DOLF : 20 Amp. Found when investigating oms job 906816 (LID unplanned Report 123368 & 123369 ) | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-12-02 | N | 163 | N | 22 | Y | Y | 1.1101 | 39.4971 | 357.3468
[7 empty] | 17209 | 6003 | 906727 | 2012-12-01 21:30 | 2012-12-02 09:50 | 740 | 11kV | 618668 | 1526 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123343 2 fault operations Earth Fault; Overcurrent Excluded oms # 906733, 906735, 906738 etc. B & C phase O/C & E/F | December | 2012 | 2013Q2 | 2013 | 232:33411 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2012-12-01 | N | 405.4181 | N | 17 | N | N | 1.1101 | 39.4971 | 452104.3268
[7 empty] | 17008 | 3641 | 909176 | 2012-12-02 05:30 | 2012-12-02 09:55 | 265 | 11kV | 2120 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123366 B & C phase DOLF : 16 Amp | December | 2012 | 2013Q2 | 2013 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2012-12-02 | N | 265 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1549.2335
[7 empty] | 18070 | 15510 | 906839 | 2012-12-02 07:00 | 2012-12-02 10:10 | 190 | 11kV | 190 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123362 B phase DOLF : 10 Amp Excluded OMS 906839 | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-12-02 | N | 190 | N | 22 | Y | Y | 1.1101 | 39.4971 | 138.8464
[7 empty] | 17232 | 6294 | 906816 | 2012-12-02 06:47 | 2012-12-02 10:30 | 223 | 11kV | 223 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 123368 Single phase DOLF LA blown at sub. LF 27901 operated. See LID Unplanned report # 123367/OMS 909190 | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-12-02 | N | 223 | N | 22 | Y | Y | 1.1101 | 39.4971 | 162.9618
[7 empty] | 18092 | 15721 | 906804 | 2012-12-02 06:01 | 2012-12-02 11:30 | 329 | 11kV | 1645 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123364 B phase DOLF : 10 Amp Tx volts 246V | December | 2012 | 2013Q2 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2012-12-02 | N | 329 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1202.1175
[7 empty] | 18120 | 15907 | 906858 | 2012-12-02 08:55 | 2012-12-02 11:30 | 155 | 11kV | 155 | 1 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123365 A phase DOLF : 16 Amp Dead bird found at sub. Excluded OMS 906858 | December | 2012 | 2013Q2 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2012-12-02 | N | 155 | N | 22 | Y | Y | 1.1101 | 39.4971 | 113.2694
[7 empty] | 17154 | 5070 | 906773 | 2012-12-02 00:14 | 2012-12-02 11:35 | 681 | 11kV | 244154 | 1603 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At s.15002 Narrabeen, Panel 6 Fdr CB tripped on earth leakage, earth fault check , efi, #2 Tx fault check, 11kV trip, zone earth. Field efi's operated at S.16441, S.16903 S.16839. OH down into LV due to salt air causing fatigue of light csa conductors between LB.23230 & USL.22436 | December | 2012 | 2013Q2 | 2013 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2012-12-02 | N | 152.3107 | N | 22 | Y | Y | 1.1101 | 39.4971 | 178420.5419
[7 empty] | 17468 | 8496 | 906722 | 2012-12-01 21:03 | 2012-12-02 12:15 | 912 | 11kV | 268349 | 855 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123338 3 fault operations Earth fault; Overcurrent Feeder in abnormal state prior to fault | December | 2012 | 2013Q2 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2012-12-01 | N | 313.8585 | N | 17 | N | N | 1.1101 | 39.4971 | 196101.5342
[7 empty] | 18254 | 17094 | 906905 | 2012-12-02 12:21 | 2012-12-02 13:10 | 49 | 11kV | 147 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123373 B & C phase : 10 Amp TX Volts: Aph - 245V, Bph - 244V, Cph - 245V Tx Load: Aph - 4A, Bph - 1A, Cph 2A Excluded OMS No. 906905 | December | 2012 | 2013Q2 | 2013 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2012-12-02 | N | 49 | N | 22 | Y | Y | 1.1101 | 39.4971 | 107.4233
[7 empty] | 18326 | 17722 | 906819 | 2012-12-02 07:06 | 2012-12-02 13:30 | 384 | 11kV | 1152 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 123375 C phase DOLF : 10 Amp Tx Volts: Aph - 244V, Bph - 246V, Cph - 245V Tx Load: Aph - 9A, Bph - 1A, Cph - 1A Excluded OMS No. 906819 | December | 2012 | 2013Q2 | 2013 | 503:48011 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2012-12-02 | N | 384 | N | 22 | Y | Y | 1.1101 | 39.4971 | 841.8476
[7 empty] | 17307 | 7136 | 911059 | 2012-12-01 20:30 | 2012-12-02 13:35 | 1025 | 11kV | 19350 | 1870 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123347 A & B phase DOLF : 31 Amp | December | 2012 | 2013Q2 | 2013 | 503:48011 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2012-12-01 | N | 10.3476 | N | 17 | N | N | 1.1101 | 39.4971 | 14140.4093
[7 empty] | 16711 | 1277 | 906870 | 2012-12-02 12:00 | 2012-12-02 13:40 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123376 A phase DOLF : 10 Amp Excluded OMS 906870 | December | 2012 | 2013Q2 | 2013 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | UG | Not Veg | 2012-12-02 | N | 100 | N | 22 | Y | Y | 1.1101 | 39.4971 | 73.0771
[7 empty] | 18313 | 17560 | 906918 | 2012-12-02 13:46 | 2012-12-02 14:39 | 53 | 11kV | 12296 | 232 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 874 Concord Feeder Panel No.4 "O'Donnell Griffin" feeder tripped on Earth fault with EFI Zone Earth, No.4 Group, 11kv trip Field EFI's operated @ Subs 7014 & 4369 Remarks: UG cable fault between S4369 Leeds Blaxland to S8890 Walker Meredith Related jobs: #907867, 906918 | December | 2012 | 2013Q2 | 2013 | ZN874:PA4 | ZN874:PA25 | ZN00874/000025 | CANADA BAY | UG | Not Veg | 2012-12-02 | N | 53 | N | 22 | Y | Y | 1.1101 | 39.4971 | 8985.5541
[7 empty] | 17961 | 13753 | 909160 | 2012-12-02 02:56 | 2012-12-02 15:34 | 758 | 11kV | 25014 | 33 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123356 3 fault operations | December | 2012 | 2013Q2 | 2013 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2012-12-02 | N | 758 | N | 22 | Y | Y | 1.1101 | 39.4971 | 18279.4934
[7 empty] | 16967 | 3346 | 906917 | 2012-12-02 10:00 | 2012-12-02 16:35 | 395 | 11kV | 790 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123377 Single phase DOLF : 5 Amp | December | 2012 | 2013Q2 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2012-12-02 | N | 395 | N | 22 | Y | Y | 1.1101 | 39.4971 | 577.3087
[7 empty] | 16998 | 3542 | 909077 | 2012-12-02 02:13 | 2012-12-02 16:44 | 871 | 11kV | 41808 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123351 1 fault operation | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-12-02 | N | 871 | N | 22 | Y | Y | 1.1101 | 39.4971 | 30552.0533
[7 empty] | 18389 | 18282 | 906792 | 2012-12-02 04:58 | 2012-12-02 18:00 | 781.8167 | 11kV | 32836.3 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123378 A & C phase DOLF : 15 Amp CC1: 06-"Urgent - O.H Mains - No others" | December | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2012-12-02 | N | 781.8167 | N | 22 | Y | Y | 1.1101 | 39.4971 | 23995.7995
[7 empty] | 17544 | 9120 | 906969 | 2012-12-02 18:24 | 2012-12-02 20:20 | 116 | 11kV | 116 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123381 Single phase DOLF : 10 Amp Excluded OMS 906969 | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-12-02 | N | 116 | N | 22 | Y | Y | 1.1101 | 39.4971 | 84.7694
[7 empty] | 17740 | 11868 | 906973 | 2012-12-02 20:08 | 2012-12-02 22:00 | 111.7 | 11kV | 2569.1 | 23 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 123382 3 phase DOLF : 16 Amp SECTION ISOLATED TO REPAIR X-ARM POLE AI-40021 | December | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2012-12-02 | N | 111.7 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1877.4225
[7 empty] | 16833 | 2221 | 906993 | 2012-12-02 21:11 | 2012-12-02 22:20 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123384 A phase DOLF : 10 Amp Excluded OMS 906993 | December | 2012 | 2013Q2 | 2013 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | UG | Not Veg | 2012-12-02 | N | 69 | N | 22 | Y | Y | 1.1101 | 39.4971 | 50.4232
[7 empty] | 17365 | 7606 | 906997 | 2012-12-02 21:38 | 2012-12-02 23:59 | 141.1167 | 11kV | 141.1167 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123385 3 phase DOLF : 10 Amp Excluded OMS 907009 | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-12-02 | N | 141.1167 | N | 22 | Y | Y | 1.1101 | 39.4971 | 103.1239
[7 empty] | 17104 | 4458 | 907111 | 2012-12-03 09:25 | 2012-12-03 10:55 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123393 A & C phase DOLF :10 Amp Excluded OMS 907111 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-03 | N | 90 | N | 10 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 16623 | 791 | 907108 | 2012-12-03 09:23 | 2012-12-03 11:10 | 107 | 11kV | 214 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123394 A phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-03 | N | 107 | N | 10 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 16507 | 48 | 907083 | 2012-12-03 08:56 | 2012-12-03 11:20 | 144 | 11kV | 288 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123390 C phase DOLF : 10 Amp. Excluded OMS 907083 | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2012-12-03 | N | 144 | N | 10 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 16591 | 574 | 907136 | 2012-12-03 09:54 | 2012-12-03 12:10 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123396 A & C phase DOLF : 3 Amp Excluded OMS 907136 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-03 | N | 136 | N | 10 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 18441 | 19032 | 907121 | 2012-12-03 09:30 | 2012-12-03 13:10 | 220 | 11kV | 220 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123399 A & C phase DOLF : 10 Amp changed both surge arrestors. Excluded OMS 907121 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-12-03 | N | 220 | N | 10 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 17904 | 13164 | 907285 | 2012-12-03 12:11 | 2012-12-03 13:22 | 71 | 11kV | 1617 | 23 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2466 Flemington: 11kv feeder panel No 6 "Aquatic Temp" tripped on: Relays: E/L, EFI, Fault check Field EFIs: S7661 Remarks: 11kv UG cable fault from SWB @ S7661 Aquatic Temp to SW A @ S35226 Olympic Herb Elliot to SW A @ S6327 Olympic Hotel. Related jobs: #907285, 907930, 907929 | December | 2012 | 2013Q2 | 2013 | ZN2466:PA6 | ZN36000:PA8 | ZN36000/000008 | PARRAMATTA | UG | Not Veg | 2012-12-03 | N | 70.3043 | N | 10 | N | N | 1.1101 | 39.4971 | 1181.6559
[7 empty] | 16948 | 3246 | 907283 | 2012-12-03 11:30 | 2012-12-03 13:45 | 135 | 11kV | 405 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123401 C phase DOLF : 10 Amp Excluded OMS 907283 | December | 2012 | 2013Q2 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2012-12-03 | N | 135 | N | 10 | N | N | 1.1101 | 39.4971 | 295.9621
[7 empty] | 17957 | 13714 | 907299 | 2012-12-03 12:38 | 2012-12-03 14:05 | 87 | 11kV | 174 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123402 Single phase DOLF : 10 Amp Excluded OMS 907299 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-03 | N | 87 | N | 10 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 16844 | 2310 | 907446 | 2012-12-03 15:32 | 2012-12-03 16:54 | 82 | 11kV | 116838 | 1475 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12650 West gosford ex pnl.1 -REC 44936 Bently Rd tripped on SEL Trip Tree branch on OH mians. Individual @ 45 Alan St claimed fire brigade removed branch see 907793 907797 907798 | December | 2012 | 2013Q2 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2012-12-03 | N | 79.2122 | N | 10 | N | N | 1.1101 | 39.4971 | 85381.7643
[7 empty] | 17546 | 9143 | 907096 | 2012-12-03 14:50 | 2012-12-03 16:55 | 125 | 11kV | 8381 | 115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123405 C phase DOLF : 10 Amp Sub 51952 C ph LA, 10A DOLF & 100A LVF replaced. Xarm replaced pole FO-20154. Excluded OMS#s 907096 & 907333. | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-12-03 | N | 72.8783 | N | 10 | N | N | 1.1101 | 39.4971 | 6124.5876
[7 empty] | 17909 | 13182 | 907761 | 2012-12-04 00:06 | 2012-12-04 01:43 | 97 | 11kV | 19455 | 255 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn8100 GreenSquare Pa10 fdr tripped on B & C phase, Overcurrent EFI EFI: S47604 S3499 S3419 Cause: UG Fault Remarks: UG Fault in fdr between S3419 SwA to S999 SwE to S7398 SwB See 907844,50,1 GIS 907856 Exclude 907761,2 | December | 2012 | 2013Q2 | 2013 | ZN8100:PA10 | ZN8100:PA10 | ZN08100/000010 | SYDNEY | UG | Not Veg | 2012-12-04 | N | 76.2941 | N | 7 | N | N | 1.1101 | 39.4971 | 14217.1402
[7 empty] | 18087 | 15663 | 907786 | 2012-12-04 08:04 | 2012-12-04 09:30 | 85.9667 | 11kV | 154.9667 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123415 A phase DOLF : 10 Amp also blew sub fuse 70145 A ph 10 A Excluded #907786 | December | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-12-04 | N | 38.7417 | N | 7 | N | N | 1.1101 | 39.4971 | 113.2451
[7 empty] | 18280 | 17282 | 907781 | 2012-12-04 07:40 | 2012-12-04 10:17 | 157 | 11kV | 198064 | 1801 | HV | Vegetation Blow/Fall In | Vegetation | Circuit Breaker | Unplanned | Unselected | N | ZN 9252 Jannali - Pnl 12 - O/C B phase, L/O, Timed, EFI. (solenoid fuse blown) ZN 9252 Jannali - Pnl 7 out under access permit, ABS 35085 closed for switching. Tree branches touching O/H mains in rail corridor near ABS 35830 and ABS 35914 tee to S 49508 Cremona Rd. Bob Bedford advised Oatley Mains. | December | 2012 | 2013Q2 | 2013 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2012-12-04 | N | 109.9745 | N | 7 | N | N | 1.1101 | 39.4971 | 144739.3293
[7 empty] | 16571 | 486 | 907868 | 2012-12-04 09:45 | 2012-12-04 10:50 | 65 | 11kV | 65 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123416 A phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-04 | N | 65 | N | 7 | N | N | 1.1101 | 39.4971 | 47.5001
[7 empty] | 18507 | 19953 | 907789 | 2012-12-04 08:17 | 2012-12-04 11:02 | 165 | 11kV | 317.7333 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123417 A phase DOLF : 10 Amp Excluded OMS 907789 | December | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2012-12-04 | N | 158.8667 | N | 7 | N | N | 1.1101 | 39.4971 | 232.1901
[7 empty] | 18177 | 16378 | 907821 | 2012-12-04 13:10 | 2012-12-04 14:35 | 85 | 11kV | 85 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 123420 A & C phase DOLF : 10 Amp 2 LA's replaced Excluded OMS 907821 | December | 2012 | 2013Q2 | 2013 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2012-12-04 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 17526 | 8990 | 908055 | 2012-12-04 11:14 | 2012-12-04 16:00 | 286.1667 | 11kV | 21139.95 | 83 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 123421 C phase DOLF : 20 Amp | December | 2012 | 2013Q2 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2012-12-04 | N | 254.6982 | N | 7 | N | N | 1.1101 | 39.4971 | 15448.4519
[7 empty] | 16624 | 792 | 908225 | 2012-12-05 06:29 | 2012-12-05 08:15 | 106 | 11kV | 106 | 1 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 123431 A phase DOLF : 10 Amp possum in mains | December | 2012 | 2013Q2 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2012-12-05 | N | 106 | N | 7 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 17428 | 8161 | 908288 | 2012-12-05 09:19 | 2012-12-05 10:33 | 73.5333 | 11kV | 6838.6 | 93 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Link | Unplanned | Unselected | N | LID 123438 Incoming link on 42002 damaged bridged out Cph incoming link burnt out. recloser bypassed. | December | 2012 | 2013Q2 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2012-12-05 | N | 73.5333 | N | 7 | N | N | 1.1101 | 39.4971 | 4997.4472
[7 empty] | 16671 | 1070 | 908256 | 2012-12-05 08:37 | 2012-12-05 12:03 | 206.35 | 11kV | 324.35 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123436 A & C phase DOLF : 3 Amp Excluded OMS 908256 | December | 2012 | 2013Q2 | 2013 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | UG | Not Veg | 2012-12-05 | N | 162.175 | N | 7 | N | N | 1.1101 | 39.4971 | 237.0254
[7 empty] | 17831 | 12555 | 908462 | 2012-12-05 12:45 | 2012-12-05 13:00 | 15 | 11kV | 1035 | 69 | HV | Vegetation Blow/Fall In | Vegetation | DC Not Transformer | Unplanned | Wind | N | LID 123443 A phase LV dist fuse Volts = 247. Amps = 48, 22, 36. Excluded OMS # 908462 | December | 2012 | 2013Q2 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2012-12-05 | N | 15 | N | 7 | N | N | 1.1101 | 39.4971 | 756.3475
[7 empty] | 17348 | 7456 | 908489 | 2012-12-05 13:13 | 2012-12-05 14:49 | 96 | 11kV | 138396 | 1464 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn188 Zetland 11kv Pa14 fdr tripped on Earth ault with fault check Signals: 11kv trip, Group 3 Earth, Zone Earth and EFI EFI: S2937 Abnormal: Open S7457SwB, Close S7871SwA, Close S7325SwD. Open S7454SwA, access permit from S7454 to S5644. Remarks: UG Cable fault between S2937 and S4250. See 908747,51 Exclude 908489,90 | December | 2012 | 2013Q2 | 2013 | ZN188:PA32 | ZN8100:PA30 | ZN08100/000030 | SYDNEY | UG | Not Veg | 2012-12-05 | N | 94.5328 | N | 7 | N | N | 1.1101 | 39.4971 | 101135.7148
[7 empty] | 16547 | 303 | 908512 | 2012-12-05 14:45 | 2012-12-05 16:15 | 90 | 11kV | 900 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123447 A phase HV dropper to DOLF broken. Excluded OMS# 908512 | December | 2012 | 2013Q2 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2012-12-05 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 16949 | 3254 | 908579 | 2012-12-05 15:03 | 2012-12-05 18:10 | 187 | 11kV | 1309 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11271 Fern Tree Pamldale 0.4 - Centre phase HDO blown 16A Fuse fatigue | December | 2012 | 2013Q2 | 2013 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2012-12-05 | N | 187 | N | 7 | N | N | 1.1101 | 39.4971 | 956.5786
[7 empty] | 18026 | 14665 | 908719 | 2012-12-06 07:55 | 2012-12-06 09:20 | 85 | 11kV | 255 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 123452 A phase sub isolated to replace 3 x la Excluded oms 908719 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2012-12-06 | N | 85 | N | 4 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 18378 | 18182 | 908947 | 2012-12-06 13:38 | 2012-12-06 14:30 | 52 | 11kV | 156 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123468 A phase DOLF : 16 Amp FUSE FATIGUE.VOLTS =249 Excluded OMS REPORT NO 908947. | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2012-12-06 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 17913 | 13243 | 909123 | 2012-12-06 11:00 | 2012-12-06 20:02 | 542 | 11kV | 2710 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Section of Wyong Pnl.14R from LK 42294 interrupted for safety. Emergency work on 957 FDR which is hanging low over the F4 freeway after an insulator broke. Is on same pole as 957 FDR. | December | 2012 | 2013Q2 | 2013 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Not Veg | 2012-12-06 | N | 542 | N | 4 | N | N | 1.1101 | 39.4971 | 1980.3881
[7 empty] | 17240 | 6401 | 909147 | 2012-12-07 01:13 | 2012-12-07 02:33 | 80 | 11kV | 80 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123472 Vandals set fire to Kiosk sub 55649. Excluded OMS 909147 | December | 2012 | 2013Q2 | 2013 |  |  |  | CESSNOCK | OH | Not Veg | 2012-12-07 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 17487 | 8667 | 909137 | 2012-12-06 20:50 | 2012-12-07 02:34 | 344 | 11kV | 6180 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 123471 2 fault operations Twisted OHM near sub 70419. Excluded OMS REPORT NO 909137 & 909144.. | December | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-12-06 | N | 206 | N | 4 | N | N | 1.1101 | 39.4971 | 4516.1617
[7 empty] | 18022 | 14586 | 909228 | 2012-12-07 09:32 | 2012-12-07 10:25 | 52.6 | 11kV | 1262.4 | 24 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123480 Fdr de-energised to remove tree near sub 44045 | December | 2012 | 2013Q2 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2012-12-07 | N | 52.6 | N | 5 | N | N | 1.1101 | 39.4971 | 922.5247
[7 empty] | 17080 | 4272 | 909212 | 2012-12-07 09:03 | 2012-12-07 13:15 | 252 | 11kV | 76401 | 1936 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.10 tripped on Earth Fault Private contractor hit cable while horizontal drilling cnr Donnison St West & Batley Sts. Also UG feeder fault between S14925 to CP1665 to S11037 Found while restoring Pnl.10 See 910546 & 910551 for interruptions to Pnl.3 & 910564 for interruption to Pnl.14 related 910542 910544 910546 910547 910551 910564 910566 | December | 2012 | 2013Q2 | 2013 | ZN12650:PA10 | ZN12650:PA10 | ZN12650/000010 | CENTRAL COAST | UG | Not Veg | 2012-12-07 | N | 39.4633 | N | 5 | N | N | 1.1101 | 39.4971 | 55831.5974
[7 empty] | 16590 | 573 | 909415 | 2012-12-07 13:18 | 2012-12-07 13:31 | 13 | 11kV | 19287 | 2084 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123492 1 fault operation 3 phase Sensitive Earth Fault Excluded OMS 909415 & 909422 | December | 2012 | 2013Q2 | 2013 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2012-12-07 | N | 9.2548 | N | 5 | N | N | 1.1101 | 39.4971 | 14094.3707
[7 empty] | 17670 | 11036 | 909555 | 2012-12-07 19:17 | 2012-12-07 22:35 | 198 | 11kV | 396 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123486 burnt off live line clamp at pole 9G-10275. Excluded oms report no 909555. | December | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-12-07 | N | 198 | N | 5 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 18082 | 15630 | 909574 | 2012-12-08 00:10 | 2012-12-08 00:50 | 40 | 11kV | 480 | 12 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT13297 Scenic Bounty Hill - 16A roadside phase HDO fuse blown Possum on PT | December | 2012 | 2013Q2 | 2013 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2012-12-08 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 16896 | 2843 | 909612 | 2012-12-08 11:35 | 2012-12-08 12:14 | 39 | 11kV | 59514 | 1526 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 123493 2 fault operations A & B phases Overcurrent Branch on mains near sub 7590. Excluded OMS 909612 | December | 2012 | 2013Q2 | 2013 | 232:33411 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2012-12-08 | N | 39 | N | 6 | N | N | 1.1101 | 39.4971 | 43491.0758
[7 empty] | 16629 | 838 | 909635 | 2012-12-08 14:33 | 2012-12-08 16:20 | 107 | 11kV | 3638 | 34 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT48816 Wolseley McDonagh - roadside HDO operated fuse fatigue | December | 2012 | 2013Q2 | 2013 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2012-12-08 | N | 107 | N | 6 | N | N | 1.1101 | 39.4971 | 2658.5431
[7 empty] | 16741 | 1531 | 909681 | 2012-12-08 19:00 | 2012-12-08 19:40 | 40 | 11kV | 27920 | 698 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.15002 Narrabeen - Panel 4 Fdr CB tripped on C phase OC. Suspect tree on OH O/S #5 Wakehurst Parkway | December | 2012 | 2013Q2 | 2013 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Veg | 2012-12-08 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 20403.1125
[7 empty] | 17709 | 11640 | 909686 | 2012-12-08 19:12 | 2012-12-08 20:06 | 54 | 11kV | 130298 | 2521 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | At S2635 Epping Panel 21 Tripped on Relays: A and C phase IOC and Timed O/C, Fault Check, EFI Signals: Zone Earth, No1 and No3 Group Earth and 11kV trip Abnormal Switching: LB916 Open, AB3036, Ab767 Closed. Cause: CB failed on SWC at S647 M2 Norfolk Rd Tunnel. Failed on being racked up. See interruption for Panel 10. | December | 2012 | 2013Q2 | 2013 | ZN2635:PA10 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | Unknown | Not Veg | 2012-12-08 | N | 51.685 | N | 6 | N | N | 1.1101 | 39.4971 | 95217.9353
[7 empty] | 16616 | 763 | 909688 | 2012-12-08 19:17 | 2012-12-08 20:55 | 98 | 11kV | 10584 | 108 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123496 A phase DOLF : 31 Amp | December | 2012 | 2013Q2 | 2013 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | UG | Not Veg | 2012-12-08 | N | 98 | N | 6 | N | N | 1.1101 | 39.4971 | 7734.475
[7 empty] | 18510 | 19966 | 909721 | 2012-12-09 04:57 | 2012-12-09 05:54 | 57 | 11kV | 42237 | 741 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Rec46113 Wharf Coronga tripped ex Pa30 Pymble Cause: Large piece of Bark contacted mains near LB432 See OMS 911808 909721 | December | 2012 | 2013Q2 | 2013 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2012-12-09 | N | 57 | N | 19 | N | N | 1.1101 | 39.4971 | 30865.5538
[7 empty] | 16919 | 3039 | 909865 | 2012-12-09 13:45 | 2012-12-09 14:45 | 60 | 11kV | 600 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123519 3 phase DOLF : 5 Amp | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2012-12-09 | N | 60 | N | 19 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 16637 | 887 | 909897 | 2012-12-09 14:16 | 2012-12-09 14:45 | 29 | 11kV | 29087 | 1003 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn.14144 Wamberal Pnl.2 tripped & locked out on inst O/C, EFI Weather related - strong winds dislodged tree brnach onto mains near PT11840. | December | 2012 | 2013Q2 | 2013 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2012-12-09 | N | 29 | N | 19 | N | N | 1.1101 | 39.4971 | 21255.9217
[7 empty] | 16780 | 1911 | 909920 | 2012-12-09 14:46 | 2012-12-09 15:37 | 51 | 11kV | 51 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123520 C phase DOLF : 10 Amp Excluded OMS 909920 | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2012-12-09 | N | 51 | N | 19 | N | N | 1.1101 | 39.4971 | 37.2693
[7 empty] | 17370 | 7667 | 909870 | 2012-12-09 13:47 | 2012-12-09 16:25 | 158 | 11kV | 213913 | 1799 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | ZN 9700 Kirrawee - Pnl 20 - IOC A & C phase, Timer, LO. 11kV Stranded lines clashing near PT 9476 Princes Park. Repaired by Mains. | December | 2012 | 2013Q2 | 2013 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2012-12-09 | N | 118.9066 | N | 19 | N | N | 1.1101 | 39.4971 | 156321.311
[7 empty] | 17469 | 8504 | 909945 | 2012-12-09 15:25 | 2012-12-09 17:10 | 105 | 11kV | 420 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123516 A phase DOLF : 16 Amp FAULTY ARRESTOR Excluded OMS REPORT NO 909945. | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-12-09 | N | 105 | N | 19 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 18074 | 15553 | 909910 | 2012-12-09 14:25 | 2012-12-09 17:30 | 185 | 11kV | 13126 | 1306 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12690 Berkeley vale Pnl.12 tripped & reclosed on A & B phase O/C, E/F, EFI 11kV bond on line side of LK 42802 tee PT12207 failed. required to interrupt PT11512 @ 1645 to enable repairs see 911076 911080 911081 | December | 2012 | 2013Q2 | 2013 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Not Veg | 2012-12-09 | N | 10.0505 | N | 19 | N | N | 1.1101 | 39.4971 | 9592.0936
[7 empty] | 17192 | 5780 | 909995 | 2012-12-09 17:07 | 2012-12-09 18:53 | 106 | 11kV | 77334 | 1050 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN1290 Leightonfield 11kv Pnl 12 "Miller Bil #1" feeder tripped on C phase IOC and timed, reclose and lockout relay. Signals: 11kv trip Field efi's: nil Remarks: suspect flashover...did not reclose Related jobs: #909995, 910010, 910789, 910787 | December | 2012 | 2013Q2 | 2013 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-12-09 | N | 73.6514 | N | 19 | N | N | 1.1101 | 39.4971 | 56513.4062
[7 empty] | 17763 | 12041 | 909954 | 2012-12-09 15:47 | 2012-12-09 19:38 | 231 | 11kV | 11319 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123513 A & B phase Overcurrent SECTIONALISER 42007 LOCKED OUT.FDR SECTIONALISED & RETURNED TO SERVICE .NO FAULT FOUND PLEASE PATROL . Excluded OMS REPORT NO 909954. | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-12-09 | N | 231 | N | 19 | N | N | 1.1101 | 39.4971 | 8271.5913
[7 empty] | 17970 | 13902 | 909774 | 2012-12-09 11:40 | 2012-12-09 20:00 | 500 | 11kV | 53858 | 119 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Truck hit UG/OH pole O/S 38 Telegraph Rd, Pymble; damaging "J" pipe. Fault current in both #2 and #3 dists caused HV fuse to blow at S.4635. SHOCK LOAD POLE, BROKEN CROSS ARM. 4 BAYS OF S/L REMOVED | December | 2012 | 2013Q2 | 2013 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | OH | Not Veg | 2012-12-09 | N | 452.5882 | N | 19 | N | N | 1.1101 | 39.4971 | 39357.8379
[7 empty] | 16881 | 2568 | 910007 | 2012-12-09 17:37 | 2012-12-09 20:30 | 173 | 11kV | 692 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123517 3 phase DOLF : 16 Amp RENEWED 3 ARRESTORS & HV FUSES. Excluded OMS REPORT NO 910007. | December | 2012 | 2013Q2 | 2013 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2012-12-09 | N | 173 | N | 19 | N | N | 1.1101 | 39.4971 | 505.6932
[7 empty] | 17936 | 13422 | 910009 | 2012-12-09 17:30 | 2012-12-09 20:35 | 185 | 11kV | 185 | 1 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 123524 3 phase DOLF : 63 Amp Excluded OMS 910009 | December | 2012 | 2013Q2 | 2013 |  |  |  |  | OH | Not Veg | 2012-12-09 | N | 185 | N | 19 | N | N | 1.1101 | 39.4971 | 135.1925
[7 empty] | 16775 | 1866 | 909936 | 2012-12-09 15:10 | 2012-12-09 20:45 | 335 | 11kV | 3685 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123525 A phase DOLF : 10 Amp Excluded OMS 909936 | December | 2012 | 2013Q2 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2012-12-09 | N | 335 | N | 19 | N | N | 1.1101 | 39.4971 | 2692.8893
[7 empty] | 16805 | 2089 | 909909 | 2012-12-09 14:34 | 2012-12-09 21:30 | 416.4833 | 11kV | 5830.7667 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123526 C phase DOLF : 20 Amp | December | 2012 | 2013Q2 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2012-12-09 | N | 416.4833 | N | 19 | N | N | 1.1101 | 39.4971 | 4260.9523
[7 empty] | 16687 | 1133 | 909950 | 2012-12-09 15:42 | 2012-12-09 21:44 | 362 | 11kV | 362 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123527 B phase DOLF : 10 Amp Excluded OMS REPORT NO 909950 | December | 2012 | 2013Q2 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2012-12-09 | N | 362 | N | 19 | N | N | 1.1101 | 39.4971 | 264.5389
[7 empty] | 18170 | 16288 | 909890 | 2012-12-09 14:07 | 2012-12-09 22:00 | 473 | 11kV | 28242 | 198 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123531 B phase 11KV MAIN DOWN BETWEEN POLES DG-50061 & DG-50148, SW 74147 DID NOT TRIP (MAIN ALIVE ON GROUND BACK FED VIA TX 70267)PLEASE CHECK PROTECTION. Excluded OMS REPORT NO 909890 & 909917. | December | 2012 | 2013Q2 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2012-12-09 | N | 142.6364 | N | 19 | N | N | 1.1101 | 39.4971 | 20638.4206
[7 empty] | 16801 | 2052 | 910073 | 2012-12-09 20:37 | 2012-12-09 22:01 | 84.0833 | 11kV | 16015.1833 | 2087 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 123518 No protection operation Fdr opened by system operator. Broken xarm at pole JU-63257. Excluded OMS # 910073 | December | 2012 | 2013Q2 | 2013 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Not Veg | 2012-12-09 | N | 7.6738 | N | 19 | N | N | 1.1101 | 39.4971 | 11703.4236
[7 empty] | 16541 | 271 | 910096 | 2012-12-09 19:58 | 2012-12-09 22:12 | 133.6833 | 11kV | 227.8 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123528 A phase DOLF : 10 Amp Excluded OMS 910096 | December | 2012 | 2013Q2 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | UG | Not Veg | 2012-12-09 | N | 113.9 | N | 19 | N | N | 1.1101 | 39.4971 | 166.4695
[7 empty] | 16670 | 1055 | 911830 | 2012-12-09 22:08 | 2012-12-10 00:15 | 127 | 11kV | 158242 | 1246 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S195 Pymble panel 9 Tripped on Earth Leakage, EFI and Fault Check. Cause: front line feeder fault from Pa9 at S195 Pymble to S47348 Pacific Cecil. See OMS 911830 910103 910108 | December | 2012 | 2013Q2 | 2013 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2012-12-09 | N | 127 | N | 19 | N | N | 1.1101 | 39.4971 | 115638.5863
[7 empty] | 17276 | 6841 | 910130 | 2012-12-10 01:21 | 2012-12-10 02:34 | 73 | 11kV | 90374 | 1238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S587 Hornsby Panel 15 Tripped on Earth Leakage, EFI and Fault Check. Signals: 11kV Trip Zn Earth and No1 Group Earth. Cause: Trees contacting 11kV on Cnr of Page and Curtain. See OMS 912992 910130 | December | 2012 | 2013Q2 | 2013 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2012-12-10 | N | 73 | N | 10 | N | N | 1.1101 | 39.4971 | 66042.6536
[7 empty] | 17048 | 4004 | 910113 | 2012-12-10 00:05 | 2012-12-10 03:30 | 205 | 11kV | 23562 | 1631 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.11 tripped on SEL 11kV feeder came down Barrett Drive 500m north - came in as glowing wires job see 911560 911562 | December | 2012 | 2013Q2 | 2013 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2012-12-10 | N | 14.4464 | N | 10 | N | N | 1.1101 | 39.4971 | 17218.4146
[7 empty] | 17280 | 6886 | 910172 | 2012-12-10 06:35 | 2012-12-10 07:49 | 74 | 11kV | 2552 | 43 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN1610 HOMEBUSH BAY Panel #20 "Coal St" fdr tripped on C ph O/C (SCADA Computer not working at Zone) Remarks: UG Fault. Suspected UG fault between S823 Fariola St & S3203 Day Fariola No1. Related jobs: #910184, 910172, 910875, 910873 | December | 2012 | 2013Q2 | 2013 | ZN1610:PA20 | ZN1610:PA20 | ZN01610/000020 | PARRAMATTA | UG | Not Veg | 2012-12-10 | N | 59.3488 | N | 10 | N | N | 1.1101 | 39.4971 | 1864.9263
[7 empty] | 18006 | 14251 | 910216 | 2012-12-10 08:08 | 2012-12-10 10:19 | 131 | 11kV | 2096 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14676 Empire bay School - roadside phase 31.5A HDO operated fuse fatigue | December | 2012 | 2013Q2 | 2013 | ZN12660:PA5 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2012-12-10 | N | 131 | N | 10 | N | N | 1.1101 | 39.4971 | 1531.695
[7 empty] | 17813 | 12483 | 910152 | 2012-12-10 05:20 | 2012-12-10 10:40 | 320 | 11kV | 125399 | 2247 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 123534 2 fault operations Earth fault Excluded OMS 910152, 910153, 910155, 910156, 910175 | December | 2012 | 2013Q2 | 2013 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2012-12-10 | N | 55.8073 | N | 10 | N | N | 1.1101 | 39.4971 | 91637.8906
[7 empty] | 16993 | 3513 | 910242 | 2012-12-10 08:29 | 2012-12-10 13:25 | 296 | 11kV | 2368 | 8 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123537 11kV mains down between pole DN-10158 & Sub 51637 | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-12-10 | N | 296 | N | 10 | N | N | 1.1101 | 39.4971 | 1730.4646
[7 empty] | 18056 | 15397 | 910355 | 2012-12-10 10:16 | 2012-12-10 14:12 | 236 | 11kV | 108401 | 1238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Panel 15 Tripped on Relays: Earth Fault, EFI, Earth Fault Check Signals: 11kV Trip, Zone Earth and No1 Group Earth Cause: Tree banch in contact with Mains Near PT2046 - Mains to inspect and clear trees. See OMS 911553 911555 910355 | December | 2012 | 2013Q2 | 2013 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | OH | Veg | 2012-12-10 | N | 87.5614 | N | 10 | N | N | 1.1101 | 39.4971 | 79216.2535
[7 empty] | 17108 | 4484 | 910623 | 2012-12-10 15:25 | 2012-12-10 17:30 | 125 | 11kV | 250 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 123540 Isolate sub 52944 to replace LV xarm & repair low LV OHM between poles FU-42502, FU-42503 & FU-42504. Excluded OMS 910623 | December | 2012 | 2013Q2 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2012-12-10 | N | 125 | N | 10 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 17833 | 12578 | 910670 | 2012-12-10 17:22 | 2012-12-10 21:45 | 263 | 11kV | 263 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 123542 A phase DOLF : 10 Amp Blown HV L/A. Sub isolated for repairs Replaced all 3 L/As. Volts = 246V Excluded OMS 910670 | December | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2012-12-10 | N | 263 | N | 10 | N | N | 1.1101 | 39.4971 | 192.1926
[7 empty] | 17408 | 8034 | 910685 | 2012-12-10 17:50 | 2012-12-10 23:59 | 369 | 11kV | 153663 | 781 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | LID 123541 2 fault operations C phase Overcurrent; Earth fault Sw 2015 OP/CL/OP E/F Timed, c phase O/C, BGN Wires down Maneela St Blacksmith pole SW-60357 Broken x arm. High into Low sub 16818 Excluded OMS 910685, 910733, 910734, 910735 | December | 2012 | 2013Q2 | 2013 | 222:2015 | 222:33601 | ZN00222/033601 | LAKE MACQUARIE | OH | Not Veg | 2012-12-10 | N | 196.7516 | N | 10 | N | N | 1.1101 | 39.4971 | 112292.3881
[7 empty] | 18394 | 18356 | 910702 | 2012-12-11 06:40 | 2012-12-11 10:15 | 215 | 11kV | 215 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 123544 broken connection on line side of DOLF Excluded oms 910702 | December | 2012 | 2013Q2 | 2013 | 238:34141 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2012-12-11 | N | 215 | N | 6 | N | N | 1.1101 | 39.4971 | 157.1157
[7 empty] | 16914 | 3019 | 910840 | 2012-12-11 09:00 | 2012-12-11 14:40 | 340 | 11kV | 2040 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 123545 Emergency isolation to repair low 11kV ground clearance adj MG-77006. Excluded OMS 910840 | December | 2012 | 2013Q2 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2012-12-11 | N | 340 | N | 6 | N | N | 1.1101 | 39.4971 | 1490.7718
[7 empty] | 16607 | 709 | 911020 | 2012-12-11 13:43 | 2012-12-11 14:45 | 62 | 11kV | 124 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 123547 A phase DOLF : 10 Amp Excluded OMS 911020 | December | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2012-12-11 | N | 62 | N | 6 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 17376 | 7705 | 910806 | 2012-12-11 08:28 | 2012-12-11 15:00 | 392 | 11kV | 1568 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123546 Single phase RE INSTALLED LIVE LINE CLAMP OFF AT POLE DV-51704 Excluded OMS 910806 | December | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2012-12-11 | N | 392 | N | 6 | N | N | 1.1101 | 39.4971 | 1145.8482
[7 empty] | 17809 | 12464 | 910907 | 2012-12-11 10:42 | 2012-12-11 18:40 | 478 | 11kV | 15778 | 205 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn.14891 Wyong Pnl.6 tripped / reclosed / tripped on A & C phase IOC, reclose timing, lockout UG feeder fault between S12665, S12173 & S14209 see 912166 912167 912167 912171 912177 912174 912168 912175 | December | 2012 | 2013Q2 | 2013 | ZN14891:PA6 | ZN14891:PA6 | ZN14891/000006 | CENTRAL COAST | UG | Not Veg | 2012-12-11 | N | 76.9659 | N | 6 | N | N | 1.1101 | 39.4971 | 11530.097
[7 empty] | 17454 | 8354 | 911258 | 2012-12-11 23:23 | 2012-12-12 00:20 | 57 | 11kV | 64706 | 1444 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Zn.12600 lisarow Pnl.3 tripped on C phase timed Overcurrent Possum at Pt14381 - HDOs blown see 911576 911577 | December | 2012 | 2013Q2 | 2013 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2012-12-11 | N | 44.8102 | N | 6 | N | N | 1.1101 | 39.4971 | 47285.2363
[7 empty] | 17614 | 10232 | 911271 | 2012-12-12 01:37 | 2012-12-12 03:07 | 90 | 11kV | 12870 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Pa4 ex Galston Zone Recloser CP428 Bayfield Tripped reclosed tripped and locked out on Overcurrent Cause: Removed tree branch from Pole AR23857 vicinity PT797 See OMS 913106 913108 911271 | December | 2012 | 2013Q2 | 2013 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2012-12-12 | N | 78.4756 | N | 6 | N | N | 1.1101 | 39.4971 | 9405.0164
[7 empty] | 17706 | 11615 | 911308 | 2012-12-12 07:42 | 2012-12-12 09:22 | 100 | 11kV | 62884 | 908 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | ZN 9118 Cronulla - Pnl 7 - Earth Fault with EFI. UG cable fault from S 9226 Resolution Endeavour to S 9414 Resolution Adventure to S 9525 Endeavour Resol No. 1. | December | 2012 | 2013Q2 | 2013 | ZN9118:PA7 | ZN9118:PA7 | ZN09118/000007 | SUTHERLAND | Unknown | Not Veg | 2012-12-12 | N | 69.2555 | N | 6 | N | N | 1.1101 | 39.4971 | 45953.7724
[7 empty] | 17106 | 4481 | 911607 | 2012-12-12 15:00 | 2012-12-12 15:50 | 50 | 11kV | 50 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123565 Burnt off tapping pole AJ-20573 sub isolated & repaired Live Line Excluded OMS 911607 | December | 2012 | 2013Q2 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2012-12-12 | N | 50 | N | 6 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 17530 | 9012 | 911600 | 2012-12-12 15:04 | 2012-12-12 15:50 | 46 | 11kV | 61180 | 1330 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 33 Tripped on A and C Phase O/C Timing Relay and Lockout RelayEFI. Cause: Tree on Mains (OS 36 Eloura St) - Cleared by DOp Mains to Investigate See OMS 911999 912030 912033 911600 911608 911613 | December | 2012 | 2013Q2 | 2013 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2012-12-12 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 44708.5395
[7 empty] | 16699 | 1232 | 911582 | 2012-12-12 14:20 | 2012-12-12 15:58 | 98 | 11kV | 5488 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC 44604 Dog Trap Rd - tripped & reclosed on IOC & OC 11kV mains down near PT12576 - REC opened by DOp @ 1534 hrs | December | 2012 | 2013Q2 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2012-12-12 | N | 98 | N | 6 | N | N | 1.1101 | 39.4971 | 4010.4685
[7 empty] | 18504 | 19941 | 911646 | 2012-12-12 16:20 | 2012-12-12 18:25 | 125 | 11kV | 500 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 123567 Section isolated to repair xarm/insulator pole BM-20094 Excluded OMS 911646 | December | 2012 | 2013Q2 | 2013 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2012-12-12 | N | 125 | N | 6 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 18133 | 15981 | 911785 | 2012-12-13 08:35 | 2012-12-13 10:25 | 110 | 11kV | 197555 | 1882 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | @Zn2568 St Peters 11kv fdr pa29 tripped Relays-Bph O/C, E/F, EFI, Fault CHeck Signals: 11kv trip, Zone Earth, No3 Group Earth Feild EFI's Nil Cause: Cable UG damaged by contractor On corner Angel and Harold damaged section of 11kv ug feeder from S2568 St Peters Pa29 to S47032 SwA Harold Union See 912897,900 GIS 912908 exclude 911785,9,90,98,801,7,10 | December | 2012 | 2013Q2 | 2013 | ZN2568:PA29 | ZN2568:PA29 | ZN02568/000029 | SYDNEY | UG | Not Veg | 2012-12-13 | N | 104.9708 | N | 2 | N | N | 1.1101 | 39.4971 | 144367.3671
[7 empty] | 16800 | 2049 | 911980 | 2012-12-13 13:58 | 2012-12-13 15:17 | 79 | 11kV | 77894 | 986 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | ZN 398 Dulwich Hill - Pnl 11 - B phase Earth Fault, EFIs. UG fault located between S 1942 Arthur Queen and S 4158 Norton Joseph. | December | 2012 | 2013Q2 | 2013 | ZN398:PA11 | ZN398:PA11 | ZN00398/000011 | INNER WEST | Unknown | Not Veg | 2012-12-13 | N | 79 | N | 2 | N | N | 1.1101 | 39.4971 | 56922.6377
[7 empty] | 17291 | 6994 | 912163 | 2012-12-14 07:41 | 2012-12-14 11:50 | 249 | 11kV | 18675 | 75 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn.12960 Berkeley Vale Pnl.16 - Bond burnt off near AB 43697 Feeder interrupted from LB43360 for linesman to repair | December | 2012 | 2013Q2 | 2013 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2012-12-14 | N | 249 | N | 3 | N | N | 1.1101 | 39.4971 | 13647.1392
[7 empty] | 16681 | 1119 | 912440 | 2012-12-14 14:05 | 2012-12-14 15:20 | 75 | 11kV | 8250 | 110 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Ex Pnl.33 Avoca Zn - AB40455 Opened linesman found 11kV OH mains on crossarm between LB46366 abd BA40455. Feeder was interrupted for safety while repairs took place | December | 2012 | 2013Q2 | 2013 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Not Veg | 2012-12-14 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 6028.8567
[7 empty] | 17603 | 10000 | 912467 | 2012-12-14 16:02 | 2012-12-14 16:42 | 40 | 11kV | 41400 | 1035 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn80 Chatswood Panel 31 feeder tripped on A and B phase IOC and Timed O/C, EFI and Fault Check relays Signals: 11kV Trip Abnromal Swithcing: LB2539 Closed With AB2862 Open. Cause: Tree branch on 11kV mains O/S 9 Sherland Ave See OMS 9131436 912467 912470 912468 912472 | December | 2012 | 2013Q2 | 2013 | ZN80:PA31 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2012-12-14 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 30253.8989
[7 empty] | 18205 | 16646 | 912538 | 2012-12-15 03:05 | 2012-12-15 04:29 | 84 | 11kV | 72540 | 882 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | @Zn1287 Revesby Pa23 11kv fdr tripped, reclosed 7 locked out on EF, EFI, Timer, LO, FC Alarms: Zone Earth, Tx3 Group Earth, 11kv trip EFI: S35560 S4580 S5435 S5645 S1234 S35484 Cause: Animals/Birds Comments: Deceased Possum located at base of pole for PT1244 Parmal Ave See 912941,3 Exclude 912538,9 | December | 2012 | 2013Q2 | 2013 | ZN1287:PA23 | ZN1287:PA23 | ZN01287/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2012-12-15 | N | 82.2449 | N | 5 | N | N | 1.1101 | 39.4971 | 53010.0924
[7 empty] | 17611 | 10170 | 912541 | 2012-12-15 06:41 | 2012-12-15 06:57 | 16 | 11kV | 2896 | 181 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123609 As directed for all switching at Nelson Bay zone during the dressing of DNMS Sw 39257 was dressed open which was a Scada Control sub thus de-energising the feeder. Analogue box adjacent to these switches is required similar to ALL other operational points in the Newcastle Region. Excluded oms 912541, 912542, 912543. | December | 2012 | 2013Q2 | 2013 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2012-12-15 | N | 16 | N | 5 | N | N | 1.1101 | 39.4971 | 2116.3114
[7 empty] | 18416 | 18757 | 912540 | 2012-12-15 06:03 | 2012-12-15 07:35 | 92 | 11kV | 184 | 2 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 123610 Single phase DOLF : 10 Amp Dead Possum Found at pole. Tx Volts - 241V Excluded OMS No. 912540 | December | 2012 | 2013Q2 | 2013 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2012-12-15 | N | 92 | N | 5 | N | N | 1.1101 | 39.4971 | 134.4618
[7 empty] | 18485 | 19667 | 912574 | 2012-12-15 09:55 | 2012-12-15 12:10 | 135 | 11kV | 810 | 6 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123611 Section of 11kV Fdr isolated to repair sub pole & stay wire that were found energised at Ka-Mahi sub 72365. Cracked insulators also replaced at t-off pole 4K-20072. | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2012-12-15 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 591.9241
[7 empty] | 17633 | 10603 | 912659 | 2012-12-15 22:57 | 2012-12-15 23:58 | 61 | 11kV | 10980 | 180 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.8 Tripped on A & B phase O/C, EFI Suspect UG fault from S14912 to S14127 to S14169 | December | 2012 | 2013Q2 | 2013 | ZN12650:PA8 | ZN12650:PA8 | ZN12650/000008 | CENTRAL COAST | UG | Not Veg | 2012-12-15 | N | 61 | N | 5 | N | N | 1.1101 | 39.4971 | 8023.8601
[7 empty] | 17182 | 5561 | 912687 | 2012-12-16 10:33 | 2012-12-16 15:35 | 302 | 11kV | 40806 | 154 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 123620 C phase bond Burnt off CCT tapping pole FR-64706 started grass fire. Outage area had to be extended beyond ABS 41435 & LF 41242 due to NO earthing points on CCT OHM. (Does not comply with network standards NS126 3.5.4). HINT PLEASE INSTALL THE EARTHING POINTS ASAP. Excluded OMS 912687 & 912693 | December | 2012 | 2013Q2 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2012-12-16 | N | 264.974 | N | 4 | N | N | 1.1101 | 39.4971 | 29819.8212
[7 empty] | 17163 | 5211 | 912743 | 2012-12-16 16:09 | 2012-12-16 16:45 | 36.1833 | 11kV | 325.65 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 123621 C phase DOLF : 40 Amp Please do full line patrol beyonfd these fuses. | December | 2012 | 2013Q2 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2012-12-16 | N | 36.1833 | N | 4 | N | N | 1.1101 | 39.4971 | 237.9754
[7 empty] | 18551 | 20353 | 912742 | 2012-12-16 16:00 | 2012-12-16 17:17 | 77 | 11kV | 77 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 123623 DOLF Found L/F down, probable fuse fatigue. Excluded OMS No's 912742 & 912752 | December | 2012 | 2013Q2 | 2013 | 232:33411 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Not Veg | 2012-12-16 | N | 77 | N | 4 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 17851 | 12724 | 912728 | 2012-12-16 14:16 | 2012-12-16 17:50 | 214.2333 | 11kV | 10068.9667 | 47 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 123622 No protection operation, burnt tapping at Line Fuse 40563. CC1: 22-"Refer to SOp" | December | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2012-12-16 | N | 214.2333 | N | 4 | N | N | 1.1101 | 39.4971 | 7358.1039
[7 empty] | 17637 | 10660 | 912812 | 2012-12-17 03:15 | 2012-12-17 04:20 | 65 | 11kV | 5980 | 92 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | PT13389 matthews Brisbane Water - road & middle phase HDO operated Bird @ PT13389 | December | 2012 | 2013Q2 | 2013 | ZN12650:PA17 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2012-12-17 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 4370.0076
[7 empty] | 17720 | 11724 | 913055 | 2012-12-17 12:20 | 2012-12-17 13:15 | 55 | 11kV | 48345 | 879 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn901 Surry Hills Pa31 tripped on Relays: Earth Leakage (element on O/C rlay) EFI Signals: Group Earth. Zone Earth Feild EFI: nil Cause: UG Fault From Pa31 to S5653 to S8232. UG cable fault Landsdowne st near high holburn See 913363,4 Exclude 913055, 63 | December | 2012 | 2013Q2 | 2013 | ZN901:PA31 | ZN901:PA9 | ZN00901/000009 | SYDNEY | UG | Not Veg | 2012-12-17 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 35329.1001
[7 empty] | 17253 | 6564 | 913219 | 2012-12-17 19:23 | 2012-12-17 20:40 | 76.8 | 11kV | 1766.4 | 23 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123640 B & C phase DOLF : 20 Amp IBIS FLEW INTO MAINS- Excluded REPORT NO 913222 & 913223. | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-12-17 | N | 76.8 | N | 4 | N | N | 1.1101 | 39.4971 | 1290.833
[7 empty] | 17743 | 11910 | 913236 | 2012-12-17 20:52 | 2012-12-17 21:24 | 32 | 11kV | 53888 | 1684 | HV | Animal Flying Fox | Animal | Circuit Breaker | Unplanned | Unselected | N | ZN 9700 Kirrawee - Pnl 23 - A & C phase overcurrent. Bat flew into wires near PT 9072 Vernon Ellesmere. | December | 2012 | 2013Q2 | 2013 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2012-12-17 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 39379.761
[7 empty] | 18478 | 19562 | 913286 | 2012-12-18 08:33 | 2012-12-18 10:15 | 102 | 11kV | 83637 | 951 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S4545 Meadowbank Panel 17 Tripped reclosed tripped and locked out Relays: A PHase IOC and Timed O/C, Timingm lockout Cause: Bird on pole near AB792 See OMS 914016 914014 914015 913310/304/286 | December | 2012 | 2013Q2 | 2013 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Not Veg | 2012-12-18 | N | 87.9464 | N | 3 | N | N | 1.1101 | 39.4971 | 61119.4527
[7 empty] | 16979 | 3416 | 913528 | 2012-12-18 14:25 | 2012-12-18 17:45 | 200 | 11kV | 22600 | 113 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123659 2 fault operations 3 phase Excluded OMS 913528, 913570 & 913575 | December | 2012 | 2013Q2 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2012-12-18 | N | 200 | N | 3 | N | N | 1.1101 | 39.4971 | 16515.4134
[7 empty] | 17587 | 9756 | 913609 | 2012-12-18 18:57 | 2012-12-18 21:25 | 148 | 11kV | 148 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 123667 A & C phase DOLF : 10 Amp Faulty LVF assemblies, damaged cause unknown. Assemblies replaced, blown DOLD's replaced. Excluded OMS No 913609. | December | 2012 | 2013Q2 | 2013 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | Unknown | Unknown | 2012-12-18 | N | 148 | N | 3 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 17170 | 5307 | 913767 | 2012-12-19 10:17 | 2012-12-19 17:30 | 433 | 11kV | 13900 | 60 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 123682 2 fault operations OHM down at polesIT-41723. Excluded oms-913811 | December | 2012 | 2013Q2 | 2013 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2012-12-19 | N | 231.6667 | N | 2 | N | N | 1.1101 | 39.4971 | 10157.71
[7 empty] | 17172 | 5312 | 914084 | 2012-12-19 20:30 | 2012-12-20 10:15 | 825 | 11kV | 18965 | 77 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 123688 3 fault operations Fault beyond 11kV links 41505. Possibly faulty transformer. Excluded OMS No's 914088 & 914084. ## | December | 2012 | 2013Q2 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2012-12-19 | N | 246.2987 | N | 2 | N | N | 1.1101 | 39.4971 | 13859.0626
[7 empty] | 16806 | 2101 | 914322 | 2012-12-20 12:21 | 2012-12-20 13:45 | 84 | 11kV | 7140 | 85 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | 11kv Bond burnt off on LK23651 ex Pa5 "Queenscliffe Fdr" (Zn15008 Harbord Zone) See 914617 exclude 914319,22,8 | December | 2012 | 2013Q2 | 2013 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | OH | Not Veg | 2012-12-20 | N | 84 | N | 2 | N | N | 1.1101 | 39.4971 | 5217.7014
[7 empty] | 17597 | 9811 | 914447 | 2012-12-20 18:05 | 2012-12-20 20:11 | 126 | 11kV | 252 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123703 Single phase DOLF : 3 Amp Excluded OMS 914447 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-20 | N | 126 | N | 2 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 18086 | 15660 | 914507 | 2012-12-21 01:09 | 2012-12-21 02:30 | 81 | 11kV | 1215 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | PT2214 Mansfield End 3 x 31.5k HDO Fuses Operated Ex Panel 4L 'S47361 Galston Aux No.1" @ S35370 Galston Cause: cause not ascertained Remarks: Unknown See 914679 exclude 914507,8 | December | 2012 | 2013Q2 | 2013 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2012-12-21 | N | 81 | N | 7 | N | N | 1.1101 | 39.4971 | 887.8862
[7 empty] | 16730 | 1408 | 914509 | 2012-12-21 03:45 | 2012-12-21 05:19 | 93.5667 | 11kV | 163.5167 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123706 DOLF : 10 Amp 2 X DOLF's Blown Volts 245 Excluded OMS 914509 | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-12-21 | N | 81.7583 | N | 7 | N | N | 1.1101 | 39.4971 | 119.4932
[7 empty] | 18345 | 17838 | 914512 | 2012-12-21 05:25 | 2012-12-21 06:20 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123707 A & B phase DOLF : 40 Amp Excluded OMS 914512 | December | 2012 | 2013Q2 | 2013 | 238:34137 | 532:83301 | ZN00532/083301 | MAITLAND | UG | Not Veg | 2012-12-21 | N | 55 | N | 7 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 18406 | 18533 | 915231 | 2012-12-21 06:18 | 2012-12-21 06:22 | 4 | 11kV | 7076 | 1769 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 123721 fdr interupted by aop to carry out emergency isolation of defective greta regulator | December | 2012 | 2013Q2 | 2013 | 512:48046 | 512:83736 | ZN00512/083736 | CESSNOCK | OH | Not Veg | 2012-12-21 | N | 4 | N | 7 | N | N | 1.1101 | 39.4971 | 5170.9321
[7 empty] | 16918 | 3034 | 914552 | 2012-12-21 09:01 | 2012-12-21 10:27 | 86 | 11kV | 312.7333 | 4 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 123720 B phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-12-21 | N | 78.1833 | N | 7 | N | N | 1.1101 | 39.4971 | 228.5363
[7 empty] | 16674 | 1091 | 914728 | 2012-12-21 15:35 | 2012-12-21 19:00 | 205 | 11kV | 410 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | Unselected | N | LID 123725 3 phase No protection operations. Car into pole JQ-46142. Pole replaced under A/P Excluded OMS # 914728 | December | 2012 | 2013Q2 | 2013 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2012-12-21 | N | 205 | N | 7 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 16707 | 1254 | 914657 | 2012-12-21 20:15 | 2012-12-21 21:00 | 45 | 11kV | 45 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123874 B phase DOLF ; 40 Amp Excluded OMS 914657 | December | 2012 | 2013Q2 | 2013 | 203:8090 | 204:82701 | ZN00204/082701 | NEWCASTLE | UG | Not Veg | 2012-12-21 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 16667 | 1043 | 914894 | 2012-12-22 15:47 | 2012-12-22 18:00 | 133 | 11kV | 1064 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123731 Single phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2012-12-22 | N | 133 | N | 1 | N | N | 1.1101 | 39.4971 | 777.5398
[7 empty] | 18482 | 19613 | 914971 | 2012-12-23 08:36 | 2012-12-23 10:10 | 94 | 11kV | 41110 | 833 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 123735 4 fault operatio ns 3 phase Earth fault UG cable fault between 35412 & 8717. | December | 2012 | 2013Q2 | 2013 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | UG | Not Veg | 2012-12-23 | N | 49.3517 | N | 3 | N | N | 1.1101 | 39.4971 | 30041.9755
[7 empty] | 16832 | 2214 | 915018 | 2012-12-23 14:48 | 2012-12-23 16:03 | 74.9333 | 11kV | 50879.7333 | 679 | HV | Vegetation Blow/Fall In | Vegetation | Circuit Breaker | Unplanned | Unselected | N | ZN 129 Hunters Hill - Pnl 21 - A phase timed O/C. Tree branch on 11kV mains. Removed by DOp. | December | 2012 | 2013Q2 | 2013 | ZN129:PA21 | ZN129:PA63 | ZN00129/000063 | LANE COVE | OH | Veg | 2012-12-23 | N | 74.9333 | N | 3 | N | N | 1.1101 | 39.4971 | 37181.4084
[7 empty] | 18353 | 17890 | 915048 | 2012-12-23 18:17 | 2012-12-23 20:31 | 134 | 11kV | 13380 | 151 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 123740 2 fault operations A & C phases Overcurrent branch on mains beyond abs 74579 at pole 9L-20910 Excluded oms 915048 | December | 2012 | 2013Q2 | 2013 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2012-12-23 | N | 88.6093 | N | 3 | N | N | 1.1101 | 39.4971 | 9777.7094
[7 empty] | 17005 | 3604 | 115 | 2012-12-24 | 2012-12-24 00:12 | 12 | 11kV | 7752 | 646 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting OMS update(s) | December | 2012 | 2013Q2 | 2013 |  |  |  |  | Unknown | Unknown | 2012-12-24 | N | 12 | N | 26 | Y | Y | 1.1101 | 39.4971 | 5664.933
[7 empty] | 16915 | 3027 | 114 | 2012-12-24 | 2012-12-24 02:16 | 136 | 11kV | 13872 | 102 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting OMS update(s) | December | 2012 | 2013Q2 | 2013 |  |  |  |  | Unknown | Unknown | 2012-12-24 | N | 136 | N | 26 | Y | Y | 1.1101 | 39.4971 | 10137.2484
[7 empty] | 18069 | 15504 | 915093 | 2012-12-24 06:08 | 2012-12-24 08:30 | 142 | 11kV | 142 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123746 B phase DOLF : 10 Amp Excluded OMS 915093 | December | 2012 | 2013Q2 | 2013 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2012-12-24 | N | 142 | N | 26 | Y | Y | 1.1101 | 39.4971 | 103.7694
[7 empty] | 17114 | 4525 | 915109 | 2012-12-24 07:48 | 2012-12-24 10:45 | 177 | 11kV | 36793 | 797 | HV | Animal Bird | Animal | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 123747 1 fault operation No Protection Flags Found. Discovered magpie in mains beyond L/F 74090. Please check protection relays for flag fall. | December | 2012 | 2013Q2 | 2013 | 801:74118 | 801:74118 | ZN00801/074118 | MUSWELLBROOK | OH | Not Veg | 2012-12-24 | N | 46.1644 | N | 26 | Y | Y | 1.1101 | 39.4971 | 26887.2392
[7 empty] | 18030 | 14711 | 915240 | 2012-12-24 10:59 | 2012-12-24 12:35 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123749 Single phase DOLF : 10 Amp Excluded OMS 915240 | December | 2012 | 2013Q2 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2012-12-24 | N | 96 | N | 26 | Y | Y | 1.1101 | 39.4971 | 70.154
[7 empty] | 18141 | 16028 | 915348 | 2012-12-24 13:16 | 2012-12-24 16:00 | 164 | 11kV | 8563 | 94 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 44607 tripped and locked out on OC, E/F trip & lockout. One phase of OH mains down at corner of Matcham near Wambina Rd. Made contact with LV mains, EmSO checked customer's premises. | December | 2012 | 2013Q2 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2012-12-24 | N | 91.0957 | N | 26 | Y | Y | 1.1101 | 39.4971 | 6257.5878
[7 empty] | 17672 | 11061 | 915475 | 2012-12-24 17:27 | 2012-12-24 18:45 | 78 | 11kV | 32130 | 420 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | Although no evidence - lightning at the time of occurrence. At S.12630 Peats Ridge, Panel 3 Fdr CB tripped and locked out on C phase timed OC | December | 2012 | 2013Q2 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2012-12-24 | N | 76.5 | N | 26 | Y | Y | 1.1101 | 39.4971 | 23479.6563
[7 empty] | 18223 | 16835 | 915479 | 2012-12-24 17:35 | 2012-12-24 18:50 | 75 | 11kV | 11925 | 159 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Tree branch on mains - D.Op removed tree branch from OH at pole PR 652 | December | 2012 | 2013Q2 | 2013 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2012-12-24 | N | 75 | N | 26 | Y | Y | 1.1101 | 39.4971 | 8714.4383
[7 empty] | 17032 | 3939 | 915499 | 2012-12-24 18:23 | 2012-12-24 19:25 | 61.8667 | 11kV | 371.2 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123752 C phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2012-12-24 | N | 61.8667 | N | 26 | Y | Y | 1.1101 | 39.4971 | 271.262
[7 empty] | 17184 | 5593 | 915498 | 2012-12-24 17:27 | 2012-12-24 19:45 | 138 | 11kV | 829 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | Recloser 61084 tripped and reclosed on OC. At PT.11878 the HDO fuse 31.5 amp operated - the lightning arrestor was cut away | December | 2012 | 2013Q2 | 2013 | ZN12630:PA5 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2012-12-24 | N | 118.4286 | N | 26 | Y | Y | 1.1101 | 39.4971 | 605.8087
[7 empty] | 17319 | 7236 | 915483 | 2012-12-24 17:30 | 2012-12-24 20:40 | 190 | 11kV | 840 | 273 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | At S.12630 Peats Ridge, Panel 4 Fdr CB tripped and reclosed on A phase timed OC. At PT.12367 the A and B phase HDO 16 amp fuses operated. All L/A's cut away | December | 2012 | 2013Q2 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2012-12-24 | N | 3.0769 | N | 26 | Y | Y | 1.1101 | 39.4971 | 613.8472
[7 empty] | 16969 | 3353 | 915568 | 2012-12-24 21:40 | 2012-12-24 22:55 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123786 A phase DOLF : 10 Amp Excluded OMS 915568 & 915579 | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-12-24 | N | 75 | N | 26 | Y | Y | 1.1101 | 39.4971 | 54.8078
[7 empty] | 17387 | 7841 | 915596 | 2012-12-24 22:19 | 2012-12-24 22:57 | 38 | 11kV | 47500 | 1250 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Lightning storm at time of occurrence. At S.12650 Noraville, Panel 8 Fdr CB tripped on 1.2.1 51B OC and E/F, efi, #1 group earth with 11kV trip signal. Field efi's down at S.18799 and S.14824 | December | 2012 | 2013Q2 | 2013 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Veg | 2012-12-24 | N | 38 | N | 26 | Y | Y | 1.1101 | 39.4971 | 34711.599
[7 empty] | 18302 | 17490 | 915597 | 2012-12-24 22:19 | 2012-12-24 22:58 | 39 | 11kV | 41886 | 1074 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Lightning | N | Lightning storm at time of occurrence. At S.12650 Noraville, Panel 10 Fdr CB tripped on 1.2.1 51C OC and E/F, efi, #1 group earth. Field efi's down at S.18584, S.18098 and S.49389 | December | 2012 | 2013Q2 | 2013 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | Unknown | Not Veg | 2012-12-24 | N | 39 | N | 26 | Y | Y | 1.1101 | 39.4971 | 30609.0534
[7 empty] | 17054 | 4051 | 915529 | 2012-12-24 22:41 | 2012-12-24 23:04 | 23 | 11kV | 15249 | 663 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123784 1 fault operation 3 phase Overcurrent No fault found. Reclose off due to sub jobs beyond device. Excluded OMS 915529 | December | 2012 | 2013Q2 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2012-12-24 | N | 23 | N | 26 | Y | Y | 1.1101 | 39.4971 | 11143.5194
[7 empty] | 16975 | 3384 | 915567 | 2012-12-24 21:38 | 2012-12-24 23:05 | 87 | 11kV | 1218 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123789 B phase DOLF : 10 Amp OMS 915567 10A Bph L/F 40607 10A DOLF sub 51244 Volts at sub 51244 251, 250, 249 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-12-24 | N | 87 | N | 26 | Y | Y | 1.1101 | 39.4971 | 890.0785
[7 empty] | 17652 | 10804 | 915593 | 2012-12-24 22:12 | 2012-12-24 23:58 | 106 | 11kV | 3710 | 35 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn3471 Sefton Pa18 tripped Relays: 'A' IOC + TImed, 'B' E/F, Lockout, Timing, Fault Check, EFI Signals: 11kv trip, Group Earth, Zone EFI's S7409 S7474 S7008 S5215 S1256 S8142 S3329 Cause: Tree branch contact - other. Bark on UGOH Adjacent S1211 See 916188 Exclude 915593 | December | 2012 | 2013Q2 | 2013 | ZN3472:PA18 | ZN3472:PA18 | ZN03472/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2012-12-24 | N | 106 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2711.1586
[7 empty] | 16787 | 1962 | 915601 | 2012-12-24 22:22 | 2012-12-25 00:17 | 115 | 11kV | 58995 | 513 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At S.14891 Wyong, Panel 20 Fdr CB tripped on C phase OC, efi, fault check, #2 Tx fault check, frame leakage prohibition. | December | 2012 | 2013Q2 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2012-12-24 | N | 115 | N | 26 | Y | Y | 1.1101 | 39.4971 | 43111.8059
[7 empty] | 16521 | 113 | 915632 | 2012-12-24 23:18 | 2012-12-25 00:55 | 97 | 11kV | 4656 | 48 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123793 C phase DOLF : 20 Amp Faulty arrestor cut away. Excluded OMS # 915632 | December | 2012 | 2013Q2 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2012-12-24 | N | 97 | N | 26 | Y | Y | 1.1101 | 39.4971 | 3402.4675
[7 empty] | 17678 | 11165 | 915564 | 2012-12-24 21:17 | 2012-12-25 02:00 | 283 | 11kV | 283 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123796 A & C phase DOLF : 10 Amp Excluded oms 915564 | December | 2012 | 2013Q2 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2012-12-24 | N | 283 | N | 26 | Y | Y | 1.1101 | 39.4971 | 206.8081
[7 empty] | 16648 | 939 | 915566 | 2012-12-24 21:31 | 2012-12-25 02:40 | 309 | 11kV | 25071 | 232 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Electrical Storm | N | LID 123790 4 fault operations Earth fault Cable box damaged by lightning. Sw unit replaced. at sub 29673 | December | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | Unknown | Not Veg | 2012-12-24 | N | 108.0647 | N | 26 | Y | Y | 1.1101 | 39.4971 | 18321.1473
[7 empty] | 18306 | 17528 | 915638 | 2012-12-24 23:28 | 2012-12-25 03:15 | 227 | 11kV | 454 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123797 C phase DOLF : 5 Amp Excluded OMS 915638 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2012-12-24 | N | 227 | N | 26 | Y | Y | 1.1101 | 39.4971 | 331.7698
[7 empty] | 17925 | 13371 | 915674 | 2012-12-25 02:25 | 2012-12-25 03:20 | 55 | 11kV | 4015 | 73 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123799 C phase DOLF : 40 Amp Volts = 250 x 3. Amps = 170, 40, 300. Excluded OMS # 915674, 915680, 915676, 915674 | December | 2012 | 2013Q2 | 2013 | 223:14399 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | UG | Not Veg | 2012-12-25 | N | 55 | N | 37 | Y | Y | 1.1101 | 39.4971 | 2934.0436
[7 empty] | 18323 | 17718 | 915633 | 2012-12-25 01:35 | 2012-12-25 04:05 | 150 | 11kV | 13950 | 93 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | Electrical Storm | N | LID 123794 No protection operations. 11kV mains down between poles CH-50157 & CH-50292. Excluded OMS # 915633 & 915650 | December | 2012 | 2013Q2 | 2013 | 223:14395 | 223:14395 | ZN00223/014395 | LAKE MACQUARIE | OH | Not Veg | 2012-12-25 | N | 150 | N | 37 | Y | Y | 1.1101 | 39.4971 | 10194.2485
[7 empty] | 16987 | 3455 | 915554 | 2012-12-24 21:08 | 2012-12-25 04:20 | 432 | 11kV | 432 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123800 A & C phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 |  |  |  |  | UG | Not Veg | 2012-12-24 | N | 432 | N | 26 | Y | Y | 1.1101 | 39.4971 | 315.6929
[7 empty] | 17144 | 4850 | 116 | 2012-12-25 | 2012-12-25 04:55 | 295 | 11kV | 13275 | 45 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting OMS update(s) | December | 2012 | 2013Q2 | 2013 |  |  |  |  | Unknown | Unknown | 2012-12-25 | N | 295 | N | 37 | Y | Y | 1.1101 | 39.4971 | 9700.9785
[7 empty] | 17565 | 9511 | 915657 | 2012-12-25 00:08 | 2012-12-25 05:00 | 292 | 11kV | 1752 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123802 C Phase DOLF : 10 Amp Excluded OMS 915657 | December | 2012 | 2013Q2 | 2013 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2012-12-25 | N | 292 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1280.3099
[7 empty] | 16569 | 431 | 915681 | 2012-12-25 03:28 | 2012-12-25 06:23 | 175 | 11kV | 525 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123803 3 phase DOLF : 16 Amp Excluded OMS 915681 | December | 2012 | 2013Q2 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2012-12-25 | N | 175 | N | 37 | Y | Y | 1.1101 | 39.4971 | 383.6545
[7 empty] | 16848 | 2316 | 915628 | 2012-12-24 21:04 | 2012-12-25 06:45 | 581 | 11kV | 2905 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 123792 3 phase DOLF : 10 Amp Faulty arrestors. Suspect txf. AP left. FS to arrange repairs. Transformer change completed. Excluded OMS # 915628 | December | 2012 | 2013Q2 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | UG | Not Veg | 2012-12-24 | N | 581 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2122.8883
[7 empty] | 16952 | 3265 | 915701 | 2012-12-24 22:40 | 2012-12-25 07:48 | 548 | 11kV | 3288 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123804 A phase DOLF : 20 Amp Excluded OMS 915201 | December | 2012 | 2013Q2 | 2013 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | UG | Not Veg | 2012-12-24 | N | 548 | N | 26 | Y | Y | 1.1101 | 39.4971 | 2402.7734
[7 empty] | 17728 | 11792 | 915692 | 2012-12-25 05:39 | 2012-12-25 08:40 | 180.85 | 11kV | 723.4 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | Lightning storm at time of occurrence, At PT.12142 the roadside 16 amp HDO fuse operated, suspect lightning | December | 2012 | 2013Q2 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2012-12-25 | N | 180.85 | N | 37 | Y | Y | 1.1101 | 39.4971 | 528.6394
[7 empty] | 16723 | 1372 | 915731 | 2012-12-25 08:24 | 2012-12-25 09:35 | 71 | 11kV | 142 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123806 B phase DOLF : 16 Amp Excluded OMS 915731 | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-12-25 | N | 71 | N | 37 | Y | Y | 1.1101 | 39.4971 | 103.7694
[7 empty] | 18231 | 16896 | 915753 | 2012-12-25 08:05 | 2012-12-25 10:15 | 130 | 11kV | 130 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 123811 C phase DOLF : 10 Amp Replaced Lightning Arrester Excluded OMS # 915753. | December | 2012 | 2013Q2 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2012-12-25 | N | 130 | N | 37 | Y | Y | 1.1101 | 39.4971 | 95.0002
[7 empty] | 17610 | 10167 | 915748 | 2012-12-25 09:20 | 2012-12-25 10:26 | 66 | 11kV | 3234 | 49 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn1610 Homebush Pa26 tripped Relays: FN, G1, C, N*-* Signals: N/A EFI-S8931 S6377 S4908 S6108 (suspect all down from previous fault) Cause: UG Fault 11kv feeder fault from Pa26 at Zn1610 Homebush Bay SwA at S3212 See 916198 exclude 915748 | December | 2012 | 2013Q2 | 2013 | ZN1610:PA26 | ZN1610:PA26 | ZN01610/000026 | PARRAMATTA | UG | Not Veg | 2012-12-25 | N | 66 | N | 37 | Y | Y | 1.1101 | 39.4971 | 2363.3118
[7 empty] | 16635 | 875 | 915755 | 2012-12-25 09:53 | 2012-12-25 10:28 | 35 | 11kV | 40145 | 1147 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | @Zn10990 Arncliffe Pa11 tripped reclosed and locked out Relays: Cph inst+timed overcurrent, reclose timing, lockout Signals: 11kv protection trip EFI:N/A Cause: Animals/Birds. Cockatoo on mains adjacent AB31125 See 916210 exclude 915755 | December | 2012 | 2013Q2 | 2013 | ZN10990:PA11 | ZN10998:PA5 | ZN10998/000005 | BAYSIDE | OH | Not Veg | 2012-12-25 | N | 35 | N | 37 | Y | Y | 1.1101 | 39.4971 | 29336.7819
[7 empty] | 17374 | 7690 | 915747 | 2012-12-25 09:17 | 2012-12-25 10:37 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123808 A phase DOLF : 10 Amp Excluded OMS 915747 | December | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2012-12-25 | N | 80 | N | 37 | Y | Y | 1.1101 | 39.4971 | 116.9233
[7 empty] | 18093 | 15722 | 915704 | 2012-12-25 10:03 | 2012-12-25 11:02 | 59 | 11kV | 96172 | 1732 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Panel 13 Fdr CB tripped, reclosed, tripped and locked out at S.12650 West gosford - E/F, C phase OC, efi and lockout, 11kV trip. Field efi down at S.14116. Tree branch brought down OH in Deane St Narara | December | 2012 | 2013Q2 | 2013 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2012-12-25 | N | 55.5266 | N | 37 | Y | Y | 1.1101 | 39.4971 | 70279.661
[7 empty] | 16739 | 1511 | 915541 | 2012-12-24 20:53 | 2012-12-25 12:18 | 924.5833 | 11kV | 597280.8333 | 646 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Based ON Customer Comments suspect Bond burnt off beyond CP3228 See OMS 915541 915713 CC1: 22-"Refer to SOp" | December | 2012 | 2013Q2 | 2013 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2012-12-24 | N | 924.5833 | N | 26 | Y | Y | 1.1101 | 39.4971 | 436475.2162
[7 empty] | 17041 | 3973 | 915773 | 2012-12-25 10:26 | 2012-12-25 13:05 | 159 | 11kV | 318 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123816 Single phase DOLF : 10 Amp Readings as left 252V @ 8A. Excluded OMS 915773. | December | 2012 | 2013Q2 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | UG | Not Veg | 2012-12-25 | N | 159 | N | 37 | Y | Y | 1.1101 | 39.4971 | 232.385
[7 empty] | 17123 | 4588 | 915696 | 2012-12-25 06:03 | 2012-12-25 13:30 | 447 | 11kV | 1788 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123818 Unknown phase DOLF : 5 Amp Excluded OMS 915696 | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-12-25 | N | 447 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1306.6177
[7 empty] | 16864 | 2432 | 915764 | 2012-12-25 10:11 | 2012-12-25 15:10 | 299 | 11kV | 2392 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | LID 123820 C phase DOLF : 16 Amp REPLACED DOLF CARRIER BURNT UP | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2012-12-25 | N | 299 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1748.003
[7 empty] | 17086 | 4319 | 915811 | 2012-12-25 10:43 | 2012-12-25 15:45 | 302 | 11kV | 302 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Fuse fatigue of the roadside HDO at PT.18504 | December | 2012 | 2013Q2 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-12-25 | N | 302 | N | 37 | Y | Y | 1.1101 | 39.4971 | 220.6927
[7 empty] | 18438 | 18972 | 915819 | 2012-12-25 14:27 | 2012-12-25 16:05 | 98 | 11kV | 1764 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123828 C phase DOLF : 16 Amp Excluded OMS 915816 | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2012-12-25 | N | 98 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1289.0792
[7 empty] | 16736 | 1496 | 915820 | 2012-12-25 14:49 | 2012-12-25 16:55 | 126 | 11kV | 83538 | 663 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 123829 Faulty arresters cut away at DP-37012 | December | 2012 | 2013Q2 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2012-12-25 | N | 126 | N | 37 | Y | Y | 1.1101 | 39.4971 | 61047.1064
[7 empty] | 16923 | 3061 | 915830 | 2012-12-25 15:31 | 2012-12-25 17:35 | 124 | 11kV | 124 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123833 B phase DOLF : 3 Amp Excluded OMS 915830 | December | 2012 | 2013Q2 | 2013 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | UG | Not Veg | 2012-12-25 | N | 124 | N | 37 | Y | Y | 1.1101 | 39.4971 | 90.6155
[7 empty] | 17867 | 12855 | 915859 | 2012-12-25 17:30 | 2012-12-25 18:10 | 40 | 11kV | 1720 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @PT9497 Kangaroo Point Road Central 11kv HDO operated roadside (?Amps) Section of 11kv feeder Pa2 ex Zn9037 Miranda Zone Cause: Other details provided HDO fixed contact is burnt and damaged, HDO needs replacing PT 9497 Kangaroo Pt RD Central in LV// See 916215 exclude 915859,61,88 | December | 2012 | 2013Q2 | 2013 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Veg | 2012-12-25 | N | 40 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1256.9253
[7 empty] | 16734 | 1494 | 915852 | 2012-12-25 16:19 | 2012-12-25 18:15 | 116 | 11kV | 232 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123832 A Phase DOLF : 3 Amp Excluded OMS 915852 | December | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2012-12-25 | N | 116 | N | 37 | Y | Y | 1.1101 | 39.4971 | 169.5388
[7 empty] | 17669 | 10998 | 915879 | 2012-12-25 17:19 | 2012-12-25 19:00 | 101 | 11kV | 3333 | 33 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123835 1 fgault operation Earth fault Excluded OMS 915879 | December | 2012 | 2013Q2 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2012-12-25 | N | 101 | N | 37 | Y | Y | 1.1101 | 39.4971 | 2435.6581
[7 empty] | 17780 | 12255 | 915878 | 2012-12-25 17:17 | 2012-12-25 19:07 | 110 | 11kV | 18040 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | At Recloser 44946 tripped, reclosed, tripped and locked out on OC. Tree branch on mains adjacent to PT.48452 | December | 2012 | 2013Q2 | 2013 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2012-12-25 | N | 110 | N | 37 | Y | Y | 1.1101 | 39.4971 | 13183.0999
[7 empty] | 17969 | 13881 | 915843 | 2012-12-25 15:56 | 2012-12-25 19:10 | 194 | 11kV | 53402 | 747 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | At S.14143 Somersby, 11kV Feeder 17 CB tripped on B and C phase OC. Surge Divertors cutaway at S.14926 | December | 2012 | 2013Q2 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2012-12-25 | N | 71.4886 | N | 37 | Y | Y | 1.1101 | 39.4971 | 39024.6065
[7 empty] | 16972 | 3358 | 915700 | 2012-12-25 16:20 | 2012-12-25 19:50 | 210.3 | 11kV | 210.3 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Lightning | N | A single 11kV conductor fell into tree beyond LB.43076 to PT.12367 | December | 2012 | 2013Q2 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2012-12-25 | N | 210.3 | N | 37 | Y | Y | 1.1101 | 39.4971 | 153.681
[7 empty] | 16689 | 1138 | 915855 | 2012-12-25 16:21 | 2012-12-25 20:09 | 228 | 11kV | 23028 | 101 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N |  | December | 2012 | 2013Q2 | 2013 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2012-12-25 | N | 228 | N | 37 | Y | Y | 1.1101 | 39.4971 | 16828.1832
[7 empty] | 17681 | 11336 | 915817 | 2012-12-25 14:28 | 2012-12-25 20:30 | 362 | 11kV | 362 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 123844 DOLF : 10 Amp Replace faulty transformer | December | 2012 | 2013Q2 | 2013 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | UG | Not Veg | 2012-12-25 | N | 362 | N | 37 | Y | Y | 1.1101 | 39.4971 | 264.5389
[7 empty] | 17401 | 7956 | 915901 | 2012-12-25 18:00 | 2012-12-25 20:46 | 166.2333 | 11kV | 5319.4667 | 32 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | No supported by Sydney Control Room Documentation CC1: 22-"Refer to SOp" | December | 2012 | 2013Q2 | 2013 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Not Veg | 2012-12-25 | N | 166.2333 | N | 37 | Y | Y | 1.1101 | 39.4971 | 3887.3093
[7 empty] | 18162 | 16179 | 915828 | 2012-12-25 15:27 | 2012-12-25 21:00 | 333 | 11kV | 333 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 123843 Single phase DOLF : 10 Amp replace faulty trans SAO required | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-12-25 | N | 333 | N | 37 | Y | Y | 1.1101 | 39.4971 | 243.3466
[7 empty] | 17134 | 4690 | 915934 | 2012-12-25 19:10 | 2012-12-25 21:06 | 116 | 11kV | 5800 | 50 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 123850 Isolation to repair burnt tapping on LK 27638 also refer to OMS 9158251 | December | 2012 | 2013Q2 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2012-12-25 | N | 116 | N | 37 | Y | Y | 1.1101 | 39.4971 | 4238.4689
[7 empty] | 17757 | 11980 | 915860 | 2012-12-25 16:39 | 2012-12-25 22:10 | 331 | 11kV | 31481 | 529 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 123840 2 fault operations B phase Earth fault B phase 11kV OHM down between poles JR-85035 & JR-85036. Also replaced A ph DOLF 10 A sub 8128. | December | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2012-12-25 | N | 59.5104 | N | 37 | Y | Y | 1.1101 | 39.4971 | 23005.3863
[7 empty] | 17382 | 7774 | 915931 | 2012-12-25 19:18 | 2012-12-25 23:00 | 222 | 11kV | 222 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123849 DOLF : 10 Amp Excluded OMS 915931 | December | 2012 | 2013Q2 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2012-12-25 | N | 222 | N | 37 | Y | Y | 1.1101 | 39.4971 | 162.2311
[7 empty] | 17302 | 7124 | 915954 | 2012-12-25 21:05 | 2012-12-26 00:15 | 190.3167 | 11kV | 6090.1333 | 32 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Previous Storm | N | LID 123845 No protection operations. LV service UGOH faulty - within clearance of HV. Sub isolated for repair under AP. Refer previous event 915918 | December | 2012 | 2013Q2 | 2013 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | Unknown | Unknown | 2012-12-25 | N | 190.3167 | N | 37 | Y | Y | 1.1101 | 39.4971 | 4450.4898
[7 empty] | 17359 | 7562 | 915847 | 2012-12-25 16:08 | 2012-12-26 00:25 | 497 | 11kV | 2485 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | No LID Consulted Control room & dispatch. Suspected blown DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2012-12-25 | N | 497 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1815.9647
[7 empty] | 17432 | 8182 | 915915 | 2012-12-25 18:34 | 2012-12-26 00:45 | 370.5 | 11kV | 8521.5 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123847 B phase DOLF : 16 Amp | December | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-12-25 | N | 370.5 | N | 37 | Y | Y | 1.1101 | 39.4971 | 6227.2609
[7 empty] | 17043 | 3985 | 915983 | 2012-12-26 06:32 | 2012-12-26 08:30 | 118 | 11kV | 472 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123852 3 phase DOLFs : 10 Amp Excluded OMS 915983 | December | 2012 | 2013Q2 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2012-12-26 | N | 118 | N | 8 | N | N | 1.1101 | 39.4971 | 344.9237
[7 empty] | 17879 | 12928 | 916267 | 2012-12-25 23:31 | 2012-12-26 10:01 | 630 | 11kV | 55011 | 408 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.14143 Somersby, Panel 5 Fdr CB tripped on earth fault, 11kV trip. Field efi's down at S.18048 and CP.45441. Suspect UG fault from Sw.B at CP.45441 to Sw A at S.14863 to AB.40492 to L.43585 tp L.LB.43658. Possum on UG/OH | December | 2012 | 2013Q2 | 2013 | ZN14143:PA5 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | OH | Not Veg | 2012-12-25 | N | 134.8309 | N | 37 | Y | Y | 1.1101 | 39.4971 | 40200.4163
[7 empty] | 18071 | 15516 | 916003 | 2012-12-26 10:00 | 2012-12-26 10:50 | 50 | 11kV | 150 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123854 Single phase DOLF : 10 Amp Excluded OMS 916003 | December | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2012-12-26 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 16617 | 778 | 916049 | 2012-12-26 10:39 | 2012-12-26 11:50 | 71 | 11kV | 71 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123856 C phase DOLF : 10 Amp Excluded OMS 916049 | December | 2012 | 2013Q2 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2012-12-26 | N | 71 | N | 8 | N | N | 1.1101 | 39.4971 | 51.8847
[7 empty] | 17618 | 10272 | 916015 | 2012-12-26 10:00 | 2012-12-26 13:15 | 195 | 11kV | 4485 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 123858 A phase DOLF : 16 Amp Excluded OMS 916015 | December | 2012 | 2013Q2 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2012-12-26 | N | 195 | N | 8 | N | N | 1.1101 | 39.4971 | 3277.5057
[7 empty] | 18532 | 20164 | 915891 | 2012-12-25 17:38 | 2012-12-26 13:40 | 1202 | 11kV | 313170 | 1687 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID 123836 7 fault operations 3 phase Earth fault; Overcurrent repeated trips while sectionalising brought up E/F &/or O/C Flags Suspect cable fault between 75169 & 74093 though this section had been energised and held in during switching. Excluded OMS 915891 | December | 2012 | 2013Q2 | 2013 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | UG | Not Veg | 2012-12-25 | N | 185.6372 | N | 37 | Y | Y | 1.1101 | 39.4971 | 228855.399
[7 empty] | 17246 | 6512 | 916141 | 2012-12-26 18:55 | 2012-12-26 20:00 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123863 Single phase DOLF : 10 Amp Excluded OMS 916141 | December | 2012 | 2013Q2 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | CENTRAL COAST | UG | Not Veg | 2012-12-26 | N | 65 | N | 8 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 17600 | 9882 | 915892 | 2012-12-26 17:43 | 2012-12-26 23:00 | 317 | 11kV | 7608 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123846 3 phase DOLF's : 31 Amp Excluded OMS 915892 | December | 2012 | 2013Q2 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2012-12-26 | N | 317 | N | 8 | N | N | 1.1101 | 39.4971 | 5559.702
[7 empty] | 16560 | 370 | 916128 | 2012-12-26 18:25 | 2012-12-27 00:23 | 358 | 11kV | 6486 | 43 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 123865 HDWB 33kV fdr fell into 11kV Fdr at pole KQ-40010 | December | 2012 | 2013Q2 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2012-12-26 | N | 150.8372 | N | 8 | N | N | 1.1101 | 39.4971 | 4739.7775
[7 empty] | 17523 | 8984 | 916160 | 2012-12-26 21:45 | 2012-12-27 01:55 | 250 | 11kV | 286231 | 1316 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.14891 Wyong new, Panel 8 Fdr CB tripped on Basler (51N) time delayed earth fault and OC, E/F chaeck, efi. 11kV trip, #1 Tx group earth. UG cable fault between S.14688, S.14791 USL 43210 and recloser 48425. | December | 2012 | 2013Q2 | 2013 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | UG | Not Veg | 2012-12-26 | N | 217.5008 | N | 8 | N | N | 1.1101 | 39.4971 | 209169.1724
[7 empty] | 17644 | 10713 | 916165 | 2012-12-27 03:47 | 2012-12-27 05:00 | 73 | 11kV | 92874 | 1380 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah Nth, Panel 17 Fdr CB tripped on B phASE ioc, 11Kv TRIP, #3 tX cOOLING FAILURE AND 415V NO-VOLT Tree branch hit 11kV | December | 2012 | 2013Q2 | 2013 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Veg | 2012-12-27 | N | 67.3 | N | 5 | N | N | 1.1101 | 39.4971 | 67869.5799
[7 empty] | 16770 | 1783 | 916241 | 2012-12-27 09:13 | 2012-12-27 09:45 | 32 | 11kV | 13889 | 472 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.384 Camperdown, 5kV Panel 41 Fdr CB tripped on B phase E/F relay, efi, 5kV trip, #1 group earth. Field efi down at S.5662. UG cable fault | December | 2012 | 2013Q2 | 2013 | ZN384:PA41 | ZN7481:PA20 | ZN07481/000020 | SYDNEY | UG | Not Veg | 2012-12-27 | N | 29.4258 | N | 5 | N | N | 1.1101 | 39.4971 | 10149.6715
[7 empty] | 17201 | 5906 | 916255 | 2012-12-27 09:55 | 2012-12-27 12:00 | 125 | 11kV | 10125 | 81 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 123868 Faulty 11kV cable from previous fdr fault, outage for fault location. see report# 123836/OMS 918105 Excluded OMS# 916255 & 916256. | December | 2012 | 2013Q2 | 2013 | 812:19066 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | UG | Not Veg | 2012-12-27 | N | 125 | N | 5 | N | N | 1.1101 | 39.4971 | 7399.0514
[7 empty] | 16753 | 1643 | 916342 | 2012-12-27 11:36 | 2012-12-27 13:15 | 99.2 | 11kV | 254.2 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123875 A phase DOLF : 10 Amp Excluded OMS 916342 | December | 2012 | 2013Q2 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | UG | Not Veg | 2012-12-27 | N | 84.7333 | N | 5 | N | N | 1.1101 | 39.4971 | 185.7619
[7 empty] | 18344 | 17830 | 916297 | 2012-12-27 10:03 | 2012-12-27 14:30 | 267 | 11kV | 2388 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | Recloser 47302 opened for safety to repair burnt bond in a teed section. PT.13927 also islaoted for safety | December | 2012 | 2013Q2 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2012-12-27 | N | 265.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 1745.08
[7 empty] | 18414 | 18736 | 117 | 2012-12-28 | 2012-12-28 03:04 | 184 | 11kV | 5704 | 31 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting OMS update(s) | December | 2012 | 2013Q2 | 2013 |  |  |  |  | Unknown | Unknown | 2012-12-28 | N | 184 | N | 15 | N | N | 1.1101 | 39.4971 | 4168.315
[7 empty] | 18036 | 14894 | 918249 | 2012-12-28 02:16 | 2012-12-28 05:57 | 221 | 11kV | 22411 | 232 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 123878 3 fault operations 3 phase HWCPID Pump at sub 29673 was not returned to service until 10:15 - Customer not shown in OMS - GIS correction lodged Excluded OMS 916505 | December | 2012 | 2013Q2 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | Unknown | Unknown | 2012-12-28 | N | 96.5991 | N | 15 | N | N | 1.1101 | 39.4971 | 16377.2978
[7 empty] | 16538 | 263 | 916518 | 2012-12-28 07:00 | 2012-12-28 09:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123879 Single phase DOLF : 10 Amp Excluded OMS 916518 | December | 2012 | 2013Q2 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2012-12-28 | N | 120 | N | 15 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 16852 | 2340 | 916590 | 2012-12-28 09:29 | 2012-12-28 10:45 | 76 | 11kV | 304 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 123881 A phase DOLF : 10 Amp Excluded OMSA 916590 | December | 2012 | 2013Q2 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | UG | Not Veg | 2012-12-28 | N | 76 | N | 15 | N | N | 1.1101 | 39.4971 | 222.1542
[7 empty] | 17703 | 11579 | 916504 | 2012-12-28 11:33 | 2012-12-28 11:42 | 9 | 11kV | 3465 | 385 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 123882 No protection operation. ABS 13185 road side phase burning up, section isolated to bridge out ABS 13185 Live Line. Excluded OMS 916504. | December | 2012 | 2013Q2 | 2013 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2012-12-28 | N | 9 | N | 15 | N | N | 1.1101 | 39.4971 | 2532.1198
[7 empty] | 17912 | 13231 | 916560 | 2012-12-28 09:00 | 2012-12-28 14:30 | 330 | 11kV | 330 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 123892 Sub replaced Excluded OMS 916560 | December | 2012 | 2013Q2 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2012-12-28 | N | 330 | N | 15 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 17517 | 8949 | 916683 | 2012-12-28 13:34 | 2012-12-28 14:56 | 82 | 11kV | 92166 | 1257 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | At S.847 JHHornsby, Panel 15 Fdr CB tripped on OC and Eatrth Fault, trip lampo, alarm lamp A-B-C, 11kV trip, zone earth, #3 group earth, #3 capictor bank defect, #3 Tx earth fault check. Field efi down at S.4722 | December | 2012 | 2013Q2 | 2013 | ZN847:PA15 | ZN847:PA15 | ZN00847/000015 | KU-RING-GAI | UG | Not Veg | 2012-12-28 | N | 73.3222 | N | 15 | N | N | 1.1101 | 39.4971 | 67352.1944
[7 empty] | 17138 | 4722 | 916707 | 2012-12-28 15:00 | 2012-12-28 15:26 | 26 | 11kV | 26 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123894 A phase DOLF : 10 Amp Excluded OMS 916707 | December | 2012 | 2013Q2 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2012-12-28 | N | 26 | N | 15 | N | N | 1.1101 | 39.4971 | 19
[7 empty] | 16826 | 2190 | 916715 | 2012-12-28 14:21 | 2012-12-28 15:30 | 69 | 11kV | 4944 | 660 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Recloser 46529 tripped and reclosed on OC and IOC. At PT.12057 the standoff insulator between HDO and Tx failed. Section of OH isolated and PT in LV // | December | 2012 | 2013Q2 | 2013 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2012-12-28 | N | 7.4909 | N | 15 | N | N | 1.1101 | 39.4971 | 3612.9294
[7 empty] | 16943 | 3189 | 916721 | 2012-12-28 14:12 | 2012-12-28 16:55 | 162.7833 | 11kV | 12380.2833 | 97 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123895 C Phase DOLF : 40 Amp Excluded OMS 916721, 916726, 916727, 916742. | December | 2012 | 2013Q2 | 2013 | 232:33411 | 242:81541 | ZN00242/081541 | PORT STEPHENS | UG | Not Veg | 2012-12-28 | N | 127.6318 | N | 15 | N | N | 1.1101 | 39.4971 | 9047.1459
[7 empty] | 18287 | 17351 | 916795 | 2012-12-28 16:15 | 2012-12-28 17:40 | 85 | 11kV | 85 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 123901 C phase DOLF : 10 Amp | December | 2012 | 2013Q2 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2012-12-28 | N | 85 | N | 15 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 16831 | 2212 | 916814 | 2012-12-28 16:39 | 2012-12-28 18:05 | 86 | 11kV | 105752 | 1641 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 123899 3 fault operations A & C phase Overcurrent oms 916814 see outage 123898 Lightening across N/O ABS 4002 Damage to UGOH pole OR-67115 2 LA's replaced 29/12/12 | December | 2012 | 2013Q2 | 2013 | 232:11460 | 242:81532 | ZN00242/081532 | PORT STEPHENS | Unknown | Unknown | 2012-12-28 | N | 64.4436 | N | 15 | N | N | 1.1101 | 39.4971 | 77280.4424
[7 empty] | 16606 | 701 | 916884 | 2012-12-28 19:33 | 2012-12-28 20:25 | 52 | 11kV | 2536 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 123904 A & B phase Overcurrent Sectionaliser | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2012-12-28 | N | 50.72 | N | 15 | N | N | 1.1101 | 39.4971 | 1853.234
[7 empty] | 17322 | 7281 | 916833 | 2012-12-28 17:20 | 2012-12-28 20:47 | 207 | 11kV | 2898 | 14 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 123902 Section isolated after lightning strike for repairs ABS 8337 hit by Lightening. Interruption for repairs Excluded OMS 916833 | December | 2012 | 2013Q2 | 2013 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2012-12-28 | N | 207 | N | 15 | N | N | 1.1101 | 39.4971 | 2117.7729
[7 empty] | 18100 | 15793 | 916688 | 2012-12-28 13:32 | 2012-12-29 13:29 | 1437 | 11kV | 85008 | 334 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 123900 Trip & reclose of feeder CB Sub 54122 held in LV parallel during repairs UGOH at pole FS-93214 at broken tapping at pole FS-93202 Excluded oms 916684, 916688, 916689 etc. | December | 2012 | 2013Q2 | 2013 | 504:48032 | 522:83121 | ZN00522/083121 | CESSNOCK | Unknown | Unknown | 2012-12-28 | N | 254.515 | N | 15 | N | N | 1.1101 | 39.4971 | 62121.3391
[7 empty] | 17070 | 4195 | 917024 | 2012-12-29 19:45 | 2012-12-29 20:45 | 60 | 11kV | 120 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | LID 123911 A & B phase DOLF : 10 Amp Excluded OMS 917024 | December | 2012 | 2013Q2 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2012-12-29 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 16982 | 3443 | 917029 | 2012-12-29 20:22 | 2012-12-29 21:28 | 65.6833 | 11kV | 3018.4667 | 48 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 123912 A phase DOLF : 20 Amp excluded OMS 917029, 917030 | December | 2012 | 2013Q2 | 2013 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2012-12-29 | N | 62.8847 | N | 3 | N | N | 1.1101 | 39.4971 | 2205.8064
[7 empty] | 18535 | 20190 | 916985 | 2012-12-29 13:50 | 2012-12-30 09:37 | 1187 | 11kV | 1187 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123913 Single phase DOLF : 10 Amp Cust requested attendance at 9:00am 30/12/2013 Excluded OMS 916985 | December | 2012 | 2013Q2 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | UG | Not Veg | 2012-12-29 | N | 1187 | N | 3 | N | N | 1.1101 | 39.4971 | 867.4246
[7 empty] | 18149 | 16075 | 917122 | 2012-12-30 12:54 | 2012-12-30 17:15 | 261 | 11kV | 94914 | 910 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 123915 2 fault operations B phase Overcurrent, Earth fault tree lopping gone wrong! at sub 2975 Excluded oms 917122, 917124, 917133, 917139, 917140, 917141, 917142 | December | 2012 | 2013Q2 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2012-12-30 | N | 104.3011 | N | 4 | N | N | 1.1101 | 39.4971 | 69360.3517
[7 empty] | 18490 | 19824 | 917135 | 2012-12-30 17:15 | 2012-12-30 18:35 | 80 | 11kV | 160 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 123917 B phase DOLF : 10 Amp Excluded OMS 917135 | December | 2012 | 2013Q2 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | UG | Not Veg | 2012-12-30 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 17373 | 7681 | 917151 | 2012-12-30 17:42 | 2012-12-30 20:05 | 143 | 11kV | 3718 | 50 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | LID 123939 Overcurrent, Sectionaliser. Inadequate 11kV phase spacing at pole DN70037. J Frazer to notify M Judge. Refer to related records 918345, 918349, 917152, 917151, 917152 | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-12-30 | N | 74.36 | N | 4 | N | N | 1.1101 | 39.4971 | 2717.0047
[7 empty] | 17834 | 12587 | 917166 | 2012-12-30 19:36 | 2012-12-31 04:45 | 549 | 11kV | 124646 | 1731 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 123918 2 fault operations C phase Overcurrent Wires & pole fell down Marconi Rd, Morisset. Excluded OMS 917166 | December | 2012 | 2013Q2 | 2013 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2012-12-30 | N | 72.0081 | N | 4 | N | N | 1.1101 | 39.4971 | 91087.6204
[7 empty] | 18432 | 18942 | 917221 | 2012-12-31 08:32 | 2012-12-31 09:23 | 51.25 | 11kV | 307.5 | 6 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | LID 123920 Section isolated to install stay on sub pole 51163 and retire mains pole DN-70036 Refer to previous event 918339 T&R and 918345 | December | 2012 | 2013Q2 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2012-12-31 | N | 51.25 | N | 4 | N | N | 1.1101 | 39.4971 | 224.7119
[7 empty] | 17418 | 8122 | 917202 | 2012-12-31 07:56 | 2012-12-31 14:30 | 394 | 11kV | 7622 | 94 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC 44607 matcham - opened on IOC 11kV dpwn beyond USL 42162 in Wambina St see 917647 917648 | December | 2012 | 2013Q2 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2012-12-31 | N | 81.0851 | N | 4 | N | N | 1.1101 | 39.4971 | 5569.9328
[7 empty] | 17537 | 9051 | 917401 | 2012-12-31 16:45 | 2012-12-31 17:15 | 30 | 11kV | 2340 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 123924 Tree Branch on LV mains adjacent pole IR 71855 Eyre St East Maitland also refer to related record 917429 | December | 2012 | 2013Q2 | 2013 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | OH | Veg | 2012-12-31 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 1710.003
[7 empty] | 17627 | 10443 | 917472 | 2013-01-01 06:00 | 2013-01-01 08:30 | 150 | 11kV | 450 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 133927 B phase HV fuse at sub 70145 &. B Phase line fuse 74993 both blown. Also refer to oms report no 919161 and withdrawn OM S 917472. | January | 2013 | 2013Q3 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2013-01-01 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 17875 | 12898 | 917413 | 2012-12-31 16:13 | 2013-01-01 10:40 | 1107 | 11kV | 35879 | 231 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 123925 and 123926 Earth Fault and Sensitive Earth Fault Initial trip was on Earth fault (85A), SEF tripped as well, therefore no reclose. Subsequent attempts to close Sw 74080 failed on SEF (12A). Cause found to be faulty Tx 70312. | December | 2012 | 2013Q2 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2012-12-31 | N | 155.3203 | N | 4 | N | N | 1.1101 | 39.4971 | 26219.3149
[7 empty] | 16506 | 30 | 917506 | 2013-01-01 13:00 | 2013-01-01 16:35 | 215.2 | 11kV | 5380 | 25 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 133928 DOLF and assembly burnt up, replaced all 3 live line technique. | January | 2013 | 2013Q3 | 2013 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2013-01-01 | N | 215.2 | N | 5 | N | N | 1.1101 | 39.4971 | 3931.5453
[7 empty] | 17230 | 6278 | 917524 | 2013-01-01 15:48 | 2013-01-01 17:25 | 97 | 11kV | 44226 | 1213 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 133929 A phase Overcurrent Tree branch on 11kV mains cnr Sturt & Edinburgh St Singleton Excluded OMS 917524, 917525, 917529, 917530. | January | 2013 | 2013Q3 | 2013 | 513:48051 | 513:83493 | ZN00513/083493 | SINGLETON | OH | Veg | 2013-01-01 | N | 36.46 | N | 5 | N | N | 1.1101 | 39.4971 | 32319.0564
[7 empty] | 18142 | 16031 | 917583 | 2013-01-01 22:52 | 2013-01-02 01:04 | 132 | 11kV | 103865.2833 | 1220 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | At S129 Hunters Hill Panel 24 Tripped and reclosed on C phase OC Signals: 11kV Trip DOp reports that insulator on UGOH to S921 Romani is Cracked. Section of feeder from Ab1988 to AB3102 tee S921 Romani Ave has been isolated See OMS 917655 917660 917659 917585 917586 917584 917583 | January | 2013 | 2013Q3 | 2013 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Not Veg | 2013-01-01 | N | 85.1355 | N | 5 | N | N | 1.1101 | 39.4971 | 75901.6856
[7 empty] | 17901 | 13136 | 917590 | 2013-01-02 02:36 | 2013-01-02 04:46 | 130 | 11kV | 121420 | 934 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 133935 Failure or Defect - Conductor (Initial record - OMS 917590) tap burnt off at UGOH pole IS-62401 | January | 2013 | 2013Q3 | 2013 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2013-01-02 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 88730.1547
[7 empty] | 18451 | 19124 | 917646 | 2013-01-02 08:59 | 2013-01-02 10:00 | 61 | 11kV | 78385 | 1285 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn1850 Bass Hill 11kv OCB panel 13 "S-4312 Edgar Marion" feeder tripped reclosed tripped and locked out on: Relays: C phase INST + timmed, timing lockdown, lockout, EFI Field EFI's: Nil Signals: 11kv trip, Zone Earth, No.3 Tx Group Earth Remarks: UG fault. Suspect front line 11kv UG fault from Zn1850 Bass Hill Panel 13 to "SW-A" @ S-4312 Edgar Marion Related jobs: #917646, 917699, 918865 | January | 2013 | 2013Q3 | 2013 | ZN1850:PA13 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-02 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 57281.446
[7 empty] | 17806 | 12446 | 917553 | 2013-01-01 18:18 | 2013-01-02 11:40 | 1042 | 11kV | 9315 | 24 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 133933 1 fault operation Sensitive Earth Fault DOLF blown but did not drop at sub 73043. Field operator inspected sub, replaced DOLF. SO unable to dial into RAGCB, Field Operator not authorised to close Sw 46638. Muswellbrook on call contact requested to send Authorised person. TX REPLACED 2.1.13 MDV Excluded OMS 917553, 917555. | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-01-01 | N | 388.125 | N | 5 | N | N | 1.1101 | 39.4971 | 6807.1273
[7 empty] | 18462 | 19196 | 917910 | 2013-01-02 20:35 | 2013-01-03 04:45 | 490 | 11kV | 3920 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 133949 Also refer to 917930, Fuse Fatigue. Fuse size: 16 Amp Note customers of this sub also rang at 20:35 and 20:36 see OMS 917910 to report NS. unable to confirm if supply was restored prior to the 3rd call in from this sub on OMS 917930 at 02:28 on the 3.01.13. Changed start time to align with first phone call in | January | 2013 | 2013Q3 | 2013 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2013-01-02 | N | 490 | N | 3 | N | N | 1.1101 | 39.4971 | 2864.6204
[7 empty] | 16764 | 1732 | 920088 | 2013-01-03 08:00 | 2013-01-03 10:33 | 153 | 11kV | 306 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 133954 C phase DOLF : 10 Amp FUSE FATIGUE VOLTS 240, 240, 240. | January | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2013-01-03 | N | 153 | N | 1 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 18476 | 19516 | 918232 | 2013-01-04 03:29 | 2013-01-04 05:21 | 112 | 11kV | 6460 | 70 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn1290 Leightonfield 11kv OCB panel 9 "S-664 Christina Birmingham" feeder tripped on: Relays: Earth fault, Ceiling contactor, EFI Field EFI's: S664, S5764, S5923, S3119, S1288, CP311 Remarks: suspect 11kv feeder fault between CP-311 Marple Telecom and CP263 Colgate. Related jobs: #918232, 919051, 919064 | January | 2013 | 2013Q3 | 2013 | ZN1290:PA9 | ZN1290:PA9 | ZN01290/000009 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-04 | N | 92.2857 | N | 2 | N | N | 1.1101 | 39.4971 | 4720.7775
[7 empty] | 18408 | 18570 | 918547 | 2013-01-04 23:12 | 2013-01-05 00:02 | 50 | 11kV | 40750 | 815 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 133976 1 fault operation C phase Overcurrent; Sensitive Earth Fault; Earth fault Dead possum UGOH pole MQ-10137 Bundabah St, Karuah. Please inspect during daylight Reclose Relay has had 1 operation since 28/03/2012. Excluded OMS 918547 & 918549 | January | 2013 | 2013Q3 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2013-01-04 | N | 50 | N | 2 | N | N | 1.1101 | 39.4971 | 29778.8981
[7 empty] | 17396 | 7927 | 918560 | 2013-01-05 10:14 | 2013-01-05 10:55 | 41 | 11kV | 41 | 1 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 133981 Broken stay wire. Sub isolated for repair. Excluded OMS 918560 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-01-05 | N | 41 | N | 5 | N | N | 1.1101 | 39.4971 | 29.9616
[7 empty] | 17324 | 7294 | 918613 | 2013-01-05 15:19 | 2013-01-05 16:10 | 51 | 11kV | 32526 | 1001 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2310 Punchbowl, Panel 16 "Rossmore Ave" etc fdr tripped on; Translay, EFI Alarms; 11kv trip, tx3 GE, tx1,2,3,4,5 415v no volt, cl defect, battery defect Remarks: UG fdr fault from S2310 Punchbowl (Pnl 16) to S.278 Rossmore Ave (Sw/A) tee to S3585 Bonds Patrick (Tx2) Related jobs: #918613, 919336, 919334 | January | 2013 | 2013Q3 | 2013 | ZN2310:PA16 | ZN35800:PA4 | ZN35800/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-05 | N | 32.4935 | N | 5 | N | N | 1.1101 | 39.4971 | 23769.0414
[7 empty] | 16958 | 3306 | 918619 | 2013-01-05 15:52 | 2013-01-05 17:00 | 68 | 11kV | 4352 | 64 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.11084 Shakespeare Kipling - Centre phase HV fuse operated Fuse fatigue | January | 2013 | 2013Q3 | 2013 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2013-01-05 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 3180.3132
[7 empty] | 18240 | 16985 | 918614 | 2013-01-05 15:07 | 2013-01-05 18:30 | 203 | 11kV | 15834 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Panel 7 S4707 Tennyson Eastern At PT1059 Harrington Ave Centre Phase HDO fuse blown Cause: Trees on OH mains O/S 2 Harrington Ave 918614 918633 918911 CC1: 22-"Refer to SOp" | January | 2013 | 2013Q3 | 2013 | ZN1673:PA7 | ZN1673:PA7 | ZN01673/000007 | KU-RING-GAI | OH | Veg | 2013-01-05 | N | 203 | N | 5 | N | N | 1.1101 | 39.4971 | 11571.0202
[7 empty] | 18173 | 16349 | 918642 | 2013-01-05 18:15 | 2013-01-05 19:35 | 80 | 11kV | 2400 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 133983 nil protection operation rec opened by aop for safety on report of location by RFS. Tree branch on OHM brought mains down to ground level adj pole 8e70006 and started a grass fire 20m x 2.5m out by RFS. Excluded OMS 918642 & 918644 | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-01-05 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 16614 | 751 | 918680 | 2013-01-06 05:45 | 2013-01-06 07:15 | 90 | 11kV | 360 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 133984 Single phase DOLF : 10 Amp. Readings as left 63A @ 245V Excluded OMS 918680. | January | 2013 | 2013Q3 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | UG | Not Veg | 2013-01-06 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 16903 | 2919 | 918679 | 2013-01-06 05:39 | 2013-01-06 08:25 | 166 | 11kV | 1660 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13684 Tall Timbers Karoola - Roadside HDO operated Fuse faitgue | January | 2013 | 2013Q3 | 2013 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Not Veg | 2013-01-06 | N | 166 | N | 6 | N | N | 1.1101 | 39.4971 | 1213.079
[7 empty] | 18063 | 15444 | 918696 | 2013-01-06 08:21 | 2013-01-06 09:02 | 41 | 11kV | 3046 | 80 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 630 Mascot Panel #34 "Bradford St" fdr tripped on Earth Fault EFI @ S106-S4002-S6207-S2994-S644 11kv trip-zone earh - #6 Group Earth Remarks: Suspect UG fault between S644 Raldoo & S35380 Dunning Hayes Related jobs: #918696, 919443, 919440 | January | 2013 | 2013Q3 | 2013 | ZN630:PA34 | ZN630:PA34 | ZN00630/000034 | SYDNEY | UG | Not Veg | 2013-01-06 | N | 38.075 | N | 6 | N | N | 1.1101 | 39.4971 | 2225.927
[7 empty] | 17837 | 12614 | 918729 | 2013-01-06 11:45 | 2013-01-06 12:45 | 60 | 11kV | 48343 | 912 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills 11kV Feeder Panel 26 Tripped reclosed tripped and locked out Relays: A and C phasxe IOC and OC, Timing and Lockout Cause Tree branch on mains between AB143 and S6408 Sefton Kooringal See OMS 919907 919908 918729 918737 | January | 2013 | 2013Q3 | 2013 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2013-01-06 | N | 53.0077 | N | 6 | N | N | 1.1101 | 39.4971 | 35327.6385
[7 empty] | 18059 | 15413 | 918761 | 2013-01-06 15:12 | 2013-01-06 15:55 | 43 | 11kV | 44905 | 1055 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S72 Fivedock Panel 26 "Paramatta Davids etc" 11kv feeder tripped on; EF, EFI Alarms; 11kv, ZE, Tx2 GE Field EFI's operated at; S46567, S1518 Remarks: UF fault. From S1518 St Davids Rd (Sw/B) to S.4584 Nicholls Ave (Sw/A) Related jobs: #918767, 918761, 919265, 919266, 919264 | January | 2013 | 2013Q3 | 2013 | ZN72:PA26 | ZN35555:PA13 | ZN35555/000013 | INNER WEST | UG | Not Veg | 2013-01-06 | N | 42.564 | N | 6 | N | N | 1.1101 | 39.4971 | 32815.2495
[7 empty] | 17518 | 8958 | 918693 | 2013-01-06 15:19 | 2013-01-06 16:30 | 71 | 11kV | 8804 | 124 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13781 Trafalgar Donals - Centre phase HDO found broken Centre restored via LV // link 35098 35849 36678 35067 No load reading taken due to condemmed pole see 918890 918892 | January | 2013 | 2013Q3 | 2013 | ZN12640:PA2 | ZN12660:PA16 | ZN12660/000016 | CENTRAL COAST | OH | Not Veg | 2013-01-06 | N | 71 | N | 6 | N | N | 1.1101 | 39.4971 | 6433.7035
[7 empty] | 17153 | 5069 | 919535 | 2013-01-07 08:29 | 2013-01-07 10:10 | 101 | 11kV | 909 | 9 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Link | Unplanned | Unselected | N | LID 133992 Farmer reported glowing 11kv link operator opened and jammed closed link 75247. Can local staff please confirm this link does not need any maintenence to prevent it from coming loose again. No protection operated. | January | 2013 | 2013Q3 | 2013 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2013-01-07 | N | 101 | N | 2 | N | N | 1.1101 | 39.4971 | 664.2704
[7 empty] | 17668 | 10997 | 918818 | 2013-01-07 09:49 | 2013-01-07 11:42 | 113 | 11kV | 26739 | 255 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 133988 B Phase No protection operated, blowing B phase 11kV tapping at pole BI-50207. Excluded OMS #918818, 918820, 918821 AND 918819. | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2013-01-07 | N | 104.8588 | N | 2 | N | N | 1.1101 | 39.4971 | 19540.0725
[7 empty] | 18426 | 18889 | 919218 | 2013-01-08 01:21 | 2013-01-08 05:20 | 239 | 11kV | 10277 | 43 | HV | Vandalism | 3rd Party Impact | UGOH | Unplanned | Unselected | N | LID 133998 Vandels lighting fire at UGOH pole GS-60031 feeding sub 47656. UGOH damaged & isolated ready to repair. Excluded oms-919218. | January | 2013 | 2013Q3 | 2013 | 507:80926 | 507:80926 | ZN00507/080926 | CESSNOCK | UG | Not Veg | 2013-01-08 | N | 239 | N | 28 | Y | Y | 1.1101 | 39.4971 | 7510.1285
[7 empty] | 16874 | 2510 | 919221 | 2013-01-08 05:01 | 2013-01-08 06:40 | 99 | 11kV | 87464 | 1050 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.3 tripped / reclosed / tripped & locked out on : A phase IOC & EF Suspect UG cable fault between S11948 and S63152 see 919296 919317 919319 919316 | January | 2013 | 2013Q3 | 2013 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | UG | Not Veg | 2013-01-08 | N | 83.299 | N | 28 | Y | Y | 1.1101 | 39.4971 | 63916.1114
[7 empty] | 18197 | 16571 | 919220 | 2013-01-08 04:20 | 2013-01-08 09:10 | 290 | 11kV | 7540 | 26 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn35370 Galston Panel 8 PT655 Arcadia Carrs Roadside 11kV HVDO Operated Cause: Possum Found at the base of Pole See OMS 919946 919220 | January | 2013 | 2013Q3 | 2013 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2013-01-08 | N | 290 | N | 28 | Y | Y | 1.1101 | 39.4971 | 5510.0096
[7 empty] | 16551 | 326 | 919229 | 2013-01-08 06:59 | 2013-01-08 10:02 | 183 | 11kV | 21800 | 120 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 133999 1 fault operation - reclose disabled TOBAN C phase Overcurrent patrolled. found large tree branch on ground near mains. pole no. GV-97008. no damage. | January | 2013 | 2013Q3 | 2013 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2013-01-08 | N | 181.6667 | N | 28 | Y | Y | 1.1101 | 39.4971 | 15930.797
[7 empty] | 17152 | 5067 | 919227 | 2013-01-08 06:26 | 2013-01-08 11:07 | 281 | 11kV | 15219 | 59 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Hot >35C | N | LID 134001 1 fault operation B phase Overcurrent Total fire ban - A/R off. Trip I = 275A on Bph, 273A on Cph. Patrolled each section before energising. Possible tree problem near pole 8N-80302. (branch cut away) Excluded OMS 919227 | January | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2013-01-08 | N | 257.9492 | N | 28 | Y | Y | 1.1101 | 39.4971 | 11121.5963
[7 empty] | 17814 | 12485 | 919285 | 2013-01-08 09:20 | 2013-01-08 11:31 | 131 | 11kV | 25761 | 315 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zone 630 Mascot 11kv Panel 27 C/B 'Sub 3379 O'Riordan Miles' tripped on: Relays: Earth Fault, (EFI defective) Signals: Group Earth, Zone Earth. Field EFI's, S3379, S5743 EFI faulty. Remarks: 11kv U/G feeder fault from Sub 5743 Kent Church (Sw/B) to Sub 35553 Ricketty Kent 2 (Sw/A). Note: Unable to access Sub 5743 chain was cut by T/Con. At Sub 5743 Kent Church EFI was faulty. Due to false indication P43 tripped at St Peters when attempting to restore S5743 fromS35553 Related jobs: #923276 | January | 2013 | 2013Q3 | 2013 | ZN630:PA27 | ZN630:PA27 | ZN00630/000027 | BAYSIDE | UG | Not Veg | 2013-01-08 | N | 81.781 | N | 28 | Y | Y | 1.1101 | 39.4971 | 18825.379
[7 empty] | 16622 | 790 | 919353 | 2013-01-08 10:49 | 2013-01-08 13:00 | 131 | 11kV | 3878 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44607 matcham North tripped on : Earth Fault Tree branch brought down centre phase adjacent PT12878 see 919928 919929 | January | 2013 | 2013Q3 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2013-01-08 | N | 41.2553 | N | 28 | Y | Y | 1.1101 | 39.4971 | 2833.928
[7 empty] | 18359 | 17924 | 919451 | 2013-01-08 12:54 | 2013-01-08 14:10 | 76 | 11kV | 152 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Hot >35C | N | LID 134003 C phase DOLF : 31 Amp TX Volts: Aph - 251V, Bph - 253V, Cph - 251V TX Load: Aph - 61A, Bph - 58A, Cph - 84A Excluded OMS No. 919451 | January | 2013 | 2013Q3 | 2013 | 512:48046 | 512:83741 | ZN00512/083741 | CESSNOCK | UG | Not Veg | 2013-01-08 | N | 76 | N | 28 | Y | Y | 1.1101 | 39.4971 | 111.0771
[7 empty] | 17667 | 10991 | 919396 | 2013-01-08 11:50 | 2013-01-08 15:00 | 190 | 11kV | 132148 | 1537 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | At S10999 Kogarah Pa17 tripped reclosed tripped and locked out on Relays: 51N, Earth Fault Check and Reclose Timing Cause: Between AB31256 and S10297 tee PT10502 bond burnt off. See OMS 920200 920201/204/206/203 919396 | January | 2013 | 2013Q3 | 2013 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2013-01-08 | N | 85.9779 | N | 28 | Y | Y | 1.1101 | 39.4971 | 96569.8607
[7 empty] | 18252 | 17079 | 919468 | 2013-01-08 13:17 | 2013-01-08 15:00 | 103 | 11kV | 72907 | 2099 | HV | Fire (non-electrical) | Adverse Weather/Environment | Pole | Unplanned | Unselected | N | At S.15008 Harbord, Panel 9 Fdr CB tripped on B phase OC, earth fault,, efi, reclose timer and lockout relays, zone earth, 11kV trip. Pole fire O/S #3 Libra Cres. Allambie Hts. Supply to S.16026 via LV// | January | 2013 | 2013Q3 | 2013 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2013-01-08 | N | 34.7342 | N | 28 | Y | Y | 1.1101 | 39.4971 | 53278.2852
[7 empty] | 18046 | 15118 | 919508 | 2013-01-08 14:13 | 2013-01-08 15:30 | 77 | 11kV | 36541 | 683 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At S10996 Rockdale Panel 19 Tripped reclosed tripped and locked out on Cphase IOC, EFI, Lockout and Timer Cause: UGOH fault adjacent to S10953 See OMS 920194 920195 920196 | January | 2013 | 2013Q3 | 2013 | ZN10996:PA19 | ZN10998:PA31 | ZN10998/000031 | BAYSIDE | Unknown | Unknown | 2013-01-08 | N | 53.5007 | N | 28 | Y | Y | 1.1101 | 39.4971 | 26703.085
[7 empty] | 17383 | 7793 | 919514 | 2013-01-08 14:22 | 2013-01-08 16:40 | 138 | 11kV | 3450 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | At S35000 Mowbray Rd 400A fuse blown on A phase of distributor 4. Cause not ascertained for outage See OMS 920084 919514 919561 919601 | January | 2013 | 2013Q3 | 2013 | ZN80:PA22 | ZN80:PA22 | ZN00080/000022 | LANE COVE | OH | Veg | 2013-01-08 | N | 138 | N | 28 | Y | Y | 1.1101 | 39.4971 | 2521.1582
[7 empty] | 17460 | 8401 | 919505 | 2013-01-08 14:07 | 2013-01-08 17:20 | 193 | 11kV | 167670 | 1119 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn.12610 long Jetty Pnl.18 tripped on: Earth Fault, EFI Blown bond on 11kB oH near AB 41762 - @ S11788 Waratah Marlowe Sw/B endbox defective. DOp advises carbon around RMI see 919931 919932 919936 919940 | January | 2013 | 2013Q3 | 2013 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2013-01-08 | N | 149.8391 | N | 28 | Y | Y | 1.1101 | 39.4971 | 122528.2906
[7 empty] | 16750 | 1608 | 919611 | 2013-01-08 16:21 | 2013-01-08 17:27 | 66 | 11kV | 77154 | 1169 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | At Zn9252 Jannali 11kV Pa2 feeder has tripped on A phase IOC, Lockout and Timer Signals: Battery Defect and 11kV trip Cause NOt ascertained for outage See OMS 920161 920162 919611 | January | 2013 | 2013Q3 | 2013 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Veg | 2013-01-08 | N | 66 | N | 28 | Y | Y | 1.1101 | 39.4971 | 56381.8675
[7 empty] | 18042 | 14999 | 919592 | 2013-01-08 15:51 | 2013-01-08 18:00 | 129 | 11kV | 64961 | 619 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Zn.12600 Lisarow Pnl.1 tripped on: IOC and EFI Weather related - extreme heat - no overload on panel see 920024 920026 920029 920023 Gis 920033 920036 | January | 2013 | 2013Q3 | 2013 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2013-01-08 | N | 104.9451 | N | 28 | Y | Y | 1.1101 | 39.4971 | 47471.5828
[7 empty] | 17655 | 10839 | 919586 | 2013-01-08 15:39 | 2013-01-08 18:10 | 151 | 11kV | 146050 | 1591 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.22 tripped on: OC and EF and EFI UGOH Fault short circuit - 2 UGOH faults on feeder - UGOH near AB44856, UGOH near REC 46529 see 920008 920009 920010 920014 | January | 2013 | 2013Q3 | 2013 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | Unknown | Unknown | 2013-01-08 | N | 91.7976 | N | 28 | Y | Y | 1.1101 | 39.4971 | 106729.0323
[7 empty] | 17731 | 11821 | 919612 | 2013-01-08 16:22 | 2013-01-08 18:29 | 127 | 11kV | 191262 | 1506 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | Zn.12580 Erina - Pnl.10 tripped on IOC A Phase IOC, C phase, EFI Bird found at first UGOH below Sub18183 see 920049 920048 | January | 2013 | 2013Q3 | 2013 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Not Veg | 2013-01-08 | N | 127 | N | 28 | Y | Y | 1.1101 | 39.4971 | 139768.6283
[7 empty] | 17494 | 8749 | 919664 | 2013-01-08 17:42 | 2013-01-08 18:30 | 48 | 11kV | 48 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134006 C phase DOLF : 10 Amp Customer Volts: Aph - 254V, Bph - 255V, Cph - 254V Excluded OMS No. 919664 | January | 2013 | 2013Q3 | 2013 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2013-01-08 | N | 48 | N | 28 | Y | Y | 1.1101 | 39.4971 | 35.077
[7 empty] | 18101 | 15805 | 919662 | 2013-01-08 17:38 | 2013-01-08 19:15 | 97 | 11kV | 8147.0667 | 84 | HV | Overload | Utility Process Issue | Fuse | Unplanned | Unselected | N | Suspected overload in hot conditions caused the centre phase HDO fuse to operate at PT.15410 | January | 2013 | 2013Q3 | 2013 | ZN15011:PA6 | ZN15011:PA4 | ZN15011/000004 | NORTHERN BEACHES | OH | Not Veg | 2013-01-08 | N | 96.9889 | N | 28 | Y | Y | 1.1101 | 39.4971 | 5953.636
[7 empty] | 17266 | 6756 | 919532 | 2013-01-08 14:30 | 2013-01-08 19:22 | 292 | 11kV | 76786.35 | 567 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | ZN 9035 Caringbah - Pnl 1 - Earth Fault, EFIs. RMI failed dramatically at S9031 Paraweena Aitken No. 2. | January | 2013 | 2013Q3 | 2013 | ZN9035:PA1 | ZN9035:PA1 | ZN09035/000001 | SUTHERLAND | Unknown | Not Veg | 2013-01-08 | N | 135.4257 | N | 28 | Y | Y | 1.1101 | 39.4971 | 56113.1998
[7 empty] | 16528 | 143 | 919698 | 2013-01-08 18:16 | 2013-01-08 19:42 | 86 | 11kV | 110020 | 1490 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15006 Dee Why West, Panel 1 Fdr CB tripped on earth leakage, fault check, efi, 11kV trip due to cable failure | January | 2013 | 2013Q3 | 2013 | ZN15006:PA1 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | UG | Not Veg | 2013-01-08 | N | 73.8389 | N | 28 | Y | Y | 1.1101 | 39.4971 | 80399.371
[7 empty] | 16552 | 327 | 919512 | 2013-01-08 14:18 | 2013-01-08 19:50 | 332 | 11kV | 5312 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13326 Milina Coachwood - HV fuse assembly defective - centre phase restored via LV lk 16979 | January | 2013 | 2013Q3 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2013-01-08 | N | 332 | N | 28 | Y | Y | 1.1101 | 39.4971 | 3881.8529
[7 empty] | 17601 | 9980 | 919674 | 2013-01-08 17:54 | 2013-01-08 20:04 | 130 | 11kV | 125320 | 964 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | ZN 171 Arncliffe - Pnl 11 'Station Wollongong' - Section beyond S 10427 SW/A. UGOH failed in service and became open circuit adjacent to S 10427 Fripp Lorraine SW/A. Restored through open point. | January | 2013 | 2013Q3 | 2013 | ZN10990:PA11 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | Unknown | Unknown | 2013-01-08 | N | 130 | N | 28 | Y | Y | 1.1101 | 39.4971 | 91580.1597
[7 empty] | 17712 | 11675 | 919734 | 2013-01-08 18:51 | 2013-01-08 20:28 | 97 | 11kV | 84585 | 905 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn3922 Drummoyne 11kv Panel 22 "The Parade etc" feeder has tripped. Relays: 50TA, 50TN(EFC) Signals: 11kv trip EFI's: Nil Remarks: Suspected UG fault between Zn 3922 Drummoyne 11kv Panel 22, Sw/A @ Sub 2076 Gears Ave, Sw/A @ Sub 1593 The Parade and Sw/B @ Sub 7804 Point Av Related jobs: #919734, 919925, 919924 | January | 2013 | 2013Q3 | 2013 | ZN3922:PA22 | ZN3922:PA22 | ZN03922/000022 | CANADA BAY | UG | Not Veg | 2013-01-08 | N | 93.4641 | N | 28 | Y | Y | 1.1101 | 39.4971 | 61812.2232
[7 empty] | 18207 | 16648 | 919761 | 2013-01-08 19:20 | 2013-01-08 21:32 | 132 | 11kV | 324978 | 2713 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn3922 Drummoyne 11kv Panel 5 "Byrnes Manning etc" feeder has tripped Relays: B phase timed, EFI and FC Signals: 11kv trip EFI's: S36163, S7583, S7681, S7682, S7683, S8614 Abnormal Switching: UG fault between Sw/B @ S48988 Little Arthur and Sw/A @ S1460 Elliot Sw/B closed @ S2134 Barr St Remarks: Suspected UG cable fault between Sw/A @ Sw/B @ Sub 8614 Yara Margaret and Sub 5302 Wullumay Waragul No.1 Related jobs: #919761, 919957, 919955 | January | 2013 | 2013Q3 | 2013 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2013-01-08 | N | 119.7855 | N | 28 | Y | Y | 1.1101 | 39.4971 | 237484.3372
[7 empty] | 18380 | 18187 | 919665 | 2013-01-08 17:44 | 2013-01-08 21:50 | 246 | 11kV | 135917 | 1306 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12690 berkeley Avle Pnl.12 tripped on: A & C phase overcurrent Note: Reclsoer was Non-auto on this feeder due to total fire ban Tree hit mains on pacific Hwy near Tambelin Ave causing grass fire near Pole WY2585 - also causing bond to burnt off feeder side of LK42802. see 920063 920065 920066 920067 | January | 2013 | 2013Q3 | 2013 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2013-01-08 | N | 104.0712 | N | 28 | Y | Y | 1.1101 | 39.4971 | 99324.1347
[7 empty] | 17290 | 6993 | 919515 | 2013-01-08 14:20 | 2013-01-08 21:50 | 450 | 11kV | 190689.1 | 1835 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.36300 Balgowlah Nth, 11kV Panel 19 Fdr CB tripped on earth fault, efi, fault check, #1 Tx earth fault check. Field efi's down at S.16827, S.16064, S.49927 and S.16928. UG cable fault adjacent to S.16514 (O/S #4B Alto Ave) | January | 2013 | 2013Q3 | 2013 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | UG | Not Veg | 2013-01-08 | N | 103.9178 | N | 28 | Y | Y | 1.1101 | 39.4971 | 139349.9699
[7 empty] | 16527 | 142 | 919446 | 2013-01-08 12:39 | 2013-01-09 08:10 | 1171 | 11kV | 139588 | 1226 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN 9900 Menai - Pnl 1 - Tripped/Reclosed/Tripped and locked out Left EF, Left EFI. Suspect UG cable fault in area from S9428 to S9020 to S9480 to AB35014. | January | 2013 | 2013Q3 | 2013 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2013-01-08 | N | 113.8564 | N | 28 | Y | Y | 1.1101 | 39.4971 | 102006.7933
[7 empty] | 17993 | 14163 | 919892 | 2013-01-09 06:40 | 2013-01-09 09:41 | 181 | 11kV | 8998 | 59 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134015 1 fault operation Overcurrent | January | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2013-01-09 | N | 152.5085 | N | 5 | N | N | 1.1101 | 39.4971 | 6575.473
[7 empty] | 17992 | 14160 | 919878 | 2013-01-09 03:35 | 2013-01-09 12:30 | 535 | 11kV | 27182 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134014 1 fault operation TFB no reclose. OHM down at pole GW-90322 repairs complete. Excluded oms-919878 & 920403 | January | 2013 | 2013Q3 | 2013 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Not Veg | 2013-01-09 | N | 485.3929 | N | 5 | N | N | 1.1101 | 39.4971 | 19863.8039
[7 empty] | 16793 | 2001 | 919975 | 2013-01-09 09:19 | 2013-01-09 12:40 | 201 | 11kV | 4221 | 21 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At Sub 36019 Roseby St No.3 The 11kv Fuse switch has tripped with B phase fuse blown. Fuse 80A OHFMA80 Remarks: Tx failure. Transformer short circuit on B phase Related jobs: #919975, 920025, 920371 | January | 2013 | 2013Q3 | 2013 |  |  |  |  | UG | Not Veg | 2013-01-09 | N | 201 | N | 5 | N | N | 1.1101 | 39.4971 | 3084.5823
[7 empty] | 17617 | 10269 | 920085 | 2013-01-09 12:09 | 2013-01-09 17:55 | 346 | 11kV | 57246 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134025 2 fault operations A phase Overcurrent opened by SO after multiple trip & recloses. patrolled by M.judge and J.frazer Branch found touching mains at pole DP-30601. Feeder tripped after branch was removed at 1454hrs. Detailed patrol required. Excluded OMS no. 920085 & 920173 | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2013-01-09 | N | 227.1667 | N | 5 | N | N | 1.1101 | 39.4971 | 41833.6883
[7 empty] | 18366 | 18049 | 920263 | 2013-01-09 16:56 | 2013-01-09 22:45 | 349 | 11kV | 698 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134030 A & C phase DOLF : 3 Amp Tx has oil small oil leak please check in day light. Excluded oms-920263. | January | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-01-09 | N | 349 | N | 5 | N | N | 1.1101 | 39.4971 | 510.0778
[7 empty] | 16926 | 3080 | 920320 | 2013-01-10 02:46 | 2013-01-10 04:15 | 89 | 11kV | 8366 | 94 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT13061 Garland Wyong - roadside and middle HDOs blown Possum found on PT13061 | January | 2013 | 2013Q3 | 2013 | ZN12610:PA17 | ZN12610:PA23 | ZN12610/000023 | CENTRAL COAST | OH | Not Veg | 2013-01-10 | N | 89 | N | 7 | N | N | 1.1101 | 39.4971 | 6113.626
[7 empty] | 16799 | 2037 | 920412 | 2013-01-10 11:00 | 2013-01-10 11:10 | 10 | 11kV | 50 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134034 B phase DOLF : 20 Amp Excluded OMS 920412 | January | 2013 | 2013Q3 | 2013 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2013-01-10 | N | 10 | N | 7 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 17863 | 12829 | 920316 | 2013-01-10 00:12 | 2013-01-10 13:17 | 785 | 11kV | 80237 | 721 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9301 Kurnell - Pnl 8 - Earth Fault, Lock out, fault check, timing, EFI. UG fault in feeder from AB 35123 to S 9724 SW/B to PT 9093. DOp checked EFI at UGOH near AB 35123 but found EFI defective. PT 9093 Kurnell Park still off see 920435. | January | 2013 | 2013Q3 | 2013 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | UG | Not Veg | 2013-01-10 | N | 111.2857 | N | 7 | N | N | 1.1101 | 39.4971 | 58634.833
[7 empty] | 17181 | 5557 | 920538 | 2013-01-10 12:29 | 2013-01-10 13:57 | 88 | 11kV | 89040 | 1152 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 134037 solated faulty cable between Sw 28418 & Sw 24530. Excluded oms # 920538 | January | 2013 | 2013Q3 | 2013 | 213:33770 | 213:33770 | ZN00213/033770 | NEWCASTLE | UG | Not Veg | 2013-01-10 | N | 77.2917 | N | 7 | N | N | 1.1101 | 39.4971 | 65067.8058
[7 empty] | 16995 | 3524 | 920595 | 2013-01-10 14:04 | 2013-01-10 14:35 | 31 | 11kV | 8680 | 280 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 16 - Part of distributor beyond AB 35860. Bond burnt off AB 35860. | January | 2013 | 2013Q3 | 2013 | ZN9037:PA16 | ZN9037:PA16 | ZN09037/000016 | SUTHERLAND | OH | Not Veg | 2013-01-10 | N | 31 | N | 7 | N | N | 1.1101 | 39.4971 | 6343.088
[7 empty] | 17734 | 11838 | 920416 | 2013-01-10 09:46 | 2013-01-10 15:10 | 324 | 11kV | 27703 | 194 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | RC 45013 - tripped / reclosed and locked out on: O/C Tree trimmer felled a tree onto mains O/S 5900 Wisemans Ferry Rd Gunderson see 922138 922139 922142 922141 | January | 2013 | 2013Q3 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2013-01-10 | N | 142.799 | N | 7 | N | N | 1.1101 | 39.4971 | 20244.5353
[7 empty] | 17914 | 13252 | 920619 | 2013-01-10 15:02 | 2013-01-10 16:55 | 113 | 11kV | 678 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134044 B phase DOLF : 31 Amp fuse fatigue Excluded OMS 920619 | January | 2013 | 2013Q3 | 2013 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2013-01-10 | N | 113 | N | 7 | N | N | 1.1101 | 39.4971 | 495.4624
[7 empty] | 16996 | 3537 | 920727 | 2013-01-11 07:24 | 2013-01-11 09:55 | 151 | 11kV | 7091 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | REC 45015 - tripped on OC & IOC Cause not asctertained - suspect tree brnach touched OH mains. Tree trimming required see 922160 922159 | January | 2013 | 2013Q3 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-01-11 | N | 126.625 | N | 9 | N | N | 1.1101 | 39.4971 | 5181.8937
[7 empty] | 17952 | 13676 | 920781 | 2013-01-11 09:13 | 2013-01-11 10:27 | 74 | 11kV | 118556 | 1860 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At Zn3472 Sefton Panel 31 "Stephenson Auburn" 11kv feeder has tripped. Relays: SEL Signals: 11kv trip EFIs: Nil Remarks: burnt bond @ AB 513 Related jobs: #920806, 920802, 920797, 920787, 920781, 922785, 922783, 922781, 922779 | January | 2013 | 2013Q3 | 2013 | ZN3472:PA31 | ZN35900:PA4 | ZN35900/000004 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-01-11 | N | 63.7398 | N | 9 | N | N | 1.1101 | 39.4971 | 86637.228
[7 empty] | 17807 | 12455 | 920877 | 2013-01-11 12:01 | 2013-01-11 20:25 | 504 | 11kV | 77462 | 283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Hot >35C | N | LID 134054 3 fault operations Single phase Earth Fault Tree branch fell bringing down mains. Motorcycle Accident. Motorcyclist died at scene. Repairs effected after police investigation completed. Excluded OMS# 920877 & 921047 | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-01-11 | N | 273.7173 | N | 9 | N | N | 1.1101 | 39.4971 | 56606.9449
[7 empty] | 18498 | 19878 | 920793 | 2013-01-11 09:46 | 2013-01-11 20:50 | 664 | 11kV | 664 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | LID 134053 A & B phase DOLF : 20 Amp Trans failed. replaced 315kVA with 400kVA. 20A dolfs installed. SAO required. Excluded OMS# 920793 | January | 2013 | 2013Q3 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | UG | Not Veg | 2013-01-11 | N | 664 | N | 9 | N | N | 1.1101 | 39.4971 | 485.2316
[7 empty] | 16902 | 2911 | 921057 | 2013-01-11 18:47 | 2013-01-11 20:50 | 123.3333 | 11kV | 5303.3333 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134055 C phase DOLF : 16 Amp | January | 2013 | 2013Q3 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2013-01-11 | N | 123.3333 | N | 9 | N | N | 1.1101 | 39.4971 | 3875.5196
[7 empty] | 17950 | 13620 | 921056 | 2013-01-11 18:46 | 2013-01-11 22:30 | 224 | 11kV | 672 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134057 Single phase Dist fuse : 100 Amp Readings as left 40A @ 240V. Excluded OMS 921056. | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-01-11 | N | 224 | N | 9 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 17270 | 6797 | 921073 | 2013-01-11 20:08 | 2013-01-11 23:00 | 172 | 11kV | 860 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 134058 Single phase Replace broken 11kV dropper lead From LLC to DOLF Readings as left 16A @ 246V. Excluded OMS 921073, 921077. | January | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-01-11 | N | 172 | N | 9 | N | N | 1.1101 | 39.4971 | 628.4626
[7 empty] | 17800 | 12402 | 921087 | 2013-01-11 22:42 | 2013-01-12 00:20 | 98 | 11kV | 29509 | 368 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | Zn.12690 Pnl.16 tripped on : A & B phase timed Overcurrent Cause not ascertained see 922221 922223 922222 922224 | January | 2013 | 2013Q3 | 2013 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | UG | Not Veg | 2013-01-11 | N | 80.1875 | N | 9 | N | N | 1.1101 | 39.4971 | 21564.3068
[7 empty] | 18184 | 16441 | 921081 | 2013-01-11 21:45 | 2013-01-12 03:20 | 335 | 11kV | 8845 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134060 Single phase Sectionaliser A phase Auto Link 47356 operated. Fdr patrolled & no fault found. Sw 42064 Laguna RAGCB Reclose was off when dialed up in WSOS. Also see report134054 Excluded OMS 921081. | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-01-11 | N | 327.5926 | N | 9 | N | N | 1.1101 | 39.4971 | 6463.6651
[7 empty] | 17990 | 14147 | 921118 | 2013-01-12 07:30 | 2013-01-12 09:15 | 105 | 11kV | 525 | 5 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134065 Active tree services to remove tree from mains Excluded OMS 92118 | January | 2013 | 2013Q3 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2013-01-12 | N | 105 | N | 35 | Y | Y | 1.1101 | 39.4971 | 383.6545
[7 empty] | 18296 | 17427 | 921168 | 2013-01-12 12:33 | 2013-01-12 14:20 | 107 | 11kV | 6527 | 61 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT11146 Newell Wallace - Centre phase HDO failed HDo mechanical failure - restored via LV //. LKs 21426 19020 19914 | January | 2013 | 2013Q3 | 2013 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2013-01-12 | N | 107 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4769.7391
[7 empty] | 17673 | 11099 | 921088 | 2013-01-12 01:00 | 2013-01-12 14:45 | 825 | 11kV | 825 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 134059 Sub isolated as fire believed to have started at base of sub pole. White ant treated pole. Crew & EWP to be arranged to investigate in daylight. Excluded OMS 921088. | January | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2013-01-12 | N | 825 | N | 35 | Y | Y | 1.1101 | 39.4971 | 602.8857
[7 empty] | 18052 | 15351 | 921208 | 2013-01-12 15:15 | 2013-01-12 16:46 | 91 | 11kV | 143598 | 1578 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.847 Hornsby Pnl.18 tripped / reclosed / tripped / locked out on A & C phase inst & timed O/C Branch on 11kV mains near PT2433. | January | 2013 | 2013Q3 | 2013 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Veg | 2013-01-12 | N | 91 | N | 35 | Y | Y | 1.1101 | 39.4971 | 104937.183
[7 empty] | 17723 | 11754 | 921175 | 2013-01-12 13:20 | 2013-01-12 17:30 | 250 | 11kV | 4000 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 134069 No protection operated as burnt 11kV tapping. Tapping was burnt off beyond ABS 4626. Excluded OMS # 921175, 921117 & 921176. | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-01-12 | N | 250 | N | 35 | Y | Y | 1.1101 | 39.4971 | 2923.082
[7 empty] | 17910 | 13197 | 921179 | 2013-01-12 13:44 | 2013-01-12 17:45 | 241 | 11kV | 241 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134080 C phase DOLF : 10 Amp. Excluded OMS 921179 | January | 2013 | 2013Q3 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2013-01-12 | N | 241 | N | 35 | Y | Y | 1.1101 | 39.4971 | 176.1157
[7 empty] | 18388 | 18281 | 921246 | 2013-01-12 17:47 | 2013-01-12 18:41 | 54 | 11kV | 16794 | 311 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134076 1 fault operation B & C phase Overcurrent Reclose off due to total fire ban | January | 2013 | 2013Q3 | 2013 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2013-01-12 | N | 54 | N | 35 | Y | Y | 1.1101 | 39.4971 | 12272.5599
[7 empty] | 17651 | 10795 | 922249 | 2013-01-12 17:54 | 2013-01-12 18:47 | 53 | 11kV | 20087 | 379 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134079 1 fault operation A & B phase Overcurrent Reclose off due to total fire ban | January | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2013-01-12 | N | 53 | N | 35 | Y | Y | 1.1101 | 39.4971 | 14678.9871
[7 empty] | 17701 | 11550 | 921230 | 2013-01-12 17:16 | 2013-01-12 18:59 | 103 | 11kV | 10506 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134074 1 fault operation A & B phase Instantaneous Overcurrent Reclose off due to total fire ban | January | 2013 | 2013Q3 | 2013 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2013-01-12 | N | 103 | N | 35 | Y | Y | 1.1101 | 39.4971 | 7677.4749
[7 empty] | 17873 | 12883 | 921255 | 2013-01-12 17:53 | 2013-01-12 19:03 | 70 | 11kV | 5530 | 79 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134077 1 fault operation Overcurrent Reclose off due to total fire ban. | January | 2013 | 2013Q3 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2013-01-12 | N | 70 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4041.1609
[7 empty] | 18425 | 18870 | 921244 | 2013-01-12 17:44 | 2013-01-12 19:17 | 93 | 11kV | 23436 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134072 2 fault operations A phase Overcurrent No cause foumd, suspect outage was due to the electrical storm. Excluded OMS # 921245. | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2013-01-12 | N | 93 | N | 35 | Y | Y | 1.1101 | 39.4971 | 17126.3376
[7 empty] | 17829 | 12543 | 921257 | 2013-01-12 18:05 | 2013-01-12 20:15 | 130 | 11kV | 14922 | 157 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134073 1 fault operation 3 phase Sensitive Earth Fault; Overcurrent; Earth fault Reclose function was off at Sw 42021 due to the fire ban. The feeder was patrolled but we found no cause, expect the cause occurred at the time of the storm. Excluded OMS # 921258. | January | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2013-01-12 | N | 95.0446 | N | 35 | Y | Y | 1.1101 | 39.4971 | 10904.5575
[7 empty] | 17727 | 11790 | 921296 | 2013-01-12 18:40 | 2013-01-12 20:25 | 105 | 11kV | 13335 | 127 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134081 1 fault operation B & C phase Overcurrent Reclose due to total fire ban, Fdr patrolled & returned to service. | January | 2013 | 2013Q3 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-01-12 | N | 105 | N | 35 | Y | Y | 1.1101 | 39.4971 | 9744.8247
[7 empty] | 17860 | 12802 | 921232 | 2013-01-12 17:14 | 2013-01-12 20:47 | 213 | 11kV | 1065 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134082 1 fault operation B & C phase Overcurrent 11kV was on the ground at pole AL-60304. Reclose was off due to fire ban. Excluded OMS # 921232. | January | 2013 | 2013Q3 | 2013 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Veg | 2013-01-12 | N | 213 | N | 35 | Y | Y | 1.1101 | 39.4971 | 778.2706
[7 empty] | 18304 | 17503 | 921302 | 2013-01-12 18:29 | 2013-01-12 20:50 | 141 | 11kV | 18753 | 133 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134086 1 fault operation B & C phase Overcurrent Reclose off due to total fire ban | January | 2013 | 2013Q3 | 2013 | 526:34641 | 526:34641 | ZN00526/034641 | CESSNOCK | OH | Veg | 2013-01-12 | N | 141 | N | 35 | Y | Y | 1.1101 | 39.4971 | 13704.1393
[7 empty] | 16742 | 1533 | 923904 | 2013-01-12 19:17 | 2013-01-12 21:00 | 103 | 11kV | 103 | 1 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | Unselected | N | ZN 9118 Cronulla - Pnl 25 - Timed O/C, 11kV trip zone earth, Tx.2 trip Group earth. Failed due to suspected underground fault. | January | 2013 | 2013Q3 | 2013 |  |  |  | SUTHERLAND | UG | Not Veg | 2013-01-12 | N | 103 | N | 35 | Y | Y | 1.1101 | 39.4971 | 75.2694
[7 empty] | 17880 | 12932 | 921310 | 2013-01-12 18:59 | 2013-01-12 21:30 | 151 | 11kV | 29898 | 198 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134090 1 fault operation Single phase Earth fault | January | 2013 | 2013Q3 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2013-01-12 | N | 151 | N | 35 | Y | Y | 1.1101 | 39.4971 | 21848.5766
[7 empty] | 16777 | 1871 | 921281 | 2013-01-12 18:35 | 2013-01-12 21:36 | 181.45 | 11kV | 55160.8 | 304 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134083 DOLF : 10 Amp Sub 50459 20A DOLF OMS# 921276 | January | 2013 | 2013Q3 | 2013 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2013-01-12 | N | 181.45 | N | 35 | Y | Y | 1.1101 | 39.4971 | 40309.8857
[7 empty] | 16762 | 1724 | 921262 | 2013-01-12 18:13 | 2013-01-12 21:37 | 204 | 11kV | 139931 | 688 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134085 1 fault operation A & B phase Overcurrent RECLOSE FUNCTION OFF DUE TO THE FIRE BAN. Excluded OMS # 921262. | January | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-01-12 | N | 203.3881 | N | 35 | Y | Y | 1.1101 | 39.4971 | 102257.4475
[7 empty] | 16754 | 1646 | 922594 | 2013-01-12 18:13 | 2013-01-12 21:43 | 210 | 11kV | 37170 | 177 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134089 1 fault operation A phase Overcurrent | January | 2013 | 2013Q3 | 2013 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2013-01-12 | N | 210 | N | 35 | Y | Y | 1.1101 | 39.4971 | 27162.7397
[7 empty] | 17718 | 11709 | 921339 | 2013-01-12 19:18 | 2013-01-12 22:18 | 180 | 11kV | 7200 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134094 1 fault operation A & C phase Overcurrent | January | 2013 | 2013Q3 | 2013 | 806:74076 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2013-01-12 | N | 180 | N | 35 | Y | Y | 1.1101 | 39.4971 | 5261.5476
[7 empty] | 17750 | 11948 | 921316 | 2013-01-12 19:13 | 2013-01-12 22:20 | 187 | 11kV | 115479 | 1539 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.15005 Belrose Pnl.8 - tripped on : B & C phase inst O/C, EFI, Earth Fault Tree on HV mains @ Opala St, Belrose. HV into LV @ PT15553 - EMSO to Check see 922095 922096 | January | 2013 | 2013Q3 | 2013 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Veg | 2013-01-12 | N | 75.0351 | N | 35 | Y | Y | 1.1101 | 39.4971 | 84388.6471
[7 empty] | 18474 | 19480 | 922662 | 2013-01-12 18:26 | 2013-01-12 23:06 | 280 | 11kV | 71400 | 255 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134091 1 fault operation A & B phase Overcurrent | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-01-12 | N | 280 | N | 35 | Y | Y | 1.1101 | 39.4971 | 52177.0141
[7 empty] | 17602 | 9999 | 921283 | 2013-01-12 18:37 | 2013-01-12 23:31 | 294 | 11kV | 11760 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134095 1 fault operation A & B phase Overcurrent | January | 2013 | 2013Q3 | 2013 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Veg | 2013-01-12 | N | 294 | N | 35 | Y | Y | 1.1101 | 39.4971 | 8593.8611
[7 empty] | 18549 | 20348 | 923916 | 2013-01-12 19:40 | 2013-01-12 23:49 | 249 | 11kV | 45528 | 200 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134097 1 fault operation 3 phase Overcurrent Excluded 923916 & 923917 | January | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2013-01-12 | N | 227.64 | N | 35 | Y | Y | 1.1101 | 39.4971 | 33270.5196
[7 empty] | 17874 | 12895 | 921353 | 2013-01-12 19:53 | 2013-01-13 00:05 | 252 | 11kV | 10836 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134098 1 fault operation Overcurrent | January | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2013-01-12 | N | 252 | N | 35 | Y | Y | 1.1101 | 39.4971 | 7918.6292
[7 empty] | 16815 | 2139 | 922659 | 2013-01-12 18:24 | 2013-01-13 00:20 | 356 | 11kV | 82592 | 232 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134099 1 fault operation 3 phase Overcurrent | January | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2013-01-12 | N | 356 | N | 35 | Y | Y | 1.1101 | 39.4971 | 60355.7975
[7 empty] | 16819 | 2156 | 921356 | 2013-01-12 20:21 | 2013-01-13 00:24 | 243.4 | 11kV | 8762.4 | 36 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | Electrical Storm | N | Switch 42020. | January | 2013 | 2013Q3 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | Unknown | Unknown | 2013-01-12 | N | 243.4 | N | 35 | Y | Y | 1.1101 | 39.4971 | 6403.3035
[7 empty] | 18193 | 16552 | 921400 | 2013-01-12 23:55 | 2013-01-13 01:05 | 70 | 11kV | 210 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134103 C phase DOLF : 10 Amp Excluded OMS 921400 | January | 2013 | 2013Q3 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | UG | Not Veg | 2013-01-12 | N | 70 | N | 35 | Y | Y | 1.1101 | 39.4971 | 153.4618
[7 empty] | 17689 | 11463 | 921363 | 2013-01-12 20:30 | 2013-01-13 02:23 | 353.0667 | 11kV | 8826.6667 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134108 A & B phase DOLF : 10 Amp | January | 2013 | 2013Q3 | 2013 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2013-01-12 | N | 353.0667 | N | 35 | Y | Y | 1.1101 | 39.4971 | 6450.2677
[7 empty] | 17341 | 7389 | 921411 | 2013-01-13 01:36 | 2013-01-13 02:40 | 64 | 11kV | 6528 | 102 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 134109 A & B phase DOLF : 40 Amp Possum found at base of sub pole. Readings as left 229A, 226A, 218A @ 245V Excluded OMS 921411 | January | 2013 | 2013Q3 | 2013 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2013-01-13 | N | 64 | N | 41 | Y | Y | 1.1101 | 39.4971 | 4770.4699
[7 empty] | 16559 | 368 | 922334 | 2013-01-13 02:43 | 2013-01-13 04:46 | 123 | 11kV | 615 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134111 CF phase DOLF : 5 Amp Excluded OMS 921418 & 921420 | January | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | SINGLETON | OH | Veg | 2013-01-13 | N | 123 | N | 41 | Y | Y | 1.1101 | 39.4971 | 449.4239
[7 empty] | 18122 | 15916 | 922639 | 2013-01-12 18:16 | 2013-01-13 05:14 | 658 | 11kV | 370856 | 909 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134107 2 fault operations A & B phase Overcurrent; Earth fault Reclose off due to total fire ban | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-01-12 | N | 407.9824 | N | 35 | Y | Y | 1.1101 | 39.4971 | 271010.6264
[7 empty] | 18515 | 19996 | 921386 | 2013-01-12 22:00 | 2013-01-13 07:38 | 578 | 11kV | 41596.25 | 74 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134126 Replaced lightning arrestors | January | 2013 | 2013Q3 | 2013 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2013-01-12 | N | 562.1115 | N | 35 | Y | Y | 1.1101 | 39.4971 | 30397.3126
[7 empty] | 17281 | 6889 | 921201 | 2013-01-12 15:09 | 2013-01-13 07:55 | 1006 | 11kV | 12072 | 12 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 134131 11kV UGOH failed at links 5410 Sheet 507/5 C2 L.McGuire explained Gen set brought in to hold LV overnight however load was too great and customers beyond pillar HS40484 were left off till larger Gen onsite Excluded OMS 921201 | January | 2013 | 2013Q3 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | Unknown | Unknown | 2013-01-12 | N | 1006 | N | 35 | Y | Y | 1.1101 | 39.4971 | 8821.8615
[7 empty] | 17129 | 4630 | 921330 | 2013-01-13 05:41 | 2013-01-13 09:30 | 229 | 11kV | 1145 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134117 A & B phase DOLF : 10 Amp Excluded OMS 921330, 921442, 921426 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 229 | N | 41 | Y | Y | 1.1101 | 39.4971 | 836.7322
[7 empty] | 18544 | 20295 | 921464 | 2013-01-13 04:14 | 2013-01-13 09:35 | 321 | 11kV | 642 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134116 A phase DOLF : 10 Amp Excluded oms 921423 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 321 | N | 41 | Y | Y | 1.1101 | 39.4971 | 469.1547
[7 empty] | 17190 | 5739 | 921443 | 2013-01-12 19:40 | 2013-01-13 10:15 | 875 | 11kV | 27125 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134121 DOLF : 20 Amp Excluded OMS 921441 & 921443 & 922704 | January | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-01-12 | N | 875 | N | 35 | Y | Y | 1.1101 | 39.4971 | 19822.1499
[7 empty] | 17981 | 14124 | 921429 | 2013-01-13 05:59 | 2013-01-13 10:15 | 256 | 11kV | 256 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134122 B phase DOLF : 10 Amp Excluded OMS 921429 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 256 | N | 41 | Y | Y | 1.1101 | 39.4971 | 187.0772
[7 empty] | 17820 | 12510 | 921446 | 2013-01-13 07:10 | 2013-01-13 10:30 | 200 | 11kV | 200 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134138 B phase DOLF : 10 Amp Excluded OMS 921446 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 200 | N | 41 | Y | Y | 1.1101 | 39.4971 | 146.1541
[7 empty] | 18261 | 17143 | 921433 | 2013-01-13 06:02 | 2013-01-13 10:33 | 271 | 11kV | 75140 | 320 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134127 3 fault operations Overcurrent | January | 2013 | 2013Q3 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2013-01-13 | N | 234.8125 | N | 41 | Y | Y | 1.1101 | 39.4971 | 54910.0957
[7 empty] | 16620 | 784 | 921447 | 2013-01-13 07:00 | 2013-01-13 11:25 | 265 | 11kV | 530 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134132 B phase DOLF : 10 Amp Excluded OMS 921447 | January | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 265 | N | 41 | Y | Y | 1.1101 | 39.4971 | 387.3084
[7 empty] | 16964 | 3342 | 921430 | 2013-01-13 06:00 | 2013-01-13 11:30 | 330 | 11kV | 1650 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134118 DOLF : 5 Amp Excluded OMS 921430, 921431, 921432, 921453 | January | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2013-01-13 | N | 330 | N | 41 | Y | Y | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 18488 | 19799 | 921448 | 2013-01-13 07:19 | 2013-01-13 11:40 | 261 | 11kV | 522 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134119 3 phase DOLF : 20 Amp Excluded OMS 921448 | January | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2013-01-13 | N | 261 | N | 41 | Y | Y | 1.1101 | 39.4971 | 381.4622
[7 empty] | 18032 | 14725 | 921503 | 2013-01-13 10:43 | 2013-01-13 11:40 | 57 | 11kV | 114 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134133 C phase DOLF : 10 Amp Excluded OMS 921503 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 57 | N | 41 | Y | Y | 1.1101 | 39.4971 | 83.3078
[7 empty] | 16794 | 2018 | 921466 | 2013-01-13 08:02 | 2013-01-13 12:30 | 268 | 11kV | 268 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134136 A phase DOLF Excluded OMS 921466 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 268 | N | 41 | Y | Y | 1.1101 | 39.4971 | 195.8465
[7 empty] | 17268 | 6778 | 921498 | 2013-01-13 11:31 | 2013-01-13 12:37 | 66 | 11kV | 114480 | 1928 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn3472 Sefton: Panel 31 "S.4114 Royal Well etc" tripped, reclosed and locked out. Relays: 'C' ph IOC + Timed, E/F, Lockout, EFI, Fault Check Signals: 11kv trip, Zone earth, Tx.4 Group earth Field EFI's: S4412, S4415, S50039, S3684, S35714, S1222, S4475 Abnormal: AB513 open and defective. Sw 'B' Closed at S.3684 Church Hume. Remarks: Section of 11kv UG fdr between S4475 Ashbry Av and S4474 Lambert Mc Millan is defective. Related jobs: #921526, 923065, 922822, 922824, 921498 | January | 2013 | 2013Q3 | 2013 | ZN3472:PA31 | ZN35900:PA4 | ZN35900/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-13 | N | 59.3776 | N | 41 | Y | Y | 1.1101 | 39.4971 | 83658.6074
[7 empty] | 17060 | 4137 | 921494 | 2013-01-13 09:36 | 2013-01-13 13:00 | 204 | 11kV | 204 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134128 A phase DOLF : 10 Amp Excluded OMS 921494 | January | 2013 | 2013Q3 | 2013 | 526:34635 | 526:34635 | ZN00526/034635 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 204 | N | 41 | Y | Y | 1.1101 | 39.4971 | 149.0772
[7 empty] | 17810 | 12465 | 921515 | 2013-01-13 11:35 | 2013-01-13 13:15 | 100 | 11kV | 149115 | 1502 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn.12580 Erina Zone Pnl.10 tripped on: A Phase IOC, timed OC, EFI in #8 ruby place, Greenpoint on RHS of battle axe block in residential housing block. Customer jackhamering old BBQ hit feeder cable see 922242 922243 | January | 2013 | 2013Q3 | 2013 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | UG | Not Veg | 2013-01-13 | N | 99.2776 | N | 41 | Y | Y | 1.1101 | 39.4971 | 108968.8439
[7 empty] | 18146 | 16057 | 921491 | 2013-01-13 08:59 | 2013-01-13 13:28 | 269 | 11kV | 538 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | NO LID report DOLF replaced | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 269 | N | 41 | Y | Y | 1.1101 | 39.4971 | 393.1545
[7 empty] | 16576 | 508 | 921461 | 2013-01-13 07:43 | 2013-01-13 14:24 | 400.7667 | 11kV | 1094.4833 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134130 DOLF : 10 Amp Excluded OMS 921461 | January | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2013-01-13 | N | 364.8278 | N | 41 | Y | Y | 1.1101 | 39.4971 | 799.8161
[7 empty] | 16854 | 2367 | 921449 | 2013-01-13 05:28 | 2013-01-13 14:30 | 542.4667 | 11kV | 2169.8667 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134137 C phase DOLF : 16 Amp | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-01-13 | N | 542.4667 | N | 41 | Y | Y | 1.1101 | 39.4971 | 1585.6746
[7 empty] | 17438 | 8224 | 922839 | 2013-01-13 14:00 | 2013-01-13 15:20 | 80 | 11kV | 1200 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 134143 1 fault operation A phase Sectionaliser MAINS DOWN NEAR ABS 75233 | January | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2013-01-13 | N | 80 | N | 41 | Y | Y | 1.1101 | 39.4971 | 876.9246
[7 empty] | 16905 | 2937 | 921574 | 2013-01-13 07:55 | 2013-01-13 16:30 | 515 | 11kV | 7210 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134142 A phase DOLF : 10 Amp Excluded OMS 921574 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-01-13 | N | 515 | N | 41 | Y | Y | 1.1101 | 39.4971 | 5268.8553
[7 empty] | 17891 | 13064 | 921670 | 2013-01-13 17:01 | 2013-01-13 17:54 | 53 | 11kV | 78047 | 1627 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Lightning | N | ZN 9245 Engadine - Pnl 4 - A phase IOC, tripped, reclosed and tripped. AB 35668 Post insulator failed. | January | 2013 | 2013Q3 | 2013 | ZN9245:PA4 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2013-01-13 | N | 47.9699 | N | 41 | Y | Y | 1.1101 | 39.4971 | 57034.4456
[7 empty] | 16843 | 2308 | 921488 | 2013-01-13 12:25 | 2013-01-13 18:30 | 365 | 11kV | 365 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 134144 B phase LLC dropper broken | January | 2013 | 2013Q3 | 2013 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2013-01-13 | N | 365 | N | 41 | Y | Y | 1.1101 | 39.4971 | 266.7312
[7 empty] | 16554 | 343 | 921704 | 2013-01-13 17:29 | 2013-01-13 18:33 | 64 | 11kV | 63530 | 1195 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.40 tripped on C phase O/C, Earth Fault, EFI Explosion from UGOH between USL 41470 to S18162 see 922262 922263 922265 | January | 2013 | 2013Q3 | 2013 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | Unknown | Unknown | 2013-01-13 | N | 53.1632 | N | 41 | Y | Y | 1.1101 | 39.4971 | 46425.8502
[7 empty] | 17455 | 8355 | 921739 | 2013-01-13 17:58 | 2013-01-13 19:05 | 67 | 11kV | 2613 | 39 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Unselected | N | PT12334 Berrys Head Gregory - A & B Phase HDos operated Tree branch across Lightning arrestors @ PT12334 | January | 2013 | 2013Q3 | 2013 | ZN12600:PA11 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2013-01-13 | N | 67 | N | 41 | Y | Y | 1.1101 | 39.4971 | 1909.5033
[7 empty] | 18369 | 18085 | 921677 | 2013-01-13 17:05 | 2013-01-13 19:39 | 154 | 11kV | 227606 | 2047 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | Zn.15008 Harbord Zn - Pnl.9 tripped & locked out on: B & C phase timed OC Lightning arrestor blown clear at UGOH beneath PT15344. Will require cutout for repair see 922114 922115 922118 922117 | January | 2013 | 2013Q3 | 2013 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2013-01-13 | N | 111.19 | N | 41 | Y | Y | 1.1101 | 39.4971 | 166327.7516
[7 empty] | 16816 | 2140 | 921797 | 2013-01-13 19:00 | 2013-01-13 20:33 | 93 | 11kV | 465 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 134159/02 Isolation for transformer replacement | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 93 | N | 41 | Y | Y | 1.1101 | 39.4971 | 339.8083
[7 empty] | 16544 | 294 | 921450 | 2013-01-13 07:22 | 2013-01-13 20:45 | 803 | 11kV | 3212 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 134159 A & B phase DOLF : 10 Amp Excluded OMS 921450 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-13 | N | 803 | N | 41 | Y | Y | 1.1101 | 39.4971 | 2347.2349
[7 empty] | 17536 | 9031 | 921650 | 2013-01-13 16:45 | 2013-01-13 21:04 | 259 | 11kV | 8547 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 134162 2 fault operations Single phase Earth fault sub 72223 tee off taps broken, mains down, to be repaired at later date. Excluded 921650 | January | 2013 | 2013Q3 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2013-01-13 | N | 259 | N | 41 | Y | Y | 1.1101 | 39.4971 | 6245.8955
[7 empty] | 16909 | 2986 | 921853 | 2013-01-13 20:46 | 2013-01-13 21:35 | 49.15 | 11kV | 39565.75 | 805 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Lightning | N | Ex Dee Why Zone - Pnl.12L - iR 48234 South Creek Toronto - Opened on one Phase only at 20:45. Opened by AOp on all 3 phases @ 21:09 No protection operations - failed to send trip signal Vehicle hit intellirupter pole - car rego BP 87 KM | January | 2013 | 2013Q3 | 2013 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Not Veg | 2013-01-13 | N | 49.15 | N | 41 | Y | Y | 1.1101 | 39.4971 | 28913.4831
[7 empty] | 17848 | 12693 | 921810 | 2013-01-13 19:27 | 2013-01-13 22:14 | 167 | 11kV | 11918 | 76 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | REC 3280 HUNT Ave - tripped on B & C phase O/C Possible lightning strike. Patrolled see 922651 922653 922652 | January | 2013 | 2013Q3 | 2013 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2013-01-13 | N | 156.8158 | N | 41 | Y | Y | 1.1101 | 39.4971 | 8709.3229
[7 empty] | 18137 | 16012 | 921852 | 2013-01-13 20:44 | 2013-01-13 22:25 | 101 | 11kV | 505 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134164 Single phase DOLF : 5 Amp Excluded OMS 921852 | January | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | SINGLETON | OH | Veg | 2013-01-13 | N | 101 | N | 41 | Y | Y | 1.1101 | 39.4971 | 369.0391
[7 empty] | 18157 | 16120 | 921790 | 2013-01-13 18:54 | 2013-01-13 22:46 | 232 | 11kV | 20184 | 87 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134166 3 fault operations Overcurrent Excluded OMS 921790 | January | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2013-01-13 | N | 232 | N | 41 | Y | Y | 1.1101 | 39.4971 | 14749.8719
[7 empty] | 17821 | 12511 | 921891 | 2013-01-13 22:01 | 2013-01-13 22:58 | 57 | 11kV | 115716 | 2085 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @Zn188 Zetland - 11kv Panel No.1 "Sub 7570 Cope McEvoy" feeder tripped. Relays: Earth fault, EFI, Fault check relay Signals: 11kv trip, Zone earth, No.3 Group earth Field EFI's: S7570, S8053, S1253 Abnormal: N/O closed @ S6315 Power Loveridge & Sw A open @ Sub 6068 Alexander Renwick (Panel No.17) Remarks: 11kv UG fault from Sub 1253 Wyndham McEvoy to Sub 7995 Brennan Power Related jobs: #921891, 921892, 925764, 925763 | January | 2013 | 2013Q3 | 2013 | ZN188:PA1 | ZN188:PA1 | ZN00188/000001 | SYDNEY | UG | Not Veg | 2013-01-13 | N | 55.4993 | N | 41 | Y | Y | 1.1101 | 39.4971 | 84561.8398
[7 empty] | 16807 | 2108 | 921792 | 2013-01-13 18:59 | 2013-01-13 23:20 | 261 | 11kV | 3915 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134169 B phase DOLF : 20 Amp Excluded OMS 921792 | January | 2013 | 2013Q3 | 2013 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2013-01-13 | N | 261 | N | 41 | Y | Y | 1.1101 | 39.4971 | 2860.9665
[7 empty] | 16733 | 1483 | 921837 | 2013-01-13 23:17 | 2013-01-13 23:22 | 5 | 11kV | 12145 | 2429 | HV | Arcing | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134177 De energised Fdr for Fire Brigade to put out pole fire. | January | 2013 | 2013Q3 | 2013 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2013-01-13 | N | 5 | N | 41 | Y | Y | 1.1101 | 39.4971 | 8875.2078
[7 empty] | 17121 | 4575 | 921820 | 2013-01-13 19:51 | 2013-01-13 23:25 | 214 | 11kV | 428 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134168 A phase DOLF : 10 Amp Excluded OMS 921820 | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-01-13 | N | 214 | N | 41 | Y | Y | 1.1101 | 39.4971 | 312.7698
[7 empty] | 17816 | 12490 | 921754 | 2013-01-13 18:15 | 2013-01-13 23:32 | 316.8667 | 11kV | 4436.1333 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134170 C phase DOLF : 10 Amp Excluded OMS 921780 | January | 2013 | 2013Q3 | 2013 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2013-01-13 | N | 316.8667 | N | 41 | Y | Y | 1.1101 | 39.4971 | 3241.7954
[7 empty] | 17342 | 7399 | 921849 | 2013-01-13 20:45 | 2013-01-14 00:15 | 210 | 11kV | 420 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134172 C phase DOLF : 40 Amp Incorrect fuse sizes in all 3 phases 10A replaced with 40A. Excluded OMS 921849. | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2013-01-13 | N | 210 | N | 41 | Y | Y | 1.1101 | 39.4971 | 306.9236
[7 empty] | 17490 | 8711 | 921881 | 2013-01-13 21:43 | 2013-01-14 00:55 | 192 | 11kV | 384 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134173 B phase DOLF : 10 Amp Excluded OMS 921881 | January | 2013 | 2013Q3 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | UG | Not Veg | 2013-01-13 | N | 192 | N | 41 | Y | Y | 1.1101 | 39.4971 | 280.6159
[7 empty] | 16999 | 3546 | 923116 | 2013-01-14 00:50 | 2013-01-14 01:10 | 20 | 11kV | 120 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134181 4 fault operations Sw tripped while restoring supply to sub 71563 See report 134180/OMS 923105 & 923115 | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2013-01-14 | N | 20 | N | 14 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 18555 | 20384 | 921898 | 2013-01-13 22:08 | 2013-01-14 01:30 | 202 | 11kV | 17400 | 135 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.13000 lake Munmorah - Pnl.8 tripped on A & C phase IOC, lock out UGOH near S14752 has damage - open circuit see 922281 922282 921933 CC1: 22-"Refer to SOp" | January | 2013 | 2013Q3 | 2013 | ZN13000:PA8 | ZN13000:PA8 | ZN13000/000008 | CENTRAL COAST | Unknown | Unknown | 2013-01-13 | N | 128.8889 | N | 41 | Y | Y | 1.1101 | 39.4971 | 12715.4068
[7 empty] | 16525 | 132 | 921808 | 2013-01-13 19:20 | 2013-01-14 02:00 | 400 | 11kV | 800 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134178 Single phase DOLF : 10 Amp Excluded OMS 921808 | January | 2013 | 2013Q3 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2013-01-13 | N | 400 | N | 41 | Y | Y | 1.1101 | 39.4971 | 584.6164
[7 empty] | 18001 | 14225 | 923117 | 2013-01-14 02:30 | 2013-01-14 02:50 | 20 | 11kV | 120 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134182 1 fault operation see reports 134180 /OMS 923115 & 134181/OMS 923116 | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2013-01-14 | N | 20 | N | 14 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 17214 | 6069 | 921418 | 2013-01-14 02:02 | 2013-01-14 05:25 | 203 | 11kV | 1015 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 134184 Single phase DOLF : 5 Amp Suspect Tx 3453 Excluded OMS 921951, 921953, 923101 | January | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | SINGLETON | UG | Not Veg | 2013-01-14 | N | 203 | N | 14 | N | N | 1.1101 | 39.4971 | 741.7321
[7 empty] | 16619 | 783 | 922018 | 2013-01-14 08:43 | 2013-01-14 10:55 | 132 | 11kV | 264 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134193 B phase DOLF : 10 Amp Excluded OMS 922018 | January | 2013 | 2013Q3 | 2013 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | UG | Not Veg | 2013-01-14 | N | 132 | N | 14 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 18393 | 18350 | 922025 | 2013-01-14 08:00 | 2013-01-14 12:45 | 285 | 11kV | 570 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134195 C phase DOLF : 10 Amp Excluded OMS 922025 | January | 2013 | 2013Q3 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2013-01-14 | N | 285 | N | 14 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 17680 | 11181 | 922080 | 2013-01-14 08:00 | 2013-01-14 13:45 | 345 | 11kV | 690 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134196 A & C phase DOLF : 3 Amp also blew 100A LVF Excluded cass 794780/ OMS 922080 | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2013-01-14 | N | 345 | N | 14 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 18108 | 15844 | 922269 | 2013-01-14 12:00 | 2013-01-14 15:05 | 185 | 11kV | 185 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134197 A phase DOLF : 10 Amp Excluded OMS 922269 | January | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-01-14 | N | 185 | N | 14 | N | N | 1.1101 | 39.4971 | 135.1925
[7 empty] | 17881 | 12943 | 922215 | 2013-01-14 12:35 | 2013-01-14 15:45 | 190 | 11kV | 112982 | 1632 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.6 tripped on 6L - SEF OH down line side of iR50531 see 922558 922559 922560 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2013-01-14 | N | 69.2292 | N | 14 | N | N | 1.1101 | 39.4971 | 82563.9132
[7 empty] | 17550 | 9153 | 922195 | 2013-01-14 11:00 | 2013-01-14 16:00 | 300 | 11kV | 300 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 134198 DOLF : 10 Amp replace faulty surge divertors Excluded oms 922195 | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-01-14 | N | 300 | N | 14 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 17118 | 4546 | 922344 | 2013-01-14 16:10 | 2013-01-14 17:10 | 60 | 11kV | 60 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 134199 3 phase isolation isolated because of fire under mains. Excluded oms DF 80031 | January | 2013 | 2013Q3 | 2013 | 806:74076 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2013-01-14 | N | 60 | N | 14 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 17079 | 4262 | 933955 | 2013-01-12 14:08 | 2013-01-14 17:40 | 3092 | 11kV | 6535 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 134200 Trip & locked out No Auto Reclose Total Fire Ban isolated. mains down. back on after mains cut away at pole CM-20038 Excluded OMS 921188 | January | 2013 | 2013Q3 | 2013 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2013-01-12 | N | 1307 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4775.5853
[7 empty] | 17826 | 12531 | 921973 | 2013-01-14 07:21 | 2013-01-14 20:10 | 769.4667 | 11kV | 13080.9333 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 134204 3 phase DOLF : 20 Amp high into low. LV checked by J. Frazer OK replaced Bph 100A LVF at sub 53452 Requires new 11kv pole, crews on site now | January | 2013 | 2013Q3 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2013-01-14 | N | 769.4667 | N | 14 | N | N | 1.1101 | 39.4971 | 9559.1603
[7 empty] | 18232 | 16900 | 922446 | 2013-01-14 16:30 | 2013-01-14 20:45 | 255 | 11kV | 1020 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134206 A phase DOLF : 10 Amp Excluded OMS 922446 | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-01-14 | N | 255 | N | 14 | N | N | 1.1101 | 39.4971 | 745.3859
[7 empty] | 17343 | 7401 | 922431 | 2013-01-14 19:00 | 2013-01-14 21:00 | 120 | 11kV | 240 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134207 A phase DOLF : 10 Amp Excluded OMS 922431 | January | 2013 | 2013Q3 | 2013 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | UG | Not Veg | 2013-01-14 | N | 120 | N | 14 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 17239 | 6377 | 922474 | 2013-01-14 22:44 | 2013-01-15 00:44 | 120 | 11kV | 71760 | 598 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134209 no fault found, daylight patrol required. Excluded OMS 922474 | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-01-14 | N | 120 | N | 14 | N | N | 1.1101 | 39.4971 | 52440.0914
[7 empty] | 18283 | 17310 | 922481 | 2013-01-15 00:31 | 2013-01-15 01:47 | 76 | 11kV | 109972 | 1447 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Zn.15004 Newport Pnl.5 tripped on: A & C phase inst and timmed OC. fault check EFI Possum found at base of PT15630. No damaged caused | January | 2013 | 2013Q3 | 2013 | ZN15004:PA5 | ZN15004:PA5 | ZN15004/000005 | NORTHERN BEACHES | OH | Not Veg | 2013-01-15 | N | 76 | N | 7 | N | N | 1.1101 | 39.4971 | 80364.294
[7 empty] | 17785 | 12300 | 922483 | 2013-01-15 03:06 | 2013-01-15 03:27 | 21 | 11kV | 7182 | 342 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134211 Fdr opened to bridge out ABS 951 Live Line de energised. Excluded OMS 922479, 922483. | January | 2013 | 2013Q3 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2013-01-15 | N | 21 | N | 7 | N | N | 1.1101 | 39.4971 | 5248.3938
[7 empty] | 17549 | 9152 | 922521 | 2013-01-15 07:48 | 2013-01-15 09:20 | 92 | 11kV | 92 | 1 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Previous Storm | N | LID 134218 Replaced B phase dolf 10amp at sub 71990. | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-01-15 | N | 92 | N | 7 | N | N | 1.1101 | 39.4971 | 67.2309
[7 empty] | 17271 | 6800 | 922892 | 2013-01-15 16:23 | 2013-01-15 17:40 | 77 | 11kV | 77 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134224 A phase DOLF : 10 Amp Excluded OMS 922892 | January | 2013 | 2013Q3 | 2013 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | UG | Not Veg | 2013-01-15 | N | 77 | N | 7 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 16796 | 2023 | 922854 | 2013-01-15 15:08 | 2013-01-15 18:00 | 172 | 11kV | 1376 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT14485 Boundary Flether - Roadside HDO fuse blown Fuse Fatigue | January | 2013 | 2013Q3 | 2013 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2013-01-15 | N | 172 | N | 7 | N | N | 1.1101 | 39.4971 | 1005.5402
[7 empty] | 18119 | 15903 | 922909 | 2013-01-15 17:05 | 2013-01-15 19:10 | 125 | 11kV | 250 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134225 A phase DOLF : 10 Amp Excluded OMS 922909 | January | 2013 | 2013Q3 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | UG | Not Veg | 2013-01-15 | N | 125 | N | 7 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 17176 | 5450 | 922935 | 2013-01-15 18:45 | 2013-01-15 19:45 | 60 | 11kV | 420 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134226 A phase DOLF : 16 Amp Excluded OMS 922935 | January | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-01-15 | N | 60 | N | 7 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 17075 | 4230 | 923153 | 2013-01-16 10:41 | 2013-01-16 11:40 | 59 | 11kV | 10148 | 172 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex ZN 10990 Arncliffe - Pnl 5 - AB 31208. A phase bond at AB 31208 burnt off. | January | 2013 | 2013Q3 | 2013 | ZN10990:PA5 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | OH | Not Veg | 2013-01-16 | N | 59 | N | 2 | N | N | 1.1101 | 39.4971 | 7415.8591
[7 empty] | 16691 | 1142 | 923291 | 2013-01-16 14:16 | 2013-01-16 19:25 | 309 | 11kV | 309 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 134240 B phase DOLF : 10 Amp Excluded OMS 923291 | January | 2013 | 2013Q3 | 2013 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | UG | Not Veg | 2013-01-16 | N | 309 | N | 2 | N | N | 1.1101 | 39.4971 | 225.8081
[7 empty] | 17115 | 4529 | 923451 | 2013-01-17 07:26 | 2013-01-17 10:12 | 166 | 11kV | 1342 | 29 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 134244 Faulty LL Clamp sub 27894. Isolated from ABS 43794 to repair. Excluded OMS 923451 | January | 2013 | 2013Q3 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-01-17 | N | 46.2759 | N | 4 | N | N | 1.1101 | 39.4971 | 980.694
[7 empty] | 17288 | 6963 | 923553 | 2013-01-17 10:54 | 2013-01-17 11:49 | 55 | 11kV | 84315 | 1589 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 134251 2 fault operations Concrete pump boom hit 11kV OHM near sub 43746. Reported by G Johns (driving past). DOp checked safe to energise. C Chapman onsite for details. Excluded OMS 923553 | January | 2013 | 2013Q3 | 2013 | 503:48078 | 532:83314 | ZN00532/083314 | MAITLAND | OH | Not Veg | 2013-01-17 | N | 53.0617 | N | 4 | N | N | 1.1101 | 39.4971 | 61614.9151
[7 empty] | 17778 | 12217 | 923602 | 2013-01-17 12:08 | 2013-01-17 14:30 | 142 | 11kV | 142 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134254 C phase DOLF : 10 Amp Excluded OMS 923602 | January | 2013 | 2013Q3 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2013-01-17 | N | 142 | N | 4 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 18198 | 16590 | 923774 | 2013-01-17 19:54 | 2013-01-17 20:45 | 51 | 11kV | 13901 | 273 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.3425 Castle Cove - Pnl.8 tripped on: Timed earth Fault UG fault - cable failed between S4391 to S6947 see 923834 923836 | January | 2013 | 2013Q3 | 2013 | ZN3425:PA8 | ZN3425:PA8 | ZN03425/000008 | WILLOUGHBY | UG | Not Veg | 2013-01-17 | N | 50.9194 | N | 4 | N | N | 1.1101 | 39.4971 | 10158.4408
[7 empty] | 16613 | 744 | 923795 | 2013-01-18 02:50 | 2013-01-18 03:50 | 60 | 11kV | 5640 | 94 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 134256 DOLF : 40 Amp Sub isolated to replace faulty L/A. Excluded OMS 923795. | January | 2013 | 2013Q3 | 2013 | 208:62 | 257:81987 | ZN00257/081987 | NEWCASTLE | OH | Not Veg | 2013-01-18 | N | 60 | N | 48 | Y | Y | 1.1101 | 39.4971 | 4121.5456
[7 empty] | 17939 | 13456 | 924111 | 2013-01-18 07:40 | 2013-01-18 07:45 | 5 | 11kV | 5 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CUSTOMER RANG ANDREW TAYLOR @ 7.00am TO REPORT NO SUPPLY - FIXED 7.45am refer to related record 924111 | January | 2013 | 2013Q3 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2013-01-18 | N | 5 | N | 48 | Y | Y | 1.1101 | 39.4971 | 3.6539
[7 empty] | 18234 | 16913 | 925496 | 2013-01-18 07:45 | 2013-01-18 07:49 | 4 | 11kV | 516 | 129 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134257 1 fault operation Sensitive Earth Fault related to S.I. 26881 | January | 2013 | 2013Q3 | 2013 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2013-01-18 | N | 4 | N | 48 | Y | Y | 1.1101 | 39.4971 | 377.0776
[7 empty] | 18033 | 14762 | 923811 | 2013-01-18 07:35 | 2013-01-18 09:07 | 92 | 11kV | 89951 | 1030 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S847 Hornsby Panel 5 Tripped on Earth Fault with Fault Check, Cause: Cable failure from S8196 Ashley High No2 To S35663 Dural Pacific See OMS 929917 929925 923811 | January | 2013 | 2013Q3 | 2013 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | UG | Not Veg | 2013-01-18 | N | 87.3311 | N | 48 | Y | Y | 1.1101 | 39.4971 | 65733.5377
[7 empty] | 17792 | 12349 | 924027 | 2013-01-18 12:43 | 2013-01-18 14:15 | 92 | 11kV | 94638 | 1654 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | ZN 10994 Mortdale - Pnl 4 - All phases IOC, EFIs, LO, Timer, Earth fault check. 11kV UGOH exploded in Penshurst Rd near George St, Penshurst due to short circuit. | January | 2013 | 2013Q3 | 2013 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | Unknown | Unknown | 2013-01-18 | N | 57.2177 | N | 48 | Y | Y | 1.1101 | 39.4971 | 69158.6591
[7 empty] | 17273 | 6833 | 926141 | 2013-01-18 14:20 | 2013-01-18 14:24 | 4 | 11kV | 1880 | 470 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.14 tripped on E/F Abnormal: S11328 Sw2353 CLOSED - S18166 SwA OPEN - S12733 Sw3548 OPEN - S11035 Sw A Open - S11034 Sw A Open Failed on restoring pnl 5 - see 926138 926141 926142 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | UG | Not Veg | 2013-01-18 | N | 4 | N | 48 | Y | Y | 1.1101 | 39.4971 | 1373.8485
[7 empty] | 18530 | 20145 | 931980 | 2013-01-18 13:40 | 2013-01-18 15:30 | 110 | 11kV | 11220 | 102 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT 9981 Venetia St - Roadside phase HDO - Failed in service. Roadside phase HDO fell apart. Supply restored via LV//. | January | 2013 | 2013Q3 | 2013 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2013-01-18 | N | 110 | N | 48 | Y | Y | 1.1101 | 39.4971 | 8199.2451
[7 empty] | 16851 | 2334 | 924078 | 2013-01-18 13:25 | 2013-01-18 15:50 | 145 | 11kV | 145 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Hot >35C | N | LID 134274 Single phase DOLF : 10 Amp Excluded OMS # 924078 223 Volts | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2013-01-18 | N | 145 | N | 48 | Y | Y | 1.1101 | 39.4971 | 105.9617
[7 empty] | 17940 | 13457 | 924176 | 2013-01-18 14:41 | 2013-01-18 16:06 | 85 | 11kV | 41971 | 529 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | Hot >35C | N | At S3472 Sefton Panel 34 "English Electric etc' 11kv feeder tripped on; E/F, EFI, Fault check Alarms; tx GE, 11kv trip Remarks: End box fault. cable blown out at S1567 chisolm rd #1 Related jobs: #924176, 924190, 927171, 927170 | January | 2013 | 2013Q3 | 2013 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | UG | Not Veg | 2013-01-18 | N | 79.3403 | N | 48 | Y | Y | 1.1101 | 39.4971 | 30671.1689
[7 empty] | 18514 | 19993 | 924193 | 2013-01-18 14:52 | 2013-01-18 16:50 | 118 | 11kV | 49785 | 474 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3154 St Ives, Panel 23 Fdr CB tripped on B phase IOC and timed OC, 11kV trip, zone earth. Field efi's operated at S.47672 and S.4916. Suspect UG cable fault between S.4916 and AB.2959 | January | 2013 | 2013Q3 | 2013 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | UG | Not Veg | 2013-01-18 | N | 105.0316 | N | 48 | Y | Y | 1.1101 | 39.4971 | 36381.4096
[7 empty] | 17238 | 6372 | 924394 | 2013-01-18 15:59 | 2013-01-18 16:53 | 54 | 11kV | 17226 | 319 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134276 1 fault operation Cap bank 1 trip. F1 neutral unbalance. Cap Bank left isolated. Excluded OMS 924394 | January | 2013 | 2013Q3 | 2013 | 258:80776 | 258:80776 | ZN00258/080776 | NEWCASTLE | OH | Veg | 2013-01-18 | N | 54 | N | 48 | Y | Y | 1.1101 | 39.4971 | 12588.2527
[7 empty] | 18259 | 17129 | 924114 | 2013-01-18 13:58 | 2013-01-18 16:54 | 176 | 11kV | 6512 | 37 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | At S6371 Beauchamp McPherson, (Panel 11-S.8708 Botany Bumborah Point fdr) No2 Tx 'A' phase HV fuse blown. Type KEMXO 90Amp Remarks: fuse fatigue Related jobs: #930077, 930073, 924114, 924140 | January | 2013 | 2013Q3 | 2013 | ZN3672:PA42 | ZN35700:PA10 | ZN35700/000010 | BAYSIDE | OH | Not Veg | 2013-01-18 | N | 176 | N | 48 | Y | Y | 1.1101 | 39.4971 | 4758.7775
[7 empty] | 17575 | 9625 | 924453 | 2013-01-18 16:47 | 2013-01-18 16:59 | 12 | 11kV | 33180 | 2765 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S1285 Greenacre Park Panel 19 Hume Rook feeder tripped on: A & C Phase O/C Abnormal: Panel 19 and Panel 30 at Sefton tied together switching to allow isolation of HV into Low Vlotage at Pt 1657 Elizabeth Edgar Remarks: OH cables twisted together. 11KV into LV after feeder failure Panel 30 at Sefton Zone near PT 1657 see interuption report for panel 30 at Sefton. Related jobs: #924456, 924455, 924453, 927271 | January | 2013 | 2013Q3 | 2013 | ZN1285:PA19 | ZN35900:PA1 | ZN35900/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-01-18 | N | 12 | N | 48 | Y | Y | 1.1101 | 39.4971 | 24246.9654
[7 empty] | 16892 | 2800 | 924230 | 2013-01-18 15:23 | 2013-01-18 17:28 | 125 | 11kV | 154939 | 1592 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.12570 Avoca Pnl.22 tripped / reclosed & locked out on A & B timed O/C UGOH to S14878 short circuit see 926207 926206 | January | 2013 | 2013Q3 | 2013 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | Unknown | Unknown | 2013-01-18 | N | 97.3235 | N | 48 | Y | Y | 1.1101 | 39.4971 | 113224.8513
[7 empty] | 18050 | 15345 | 924072 | 2013-01-18 15:41 | 2013-01-18 17:45 | 124 | 11kV | 180566 | 2097 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.12610 Long Jetty Pnl.10 tripped on Earth Fault Abnormal: AB43226 CLOSED - S12134 SwA OPEN (end box failure) -S18080 SwA OPEN (for load relief) HV UGOH to S14803 failed see 926760 926747 926749 926752 926756 926757 926755 926765 | January | 2013 | 2013Q3 | 2013 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | Unknown | Unknown | 2013-01-18 | N | 86.1068 | N | 48 | Y | Y | 1.1101 | 39.4971 | 131952.307
[7 empty] | 16834 | 2223 | 924148 | 2013-01-18 14:16 | 2013-01-18 17:50 | 214 | 11kV | 352389 | 2165 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Zn.12610 long Jetty Pnl 22 tripped on IOC Fuse assembly failed @ PT11849 see 926220 926219 | January | 2013 | 2013Q3 | 2013 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 162.7663 | N | 48 | Y | Y | 1.1101 | 39.4971 | 257515.4875
[7 empty] | 18301 | 17479 | 924395 | 2013-01-18 16:05 | 2013-01-18 17:55 | 110 | 11kV | 1980 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Hot >35C | N | PT2063 Cotsworld End 200A fuse blown on A phase Tree brought down OH See OMS 924414 927378 924402 924395 924571 CC1: 22-"Refer to SOp" | January | 2013 | 2013Q3 | 2013 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2013-01-18 | N | 110 | N | 48 | Y | Y | 1.1101 | 39.4971 | 1446.9256
[7 empty] | 17608 | 10138 | 924454 | 2013-01-18 16:58 | 2013-01-18 18:09 | 71 | 11kV | 15691 | 221 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.15013 Terrey Hills Panel 6 Fdr CB tripped on C phase IOC AND TIMED oc, lockout, timing, A tree branch brought down OH between Link 24464, Link 24937 and Link 20850 | January | 2013 | 2013Q3 | 2013 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2013-01-18 | N | 71 | N | 48 | Y | Y | 1.1101 | 39.4971 | 11466.52
[7 empty] | 18185 | 16443 | 924269 | 2013-01-18 15:28 | 2013-01-18 18:20 | 172 | 11kV | 20124 | 117 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | At S3499 reserve Bot, ex Panel 10 "S47604 O'Reardon Collins No3" fdr A and C phase HV fuse type OQFRN 71 amp Remarks: tx at S3499 reserve Bot is defective after blowing 2 x HV fuses. suppy restored via LV//. See also interruption for S2079 Related jobs: #924269, 929738 | January | 2013 | 2013Q3 | 2013 | ZN8100:PA10 | ZN8100:PA10 | ZN08100/000010 | SYDNEY | UG | Not Veg | 2013-01-18 | N | 172 | N | 48 | Y | Y | 1.1101 | 39.4971 | 14706.0256
[7 empty] | 16703 | 1246 | 924236 | 2013-01-18 17:07 | 2013-01-18 18:46 | 99 | 11kV | 7025 | 75 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S35500 Top Ryde panel 14 tripped on A and B phase IOC. Suspected UG fault between S7888/SWB and S7889 SW/A See OMS 934133 934134 924236 | January | 2013 | 2013Q3 | 2013 | ZN35500:PA14 | ZN35500:PA14 | ZN35500/000014 | RYDE | UG | Not Veg | 2013-01-18 | N | 93.6667 | N | 48 | Y | Y | 1.1101 | 39.4971 | 5133.6628
[7 empty] | 18297 | 17430 | 924420 | 2013-01-18 16:59 | 2013-01-18 18:48 | 109 | 11kV | 10187 | 1115 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor ABC | Unplanned | Hot >35C | N | Nil opened panel 30 by AOP for safety to allow isolation at S4339 SW B Abnormal: Sw A at S5096 closed across Panel 19 at Greenacre Park Remarks: interrupted for safety reasons. High into LV near PT 1657 see other interruption report Related jobs: # 924451, 927186, 927191, 927185, 924420, 924430, 924432, 924450, 924465 | January | 2013 | 2013Q3 | 2013 | ZN3472:PA30 | ZN3472:PA30 | ZN03472/000030 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-01-18 | N | 9.1363 | N | 48 | Y | Y | 1.1101 | 39.4971 | 7444.3591
[7 empty] | 16761 | 1719 | 924611 | 2013-01-18 19:26 | 2013-01-18 20:13 | 47 | 11kV | 3525 | 75 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134286 2 fault operations A & B phase Overcurrent; Earth fault Excluded OMS 924611 | January | 2013 | 2013Q3 | 2013 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2013-01-18 | N | 47 | N | 48 | Y | Y | 1.1101 | 39.4971 | 2575.966
[7 empty] | 16610 | 729 | 924576 | 2013-01-18 19:00 | 2013-01-18 20:32 | 92 | 11kV | 26107 | 383 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Hot >35C | N | LID 134291 1 fault operation B & C phase Overcurrent; Earth fault Tree on Mains at pole HY-20276 Excluded OMS # 924576 | January | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2013-01-18 | N | 68.1645 | N | 48 | Y | Y | 1.1101 | 39.4971 | 19078.2256
[7 empty] | 17783 | 12288 | 924145 | 2013-01-18 14:13 | 2013-01-18 21:36 | 443 | 11kV | 82506 | 1050 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At S1290 Leightonfield Panel 12 'Miller Bil No.1' 11kv feeder tripped, reclosed and locked out on; C phase IOC, LO, EFI, TImer. Alarms; 11kv trip, ZE, TX3 GE Field EFI's Remarks: UGOH fault short circuit. UGOH Problem Related jobs: #924162, 924153, 924785, 924145, 926795, 926792, 926790 | January | 2013 | 2013Q3 | 2013 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2013-01-18 | N | 78.5771 | N | 48 | Y | Y | 1.1101 | 39.4971 | 60292.9513
[7 empty] | 18023 | 14610 | 924724 | 2013-01-18 20:47 | 2013-01-18 22:00 | 73 | 11kV | 1679 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 134293 A & C phase : 16 Amp There seems to be a problem with the number of customers. Excluded OMS 924724 | January | 2013 | 2013Q3 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2013-01-18 | N | 73 | N | 48 | Y | Y | 1.1101 | 39.4971 | 1226.9637
[7 empty] | 18560 | 20433 | 924627 | 2013-01-18 19:47 | 2013-01-18 22:09 | 141.8167 | 11kV | 21556.1333 | 152 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1533 of Panel 24 Revesby Workers Club fdr Roadside phase HDO assembly broken Remarks: HDO assembly failed roadside supply restored via LV// Related jobs: #924627, 924682 | January | 2013 | 2013Q3 | 2013 | ZN1287:PA24 | ZN1287:PA24 | ZN01287/000024 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-01-18 | N | 141.8167 | N | 48 | Y | Y | 1.1101 | 39.4971 | 15752.5864
[7 empty] | 18506 | 19951 | 924648 | 2013-01-18 20:30 | 2013-01-18 22:25 | 115 | 11kV | 230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134294 A & C phase DOLF : 3 Amp Excluded OMS 924648 | January | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2013-01-18 | N | 115 | N | 48 | Y | Y | 1.1101 | 39.4971 | 168.0772
[7 empty] | 16908 | 2980 | 924643 | 2013-01-18 20:00 | 2013-01-18 22:30 | 150 | 11kV | 92479 | 1071 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 10994 Mortdale - Pnl 13 - A & B phase IOC, Group earth, Timing, lockout. Tree branch brought down OH in Neville St, near Oatley Pde. | January | 2013 | 2013Q3 | 2013 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Veg | 2013-01-18 | N | 86.3483 | N | 48 | Y | Y | 1.1101 | 39.4971 | 67580.9255
[7 empty] | 17318 | 7230 | 924583 | 2013-01-18 19:06 | 2013-01-18 23:00 | 234 | 11kV | 47034 | 201 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 134292 1 fault operation 3 phase Earth fault HV & LV ohm on ground near pole KU-41975. # | January | 2013 | 2013Q3 | 2013 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | OH | Not Veg | 2013-01-18 | N | 234 | N | 48 | Y | Y | 1.1101 | 39.4971 | 34371.0599
[7 empty] | 17440 | 8226 | 924634 | 2013-01-18 19:47 | 2013-01-18 23:03 | 196 | 11kV | 48262 | 282 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134295 3 Phase Overcurrent Excluded OMS 924634 | January | 2013 | 2013Q3 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2013-01-18 | N | 171.1418 | N | 48 | Y | Y | 1.1101 | 39.4971 | 35268.4461
[7 empty] | 16837 | 2240 | 924721 | 2013-01-18 21:00 | 2013-01-19 00:15 | 195 | 11kV | 1560 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 134297 Isolated to change transformer | January | 2013 | 2013Q3 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | UG | Not Veg | 2013-01-18 | N | 195 | N | 48 | Y | Y | 1.1101 | 39.4971 | 1140.002
[7 empty] | 17392 | 7893 | 924143 | 2013-01-18 14:14 | 2013-01-19 00:44 | 630 | 11kV | 33390 | 53 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | pt outside #44 dalnott (PT 11524) has broken insulator that holds hv drop out causing low volts in street No blue form from control room - going off info from notepad restore time taken as oms completion time | January | 2013 | 2013Q3 | 2013 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 630 | N | 48 | Y | Y | 1.1101 | 39.4971 | 24400.4272
[7 empty] | 18085 | 15659 | 924105 | 2013-01-18 13:49 | 2013-01-19 00:44 | 655 | 11kV | 11790 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | pt 12722 has a broken h/v drop out,hanging from hv croosarm above pt.causing low volts in dist no blue form from control room | January | 2013 | 2013Q3 | 2013 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 655 | N | 48 | Y | Y | 1.1101 | 39.4971 | 8615.7843
[7 empty] | 18548 | 20344 | 924361 | 2013-01-18 15:54 | 2013-01-19 01:00 | 546 | 11kV | 153947 | 443 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | REC 47817 Buff Point Elouera tripped C phase HV dropout assembly broken @PT11753 see 926318 926320 926321 926323 | January | 2013 | 2013Q3 | 2013 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 347.5102 | N | 48 | Y | Y | 1.1101 | 39.4971 | 112499.9269
[7 empty] | 18477 | 19539 | 924655 | 2013-01-18 20:00 | 2013-01-19 01:08 | 308 | 11kV | 34187 | 120 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134299 Reclose off total fire ban Earth fault Sub 53095 DOLF restored at 00:54 19/1/13 during switching Excluded OMS 924655 & 924672 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-01-18 | N | 284.8917 | N | 48 | Y | Y | 1.1101 | 39.4971 | 24982.8513
[7 empty] | 17009 | 3658 | 924890 | 2013-01-18 23:38 | 2013-01-19 01:24 | 106 | 11kV | 127094 | 1199 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Zn.12690 berkeley Vale Pnl.19 tripped on A & C phase IOC weather related | January | 2013 | 2013Q3 | 2013 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2013-01-18 | N | 106 | N | 48 | Y | Y | 1.1101 | 39.4971 | 92876.5466
[7 empty] | 17013 | 3712 | 924872 | 2013-01-18 22:57 | 2013-01-19 02:55 | 238 | 11kV | 10472 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At CP823 Eton Winchester A and C phase fuse operated Cause: Tree brought down OH outside 37 Winchester Ave | January | 2013 | 2013Q3 | 2013 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | KU-RING-GAI | OH | Veg | 2013-01-18 | N | 238 | N | 48 | Y | Y | 1.1101 | 39.4971 | 7652.6287
[7 empty] | 16664 | 1022 | 924014 | 2013-01-18 12:24 | 2013-01-19 05:58 | 1054 | 11kV | 57120 | 369 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn.12650 West Gosford tripped on E/F, EFI UG ground fault in sections from Zn.12650 to S18166 and from S18166 to S12281 - both failed see 926138 926141 926142 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA5 | ZN12650:PA5 | ZN12650/000005 | CENTRAL COAST | UG | Not Veg | 2013-01-18 | N | 154.7967 | N | 48 | Y | Y | 1.1101 | 39.4971 | 41741.6112
[7 empty] | 18159 | 16132 | 924925 | 2013-01-19 07:08 | 2013-01-19 08:30 | 82 | 11kV | 902 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134303 A phase DOLF : 10 Amp Exclyuded OMS 924934 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-01-19 | N | 82 | N | 9 | N | N | 1.1101 | 39.4971 | 659.155
[7 empty] | 17541 | 9066 | 924462 | 2013-01-18 17:01 | 2013-01-19 09:30 | 989 | 11kV | 104978 | 272 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 1126 Mona Vale Rd tripped on OC and lockout after trees on OH due to southerly wind change | January | 2013 | 2013Q3 | 2013 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2013-01-18 | N | 385.9485 | N | 48 | Y | Y | 1.1101 | 39.4971 | 76714.8261
[7 empty] | 17687 | 11427 | 924484 | 2013-01-18 17:12 | 2013-01-19 09:30 | 978 | 11kV | 42054 | 43 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT13954 Meroo Bay - Footpath phase HDO assembly failed heat CC1: 22-"Refer to SOp" | January | 2013 | 2013Q3 | 2013 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 978 | N | 48 | Y | Y | 1.1101 | 39.4971 | 30731.8228
[7 empty] | 16508 | 55 | 924855 | 2013-01-18 22:38 | 2013-01-19 09:30 | 652 | 11kV | 7824 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT13268 Jilliby Durrens 4.1 - centre phase 16A HD failed | January | 2013 | 2013Q3 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 652 | N | 48 | Y | Y | 1.1101 | 39.4971 | 5717.5484
[7 empty] | 18081 | 15605 | 924917 | 2013-01-18 22:30 | 2013-01-19 09:50 | 680 | 11kV | 38760 | 57 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 10202 Neville Rosa - HDO centre phase. Possibly blown during outage earlier and was not reinstated afterwards. First call came in at 22 30. Rolled up late at 06 13. | January | 2013 | 2013Q3 | 2013 | ZN10994:PA13 | ZN10994:PA13 | ZN10994/000013 | GEORGES RIVER | OH | Not Veg | 2013-01-18 | N | 680 | N | 48 | Y | Y | 1.1101 | 39.4971 | 28324.6648
[7 empty] | 17733 | 11833 | 924786 | 2013-01-18 21:32 | 2013-01-19 09:50 | 738 | 11kV | 4428 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13265 Jilliby Durren 2.4 - Footpath side HDO assembly failed resotred via LV // | January | 2013 | 2013Q3 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 738 | N | 48 | Y | Y | 1.1101 | 39.4971 | 3235.8518
[7 empty] | 16951 | 3264 | 924943 | 2013-01-19 07:28 | 2013-01-19 10:00 | 152 | 11kV | 456 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134307 Single phase DOLF : 10 Amp Excluded OMS 924943 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-01-19 | N | 152 | N | 9 | N | N | 1.1101 | 39.4971 | 333.2314
[7 empty] | 18038 | 14907 | 924622 | 2013-01-18 19:40 | 2013-01-19 10:21 | 881 | 11kV | 52026 | 180 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 134302 1 fault operation 3 phase Reclose disabled due to Total Fire Ban. Termination broken to LF 27387. Excluded OMS No. 924622 + 924911 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-01-18 | N | 289.0333 | N | 48 | Y | Y | 1.1101 | 39.4971 | 38019.0663
[7 empty] | 17155 | 5074 | 924147 | 2013-01-18 14:16 | 2013-01-19 10:45 | 1229 | 11kV | 4916 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT11597 Scenic Charles Kay 0.5 - Centre phase HDO failed see 926107 926106 | January | 2013 | 2013Q3 | 2013 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 1229 | N | 48 | Y | Y | 1.1101 | 39.4971 | 3592.4678
[7 empty] | 16526 | 137 | 924779 | 2013-01-18 21:31 | 2013-01-19 11:30 | 839 | 11kV | 839 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134313 Single phase DOLF : 10 Amp Excluded OMS No. 924779 | January | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-01-18 | N | 839 | N | 48 | Y | Y | 1.1101 | 39.4971 | 613.1165
[7 empty] | 17012 | 3701 | 924531 | 2013-01-18 17:58 | 2013-01-19 11:45 | 1067 | 11kV | 9603 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | PT11670 Tapley Taylors - Footpath & roadside phase HDO operated transformer failure | January | 2013 | 2013Q3 | 2013 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 1067 | N | 48 | Y | Y | 1.1101 | 39.4971 | 7017.5892
[7 empty] | 17935 | 13421 | 924922 | 2013-01-19 06:19 | 2013-01-19 12:05 | 346.2 | 11kV | 1204.35 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134310 Single phase DOLF : 16 Amp Tx Volts : 241Volts | January | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2013-01-19 | N | 301.0875 | N | 9 | N | N | 1.1101 | 39.4971 | 880.1035
[7 empty] | 17249 | 6534 | 925046 | 2013-01-19 10:42 | 2013-01-19 15:00 | 258 | 11kV | 516 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134319 A phase DOLF : 10 Amp Excluded OMS 925046 | January | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-01-19 | N | 258 | N | 9 | N | N | 1.1101 | 39.4971 | 377.0776
[7 empty] | 17470 | 8526 | 924179 | 2013-01-18 14:44 | 2013-01-19 15:15 | 1471 | 11kV | 58840 | 40 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | PT13649 Pacific Point 0.3 - Centre phase HDo broken Carrier failure due to extreme heat | January | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-01-18 | N | 1471 | N | 48 | Y | Y | 1.1101 | 39.4971 | 42998.5365
[7 empty] | 18410 | 18679 | 925111 | 2013-01-19 14:00 | 2013-01-19 15:20 | 80 | 11kV | 240 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | S.13797 & PT46997 interrupted to allow repairs to PT HDO fuse assembly fuse carrier failed due to extreme heat @ PT13649 | January | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-01-19 | N | 80 | N | 9 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 17583 | 9716 | 924987 | 2013-01-19 08:56 | 2013-01-19 17:00 | 484 | 11kV | 3388 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13247 Yarramalong Boyds 3.2 -roadside HDO broken see seperate in terruption to PT18116 for repairs | January | 2013 | 2013Q3 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-01-19 | N | 484 | N | 9 | N | N | 1.1101 | 39.4971 | 2475.8505
[7 empty] | 17262 | 6658 | 924981 | 2013-01-19 08:41 | 2013-01-19 17:50 | 549 | 11kV | 1647 | 3 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 134308 A & B phase DOLF : 16 Amp, LF 12058 found blown & tapping off at top of LF. section isolated to make repairs suspect fault on UG cable, left isolated. Repairs completed at 20/01/13 15:35 as per LID Note: 19/01/13 19:23 T45340: gen installed @ 17.15hrs Excluded oms # 924981 | January | 2013 | 2013Q3 | 2013 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | UG | Not Veg | 2013-01-19 | N | 549 | N | 9 | N | N | 1.1101 | 39.4971 | 1203.579
[7 empty] | 17865 | 12844 | 925119 | 2013-01-19 15:38 | 2013-01-19 18:10 | 152 | 11kV | 304 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134324 A phase DOLF Excluded OMS 925119 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-19 | N | 152 | N | 9 | N | N | 1.1101 | 39.4971 | 222.1542
[7 empty] | 17899 | 13127 | 925008 | 2013-01-19 13:00 | 2013-01-19 18:15 | 315 | 11kV | 43925 | 454 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | iR49684 tripped & locked out on O/C earth fault Defective UGOH to S14713 Glenrock Johns - UGOH disconnected and generator attached see 926369 926370 926371 | January | 2013 | 2013Q3 | 2013 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | Unknown | Unknown | 2013-01-19 | N | 96.7511 | N | 9 | N | N | 1.1101 | 39.4971 | 32099.0944
[7 empty] | 18293 | 17393 | 925218 | 2013-01-20 08:01 | 2013-01-20 09:03 | 62 | 11kV | 124 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Rain Light | N | LID 134330 C phase DOLF : 20 Amp Dead bird found at sub. Tx Volts: 250V Excluded OMS No. 925218 | January | 2013 | 2013Q3 | 2013 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-01-20 | N | 62 | N | 7 | N | N | 1.1101 | 39.4971 | 90.6155
[7 empty] | 18233 | 16912 | 925599 | 2013-01-20 09:04 | 2013-01-20 09:10 | 6 | 11kV | 774 | 129 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134331 1 fault operation RAGCB opened during SI 30063 no cause found. System abnormal ABS 18680 closed & Sw 46031 open. | January | 2013 | 2013Q3 | 2013 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2013-01-20 | N | 6 | N | 7 | N | N | 1.1101 | 39.4971 | 565.6164
[7 empty] | 16511 | 78 | 925207 | 2013-01-20 06:35 | 2013-01-20 11:42 | 307 | 11kV | 151092 | 815 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 134327 3 fault operations Earth fault Replaced faulty LAs at UGOH pole MQ-10137 Excluded oms # 925207 | January | 2013 | 2013Q3 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2013-01-20 | N | 185.389 | N | 7 | N | N | 1.1101 | 39.4971 | 110413.5771
[7 empty] | 16654 | 962 | 925243 | 2013-01-20 09:54 | 2013-01-20 16:00 | 366 | 11kV | 49099 | 613 | HV | Arcing | Equipment Failure | Pole | Unplanned | Unselected | N | REC 48039 tripped on SEL Pole fire due to surge arrestors tracking @ PT11723 see 926390 926391 | January | 2013 | 2013Q3 | 2013 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2013-01-20 | N | 80.0962 | N | 7 | N | N | 1.1101 | 39.4971 | 35880.101
[7 empty] | 16517 | 98 | 925272 | 2013-01-20 11:34 | 2013-01-20 16:51 | 317 | 11kV | 13547 | 172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 27 - Earth Leakage, EFIs, EFC. Suspected UG fault from S 1825 SW/B to S 7885 SW/A. | January | 2013 | 2013Q3 | 2013 | ZN690:PA27 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-20 | N | 78.7616 | N | 7 | N | N | 1.1101 | 39.4971 | 9899.748
[7 empty] | 16879 | 2545 | 925278 | 2013-01-20 11:50 | 2013-01-20 18:50 | 420 | 11kV | 167940 | 401 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | REC 50001 tripped on OC trip, LO Bond on pole @ Re45202 shorted onto king bolt of LA's see 926396 926397 926400 926399 | January | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-01-20 | N | 418.803 | N | 7 | N | N | 1.1101 | 39.4971 | 122725.5986
[7 empty] | 18545 | 20322 | 925340 | 2013-01-20 20:06 | 2013-01-20 20:51 | 45 | 11kV | 14715 | 327 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 22381 tripped after tree branch fell onto OH mains in Walter Rd near Cicada Glen Rd, Bayview. D.Op removed branch | January | 2013 | 2013Q3 | 2013 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2013-01-20 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 10753.288
[7 empty] | 17922 | 13347 | 925596 | 2013-01-21 11:04 | 2013-01-21 14:10 | 186 | 11kV | 5022 | 27 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Section of Pnl5 Wyong interrupted from LB42565 to AB42820 to allow T/Con to reapir HV fuse assembly @ PT13265 which was broken after heatwave on 18/1/13 | January | 2013 | 2013Q3 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-01-21 | N | 186 | N | 5 | N | N | 1.1101 | 39.4971 | 3669.9295
[7 empty] | 17360 | 7569 | 925785 | 2013-01-21 15:08 | 2013-01-21 16:01 | 53 | 11kV | 95506 | 1802 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | ZN 9035 Caringbah - Pnl 4R - A & C phase IOC, EFIs, Timing, LO. S 9216 Parkes Davis possible 11kV Feeder fualt on customers Feeder/Switchgear. OCB at S 9216 SW/A found closed. O/C flag found down but fault was cleared back at the Zone. T/PE to investigate. | January | 2013 | 2013Q3 | 2013 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | Unknown | Not Veg | 2013-01-21 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 69792.9678
[7 empty] | 16598 | 599 | 925765 | 2013-01-21 14:48 | 2013-01-21 16:40 | 112 | 11kV | 10192 | 91 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT12722 defective HV fuse from 18/1/13 interrupted from USL40165 to repair | January | 2013 | 2013Q3 | 2013 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2013-01-21 | N | 112 | N | 5 | N | N | 1.1101 | 39.4971 | 7448.013
[7 empty] | 16760 | 1710 | 926022 | 2013-01-21 21:15 | 2013-01-21 22:10 | 55 | 11kV | 44770 | 814 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15002 Narrabeen, Panel 8 Fdr CB tripped on earth fault, fault check, efi, 11kV trip, zone earth. Field efi's down at CP.24276, S.47436, S.15366, S.16347, S.16193. Possum on 11kV UG/OH in Garden St, North Narrabeen | January | 2013 | 2013Q3 | 2013 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2013-01-21 | N | 55 | N | 5 | N | N | 1.1101 | 39.4971 | 32716.5955
[7 empty] | 18340 | 17790 | 926030 | 2013-01-21 23:58 | 2013-01-22 01:45 | 107 | 11kV | 155484 | 2344 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.17L tripped on: IOC, Earth Fault Possilbe 11kV UG feeder fault from S18093 to S14673 tee PT11627 see 926832 926831 926829 926828 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | UG | Not Veg | 2013-01-21 | N | 66.3328 | N | 5 | N | N | 1.1101 | 39.4971 | 113623.1212
[7 empty] | 17539 | 9057 | 926028 | 2013-01-22 01:20 | 2013-01-22 02:45 | 85 | 11kV | 255 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134344 Isolated sub to repair twisted service, sub not retrofitted. Excluded OMS 926028 | January | 2013 | 2013Q3 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2013-01-22 | N | 85 | N | 18 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 18113 | 15864 | 926258 | 2013-01-22 11:22 | 2013-01-22 15:37 | 255 | 11kV | 8079 | 82 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 134352 1 fault operation A & B phase Earth fault: Overcurrent 11kV OHM off insulator at pole SF-70166. Excluded OMS No. 926258 + 926338 | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-01-22 | N | 98.5244 | N | 18 | N | N | 1.1101 | 39.4971 | 5903.8949
[7 empty] | 18375 | 18142 | 926456 | 2013-01-22 15:58 | 2013-01-22 17:48 | 110 | 11kV | 148814 | 1685 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | ZN 9700 Kirrawee - Pnl 23 - Overcurrent. Lightning strike during storm in the area. DOp patrolled and restored progressively. | January | 2013 | 2013Q3 | 2013 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Veg | 2013-01-22 | N | 88.3169 | N | 18 | N | N | 1.1101 | 39.4971 | 108748.8819
[7 empty] | 17974 | 13974 | 926493 | 2013-01-22 17:18 | 2013-01-22 18:33 | 75 | 11kV | 7950 | 106 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Unselected | N | PT 9458 Pinaroo Pl hit by lightning HDO blown. Dop tried restoring HDO but volts at PT were 190 volts on one phase with no load connected. PT 9458 Pinaroo in LV// and de energised only HV and Alive in LV. T/Con to inspect tomorrow DMA created. Note: OATLEY SUBS REPLACED DEFECTIVE TRANSFORMER ON 24.1.13.NFA. also refer to 926493 and 926505 | January | 2013 | 2013Q3 | 2013 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2013-01-22 | N | 75 | N | 18 | N | N | 1.1101 | 39.4971 | 5809.6255
[7 empty] | 16628 | 834 | 926688 | 2013-01-22 17:16 | 2013-01-22 19:00 | 104 | 11kV | 94536 | 909 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134365 2 fault operations 3 phase Overcurrent locked out | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-01-22 | N | 104 | N | 18 | N | N | 1.1101 | 39.4971 | 69084.1205
[7 empty] | 16713 | 1295 | 926048 | 2013-01-22 15:20 | 2013-01-22 19:30 | 250 | 11kV | 250 | 1 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S14107 interrupted for jointers to repair HV UGOH Organised with customer prior | January | 2013 | 2013Q3 | 2013 | ZN14892:PA8 | ZN14892:PA8 | ZN14892/000008 | CENTRAL COAST | UG | Not Veg | 2013-01-22 | N | 250 | N | 18 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 17109 | 4485 | 926518 | 2013-01-22 18:04 | 2013-01-22 19:48 | 104.1333 | 11kV | 2499.2 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134373 B phase DOLF : 31 Amp | January | 2013 | 2013Q3 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2013-01-22 | N | 104.1333 | N | 18 | N | N | 1.1101 | 39.4971 | 1826.3416
[7 empty] | 16944 | 3195 | 926504 | 2013-01-22 17:35 | 2013-01-22 20:45 | 190 | 11kV | 19380 | 102 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134370 2 fault operations 3 phase Earth fault; Overcurrent fdr tripped and lock out on: Excluded oms 926504 | January | 2013 | 2013Q3 | 2013 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2013-01-22 | N | 190 | N | 18 | N | N | 1.1101 | 39.4971 | 14162.3324
[7 empty] | 18257 | 17109 | 926557 | 2013-01-22 19:39 | 2013-01-22 21:18 | 99 | 11kV | 84150 | 850 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | iR49613 - suspected to have tripped - no outage report from control room based on dmns data iR49613 tripped and was resotred @ 21:18 Cause not ascertained | January | 2013 | 2013Q3 | 2013 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2013-01-22 | N | 99 | N | 18 | N | N | 1.1101 | 39.4971 | 61494.338
[7 empty] | 17130 | 4631 | 926500 | 2013-01-22 17:29 | 2013-01-22 21:30 | 241 | 11kV | 241 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134374 Single phase DOLF : 10 Amp Excluded OMS 926500 Note: customer was also affected prior and during this event by feeder level outage - refer to 926688 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-22 | N | 241 | N | 18 | N | N | 1.1101 | 39.4971 | 176.1157
[7 empty] | 18405 | 18531 | 926583 | 2013-01-22 17:29 | 2013-01-22 22:00 | 271 | 11kV | 271 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134375 A & B phase DOLF : 10 Amp Excluded OMS 926583 Note: customer was also affected prior and during this event by feeder level outage - refer to 926688 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-22 | N | 271 | N | 18 | N | N | 1.1101 | 39.4971 | 198.0388
[7 empty] | 17202 | 5922 | 926594 | 2013-01-22 20:55 | 2013-01-22 22:45 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134378 C phase DOLF : 10 Amp Stated sub 48872 but found OK nobody answering phone but found DOLF down D Howe sub 49173 with same name as customer in OMS. Excluded OMS 926594 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-22 | N | 110 | N | 18 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 16883 | 2589 | 926544 | 2013-01-22 19:00 | 2013-01-22 23:24 | 264.9333 | 11kV | 474.9333 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134376 A phase DOLF : 3 Amp Excluded OMS 926603 | January | 2013 | 2013Q3 | 2013 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | UG | Not Veg | 2013-01-22 | N | 237.4667 | N | 18 | N | N | 1.1101 | 39.4971 | 347.0673
[7 empty] | 17001 | 3571 | 926555 | 2013-01-22 19:32 | 2013-01-23 00:05 | 273 | 11kV | 199799 | 1340 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | REC 47607 Toomeys tripped on SEF HV UGOH fault on tee to S14191 see 926847 926849 826850 | January | 2013 | 2013Q3 | 2013 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | Unknown | Unknown | 2013-01-22 | N | 149.1037 | N | 18 | N | N | 1.1101 | 39.4971 | 146007.2161
[7 empty] | 17988 | 14140 | 926488 | 2013-01-22 17:10 | 2013-01-23 02:25 | 555 | 11kV | 9990 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134384 A phase DOLF : 2 Amp Excluded OMS 926488 | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | SINGLETON | OH | Veg | 2013-01-22 | N | 555 | N | 18 | N | N | 1.1101 | 39.4971 | 7300.3973
[7 empty] | 17872 | 12876 | 926614 | 2013-01-23 04:14 | 2013-01-23 08:05 | 231 | 11kV | 462 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134398 A phase DOLF | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-23 | N | 231 | N | 9 | N | N | 1.1101 | 39.4971 | 337.616
[7 empty] | 17355 | 7504 | 926625 | 2013-01-23 06:27 | 2013-01-23 08:20 | 113 | 11kV | 226 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134397 C phase DOLF : 10 Amp Excluded MS 926625 | January | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-01-23 | N | 113 | N | 9 | N | N | 1.1101 | 39.4971 | 165.1541
[7 empty] | 17796 | 12360 | 926641 | 2013-01-23 07:38 | 2013-01-23 08:44 | 66 | 11kV | 330 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134395 C phase DOLF : 10 Amp Excluded OMS 926641 | January | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2013-01-23 | N | 66 | N | 9 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 17858 | 12765 | 926633 | 2013-01-23 07:07 | 2013-01-23 09:34 | 147 | 11kV | 294 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134392 C phase DOLF : 10 Amp Excluded OMS 926633 | January | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-01-23 | N | 147 | N | 9 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 17596 | 9808 | 926550 | 2013-01-22 19:25 | 2013-01-23 09:45 | 860 | 11kV | 24925 | 31 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134383 A phase DOLF : 20 Amp replaced lightning arrestors at recloser Excluded OMS 926550 | January | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2013-01-22 | N | 804.0323 | N | 18 | N | N | 1.1101 | 39.4971 | 18214.4548
[7 empty] | 18428 | 18908 | 926516 | 2013-01-22 17:55 | 2013-01-23 11:15 | 1040 | 11kV | 17680 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 134382 3 phase DOLF : 10 Amp DOLF's replaced still down LV phase unable to climb nailed pole to check. EWP arranged for 0700hrs 23/1/13 Excluded OMS 926516 | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | UG | Not Veg | 2013-01-22 | N | 1040 | N | 18 | N | N | 1.1101 | 39.4971 | 12920.0225
[7 empty] | 17471 | 8530 | 926471 | 2013-01-22 16:37 | 2013-01-23 13:20 | 1243 | 11kV | 42006 | 77 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 134364 3 fault operations 3 phase Earth fault Faulty Transformer sub 52622 to be replaced 23/1/13 at start day shift. Excluded oms 926471, 926581, 926609 | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2013-01-22 | N | 545.5325 | N | 18 | N | N | 1.1101 | 39.4971 | 30696.7458
[7 empty] | 18315 | 17589 | 926731 | 2013-01-23 09:46 | 2013-01-23 15:00 | 314 | 11kV | 1570 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134402 Single phase Earth fault recloser tripped when staff were rreplacing fuses at sub 70225 see report 134401, OMS 933503 Excluded records 926731 and 927435 | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2013-01-23 | N | 314 | N | 9 | N | N | 1.1101 | 39.4971 | 1147.3097
[7 empty] | 18520 | 20037 | 927421 | 2013-01-23 09:46 | 2013-01-23 15:30 | 344 | 11kV | 344 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134400 Single phase DOLF Excluded 927421 | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2013-01-23 | N | 344 | N | 9 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 16790 | 1985 | 926845 | 2013-01-23 12:10 | 2013-01-23 16:00 | 230 | 11kV | 5750 | 25 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 134404 sub 58423 isolated to repair pole sw 32000 Excluded OMS 926845 | January | 2013 | 2013Q3 | 2013 | 222:2017 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | UG | Not Veg | 2013-01-23 | N | 230 | N | 9 | N | N | 1.1101 | 39.4971 | 4201.9304
[7 empty] | 18251 | 17078 | 926681 | 2013-01-23 08:39 | 2013-01-23 18:10 | 571 | 11kV | 571 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC Transformer | Unplanned | Previous Storm | N | LID 134401 Single phase sub isolated to replace faulty tx Excluded oms 926681, 927416 | January | 2013 | 2013Q3 | 2013 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2013-01-23 | N | 571 | N | 9 | N | N | 1.1101 | 39.4971 | 417.27
[7 empty] | 16513 | 86 | 927098 | 2013-01-23 18:52 | 2013-01-23 22:50 | 238 | 11kV | 2380 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134406 LL Crew replaced faulty DOLF. Excluded OMS 927098. | January | 2013 | 2013Q3 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2013-01-23 | N | 238 | N | 9 | N | N | 1.1101 | 39.4971 | 1739.2338
[7 empty] | 17014 | 3726 | 927480 | 2013-01-24 14:02 | 2013-01-24 15:50 | 108 | 11kV | 108 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134421 C phase DOLF : VOLTS =245 LOAD A-230 B- 330 C- 315. Excluded OMS REPORT NO 927480. | January | 2013 | 2013Q3 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | UG | Not Veg | 2013-01-24 | N | 108 | N | 4 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 18321 | 17688 | 927506 | 2013-01-24 14:47 | 2013-01-24 16:15 | 88 | 11kV | 99264 | 1128 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn901 Surry Hills - 11kv Panel No.14 "Sub 1266 Bourke Crescent No.2 " feeder tripped. Relays: A phase timed O/C, earth faults, EFI Signals: 11kv trip, No.3 Group Earth, Zone Earth Field EFI's: Nil Remarks: UG fault on 11kv feeder from Zn901 Surry Hills Panel No.14 to Sub 12660 Bourke Crescent NO.2. Suspect parallel with S35036 Dist 1 & S8766 Dist 3 Related jobs: #930976, 930982, 930970, 927506, 927532, 927524, 927529 | January | 2013 | 2013Q3 | 2013 | ZN901:PA14 | ZN901:PA32 | ZN00901/000032 | SYDNEY | UG | Not Veg | 2013-01-24 | N | 88 | N | 4 | N | N | 1.1101 | 39.4971 | 72539.2034
[7 empty] | 17645 | 10716 | 930160 | 2013-01-24 18:04 | 2013-01-24 19:00 | 56 | 11kV | 9304 | 179 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3425 Castle Cove Pa32 Tripped on Earth Leakage, Sealing Contactor, EFI and Fault Check. Cause: 11kV Feeder from S8016 High Short See OMS 930160 930162 927592 | January | 2013 | 2013Q3 | 2013 | ZN3425:PA32 | ZN3425:PA32 | ZN03425/000032 | WILLOUGHBY | UG | Not Veg | 2013-01-24 | N | 51.9777 | N | 4 | N | N | 1.1101 | 39.4971 | 6799.0888
[7 empty] | 17683 | 11346 | 927618 | 2013-01-25 00:12 | 2013-01-25 01:16 | 64 | 11kV | 44474 | 746 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | At S901 Surry Hills, Pabek 19 'Redfern Gib' 11kv feeder tripped on; A phase O/L, EFI Alarms: 11kv trip, ZE, TX3 GE Field EFI's operated at S3744, S35287 Remarks: end box fault. At S1916 James Ren, TX1 etc fdr Related jobs: #927618, 930583, 930580 | January | 2013 | 2013Q3 | 2013 | ZN901:PA19 | ZN901:PA31 | ZN00901/000031 | SYDNEY | Unknown | Not Veg | 2013-01-25 | N | 59.6166 | N | 3 | N | N | 1.1101 | 39.4971 | 32500.2874
[7 empty] | 17029 | 3926 | 927360 | 2013-01-24 11:33 | 2013-01-25 03:11 | 938 | 11kV | 64778 | 1521 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Rain Heavy | N | LID 134418 2 fault operations A & B phase Overcurrent Back hoe dug up cable at BHP research Labs. University to arrange cable repairs. Excluded OMS# 927375 | January | 2013 | 2013Q3 | 2013 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | UG | Not Veg | 2013-01-24 | N | 42.5891 | N | 4 | N | N | 1.1101 | 39.4971 | 47337.8518
[7 empty] | 17729 | 11797 | 927990 | 2013-01-25 18:42 | 2013-01-25 20:10 | 88 | 11kV | 36518 | 461 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Section of 11kV feeder from Ab398 to Ab1775 Interrupted by DOp to Extinguish fire on AB1775. See OMS 933214 933216 933218 927911/996/8011/8012 | January | 2013 | 2013Q3 | 2013 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Not Veg | 2013-01-25 | N | 79.2148 | N | 3 | N | N | 1.1101 | 39.4971 | 26686.2773
[7 empty] | 17136 | 4699 | 928016 | 2013-01-25 19:56 | 2013-01-25 21:30 | 94 | 11kV | 94 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134436 A & C phase DOLF : 10 Amp possible previous storm Excluded OMS 928016 | January | 2013 | 2013Q3 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2013-01-25 | N | 94 | N | 3 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 17493 | 8745 | 928032 | 2013-01-26 00:42 | 2013-01-26 06:45 | 363 | 11kV | 32670 | 90 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT13980 Cutler Harvey - roadside HDO fuse failed fuse failure see 929558 929559 | January | 2013 | 2013Q3 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-01-26 | N | 363 | N | 5 | N | N | 1.1101 | 39.4971 | 23874.2724
[7 empty] | 16732 | 1425 | 928052 | 2013-01-26 08:20 | 2013-01-26 09:20 | 60 | 11kV | 60 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134437 A phase DOLF : 10 Amp Excluded OMS 928052 | January | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2013-01-26 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 17020 | 3820 | 928110 | 2013-01-26 13:15 | 2013-01-26 14:31 | 76 | 11kV | 19152 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 134440 2 fault operation A phase Overcurrent No Fault found PLEASE PATROL FDR. Exclided OMS report no 928110 | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2013-01-26 | N | 76 | N | 5 | N | N | 1.1101 | 39.4971 | 13995.7167
[7 empty] | 17695 | 11496 | 928149 | 2013-01-26 16:19 | 2013-01-26 18:00 | 101 | 11kV | 25452 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 134442 3 fault operations A phase Overcurrent OMS REPORT NO 928150. FDR TRIPPED & RECLOSED THEN TRIPPED AGAIN. LINE PATROL CARRIED OUT WITH NOTHING FOUND. FULL LINE PATROL REQUIRED. 13 FAULT OPERATIONS SINCE 09/01/13 | January | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2013-01-26 | N | 101 | N | 5 | N | N | 1.1101 | 39.4971 | 18599.5709
[7 empty] | 17773 | 12107 | 928102 | 2013-01-26 12:56 | 2013-01-26 20:00 | 424 | 11kV | 50984 | 419 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 134443 2 fault operation A phase Earth fault; Overcurrent OMS REPORT NO 928102.MAINS DOWN AT POLE JP-86503. SW 47812 TRIPPED & RECLOSED ON OVERCURRENT. SW 82578 TRIPPED & LOCKED OUT ON E/FAULT. PLEASE INVESTIGATE GRADINGS. # | January | 2013 | 2013Q3 | 2013 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2013-01-26 | N | 121.6802 | N | 5 | N | N | 1.1101 | 39.4971 | 37257.6034
[7 empty] | 17317 | 7227 | 928251 | 2013-01-27 02:10 | 2013-01-27 06:35 | 265 | 11kV | 5936 | 33 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 134444 4 fault operations Blown LA at sub 72108 replaced by A Regan. It appears sub fuse may not have graded with rec w/ 35A PU Excluded OMS 928251 | January | 2013 | 2013Q3 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2013-01-27 | N | 179.8788 | N | 17 | N | N | 1.1101 | 39.4971 | 4337.8537
[7 empty] | 18381 | 18216 | 928260 | 2013-01-27 06:16 | 2013-01-27 07:32 | 76 | 11kV | 53470 | 713 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | LID 134446 2 fault operations 3 phase Overcurrent Tree branch on mains near pole NR-60683 Hutcheson Rd. Trees overhanging mains in this area. Excluded OMS 928260 | January | 2013 | 2013Q3 | 2013 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2013-01-27 | N | 74.993 | N | 17 | N | N | 1.1101 | 39.4971 | 39074.2989
[7 empty] | 18519 | 20020 | 928253 | 2013-01-27 04:57 | 2013-01-27 08:05 | 188 | 11kV | 376 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 134447 Single phase DOLF : 10 Amp Excluded OMS 928253 | January | 2013 | 2013Q3 | 2013 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2013-01-27 | N | 188 | N | 17 | N | N | 1.1101 | 39.4971 | 274.7697
[7 empty] | 18307 | 17529 | 928307 | 2013-01-27 08:29 | 2013-01-27 09:15 | 46 | 11kV | 93850 | 2835 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | S342 Paddington Panel 26 "McLachlan Boundary etc" fdr tripped Relays - Earth Fault, EFI Signals - Zone Earth, Group earth Tx4 Remarks: Front line feeder fault from Panel 26 to S8252 McLachlan Boundary to S6899 Brougham Lane to S778 Glenmore Rd Related jobs: #928307, 930713, 930712, 930708 | January | 2013 | 2013Q3 | 2013 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2013-01-27 | N | 33.1041 | N | 17 | N | N | 1.1101 | 39.4971 | 68582.8119
[7 empty] | 17662 | 10929 | 928286 | 2013-01-27 07:51 | 2013-01-27 09:22 | 91 | 11kV | 11102 | 122 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 21350 tripped and locked out on OC. Tree branch removedd from OH near UG/OH supplying Japanese School | January | 2013 | 2013Q3 | 2013 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2013-01-27 | N | 91 | N | 17 | N | N | 1.1101 | 39.4971 | 8113.0141
[7 empty] | 16953 | 3272 | 928289 | 2013-01-27 08:04 | 2013-01-27 09:31 | 87 | 11kV | 174 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 134448 A phase DOLF : 10 Amp Excluded OMS 928289 | January | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2013-01-27 | N | 87 | N | 17 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 18075 | 15557 | 928295 | 2013-01-27 08:15 | 2013-01-27 10:10 | 115 | 11kV | 805 | 7 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | PT14507 Arundal Milina - Centre phase HDO operated Bark across curge diverter | January | 2013 | 2013Q3 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2013-01-27 | N | 115 | N | 17 | N | N | 1.1101 | 39.4971 | 588.2703
[7 empty] | 17819 | 12500 | 928403 | 2013-01-27 11:50 | 2013-01-27 13:35 | 105.1833 | 11kV | 1367.3833 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 134450 Single phase DOLF : 20 Amp | January | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-01-27 | N | 105.1833 | N | 17 | N | N | 1.1101 | 39.4971 | 999.2434
[7 empty] | 18495 | 19845 | 928275 | 2013-01-27 07:20 | 2013-01-27 13:40 | 380 | 11kV | 128540 | 1178 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.12610 Long Jetty Pnl.17 tripped, reclosed & locked out on A phase IOC 11kV UGOH from Sw B @ S14943 defective. UGOH @ Sw A from S14913 failed on energising (damaged by fault current ) see 929588 929593 929597 | January | 2013 | 2013Q3 | 2013 | ZN12610:PA17 | ZN12610:PA17 | ZN12610/000017 | CENTRAL COAST | Unknown | Unknown | 2013-01-27 | N | 109.1171 | N | 17 | N | N | 1.1101 | 39.4971 | 93933.2407
[7 empty] | 17774 | 12115 | 928393 | 2013-01-27 11:33 | 2013-01-27 15:40 | 247 | 11kV | 56491 | 585 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | ZN 9252 Jannali - Pnl 7 - A & C phase IOC, timing, lockout, reclose, tripped, recloser lockout. Bond burnt off. 11kV cable on the ground. | January | 2013 | 2013Q3 | 2013 | ZN9252:PA7 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2013-01-27 | N | 96.5658 | N | 17 | N | N | 1.1101 | 39.4971 | 41281.9566
[7 empty] | 18278 | 17272 | 928464 | 2013-01-27 14:25 | 2013-01-27 16:14 | 109 | 11kV | 98893 | 1027 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn.14144 Wamberal Pnl.17 tripped & locked out on Earth Fault Cause not ascertained see 929617 929621 929623 929626 | January | 2013 | 2013Q3 | 2013 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2013-01-27 | N | 96.2931 | N | 17 | N | N | 1.1101 | 39.4971 | 72268.0876
[7 empty] | 17077 | 4258 | 928519 | 2013-01-27 16:50 | 2013-01-27 17:50 | 60 | 11kV | 8988 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44947 Gavenlock Rd - tripped and locked out on IOC tree branch on OH mains near PT12444 see 929933 929931 | January | 2013 | 2013Q3 | 2013 | ZN12690:PA12 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2013-01-27 | N | 54.8049 | N | 17 | N | N | 1.1101 | 39.4971 | 6568.1653
[7 empty] | 18250 | 17075 | 928462 | 2013-01-27 14:33 | 2013-01-27 18:50 | 257 | 11kV | 514 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134454 Sub isolated to repair LV CABLE BETWEEN TX & LVF BURNT UP. Excluded OMS 928462 | January | 2013 | 2013Q3 | 2013 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2013-01-27 | N | 257 | N | 17 | N | N | 1.1101 | 39.4971 | 375.616
[7 empty] | 18044 | 15070 | 928495 | 2013-01-27 15:53 | 2013-01-27 19:10 | 197 | 11kV | 181711 | 1243 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12620 Noraville Pnl.8 tripped on Basler 51B earth leakage 11kV down at AB41864 causing 2x burnt off bonds at AB42641 centre phase and USL43866 footpath phase see 929868 929870 929872 | January | 2013 | 2013Q3 | 2013 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2013-01-27 | N | 146.1874 | N | 17 | N | N | 1.1101 | 39.4971 | 132789.0392
[7 empty] | 16584 | 556 | 928597 | 2013-01-27 20:01 | 2013-01-27 21:06 | 65 | 11kV | 92651 | 1501 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn.12580 Erina pnl.10 tripped on C phase O/C UGOH Fault short circuit see 930582 930584 | January | 2013 | 2013Q3 | 2013 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | Unknown | Unknown | 2013-01-27 | N | 61.7262 | N | 17 | N | N | 1.1101 | 39.4971 | 67706.6181
[7 empty] | 16846 | 2312 | 928616 | 2013-01-28 00:43 | 2013-01-28 00:57 | 14 | 11kV | 17402 | 1243 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 134455 No protection operation. Fdr opened to make repair at pole MW-47121 Excluded OMS # 928642 & 928616 | January | 2013 | 2013Q3 | 2013 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Not Veg | 2013-01-28 | N | 14 | N | 22 | Y | Y | 1.1101 | 39.4971 | 12716.8683
[7 empty] | 17445 | 8285 | 928630 | 2013-01-27 21:44 | 2013-01-28 04:26 | 402 | 11kV | 51452 | 466 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 134456 1 faulyt operation Overcurrent wire on xarm at pole JT-50047. Excluded oms 928630 & 928631 | January | 2013 | 2013Q3 | 2013 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2013-01-27 | N | 110.412 | N | 17 | N | N | 1.1101 | 39.4971 | 37599.604
[7 empty] | 17499 | 8818 | 928791 | 2013-01-28 12:53 | 2013-01-28 13:50 | 57.15 | 11kV | 2628.9 | 46 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S5086 West Gordon 400A fuse blown on B phase of distributor 2. Cause: Tree branch on Mains in Gordon Cres Near East PDE. Deniston See oMS 928971 928790 CC1: 22-"Refer to SOp" | January | 2013 | 2013Q3 | 2013 | ZN4545:PA40 | ZN4545:PA40 | ZN04545/000040 | RYDE | OH | Veg | 2013-01-28 | N | 57.15 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1921.1226
[7 empty] | 16875 | 2511 | 928563 | 2013-01-27 19:08 | 2013-01-28 15:15 | 1207 | 11kV | 21369 | 117 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC 44602 Ourimbah Cr Rd tripped / reclosed / locked out on O/C, SEF Tree brought down OH beyond LK 43922 see 930530 930531 930533 930537 930538 930540 930189 930534 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-01-27 | N | 182.641 | N | 17 | N | N | 1.1101 | 39.4971 | 15615.8349
[7 empty] | 18562 | 20439 | 928819 | 2013-01-28 13:49 | 2013-01-28 16:47 | 178 | 11kV | 44967 | 665 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.14144 Wamberal pnl.10 tripped on SEF, EFI - Pnl.10 appears to not grade with REC 44607 for a fault beyond that point. REC 44607 matcham also tripped / reclosed / tripped & locked out on : OC - Large tree on mains 33 matcham Rd see 930624 930625 930626 | January | 2013 | 2013Q3 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2013-01-28 | N | 67.6195 | N | 22 | Y | Y | 1.1101 | 39.4971 | 32860.5573
[7 empty] | 18433 | 18943 | 928919 | 2013-01-28 16:20 | 2013-01-28 17:30 | 70 | 11kV | 126673 | 2447 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Heavy | N | @S2310 Punchbowl Panel 28 'AB 748' feeder tripped on: Relays: A & C phase IOC, lockout, timing Signals: 11kv trip, ZE, Tx4 GE Remarks: insulators failed @ AB2462 Related jobs: #930768, 930767, 930764, 928919, 928926, 928934, 928938, 928922, 928930 | January | 2013 | 2013Q3 | 2013 | ZN2310:PA28 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-01-28 | N | 51.7667 | N | 22 | Y | Y | 1.1101 | 39.4971 | 92568.8922
[7 empty] | 17660 | 10925 | 928904 | 2013-01-28 17:06 | 2013-01-28 18:00 | 54 | 11kV | 4644 | 86 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At PT485 Blue Ridge Turner Centre phase HDO blown and C phase doistributor Fuse Cause: Tree Branch on OH mains 928904/949/950/960/015 NOte: Based on customer calls suspect Distributor 1 and 2 Were in Parallel at the time of interruption CC1: 22-"Refer to SOp" | January | 2013 | 2013Q3 | 2013 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2013-01-28 | N | 54 | N | 22 | Y | Y | 1.1101 | 39.4971 | 3393.6982
[7 empty] | 17186 | 5636 | 928878 | 2013-01-28 15:36 | 2013-01-28 18:20 | 164 | 11kV | 94045 | 909 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Rain Light | N | At S1673 Turramurra Panel 13 Tripped on A and B phase IOC Signals: 11kV Trip Field EFIs NIL Cause: 11kV conductors Twistes together in section of OH from UGOH in Grosvenor RD Near Barton Cres. See OMS 930972 979 975 977 931302 928878 928907 | January | 2013 | 2013Q3 | 2013 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Not Veg | 2013-01-28 | N | 103.4598 | N | 22 | Y | Y | 1.1101 | 39.4971 | 68725.3121
[7 empty] | 16907 | 2951 | 928879 | 2013-01-28 16:42 | 2013-01-28 18:47 | 125 | 11kV | 52081 | 1585 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 134460 Tree across 11kV OHM near ABS 2082 & sub 4547 Excluded oms 928879 & 928935 | January | 2013 | 2013Q3 | 2013 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Veg | 2013-01-28 | N | 32.8587 | N | 22 | Y | Y | 1.1101 | 39.4971 | 38059.2587
[7 empty] | 17953 | 13686 | 931826 | 2013-01-28 16:38 | 2013-01-28 18:52 | 134 | 11kV | 36098 | 311 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At S965 Pennant Hills Panel 42 tripped on Aphase Overcurrent, Earth Fault anD EFI Cause; Tree banch on OH mains near PT482 Abnormal Switching: Open Bonds Beyond PT615. Distributors at PT482 and PT615 Normally Open See OMS 931826 931831 931832 | January | 2013 | 2013Q3 | 2013 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Veg | 2013-01-28 | N | 116.0707 | N | 22 | Y | Y | 1.1101 | 39.4971 | 26379.3537
[7 empty] | 17345 | 7405 | 928993 | 2013-01-28 17:33 | 2013-01-28 20:19 | 166 | 11kV | 10458 | 63 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At PT1887 Chapman Cardinal Centre phase and Footpath HDO fuse blew. Cause: Tree branch on PT 11887 Chapman Cardinal Tree on OH mains See OMS 928993 933703 928994 | January | 2013 | 2013Q3 | 2013 | ZN965:PA21 | ZN965:PA21 | ZN00965/000021 | HORNSBY | OH | Veg | 2013-01-28 | N | 166 | N | 22 | Y | Y | 1.1101 | 39.4971 | 7642.3979
[7 empty] | 17646 | 10718 | 929070 | 2013-01-28 18:41 | 2013-01-28 20:30 | 109 | 11kV | 158891 | 2062 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN 9700 Kirrawee - Pnl 17 - A & C phase IOC, timing, fault check, Lockout, EFIs. 11kV UG cable fault from S 9048 to S 9587 tee PT 9551. | January | 2013 | 2013Q3 | 2013 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | UG | Not Veg | 2013-01-28 | N | 77.0567 | N | 22 | Y | Y | 1.1101 | 39.4971 | 116112.8563
[7 empty] | 18503 | 19913 | 928941 | 2013-01-28 16:46 | 2013-01-28 20:35 | 229 | 11kV | 94870 | 482 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At Zn35370 Galston 11kV Pa8 Tripped on B and C phase IOC, EFI and Lockout Cause: Trees O/S No40 Johnson at the beginning of Gully Crossing See OMS 931978 931985 931983 928941/928978 928980 | January | 2013 | 2013Q3 | 2013 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-01-28 | N | 196.8257 | N | 22 | Y | Y | 1.1101 | 39.4971 | 69328.1978
[7 empty] | 17632 | 10564 | 929063 | 2013-01-28 18:36 | 2013-01-28 20:35 | 119 | 11kV | 107112 | 993 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN1193 Lindfield Panel 6 has tripped, Relays 3 pase overcurrent and EFI Signals:11kV Zone Earth Tx1 Group Earth. Cause: Cable Fault between S3420 and S5119 At Cp530 (20:19 to 20:20) Greville Wilfred Tripped and reclosed on Relays: IOC and O/C, Abnormal switching: SW/B Closed at S5122, SW/A open At S5119. On CLosing SWB at S5122 to restore a fault at lindfield RREC530 tripped on inrush current 932049 932051 929063 | January | 2013 | 2013Q3 | 2013 | ZN1193:PA6 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | UG | Not Veg | 2013-01-28 | N | 107.8671 | N | 22 | Y | Y | 1.1101 | 39.4971 | 78274.2903
[7 empty] | 16719 | 1322 | 929220 | 2013-01-28 21:07 | 2013-01-28 21:53 | 46.3167 | 11kV | 2686.3667 | 58 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | PT12362 Hastings Aspen - roadside HDo operated no obvious cause | January | 2013 | 2013Q3 | 2013 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2013-01-28 | N | 46.3167 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1963.1175
[7 empty] | 18131 | 15967 | 929208 | 2013-01-28 20:52 | 2013-01-28 22:47 | 115 | 11kV | 50600 | 440 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134466 1 fault operation Sensitive Earth Fault Sub 12372 isolated LV interconnected. L/A's faulty. Excluded OMS 929208. | January | 2013 | 2013Q3 | 2013 | 225:13444 | 270:83593 | ZN00270/083593 | LAKE MACQUARIE | OH | Not Veg | 2013-01-28 | N | 115 | N | 22 | Y | Y | 1.1101 | 39.4971 | 36976.9876
[7 empty] | 17391 | 7887 | 929281 | 2013-01-28 22:05 | 2013-01-28 23:22 | 77 | 11kV | 7236 | 96 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S.15011 Beacon Hill Panel 1 Fdr CB tripped on the Left Leg:- Earth DFault, fault check, efi, 11kV trip. Field efi's down at S.16649, S.16396, S.16350 ,S.16657 and S.15123. Suspedct cable fault between S.15123 and S.16531 | January | 2013 | 2013Q3 | 2013 | ZN15011:PA1 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | UG | Not Veg | 2013-01-28 | N | 75.375 | N | 22 | Y | Y | 1.1101 | 39.4971 | 5287.8554
[7 empty] | 16685 | 1125 | 929099 | 2013-01-28 19:13 | 2013-01-28 23:55 | 282 | 11kV | 20395 | 76 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Recloser CP3280 Tripped reclosed tripped and locked out on A and B phase O/C Cause: Large Tree on Mains O/S 19 Cotsworld Rd Dural. See OMS 936278 936280 936281 | January | 2013 | 2013Q3 | 2013 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2013-01-28 | N | 268.3553 | N | 22 | Y | Y | 1.1101 | 39.4971 | 14904.0644
[7 empty] | 18466 | 19209 | 929216 | 2013-01-28 20:58 | 2013-01-29 00:01 | 183 | 11kV | 20820 | 159 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 46803 Wise Ferry Dog Trap 0.1 tripped - reclosed and locked out on OC Tree branch on mains near pT13778 see 930751 930753 930755 | January | 2013 | 2013Q3 | 2013 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2013-01-28 | N | 130.9434 | N | 22 | Y | Y | 1.1101 | 39.4971 | 15214.6419
[7 empty] | 16782 | 1939 | 929086 | 2013-01-28 18:58 | 2013-01-29 00:40 | 342 | 11kV | 36088 | 340 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 134462 2 fault operation Earth fault wire on ground at pole ET-87013. Excluded oms 929086 | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2013-01-28 | N | 106.1412 | N | 22 | Y | Y | 1.1101 | 39.4971 | 26372.046
[7 empty] | 16692 | 1144 | 929350 | 2013-01-29 01:11 | 2013-01-29 02:52 | 101 | 11kV | 6451 | 64 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | ZN 1648 Enfield - Pnl 13 - Translay, EFI. UG cable fault between Sub 73902 and S 7815. | January | 2013 | 2013Q3 | 2013 | ZN1648:PA13 | ZN4853:PA22 | ZN04853/000022 | STRATHFIELD | UG | Not Veg | 2013-01-29 | N | 100.7969 | N | 12 | N | N | 1.1101 | 39.4971 | 4714.2005
[7 empty] | 17754 | 11960 | 929274 | 2013-01-28 22:07 | 2013-01-29 03:30 | 323 | 11kV | 24452 | 231 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44995 Kulnura tripped / reclosed / locked out on earth fault tree branch fell across rd bringing down 11kV mains near PT47388 see 931439 931437 | January | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-01-28 | N | 105.8528 | N | 22 | Y | Y | 1.1101 | 39.4971 | 17868.8004
[7 empty] | 17219 | 6144 | 929336 | 2013-01-29 00:08 | 2013-01-29 04:50 | 282 | 11kV | 16238 | 69 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | At S.15013 Terrey Hills, Panel 2 Fdr CB tripped, reclosed tripped and locked out on A&C phase IOC, timing reclose, lockout, fault check, 11kV trip. No field efi's down. Tree branch brought down 11kV OH adjacent to LB.47711 O/S #321 Mona Vale Rd, Terrey Hills | January | 2013 | 2013Q3 | 2013 | ZN15013:PA2 | ZN15013:PA2 | ZN15013/000002 | NORTHERN BEACHES | OH | Veg | 2013-01-29 | N | 235.3333 | N | 12 | N | N | 1.1101 | 39.4971 | 11866.2515
[7 empty] | 18417 | 18773 | 929384 | 2013-01-29 04:42 | 2013-01-29 08:15 | 213 | 11kV | 73201 | 1151 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | At S.15012 killarney, Panel 8 Fdr CB tripped on SEL, fault check, efi, 11kV trip. Field efi's down at S.16789 and S.16846. Flashover and arcing at PT.15429 | January | 2013 | 2013Q3 | 2013 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2013-01-29 | N | 63.5977 | N | 12 | N | N | 1.1101 | 39.4971 | 53493.1317
[7 empty] | 18469 | 19259 | 929710 | 2013-01-29 08:59 | 2013-01-29 10:19 | 80 | 11kV | 154080 | 1950 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn35800 Bankstown 11kv feeder Panel 14 'S5773 Hixsen Archer, S4168 Chapel Shenton' tripped on; Relays: Earth fault, EFI Signals: 11kv trip Field EFI's: Nil Remarks: UG fault.front line 11kv feeder fault from Zn35800 Bankstown to Sub 5773 Hixsen Archer (Sw/B) to sub 4168 Chapel Shenton (Sw/A) Related jobs: #929752, 929751, 929748, 929722, 929714, 929713, 930932, 930931 | January | 2013 | 2013Q3 | 2013 | ZN35800:PA14 | ZN35800:PA14 | ZN35800/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-29 | N | 79.0154 | N | 12 | N | N | 1.1101 | 39.4971 | 112597.1194
[7 empty] | 16758 | 1698 | 929136 | 2013-01-28 19:56 | 2013-01-29 11:00 | 904.4167 | 11kV | 169125.9167 | 187 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 134464 Wind - including wind borne material | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-01-28 | N | 904.4167 | N | 22 | Y | Y | 1.1101 | 39.4971 | 123592.2315
[7 empty] | 17140 | 4750 | 929161 | 2013-01-28 20:00 | 2013-01-29 12:05 | 965 | 11kV | 43177 | 757 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 45133 McMasters Beach tripped reclosed tripped and locked out on OC Tree branch brought down OH see 930769 930770 | January | 2013 | 2013Q3 | 2013 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2013-01-28 | N | 57.037 | N | 22 | Y | Y | 1.1101 | 39.4971 | 31552.4781
[7 empty] | 17741 | 11896 | 929279 | 2013-01-28 22:15 | 2013-01-29 13:46 | 931 | 11kV | 22971 | 117 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 44602 Ourimbah Ck Rd tripped / reclosed / tripped / locked out on SEF Beyond LK 43922 not accessible at night. Needs to be patrolled in daylight - same section of feeder interrupted from the previous night. Held all day until the section was attempted to be restored see 931441 931442 Note: job details updated as per comments on related record 929963 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-01-28 | N | 196.3333 | N | 22 | Y | Y | 1.1101 | 39.4971 | 16786.5293
[7 empty] | 16662 | 1008 | 929400 | 2013-01-29 13:00 | 2013-01-29 13:55 | 55 | 11kV | 550 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 134476 burnt off tapping pole ET-87011 Excluded oms 929400, 929443, 930117 | January | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-01-29 | N | 55 | N | 12 | N | N | 1.1101 | 39.4971 | 401.9238
[7 empty] | 16625 | 794 | 930151 | 2013-01-29 14:07 | 2013-01-29 15:33 | 86.1667 | 11kV | 153.55 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134479 A phase DOLF : 10 Amp 250V x 3 Excluded oms 930151 | January | 2013 | 2013Q3 | 2013 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | UG | Not Veg | 2013-01-29 | N | 76.775 | N | 12 | N | N | 1.1101 | 39.4971 | 112.2098
[7 empty] | 16813 | 2136 | 930027 | 2013-01-29 12:32 | 2013-01-29 16:25 | 233 | 11kV | 11990 | 88 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 134477 pole top fire at sub 54274 Excluded oms 930050 | January | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-01-29 | N | 136.25 | N | 12 | N | N | 1.1101 | 39.4971 | 8761.9384
[7 empty] | 17006 | 3605 | 930312 | 2013-01-29 16:23 | 2013-01-29 17:21 | 58 | 11kV | 19763 | 377 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9245 Engadine - Pnl 12 - Trip/reclose/trip: A, B, C phase IOC, sealing in contactor, lockout, timing relay. Trees in Stephen Rd on OH mains. Cleared by Oatley on-call mains. See also 930994 930999 for tree clearing follow up. | January | 2013 | 2013Q3 | 2013 | ZN9245:PA12 | ZN9245:PA9 | ZN09245/000009 | SUTHERLAND | OH | Veg | 2013-01-29 | N | 52.4218 | N | 12 | N | N | 1.1101 | 39.4971 | 14442.2175
[7 empty] | 17714 | 11681 | 929763 | 2013-01-29 09:31 | 2013-01-29 17:35 | 484 | 11kV | 36615 | 368 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 134471 1 fault operation B & C phase Sensitive Earth Fault; Earth fault Cable fault between UGOH & Hazemeyer Switchgear at Cessnock Tech College sub 54269. Targets: Fault Trip indication on Cap Back Sw 29636 & 29638. Fdr Sw 48029: B-C EF & SEF. Excluded OMS No. 929763 + 930038 | January | 2013 | 2013Q3 | 2013 | 504:48029 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2013-01-29 | N | 99.4973 | N | 12 | N | N | 1.1101 | 39.4971 | 26757.162
[7 empty] | 17349 | 7465 | 930276 | 2013-01-29 13:32 | 2013-01-29 19:25 | 353 | 11kV | 2283 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 45010 Palm Grove tripped / reclosed / tripped locked out Tree brought down mains on top of LK44526 see 931451 931452 | January | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-01-29 | N | 134.2941 | N | 12 | N | N | 1.1101 | 39.4971 | 1668.3491
[7 empty] | 17966 | 13827 | 930195 | 2013-01-29 14:42 | 2013-01-29 19:50 | 308.2167 | 11kV | 1541.0833 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134481 A phase DOLF : 5 Amp repair downed 11kV main | January | 2013 | 2013Q3 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2013-01-29 | N | 308.2167 | N | 12 | N | N | 1.1101 | 39.4971 | 1126.1782
[7 empty] | 17551 | 9161 | 930245 | 2013-01-29 15:25 | 2013-01-29 21:00 | 335 | 11kV | 60980 | 313 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 134482 B & C phase dist fuse : 250 Amp Underground Mains Cable. Sect isolated to repair Tx leads at sub 52113.# Excluded OMS 930245. | January | 2013 | 2013Q3 | 2013 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | UG | Not Veg | 2013-01-29 | N | 194.8243 | N | 12 | N | N | 1.1101 | 39.4971 | 44562.3854
[7 empty] | 17561 | 9470 | 930453 | 2013-01-30 05:53 | 2013-01-30 07:35 | 102 | 11kV | 46164 | 949 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | @ S3472 Sefton Panel 15 'S5471' Carlingford Guelph' feeder tripped, reclosed, tripped & locked out on Relays - IOC ABC phases, reclose timing, lockout, EFI Signals - 11kv trip, Group Earth Tx1 EFI's: Only S.4473 Remarks: end box fault. S4473 Sutherland Brunker Haz endbox failed explosively Related jobs: #930453, 930458, 930998, 930995 | January | 2013 | 2013Q3 | 2013 | ZN3472:PA15 | ZN35900:PA2 | ZN35900/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-30 | N | 48.6449 | N | 4 | N | N | 1.1101 | 39.4971 | 33735.2896
[7 empty] | 18457 | 19150 | 932943 | 2013-01-30 06:50 | 2013-01-30 07:50 | 60 | 11kV | 360 | 6 | HV | Staff Other | Utility Process Issue | Cable End Box | Unplanned | No Weather Impact | N | Section of feeder from S.4396 Ballad St No.1 Sw/A to S.4877 Ballad St. No2 interrupted. Ex panel 18 "Brunker Beresford" fdr Remarks: While carrying out switching due to endbox failure at S4473 Sutherland Brunker, Dop opened S1254 Sw/B. Please see separate interruptions for Sefton Panel 15. | January | 2013 | 2013Q3 | 2013 | ZN1285:PA18 | ZN35900:PA16 | ZN35900/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-01-30 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 17002 | 3587 | 930895 | 2013-01-30 12:59 | 2013-01-30 13:25 | 26 | 11kV | 26 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 134492 DOLF : 10 Amp | January | 2013 | 2013Q3 | 2013 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2013-01-30 | N | 26 | N | 4 | N | N | 1.1101 | 39.4971 | 19
[7 empty] | 17361 | 7576 | 931085 | 2013-01-30 19:30 | 2013-01-30 23:45 | 255 | 11kV | 11220 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | PT11533 North Burge Brock Nt -Dist #1 - all phases interrupted Oh down - repaired by linesman | January | 2013 | 2013Q3 | 2013 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2013-01-30 | N | 255 | N | 4 | N | N | 1.1101 | 39.4971 | 8199.2451
[7 empty] | 18440 | 18981 | 931115 | 2013-01-31 03:24 | 2013-01-31 04:25 | 61 | 11kV | 4148 | 68 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134495 A phase DOLF : 31 Amp Excluded OMS 931115 & 931116 | January | 2013 | 2013Q3 | 2013 | 214:8670 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Veg | 2013-01-31 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 3031.2361
[7 empty] | 16695 | 1205 | 931118 | 2013-01-31 05:19 | 2013-01-31 07:08 | 109 | 11kV | 1417 | 13 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT12616 Dog Trap Youngs - roadside HDO open circuit fuse fatigue | January | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-01-31 | N | 109 | N | 3 | N | N | 1.1101 | 39.4971 | 1035.5018
[7 empty] | 17244 | 6449 | 931643 | 2013-01-31 20:55 | 2013-01-31 22:49 | 114 | 11kV | 9234 | 81 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | LID: 134509 2 Fault Operations A Phase Earth Fault Circuit Breaker failed to reclose due to permanent voltage at trip coil. Switch was racked out & operated om the floor & was found to be OK, CB Re-installed & OK as left. Maintenance required. | January | 2013 | 2013Q3 | 2013 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | Unknown | Not Veg | 2013-01-31 | N | 114 | N | 3 | N | N | 1.1101 | 39.4971 | 6747.9348
[7 empty] | 18228 | 16878 | 931711 | 2013-02-01 08:48 | 2013-02-01 09:30 | 42 | 11kV | 1932 | 46 | HV | Animal Insect | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 134517 A phase DOLF : 40 Amp Wasps nest in DOLF. Tx Volts: Aph - 247V, Bph - 245V, Cph - 245V TX Load: Aph - 75A, Bph - 70A, Cph - 40A Excluded OMS NO. 931711+931746 | February | 2013 | 2013Q3 | 2013 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2013-02-01 | N | 42 | N | 16 | N | N | 1.1101 | 39.4971 | 1411.8486
[7 empty] | 18166 | 16271 | 932948 | 2013-02-01 09:57 | 2013-02-01 10:01 | 4 | 11kV | 6828 | 1707 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | Unselected | N | ZN 9252 Jannali - Pnl 2 - Trip/reclose, C phase O/C, ceiling contactor, Timing relay, Lockout. Cause not ascertained. DOp patrolled and found nothing. | February | 2013 | 2013Q3 | 2013 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | Unknown | Unknown | 2013-02-01 | N | 4 | N | 16 | N | N | 1.1101 | 39.4971 | 4989.701
[7 empty] | 18419 | 18808 | 931895 | 2013-02-01 11:55 | 2013-02-01 12:58 | 63 | 11kV | 117516 | 1965 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | @Zn12610 Long Jetty Pa13 fdr tripped on: ABCph Overcurrent fault Check EDFI NB No Recloser on this feeder Suspected lightning strike, no recloser See 933442,3 exclude 931895 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2013-02-01 | N | 59.8046 | N | 16 | N | N | 1.1101 | 39.4971 | 85877.2267
[7 empty] | 18332 | 17752 | 931856 | 2013-02-01 11:22 | 2013-02-01 14:00 | 158 | 11kV | 3160 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Autlink 44778 road phase actuator had operated ex panel 12 "Yarramalong fdr" DOp patrolled section of feeder beyond autolink but could not find a cause See 933171 exclude 931856 | February | 2013 | 2013Q3 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-02-01 | N | 158 | N | 16 | N | N | 1.1101 | 39.4971 | 2309.2348
[7 empty] | 16583 | 552 | 931970 | 2013-02-01 13:25 | 2013-02-01 14:35 | 70.3 | 11kV | 913.9 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134527 A & B phase DOLF : 31 Amp | February | 2013 | 2013Q3 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2013-02-01 | N | 70.3 | N | 16 | N | N | 1.1101 | 39.4971 | 667.8512
[7 empty] | 17497 | 8800 | 932076 | 2013-02-01 15:07 | 2013-02-01 16:14 | 67 | 11kV | 70830 | 1186 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S.15012 Killarney, Panel 4 Fdr CB tripped, reclosed, tripped and locked out on Earth Fault, lockout, timing relay, fault check, efi, 11kV trip, zone earth. The 11kV UG/OH at pole FF84695 at #13 Darley St near Warringah had faiiled. | February | 2013 | 2013Q3 | 2013 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | Unknown | Unknown | 2013-02-01 | N | 59.7218 | N | 16 | N | N | 1.1101 | 39.4971 | 51760.4749
[7 empty] | 17604 | 10076 | 932135 | 2013-02-01 15:53 | 2013-02-01 16:50 | 57 | 11kV | 78593 | 1516 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Lightning | N | ZN 9252 Jannali - Pnl 10 - Trip/reclose/trip, A phase IOC, Reclose, timing and lockout flags. Air break switch 35577 exploded and fell apart. | February | 2013 | 2013Q3 | 2013 | ZN9252:PA10 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Not Veg | 2013-02-01 | N | 51.8423 | N | 16 | N | N | 1.1101 | 39.4971 | 57433.4463
[7 empty] | 16744 | 1539 | 932077 | 2013-02-01 15:15 | 2013-02-01 17:45 | 150 | 11kV | 8400 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 134537 Fdr isolated at 41601 to remove tree adj pole CB-14625 sub 54762 | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-02-01 | N | 150 | N | 16 | N | N | 1.1101 | 39.4971 | 6138.4722
[7 empty] | 16795 | 2020 | 932078 | 2013-02-01 15:18 | 2013-02-01 18:10 | 171.6833 | 11kV | 171.6833 | 1 | HV | Arcing | Equipment Failure | UGOH | Unplanned | Unselected | N | repaired UGOH fault CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-02-01 | N | 171.6833 | N | 16 | N | N | 1.1101 | 39.4971 | 125.4611
[7 empty] | 16565 | 407 | 932108 | 2013-02-01 15:09 | 2013-02-01 18:15 | 186 | 11kV | 28235 | 2335 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN 10995 Riverwood - Pnl 2 - Trip/reclose, A phase IOC and timed overload. At PT 10254 Mountview Stoney - Roadside HV assembly hit by lightning and flashed over to tank. Lightning strike on PT 10254 Mountview Stoney. Restored via LV//. | February | 2013 | 2013Q3 | 2013 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2013-02-01 | N | 12.0921 | N | 16 | N | N | 1.1101 | 39.4971 | 20633.3052
[7 empty] | 17906 | 13173 | 932177 | 2013-02-01 16:36 | 2013-02-01 18:51 | 135 | 11kV | 79507 | 601 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Zn12600 Panel 1 fdr tripped, reclosed, tripped and locked out Relays: Aph & Cph overcurrent, reclose timing, lockout relay Signals: 11kv trip Cause: First UGOH out from the zone has a short circuit connection on it See 933467,8 Exclude 932177 | February | 2013 | 2013Q3 | 2013 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | Unknown | Unknown | 2013-02-01 | N | 132.2912 | N | 16 | N | N | 1.1101 | 39.4971 | 58101.3705
[7 empty] | 17972 | 13939 | 931906 | 2013-02-01 12:10 | 2013-02-01 20:01 | 471 | 11kV | 6691 | 17 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134525 2 fault operations single phase Overcurrent Cut away L/A at Sw 74815 Blown DOLF sub 72561 | February | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2013-02-01 | N | 393.5882 | N | 16 | N | N | 1.1101 | 39.4971 | 4889.5854
[7 empty] | 17977 | 14045 | 932254 | 2013-02-01 17:51 | 2013-02-01 21:00 | 189 | 11kV | 1134 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 134539 A & C phase DOLF : 10 Amp Pole SF-60594 hit by lightning damaged xarm brace sub 51096 blown DOLFs Isolated from LK 26181 for repair Excluded OMS 932254 & 932285 | February | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-02-01 | N | 189 | N | 16 | N | N | 1.1101 | 39.4971 | 828.6938
[7 empty] | 17594 | 9801 | 932269 | 2013-02-01 18:11 | 2013-02-01 23:55 | 344 | 11kV | 344 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 134542 C Phase Lead to DOLF broken away. Sub isolated for repair. Excluded OMS No. 932269. | February | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-02-01 | N | 344 | N | 16 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 17686 | 11421 | 932369 | 2013-02-01 23:25 | 2013-02-02 00:39 | 73.5167 | 11kV | 77764.6833 | 1751 | HV | Arcing | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At S4545 Meadowbank Panel 44 tripped on A and B phase IOC, Fault Check and EFI. At S4545 Meadowbank Panel 6 Tripped on A and C phase Timed and TOC. Cause: LB61232 Flashed over. OMS:935498 935501 935498 932370/374/390 | February | 2013 | 2013Q3 | 2013 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Not Veg | 2013-02-01 | N | 44.4116 | N | 16 | N | N | 1.1101 | 39.4971 | 56828.1369
[7 empty] | 17167 | 5237 | 932379 | 2013-02-02 00:33 | 2013-02-02 02:30 | 117 | 11kV | 70281 | 747 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @Zn14143 Somersby 11kv VCB Pa17 fdr tripped on: Relays: Overcurrent and Instantaneous Overcurrent Field EFI: Nil Signals: 11kv trip Cause: Cause not ascertained. DOp patrolled nothing found See 933489,2,3 Exclude 932379 | February | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2013-02-02 | N | 94.0843 | N | 11 | N | N | 1.1101 | 39.4971 | 51359.2819
[7 empty] | 16634 | 862 | 932380 | 2013-02-02 00:50 | 2013-02-02 10:45 | 595 | 11kV | 1190 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 134545 B & C phase DOLF : 3 Amp sinlge phase sub blown arrester Excluded oms 932380 | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-02-02 | N | 595 | N | 11 | N | N | 1.1101 | 39.4971 | 869.6169
[7 empty] | 18276 | 17247 | 932438 | 2013-02-02 10:00 | 2013-02-02 10:45 | 45 | 11kV | 2295 | 51 | HV | 3rd Party Action | 3rd Party Impact | Fuse | Unplanned | Rain Heavy | N | S 10189 Hill Treacy No.3 - HV Fuses. S 10189 interrupted for safety reasons. Dist 1 is a direct 1200A feed to customer's switchboard. The customer's main CB was wer and required urgent attention. Due to Dist 1 fuses being bolt on type, the DOp interrupted the entire LV board which also included Dist 2 and 3 for immediate dry and clean of Customer's CB. | February | 2013 | 2013Q3 | 2013 | ZN10999:PA24 | ZN10999:PA24 | ZN10999/000024 | GEORGES RIVER | OH | Not Veg | 2013-02-02 | N | 45 | N | 11 | N | N | 1.1101 | 39.4971 | 1677.1183
[7 empty] | 16838 | 2243 | 932562 | 2013-02-02 13:11 | 2013-02-02 14:25 | 74 | 11kV | 5846 | 79 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | PT11559 Norfol Willow Footpath and Centre phase HDO's blown ex panel 25 "long Jetty Aux" fdr Cause: animal/birds Magpie bridged across 2 HDO's, damaging the fuse assembly See 933518 exclude 932561,2,3,4,6,80 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2013-02-02 | N | 74 | N | 11 | N | N | 1.1101 | 39.4971 | 4272.0844
[7 empty] | 17381 | 7747 | 932571 | 2013-02-02 13:32 | 2013-02-02 14:30 | 58 | 11kV | 57942 | 999 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 134547 2 fault operations A phase Earth fault, Overcurrent Cable fault Cnr Watt St & Church St. Target from Sw 34259 -- Left leg A phase O/C & E/F. Fault was actually in Right Leg. Please Investigate. Excluded OMS 932571 | February | 2013 | 2013Q3 | 2013 | 202:34259 | 202:34240 | ZN00202/034240 | NEWCASTLE | OH | Veg | 2013-02-02 | N | 58 | N | 11 | N | N | 1.1101 | 39.4971 | 42342.3046
[7 empty] | 17287 | 6958 | 932596 | 2013-02-02 15:21 | 2013-02-02 16:07 | 46 | 11kV | 52946 | 1151 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.15012 Killarney, Panel 8 Fdr CB tripped, reclosed and tripped on A&C phase IOC and timed OC, timing and lockout relays. Tree branch on OH mains O/S #11 Tyalla Ave, Frenchs Forest | February | 2013 | 2013Q3 | 2013 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2013-02-02 | N | 46 | N | 11 | N | N | 1.1101 | 39.4971 | 38691.3752
[7 empty] | 16561 | 372 | 932621 | 2013-02-02 16:42 | 2013-02-02 17:49 | 67 | 11kV | 25241 | 447 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S2473 North Sydney Panel 15 tripped on E/F with EFI. Cause: Cable fault between S3589 abd S2778 See OMS 935770 935773 932621 | February | 2013 | 2013Q3 | 2013 | ZN2473:PA15 | ZN35400:PA61 | ZN35400/000061 | NORTH SYDNEY | UG | Not Veg | 2013-02-02 | N | 56.4676 | N | 11 | N | N | 1.1101 | 39.4971 | 18445.3783
[7 empty] | 17964 | 13797 | 932434 | 2013-02-02 17:04 | 2013-02-02 19:00 | 115.4667 | 11kV | 3348.5333 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | 11kv beyond AB44878 interrupted by DOp to allow Overhead to repair damaged mains Ex Panel 3 "Mangrove Mountain" fdr Cause: Tree/Branch on Overhead Mains Outside 270 Waratah rd. Interrupted at 1704 See 932434,625 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-02-02 | N | 115.4667 | N | 11 | N | N | 1.1101 | 39.4971 | 2447.0094
[7 empty] | 18356 | 17896 | 932415 | 2013-02-02 18:35 | 2013-02-02 20:00 | 85 | 11kV | 935 | 11 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Section of 11kv feeder beyond LB47036 interrupted ex Panel 4 "Kulnura" feeder Cause: Interrupted for safety reasons Very large tree resting against CCT See 933543 exclude 932415 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2013-02-02 | N | 85 | N | 11 | N | N | 1.1101 | 39.4971 | 683.2704
[7 empty] | 18049 | 15294 | 932657 | 2013-02-02 20:21 | 2013-02-03 00:45 | 264 | 11kV | 60926 | 344 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 134550 Tapping burnt off at pole JU-20311 | February | 2013 | 2013Q3 | 2013 | 208:56 | 257:81997 | ZN00257/081997 | NEWCASTLE | OH | Not Veg | 2013-02-02 | N | 177.1105 | N | 11 | N | N | 1.1101 | 39.4971 | 44522.9238
[7 empty] | 16587 | 562 | 932687 | 2013-02-02 23:26 | 2013-02-03 02:47 | 201 | 11kV | 69746 | 398 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Recloser CP3281 Bay Cooper Tripped and Locked Out Cause Not ascertained for outage See OMS 936301/312/313 | February | 2013 | 2013Q3 | 2013 | ZN2400:PA18 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-02-02 | N | 175.2412 | N | 11 | N | N | 1.1101 | 39.4971 | 50968.3196
[7 empty] | 16579 | 517 | 932709 | 2013-02-03 05:55 | 2013-02-03 08:35 | 160.2167 | 11kV | 8651.7 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134554 A & B phase DOLF : 20 Amp no fault found please patrol. | February | 2013 | 2013Q3 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2013-02-03 | N | 160.2167 | N | 6 | N | N | 1.1101 | 39.4971 | 6322.4072
[7 empty] | 16829 | 2203 | 932748 | 2013-02-03 09:26 | 2013-02-03 10:35 | 69 | 11kV | 138 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134555 A phase DOLF : 10 Amp Fuse Fatigue | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-02-03 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 17415 | 8074 | 932833 | 2013-02-03 16:43 | 2013-02-03 17:45 | 62 | 11kV | 3782 | 61 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | Section of 11kv feeer from AB42586 to AB44154 tee PT12115 Lake View Minell interrupted ex panel 1 "Dover Memeorial Club" fdr Cause: interrupted for safety reasons Kite surfers Kite had tangled between the 11kv and 415v mains causing arcing See 933555 exclude 932833,55 | February | 2013 | 2013Q3 | 2013 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Not Veg | 2013-02-03 | N | 62 | N | 6 | N | N | 1.1101 | 39.4971 | 2763.774
[7 empty] | 16835 | 2225 | 932875 | 2013-02-03 19:35 | 2013-02-03 20:10 | 35.3667 | 11kV | 353.6667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134561 C phase DOLF : 10 Amp Volts at sub 7579 248V each phase | February | 2013 | 2013Q3 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2013-02-03 | N | 35.3667 | N | 6 | N | N | 1.1101 | 39.4971 | 258.4492
[7 empty] | 18343 | 17817 | 932867 | 2013-02-03 19:09 | 2013-02-03 22:45 | 215.85 | 11kV | 5396.25 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134563 Transformer lead burnt off Burnt off LL Lead, tail on xarm. isolated from LF 40489 to open LL Clamps. Isolation from LL Clamps for repair CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2013-02-03 | N | 215.85 | N | 6 | N | N | 1.1101 | 39.4971 | 3943.4203
[7 empty] | 18412 | 18721 | 932888 | 2013-02-03 21:43 | 2013-02-03 23:10 | 87 | 11kV | 67544 | 812 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1164 Rose Bay: 11kv feeder Panel No12 "Polybank Pde" feeder TRIPPED Relays: E/F, EFI Field EFI's: S2222, S8937, S35907 Remarks: 11kv cable fault in section of feeder S35907 Military Cadigal (SWB) to S594 Pindari Rd (SWA). NOTE: Compund Endbox @ S594 LV// required to extend cut out. Related jobs: #932888, 933116, 933113 | February | 2013 | 2013Q3 | 2013 | ZN1164:PA12 | ZN36100:PA15 | ZN36100/000015 | WAVERLEY | UG | Not Veg | 2013-02-03 | N | 83.1823 | N | 6 | N | N | 1.1101 | 39.4971 | 49359.163
[7 empty] | 16865 | 2444 | 932002 | 2013-02-01 13:48 | 2013-02-04 04:10 | 3742 | 11kV | 69274 | 837 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 134528 2 fault operation 3 phase Overcurrent UGOH to sub 29855 Blew up. Excluded OMS# 932002 & 932069 | February | 2013 | 2013Q3 | 2013 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | UG | Not Veg | 2013-02-01 | N | 82.7646 | N | 16 | N | N | 1.1101 | 39.4971 | 50623.396
[7 empty] | 17377 | 7711 | 932936 | 2013-02-04 07:42 | 2013-02-04 13:50 | 368 | 11kV | 368 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID: 134571 Phase A Dolf : 10Amp Excludes OMS: 932936 | February | 2013 | 2013Q3 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2013-02-04 | N | 368 | N | 5 | N | N | 1.1101 | 39.4971 | 268.9235
[7 empty] | 16857 | 2377 | 933054 | 2013-02-04 09:45 | 2013-02-04 14:50 | 305 | 11kV | 27450 | 90 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | D.OP interrupted supply for safety to allow emergency repairs to pole and LV OH | February | 2013 | 2013Q3 | 2013 | ZN15010:PA1 | ZN15010:PA24 | ZN15010/000024 | NORTHERN BEACHES | OH | Not Veg | 2013-02-04 | N | 305 | N | 5 | N | N | 1.1101 | 39.4971 | 20059.6504
[7 empty] | 18442 | 19036 | 933085 | 2013-02-04 10:58 | 2013-02-04 18:50 | 472 | 11kV | 472 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID: 134570 Phase A DOLF : 10 Amp Excludes OMS: 933085 | February | 2013 | 2013Q3 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2013-02-04 | N | 472 | N | 5 | N | N | 1.1101 | 39.4971 | 344.9237
[7 empty] | 18045 | 15117 | 933398 | 2013-02-04 21:39 | 2013-02-04 23:10 | 91 | 11kV | 58898 | 747 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | @Zn14143 Somersby 11kv VCB Pa17 "Somersby Falls" fdr tripped on Relays: A=B Phase Overcurrent Feild EFI: Nil Signals: 11kv trip Circuit breaker Overcurrent trip Cause: Moving Vehicle Accident into pole. section of 11kv fdr between AB40512 to LK40578 to LB61390 tee to PT13568 Wise Ferry Debenham isolated/ earthed Access Permit's issued to replace broken pole. see 933595,7,8 exclude 933398 | February | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-02-04 | N | 78.8461 | N | 5 | N | N | 1.1101 | 39.4971 | 43040.9212
[7 empty] | 17137 | 4720 | 933391 | 2013-02-04 21:10 | 2013-02-05 11:45 | 875 | 11kV | 88070 | 881 | HV | 3rd Party Vehicle | 3rd Party Impact | UGOH | Unplanned | Unselected | N | ZN 10996 Rockdale - Pnl 10 - Tip/Reclose/Trip, C phase IOC, reclose timing, lockout. Vehicle hit pole in Bestic St near Highclere St. UGOH to SW/B @ S 10109 possibly damaged. Requires Jointer to Megger before returning to service. Extended outage at S 10624 Bestic Barton Park as it is a non paralleling centre. Will require MG if damaged until repaired. Associated section of 11kV feeder from S 10109 to ABS 30119 tee S 10624. See 933927 restoration step for associated LV outage at S 10109. | February | 2013 | 2013Q3 | 2013 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | UG | Not Veg | 2013-02-04 | N | 99.9659 | N | 5 | N | N | 1.1101 | 39.4971 | 64358.9584
[7 empty] | 18373 | 18111 | 933768 | 2013-02-05 16:12 | 2013-02-05 21:14 | 302 | 11kV | 19028 | 100 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 134583 3 fault operations 3 phase Earth fault 11kV OHM off pin adj cameron sub 42062 Excluded OMS 933768 | February | 2013 | 2013Q3 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2013-02-05 | N | 190.28 | N | 2 | N | N | 1.1101 | 39.4971 | 13905.1012
[7 empty] | 17313 | 7203 | 933845 | 2013-02-06 01:20 | 2013-02-06 02:14 | 54 | 11kV | 62262 | 1153 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | @Zn12610 Long Jetty 11kv VCB Pa9 "Denning st" feeder tripped on: Relays: ABph timmed Overcurrent, EFI, E/F Check Field EFI: S12120 S12170 S12230 S11201 S18382 S14951 Signals: 11kv trip Cause: Possum on UGOH in Manning St pole no TE 280. Linesman or Jointer to inspect for dmaage. See 933868 Exclude 933845,7,8,50 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | OH | Not Veg | 2013-02-06 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 45499.2332
[7 empty] | 18291 | 17367 | 933838 | 2013-02-05 21:42 | 2013-02-06 07:45 | 603 | 11kV | 48238 | 322 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S35800 Bankstown P16 Canterbury Fair tripped on: Relays: A + C phase IOC, earth fault check. Field EFIs: S5149, S4115, S5412, S5946 Signals: 11kv trip Remarks: No access to S6417 Seddon St. No EFI down at Zone panel. 11kv feeder isolated from S-5946 Arkley Starkey SW-B to S5153 Seddon St SW-A via S6417 Seddon St West tee to S35925 Boxley Crescent. S35925 restored via LV// link no.s Related jobs: #933838, 934491, 934489, 934490, 934488 | February | 2013 | 2013Q3 | 2013 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-02-05 | N | 149.8075 | N | 2 | N | N | 1.1101 | 39.4971 | 35250.9076
[7 empty] | 17585 | 9739 | 934140 | 2013-02-06 14:29 | 2013-02-06 16:50 | 141 | 11kV | 45706 | 770 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S.15005 Belrose, Panel 10 Fdr CB tripped on A and C phase IOC, efi, fault check. Field efi's down at S.16781. UG/OH fault short circuit to PT.15625 | February | 2013 | 2013Q3 | 2013 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | Unknown | Unknown | 2013-02-06 | N | 59.3584 | N | 4 | N | N | 1.1101 | 39.4971 | 33400.5967
[7 empty] | 18387 | 18276 | 934244 | 2013-02-06 18:55 | 2013-02-06 20:00 | 65 | 11kV | 16640 | 256 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1193 Lindfield Panel 6 Tripped on Timed Earth fault and EFI. Abnormal Switching: S3420 SW/B to S5119 Wyvern Peckham SW/A to S312 SW/D Isolated due to existing fault. Supply Restored Via LV Parallel. See OMS 935804 934244 | February | 2013 | 2013Q3 | 2013 | ZN1193:PA6 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | UG | Not Veg | 2013-02-06 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 12160.0212
[7 empty] | 17895 | 13082 | 934255 | 2013-02-06 21:30 | 2013-02-06 21:45 | 15 | 11kV | 1635 | 109 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Interrupted to allow repairs and restoration of repairs to #2 dist ex S.1332 - Refer to previous event 933837 | February | 2013 | 2013Q3 | 2013 | ZN180:PA7 | ZN180:PA18 | ZN00180/000018 | MOSMAN | UG | Not Veg | 2013-02-06 | N | 15 | N | 4 | N | N | 1.1101 | 39.4971 | 1194.8098
[7 empty] | 18016 | 14551 | 934262 | 2013-02-07 00:14 | 2013-02-07 01:07 | 52.85 | 11kV | 68757.85 | 1301 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | U/G Cable | Unplanned | Unselected | N | At Zn1193 Lindfield 11kV Panel 26 was interrupted for safety reasons 11kV Feeder fault on panel 6 Caused pit lid in middle of road to move. 11kV feeder Pa26 Runs through the same pit. Cause: feeder de energised to inspect after pa 6 failure | February | 2013 | 2013Q3 | 2013 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | UG | Not Veg | 2013-02-07 | N | 52.85 | N | 6 | N | N | 1.1101 | 39.4971 | 50246.2088
[7 empty] | 16752 | 1642 | 934444 | 2013-02-07 11:44 | 2013-02-07 13:30 | 106 | 11kV | 212 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134607 A phase DOLF : 10 Amp No obvious cause, customer had not been on site for a week or so. Excluded OMS 934444 | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2013-02-07 | N | 106 | N | 6 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 18095 | 15742 | 934549 | 2013-02-07 15:09 | 2013-02-07 16:10 | 61.2 | 11kV | 8861.6 | 150 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | NO LID report | February | 2013 | 2013Q3 | 2013 | 260:33353 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2013-02-07 | N | 59.0773 | N | 6 | N | N | 1.1101 | 39.4971 | 6475.7959
[7 empty] | 18260 | 17132 | 934601 | 2013-02-07 16:39 | 2013-02-07 18:45 | 126.4667 | 11kV | 3288.1333 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134609 B phase DOLF : 10 Amp Changed spur fuses 74742 | February | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-02-07 | N | 126.4667 | N | 6 | N | N | 1.1101 | 39.4971 | 2402.8709
[7 empty] | 17439 | 8225 | 934639 | 2013-02-07 08:30 | 2013-02-07 22:45 | 855 | 11kV | 5130 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134611 Single phase field operator Brown did not close recloser 74830 during reconnect switching after planned interuption Excluded oms 934639 | February | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2013-02-07 | N | 855 | N | 6 | N | N | 1.1101 | 39.4971 | 3748.8527
[7 empty] | 18107 | 15840 | 934631 | 2013-02-07 08:30 | 2013-02-07 22:45 | 855 | 11kV | 5130 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134612 Single phase field operator Brown did not close recloser 74825 during reconnect switching after planned interuption Excluded oms 934631 | February | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2013-02-07 | N | 855 | N | 6 | N | N | 1.1101 | 39.4971 | 3748.8527
[7 empty] | 17650 | 10794 | 934772 | 2013-02-08 11:04 | 2013-02-08 12:40 | 96 | 11kV | 4128 | 43 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134625 A phase DOLF Dolf carrier broken. Excluded oms-934772. | February | 2013 | 2013Q3 | 2013 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2013-02-08 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 3016.6206
[7 empty] | 17353 | 7494 | 934802 | 2013-02-08 12:06 | 2013-02-08 13:05 | 59.3833 | 11kV | 4097.45 | 69 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134626 A phase DOLF : 20 Amp | February | 2013 | 2013Q3 | 2013 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2013-02-08 | N | 59.3833 | N | 5 | N | N | 1.1101 | 39.4971 | 2994.2956
[7 empty] | 17769 | 12077 | 934873 | 2013-02-08 14:52 | 2013-02-08 17:04 | 131.9 | 11kV | 22535.0333 | 191 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134629 B phase DOLF : 40 Amp Found DOLF down, probable fuse fatigue. Excluded OMS No. 934879 & 934888. | February | 2013 | 2013Q3 | 2013 | 223:14394 | 223:14394 | ZN00223/014394 | LAKE MACQUARIE | OH | Not Veg | 2013-02-08 | N | 117.9845 | N | 5 | N | N | 1.1101 | 39.4971 | 16467.9377
[7 empty] | 18512 | 19984 | 934944 | 2013-02-08 19:03 | 2013-02-08 20:53 | 110.4667 | 11kV | 188456.1333 | 1706 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134631 4 fault operations B phase Earth fault | February | 2013 | 2013Q3 | 2013 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2013-02-08 | N | 110.4667 | N | 5 | N | N | 1.1101 | 39.4971 | 137718.1837
[7 empty] | 17022 | 3837 | 934940 | 2013-02-08 19:03 | 2013-02-09 11:00 | 957 | 11kV | 91872 | 96 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1221 Old Kent Noble. The Footpath side HV drop out assembly found blown and defective supply restored via LV// Remarks: At PT1221 F/P HV dropout broken and assembly requires replacement Related jobs: #934940, 935971 | February | 2013 | 2013Q3 | 2013 | ZN1285:PA27 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-02-08 | N | 957 | N | 5 | N | N | 1.1101 | 39.4971 | 67137.3478
[7 empty] | 18258 | 17125 | 935030 | 2013-02-09 11:30 | 2013-02-09 12:30 | 60 | 11kV | 1680 | 28 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At S6893 Chapel The Mall #1 tx rmi found tripped and centre ph KEMXO90 amp fuse blown Remarks: Dop tried back tee off with new fuse but failed again blowing both lefthand side and centre ph fuses. Suspect defective tx. Related jobs: #935030, 936008 | February | 2013 | 2013Q3 | 2013 | ZN1285:PA29 | ZN37100:PA17 | ZN37100/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-02-09 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 16827 | 2196 | 935027 | 2013-02-09 11:17 | 2013-02-09 14:53 | 216 | 11kV | 3672 | 17 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section Panel #6 @ S35800 Bankstown "S46101" fdr Remarks: Bond. Centre ph bond off AB3293 Related jobs: #935027, 936012 | February | 2013 | 2013Q3 | 2013 | ZN35800:PA6 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-02-09 | N | 216 | N | 4 | N | N | 1.1101 | 39.4971 | 2683.3893
[7 empty] | 17350 | 7474 | 935076 | 2013-02-09 15:07 | 2013-02-09 16:00 | 53 | 11kV | 65455 | 1235 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn126550 West Gosford Zone Ex Panel 12 Air break switch. Open bond roadside phase, lineside of AB43065. See 936090 exclude 935071,6,81,6,7 | February | 2013 | 2013Q3 | 2013 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2013-02-09 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 47832.5834
[7 empty] | 16916 | 3028 | 935120 | 2013-02-09 20:49 | 2013-02-09 23:15 | 146 | 11kV | 102600 | 1260 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 134637 2 fault operations A phase Earth fault, Overcurrent Ties broken & conductors on x arm after car into pole FT-12610. Repaired inder AP Excluded OMS 935120 | February | 2013 | 2013Q3 | 2013 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2013-02-09 | N | 81.4286 | N | 4 | N | N | 1.1101 | 39.4971 | 74977.0538
[7 empty] | 17755 | 11978 | 935140 | 2013-02-10 05:30 | 2013-02-10 08:15 | 165 | 11kV | 1320 | 8 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn35500 Top Ryde Panel 32 F1835 Roadside and Centre Phase 63A HVDO fuses operated. Cause: Possum found at the base of pole in Plassey Rd Adjacent to cremotorium See OMS 936200 935140 935141 | February | 2013 | 2013Q3 | 2013 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2013-02-10 | N | 165 | N | 24 | Y | Y | 1.1101 | 39.4971 | 964.6171
[7 empty] | 18111 | 15854 | 935212 | 2013-02-10 14:18 | 2013-02-10 15:00 | 42 | 11kV | 1680 | 40 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | @PT12611 Bottle Brush Rain, Footpath Phase HDO broke away from HV mains Ex Zn12600 Lisarow, Pa8 'Wyoming South' 11kv fdr Cause: Fuse equipment - Footpath Phase HDO broke away from HV mains. See 936100 GIS 936101 exclude 935212 | February | 2013 | 2013Q3 | 2013 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2013-02-10 | N | 42 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 17204 | 5935 | 935241 | 2013-02-10 16:28 | 2013-02-10 18:45 | 137 | 11kV | 411 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 134646 A phase DOLF : 15 Amp Line DOLF replaced OK, posibly trees in mains. Excluded OMS No. 935241. | February | 2013 | 2013Q3 | 2013 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Veg | 2013-02-10 | N | 137 | N | 24 | Y | Y | 1.1101 | 39.4971 | 300.3467
[7 empty] | 17119 | 4550 | 935268 | 2013-02-10 18:12 | 2013-02-10 18:55 | 43 | 11kV | 301 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134647 A & B Phase DOLF : 16 Amp Excluded OMS 935268 | February | 2013 | 2013Q3 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2013-02-10 | N | 43 | N | 24 | Y | Y | 1.1101 | 39.4971 | 219.9619
[7 empty] | 16859 | 2392 | 935263 | 2013-02-10 17:38 | 2013-02-10 19:10 | 92 | 11kV | 276 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134874 A phase DOLF : 10 Amp Excluded OMS 935263 | February | 2013 | 2013Q3 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | UG | Not Veg | 2013-02-10 | N | 92 | N | 24 | Y | Y | 1.1101 | 39.4971 | 201.6927
[7 empty] | 17141 | 4772 | 935838 | 2013-02-10 18:00 | 2013-02-10 19:50 | 110 | 11kV | 2530 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134650 3 phase DOLF : 16 Amp Customer reports 4th time these fuses have blown this year. Please investigate. | February | 2013 | 2013Q3 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2013-02-10 | N | 110 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1848.8494
[7 empty] | 18172 | 16346 | 935308 | 2013-02-10 20:40 | 2013-02-10 21:50 | 69.7333 | 11kV | 245.7 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134660 Single phase DOLF : 16 Amp Excluded OMS 935308 | February | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-02-10 | N | 61.425 | N | 24 | Y | Y | 1.1101 | 39.4971 | 179.5503
[7 empty] | 17767 | 12055 | 935636 | 2013-02-10 20:53 | 2013-02-10 23:30 | 157 | 11kV | 3297 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134684 A phase DOLF : 10 Amp NOTE PAUL LEE ALSO ATENDED TO ANOTHER LID JOB NUMBER 134663 ON THE SAME OMS NUMBER. | February | 2013 | 2013Q3 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2013-02-10 | N | 157 | N | 24 | Y | Y | 1.1101 | 39.4971 | 2409.3504
[7 empty] | 18531 | 20162 | 935367 | 2013-02-10 22:43 | 2013-02-10 23:30 | 47.3833 | 11kV | 2263.5 | 48 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 134707 B phase No protection operations. B phase DOLF broken at top connection. Sub interconnected. CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | 260:33344 | 239:82136 | ZN00239/082136 | LAKE MACQUARIE | OH | Not Veg | 2013-02-10 | N | 47.1562 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1654.099
[7 empty] | 17465 | 8461 | 935338 | 2013-02-10 21:42 | 2013-02-10 23:45 | 123 | 11kV | 246 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134686 A & C phase DOLF : 10 Amp Glen Austin reported the HV surge arrestors were previously cut away when he arrived on site. Excluded OMS 935338 | February | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-02-10 | N | 123 | N | 24 | Y | Y | 1.1101 | 39.4971 | 179.7695
[7 empty] | 17042 | 3983 | 935334 | 2013-02-10 21:38 | 2013-02-11 00:20 | 162 | 11kV | 324 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134688 Single phase DOLF : 5 Amp Excluded OMS 935334 | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-02-10 | N | 162 | N | 24 | Y | Y | 1.1101 | 39.4971 | 236.7696
[7 empty] | 16861 | 2420 | 935337 | 2013-02-10 21:42 | 2013-02-11 00:30 | 168 | 11kV | 672 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134689 Single phase DOLF : 10 Amp Excluded OMS 935337 | February | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2013-02-10 | N | 168 | N | 24 | Y | Y | 1.1101 | 39.4971 | 491.0778
[7 empty] | 16804 | 2084 | 936024 | 2013-02-10 23:37 | 2013-02-11 01:00 | 83 | 11kV | 1660 | 20 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134701 3 phase DOLF : 10 Amp Excluded OMS 935380 | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-02-10 | N | 83 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1213.079
[7 empty] | 17599 | 9853 | 935344 | 2013-02-10 21:56 | 2013-02-11 01:00 | 184 | 11kV | 184 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134690 A phase DOLF : 10 Amp Excluded OMS 935344 | February | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2013-02-10 | N | 184 | N | 24 | Y | Y | 1.1101 | 39.4971 | 134.4618
[7 empty] | 17300 | 7100 | 935321 | 2013-02-10 21:03 | 2013-02-11 01:30 | 267 | 11kV | 534 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134694 Three phase DOLF : 20 Amp Excluded OMS 935321 | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-02-10 | N | 267 | N | 24 | Y | Y | 1.1101 | 39.4971 | 390.2314
[7 empty] | 16894 | 2823 | 935348 | 2013-02-10 22:01 | 2013-02-11 01:30 | 209 | 11kV | 418 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134693 C phase DOLF : 10 Amp Volts = 244 Excluded OMS 935348 | February | 2013 | 2013Q3 | 2013 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | UG | Not Veg | 2013-02-10 | N | 209 | N | 24 | Y | Y | 1.1101 | 39.4971 | 305.4621
[7 empty] | 18195 | 16567 | 935358 | 2013-02-10 22:18 | 2013-02-11 01:45 | 207 | 11kV | 2277 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134696 C phase DOLF : 20 Amp Excluded OMS 935358 | February | 2013 | 2013Q3 | 2013 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2013-02-10 | N | 207 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1663.9644
[7 empty] | 17434 | 8203 | 935339 | 2013-02-10 21:43 | 2013-02-11 01:48 | 245 | 11kV | 35280 | 144 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134695 B phase DOLF : 40 Amp Excluded OMS 935339 | February | 2013 | 2013Q3 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2013-02-10 | N | 245 | N | 24 | Y | Y | 1.1101 | 39.4971 | 25781.5834
[7 empty] | 18528 | 20125 | 935388 | 2013-02-11 00:55 | 2013-02-11 02:10 | 75 | 11kV | 600 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134697 C phase DOLF : 10 Amp Excluded OMS 935388 | February | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2013-02-11 | N | 75 | N | 16 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 16725 | 1383 | 935380 | 2013-02-10 23:37 | 2013-02-11 02:15 | 158 | 11kV | 158 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 134702 3 phase DOLF : 10 Amp Faulty arrestors cut away under AP. | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-02-10 | N | 158 | N | 24 | Y | Y | 1.1101 | 39.4971 | 115.4617
[7 empty] | 16645 | 923 | 935343 | 2013-02-10 21:55 | 2013-02-11 02:50 | 295 | 11kV | 885 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 134703 C phase DOLF : 10 Amp Volts = 245, 251, 253. Excluded OMS 935343 | February | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-02-10 | N | 295 | N | 24 | Y | Y | 1.1101 | 39.4971 | 646.7319
[7 empty] | 17223 | 6233 | 935360 | 2013-02-10 22:24 | 2013-02-11 03:30 | 306 | 11kV | 7344 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134704 A phase Sectionaliser Excluded OMS 935360 | February | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-02-10 | N | 306 | N | 24 | Y | Y | 1.1101 | 39.4971 | 5366.7786
[7 empty] | 16531 | 175 | 935378 | 2013-02-10 23:31 | 2013-02-11 04:40 | 309 | 11kV | 13287 | 43 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Previous Storm | N | LID 134708 A phase DOLF : 20 Amp Possum Excluded OMS 935378 | February | 2013 | 2013Q3 | 2013 | 501:48115 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2013-02-10 | N | 309 | N | 24 | Y | Y | 1.1101 | 39.4971 | 9709.7477
[7 empty] | 18282 | 17299 | 935394 | 2013-02-11 04:07 | 2013-02-11 08:40 | 272.7167 | 11kV | 2181.7333 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134714 3 phase DOLF : 16 Amp CC1: 06-"Urgent - O.H Mains - No others" | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2013-02-11 | N | 272.7167 | N | 16 | N | N | 1.1101 | 39.4971 | 1594.3464
[7 empty] | 18386 | 18270 | 936237 | 2013-02-11 07:00 | 2013-02-11 08:40 | 100 | 11kV | 700 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134712 A & C phase DOLF : 20 Amp Excluded OMS 935404 | February | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2013-02-11 | N | 100 | N | 16 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 18189 | 16465 | 935407 | 2013-02-11 05:30 | 2013-02-11 09:15 | 225 | 11kV | 2250 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134720 3 Phase DOLF : 16 Amp Excluded oms 935433, 935402, 935407, 935418 | February | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-02-11 | N | 225 | N | 16 | N | N | 1.1101 | 39.4971 | 1644.2336
[7 empty] | 16536 | 255 | 935439 | 2013-02-11 07:26 | 2013-02-11 09:30 | 124 | 11kV | 496 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134721 A phase DOLF : 5 Amp Excluded OMS 935439 | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-02-11 | N | 124 | N | 16 | N | N | 1.1101 | 39.4971 | 362.4622
[7 empty] | 17016 | 3750 | 936067 | 2013-02-11 09:43 | 2013-02-11 09:50 | 7 | 11kV | 1596 | 228 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134723 Interruption by SO to isolate area due to phasing issues between Morisset and Eraring | February | 2013 | 2013Q3 | 2013 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2013-02-11 | N | 7 | N | 16 | N | N | 1.1101 | 39.4971 | 1166.3097
[7 empty] | 16893 | 2805 | 935464 | 2013-02-11 06:00 | 2013-02-11 11:00 | 300 | 11kV | 300 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134725 A phase DOLF : 10 Amp Excluded OMS 935454 | February | 2013 | 2013Q3 | 2013 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2013-02-11 | N | 300 | N | 16 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 16535 | 252 | 935457 | 2013-02-10 22:00 | 2013-02-11 12:00 | 840 | 11kV | 2520 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134726 A phase DOLF : 10 Amp Excluded OMS 935457 | February | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-02-10 | N | 840 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1841.5417
[7 empty] | 17641 | 10708 | 935403 | 2013-02-11 05:34 | 2013-02-11 12:13 | 399 | 11kV | 3136 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 134727 broken Cph tapping at pole FT-11452 near sub 54605. isolated from sw 58244 to make repairs at 1120 Excluded OMS 935403 | February | 2013 | 2013Q3 | 2013 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2013-02-11 | N | 156.8 | N | 16 | N | N | 1.1101 | 39.4971 | 2291.6963
[7 empty] | 18295 | 17426 | 935794 | 2013-02-11 12:00 | 2013-02-11 13:55 | 115 | 11kV | 230 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 134735 A & B phase DOLF : 16 Amp | February | 2013 | 2013Q3 | 2013 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2013-02-11 | N | 115 | N | 16 | N | N | 1.1101 | 39.4971 | 168.0772
[7 empty] | 17630 | 10533 | 935622 | 2013-02-11 10:30 | 2013-02-11 14:50 | 260 | 11kV | 260 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134736 A phase DOLF : 10 Amp Excluded OMS 935622 | February | 2013 | 2013Q3 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | UG | Not Veg | 2013-02-11 | N | 260 | N | 16 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 17035 | 3948 | 935382 | 2013-02-10 23:45 | 2013-02-11 15:00 | 915.0333 | 11kV | 39196.8333 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 134728 Tripped and locked out LID 134729 contiued outage from report 134728 on sub 52418 only CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-02-10 | N | 712.6697 | N | 24 | Y | Y | 1.1101 | 39.4971 | 28643.8897
[7 empty] | 16659 | 994 | 935624 | 2013-02-11 13:30 | 2013-02-11 15:30 | 120 | 11kV | 600 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134738 C phase DOLF : 10 Amp Excluded OMS 935624 | February | 2013 | 2013Q3 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | UG | Not Veg | 2013-02-11 | N | 120 | N | 16 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 17113 | 4523 | 935866 | 2013-02-11 16:00 | 2013-02-11 17:10 | 70 | 11kV | 140 | 2 | HV | Animal Goanna | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | LID 134739 C phase DOLF : 10 Amp Goanna Excluded OMS 935866 | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-02-11 | N | 70 | N | 16 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 17934 | 13420 | 935420 | 2013-02-11 04:23 | 2013-02-11 19:10 | 887 | 11kV | 1774 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 134742 Single phase DOLF : 10 Amp Excluded OMS 935397 | February | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | UG | Not Veg | 2013-02-11 | N | 887 | N | 16 | N | N | 1.1101 | 39.4971 | 1296.3869
[7 empty] | 17264 | 6696 | 935941 | 2013-02-11 22:31 | 2013-02-12 01:13 | 162 | 11kV | 96724 | 755 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | @Zn12610 Long Jetty Pa25 'Long Jetty Aux 2' tripped on Earth Fault, Earth Fault check relay, Lockout, 11kv frame leakage prob relay, EFI 11kv trip Zone earth #3 Group Earth EFI's-S18095 Abnormal: LB41635 open PT11559 in LV// Cause: not ascertained PT13065 was in LV// with S12230 See 936131,2,3,4,5 LV// 936127 exclude 935941,4 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Veg | 2013-02-11 | N | 128.1113 | N | 16 | N | N | 1.1101 | 39.4971 | 70683.0463
[7 empty] | 16828 | 2199 | 935955 | 2013-02-12 06:57 | 2013-02-12 08:30 | 93 | 11kV | 558 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134747 Fuse: 16 Amp Also refer to related record 935955 | February | 2013 | 2013Q3 | 2013 | 227:13020 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2013-02-12 | N | 93 | N | 6 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 17675 | 11117 | 935919 | 2013-02-11 17:54 | 2013-02-12 09:00 | 906 | 11kV | 906 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 134748 Single phase DOLF : 10 Amp Excluded OMS 935919 | February | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-02-11 | N | 906 | N | 16 | N | N | 1.1101 | 39.4971 | 662.0781
[7 empty] | 17968 | 13871 | 935958 | 2013-02-12 07:16 | 2013-02-12 09:00 | 104 | 11kV | 416 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134749 Fuse size : 10 Amp Also refer to related record 935958 | February | 2013 | 2013Q3 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-02-12 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 304.0005
[7 empty] | 17120 | 4572 | 935700 | 2013-02-11 07:20 | 2013-02-12 09:39 | 1579.0833 | 11kV | 4737.25 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Electrical Storm | N | CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-02-11 | N | 1579.0833 | N | 16 | N | N | 1.1101 | 39.4971 | 3461.8426
[7 empty] | 17472 | 8537 | 936297 | 2013-02-12 15:13 | 2013-02-12 18:12 | 179 | 11kV | 110892 | 776 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | @Zn12610 Long Jetty 11kV fdr Pa25 'Long Jetty Aux No2' Tripped on C Phase Earth Fault, EFI Tx3 Fault Check EFI-S18095 Abnormal: Air break Switch. LB41635 Open PT11559 in LV//. PT13065 was in LV// with S12230. Remarks: Line side of LB41635 HR 11kV in contact with LV on-call mains in attendanc. See seperate interruption 11/2/13 See 936928,9,30 LV// 936169 OMS 936938,9 Exclude 36297,309,17,8,9,20,38,53 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2013-02-12 | N | 142.9021 | N | 6 | N | N | 1.1101 | 39.4971 | 81036.6028
[7 empty] | 17312 | 7200 | 936390 | 2013-02-12 17:05 | 2013-02-12 18:15 | 70 | 11kV | 1260 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134760 Interruption for safety to repair low mains DQ Refer to related record936390 | February | 2013 | 2013Q3 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2013-02-12 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 17607 | 10119 | 936428 | 2013-02-13 00:38 | 2013-02-13 01:47 | 69 | 11kV | 126753 | 1837 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | At Zn36300 Balgowlah North Panel No. 19 "Hayes Condamine" 11kV feeder has tripped. Signals: Relays: B & C phase IOC and EFI. EFI's: S16827, S16064, S49927, S16928 and UGOH O/S 16 Myrtle St. North Balgowlah. Cause not Ascertained. | February | 2013 | 2013Q3 | 2013 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Veg | 2013-02-13 | N | 69 | N | 9 | N | N | 1.1101 | 39.4971 | 92627.3538
[7 empty] | 18493 | 19837 | 936419 | 2013-02-12 20:43 | 2013-02-13 03:32 | 409.0167 | 11kV | 12679.5167 | 31 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134763 Pole Mounted RAGCB, Earth Fault 3 operations Mains down between poles WB-51908 & WB-51920 | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-02-12 | N | 409.0167 | N | 6 | N | N | 1.1101 | 39.4971 | 9265.8168
[7 empty] | 17456 | 8368 | 936436 | 2013-02-13 06:30 | 2013-02-13 08:55 | 145 | 11kV | 161284 | 1875 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @Zn1285 Greenacre Park Panel 31 'Anzac Dominion & Wangee Water' tripped reclosed and locked out. Relays - Right leg 'Wangee Water'. Earth fault, EFI, Recloser timing relay and Lockout relay Signals - Zone earth and Tx4 Group Earth, 11kv trip Remarks: UG fault. Panel 31 front line feeder fault. Related jobs: #936891, 936890, 936887, 936436, 936472 | February | 2013 | 2013Q3 | 2013 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-02-13 | N | 86.0181 | N | 9 | N | N | 1.1101 | 39.4971 | 117861.5901
[7 empty] | 18130 | 15959 | 936509 | 2013-02-13 08:23 | 2013-02-13 09:45 | 82 | 11kV | 1550 | 27 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | @Zn14143 Sommersby Pa6 Earth Fault EFI Field EFI: S18379 S14634 S18540 S18454 S18253 S18339 S18636 S18256 S14278 EFI wired Incorrectly Cause: UGOH Fault Short Circuit Remarks: Suspected UGOH fault Section of 11kV isolated & Earthed from: S14278 SwB to S18084 SwA to LB40493 Access permits issued to lineworker & jointer @ S14278 See 936963,4,5 Exclude 936477,509 | February | 2013 | 2013Q3 | 2013 | ZN14143:PA6 | ZN14143:PA6 | ZN14143/000006 | CENTRAL COAST | Unknown | Unknown | 2013-02-13 | N | 57.4074 | N | 9 | N | N | 1.1101 | 39.4971 | 1132.6943
[7 empty] | 16640 | 897 | 936489 | 2013-02-13 09:05 | 2013-02-13 09:55 | 50 | 11kV | 50 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134769 Fuse size: 16 Amp No cause found not storm conditions refer to related record 936502 | February | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2013-02-13 | N | 50 | N | 9 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 17505 | 8859 | 936430 | 2013-02-13 04:29 | 2013-02-13 14:15 | 586 | 11kV | 16175 | 40 | HV | Vegetation Grow In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 134767 2 fault operations Excluded OMS 936433 | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-02-13 | N | 404.375 | N | 9 | N | N | 1.1101 | 39.4971 | 11820.2129
[7 empty] | 18273 | 17225 | 936169 | 2013-02-12 12:19 | 2013-02-13 14:37 | 1578 | 11kV | 33813 | 364 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Original Interruption: @REC 61340 Georges Downes Bloodtree 0.2 CB Open, O/C Trip, Lockout First attempt: @Rec 61340 Georges Downes Bloodtree 0.2: CB open, O/C Trip, Lockout Cause: UG Fault. Adj S12654 HYMIX Quarry George No2 S12654 failed on energising @ 1433 on Wed 13/2/13 - see seperate interruption report See 937982,3 2nd 937985 GIS 937997 Exclude 936169,697 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | UG | Not Veg | 2013-02-12 | N | 92.8929 | N | 6 | N | N | 1.1101 | 39.4971 | 24709.5431
[7 empty] | 17647 | 10739 | 936608 | 2013-02-13 11:53 | 2013-02-13 18:05 | 372 | 11kV | 1860 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Pa5 "Wyong' @PT12723 Mandalong Dick 0.8 Foot Path Phase 16 Amp HDO:Fatigue Batch no 2591 Cause: Fuse Fatigue. Batch No 2591 See 936968 Exclude 936608 | February | 2013 | 2013Q3 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-02-13 | N | 372 | N | 9 | N | N | 1.1101 | 39.4971 | 1359.2331
[7 empty] | 17779 | 12225 | 936813 | 2013-02-13 20:48 | 2013-02-13 21:41 | 53 | 11kV | 10494 | 198 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S129 Hunters Hill Panel 27 Tripped on Relays: A and C phase O/C, IOC and EFI Signals: Tx3 Group Earth, Zone Earth and 11kV Trip Cause Not ascertained for outage See OMS 937266 937272 | February | 2013 | 2013Q3 | 2013 | ZN129:PA27 | ZN129:PA51 | ZN00129/000051 | HUNTERS HILL | OH | Veg | 2013-02-13 | N | 53 | N | 9 | N | N | 1.1101 | 39.4971 | 7668.7057
[7 empty] | 18247 | 17058 | 936814 | 2013-02-13 20:51 | 2013-02-13 23:05 | 134 | 11kV | 14951.1667 | 112 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT48320 Emerald Diamond Footpath Phase HDO fuse fell open Ex Panel 18 Cause: HDO fuse fell open See 936811 GIS 938098 Exclude 936814 CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | ZN12640:PA18 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2013-02-13 | N | 133.4926 | N | 9 | N | N | 1.1101 | 39.4971 | 10925.8716
[7 empty] | 17562 | 9491 | 936741 | 2013-02-13 16:16 | 2013-02-14 01:00 | 524 | 11kV | 34287 | 283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Pa5 IR61082 Brieses Peats 0.3 @IR61082 Brieses Peats tripped on O/C Cause: Tree branch brought down OH outside 98 Keighley Ave Somersby See 938072,3 Exclude 936741,2,8 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2013-02-13 | N | 121.1555 | N | 9 | N | N | 1.1101 | 39.4971 | 25055.9283
[7 empty] | 17310 | 7176 | 937077 | 2013-02-14 14:54 | 2013-02-14 16:20 | 86 | 11kV | 602 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134789 Single phase DOLF : 20 Amp Excluded OMS No. 937077+937087+937115 Please Patrol Feeder. | February | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2013-02-14 | N | 86 | N | 3 | N | N | 1.1101 | 39.4971 | 439.9238
[7 empty] | 18196 | 16569 | 937133 | 2013-02-14 16:08 | 2013-02-14 19:35 | 207 | 11kV | 55777 | 906 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn12690 Berkeley Vale 11kv fdr pa24 tripped on: A&B Overcurrent EFI: Nil Cause: tree branch brought down oh Outside 52 Howes rd Ourimbah See 938163,4 GIS 938161,2 Exclude 937133,5,7,43,5 | February | 2013 | 2013Q3 | 2013 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2013-02-14 | N | 61.564 | N | 3 | N | N | 1.1101 | 39.4971 | 40760.1865
[7 empty] | 17369 | 7642 | 937174 | 2013-02-14 17:44 | 2013-02-14 19:50 | 126 | 11kV | 252 | 2 | HV | Animal Goanna | Animal | DC Not Transformer | Unplanned | No Weather Impact | N | LID 134790 Single phase DOLF : 10 Amp OMS No. 937174 Dead goanna found at sub. TX Volts: 237V Tx load: 14A Excluded OMS No. 937174 | February | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-02-14 | N | 126 | N | 3 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 18316 | 17603 | 937207 | 2013-02-15 03:49 | 2013-02-15 05:35 | 106 | 11kV | 3816 | 36 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT 9395 Anzac Highway - Centre Phase HDO operated (50A). Possum on PT. Operated fuse. | February | 2013 | 2013Q3 | 2013 | ZN9245:PA15 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | OH | Not Veg | 2013-02-15 | N | 106 | N | 3 | N | N | 1.1101 | 39.4971 | 2788.6202
[7 empty] | 17738 | 11853 | 937397 | 2013-02-15 11:54 | 2013-02-15 12:51 | 57 | 11kV | 47978 | 894 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Rain Light | N | At S4545 Meadowbank Panel 26 Tripped Reclosed Tripped and Locked Out on Relays: A and C phase O/C and E/F and Lockout Signals: Zone Earth, Group Earth 11Kv Trip Cause: UG cable damaged by excavator between S2571 Railway Wernard SW/B to S8784 Railway Waterpoint No4 SW/A to S3387 Angus National Can SW/A See OMS 938416 938419 938420 937400 937406 | February | 2013 | 2013Q3 | 2013 | ZN4545:PA26 | ZN4545:PA26 | ZN04545/000026 | RYDE | UG | Not Veg | 2013-02-15 | N | 53.6667 | N | 3 | N | N | 1.1101 | 39.4971 | 35060.9073
[7 empty] | 17007 | 3627 | 937547 | 2013-02-15 15:38 | 2013-02-15 17:26 | 108 | 11kV | 13176 | 122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.342 Paddington Pnl.15 tripped on A Phase overcurrnet, Earth Fault, EFI UG cable fault from S5277 to S2246 see 937954 937953 | February | 2013 | 2013Q3 | 2013 | ZN342:PA15 | ZN342:PA15 | ZN00342/000015 | WOOLLAHRA | UG | Not Veg | 2013-02-15 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 9628.6322
[7 empty] | 17414 | 8073 | 937629 | 2013-02-16 02:39 | 2013-02-16 03:45 | 66 | 11kV | 29974 | 827 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn14144 Eamberal Pa4 fdr tripped on Relays: Earth Fault, 51N, EFI Signals: 11kv trip, Zone Earth Cause: Tree/Branch on OH Mains. DOp removed branch from 11kv mains outside 56 hastings rd between USL43116 & AB41597. Street Light Conductor down into LV @ PT12362. See 938316,9 Exclude 937629 | February | 2013 | 2013Q3 | 2013 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2013-02-16 | N | 36.2443 | N | 1 | N | N | 1.1101 | 39.4971 | 21904.1151
[7 empty] | 16716 | 1312 | 937796 | 2013-02-17 07:43 | 2013-02-17 09:40 | 117 | 11kV | 234 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134820 C phase DOLF : 10 Amp Excluded OMS No. 937796 | February | 2013 | 2013Q3 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-02-17 | N | 117 | N | 3 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 17704 | 11590 | 938005 | 2013-02-17 09:46 | 2013-02-17 10:34 | 48 | 11kV | 48 | 1 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134821 Myuna Coal Operator openned wrong Bus Isolator (BI 23) under load after opening Sw 42. No damage. | February | 2013 | 2013Q3 | 2013 |  |  |  | LAKE MACQUARIE | OH | Not Veg | 2013-02-17 | N | 48 | N | 3 | N | N | 1.1101 | 39.4971 | 35.077
[7 empty] | 17722 | 11747 | 937841 | 2013-02-17 11:23 | 2013-02-17 12:42 | 79 | 11kV | 36989 | 475 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | TCAT 12918 George Barnes Downes 0.1 Tripped on: SE Ex Pa4 labelled Kulnura Abnormal: IR61341 Closed, ZN12630:Pa1 Open Cause: DOp Patrolled could not find any cause. Poosible fault insulator See 938449,51,2 Exclude 937841,8 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-02-17 | N | 77.8716 | N | 3 | N | N | 1.1101 | 39.4971 | 27030.4702
[7 empty] | 16661 | 1001 | 937914 | 2013-02-18 00:01 | 2013-02-18 03:58 | 237 | 11kV | 220834 | 1593 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134823 4 fault operations Sensitive Earth Fault Medowie Regulator No 1 SEF fault Excluded OMS 937914 | February | 2013 | 2013Q3 | 2013 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2013-02-18 | N | 138.6277 | N | 3 | N | N | 1.1101 | 39.4971 | 161378.9737
[7 empty] | 18453 | 19133 | 937916 | 2013-02-18 04:54 | 2013-02-18 06:12 | 78 | 11kV | 116298 | 1491 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 134824 3 fault operations. 3 phase. Earth fault; Overcurrent Possum contacted a UGOH at pole AH-20566 in Main St Scone outside Woolworths, this UGOH needs to be repaired before it can be put back into service. Ist Trip 3 ph overcurrent and earth fault. 2nd trip 3 phase overcurrent (2800Amps) Excluded OMS # 937916 AND 937918. | February | 2013 | 2013Q3 | 2013 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2013-02-18 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 84987.1482
[7 empty] | 17336 | 7359 | 938083 | 2013-02-18 10:55 | 2013-02-18 11:30 | 35 | 11kV | 385 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 134830 A phase DOLF : 40 Amp Excluded OMS 938088 | February | 2013 | 2013Q3 | 2013 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | UG | Not Veg | 2013-02-18 | N | 35 | N | 3 | N | N | 1.1101 | 39.4971 | 281.3466
[7 empty] | 17531 | 9015 | 938400 | 2013-02-19 06:31 | 2013-02-19 08:18 | 107 | 11kV | 3103 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S4499 Keelendi Victoria 400A fuse blown on C phase of distributor 1. Cause: Tree branch caused mains too clash See OMS 938937 938400/401/403 | February | 2013 | 2013Q3 | 2013 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | OH | Veg | 2013-02-19 | N | 107 | N | 7 | N | N | 1.1101 | 39.4971 | 2267.5809
[7 empty] | 18018 | 14561 | 938486 | 2013-02-19 09:28 | 2013-02-19 10:07 | 39 | 11kV | 96163 | 2717 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S.15008 Harbord, Panel 7 Fdr CB tripped and reclosed. (A.OP opened feederr again at 9:36 due to smoking and arcing) B and C phase IOC, fault check, lockout relay and reclose timing relay, 11kV trip, zone earth. Car hit pole in Griffin St & cnr Adam St Curl Curl. | February | 2013 | 2013Q3 | 2013 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2013-02-19 | N | 35.3931 | N | 7 | N | N | 1.1101 | 39.4971 | 70273.0841
[7 empty] | 18537 | 20196 | 939127 | 2013-02-19 18:10 | 2013-02-19 18:25 | 15 | 11kV | 45 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Pa6 fdr from Zn148925 Charmhaven Section of fdr from AB41862 to AB40770 to S14019:SW6210 Freeway Tooheys interrupted to allow large tree to be removed from 11kv mains in Roper Rd Blue Haven. | February | 2013 | 2013Q3 | 2013 | ZN14892:PA6 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Veg | 2013-02-19 | N | 15 | N | 7 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 18538 | 20197 | 938709 | 2013-02-19 16:52 | 2013-02-19 20:00 | 188 | 11kV | 71948 | 1521 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12610 Long Jetty Pa2 fdr tripped on: Relays: Aph Instantaneous & Timed Overcurrent, EFI, Earth Fault Check Signals: 11kv trip Abnormal: Rec Pa2 was N/A due to switching Cause: 11kv UGOH Fault Short Circuit (exploded) on tee to S18087 Bowling Club Bias See 939074,5,6,7 GIS 938720,2,9070 Exclude 938709,10,4,24,6,7,8 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | Unknown | Unknown | 2013-02-19 | N | 47.3031 | N | 7 | N | N | 1.1101 | 39.4971 | 52577.4763
[7 empty] | 18430 | 18920 | 938769 | 2013-02-19 19:28 | 2013-02-19 21:15 | 107 | 11kV | 105621 | 1606 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.15002 Narrabeen, Panel 6 Fdr CB tripped on A phase timed OC, efi, 11kV trip, zone earth. Field efi's down at S.16441, s.16903. Birds contacted 11kV OH bonds burnt off between AB.22120 to USL 24420 tee S.16757 {Jacksons Rd, Narrabeen} | February | 2013 | 2013Q3 | 2013 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-02-19 | N | 65.7665 | N | 7 | N | N | 1.1101 | 39.4971 | 77184.7115
[7 empty] | 17543 | 9113 | 938792 | 2013-02-19 22:14 | 2013-02-19 23:15 | 61 | 11kV | 2806 | 46 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12600 Lisarow 11kv OCB Pa1 'dog trap gully' feeder @ PT14021 Barkala Dora - 11kv Roadside 20K HVDO operated Possible fuse fatigue See 939123,792,3,6 | February | 2013 | 2013Q3 | 2013 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2013-02-19 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 2050.542
[7 empty] | 17215 | 6080 | 938760 | 2013-02-19 19:11 | 2013-02-20 02:30 | 439 | 11kV | 11931 | 57 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Recloser 44604 Dog trap rd tripped, reclosed, tripped & locked out on O/C Ex Pa1 'Dog trap rd' Feeder from Zn12650 West Gosford Cause: Vehicle hit pole. HV Pole in Dog Trap Rd knocked down by MV See 939102,4 exclude 938760,6 | February | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-02-19 | N | 209.3158 | N | 7 | N | N | 1.1101 | 39.4971 | 8718.8229
[7 empty] | 17285 | 6950 | 939352 | 2013-02-20 08:00 | 2013-02-20 08:10 | 10 | 11kV | 410 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134851 A & B phase DOLF : 20 Amp SI 30697 cancelled after switching started. DOLFs blew while restoring FDR | February | 2013 | 2013Q3 | 2013 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2013-02-20 | N | 10 | N | 5 | N | N | 1.1101 | 39.4971 | 299.6159
[7 empty] | 16862 | 2423 | 938879 | 2013-02-20 09:20 | 2013-02-20 11:15 | 115 | 11kV | 1035 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Pa3 @PT13225 Ironbark Lombardy. 11kv roadside HDO fuse operated Cause: fuse fatigue See 939326 Exclude 938865,79 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2013-02-20 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 756.3475
[7 empty] | 17021 | 3831 | 939110 | 2013-02-20 15:06 | 2013-02-20 15:42 | 36 | 11kV | 10800 | 300 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2568 St peters Pnl.28 tripped on: Earth Fault relay UG cable fault front line of feeder. | February | 2013 | 2013Q3 | 2013 | ZN2568:PA28 | ZN2568:PA28 | ZN02568/000028 | SYDNEY | UG | Not Veg | 2013-02-20 | N | 36 | N | 5 | N | N | 1.1101 | 39.4971 | 7892.3215
[7 empty] | 18128 | 15951 | 939192 | 2013-02-20 18:43 | 2013-02-20 19:25 | 42 | 11kV | 2814 | 67 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134863 B Phase DOLF DOLF assembly broken in half Excluded OMS 939192, 939193 | February | 2013 | 2013Q3 | 2013 | 210:8682 | 210:83465 | ZN00210/083465 | LAKE MACQUARIE | OH | Not Veg | 2013-02-20 | N | 42 | N | 5 | N | N | 1.1101 | 39.4971 | 2056.3882
[7 empty] | 17083 | 4292 | 939206 | 2013-02-20 19:58 | 2013-02-20 22:00 | 122 | 11kV | 610 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 134865 C phase DOLF : 10 Amp Faulty service mains. Excluded OMS 939206 | February | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2013-02-20 | N | 122 | N | 5 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 16855 | 2369 | 939227 | 2013-02-21 01:49 | 2013-02-21 03:45 | 116 | 11kV | 6142.8 | 53 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At PT.15699 the A and B phase 31.5 amp fuses blown. Field efi down at S.16011. Possum at PT.15699 CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2013-02-21 | N | 115.9019 | N | 6 | N | N | 1.1101 | 39.4971 | 4488.9771
[7 empty] | 18212 | 16714 | 939344 | 2013-02-21 10:10 | 2013-02-21 11:00 | 50 | 11kV | 350 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134877 Fuse size: 63 Amp no cause found not storm condition also refer to 939344 | February | 2013 | 2013Q3 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2013-02-21 | N | 50 | N | 6 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 18472 | 19427 | 939242 | 2013-02-21 06:21 | 2013-02-21 12:38 | 377 | 11kV | 89025 | 921 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn 80 Chatswood 11kV Panel Tripped on Relays: IOC - EFI - L/O - Timing Relay Signals: 11kV trip Cause: Tree on 11kV OH on Cnr of elizabeth and Gordon Lane Cove North See OMS 939679 939681 939888 939680 | February | 2013 | 2013Q3 | 2013 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2013-02-21 | N | 96.6612 | N | 6 | N | N | 1.1101 | 39.4971 | 65056.8442
[7 empty] | 16709 | 1270 | 939539 | 2013-02-21 15:13 | 2013-02-21 16:30 | 77 | 11kV | 154 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 134884 OMS # 939539. Burnt off LL Clamp No protection operated as it was a burnt off connection. | February | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-02-21 | N | 77 | N | 6 | N | N | 1.1101 | 39.4971 | 112.5387
[7 empty] | 16578 | 515 | 939585 | 2013-02-21 16:48 | 2013-02-21 20:25 | 217 | 11kV | 217 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134883 Fuse size: 10 Amp No cause found not storm conditions - also refer to 939585 | February | 2013 | 2013Q3 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-02-21 | N | 217 | N | 6 | N | N | 1.1101 | 39.4971 | 158.5772
[7 empty] | 17725 | 11772 | 939376 | 2013-02-21 10:45 | 2013-02-21 21:05 | 620 | 11kV | 6200 | 43 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 134880 3 fault operations A phase Earth fault, Overcurrent Fault current was 1601 amps on A phase. Vandal damaged UGOH at pole GS-61289. Excluded OMS # 939376. | February | 2013 | 2013Q3 | 2013 | 507:80926 | 507:80926 | ZN00507/080926 | CESSNOCK | Unknown | Unknown | 2013-02-21 | N | 144.186 | N | 6 | N | N | 1.1101 | 39.4971 | 4530.7771
[7 empty] | 17320 | 7259 | 939692 | 2013-02-22 09:00 | 2013-02-22 10:20 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134888 Fuse size: 10 Amp - No cause found not storm conditions Refer to 939692 - 245 Volts | February | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2013-02-22 | N | 80 | N | 7 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 17132 | 4653 | 939993 | 2013-02-22 16:54 | 2013-02-22 18:10 | 76 | 11kV | 57212 | 833 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 134893 4 fault operations A & B phase Earth fault. Overcurrent Excluded OMS 939993 | February | 2013 | 2013Q3 | 2013 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | Unknown | Unknown | 2013-02-22 | N | 68.6819 | N | 7 | N | N | 1.1101 | 39.4971 | 41808.8421
[7 empty] | 17314 | 7204 | 939910 | 2013-02-22 14:18 | 2013-02-22 18:14 | 236 | 11kV | 92267 | 2707 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn1193 Lindfield Pnl.28L tripped & reclosed on B ph IOC CP2749 Delhi River tripped and locked out on IOC Branch on 11kV cleared by DOp - on try back mains came down on LV mains in fullers rd see 942685 942684 942682 942681 | February | 2013 | 2013Q3 | 2013 | ZN1193:PA28 | ZN80:PA31 | ZN00080/000031 | KU-RING-GAI | OH | Veg | 2013-02-22 | N | 34.0846 | N | 7 | N | N | 1.1101 | 39.4971 | 67426.0022
[7 empty] | 16721 | 1327 | 940060 | 2013-02-22 19:36 | 2013-02-22 21:00 | 84 | 11kV | 168 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | N | LID 134903 Single phase DOLF Excluded OMS 940060 | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | UG | Not Veg | 2013-02-22 | N | 84 | N | 7 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 16978 | 3409 | 940036 | 2013-02-22 18:07 | 2013-02-22 23:30 | 323 | 11kV | 5814 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 134904 A phase DOLF DOLF broken in half. Excluded oms-940036 + 940058 | February | 2013 | 2013Q3 | 2013 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2013-02-22 | N | 323 | N | 7 | N | N | 1.1101 | 39.4971 | 4248.6997
[7 empty] | 17772 | 12099 | 940043 | 2013-02-22 15:45 | 2013-02-22 23:50 | 485 | 11kV | 7275 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630Peats Ridge Zone Pa4 Section between LB41564 to AB44293 tee to PT12006 & PT14896 & PT13132 Interrupted by DOp to allow removal of tree and repair to HV link in Euloo St Large branch on Mains in Euloo st & USL44814 Centre Phase fell apart See 944834 exclude 939855,40043 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2013-02-22 | N | 485 | N | 7 | N | N | 1.1101 | 39.4971 | 5316.3554
[7 empty] | 16636 | 886 | 940083 | 2013-02-22 23:24 | 2013-02-23 02:19 | 175 | 11kV | 194950 | 1114 | HV | Equipment Failed in Service | Equipment Failure | U/G Link | Unplanned | Unselected | N | LID 134905 oms 940083 Blown Hazemeyer found at St Fagans sub 54777. 3 Fault operations, overcurrent | February | 2013 | 2013Q3 | 2013 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | UG | Not Veg | 2013-02-22 | N | 175 | N | 7 | N | N | 1.1101 | 39.4971 | 142463.7099
[7 empty] | 17674 | 11112 | 940093 | 2013-02-23 01:33 | 2013-02-23 02:23 | 50 | 11kV | 129250 | 2585 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | Y | REC 41873 Woolana Woodland Tripped abnormal: LB40928 CLOSED - AB42641 OPEN & DEFECTIVE - AB438064 CLOSED - USL43866 OPEN & DEFECTIVE Vehicle hit pole on scenic drive Buff Point | February | 2013 | 2013Q3 | 2013 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2013-02-23 | Y | 50 | N | 10 | N | Y | 1.1101 | 39.4971 | 94452.0878
[7 empty] | 16957 | 3289 | 940104 | 2013-02-23 02:59 | 2013-02-23 03:10 | 10.5167 | 11kV | 851.85 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 134906 Emergency isolation to make safe at sub 27462 | February | 2013 | 2013Q3 | 2013 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2013-02-23 | N | 10.5167 | N | 10 | N | N | 1.1101 | 39.4971 | 622.5069
[7 empty] | 17179 | 5532 | 940116 | 2013-02-23 05:58 | 2013-02-23 07:00 | 62.2667 | 11kV | 1058.5333 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex Zn12630 Peats Ridge: Section of 11kv feeder Pa4 @TCAT12918 George Downes Barnes 0.1 Tripped on Relay: Differential Cause: Branch on mains at TCAT 12918 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 62.2667 | N | 10 | N | Y | 1.1101 | 39.4971 | 773.5449
[7 empty] | 18454 | 19138 | 940115 | 2013-02-23 05:51 | 2013-02-23 08:20 | 149 | 11kV | 11368 | 98 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | Y | REC 44790 Hansens Rd tripped on IOC Suspect HDO or Transformer problem @ PT11912 | February | 2013 | 2013Q3 | 2013 | ZN12690:PA7 | ZN12690:PA7 | ZN12690/000007 | CENTRAL COAST | UG | Not Veg | 2013-02-23 | Y | 116 | N | 10 | N | Y | 1.1101 | 39.4971 | 8307.3991
[7 empty] | 17298 | 7087 | 940135 | 2013-02-23 07:26 | 2013-02-23 08:50 | 84 | 11kV | 168 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | Y | LID 134908 Single phase DOLF : 10 Amp Excluded OMS 940135 | February | 2013 | 2013Q3 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | UG | Not Veg | 2013-02-23 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 122.7694
[7 empty] | 17919 | 13294 | 942973 | 2013-02-23 04:45 | 2013-02-23 09:00 | 255 | 11kV | 5745 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | Y | LID 134907 A phase DOLF : 10 Amp top of both DOLF broken off Rang in by SRA. | February | 2013 | 2013Q3 | 2013 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2013-02-23 | N | 92.6613 | N | 10 | N | N | 1.1101 | 39.4971 | 4198.2766
[7 empty] | 17027 | 3859 | 940099 | 2013-02-23 02:10 | 2013-02-23 10:00 | 470 | 11kV | 133286 | 1163 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | Y | Zn.12610 Long Jetty Pnl.9 tripped on O/C OH resting on cross arm - broken cross arm @ uSL 42032 - HV bond needs repairing to PT11115 see 942580 942582 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | OH | Not Veg | 2013-02-23 | Y | 114.6053 | N | 10 | N | Y | 1.1101 | 39.4971 | 97401.4775
[7 empty] | 16656 | 967 | 940239 | 2013-02-23 10:04 | 2013-02-23 12:25 | 141 | 11kV | 282 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 134910 Fuse size: 10 Amp also refer 940239 | February | 2013 | 2013Q3 | 2013 | 504:48031 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2013-02-23 | Y | 141 | N | 10 | N | Y | 1.1101 | 39.4971 | 206.0773
[7 empty] | 17954 | 13702 | 940221 | 2013-02-23 09:38 | 2013-02-23 13:32 | 234 | 11kV | 16792 | 223 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | Y | REC 45000 Tumbi Umbi tripped / reclosed / tripped & locked out on Earth Fault UGOH has fault in conection on pole see 942594 942595 942596 | February | 2013 | 2013Q3 | 2013 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | Unknown | Unknown | 2013-02-23 | Y | 75.3004 | N | 10 | N | Y | 1.1101 | 39.4971 | 12271.0983
[7 empty] | 17786 | 12310 | 940237 | 2013-02-23 09:55 | 2013-02-23 14:45 | 290 | 11kV | 44417 | 425 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | Y | Ex Zn12630 Peats Ridge 11kv fdr Pa3 REC45071 Central Mangrove tripped, reclosed, tripped, reclosed, tripped, reclosed & tripped pn IOC Remarks: Large tree resting on mains. See Seperate interruption report 944858 Pa4 tripped @ 11:53 Switching made such that section of Pa3 restored via Pa4. Pa4 tripped whilst restoring Pa3. See 944925,6,7 2nd Incident 944930 Exclude 940237,8,331,72,8,9,650 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 104.5106 | N | 10 | N | Y | 1.1101 | 39.4971 | 32458.6335
[7 empty] | 17127 | 4625 | 940421 | 2013-02-23 13:19 | 2013-02-23 15:35 | 136 | 11kV | 84658 | 913 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | Y | Zn.965 Pennant Hills - Pnl.26 tripped on SEF & EFI Tree brought down OH in Larool Cr see 942719 942720 942721 | February | 2013 | 2013Q3 | 2013 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2013-02-23 | Y | 92.7251 | N | 10 | N | Y | 1.1101 | 39.4971 | 61865.5694
[7 empty] | 17293 | 7022 | 940422 | 2013-02-23 13:24 | 2013-02-23 15:59 | 155 | 11kV | 35703 | 231 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex Zn12610 Peats Ridge 11kv fdr Pa1 @ REC44995 Kulnura Tripped, Reclosed, Tripped, Reclosed, Tripped, Reclosed, Tripped on Relay: IOC, O/C, EF Cause: Tree down adj PT13280 FINNS GRETA. Mains to remove/ repair See 944877,8 Exclude 940422 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 154.5584 | N | 10 | N | Y | 1.1101 | 39.4971 | 26090.6993
[7 empty] | 18057 | 15410 | 940495 | 2013-02-23 14:37 | 2013-02-23 16:26 | 109 | 11kV | 120404 | 1622 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | Y | Zn.187 Crows Nest - Pnl.8 tripped on C phase Earth Fault UG cable fault from S963 Sw A to S884 Sw A to S2336 Sw B see 942729 942728 | February | 2013 | 2013Q3 | 2013 | ZN187:PA8 | ZN187:PA8 | ZN00187/000008 | NORTH SYDNEY | UG | Not Veg | 2013-02-23 | N | 74.2318 | N | 10 | N | N | 1.1101 | 39.4971 | 87987.6919
[7 empty] | 16663 | 1010 | 940362 | 2013-02-23 12:08 | 2013-02-23 16:45 | 277 | 11kV | 102950 | 630 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | Y | Section of Pnl.10 Noraville from USL 43994 - B phase bond went open circuit | February | 2013 | 2013Q3 | 2013 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2013-02-23 | Y | 163.4127 | N | 10 | N | Y | 1.1101 | 39.4971 | 75232.8235
[7 empty] | 17435 | 8214 | 940528 | 2013-02-23 15:18 | 2013-02-23 17:05 | 107 | 11kV | 26322 | 246 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | Y | West Gosford Pnl.6L - REC 44824 Wyoming - tripped on SEF *Pnl 1 low volts below AB40337 bond failed abnormal switching: AB44909 OPEN & Defective - Sw A @ S18568 CLOSED - LB 50248 CLOSED - Sw A @ CP41125 OPEN Open bond 1 bay from AB40337 Pole GO2764 | February | 2013 | 2013Q3 | 2013 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2013-02-23 | Y | 107 | N | 10 | N | Y | 1.1101 | 39.4971 | 19235.3412
[7 empty] | 17962 | 13757 | 940550 | 2013-02-23 16:39 | 2013-02-23 19:05 | 146 | 11kV | 14162 | 97 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | PT2382 Cotoon Downes - Dist #1 & 2 interupted for safety tree brought down mains in Downes St North Epping. No fuses blown. IDTs were found in on the corner of Cotoon and Beck st. | February | 2013 | 2013Q3 | 2013 | ZN2635:PA21 | ZN2635:PA52 | ZN02635/000052 | HORNSBY | OH | Veg | 2013-02-23 | Y | 146 | N | 10 | N | Y | 1.1101 | 39.4971 | 10349.1719
[7 empty] | 17090 | 4343 | 940768 | 2013-02-23 18:51 | 2013-02-23 19:15 | 24 | 11kV | 9432 | 393 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Zn.35500 Top Ryde -Pnl.28L section of feeder interrupted fromS46792 to AB2566 to AB280 to remove a tree off UGOH to S4679 Bottom four subs not switched due to cross power source LB1476 CLOSED - AB2566 OPEN | February | 2013 | 2013Q3 | 2013 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2013-02-23 | N | 24 | N | 10 | N | N | 1.1101 | 39.4971 | 6892.6274
[7 empty] | 18468 | 19221 | 940650 | 2013-02-23 17:00 | 2013-02-23 20:30 | 210 | 11kV | 3250 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex ZN12630 Peats Ridge 11kV Pa3 REC46895 Wise Ferry IronBark tripped on IOC Remarks:Trees on HV Mains below AB41533 See 945211 separatte interuption report Pa3@19:50. @17:40 partial restoration from REC46895-AB41553,PT18841. @19:50 Pa3 tripped. @20:30 Restoration from REC46895-rest of feeder (AB44077,PT18841).(restoration upstream of REC46895 to Pa3 see 945211 See 945209,10 Exclude 940650 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 54.1667 | N | 10 | N | Y | 1.1101 | 39.4971 | 2375.0041
[7 empty] | 17050 | 4034 | 940752 | 2013-02-23 18:31 | 2013-02-23 20:50 | 139 | 11kV | 83815 | 835 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | Y | REC 41778 Amy Kincumber 0.1 tripped / reclosed / tripped &locked out on OC C phase cable (600mm below lightning arrestor) on UGOH below S14475 short circuit see 942635 942637 942638 | February | 2013 | 2013Q3 | 2013 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | Unknown | Unknown | 2013-02-23 | Y | 100.3772 | N | 10 | N | Y | 1.1101 | 39.4971 | 61249.5299
[7 empty] | 17185 | 5608 | 940761 | 2013-02-23 18:35 | 2013-02-23 21:03 | 148 | 11kV | 8568 | 60 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Trees on HV mains between LB40866 & LB44275 - interrupted by DOp @ 18:35 for safety. iR41066 McDonalds Rd failed to operate | February | 2013 | 2013Q3 | 2013 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 142.8 | N | 10 | N | Y | 1.1101 | 39.4971 | 6261.2417
[7 empty] | 16597 | 597 | 940704 | 2013-02-23 21:06 | 2013-02-23 21:52 | 46 | 11kV | 53607 | 1227 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn.9900 Menai Pnl.1 tripped on A & B ohase IOC and Timed OC Weather related - river crossing to be patrolled in daylight see 942832 942833 942834 | February | 2013 | 2013Q3 | 2013 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | OH | Veg | 2013-02-23 | N | 43.6895 | N | 10 | N | N | 1.1101 | 39.4971 | 39174.4145
[7 empty] | 16673 | 1081 | 941027 | 2013-02-23 21:17 | 2013-02-23 23:10 | 113 | 11kV | 8701 | 77 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | PT628 - Dist #2 - ABC phase fuses blown Tree branch on mains | February | 2013 | 2013Q3 | 2013 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Veg | 2013-02-23 | N | 113 | N | 10 | N | N | 1.1101 | 39.4971 | 6358.4342
[7 empty] | 17663 | 10936 | 941191 | 2013-02-23 23:18 | 2013-02-24 00:09 | 51 | 11kV | 49419 | 969 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC 20397 Pittwater Cabbage Tree - tripped / reclosed / locked out on OC and IOC Dop removed tree from 11kV in rednal St | February | 2013 | 2013Q3 | 2013 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2013-02-23 | Y | 51 | N | 10 | N | Y | 1.1101 | 39.4971 | 36113.9476
[7 empty] | 18483 | 19621 | 940724 | 2013-02-23 22:00 | 2013-02-24 00:42 | 162 | 11kV | 486 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 134926 Broken live line lead, also refer to 940724 | February | 2013 | 2013Q3 | 2013 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Not Veg | 2013-02-23 | N | 162 | N | 10 | N | N | 1.1101 | 39.4971 | 355.1545
[7 empty] | 17398 | 7940 | 940874 | 2013-02-23 20:00 | 2013-02-24 01:30 | 330 | 11kV | 118086 | 646 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | REC 3228 Berowra Pump tripped / reclosed / tripped on Earth fault ABC phase OC Tree brought down 3 bays of HV mains in Hillcrest Ave. mains have been broken away @ AB2385 and @ tee to PT2165 see 942753 942754 also Suspect PT2033 was in parallel with pa 26 at the time of interruption those customers included in this record | February | 2013 | 2013Q3 | 2013 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Veg | 2013-02-23 | Y | 182.7957 | N | 10 | N | Y | 1.1101 | 39.4971 | 86293.7659
[7 empty] | 16897 | 2846 | 941357 | 2013-02-24 00:46 | 2013-02-24 01:46 | 60 | 11kV | 16740 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.10996 Rockdale Pnl.20 tripped on A phase IOC Appears tree in west botany st brushed feeder | February | 2013 | 2013Q3 | 2013 | ZN10996:PA20 | ZN10998:PA24 | ZN10998/000024 | BAYSIDE | OH | Veg | 2013-02-24 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 12233.0983
[7 empty] | 18312 | 17558 | 940966 | 2013-02-23 23:12 | 2013-02-24 02:02 | 170 | 11kV | 190200 | 1216 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn.2400 Berowra Pnl.15 - tripped on A & C phase OC Cause not ascertained - weather related see 942763 942764 942766 | February | 2013 | 2013Q3 | 2013 | ZN2400:PA15 | ZN2400:PA15 | ZN02400/000015 | HORNSBY | OH | Veg | 2013-02-23 | Y | 156.4145 | N | 10 | N | Y | 1.1101 | 39.4971 | 138992.55
[7 empty] | 18103 | 15823 | 941284 | 2013-02-23 23:33 | 2013-02-24 02:06 | 153 | 11kV | 64903 | 426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | REC 20112 Kalang Rd tripped / reclosed / tripped and locked out on Overcurrent Abnormal: LB20234 CLOSED - AB20129 OPEN Dop found a number of trees close to the mains along feeder see 942813 942814 | February | 2013 | 2013Q3 | 2013 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2013-02-23 | Y | 152.3545 | N | 10 | N | Y | 1.1101 | 39.4971 | 47429.1981
[7 empty] | 17257 | 6609 | 940817 | 2013-02-23 20:30 | 2013-02-24 02:20 | 350 | 11kV | 350 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 134927 also refer to 940817 | February | 2013 | 2013Q3 | 2013 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2013-02-23 | N | 350 | N | 10 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 17081 | 4277 | 940813 | 2013-02-23 19:16 | 2013-02-24 02:33 | 437 | 11kV | 1024939.7 | 4149 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | Y | LID 134923 Dual 11kV on pole Conductor clash wire down on pole IU-33094 Excluded OMS 940825, 940823 Note: Open point moved from 4591 to 8479 in planned switching 30736 putting these customers onto feeder 80793 Jesmond - refer related record 940823 | February | 2013 | 2013Q3 | 2013 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2013-02-23 | N | 247.0329 | N | 10 | N | N | 1.1101 | 39.4971 | 748995.7022
[7 empty] | 18281 | 17297 | 940974 | 2013-02-23 20:42 | 2013-02-24 04:40 | 478 | 11kV | 209421 | 1253 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn.2400 Berowora Pnl.18 tripped / reclosed / tripped and locked out on B & C IOC, Earth Fault Tree brought down 1 phase of HV in Woodcourt Rd between AB2388 and LB2904 see 942757 942758 | February | 2013 | 2013Q3 | 2013 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2013-02-23 | Y | 167.1357 | N | 10 | N | Y | 1.1101 | 39.4971 | 153038.6899
[7 empty] | 17570 | 9567 | 940780 | 2013-02-23 23:19 | 2013-02-24 05:19 | 360 | 11kV | 398894 | 1190 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | iR2935 Somersville Pike - tripped / reclosed / tripped on Overcurrent Large tripped on mains O/S 458 Somerville Rd. Section of feeder from AB3358 to AB604 tee PT2336 see 942768 942769 942771 | February | 2013 | 2013Q3 | 2013 | ZN847:PA22 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Veg | 2013-02-23 | Y | 335.205 | N | 10 | N | Y | 1.1101 | 39.4971 | 291499.9698
[7 empty] | 18325 | 17720 | 943976 | 2013-02-23 19:03 | 2013-02-24 09:10 | 847 | 11kV | 197614 | 2110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 134917 3 fault operations WIRES DOWN POLE IS-65231 | February | 2013 | 2013Q3 | 2013 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2013-02-23 | Y | 93.6559 | N | 10 | N | Y | 1.1101 | 39.4971 | 144410.4826
[7 empty] | 16534 | 243 | 941297 | 2013-02-23 23:54 | 2013-02-24 11:45 | 711 | 11kV | 666653 | 1314 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn.15006 Dee Why Pnl.13 tripped on E/F Tree brought down OH mains see 942816 942817 942819 | February | 2013 | 2013Q3 | 2013 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Veg | 2013-02-23 | Y | 507.3463 | N | 10 | N | Y | 1.1101 | 39.4971 | 487170.3495
[7 empty] | 16568 | 426 | 943892 | 2013-02-23 18:42 | 2013-02-24 11:55 | 1033 | 11kV | 50738 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | Y | LID 134919 Earth fault, Overcurrent Tree on mains between 52685 & 27689 Excluded OMS 940757 | February | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2013-02-23 | Y | 576.5682 | N | 10 | N | Y | 1.1101 | 39.4971 | 37077.8339
[7 empty] | 17979 | 14099 | 942190 | 2013-02-24 10:00 | 2013-02-24 12:00 | 120 | 11kV | 480 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | lid 134931 Sub 787 LL Dropper lug burnt up note: LID references to 942910 which is not related to this event | February | 2013 | 2013Q3 | 2013 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2013-02-24 | N | 120 | N | 10 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 18175 | 16358 | 941185 | 2013-02-24 07:12 | 2013-02-24 12:45 | 333.4167 | 11kV | 10335.9167 | 31 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Wind Storm | N | Ex Panel 33 Pennant Hills PT2005 Westleigh Garah all HDO's Blown Cause: Suspect Transformer Failure. Supply restored Via LV Parallel at 1245 24/02/2012 TRANSFORMER REPLACED MONDAY 25TH FEB 2013 CC1: 22-"Refer to SOp" | February | 2013 | 2013Q3 | 2013 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | UG | Not Veg | 2013-02-24 | N | 333.4167 | N | 10 | N | N | 1.1101 | 39.4971 | 7553.183
[7 empty] | 17474 | 8553 | 940856 | 2013-02-23 19:21 | 2013-02-24 13:00 | 1059 | 11kV | 35016 | 50 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | Y | LID 134920 2 fault operations Overcurrent; Earth fault 11kV mains on ground between sub 54044 and sub 48869. Excluded OMS # 940856 and 945151. | February | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-02-23 | Y | 700.32 | N | 10 | N | Y | 1.1101 | 39.4971 | 25588.66
[7 empty] | 17299 | 7092 | 941617 | 2013-02-24 02:33 | 2013-02-24 14:15 | 702 | 11kV | 24291 | 74 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Wind Storm | N | Ex Zn12690 Berkeley Vale @REC47878 Pacific Palmdale 0.55 tripped on SEF Cause: OH Down Remarks: Pole leaning and cct wires down at 318 Palmdale rd, Palmdale See 945398,9,401 Exclude 941617,29 | February | 2013 | 2013Q3 | 2013 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2013-02-24 | N | 328.2568 | N | 10 | N | N | 1.1101 | 39.4971 | 17751.1463
[7 empty] | 18501 | 19902 | 940467 | 2013-02-23 13:59 | 2013-02-24 15:18 | 1518.9167 | 11kV | 119994.4167 | 79 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | Y | LID 134916 3 fault operations 3 phase Sensitive Earth Fault This area suffered extensive flooding and lots of areas could not be accessed. After patrolling as much of the feeder as absolutely possible it was tried back, but tripped and locked out. Staff are to re-attend on Saturday as soon as the flood waters subside. SEF was for the initial fault at 1359hrs. Following both a helicopter and ground patrols, trees were pulled and cut away from the feeder at several locations then returned to service. | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-02-23 | Y | 1518.9167 | N | 10 | N | Y | 1.1101 | 39.4971 | 87688.3805
[7 empty] | 18004 | 14232 | 941020 | 2013-02-23 21:05 | 2013-02-24 15:35 | 1110 | 11kV | 64380 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex ZN12630 Peats Ridge 11kV Pa1 @REC46763 Grants Keighley 0.3W tripped reclosed and locked out on OC and IOC Cause: Tree down on 11kv mains near PT12486 Wise Ferry Niah See 943963 exclude 942850 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 1110 | N | 10 | N | Y | 1.1101 | 39.4971 | 47047.0051
[7 empty] | 17245 | 6487 | 942165 | 2013-02-24 00:20 | 2013-02-24 16:50 | 990 | 11kV | 16830 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Section of feeder ex S35370 Galston Pa2 to CP2831 tee PT1691 At PT1691 Galston Swimming Pool Large Tree has fallen onto PT PoleHV and LV fuses have been withdrawn See OMS 943289 921314 942165 | February | 2013 | 2013Q3 | 2013 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2013-02-24 | N | 990 | N | 10 | N | N | 1.1101 | 39.4971 | 12298.8676
[7 empty] | 17069 | 4188 | 941288 | 2013-02-23 23:32 | 2013-02-24 17:10 | 1058 | 11kV | 237189 | 727 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | At S35370 Galston Panel 8 Tripped reclosed tripped and locked out on Relays: A phase Overcurrent, Earth Fault and EFI. Signals 11kV Trip. Cause: Large tree on mains in Johnson St Galston - Section of Feeder from AB130 to AB52 Tee PT2112 Hansen Johnson is isolated See OMS 943823 943825 943826 942005 942065 942143 942686 941315 | February | 2013 | 2013Q3 | 2013 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-02-23 | Y | 326.2572 | N | 10 | N | Y | 1.1101 | 39.4971 | 173330.7253
[7 empty] | 18135 | 15992 | 942633 | 2013-02-24 17:14 | 2013-02-24 18:50 | 96.4333 | 11kV | 5593.1333 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 134938 Feeder isolated to safely revove tree | February | 2013 | 2013Q3 | 2013 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2013-02-24 | N | 96.4333 | N | 10 | N | N | 1.1101 | 39.4971 | 4087.2969
[7 empty] | 18331 | 17748 | 941320 | 2013-02-24 00:24 | 2013-02-24 18:52 | 1108 | 11kV | 77381 | 140 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 134925 1 fault operation Earth fault HV down near LF 26159 Excluded OMS 941320, 942508 | February | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-02-24 | N | 552.7214 | N | 10 | N | N | 1.1101 | 39.4971 | 56547.7524
[7 empty] | 18035 | 14856 | 941492 | 2013-02-23 23:06 | 2013-02-24 19:08 | 1202 | 11kV | 69646 | 100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12650 West Gosford 11kv Pa1 REC44602 OUrimbah Creek Rd Trip, Reclose, Trip, Lockout Relays: O/C Trip, Lockout Remarks: Fdr unable to be patrolled past AB43611 due to flooding Tree on mains at PT12952. See earlier interruption at REC45010 Palmgrove. ABNORMAL: REC45010 Open See 944032,7,8,9,41 Exclude 941596 | February | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 696.46 | N | 10 | N | Y | 1.1101 | 39.4971 | 50895.2426
[7 empty] | 17450 | 8316 | 940949 | 2013-02-23 20:24 | 2013-02-24 19:08 | 1364 | 11kV | 23188 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12650 West Gosford 11kv Pa1 @REC45010 Palmgrove tripped on SEF trip, Lockout Remarks: Mains down at PT12537. See 944032 later interruption at REC44602 OUrimbah Creek Road See 944030 exclude 940949,52,1170,42785 | February | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-02-23 | Y | 1364 | N | 10 | N | Y | 1.1101 | 39.4971 | 16945.1065
[7 empty] | 18012 | 14468 | 941836 | 2013-02-23 22:30 | 2013-02-24 19:25 | 1255 | 11kV | 591057 | 1733 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | Y | Zn12650 West Gosford 11kc Pa13 tripped Relays: Micim Relay - Trip, Phase O/C Alarm, EFI, TIming Relay, Lockout Relay EFI:Corner Racecourse rd & Furnace Rd, S14116, S12744 Cause: UGOH Fault Short Circuit Remarks: Suspected fault between SwA@S12774 to UGOH & SwB@S18009 to UGOH. Disconnected both UGOH's and restored via S18118. See 944150,1,2,3,4,5,6 Exclude 941836,2428,5 | February | 2013 | 2013Q3 | 2013 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | Unknown | Unknown | 2013-02-23 | Y | 341.06 | N | 10 | N | Y | 1.1101 | 39.4971 | 431927.0224
[7 empty] | 18236 | 16936 | 942254 | 2013-02-24 18:20 | 2013-02-24 19:35 | 75 | 11kV | 3300 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | Section of 11kV feeder from Ab2421 to LB1187 tee PT660, PT2132, PT1485, PT2278 PT2337 was isolated to safely remove a large tree adjacent to AB298 See OMS 943862 942254 | February | 2013 | 2013Q3 | 2013 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2013-02-24 | N | 75 | N | 10 | N | N | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 17927 | 13388 | 940406 | 2013-02-23 12:16 | 2013-02-24 20:18 | 1922 | 11kV | 63259 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Section of 11kv Pa12 fdr from ZN14891 Wyong @Rec45015 Brush Creek tripped on IOC, OC, Lockout Relays:IOC, OC (1st trip) Relays:IOC, OC (@1703 2nd trip) Remarks: Tree branch on 11kv mains. Span of HV OH down 1 pole down from PT13352 Brush Creek Yarramalong 3.9 and wires down beyond AB40983 See 943868,70,1 Exclude 940357,406,1960,2591 | February | 2013 | 2013Q3 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-02-23 | Y | 1129.625 | N | 10 | N | Y | 1.1101 | 39.4971 | 46227.8114
[7 empty] | 17976 | 14026 | 940993 | 2013-02-23 20:52 | 2013-02-24 20:30 | 1418 | 11kV | 264224 | 257 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12630 Peats Ridge Pa5 @REC46803 Wise Ferry Dogtrap 0.1 tripped, reclosed and locked out on E/F Protection ABNORMAL: Section of 11kv from USL41913 to AB43335 isolated as tree on LB43336. Also report of tree on 11kv in Hoipo Rd Somersby beyond REC46803 Remarks: O/H down beyond LK41913 and before RE46803. Likeley OH wires downed on or after RE61082 trip. 1st call upstream of RE46803 21:49. Tree/branch brought down OH. See 944766 exclude 940993,4,5,9,1004,22,72,116,384,488,521,645,806,2085,2228 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 1028.1089 | N | 10 | N | Y | 1.1101 | 39.4971 | 193087.1059
[7 empty] | 17034 | 3947 | 942705 | 2013-02-24 18:27 | 2013-02-24 22:10 | 223 | 11kV | 8920 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134939 Interrigated WSOS for final time. Excluded oms OMS 942711, 942705 and 942731. | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-02-24 | N | 223 | N | 10 | N | N | 1.1101 | 39.4971 | 6518.4729
[7 empty] | 17752 | 11958 | 941026 | 2013-02-23 21:13 | 2013-02-25 00:05 | 1612 | 11kV | 325698 | 272 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | @Zn12630 Peats Ridge 11kv Pa4 fdr tripped on: Relays: SEF, EFI EFI's: Nil Signals: 11kv trip Remarks: Trees down on CCT between LB45003 and LB45014 also between AB44293 and LB41564 also trees brought down OH beyond LB47036 See 944621,2,3,4,5 Exclude 941026 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 1197.4191 | N | 10 | N | Y | 1.1101 | 39.4971 | 238010.4919
[7 empty] | 18399 | 18455 | 943952 | 2013-02-23 19:38 | 2013-02-25 03:55 | 1937 | 11kV | 235342 | 129 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12630 Peats Ridge Zone 11kV Pa1 @ REC 49506 Springs rd tripped on O/C Abnormal:AB44955 Open, AB41130 Open, REC49506 Closed Cause: Storm. Tree on HV mains See 943952,4,3 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 1824.3566 | N | 10 | N | Y | 1.1101 | 39.4971 | 171980.9922
[7 empty] | 17835 | 12592 | 943399 | 2013-02-24 12:10 | 2013-02-25 07:27 | 1157 | 11kV | 63029 | 792 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind | N | LID 134933 2 fault operations 3 phase Overcurrent 11kV UGOH JT-47125 fauly TO Sub 35842 Excluded oms 942411 | February | 2013 | 2013Q3 | 2013 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | Unknown | Unknown | 2013-02-24 | N | 79.5821 | N | 10 | N | N | 1.1101 | 39.4971 | 46059.7342
[7 empty] | 17745 | 11917 | 942933 | 2013-02-25 08:20 | 2013-02-25 09:15 | 55 | 11kV | 825 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Section of Panel 37 ex Pennant Hills Zone At S8388 Pennant Hills Toyota When DOp opened SW/B at S8388 During switching dor disconnect309823 Tx tee off fuse failed See OMS 944175 942933 | February | 2013 | 2013Q3 | 2013 | ZN965:PA37 | ZN965:PA37 | ZN00965/000037 | HORNSBY | OH | Not Veg | 2013-02-25 | N | 55 | N | 9 | N | N | 1.1101 | 39.4971 | 602.8857
[7 empty] | 18444 | 19055 | 944042 | 2013-02-23 19:38 | 2013-02-25 13:20 | 2502 | 11kV | 137340 | 55 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 134922 2 fault operations Overcurrent Crews and operators reported extensive floonding in this area and could not initially access this area. Crews also had to access the area from Wiseman's Ferry Road, this significantly added to the time taken to restore supoply. 2 spans off 11kV feel to the ground during the storm on 23 February, the mains fell near pole MN-83948 just past the Mount McQuoid RAGCB. Excluded OMS # 940851. | February | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-02-23 | Y | 2497.0909 | N | 10 | N | Y | 1.1101 | 39.4971 | 100364.0212
[7 empty] | 16809 | 2116 | 943191 | 2013-02-25 12:19 | 2013-02-25 13:43 | 84 | 11kV | 109140 | 1461 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S80 Chatswood Panel 24 Tripped on C phase O/C, EFI, E/F and EFI fault check Cause: UG cable fault - Put lid blown off OS 621 Pacific Hightway. See OMS 944240 943191 943207 943216 | February | 2013 | 2013Q3 | 2013 | ZN80:PA24 | ZN80:PA24 | ZN00080/000024 | WILLOUGHBY | UG | Not Veg | 2013-02-25 | N | 74.7023 | N | 9 | N | N | 1.1101 | 39.4971 | 79756.2929
[7 empty] | 17777 | 12160 | 944592 | 2013-02-25 14:50 | 2013-02-25 14:55 | 5 | 11kV | 6370 | 1274 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134948 Field Staff left Intelliruptor 61518 Marine Drive Open after maintenance. SI 30939 Excluded OMS # 943390 | February | 2013 | 2013Q3 | 2013 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2013-02-25 | N | 5 | N | 9 | N | N | 1.1101 | 39.4971 | 4655.0081
[7 empty] | 18338 | 17773 | 943339 | 2013-02-25 14:23 | 2013-02-25 15:14 | 51 | 11kV | 70737 | 1387 | HV | Overload | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | Zn.4990 City Central - 55 / 56 H feeder dumped by Aop due to multiple overloads on 55/56H TX's 55/56 G Out of Serivce due to Bucholhz @ S390 55/56J feeder tripped on UG fault - see 943844 | February | 2013 | 2013Q3 | 2013 | ZN4990:PA55 56GHJ | ZN4990:PA55 56GHJ | ZN04990/55 56GHJ | SYDNEY | UG | Not Veg | 2013-02-25 | N | 51 | N | 9 | N | N | 1.1101 | 39.4971 | 51692.5132
[7 empty] | 16712 | 1280 | 945474 | 2013-02-25 16:30 | 2013-02-25 16:50 | 20 | 11kV | 180 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Pa1 USL47842 to PT14400 affected (3 PT's) Tree removed by mains from 11kv fdr | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2013-02-25 | N | 20 | N | 9 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 18427 | 18894 | 943465 | 2013-02-25 16:21 | 2013-02-25 17:12 | 51 | 11kV | 65841 | 1291 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2473 North Sydney Pa25 feeder tripped Signals: Group Earth Relays: B phase OC, FC and EFI Cause: UG fault between Zn2473 Pa25 and S35330 Victoria Holt SW/A See OMS 944212 943465 | February | 2013 | 2013Q3 | 2013 | ZN2473:PA25 | ZN35400:PA73 | ZN35400/000073 | NORTH SYDNEY | UG | Not Veg | 2013-02-25 | N | 51 | N | 9 | N | N | 1.1101 | 39.4971 | 48114.6608
[7 empty] | 17839 | 12629 | 943487 | 2013-02-25 17:01 | 2013-02-25 17:44 | 43 | 11kV | 15652 | 364 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Pa1 @REC61340 George Downs Bloodtree 0.2 opened by hand for mains to remove dangerous situation (Large tree on 11kv) ABNORMAL: LB48444 open (trees on feeder) Remarks: Mains used ginker to pull off tree over & off 11kv mains See945477 exclude 943487 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-02-25 | N | 43 | N | 9 | N | N | 1.1101 | 39.4971 | 11438.0199
[7 empty] | 17478 | 8571 | 940879 | 2013-02-23 21:05 | 2013-02-25 19:10 | 2765 | 11kV | 1073825 | 747 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Zn14143 Sommersby 11kv Pa17 Relays: O/C Trip, B+C Phase O/C Trip Cause: Tree branch brought down OH Remarks: No access beyond REC45037 Reeves Somersby (Flooded) Trees & OH down beyond LK41266 Tree on mains between REC48437 Peats Ridge Cook 1.5 & IS44538 See 944186,7,8,9,91,3,4,5 Exclude 941008,15,966,2861 GIS 942267 | February | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 1437.5167 | N | 10 | N | Y | 1.1101 | 39.4971 | 784719.6375
[7 empty] | 16974 | 3383 | 942390 | 2013-02-23 20:02 | 2013-02-25 20:30 | 2908 | 11kV | 34896 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12630 Peats Ridge Zone Pa1 11kv fdr from LB48444 to PT13531 OH down Remarks: LV & 11kv Cross arm broken & twisted together See 944896 Exclude 941020 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 2908 | N | 10 | N | Y | 1.1101 | 39.4971 | 25500.9675
[7 empty] | 17030 | 3928 | 943767 | 2013-02-25 21:23 | 2013-02-25 23:45 | 142 | 11kV | 238478 | 2919 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN80 Chatswood Panel 40 Helen Huxtable 11kV feeder tripped Signals: Tx11 and Tx12 Tap Changer No Volts, Zone Earth, 11kV Trip Battery Defect Relays: 40L EF and EFI and Fault ckeck. Field EFI'sS3609 S3268 S2935 S277 Abnormal Switching: SW/A at S6968 Open, SW.B at S3602 Closed Cause: UG fault between SW/F at S277 Rosenthal Ave and SW/B at S6610 Birdwood Longeuville See OMS 944652 944655 944807 943768 943772 973767 9439770 | February | 2013 | 2013Q3 | 2013 | ZN80:PA40 | ZN80:PA40 | ZN00080/000040 | LANE COVE | UG | Not Veg | 2013-02-25 | N | 81.6985 | N | 9 | N | N | 1.1101 | 39.4971 | 174272.6885
[7 empty] | 18015 | 14550 | 943775 | 2013-02-25 21:47 | 2013-02-25 23:55 | 128.55 | 11kV | 10259.1167 | 95 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 134952 C phase DOLF : 31 Amp Fatigue Volts = 246 Amps = 100/80/110 Excluded OMS 943779 | February | 2013 | 2013Q3 | 2013 | 260:33353 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2013-02-25 | N | 107.9907 | N | 9 | N | N | 1.1101 | 39.4971 | 7497.0599
[7 empty] | 16646 | 930 | 943815 | 2013-02-26 07:39 | 2013-02-26 09:02 | 83 | 11kV | 98189 | 1183 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | Section of Panel 31 Ryedale Sixth Cp46117 Balaclava Vimera Tripped and locked ouut Cause: Bird on UGOH to S35129 See OMS 944321 943815 | February | 2013 | 2013Q3 | 2013 | ZN4545:PA31 | ZN4545:PA31 | ZN04545/000031 | PARRAMATTA | OH | Not Veg | 2013-02-26 | N | 83 | N | 5 | N | N | 1.1101 | 39.4971 | 71753.6251
[7 empty] | 17357 | 7521 | 943903 | 2013-02-26 09:45 | 2013-02-26 12:15 | 150 | 11kV | 150 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 134958 Single phase LLC off LL loop | February | 2013 | 2013Q3 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2013-02-26 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 17151 | 5041 | 944006 | 2013-02-26 10:30 | 2013-02-26 12:20 | 110 | 11kV | 12100 | 110 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn12630 section of Pa2 fdr from LB43711 to rest of fdr interrupted for safety reasons Tree in 11kv near PT18542 See 945485 exclude 944006,10 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA2 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2013-02-26 | N | 110 | N | 5 | N | N | 1.1101 | 39.4971 | 8842.3231
[7 empty] | 17533 | 9018 | 944222 | 2013-02-26 14:32 | 2013-02-26 15:03 | 31 | 11kV | 14534 | 488 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S.15013 Terrey Hills, Panel 10 Fdr CB tripped and reclosed on C phase OC, Reclose timer and lockout relay, 11kV trip.Opened by A.Op as a bushfire started under AB.26212 due to burnt bond | February | 2013 | 2013Q3 | 2013 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-02-26 | N | 29.7828 | N | 5 | N | N | 1.1101 | 39.4971 | 10621.0185
[7 empty] | 17094 | 4368 | 943975 | 2013-02-26 10:00 | 2013-02-26 16:00 | 360 | 11kV | 4320 | 12 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Pa1 fdr @LB48444 interrupted for safety reasons. mains to retension HV See 945488 exclude 943975 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2013-02-26 | N | 360 | N | 5 | N | N | 1.1101 | 39.4971 | 3156.9286
[7 empty] | 17864 | 12834 | 940887 | 2013-02-23 19:50 | 2013-02-26 17:35 | 4185 | 11kV | 680713.1833 | 420 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn12630 Peats Ridge Pa3 fdr tripped on: SEF, EFI, 11kv trip ABNORMAL: AB41553 to AB44077 isolated & earthed + AP's whilst repairs being arried out Cause: Multiple causes at different times. Remarks: 11kV OH btw AB43765-S12354; Trees brought down OH btw LB43636-LB46215;Trees brought down OH btw LB42326-LK43090. PT12154 still out see 645374. For earlier interruption see 945150. See 945334,6,7,8,9,41,9 Exclude 940887 | February | 2013 | 2013Q3 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-02-23 | Y | 1620.7457 | N | 10 | N | Y | 1.1101 | 39.4971 | 497445.1167
[7 empty] | 17018 | 3801 | 945096 | 2013-02-27 10:30 | 2013-02-27 12:00 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 134966 A phase DOLF : 10 Amp. | February | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-02-27 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 18492 | 19836 | 944786 | 2013-02-27 12:54 | 2013-02-27 13:45 | 51 | 11kV | 12546 | 246 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | 11kv bond burnt off AB 2496 Panel 31L "Anzac Dominion" feeder ex Sub1285 Greenacre Park Remarks: Air break switch - details below. Bond burnt off @ AB2496 Related jobs: #944786, 945197 | February | 2013 | 2013Q3 | 2013 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-02-27 | N | 51 | N | 3 | N | N | 1.1101 | 39.4971 | 9168.2468
[7 empty] | 17623 | 10340 | 945015 | 2013-02-27 18:13 | 2013-02-27 20:25 | 132 | 11kV | 340194 | 2611 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 1285 Greenacre Park Panel No.27 Opened, Reclosed, Opened & Locked Out. 27 R on SEL with EFI & Panel 27 L on B phase Timed OC & Earth Fault with Lockout Relay & EFI. EFIs found operated @ Subs 4861, 36235, 47526, 7730 & 7806. Abnormal: SW B @ S5605 Waterloo Como No.3 Closed, AB 2496 Defective & open. Remarks: UG cable fault from Sub1285 Greenacre Park to Sub 4861 Stiller Place to Sub 6424 Naughton Roberts to S7025 Wentworth Mayvic. Related jobs: #945266, 945262, 945021, 945035, 945015, 945018 | February | 2013 | 2013Q3 | 2013 | ZN1285:PA27 | ZN1285:PA27 | ZN01285/000027 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-02-27 | N | 130.2926 | N | 3 | N | N | 1.1101 | 39.4971 | 248603.7412
[7 empty] | 16533 | 232 | 945067 | 2013-02-28 00:41 | 2013-02-28 01:45 | 64 | 11kV | 2048 | 32 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Possum found at PT.1402 | February | 2013 | 2013Q3 | 2013 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Not Veg | 2013-02-28 | N | 64 | N | 9 | N | N | 1.1101 | 39.4971 | 1496.618
[7 empty] | 18043 | 15069 | 945251 | 2013-02-28 11:11 | 2013-02-28 12:38 | 87 | 11kV | 5319 | 69 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15013 Terrey Hills, Panel 2 Fdr CB tripped on A phase IOC and timed OC, earth fault, frame leakage, efi , lockout and reclose time delay relays. | February | 2013 | 2013Q3 | 2013 | ZN15013:PA2 | ZN15013:PA2 | ZN15013/000002 | NORTHERN BEACHES | UG | Not Veg | 2013-02-28 | N | 77.087 | N | 9 | N | N | 1.1101 | 39.4971 | 3886.9683
[7 empty] | 17258 | 6612 | 945502 | 2013-02-28 16:47 | 2013-02-28 17:50 | 63 | 11kV | 3336 | 69 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15013 Terrey Hills, Panel 2 Fdr CB tripped on C phase timed earth fault, efi, frame leakage, reclose timer and lockout relays. A HV UG/OH "K2" centre phase blown below stress cone. | February | 2013 | 2013Q3 | 2013 | ZN15013:PA2 | ZN15013:PA2 | ZN15013/000002 | NORTHERN BEACHES | UG | Not Veg | 2013-02-28 | N | 48.3478 | N | 9 | N | N | 1.1101 | 39.4971 | 2437.8504
[7 empty] | 18094 | 15726 | 945500 | 2013-02-28 16:38 | 2013-02-28 18:08 | 90 | 11kV | 630 | 7 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 134981 3 phase isolation section isolated to carry out repairs at pole AG-80475 Excluded oms 945500 | February | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-02-28 | N | 90 | N | 9 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 16941 | 3181 | 945559 | 2013-02-28 18:40 | 2013-02-28 19:29 | 49 | 11kV | 40523 | 827 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN14144 Wamberal Pa4 11kv CB tripped on Relays: OC, B+C phase Singals: 11kv trip EFI: nil Remarks: Tree branch on 11kv OH mains See 946126 exclude 945559 | February | 2013 | 2013Q3 | 2013 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2013-02-28 | N | 49 | N | 9 | N | N | 1.1101 | 39.4971 | 29613.0132
[7 empty] | 17676 | 11145 | 945605 | 2013-02-28 21:52 | 2013-02-28 23:30 | 98 | 11kV | 1470 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | PT12500 Beaufort Serpentine Roadside HDO fuse 20A fuse blown Remarks: DOp removed a tree branch off PT12500 See 946130 exclude 945606 | February | 2013 | 2013Q3 | 2013 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2013-02-28 | N | 98 | N | 9 | N | N | 1.1101 | 39.4971 | 1074.2326
[7 empty] | 17220 | 6181 | 945622 | 2013-02-28 23:58 | 2013-03-01 01:12 | 74 | 11kV | 67892 | 1006 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Rain Light | N | At Sub 1850 Bass Hill panel 3 "Rex Rd" tripped on: Relays: A phase overcurrent & A phase IOC Signals: 11KV trip Field EFI's: Nil Remarks: Dop removed dead bat from mains outside 4 Athel St. Note Rec 49253 Rex McClean did not operate. At LB49711 it saw the fault current pass through it. TPE to investigate. Related jobs: #945622, 945623, 946990, 946989 | February | 2013 | 2013Q3 | 2013 | ZN1850:PA3 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-02-28 | N | 67.4871 | N | 9 | N | N | 1.1101 | 39.4971 | 49613.4711
[7 empty] | 16930 | 3102 | 945624 | 2013-03-01 00:15 | 2013-03-01 01:38 | 83 | 11kV | 41915 | 505 | HV | 3rd Party Action | 3rd Party Impact | O/H Link | Unplanned | Rain Light | N | Ex Zn14143 Somersby Pa17 @AB43233 11kv was found open and vandalised by phantom operator See 946134 exclude 945624 | March | 2013 | 2013Q3 | 2013 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-03-01 | N | 83 | N | 20 | Y | Y | 1.1101 | 39.4971 | 30630.2457
[7 empty] | 16792 | 1990 | 945578 | 2013-02-28 19:56 | 2013-03-01 01:39 | 343 | 11kV | 168821 | 1394 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah Nth., Panel 17 Fdr CB tripped on A and C phase OC and earth fault. | February | 2013 | 2013Q3 | 2013 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2013-02-28 | N | 121.1055 | N | 9 | N | N | 1.1101 | 39.4971 | 123369.4074
[7 empty] | 17395 | 7917 | 945584 | 2013-02-28 20:07 | 2013-03-01 02:00 | 353 | 11kV | 2471 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 134985 A & B phase DOLF : 20 Amp Excluded OMS 945584 | February | 2013 | 2013Q3 | 2013 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Veg | 2013-02-28 | N | 353 | N | 9 | N | N | 1.1101 | 39.4971 | 1805.7339
[7 empty] | 17064 | 4154 | 945644 | 2013-03-01 04:07 | 2013-03-01 07:20 | 193 | 11kV | 163228 | 846 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn14891 Wyong Pa21 fdr tripped, reclosed, tripped and locked out on: Relays: A&B phases overcurrent, fault check, reclose, reclose timing relay, lockout relay & EFI Relays on TX@ protection panel: 11kv E/F check, 11kV frame leakage prohibition relay Signals: 11kv trip Cause: OH earth wire down. Corner Virginia and Warnervale rds Warnervale See 947222,4 Exclude 945644 | March | 2013 | 2013Q3 | 2013 | ZN14891:PA21 | ZN14891:PA17 | ZN14891/000017 | CENTRAL COAST | OH | Not Veg | 2013-03-01 | N | 192.9409 | N | 20 | Y | Y | 1.1101 | 39.4971 | 119282.208
[7 empty] | 17559 | 9414 | 945674 | 2013-03-01 06:48 | 2013-03-01 10:10 | 202 | 11kV | 85452 | 828 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 134987 2 fault operations Single phase Sensitive Earth Fault Tree fallen on to mains at pole FU-12410 | March | 2013 | 2013Q3 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2013-03-01 | N | 103.2029 | N | 20 | Y | Y | 1.1101 | 39.4971 | 62445.8012
[7 empty] | 16820 | 2160 | 945789 | 2013-03-01 09:23 | 2013-03-01 11:30 | 127 | 11kV | 381 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | LID 134989 Single phase DOLF : 10 Amp Fuse fatigue Excluded OMS 945789 | March | 2013 | 2013Q3 | 2013 | 806:74080 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2013-03-01 | N | 127 | N | 20 | Y | Y | 1.1101 | 39.4971 | 278.4236
[7 empty] | 17516 | 8939 | 945736 | 2013-03-01 08:30 | 2013-03-01 11:50 | 200 | 11kV | 49680 | 681 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | LID 134990 2 fault operations Overcurrent Tree branch across HV & LV OHM adjacent pole NR-60253. Cust. installations inspected off sub 11295. Excluded OMS 945739 | March | 2013 | 2013Q3 | 2013 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2013-03-01 | N | 72.9515 | N | 20 | Y | Y | 1.1101 | 39.4971 | 36304.6787
[7 empty] | 17449 | 8311 | 945913 | 2013-03-01 11:28 | 2013-03-01 13:00 | 92.4167 | 11kV | 15156.3333 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Panel 4 GalstonR Recloser CP428 Bayfield Rd tripped on A and B O/C Timing and lockout Cause: Tree branch on OH mains on tee of section of 11kV feeder to PT1890 Vision Valley Arcadia. | March | 2013 | 2013Q3 | 2013 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-03-01 | N | 92.4167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 11075.8014
[7 empty] | 17708 | 11639 | 945990 | 2013-03-01 13:07 | 2013-03-01 15:22 | 135 | 11kV | 69001 | 533 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Light | N | LID 134992 FDR RESTORED AND TRIPPED AGAIN AFTER 16 MINS TREE REMOVED FROM MAINS PAST POLE FU-92683 SEF TIMER AT CESSNOCK ZONE NEEDS TO BE CHECKED AS NO RECLOSERS TRIPPED ON SEF ALONG FDR Excluded oms 945990 | March | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2013-03-01 | N | 129.4578 | N | 20 | Y | Y | 1.1101 | 39.4971 | 50423.8956
[7 empty] | 17062 | 4151 | 945842 | 2013-03-01 13:45 | 2013-03-01 16:40 | 175 | 11kV | 5075 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12650 West Gosford Pa1 Section btw LB43806 to AB44473 interrupted for safety reasons. Tree brought down wires at PT12211 Alan Niagara See 947310 exclude 945842,75,7,916,74 | March | 2013 | 2013Q3 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-03-01 | N | 175 | N | 20 | Y | Y | 1.1101 | 39.4971 | 3708.6603
[7 empty] | 18264 | 17150 | 946173 | 2013-03-01 16:42 | 2013-03-01 16:49 | 7.2333 | 11kV | 2632.9333 | 364 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | George down drive west of blood tree rd kulnura | March | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-03-01 | N | 7.2333 | N | 20 | Y | Y | 1.1101 | 39.4971 | 1924.07
[7 empty] | 18484 | 19645 | 945641 | 2013-03-01 03:29 | 2013-03-01 17:19 | 830 | 11kV | 16224 | 95 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | @Zn12630 Peats Ridge Section of pa1 "Grants rd" tripped and locked out at reclser 61364 Brieses Peats 0.4 on O/C Cause: tree/branch brough down OH at reservoir rd near Mooney Dam See 947367 exclude 945641,861 | March | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2013-03-01 | N | 170.7789 | N | 20 | Y | Y | 1.1101 | 39.4971 | 11856.0207
[7 empty] | 17142 | 4811 | 945971 | 2013-03-01 12:35 | 2013-03-01 17:27 | 292 | 11kV | 12264 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Based on customer calls suspect minor part of distributor outage on the CNR of Pailing and Cavendish See OMS 954971 958565 | March | 2013 | 2013Q3 | 2013 | ZN965:PA47 | ZN965:PA47 | ZN00965/000047 | HORNSBY | OH | Veg | 2013-03-01 | N | 292 | N | 20 | Y | Y | 1.1101 | 39.4971 | 8962.1695
[7 empty] | 18479 | 19563 | 945915 | 2013-03-01 11:25 | 2013-03-01 17:57 | 392 | 11kV | 90104 | 772 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn12570 Avoca Pa41 tripped and locked out on C Phase IOC, EFI EFI: S49887 S18034 S18033 Cause: UG Fault suspect See 947293 ,6,7,8 exclude 945915 | March | 2013 | 2013Q3 | 2013 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | UG | Not Veg | 2013-03-01 | N | 116.715 | N | 20 | Y | Y | 1.1101 | 39.4971 | 65845.3456
[7 empty] | 17496 | 8796 | 947316 | 2013-03-01 15:29 | 2013-03-01 18:48 | 199 | 11kV | 31829 | 533 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Light | N | LID 134992 FDR RESTORED AND TRIPPED AGAIN AFTER 16 MINS TREE REMOVED FROM MAINS PAST POLE FU-92683 SEF TIMER AT CESSNOCK ZONE NEEDS TO BE CHECKED AS NO RECLOSERS TRIPPED ON SEF ALONG FDR Excluded oms 945990 | March | 2013 | 2013Q3 | 2013 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2013-03-01 | N | 59.7167 | N | 20 | Y | Y | 1.1101 | 39.4971 | 23259.6944
[7 empty] | 17677 | 11149 | 946236 | 2013-03-01 18:20 | 2013-03-01 19:31 | 71 | 11kV | 54741 | 771 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn12570 Avoca 11kv pa29 @REC44982 Bensville Tripped, reclosed tripped and locked out on O/C See 947400 exclude 946236,9,43 | March | 2013 | 2013Q3 | 2013 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2013-03-01 | N | 71 | N | 20 | Y | Y | 1.1101 | 39.4971 | 40003.1082
[7 empty] | 17996 | 14180 | 946163 | 2013-03-01 16:32 | 2013-03-01 19:55 | 202.8833 | 11kV | 3854.7833 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 134997 A & B phase DOLF : 20 Amp | March | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2013-03-01 | N | 202.8833 | N | 20 | Y | Y | 1.1101 | 39.4971 | 2816.962
[7 empty] | 17103 | 4453 | 946200 | 2013-03-01 17:22 | 2013-03-01 22:55 | 333 | 11kV | 35941 | 259 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | At ZN847 Hornsby Panel 47 11kV feeder tripped Signals: 11kV trip, zone earth, Group Earth, Zone Earth Relays: C phase EF, Timer , EFI, FC and Lockout See OMS 949770/771/773/772 246200/206/271/288 | March | 2013 | 2013Q3 | 2013 | ZN847:PA47 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Not Veg | 2013-03-01 | N | 138.7683 | N | 20 | Y | Y | 1.1101 | 39.4971 | 26264.6227
[7 empty] | 18445 | 19057 | 946331 | 2013-03-02 00:33 | 2013-03-02 02:00 | 87 | 11kV | 43929 | 815 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15002 Narrabeen, Panel 8 Fdr CB tripped on A and C phase OC, timing and frame leakage, 11kV trip, zone earth. field efi's down from Panel 8 to S.16913. Possum in vicinity of AB.20259 | March | 2013 | 2013Q3 | 2013 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2013-03-02 | N | 53.9006 | N | 11 | N | N | 1.1101 | 39.4971 | 32102.0175
[7 empty] | 17110 | 4494 | 946327 | 2013-03-01 23:54 | 2013-03-02 03:10 | 196 | 11kV | 14896 | 76 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | LID 135003 A phase DOLF : 50 Amp Defective DOLF carrier - not holding in. | March | 2013 | 2013Q3 | 2013 | 222:2018 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2013-03-01 | N | 196 | N | 20 | Y | Y | 1.1101 | 39.4971 | 10885.5574
[7 empty] | 18491 | 19831 | 946341 | 2013-03-02 03:39 | 2013-03-02 08:15 | 276 | 11kV | 183086 | 1043 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12600 Lisarow 11kv Pa13 fdr tripped Aph Overcurrent and timed. Signals: 11kv trip and efi EFI: Nil ABNORMAL: AB40010 closed and AB40011 open Remarks: 11kv UGOH fault short circuit. fault from UGOH to S14776 Old Farm Shirley See 947579,82,3,6 Exclude 946341,3 | March | 2013 | 2013Q3 | 2013 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | Unknown | Unknown | 2013-03-02 | N | 175.5379 | N | 11 | N | N | 1.1101 | 39.4971 | 133793.8487
[7 empty] | 18556 | 20386 | 946383 | 2013-03-02 08:07 | 2013-03-02 10:56 | 169 | 11kV | 230741 | 1526 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 135009 Isolated to remove tree on OHM Excluded OMS 946385, 945383, 945393 | March | 2013 | 2013Q3 | 2013 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Veg | 2013-03-02 | N | 151.2064 | N | 11 | N | N | 1.1101 | 39.4971 | 168618.7171
[7 empty] | 17028 | 3896 | 946345 | 2013-03-02 04:29 | 2013-03-02 12:40 | 491 | 11kV | 12766 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | N | LID 135007 B phase DOLF : 16 Amp Readings as left 238V. No cause found | March | 2013 | 2013Q3 | 2013 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | UG | Not Veg | 2013-03-02 | N | 491 | N | 11 | N | N | 1.1101 | 39.4971 | 9329.0163
[7 empty] | 17221 | 6211 | 946328 | 2013-03-01 23:53 | 2013-03-02 13:05 | 792 | 11kV | 41557 | 113 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | Rain Heavy | N | LID 135002 5 fault operations 3 phase Overcurrent First fault -- Broken tapping near 11kV Links 1521. OHM low over ohn Renshaw Dr Second fault-- Tree on 11kV mains near ABS 46064. Excluded OMS 946328 | March | 2013 | 2013Q3 | 2013 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2013-03-01 | N | 367.7611 | N | 20 | Y | Y | 1.1101 | 39.4971 | 30368.6299
[7 empty] | 17534 | 9025 | 947112 | 2013-03-02 08:38 | 2013-03-02 13:55 | 317 | 11kV | 91871 | 1520 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | LID 135011/01 Opened by SO Tree brought down conductor near sub 10985 | March | 2013 | 2013Q3 | 2013 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2013-03-02 | N | 60.4414 | N | 11 | N | N | 1.1101 | 39.4971 | 67136.6171
[7 empty] | 17386 | 7832 | 946507 | 2013-03-02 11:59 | 2013-03-02 14:00 | 121 | 11kV | 19844 | 164 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 135101 Transformer failure Fire.. OMS No's, 946507, 946512.,946514, 946520, 946527 | March | 2013 | 2013Q3 | 2013 | 256:80647 | 256:80647 | ZN00256/080647 | NEWCASTLE | UG | Not Veg | 2013-03-02 | N | 121 | N | 11 | N | N | 1.1101 | 39.4971 | 14501.4099
[7 empty] | 17174 | 5342 | 946310 | 2013-03-01 21:33 | 2013-03-02 15:50 | 1097 | 11kV | 104399 | 722 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S.3154 St Ives, Panel 22 Fdr CB tripped on A&B phase OC, timimng and lockout relays, zone eartyh, #2 Tx group earth, 11kV trip. Field efi's down at S.7962 and S.7772 | March | 2013 | 2013Q3 | 2013 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Not Veg | 2013-03-01 | N | 144.597 | N | 20 | Y | Y | 1.1101 | 39.4971 | 76291.71
[7 empty] | 18079 | 15582 | 947661 | 2013-03-02 16:25 | 2013-03-02 16:42 | 17 | 11kV | 51 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong 11KV Pa12 Section of 11kv feeder against 11kv CCT beyond LK44875. DOp interupted for safety. Linseman have removed tree See 947661 exclude 946521 | March | 2013 | 2013Q3 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-03-02 | N | 17 | N | 11 | N | N | 1.1101 | 39.4971 | 37.2693
[7 empty] | 17705 | 11601 | 946602 | 2013-03-01 20:54 | 2013-03-02 16:50 | 1196 | 11kV | 7595 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 135001 3 phase DOLF : 16 Amp section isolated to repair mains replaced 3 x fuses | March | 2013 | 2013Q3 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2013-03-01 | N | 75.95 | N | 20 | Y | Y | 1.1101 | 39.4971 | 5550.202
[7 empty] | 17900 | 13133 | 946550 | 2013-03-02 13:56 | 2013-03-02 16:52 | 176 | 11kV | 52636 | 475 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | LID 135010 2 fault operations 3 phase Sensitive Earth fault cable fault from sw 74121 to 11 kv links 74664 section isolated tap to be issued 3.3.13 Excluded OMS 946550 | March | 2013 | 2013Q3 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2013-03-02 | N | 110.8126 | N | 11 | N | N | 1.1101 | 39.4971 | 38464.8363
[7 empty] | 18553 | 20365 | 947551 | 2013-03-02 18:56 | 2013-03-02 20:53 | 117 | 11kV | 34418 | 487 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID 135015 2 faiult operation A & C phase Earth fault tree removed from mains at pole FQ-54739 Excluded oms 946653 | March | 2013 | 2013Q3 | 2013 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2013-03-02 | N | 70.6735 | N | 11 | N | N | 1.1101 | 39.4971 | 25151.6592
[7 empty] | 17973 | 13944 | 121 | 2013-03-03 | 2013-03-03 04:42 | 282 | 11kV | 9024 | 32 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting Extract update(s) | March | 2013 | 2013Q3 | 2013 |  |  |  |  | Unknown | Unknown | 2013-03-03 | N | 282 | N | 8 | N | N | 1.1101 | 39.4971 | 6594.473
[7 empty] | 16718 | 1316 | 946697 | 2013-03-03 04:54 | 2013-03-03 07:08 | 134 | 11kV | 78424 | 641 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 7 - C phase IOC, EFI. Suspected UG fault in section of 11kV from S 9130 SW/B to S 9125 SW/B to S 9459 SW/A. | March | 2013 | 2013Q3 | 2013 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | UG | Not Veg | 2013-03-03 | N | 122.3463 | N | 8 | N | N | 1.1101 | 39.4971 | 57309.9461
[7 empty] | 17243 | 6443 | 946696 | 2013-03-03 04:34 | 2013-03-03 07:24 | 170 | 11kV | 77521 | 562 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | Ex ZN12620 Noraville 11kv Pa11 @REC45053 Norah Head tripped, reclosed, tripped and locked out on: Relays: IOC and Earth Fault Cause: UGOH fault short circuit. UGOH to S11752 Kendall Kiora failed See 947235,6 Exclude 946695 | March | 2013 | 2013Q3 | 2013 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | Unknown | Unknown | 2013-03-03 | N | 137.9377 | N | 8 | N | N | 1.1101 | 39.4971 | 56650.0603
[7 empty] | 17267 | 6764 | 947237 | 2013-03-03 11:43 | 2013-03-03 15:00 | 197 | 11kV | 197 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135021 1 fault operation Earth fault John Hunter Hospital -- A phase Diff trip, A phase Diff receive, TSC!, TSC2, Latched 1. New Lambton sub -- A phase LED 9, 87L, E/F. | March | 2013 | 2013Q3 | 2013 |  |  |  | NEWCASTLE | OH | Veg | 2013-03-03 | N | 197 | N | 8 | N | N | 1.1101 | 39.4971 | 143.9618
[7 empty] | 18342 | 17814 | 946807 | 2013-03-03 12:08 | 2013-03-03 16:00 | 232 | 11kV | 62027 | 1824 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12610 Long Jetty Pa10 opened on Earth Fault reclose Lockout & EFI EFI's: S18672 S18224 S18723 *Wamberal* Cause: UGOH fault Open Circuit Remarks: 11kv UGOH fault form USL 44641 to SwB S14803 Bellevue Tumbi High tee PT12879 Bellevue Tanderra See 947672,4,5,6 Exclude 946807 | March | 2013 | 2013Q3 | 2013 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | Unknown | Unknown | 2013-03-03 | N | 34.006 | N | 8 | N | N | 1.1101 | 39.4971 | 45327.5021
[7 empty] | 16581 | 539 | 946904 | 2013-03-03 19:44 | 2013-03-03 20:35 | 51 | 11kV | 77080 | 1828 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2602 Clovelly Pnl.4 tripped on A phase O/C, Earth Fault UG cable fault from S291 Marcel Ave to S300 Flood St to S3573 Greville Fewings to S3924 Dans Ave S2210 in LV // see 949907 949908 949909 949911 | March | 2013 | 2013Q3 | 2013 | ZN2602:PA4 | ZN2602:PA31 | ZN02602/000031 | RANDWICK | UG | Not Veg | 2013-03-03 | N | 42.1663 | N | 8 | N | N | 1.1101 | 39.4971 | 56327.7905
[7 empty] | 16592 | 576 | 946938 | 2013-03-03 23:51 | 2013-03-04 00:45 | 54 | 11kV | 108 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135025 Single phase DOLF : 3 Amp | March | 2013 | 2013Q3 | 2013 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-03-03 | N | 54 | N | 8 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 16650 | 942 | 947719 | 2013-03-04 00:26 | 2013-03-04 06:30 | 364 | 11kV | 8936 | 47 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 135027 3 fault operation 3 phase Overcurrent tree on fdr beyond 74538 Excluded OMS 946940 & 946951 | March | 2013 | 2013Q3 | 2013 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2013-03-04 | N | 190.1277 | N | 7 | N | N | 1.1101 | 39.4971 | 6530.1652
[7 empty] | 18374 | 18112 | 946945 | 2013-03-04 02:45 | 2013-03-04 12:45 | 600 | 11kV | 22200 | 37 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | Rain Heavy | N | LID 135026 2 fault operations 3 phase Overcurrent pole fire at af-50035. Replaced Pole. Excluded OMS 946945 | March | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-03-04 | N | 600 | N | 7 | N | N | 1.1101 | 39.4971 | 16223.1052
[7 empty] | 17379 | 7739 | 947190 | 2013-03-04 11:59 | 2013-03-04 14:50 | 171 | 11kV | 342 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Wind | N | LID 135033 C phase DOLF : 10 Amp Blown LAs replaced. Dead bird found at sub Excluded OMS No. 947190 | March | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-03-04 | N | 171 | N | 7 | N | N | 1.1101 | 39.4971 | 249.9235
[7 empty] | 16652 | 951 | 947303 | 2013-03-04 13:56 | 2013-03-04 15:19 | 83 | 11kV | 147265 | 1955 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman, Panel 21 Fdr CB tripped on timed earth fault, efi, fault check relay. Field efi's down at S.2989, S.380, S.8498 and S.48439 | March | 2013 | 2013Q3 | 2013 | ZN180:PA21 | ZN180:PA21 | ZN00180/000021 | MOSMAN | UG | Not Veg | 2013-03-04 | N | 75.3274 | N | 7 | N | N | 1.1101 | 39.4971 | 107616.9184
[7 empty] | 17098 | 4390 | 947329 | 2013-03-04 14:22 | 2013-03-04 16:52 | 150 | 11kV | 14100 | 94 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14144 Wamberal 11kv Pa10 fdr tripped REC44607 Matchem North was opened by AOp Cause: Interrupted for safety reasons. Remarks: Region deemed urgent re-tension works on vertical CCT as per Gregory Sturgess DOp isolated from REC44607 Matchem North to LK40248to LK41490 tee PT14895 Matchem Elaine 0.1 tee PT48782 Matchem Elaine See 947774 exclude 947329 | March | 2013 | 2013Q3 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2013-03-04 | N | 150 | N | 7 | N | N | 1.1101 | 39.4971 | 10303.8641
[7 empty] | 17049 | 4028 | 946891 | 2013-03-03 18:41 | 2013-03-04 17:10 | 1349 | 11kV | 66368 | 529 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex ZN12630 Peats Ridge Pa2 11kv feeder @ REC45189 Cooks Peats Ridge 0.5 tripped, reclosed & locked out on; ABC - OC trip Cause: OH Down Remarks: 11kv CCT down between AB45004 and LK43581 See 947697,701 Exclude 946891,2 | March | 2013 | 2013Q3 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2013-03-03 | N | 125.4594 | N | 8 | N | N | 1.1101 | 39.4971 | 48499.7769
[7 empty] | 18200 | 16610 | 947443 | 2013-03-04 17:18 | 2013-03-04 18:35 | 76.9333 | 11kV | 33773.7333 | 439 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12570 Avoca 11kv Pa24 fdr LK42014 roadside bonds line + load burnt off Bond burnt off at LK42014 roadside line+load. LK42014 opened CC1: 22-"Refer to SOp" | March | 2013 | 2013Q3 | 2013 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2013-03-04 | N | 76.9333 | N | 7 | N | N | 1.1101 | 39.4971 | 24680.8482
[7 empty] | 17363 | 7579 | 947437 | 2013-03-04 17:08 | 2013-03-04 19:42 | 154 | 11kV | 122873 | 1716 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn14892 Charmhaven Pa19 tripped on: Relays: SEL and Prohibition relay Signals: 11kv trip Cause: OH down From Zone 14892 Charmhaven section of panel 19 11kv overhead down between 11kv USL 41004 and 11kv USL 41253 tee PT18858 Stone Windbourne and S14336 Wallarah Beryl. Lineworkers on site to repair overhead. Network restored to normal See 948050,2,3,4 Exclude 947437,9,40,5,77,89,92,3 | March | 2013 | 2013Q3 | 2013 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2013-03-04 | N | 71.6043 | N | 7 | N | N | 1.1101 | 39.4971 | 89791.9643
[7 empty] | 17226 | 6244 | 947849 | 2013-03-05 01:32 | 2013-03-05 06:54 | 322 | 11kV | 25482 | 371 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 135035 Emergency isolation to replace Trans after holding bracket broke and trans fell on to LV x-arm. | March | 2013 | 2013Q3 | 2013 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | UG | Not Veg | 2013-03-05 | N | 68.6846 | N | 3 | N | N | 1.1101 | 39.4971 | 18621.494
[7 empty] | 16675 | 1096 | 947884 | 2013-03-05 02:27 | 2013-03-05 10:50 | 503 | 11kV | 26318 | 149 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135036 2 fault operations Overcurrent, Earth fault OHM down to sub 51559 Excluded OMS 947511, 947514 | March | 2013 | 2013Q3 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2013-03-05 | N | 176.6309 | N | 3 | N | N | 1.1101 | 39.4971 | 19232.4182
[7 empty] | 17636 | 10646 | 946619 | 2013-03-02 16:53 | 2013-03-05 14:44 | 4191 | 11kV | 52755 | 853 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 135012 2 fault operations A phase Overcurrent; Earth fault UGOH failed at pole SW-87013 Excluded OMS 946619, 946623, 946641 | March | 2013 | 2013Q3 | 2013 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | Unknown | Unknown | 2013-03-02 | N | 61.8464 | N | 11 | N | N | 1.1101 | 39.4971 | 38551.798
[7 empty] | 17431 | 8176 | 947993 | 2013-03-05 18:44 | 2013-03-06 10:40 | 956.4667 | 11kV | 28694 | 30 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 135044 2 fault operations Single phase Earth fault tree brought down ohm near sub 54050. | March | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-03-05 | N | 956.4667 | N | 3 | N | N | 1.1101 | 39.4971 | 20968.7289
[7 empty] | 18182 | 16438 | 948077 | 2013-03-06 09:06 | 2013-03-06 11:00 | 114 | 11kV | 798 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135051 B phase DOLF : 10 Amp Excluded OMS 948077 | March | 2013 | 2013Q3 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-03-06 | N | 114 | N | 4 | N | N | 1.1101 | 39.4971 | 583.1549
[7 empty] | 18009 | 14314 | 948263 | 2013-03-06 14:09 | 2013-03-06 16:55 | 166 | 11kV | 2158 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 135055 A phase DOLF : 31 Amp LV OHM near flood waters. LVF OK. Excluded OMS No. 948263 | March | 2013 | 2013Q3 | 2013 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | UG | Not Veg | 2013-03-06 | N | 166 | N | 4 | N | N | 1.1101 | 39.4971 | 1577.0027
[7 empty] | 17735 | 11846 | 948309 | 2013-03-06 15:26 | 2013-03-06 17:52 | 146 | 11kV | 139576 | 956 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15005 Belrose, Panel 6 Fdr CB tripped and reclosed frame leakage, earth fault, OC, efi and timing relay. Recloser 24831 tripped aand locked out on earth fault. PANEL PROTECTION DOES NOT GRADE WITH RECLOSER. UG cable fault between USL.24260 and S.16225 | March | 2013 | 2013Q3 | 2013 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | UG | Not Veg | 2013-03-06 | N | 146 | N | 4 | N | N | 1.1101 | 39.4971 | 101998.024
[7 empty] | 17547 | 9147 | 948415 | 2013-03-06 23:25 | 2013-03-07 06:00 | 394.6333 | 11kV | 3946.3333 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135056 A phase DOLF : 31 Amp full daylight patrol required | March | 2013 | 2013Q3 | 2013 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2013-03-06 | N | 394.6333 | N | 4 | N | N | 1.1101 | 39.4971 | 2883.864
[7 empty] | 17789 | 12345 | 946485 | 2013-03-02 11:09 | 2013-03-07 15:45 | 7476 | 11kV | 90557 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 135006 3 fault operations B phase Sensitive Earth Fault Earth fault; Overcurrent Original Fault was OC & EF. SEF when re-energised. Excluded OMS 946485 | March | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-03-02 | N | 1484.541 | N | 11 | N | N | 1.1101 | 39.4971 | 66176.3846
[7 empty] | 16912 | 3008 | 949544 | 2013-03-07 15:03 | 2013-03-07 16:04 | 61 | 11kV | 3904 | 64 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135064 47688 opened by operator for emergency repair to line side connection to Line DOLF 40478. | March | 2013 | 2013Q3 | 2013 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2013-03-07 | N | 61 | N | 4 | N | N | 1.1101 | 39.4971 | 2852.9281
[7 empty] | 18450 | 19117 | 949624 | 2013-03-07 15:29 | 2013-03-07 16:29 | 60 | 11kV | 7885 | 143 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 135065 Feeder interrupted to repair ABS 539 (B phase insulators broken) and replace ABS 7423 (ABS on fire, C phase burnt up). Excluded OMS 948795 | March | 2013 | 2013Q3 | 2013 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2013-03-07 | N | 55.1399 | N | 4 | N | N | 1.1101 | 39.4971 | 5762.1254
[7 empty] | 16714 | 1296 | 948869 | 2013-03-07 19:15 | 2013-03-07 20:22 | 67 | 11kV | 49251 | 809 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.1164 Rose bay Pnl.12 tripped on Earth Fault UG cable fault from S35907 to S594 see 949923 949925 949928 | March | 2013 | 2013Q3 | 2013 | ZN1164:PA12 | ZN36100:PA15 | ZN36100/000015 | WAVERLEY | UG | Not Veg | 2013-03-07 | N | 60.8789 | N | 4 | N | N | 1.1101 | 39.4971 | 35991.1781
[7 empty] | 17640 | 10690 | 948895 | 2013-03-08 01:21 | 2013-03-08 04:14 | 173 | 11kV | 122347 | 1577 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.1788 Matraville Zn Pnl.11 tripped on A phase Inst - C phase Section of feeder from S4556 Sw B to S2870 Sw A EFIs @ S8708 and CP62150 give incorrect indication @ S4556 failed to operate. Also Zone RTU went out of scan rendering control room blind. See 951838 for Pnl.11 interruption. | March | 2013 | 2013Q3 | 2013 | ZN1788:PA14 | ZN1788:PA14 | ZN01788/000014 | RANDWICK | UG | Not Veg | 2013-03-08 | N | 77.5821 | N | 2 | N | N | 1.1101 | 39.4971 | 89407.579
[7 empty] | 17921 | 13335 | 948883 | 2013-03-07 21:58 | 2013-03-08 08:35 | 637 | 11kV | 27472 | 209 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | REC45082 Dooralong tripped and reclosed and tripped/locked out on Earth Fault Ex S14891 Wyong Zn Ex Fdr #5 labelled Wyong Cause: OH Down. 11kV into LV Network See 950126,8,9,30,1 Exclude 948883,7 | March | 2013 | 2013Q3 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-03-07 | N | 131.445 | N | 4 | N | N | 1.1101 | 39.4971 | 20075.7273
[7 empty] | 16735 | 1495 | 949197 | 2013-03-08 17:54 | 2013-03-08 18:25 | 31 | 11kV | 62 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135072 B phase DOLF : 10 Amp Excluded OMS 949197 | March | 2013 | 2013Q3 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2013-03-08 | N | 31 | N | 2 | N | N | 1.1101 | 39.4971 | 45.3078
[7 empty] | 17843 | 12651 | 949324 | 2013-03-09 15:05 | 2013-03-09 18:30 | 205 | 11kV | 615 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LLoyd Winney (subs F/C) has a temporary generator connected to two affected houses untill the transformer is able to be replaced (single phase tx). Interruption of PT13667 and PT13885 required to fix this Tx. To be carried out on Monday 11/3/13 Lloyd to advise on Monday AM. See 950390 2nd 9450146 Exclude 949324 | March | 2013 | 2013Q3 | 2013 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | UG | Not Veg | 2013-03-09 | N | 205 | N | 2 | N | N | 1.1101 | 39.4971 | 449.4239
[7 empty] | 16970 | 3355 | 949356 | 2013-03-09 19:15 | 2013-03-09 20:21 | 66 | 11kV | 858 | 13 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1967 Johnson School 31.5A fuse blown on Middle phase Cause: Fuse fatigue See OMS 949789 949358 949356 | March | 2013 | 2013Q3 | 2013 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2013-03-09 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 627.0011
[7 empty] | 17502 | 8845 | 949373 | 2013-03-10 05:45 | 2013-03-10 10:15 | 270 | 11kV | 270 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | LID 135077 3 phase dist fuse : 630 Amp Open DT LVF 56470 due to fire at club S/B. Excluded OMS 949373 | March | 2013 | 2013Q3 | 2013 | 234:2001 | 264:81232 | ZN00264/081232 | PORT STEPHENS | Unknown | Not Veg | 2013-03-10 | N | 270 | N | 5 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 17250 | 6544 | 949427 | 2013-03-10 14:06 | 2013-03-10 15:08 | 62 | 11kV | 85703 | 2338 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Zn.2568 St Peters - Pnl.32 tripped on A & C phase overcurrent End box fault @ S4267 Queen Bennett Switch A faulted and TX tripped see 951313 951314 | March | 2013 | 2013Q3 | 2013 | ZN2568:PA32 | ZN2568:PA32 | ZN02568/000032 | SYDNEY | Unknown | Not Veg | 2013-03-10 | N | 36.6565 | N | 5 | N | N | 1.1101 | 39.4971 | 62629.2246
[7 empty] | 17739 | 11858 | 949438 | 2013-03-10 15:00 | 2013-03-10 17:00 | 120 | 11kV | 600 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135083 C phase DOLF : 5 Amp Excluded OMS 949438 | March | 2013 | 2013Q3 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-03-10 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 17915 | 13254 | 949442 | 2013-03-10 16:00 | 2013-03-10 18:15 | 135 | 11kV | 270 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 135084 Single phase DOLF : 10 Amp Excluded OMS 949442 | March | 2013 | 2013Q3 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2013-03-10 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 16784 | 1952 | 949462 | 2013-03-10 21:22 | 2013-03-11 01:00 | 218 | 11kV | 218 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135085 Single phase Repaired broken 11kV conductor at LL Clamp 52316 Excluded OMS 949462 | March | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2013-03-10 | N | 218 | N | 5 | N | N | 1.1101 | 39.4971 | 159.308
[7 empty] | 17208 | 5998 | 949608 | 2013-03-11 10:10 | 2013-03-11 11:26 | 76 | 11kV | 34412 | 548 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S35500 Top Ryde Panel 32 tripped on SEF. Cuase: Open bond on centre phase at AB239 See OMS 950370 950372 949608 949625 949626 949635 949626 949633 949637 949672 | March | 2013 | 2013Q3 | 2013 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2013-03-11 | N | 62.7956 | N | 4 | N | N | 1.1101 | 39.4971 | 25147.2746
[7 empty] | 17649 | 10770 | 949992 | 2013-03-11 16:00 | 2013-03-11 16:30 | 30 | 11kV | 180 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 135088 A phase Overhead CCT mains lying on crossarm at pole ER-85447 | March | 2013 | 2013Q3 | 2013 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2013-03-11 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 18505 | 19950 | 949828 | 2013-03-11 16:18 | 2013-03-12 00:23 | 485 | 11kV | 485 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135089 1 fault operation Excluded OMS 949828 | March | 2013 | 2013Q3 | 2013 | 222:2014 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Veg | 2013-03-11 | N | 485 | N | 4 | N | N | 1.1101 | 39.4971 | 354.4237
[7 empty] | 17039 | 3967 | 949887 | 2013-03-11 23:36 | 2013-03-12 00:40 | 64 | 11kV | 1152 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135091 B phase DOLF : 16 Amp Excluded OMS 949887, 949888 | March | 2013 | 2013Q3 | 2013 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | UG | Not Veg | 2013-03-11 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 841.8476
[7 empty] | 17707 | 11631 | 949889 | 2013-03-12 01:26 | 2013-03-12 03:06 | 100 | 11kV | 12922 | 188 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | ex ZN35370 Galston Panel 10 Recloser CP2691 Duneba Tripped on A and B phase O/C Signals Pulse close A B and C phases. Abnormal Switching: CP2691 Closed and CP50015 Open and Defective. Cause not ascertained for outage - mains to patrol See OMS 951853/855/856/857/859. 949889 | March | 2013 | 2013Q3 | 2013 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2013-03-12 | N | 68.734 | N | 11 | N | N | 1.1101 | 39.4971 | 9443.0165
[7 empty] | 16522 | 116 | 949895 | 2013-03-12 06:51 | 2013-03-12 09:16 | 145.1167 | 11kV | 3090.6667 | 31 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 135093 C phase DOLF : 20 Amp DOLF failed due to aging, Fuse Fatigue. | March | 2013 | 2013Q3 | 2013 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Not Veg | 2013-03-12 | N | 99.6989 | N | 11 | N | N | 1.1101 | 39.4971 | 2258.568
[7 empty] | 16887 | 2670 | 949952 | 2013-03-12 08:37 | 2013-03-12 12:15 | 217.9833 | 11kV | 4359.6667 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135102 B phase DOLF : 40 Amp CC1: 22-"Refer to SOp" | March | 2013 | 2013Q3 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2013-03-12 | N | 217.9833 | N | 11 | N | N | 1.1101 | 39.4971 | 3185.9158
[7 empty] | 17255 | 6593 | 950168 | 2013-03-12 13:48 | 2013-03-12 15:02 | 74 | 11kV | 87550 | 1294 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3425Castle Cove Panel 43 opened on A and C phase O/C, fault check, EFI, No3 Group Earth and 11kV Trip. Cause: UG cable fault S4773 to S35240. See OMS 951953 951950 950168 | March | 2013 | 2013Q3 | 2013 | ZN3425:PA43 | ZN3425:PA43 | ZN03425/000043 | WILLOUGHBY | UG | Not Veg | 2013-03-12 | N | 67.6584 | N | 11 | N | N | 1.1101 | 39.4971 | 63978.9577
[7 empty] | 16810 | 2117 | 950208 | 2013-03-12 14:56 | 2013-03-12 16:08 | 72 | 11kV | 56736 | 788 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S80 Chatswood Pa31 opened on B and C phase IOC lockout and timing relays EFI. Cause: Treee fallen on 11kV OH near AB2329 See OMS 951003 950208/221/251 | March | 2013 | 2013Q3 | 2013 | ZN80:PA31 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2013-03-12 | N | 72 | N | 11 | N | N | 1.1101 | 39.4971 | 41460.9954
[7 empty] | 17908 | 13181 | 950141 | 2013-03-12 13:11 | 2013-03-12 17:24 | 253 | 11kV | 110829 | 810 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Recloser CP2749 Delhi Rd Opened on SEL Cause: Lightning Arrestor blown on on 11kV UGOH between S5068 and CP1817. Abnormal Switching: S46817 SwB closed AB239 Open S 1896 SW/A closed and S7889 SW/A Open See OMS 952116 952119 950141 | March | 2013 | 2013Q3 | 2013 | ZN1193:PA28 | ZN80:PA31 | ZN00080/000031 | WILLOUGHBY | OH | Not Veg | 2013-03-12 | N | 136.8259 | N | 11 | N | N | 1.1101 | 39.4971 | 80990.5643
[7 empty] | 16890 | 2740 | 950148 | 2013-03-12 13:25 | 2013-03-12 17:24 | 239 | 11kV | 169451 | 709 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ex s1193 Lindfield Panel Bond burnt off CP701 See OMS 952870 950148 950255 950291 950302 | March | 2013 | 2013Q3 | 2013 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | KU-RING-GAI | OH | Not Veg | 2013-03-12 | N | 239 | N | 11 | N | N | 1.1101 | 39.4971 | 123829.7928
[7 empty] | 16520 | 105 | 950264 | 2013-03-12 16:29 | 2013-03-12 17:42 | 73 | 11kV | 92637 | 1269 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 135108 2 fault operations faulty ugoh at pole JV-20331 isolated Excluded OMS 950264 | March | 2013 | 2013Q3 | 2013 | 219:1783 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | Unknown | Unknown | 2013-03-12 | N | 73 | N | 11 | N | N | 1.1101 | 39.4971 | 67696.3873
[7 empty] | 17065 | 4155 | 950292 | 2013-03-12 17:15 | 2013-03-12 18:55 | 100 | 11kV | 5600 | 56 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 135109 Conductor has burnt through crossarm at pole CB-13901 Excluded OMS 950292 | March | 2013 | 2013Q3 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-03-12 | N | 100 | N | 11 | N | N | 1.1101 | 39.4971 | 4092.3148
[7 empty] | 18110 | 15851 | 950331 | 2013-03-12 22:33 | 2013-03-13 00:16 | 103 | 11kV | 95417 | 1023 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 2196 Milperra Panel 18 "Lachlan Cant" feeder tripped on: Relays: Earth fault, fault check, EFI Signals: 11kv trip Field EFI's: S4859, S4860, S35525, S35379, S35819, S7475, S6492 Remarks: UG fault. Suspect UG cable fault from Sub 6492 Wilfox IIma No.1 Sw B to Sub 4461 Eldridge Will SwA Related jobs: #950331, 950333, 950847, 950839, 950838 | March | 2013 | 2013Q3 | 2013 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-03-12 | N | 93.2717 | N | 11 | N | N | 1.1101 | 39.4971 | 69727.9293
[7 empty] | 17586 | 9743 | 950334 | 2013-03-12 23:51 | 2013-03-13 01:50 | 119 | 11kV | 119 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | LID 135111 A phase DOLF : 10 Amp | March | 2013 | 2013Q3 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2013-03-12 | N | 119 | N | 11 | N | N | 1.1101 | 39.4971 | 86.9617
[7 empty] | 18169 | 16287 | 951152 | 2013-03-15 03:42 | 2013-03-15 15:20 | 698 | 11kV | 119202 | 1029 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn14144 Wamberal 11kv feeder Pa7 fdr tripped and locked out on Relays: B & C Phase timed O/C, recloser lockout, EFI Field: Nil remarks: Tree in Kalakau St, ahs brought down the HV mains into LV mains, EMSO required on restoration section of 11kv fdr from LK43039 to 41206 tee PT11263 Lalakau Myee See 952043,4 Exclude 951152,64,65,77 | March | 2013 | 2013Q3 | 2013 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2013-03-15 | N | 115.8426 | N | 7 | N | N | 1.1101 | 39.4971 | 87109.3057
[7 empty] | 17149 | 4994 | 951348 | 2013-03-15 12:36 | 2013-03-15 16:05 | 209 | 11kV | 64418 | 777 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | @Zn12600 Lisarow 11kv CB pa2 tripped, reclosed, tripped on: Relays: 1&C phase. TImed O/C, A7C phase IOC Signals: 11kv trip EFI's: S14337 S14495 S14494 SMcdonald and Tuggerah rd UGOH remarks: 11kv fdr from SwB S14494 Pineridge Crestview to SwB S18040 O'Donnell Woodview 0.9 to AB41265 tee to PT11123 Faggans Tugerrah 0.7 See 952101,3,5,6,8,9,10 Exclude 951348,402 | March | 2013 | 2013Q3 | 2013 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | Unknown | Unknown | 2013-03-15 | N | 82.906 | N | 7 | N | N | 1.1101 | 39.4971 | 47074.7744
[7 empty] | 17447 | 8298 | 951441 | 2013-03-15 15:30 | 2013-03-15 16:12 | 42 | 11kV | 28014 | 667 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12570 Avoca Pa22 @ REC46529 Divstown Mundoora : Tripped reclosed and locked out IOC & Timed O/C Remarks: Tree/Branch on 11kv mains near LK42314. Removed by DOp See 952275 exclude 951441,2,9 | March | 2013 | 2013Q3 | 2013 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2013-03-15 | N | 42 | N | 7 | N | N | 1.1101 | 39.4971 | 20471.8049
[7 empty] | 17885 | 12976 | 951483 | 2013-03-15 18:02 | 2013-03-15 19:00 | 58 | 11kV | 11368 | 196 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At AS1610 Homebush Bay Panel 18 America Asia feeder tripped on: A Phase O/C Earth fault. No Field EFI's. Remarks: UG fault. Front line UG feeder fault. Related jobs: #951836, 951483 | March | 2013 | 2013Q3 | 2013 | ZN1610:PA18 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2013-03-15 | N | 58 | N | 7 | N | N | 1.1101 | 39.4971 | 8307.3991
[7 empty] | 16985 | 3452 | 951511 | 2013-03-15 20:01 | 2013-03-15 21:40 | 99 | 11kV | 198 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135138 B phase DOLF : 15 Amp Excluded OMS 951511 | March | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2013-03-15 | N | 99 | N | 7 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 17102 | 4413 | 951529 | 2013-03-15 23:03 | 2013-03-16 00:36 | 93 | 11kV | 80796 | 874 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Zn2400 Berowra panel 26 tripped on Relays: B and Cphase IOC Signals: 11kV Trip Abnormal Switching AB993 Open, LB1012 Closed Caise: Cause not ascertaine for ootage see OMS952909 952911 951529 | March | 2013 | 2013Q3 | 2013 | ZN2400:PA26 | ZN2400:PA26 | ZN02400/000026 | HORNSBY | OH | Veg | 2013-03-15 | N | 92.4439 | N | 7 | N | N | 1.1101 | 39.4971 | 59043.3337
[7 empty] | 18384 | 18259 | 951534 | 2013-03-16 00:53 | 2013-03-16 02:15 | 82 | 11kV | 102234 | 1329 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman, 11kV Fdr Panel 10 Cb ytripped on B phase timed OC, fault check, efi. Field efi's down at S.5511, S.35371 and S.2404. 11kV cable failed between S.2404 and S.35820 | March | 2013 | 2013Q3 | 2013 | ZN180:PA10 | ZN180:PA10 | ZN00180/000010 | MOSMAN | UG | Not Veg | 2013-03-16 | N | 76.9255 | N | 3 | N | N | 1.1101 | 39.4971 | 74709.5918
[7 empty] | 16797 | 2028 | 951580 | 2013-03-16 10:55 | 2013-03-16 11:40 | 45 | 11kV | 45 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135146 B phase DOLF : 10 Amp Excluded OMS 951580 | March | 2013 | 2013Q3 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | UG | Not Veg | 2013-03-16 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 18447 | 19082 | 951896 | 2013-03-15 20:57 | 2013-03-16 15:00 | 1083 | 11kV | 1083 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135137 1 fault operation B phase Overcurrent Sw 8677 New Lambton sub targets - B phase O/C, LED 1, 87L Diff trip latch. | March | 2013 | 2013Q3 | 2013 |  |  |  | NEWCASTLE | OH | Veg | 2013-03-15 | N | 1083 | N | 7 | N | N | 1.1101 | 39.4971 | 791.4245
[7 empty] | 18337 | 17763 | 951613 | 2013-03-16 14:12 | 2013-03-16 19:30 | 318 | 11kV | 81252 | 315 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135147 1 fault operation faulty 11kV ABC conductor | March | 2013 | 2013Q3 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2013-03-16 | N | 257.9429 | N | 3 | N | N | 1.1101 | 39.4971 | 59376.5651
[7 empty] | 17628 | 10501 | 951665 | 2013-03-17 04:05 | 2013-03-17 04:50 | 45 | 11kV | 3420 | 76 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | At S1017 Threlfall footpath HDO operated Cause: Flashover caused by possum See OMS 952922 951665 | March | 2013 | 2013Q3 | 2013 | ZN4545:PA41 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2013-03-17 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 2499.2351
[7 empty] | 17308 | 7141 | 951711 | 2013-03-17 10:07 | 2013-03-17 11:37 | 90 | 11kV | 90 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135152 B phase DOLF : 10 Amp Excluded OMS 951711 | March | 2013 | 2013Q3 | 2013 | 232:11460 | 232:11460 | ZN00232/011460 | PORT STEPHENS | UG | Not Veg | 2013-03-17 | N | 90 | N | 4 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 18127 | 15941 | 951757 | 2013-03-17 15:00 | 2013-03-17 15:45 | 45 | 11kV | 33410 | 1198 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 135154 2 fault operation 3 phase Earth fault tree caused flash over at ugoh JU-43957 | March | 2013 | 2013Q3 | 2013 | 205:12205 | 205:12205 | ZN00205/012205 | NEWCASTLE | Unknown | Unknown | 2013-03-17 | N | 27.8881 | N | 4 | N | N | 1.1101 | 39.4971 | 24415.0426
[7 empty] | 18076 | 15562 | 951758 | 2013-03-17 15:00 | 2013-03-17 17:25 | 145 | 11kV | 32132 | 776 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12570 Avoca Pa34 fdr tripped, reclosed, tripped & locked out on Relays: A7Bphase O/C, Lockout Signals: 11kv trip Cause: Tree/Branch on OH Mains Large tree branch removed by DOP O/S 32 Surf Rider Ave & HV Bond burnt off AB43862 See 952477,8 Exclude 951758,61,2,77 | March | 2013 | 2013Q3 | 2013 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2013-03-17 | N | 41.4072 | N | 4 | N | N | 1.1101 | 39.4971 | 23481.1179
[7 empty] | 17882 | 12951 | 951813 | 2013-03-18 03:57 | 2013-03-18 05:06 | 69 | 11kV | 170506 | 2536 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.342 Paddington Pnl.26 tripped on 26R - A phase O/C Abnormal S778 Sw A is closed with Sw B Open UG cable fault from S166 Sw A to S35521 Sw A see 951933 951932 | March | 2013 | 2013Q3 | 2013 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2013-03-18 | N | 67.2342 | N | 2 | N | N | 1.1101 | 39.4971 | 124600.7557
[7 empty] | 17425 | 8150 | 952042 | 2013-03-18 13:00 | 2013-03-18 15:00 | 120 | 11kV | 600 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 135155 Replace faulty crossarm at pole 8L-90193 Excluded #OMS 952042 | March | 2013 | 2013Q3 | 2013 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2013-03-18 | N | 120 | N | 2 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 17372 | 7672 | 952259 | 2013-03-19 07:13 | 2013-03-19 09:55 | 162 | 11kV | 250569 | 1684 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 10994 Mortdale - Pnl 4 - A phase OC and Earth fault, Fault check, EFI, Lockout. Suspected underground or UGOH fault. | March | 2013 | 2013Q3 | 2013 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | UG | Not Veg | 2013-03-19 | N | 148.7939 | N | 4 | N | N | 1.1101 | 39.4971 | 183108.4347
[7 empty] | 17797 | 12366 | 952526 | 2013-03-19 15:02 | 2013-03-19 18:49 | 226.9667 | 11kV | 4539.3333 | 20 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135171 A phase LF 47072 was not blown. 11kV Tapping open on pole IQ-71119. | March | 2013 | 2013Q3 | 2013 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2013-03-19 | N | 226.9667 | N | 4 | N | N | 1.1101 | 39.4971 | 3317.2109
[7 empty] | 18355 | 17894 | 952309 | 2013-03-19 09:31 | 2013-03-19 18:55 | 564 | 11kV | 82066 | 1324 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 135168 3 fault operations A & C phase Earth fault; Overcurrent Suspected cable fault between poles DD-60078 & GY-67002. Also suspect arrestor & VT at Sw 43321. Sw 80075 & 43321 tripped at same time. Note Sw 43146 did not trip during initial fault or tryback - protection malgrade? OMS # 952312 Targets 80075 A & C O/C & E/F. Sw 43321 E/F. Network in abnormal state. Blown Arresters at pole DD-60078. Replaced OK. | March | 2013 | 2013Q3 | 2013 | 243:80080 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | UG | Not Veg | 2013-03-19 | N | 61.9834 | N | 4 | N | N | 1.1101 | 39.4971 | 59971.4123
[7 empty] | 16936 | 3144 | 952586 | 2013-03-19 19:52 | 2013-03-20 01:25 | 333 | 11kV | 333 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 135172 Single phase DOLF : 10 Amp Replaced faulty LA. Reading as left 241V Excluded OMS 952586. | March | 2013 | 2013Q3 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-03-19 | N | 333 | N | 4 | N | N | 1.1101 | 39.4971 | 243.3466
[7 empty] | 18221 | 16809 | 952803 | 2013-03-20 11:54 | 2013-03-20 15:30 | 216 | 11kV | 278898 | 2026 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12570 Avoca Pa37 tripped on: Earth Fault EFI's: S18439 S49066,S18135 S14561 S14562 UGOH cnr Willow Moores S14563 S14564 S14565 Relays:O/C + timed, E/F O/C Signals: 11kv trip Remarks: 11kv fdr from S14565 to S14566 tee S12679 See 953697,701,2,3,4,5 Exclude 952803,42 | March | 2013 | 2013Q3 | 2013 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | UG | Not Veg | 2013-03-20 | N | 137.6594 | N | 3 | N | N | 1.1101 | 39.4971 | 203810.4323
[7 empty] | 18437 | 18969 | 952930 | 2013-03-20 14:58 | 2013-03-20 16:58 | 120 | 11kV | 4080 | 34 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT47662 Kathleen Pacific, Centre Phase 63A HDO fuse operated Ex panel 3 feeder Cause: not ascertained See 953713 exclude 952930 | March | 2013 | 2013Q3 | 2013 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2013-03-20 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 2981.5437
[7 empty] | 17932 | 13417 | 952712 | 2013-03-20 10:20 | 2013-03-20 20:45 | 625 | 11kV | 625 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S 3347 Washington Soul - Tx - Open circuit winding. Transformer winding open circuit. Transformer replaced and customers restored. Extended outage. | March | 2013 | 2013Q3 | 2013 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-03-20 | N | 625 | N | 3 | N | N | 1.1101 | 39.4971 | 456.7316
[7 empty] | 17364 | 7601 | 953117 | 2013-03-21 09:06 | 2013-03-21 15:20 | 374 | 11kV | 6572 | 45 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135196 2 fault operations B & C phase Earth fault; Overcurrent SWAN INTO MAINS ADJ POLE LI-50107. Excluded OMS REPORT NO 953117 | March | 2013 | 2013Q3 | 2013 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-03-21 | N | 146.0444 | N | 4 | N | N | 1.1101 | 39.4971 | 4802.6238
[7 empty] | 16869 | 2469 | 953420 | 2013-03-21 17:30 | 2013-03-21 18:50 | 80 | 11kV | 560 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | S 10680 Bermill Ferro - isolated by feeder control points AB 30759 and LK 30760. S 10680 (non//) was interrupted by DOp to repair 11kV OH sub link roadside. Link bond was HR. | March | 2013 | 2013Q3 | 2013 | ZN10996:PA20 | ZN10998:PA24 | ZN10998/000024 | BAYSIDE | OH | Not Veg | 2013-03-21 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 17554 | 9168 | 953398 | 2013-03-21 16:58 | 2013-03-21 19:05 | 127 | 11kV | 67735 | 964 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Ex Zn12640 Umina Pa7 @REC45025 Wagstaffe CB Opened and reclosed 3 times before locking out. Instantenous overcurrent and lock out relays Cause: UGOH Fault short circuit UGOH fault on first UGOH down to PT18229. Only customer is a toilet block in resere. PT18229 will remain interupted until repairs can be arranged. (cut out will be required from Links 44953 to PT13926_ Note: 11kV UGOH bonds broken away with 11kv OH mains above UGOH alive. See 953750,3 exclude 953398,419 | March | 2013 | 2013Q3 | 2013 | ZN12640:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | Unknown | Unknown | 2013-03-21 | N | 70.2645 | N | 4 | N | N | 1.1101 | 39.4971 | 49498.7402
[7 empty] | 17346 | 7412 | 953414 | 2013-03-21 17:22 | 2013-03-21 19:20 | 118 | 11kV | 63018 | 936 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 MEadowbank Panel 2 Trippedf on B phase timed O/C and EF relay, EFI and Fault Check. Cause: Cable fault between S4545 Meadownaml and S712 See OMS 954302 954303 954312 953414 953435 953436 | March | 2013 | 2013Q3 | 2013 | ZN4545:PA2 | ZN4545:PA2 | ZN04545/000002 | RYDE | UG | Not Veg | 2013-03-21 | N | 67.3269 | N | 4 | N | N | 1.1101 | 39.4971 | 46051.6957
[7 empty] | 18429 | 18914 | 953555 | 2013-03-22 09:24 | 2013-03-22 10:10 | 46 | 11kV | 105110 | 2285 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.15008 Harbord, Panel 1 Fdr CB tripped on A&C phase OC, lockout, reclose time delay. Palm fonds on OH opposite 102 Lawrence ST | March | 2013 | 2013Q3 | 2013 | ZN15008:PA1 | ZN15008:PA6 | ZN15008/000006 | NORTHERN BEACHES | OH | Veg | 2013-03-22 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 76811.2878
[7 empty] | 18270 | 17198 | 953570 | 2013-03-22 09:30 | 2013-03-22 11:30 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135203 C phase DOLF : 20 Amp Excluded OMS 953570 | March | 2013 | 2013Q3 | 2013 | 806:82656 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-03-22 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 16766 | 1746 | 953670 | 2013-03-22 12:50 | 2013-03-22 15:37 | 167 | 11kV | 668 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 26228 tripped, reclosed, tripped and locked out on OC and IOC. Trees on mains in vicinity of PT.16261 | March | 2013 | 2013Q3 | 2013 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2013-03-22 | N | 167 | N | 4 | N | N | 1.1101 | 39.4971 | 488.1547
[7 empty] | 17568 | 9537 | 953641 | 2013-03-22 11:40 | 2013-03-23 01:25 | 825 | 11kV | 122438 | 997 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S4545 Meadowbank Panel 17 tripped reclosed tripped and locked out on Relays: A phase Inst and Timed, C phase Timed, EFI and Lockout, fault check Signals: 11kV Trip, Zone Earth Abnormal Switching: SwB closed at S8840 Ab792 Opened Cause: large tree branch downed mains and snapped pole between S49621 to S129 hunters Hill tee Pt2421 to S8840 See OMS 955718 955719 955720 955721 953641 953853 | March | 2013 | 2013Q3 | 2013 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | OH | Veg | 2013-03-22 | N | 122.8064 | N | 4 | N | N | 1.1101 | 39.4971 | 89474.0791
[7 empty] | 16899 | 2890 | 953906 | 2013-03-23 09:48 | 2013-03-23 11:03 | 75 | 11kV | 100575 | 1341 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn2400 Berowra Panel 22 tripped O/C A and C Phase Signals: 11kV Trip Cause: Tree branch OS 657 Pacific Highway. Cause See OMS 950906 955320 | March | 2013 | 2013Q3 | 2013 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2013-03-23 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 73497.2435
[7 empty] | 18529 | 20141 | 954297 | 2013-03-23 07:47 | 2013-03-23 11:09 | 202 | 11kV | 56378 | 339 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135210 3 fault operations 3 phase Overcurrent fdr patrolled as best as possible (re rural area) by j frazer and t horn. no cause found. DQ Note Bridgman Rd rec tripped at the same time. Targets: 3 phase OC A=868 B=855 C=165 Excluded oms 953885 ## | March | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-03-23 | N | 166.3068 | N | 4 | N | N | 1.1101 | 39.4971 | 41199.3795
[7 empty] | 17609 | 10143 | 953963 | 2013-03-23 14:12 | 2013-03-23 15:10 | 58 | 11kV | 1914 | 33 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S5693 Ryde West No2 400A fuse blown on A and B phase of distributor 3. Cause: Vehicle hit pole O/S 33 Ryde Rd See OMS 955355 953966 953963 | March | 2013 | 2013Q3 | 2013 | ZN195:PA25 | ZN195:PA25 | ZN00195/000025 | KU-RING-GAI | OH | Not Veg | 2013-03-23 | N | 58 | N | 4 | N | N | 1.1101 | 39.4971 | 1398.6947
[7 empty] | 17157 | 5157 | 953957 | 2013-03-23 13:40 | 2013-03-23 17:04 | 204 | 11kV | 9071 | 153 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Zn12630 Peats ridge Section Pa3 @REC45071 Central Mangrove Opened, Reclosed, Openeded, & Locked out @REC49206 Mangrove Mountain West Opended, Reclosed, Opened & Locked out Cuase: Tree/branch brought down OH. Tree on 11kv OH @ USL 41696 brought down 2 bays of OH See 955286,8,9 exclude 953957,67,72 | March | 2013 | 2013Q3 | 2013 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-03-23 | N | 59.2876 | N | 4 | N | N | 1.1101 | 39.4971 | 6628.8193
[7 empty] | 17337 | 7362 | 954053 | 2013-03-24 08:52 | 2013-03-24 11:50 | 178 | 11kV | 14084 | 337 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135211 B & C phase Earth fault, Overcurrent section isolated to repair mains Excluded OMS 954053, 954056 | March | 2013 | 2013Q3 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-03-24 | N | 41.7923 | N | 2 | N | N | 1.1101 | 39.4971 | 10292.1718
[7 empty] | 16866 | 2445 | 954096 | 2013-03-24 13:08 | 2013-03-24 14:15 | 67 | 11kV | 3617.65 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Fuse Fatigue. No Cause Found See 955313 GIS 954096 exclude 954097 | March | 2013 | 2013Q3 | 2013 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2013-03-24 | N | 66.9935 | N | 2 | N | N | 1.1101 | 39.4971 | 2643.6719
[7 empty] | 18317 | 17622 | 955339 | 2013-03-25 00:28 | 2013-03-25 04:04 | 216 | 11kV | 430802 | 3062 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S35500 Top Ryde tripped on relay 51AC (inverse time o/c A_C ph) cause not ascertained patrolled by DOp See OMS 955339 955342 955343 | March | 2013 | 2013Q3 | 2013 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2013-03-25 | N | 140.693 | N | 2 | N | N | 1.1101 | 39.4971 | 314817.3951
[7 empty] | 17538 | 9053 | 954462 | 2013-03-25 14:51 | 2013-03-25 16:40 | 109 | 11kV | 109 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135227 A phase DOLF | March | 2013 | 2013Q3 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | UG | Not Veg | 2013-03-25 | N | 109 | N | 2 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 16789 | 1974 | 954755 | 2013-03-26 11:00 | 2013-03-26 11:45 | 45 | 11kV | 135 | 3 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 135240 B phase DOLF : 10 Amp Suspect bird Excluded OMS 954755. | March | 2013 | 2013Q3 | 2013 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2013-03-26 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 18274 | 17240 | 954998 | 2013-03-26 20:31 | 2013-03-26 21:19 | 48 | 11kV | 28272 | 589 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 135246 2 fault operations A & B phase Overcurrent Possum at pole IV-60889 Excluded OMS 954998 | March | 2013 | 2013Q3 | 2013 | 206:34438 | 206:34438 | ZN00206/034438 | LAKE MACQUARIE | OH | Not Veg | 2013-03-26 | N | 48 | N | 3 | N | N | 1.1101 | 39.4971 | 20660.3437
[7 empty] | 17696 | 11500 | 955011 | 2013-03-26 22:31 | 2013-03-27 07:45 | 554 | 11kV | 323853 | 2007 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 135247 4 fault operations B phase Overcurrent Suspect Fdr cable fault. Other targets found at sub: Tx 3315 -B ph E/F; B/U A&B E/F Tx 3317 - B ph E/F; BU A&B E/F BU Neut E/F relay - I>, I>> Excluded OMS 955011, 955032 | March | 2013 | 2013Q3 | 2013 | 229:34989 | 233:82815 | ZN00233/082815 | PORT STEPHENS | UG | Not Veg | 2013-03-26 | N | 161.3617 | N | 3 | N | N | 1.1101 | 39.4971 | 236662.2204
[7 empty] | 17148 | 4992 | 955045 | 2013-03-27 07:05 | 2013-03-27 08:07 | 62 | 11kV | 3162 | 51 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | @PT13387 Gomul Budgewoi Centre Phase 31.5A fuse blew Cause: Animals/Birds Magpie came into contact with 11kv and tank below HDO No readings taken as it is a 2 pole PT. Unable to climb See 955544 Exclude 955045,50,3,95,107,35 | March | 2013 | 2013Q3 | 2013 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2013-03-27 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 2310.6963
[7 empty] | 17210 | 6047 | 955024 | 2013-03-27 03:39 | 2013-03-27 10:00 | 381 | 11kV | 20193 | 53 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 135248 Car hit pole JT-50045. Excluded OMS 955024. | March | 2013 | 2013Q3 | 2013 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2013-03-27 | N | 381 | N | 4 | N | N | 1.1101 | 39.4971 | 14756.4488
[7 empty] | 16638 | 888 | 955280 | 2013-03-27 13:05 | 2013-03-27 13:50 | 44.7167 | 11kV | 626.0333 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135257 Section isolated from LF 42863 to repair stranded mains | March | 2013 | 2013Q3 | 2013 | 503:48011 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2013-03-27 | N | 44.7167 | N | 4 | N | N | 1.1101 | 39.4971 | 457.4867
[7 empty] | 17059 | 4103 | 955372 | 2013-03-27 16:10 | 2013-03-27 20:05 | 235 | 11kV | 42770 | 466 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 135260 2 fault operations Overcurrent Excavator came into contact with 11kV OHM at pole JT-40035. Excluded OMS No. 955372,955406 & 955381 | March | 2013 | 2013Q3 | 2013 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2013-03-27 | N | 91.7811 | N | 4 | N | N | 1.1101 | 39.4971 | 31255.0545
[7 empty] | 17799 | 12391 | 955469 | 2013-03-28 06:35 | 2013-03-28 08:08 | 93 | 11kV | 43740 | 795 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135264 1 fault operation A & C phase Instantaneous Overcurrent; Overcurrent System abnormal, Fdr 74119 also supplying Fdr 74121 due to previous cable fault. Excluded OMS 955469 & 955470 | March | 2013 | 2013Q3 | 2013 | 801:74119 | 801:74119 | ZN00801/074119 | MUSWELLBROOK | OH | Veg | 2013-03-28 | N | 55.0189 | N | 7 | N | N | 1.1101 | 39.4971 | 31963.9019
[7 empty] | 18392 | 18334 | 955687 | 2013-03-28 12:26 | 2013-03-28 13:04 | 38 | 11kV | 30248 | 796 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12600 Lisarow 11kV fdr pa1 "Dog Trap rd" Tripped, reclosed, tripped and locked out on Relays: Aph O/C, reclosing relay, timing Signals: 11kv trip Remarks:11kv UGOH on the Cnr Pacifis Hwy and Chamrberlain rd Section of feeder from zn12600 Lisarow to AB42050 to AB45435 (N/O) See 956455 Exclude 955687,8,6449 | March | 2013 | 2013Q3 | 2013 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | Unknown | Unknown | 2013-03-28 | N | 38 | N | 7 | N | N | 1.1101 | 39.4971 | 22104.3462
[7 empty] | 17278 | 6850 | 955627 | 2013-03-28 11:18 | 2013-03-28 15:15 | 237 | 11kV | 237 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135268 B phase Striker fuse : 80 Amp The striker fuse in the Sw/f had operated and staff on site advised the transformer needs to be replaced. The transformer was left isolated and the normally open LV fuse interconnecting with sub 9920 was closed. The RSPCA site had a load of about 150 amps. Staff on site advised the Control Room that during normal business hours sub 9920 may be overloaded now it is interconnected with sub 37615. MG set to be connected to guard sub 9920 from overload on Saturday. | March | 2013 | 2013Q3 | 2013 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | UG | Not Veg | 2013-03-28 | N | 237 | N | 7 | N | N | 1.1101 | 39.4971 | 173.1926
[7 empty] | 18210 | 16687 | 955860 | 2013-03-28 17:10 | 2013-03-28 17:30 | 20 | 11kV | 13717 | 927 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 135271 1 fault operation A phase Overcurrent; Earth fault Sw 33679 tripped when picking up load from tripped Fdr 13446. See report 135270. Suspect cable fault to Sw 23640. Excluded OMS # 955860 | March | 2013 | 2013Q3 | 2013 | 225:33679 | 270:83594 | ZN00270/083594 | LAKE MACQUARIE | Unknown | Unknown | 2013-03-28 | N | 14.7972 | N | 7 | N | N | 1.1101 | 39.4971 | 10023.979
[7 empty] | 17189 | 5736 | 955821 | 2013-03-28 15:29 | 2013-03-28 18:00 | 151 | 11kV | 129774 | 2099 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 135269 2 fault operations 3 phase Overcurrent; Earth fault Pole JU-80365 fell. High into low. Burnt tapping pole Ju-70043. A ph LVF 806 also replaced 200A. Excluded OMS # 955821, 955834, 955869, 955871 | March | 2013 | 2013Q3 | 2013 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2013-03-28 | N | 61.8266 | N | 7 | N | N | 1.1101 | 39.4971 | 94835.0115
[7 empty] | 18500 | 19899 | 955957 | 2013-03-28 22:40 | 2013-03-28 23:45 | 64.5333 | 11kV | 6517.8667 | 101 | HV | Vandalism | 3rd Party Impact | DC Transformer | Unplanned | Unselected | N | LID 135273 B & C phase DOLF A piece of timber was found lodged across the transformer HV bushings. Timber removed blown DOLF's replaced & supply restored OK. Excluded OMS No's 955956 & 955959 CC1: 22-"Refer to SOp" | March | 2013 | 2013Q3 | 2013 | 238:34140 | 532:83298 | ZN00532/083298 | MAITLAND | UG | Not Veg | 2013-03-28 | N | 64.5333 | N | 7 | N | N | 1.1101 | 39.4971 | 4763.0647
[7 empty] | 17666 | 10982 | 955977 | 2013-03-29 04:37 | 2013-03-29 05:50 | 73 | 11kV | 32052 | 471 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn12650 West Gosford pa14 "Kariong & Erina" fdr tripped on: Relays: 14R Earth Fault and EFI Signals: 11kv trip EFI:Nil Remarks: Cause not ascertained See 956463,4 Exclude 955977 | March | 2013 | 2013Q3 | 2013 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Veg | 2013-03-29 | N | 68.051 | N | 4 | N | N | 1.1101 | 39.4971 | 23422.6562
[7 empty] | 16803 | 2077 | 955976 | 2013-03-29 04:37 | 2013-03-29 06:55 | 137.7667 | 11kV | 30584.2 | 222 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | The centre phase bond burnt off at USL.24464 CC1: 22-"Refer to SOp" | March | 2013 | 2013Q3 | 2013 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-03-29 | N | 137.7667 | N | 4 | N | N | 1.1101 | 39.4971 | 22350.0313
[7 empty] | 16791 | 1988 | 956027 | 2013-03-29 11:56 | 2013-03-29 12:50 | 54 | 11kV | 54 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135278 A phase DOLF : 16 Amp Excluded OMS 956027 | March | 2013 | 2013Q3 | 2013 | 222:2014 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | UG | Not Veg | 2013-03-29 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 39.4616
[7 empty] | 17643 | 10712 | 955842 | 2013-03-28 16:07 | 2013-03-29 16:30 | 1463 | 11kV | 65379 | 1532 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 135270 2 fault operations A phase Overcurrent UGOH pole IV-47034 failed. Excluded OMS # 955842 | March | 2013 | 2013Q3 | 2013 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | Unknown | Unknown | 2013-03-28 | N | 42.6756 | N | 7 | N | N | 1.1101 | 39.4971 | 47777.0448
[7 empty] | 17742 | 11897 | 956052 | 2013-03-29 16:15 | 2013-03-29 17:52 | 97 | 11kV | 388 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 135280 B phase DOLF : 10 Amp Fuse fatigue Excluded OMS 956052 | March | 2013 | 2013Q3 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2013-03-29 | N | 97 | N | 4 | N | N | 1.1101 | 39.4971 | 283.539
[7 empty] | 18020 | 14565 | 956093 | 2013-03-30 04:28 | 2013-03-30 05:28 | 60 | 11kV | 102150 | 1905 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15005 Belrose, Panel 2 Fdr CB tripped on LHS IOC A,B and C phase, fault check and efi., 11kV trip, zone earth. Field efi down at S.16881, S.15425. Suspect UG cable fault between S.15425 and S.16801 | March | 2013 | 2013Q3 | 2013 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | UG | Not Veg | 2013-03-30 | N | 53.622 | N | 5 | N | N | 1.1101 | 39.4971 | 74648.2071
[7 empty] | 18543 | 20282 | 956117 | 2013-03-30 08:39 | 2013-03-30 14:20 | 341 | 11kV | 31713 | 93 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of Zn14144 Wamberal Pa10L "Wamberal Aux#2 fdr" Loos of supply beyond LB40238 due to footpath phase bond burnt at RE44582 Erina (line side) and also LB41358 defective. No circuit breaker operations Remarks: Section of 11kv fdr from RE44059 Matcham to N/O RE40239 Wattle Tre rd sth to LB40238 to RE44582 Erina and extent beyond, etc interrupted to allow emergency repairs to bonds and bypass A/B @ Rec44582 and LB41358 (could not openrequiring to extend isolation to REC44059) See 956491 exclude 956117,32 | March | 2013 | 2013Q3 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2013-03-30 | N | 341 | N | 5 | N | N | 1.1101 | 39.4971 | 23174.925
[7 empty] | 16644 | 918 | 956193 | 2013-03-30 15:58 | 2013-03-30 17:05 | 67 | 11kV | 737 | 11 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 135287 A phase DOLF : 20 Amp bird strike on PT Excluded oms 956193 | March | 2013 | 2013Q3 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-03-30 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 538.5779
[7 empty] | 17761 | 12032 | 956186 | 2013-03-30 16:31 | 2013-03-31 00:45 | 494 | 11kV | 31616 | 64 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S.6813 Lord Botany No.1 - Faulty Transformer - No devices operated Dop attended and found low vollts on one phase at sub 6816 and customer running on generator.subs either side of centre checked healthy .dop has left A/P for subs tech to check transformer (winding test) | March | 2013 | 2013Q3 | 2013 | ZN630:PA14 | ZN8100:PA39 | ZN08100/000039 | BAYSIDE | UG | Not Veg | 2013-03-30 | N | 494 | N | 5 | N | N | 1.1101 | 39.4971 | 23104.0403
[7 empty] | 17802 | 12431 | 956214 | 2013-03-30 18:16 | 2013-03-31 07:46 | 810 | 11kV | 56107 | 194 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of Zn12630 Peats Ridge 11kv Pa2 "Gunderman fdr" @RE45013 Gunderman tripped on overcurrent Cause: tree branch brought down oh between AB43179 to LK42686 See 956495,6,503,4 Exclude 956214,30,1 | March | 2013 | 2013Q3 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2013-03-30 | N | 289.2113 | N | 5 | N | N | 1.1101 | 39.4971 | 41001.3407
[7 empty] | 17884 | 12957 | 956516 | 2013-03-31 07:32 | 2013-03-31 07:47 | 15 | 11kV | 2146 | 160 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section Pa12 Peats Ridge Zone. AB43179 to LB45074 Nil CB operations. Interrupted by DOp as LB45074 does not phase Abnormal: N/O LB45074 (to endeavour energy) was closed with 11kv feeder from AB43179 to L42686 isolated for repairs. Remarks: LB45074 opened to allow resotration switching after repairs to 11kv fdr from AB43179 to L42686 tee PT14580 and PT13624 after tree brought down 11kv wires. See 956495 for previous outage. See 956516,8 | March | 2013 | 2013Q3 | 2013 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2013-03-31 | N | 13.4125 | N | 1 | N | N | 1.1101 | 39.4971 | 1568.2335
[7 empty] | 16684 | 1123 | 956327 | 2013-04-01 07:42 | 2013-04-01 09:50 | 128 | 11kV | 2176 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135295 A & B phase DOLF : 20 Amp Excluded OMS 956327 | April | 2013 | 2013Q4 | 2013 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2013-04-01 | N | 128 | N | 1 | N | N | 1.1101 | 39.4971 | 1590.1566
[7 empty] | 18328 | 17736 | 956577 | 2013-04-02 10:35 | 2013-04-02 10:57 | 22 | 11kV | 1210 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 135302 A phase DOLF : 50 Amp Fuse Fatigued. Tx Volts: Aph - 243V, Bph - 243V, Cph - 243V Excluded OMS 956577 | April | 2013 | 2013Q4 | 2013 | 513:48058 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Not Veg | 2013-04-02 | N | 22 | N | 7 | N | N | 1.1101 | 39.4971 | 884.2323
[7 empty] | 17420 | 8129 | 956517 | 2013-04-02 09:28 | 2013-04-02 12:20 | 172 | 11kV | 860 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135303 A & B phase DOLF : 20 Amp Excluded OMS No. 956581 + 956517 Please patrol Feeder. | April | 2013 | 2013Q4 | 2013 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2013-04-02 | N | 172 | N | 7 | N | N | 1.1101 | 39.4971 | 628.4626
[7 empty] | 17416 | 8089 | 956624 | 2013-04-02 11:05 | 2013-04-02 13:45 | 160 | 11kV | 112123 | 1105 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 1788 - Matraville - Pnl 8 - UG Cable Fault At ZN 1788 Matraville Panel # 8 Wilkes Ave Fdr Tripped on: Earth Leakage - Efi-#5tx Group Earth-Zone Earth.11kv Trip Suspect UG fault between S807 Raglan Victoria to S35502 Raglan Mcgowen tee S1813 Victoria Nap | April | 2013 | 2013Q4 | 2013 | ZN1788:PA8 | ZN1788:PA61 | ZN01788/000061 | RANDWICK | UG | Not Veg | 2013-04-02 | N | 101.4688 | N | 7 | N | N | 1.1101 | 39.4971 | 81936.1813
[7 empty] | 17983 | 14127 | 956684 | 2013-04-02 12:49 | 2013-04-02 14:40 | 111 | 11kV | 111 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LLID 135304 The stay wire at the sub had failed, the sub was isolated for clearance and safety reasons while restraining the repaired stay wire using live line techniques. Excluded OMS 956684 | April | 2013 | 2013Q4 | 2013 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | UG | Not Veg | 2013-04-02 | N | 111 | N | 7 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 17923 | 13348 | 956468 | 2013-04-02 08:23 | 2013-04-02 15:20 | 417 | 11kV | 2085 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | @PT14778 reserve Dooralong 0.4 HDO fuse assembly failed and broke in half. See elaso interruption at PT12371 Dooralong Yambo 1.2 See 956949 exclude 956468,70 | April | 2013 | 2013Q4 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-04-02 | N | 417 | N | 7 | N | N | 1.1101 | 39.4971 | 1523.6565
[7 empty] | 17525 | 8988 | 956695 | 2013-04-02 13:18 | 2013-04-02 15:20 | 122 | 11kV | 610 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | Section of 11kv fdr from LK43082 to PT12371 Dooralong Yambo 1.2 to PT14778 Reserve Dooralong 0.4. Was interrupted for safety so broken HDO fuse assmebly on PT14778 Rreserve Dooralong 0.4 could be replaced Ex Zn14891 Wyong Pa5 "Wyong" fdr See separate interruption report on PT14778 Reserve Dooralong 0.4 See 956954 Exclude 956695 | April | 2013 | 2013Q4 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-04-02 | N | 122 | N | 7 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 18088 | 15678 | 956798 | 2013-04-02 15:45 | 2013-04-02 17:15 | 90 | 11kV | 180 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 135306 Single phase DOLF : 10 Amp fatigue 250 volts Excluded oms 956798 | April | 2013 | 2013Q4 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-04-02 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 17883 | 12955 | 957397 | 2013-04-03 10:00 | 2013-04-03 11:02 | 62 | 11kV | 372 | 6 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 135320 Broken insulator at pole 6o-40041. Conductor on crossarm | April | 2013 | 2013Q4 | 2013 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2013-04-03 | N | 62 | N | 4 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 17452 | 8324 | 957224 | 2013-04-03 13:30 | 2013-04-03 16:00 | 150 | 11kV | 2250 | 15 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Section of Zn12600 Lisarow Pa2 fdr from AB41935 to AB41934 interrupted for safety reasons. Car hit pole 5 bays north west pf AB41934 on Fagans rd. Linesman required to perform repairs. See 957426 exclude 957224,5 | April | 2013 | 2013Q4 | 2013 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2013-04-03 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 1644.2336
[7 empty] | 17941 | 13477 | 957284 | 2013-04-03 19:08 | 2013-04-03 19:20 | 12 | 11kV | 3315 | 380 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | O/H Conductor Bare | Unplanned | Unselected | N | At Zn4545 Meadowbank ex Panel 41 Section of OH feeder interrupted beyond LB329 Cause: Section of OH broken away from insulator and within close proximity to LV See OMS 957548 957549 957317957320 957322 | April | 2013 | 2013Q4 | 2013 | ZN4545:PA41 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2013-04-03 | N | 8.7237 | N | 4 | N | N | 1.1101 | 39.4971 | 2422.5042
[7 empty] | 16954 | 3273 | 957276 | 2013-04-03 17:05 | 2013-04-03 19:32 | 147.0667 | 11kV | 4317.05 | 46 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 135323 A phase DOLF : 40 Amp defective 11kV surge arrestor on Tx cut away by dop replacement required. DQ Excluded oms 957281, 957276, 957298 | April | 2013 | 2013Q4 | 2013 | 222:2014 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2013-04-03 | N | 93.8489 | N | 4 | N | N | 1.1101 | 39.4971 | 3154.7728
[7 empty] | 18031 | 14718 | 957360 | 2013-04-04 06:56 | 2013-04-04 11:46 | 290 | 11kV | 8700 | 30 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | Rain Light | N | Ex Zn12600 Lisarow Pa1 @ PT11943 Dora Railway the A and B phase 31.5 Amp HDO failed Remarks: Bark across transformer bushing Interruption report has no details of restoration switching. Restore date from 957360 used. See 958958 Exclude 957360 | April | 2013 | 2013Q4 | 2013 | ZN12600:PA1 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | UG | Not Veg | 2013-04-04 | N | 290 | N | 5 | N | N | 1.1101 | 39.4971 | 6357.7034
[7 empty] | 18225 | 16866 | 957916 | 2013-04-04 10:00 | 2013-04-04 14:10 | 250 | 11kV | 250 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 135333 BROKEN X-ARM POLE 8K-80171.SUB 71053 LEFT ISOLATED,TO BE REMOVED AT LATER DATE. | April | 2013 | 2013Q4 | 2013 |  |  |  |  | OH | Not Veg | 2013-04-04 | N | 250 | N | 5 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 18058 | 15412 | 957805 | 2013-04-04 17:03 | 2013-04-04 18:30 | 87 | 11kV | 4915 | 61 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 116 - Leichhardt - Pnl 45 - UG Cable Fault Signals: 11kv Trip Relays: Pnl 45 Earth Fault, Trip, EFI Field EFI's: S8189, S35867, S7728, S7727, S35805, S35806, S35807, S7017 Section of 11kv feeder out of ZN116, Pnl 45, from S7017 James Craig Rd No1 "Sw B" to S7784 Sommerville Rd No1 "Sw B" Suspect UG Cable Fault See Job #957962,965 Exclude 957805 | April | 2013 | 2013Q4 | 2013 | ZN116:PA45 | ZN116:PA1 | ZN00116/000001 | INNER WEST | UG | Not Veg | 2013-04-04 | N | 80.5738 | N | 5 | N | N | 1.1101 | 39.4971 | 3591.737
[7 empty] | 17857 | 12755 | 957793 | 2013-04-04 16:53 | 2013-04-04 19:15 | 142 | 11kV | 284 | 2 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Light | N | At PT1464 Wyong Gosford Smith Centre Phase and Footpath phase HDO 16A fuses blown Cause: tree branch contact - other Remarks: Stick was removed from HV transformer bushings by DOp See 958005 exclude 957793,7 | April | 2013 | 2013Q4 | 2013 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Veg | 2013-04-04 | N | 142 | N | 5 | N | N | 1.1101 | 39.4971 | 207.5388
[7 empty] | 17331 | 7339 | 957869 | 2013-04-04 23:08 | 2013-04-05 01:08 | 120 | 11kV | 116204 | 1291 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Zn12600 Lisarow Pa13 (Brush rd fdr) tripped Relays: ACph timed overcurrent, SEF, SEF relay Signals: 11kvtrip EFI: N/A Abnormal: SwB S18186 closed, Pa2 Open for Disc #311314. AB41711 closed with AB41934 opened for load relief from Pa2 Cause: Not Ascertained Remarks: Recloser on this substancially overhead feeder is N/A. Gosford O/H to Patrol See 958105,6,7,9 Exclude 957869 | April | 2013 | 2013Q4 | 2013 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2013-04-04 | N | 90.0108 | N | 5 | N | N | 1.1101 | 39.4971 | 84918.4558
[7 empty] | 17658 | 10896 | 958032 | 2013-04-05 08:36 | 2013-04-05 08:40 | 4 | 11kV | 28 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135340 Tripped during disconnection Switching 31483. SEF & Reclsoe OFF at Sw 9109 Excluded OMS 958032 | April | 2013 | 2013Q4 | 2013 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2013-04-05 | N | 4 | N | 1 | N | N | 1.1101 | 39.4971 | 20.4616
[7 empty] | 18330 | 17740 | 958382 | 2013-04-06 22:13 | 2013-04-06 23:05 | 52 | 11kV | 3021 | 675 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135352 Trip & reclose 1 fault operation C phase Earth fault Possum. A ph DOLF sub 5159 blown. Replaced 40A. Sub On 2305hrs. Excluded OMS # 958382 | April | 2013 | 2013Q4 | 2013 | 219:1785 | 221:11895 | ZN00221/011895 | LAKE MACQUARIE | OH | Not Veg | 2013-04-06 | N | 4.4756 | N | 1 | N | N | 1.1101 | 39.4971 | 2207.6577
[7 empty] | 18277 | 17252 | 958410 | 2013-04-07 07:59 | 2013-04-07 09:30 | 91 | 11kV | 91 | 1 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 135354 3 phase Striker fuse : 80 Amp HV 80A fuses blew possibly due to flash over in cable box. Cable boots found not fitted correctly. Terminations cleaned and new boots fitted. Excluded OMS 958410 | April | 2013 | 2013Q4 | 2013 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | Unknown | Not Veg | 2013-04-07 | N | 91 | N | 3 | N | N | 1.1101 | 39.4971 | 66.5001
[7 empty] | 17473 | 8543 | 958464 | 2013-04-07 15:16 | 2013-04-07 16:25 | 69 | 11kV | 4002 | 58 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12610 Long Jetty Section Pa2 @PT13650 Bateau Bay Larkin 63a Cph HDO Cause: fuse fatigue. Batch 1004 See 958464 GIS 958961 Exclude 958466 CC1: 22-"Refer to SOp" | April | 2013 | 2013Q4 | 2013 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2013-04-07 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 2924.5436
[7 empty] | 16557 | 366 | 958463 | 2013-04-07 14:59 | 2013-04-07 18:15 | 196 | 11kV | 7252 | 37 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | S.519 Shirlow St - 11kV RMI tripped Vehicle hit kiosk restored via lV // | April | 2013 | 2013Q4 | 2013 | ZN262:PA26 | ZN262:PA26 | ZN00262/000026 | INNER WEST | Unknown | Not Veg | 2013-04-07 | N | 196 | N | 3 | N | N | 1.1101 | 39.4971 | 5299.5477
[7 empty] | 18455 | 19144 | 958639 | 2013-04-08 10:35 | 2013-04-08 12:30 | 115 | 11kV | 115 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135361 No protection operated, the live line clamp had burnt away from its connection. No customers off sub. DOLF & LVF left ODT'd. Black pinned. | April | 2013 | 2013Q4 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2013-04-08 | N | 115 | N | 4 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 18134 | 15990 | 958750 | 2013-04-08 13:49 | 2013-04-08 16:30 | 161 | 11kV | 322 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135363 A & C phase DOLF : 10 Amp Excluded OMS 958750 | April | 2013 | 2013Q4 | 2013 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-04-08 | N | 161 | N | 4 | N | N | 1.1101 | 39.4971 | 235.3081
[7 empty] | 17165 | 5230 | 958737 | 2013-04-08 17:00 | 2013-04-08 19:30 | 150 | 11kV | 600 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN 9301 Kurnell - Section of Pnl 13 - AB 35004 to rest of feeder. Bond for droppers on PT 9064 went HR. DOp isolated for safety and bond was repaired by mains. Droppers had been replaced last year and LV fuse assembly and fuses have been replaced often. DC seems to be grossly overloaded. Awaiting rectification from Rocla. | April | 2013 | 2013Q4 | 2013 | ZN9301:PA13 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2013-04-08 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 17371 | 7669 | 958892 | 2013-04-08 23:47 | 2013-04-09 01:03 | 76 | 11kV | 39064 | 514 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | @Zn14891 Wyong 11kv Pa20 "Warnervale West Railway" fdr tripped on A and B phase overcurrernt and timed Signals: 11kv trip, O/C and E/F EFI's: Nil Cause: Animals/Birds. Possum at PT14949 Railway Country See 959006 exclude 958892 | April | 2013 | 2013Q4 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2013-04-08 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 28546.819
[7 empty] | 17286 | 6953 | 958896 | 2013-04-09 04:46 | 2013-04-09 05:22 | 36 | 11kV | 72 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S5704 Hickson Pottinger - A phase 75 Amp HV fuse blown on TX #1 Transformer failure - restored via Bus Section LV board | April | 2013 | 2013Q4 | 2013 |  |  |  |  | UG | Not Veg | 2013-04-09 | N | 36 | N | 6 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 17588 | 9772 | 959040 | 2013-04-09 10:42 | 2013-04-09 12:45 | 123 | 11kV | 123 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135380 A phase DOLF : 10 Amp Excluded OMS 959040 | April | 2013 | 2013Q4 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-04-09 | N | 123 | N | 6 | N | N | 1.1101 | 39.4971 | 89.8848
[7 empty] | 17945 | 13525 | 958895 | 2013-04-09 03:10 | 2013-04-09 13:55 | 645 | 11kV | 14190 | 22 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S5055 Pacific Beechworth 400A fuse blown on A B and C phase of distributor 3. Cause: Vehicle Hit pole See OMS 959342 958894 958895 | April | 2013 | 2013Q4 | 2013 | ZN195:PA11 | ZN1673:PA21 | ZN01673/000021 | KU-RING-GAI | OH | Not Veg | 2013-04-09 | N | 645 | N | 6 | N | N | 1.1101 | 39.4971 | 10369.6335
[7 empty] | 17284 | 6946 | 959204 | 2013-04-09 15:40 | 2013-04-09 16:29 | 49 | 11kV | 5831 | 119 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 135381 LV Crossarm broken. Urgent repair required to prevent LV into HV. Sub interrupted to repair. Excluded OMS 959204 | April | 2013 | 2013Q4 | 2013 | 242:81541 | 242:81541 | ZN00242/081541 | PORT STEPHENS | OH | Not Veg | 2013-04-09 | N | 49 | N | 6 | N | N | 1.1101 | 39.4971 | 4261.1228
[7 empty] | 17616 | 10263 | 959181 | 2013-04-09 14:47 | 2013-04-09 16:54 | 127 | 11kV | 126038 | 1301 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1193 Lindfield Panel 26 Tripped on Relays: B phase IOC, EFI, Earth Fault and Fault Check Signals: 11kV trip No4 Tx Group Earth Cause: UG fault - 11kV cable See OMS 959640 959644 959645 959181 | April | 2013 | 2013Q4 | 2013 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | UG | Not Veg | 2013-04-09 | N | 96.8778 | N | 6 | N | N | 1.1101 | 39.4971 | 92104.8529
[7 empty] | 17548 | 9149 | 959273 | 2013-04-09 18:52 | 2013-04-09 18:58 | 6 | 11kV | 2004 | 334 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | Ex Zn14144 Wamberal Pa5 @REC44059 Matcham opened and locked out on lockout & O/C trip Abnormal: Closed LB40973; Open SwB S18803 Closed LB40900; Open SwB S18765 Closed REC44059; Open LB40249 MG Connected @ PT12460 Interrupted @ PT14484, PT12131, PT14425, PT13671, PT12109, (sect) @ PT12151 Cause: UGOH fault on commissioing S18826 & S48880 See SAO 311891 Fault beteen SWBS48880 & Open HV UGOH Refer DMA See 968037 Exclude 959273,4,6,7,95,7,8,472 | April | 2013 | 2013Q4 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | Unknown | Unknown | 2013-04-09 | N | 6 | N | 6 | N | N | 1.1101 | 39.4971 | 1464.4641
[7 empty] | 16937 | 3148 | 959303 | 2013-04-10 03:41 | 2013-04-10 04:30 | 49 | 11kV | 2891 | 59 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 135386 A phase DOLF : 31 Amp Possum attack. Excluded OMS No's 959303 & 959304. | April | 2013 | 2013Q4 | 2013 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2013-04-10 | N | 49 | N | 3 | N | N | 1.1101 | 39.4971 | 2112.6575
[7 empty] | 17385 | 7830 | 959348 | 2013-04-10 08:34 | 2013-04-10 14:31 | 357 | 11kV | 714 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135405 Blown DOLF replaced. Tap change on sub. tap 2 to tap 4 No load volts 242V Excluded OMS No. 959348 | April | 2013 | 2013Q4 | 2013 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | UG | Not Veg | 2013-04-10 | N | 357 | N | 3 | N | N | 1.1101 | 39.4971 | 521.7701
[7 empty] | 17058 | 4102 | 959558 | 2013-04-10 13:13 | 2013-04-10 16:55 | 222 | 11kV | 72937 | 933 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 135408 2 fault operations Earth fault Tree down on 11kV. High into low affecting sub 11583. Excluded oms-959558, 959565. | April | 2013 | 2013Q4 | 2013 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Veg | 2013-04-10 | N | 78.1747 | N | 3 | N | N | 1.1101 | 39.4971 | 53300.2083
[7 empty] | 17091 | 4347 | 959904 | 2013-04-11 07:50 | 2013-04-11 12:35 | 285 | 11kV | 570 | 2 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 135419 A & B phase DOLF : 20 Amp HV CONDUCTORS STOLEN BETWEEN POLE JT-10147 & JT-10148 ASH ISLAND. Excluded OMS REPORT NO 959904. | April | 2013 | 2013Q4 | 2013 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2013-04-11 | N | 285 | N | 4 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 16759 | 1707 | 959702 | 2013-04-11 10:30 | 2013-04-11 13:00 | 150 | 11kV | 3900 | 26 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 135422 Car hit sub pole IR-12228 on 10/4/13. Customers interrupted to replace pole following day. Excluded OMS 959702 | April | 2013 | 2013Q4 | 2013 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2013-04-11 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 2850.005
[7 empty] | 18072 | 15525 | 960098 | 2013-04-11 18:37 | 2013-04-11 19:23 | 46 | 11kV | 42964 | 934 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | ZN 3154 - ST IVES - Pnl 10 - All phases Lost At ZN3154 St Ives Panel 10 "Cowan Canoona" Fdr tripped on: C Phase IOC & Times O/C with EFI Field EFI's: All EFI's Down to S4912 Possum on 11kv at PT 1642 "Murdock Sanford" | April | 2013 | 2013Q4 | 2013 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | OH | Not Veg | 2013-04-11 | N | 46 | N | 4 | N | N | 1.1101 | 39.4971 | 31396.824
[7 empty] | 17503 | 8846 | 960124 | 2013-04-11 23:11 | 2013-04-12 00:20 | 69 | 11kV | 7524 | 1812 | HV | Animal Flying Fox | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135430 Trip & reclose 1 fault operation B & C phase Overcurrent 2 tappings burnt off pole IU-70611 tee s-42495 Dead Bat found at Pole IU-70605 Excluded oms 960124, 960125, 960126 | April | 2013 | 2013Q4 | 2013 | 224:80332 | 224:80332 | ZN00224/080332 | LAKE MACQUARIE | OH | Not Veg | 2013-04-11 | N | 4.1523 | N | 4 | N | N | 1.1101 | 39.4971 | 5498.3173
[7 empty] | 17485 | 8648 | 960959 | 2013-04-12 04:34 | 2013-04-12 12:00 | 446 | 11kV | 144131 | 1310 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | ZN 15005 - Belrose - Pnl 8 - OH Wires Down "Belrose West" 8R and "Frenchs Forest" 8L Fdr Tripped Relays: Pnl 8L - ABC phase IOC, Fault Check, EFI Signals: 11kv Trip, Zone Earth Field EFI's: S.46711, S46712 Adnormal Switching - 11kv fdr from LB 22987 to L.2445 tee S.15778 defective with LB 25623 closed Earth wire on 33kv S03 feeder came down panel 8 fdr between L.22412 & L.24367 tee S.46713 Jindabyne Weardon and LV conductors ex S.15542 Burraloo St. See OMS 960943, Restoration - 960963,964,965 | April | 2013 | 2013Q4 | 2013 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Not Veg | 2013-04-12 | N | 110.0237 | N | 5 | N | N | 1.1101 | 39.4971 | 105326.6837
[7 empty] | 17444 | 8265 | 960363 | 2013-04-12 14:00 | 2013-04-12 14:21 | 21 | 11kV | 1764 | 84 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135448 1 fault operation Overcurrent System abnormal for SI 31575. Sw 42462 trip, A/R off. Interrupt subs 61035 & 50856 only. Please patrol fdr. Excluded OMS 960363, 960367, 960372 | April | 2013 | 2013Q4 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2013-04-12 | N | 21 | N | 5 | N | N | 1.1101 | 39.4971 | 1289.0792
[7 empty] | 17665 | 10966 | 960475 | 2013-04-12 20:07 | 2013-04-12 21:40 | 93 | 11kV | 558 | 6 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Transformer | Unplanned | Unselected | N | S.7067 E.C of NSW Burrows - DOo found the TX switch in the OFF position - all fuses OK Cause not ascertained see 961553 961554 | April | 2013 | 2013Q4 | 2013 | ZN2568:PA40 | ZN2568:PA40 | ZN02568/000040 | SYDNEY | UG | Not Veg | 2013-04-12 | N | 93 | N | 5 | N | N | 1.1101 | 39.4971 | 407.7699
[7 empty] | 17762 | 12039 | 960482 | 2013-04-12 21:06 | 2013-04-13 09:55 | 769 | 11kV | 57970 | 538 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN Campsie - Pnl 5 - Earth Fault, Fault check, Field EFIs. UG cable failed in service from S1301 to S 49897. Extended outage at S1301>8hrs. ME: 961967 Rest Steps: 961970, 961974. Withdrawn: 960482, 960485. | April | 2013 | 2013Q4 | 2013 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-04-12 | N | 107.7509 | N | 5 | N | N | 1.1101 | 39.4971 | 42362.7662
[7 empty] | 16548 | 306 | 960471 | 2013-04-12 19:25 | 2013-04-13 14:30 | 1145 | 11kV | 8580 | 21 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | ZN 9301 Kurnell - Pnl 13 - C phase timed. Vehicle broke HV pole in Captain Cook Drive near PT 9934. Master: 961778. Rest steps: 961780. Other: 960471, 961762. | April | 2013 | 2013Q4 | 2013 | ZN9301:PA13 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2013-04-12 | N | 408.5714 | N | 5 | N | N | 1.1101 | 39.4971 | 6270.0109
[7 empty] | 18371 | 18100 | 960614 | 2013-04-14 05:15 | 2013-04-14 07:10 | 115 | 11kV | 115 | 1 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Unselected | N | Ex Pa26L "Sanitarium Sanit No.4" fdr @S14527 Sanitarium Sanit No.2 Tx2 RMI Bph fuse blew EFI: Pa26L, S18537 Cause: Tx fail defective Remarks: Bph tx tails shorted to earth at the tx bushing See 960785 GIS 960784 Exclude 960614 | April | 2013 | 2013Q4 | 2013 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | Unknown | Not Veg | 2013-04-14 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 17296 | 7052 | 960629 | 2013-04-14 07:46 | 2013-04-14 09:20 | 94 | 11kV | 233674 | 3556 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ZN 36300 - Balgowlah North - Pnl 11 - Tree on Fdr Mains At Sub 36300 Balgowlah North panel 11 "Sydney Waratah etc" feeder tripped on: Relays : RHS A&C phases Overcurrent, EFI Signals: 11kv Trip Field EFI's: None Burnt tree Branch found on ground in Rickard St near Brighton St Balgowlad. Burnt off Bond found on UGOH below Sub 46413 Maretimo Audery. Section of Feeder from Sub 46413 Maretimo Audery to LK 21220 is isolated. See Job # 960859 | April | 2013 | 2013Q4 | 2013 | ZN36300:PA11 | ZN36300:PA11 | ZN36300/000011 | NORTHERN BEACHES | OH | Veg | 2013-04-14 | N | 65.7126 | N | 5 | N | N | 1.1101 | 39.4971 | 170762.067
[7 empty] | 17402 | 7961 | 960656 | 2013-04-14 11:25 | 2013-04-14 12:15 | 50 | 11kV | 2800 | 56 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1431 Raven hill Carina Footpath HDO fuse blown. Cause: Fuse fatigue Abnormal Switching: LV Link 12411 Closed and LV Link 26281 Open. See OMS 960995 960656 | April | 2013 | 2013Q4 | 2013 | ZN1673:PA11 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Not Veg | 2013-04-14 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 2046.1574
[7 empty] | 17024 | 3851 | 960683 | 2013-04-14 18:55 | 2013-04-14 20:08 | 73 | 11kV | 111569 | 1601 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 262 Marrickville - Pnl 17 - Earth fault, Field EFIs, Fault check. UG fault between SW/B S 3776 and SW/A 169. | April | 2013 | 2013Q4 | 2013 | ZN262:PA17 | ZN262:PA17 | ZN00262/000017 | INNER WEST | UG | Not Veg | 2013-04-14 | N | 69.6871 | N | 5 | N | N | 1.1101 | 39.4971 | 81531.3345
[7 empty] | 18327 | 17726 | 961762 | 2013-04-14 23:00 | 2013-04-15 00:45 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | S 10914 Harslett Water Board - HDO 20K. Fuse fatigue. Failed in service. Abnormal switching does not affect customer outages. | April | 2013 | 2013Q4 | 2013 |  |  |  | GEORGES RIVER | OH | Not Veg | 2013-04-14 | N | 105 | N | 5 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 17424 | 8141 | 960815 | 2013-04-15 10:32 | 2013-04-15 11:49 | 77 | 11kV | 231 | 3 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2568 St peters Pnl.8 tripped on Earth Fault EFI down @ S35793 UG cable fault suspected from S35793 Griffith Taylor Building to S7244 Education Building | April | 2013 | 2013Q4 | 2013 | ZN2568:PA8 | ZN2568:PA6 | ZN02568/000006 | SYDNEY | UG | Not Veg | 2013-04-15 | N | 77 | N | 8 | N | N | 1.1101 | 39.4971 | 168.808
[7 empty] | 17325 | 7302 | 961063 | 2013-04-15 19:31 | 2013-04-15 20:46 | 75 | 11kV | 14830 | 202 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Electrical Storm | N | LID 135465 3 fault operations 3 phase Earth fault B Horner reports found outgoing link 74434 not closed fully w/ reports of arcing a recloser 74434. Link closed OK B Horner will report to depot AM Tues. dq Excluded OMS 961063, 961065, 961066 & 961068 | April | 2013 | 2013Q4 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-04-15 | N | 73.4158 | N | 8 | N | N | 1.1101 | 39.4971 | 10837.3266
[7 empty] | 16601 | 646 | 961067 | 2013-04-15 19:43 | 2013-04-15 21:55 | 132 | 11kV | 32108 | 298 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | @Zn14143 Somersby 11kv Pa10 CB tripped, reclosed and tripped on; Relays: BCphase overcurrent Signals: nil Cause: Tree/branch on OH Mains Remarks: Tree Branch on OVerhead Mains near USL 43119 See 961271,3,4,5 Exclude 961067 | April | 2013 | 2013Q4 | 2013 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Veg | 2013-04-15 | N | 107.745 | N | 8 | N | N | 1.1101 | 39.4971 | 23463.5794
[7 empty] | 18238 | 16977 | 961087 | 2013-04-15 21:54 | 2013-04-15 22:37 | 43 | 11kV | 39001 | 907 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135467 2 fault operations A & C phase Overcurrent Excluded OMS 961087 | April | 2013 | 2013Q4 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-04-15 | N | 43 | N | 8 | N | N | 1.1101 | 39.4971 | 28500.7805
[7 empty] | 17274 | 6834 | 961093 | 2013-04-15 22:31 | 2013-04-15 22:59 | 28 | 11kV | 22232 | 794 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 135468 2 fault operations C phase Overcurrent Excluded OMS 961093 | April | 2013 | 2013Q4 | 2013 | 216:10728 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Veg | 2013-04-15 | N | 28 | N | 8 | N | N | 1.1101 | 39.4971 | 16246.4899
[7 empty] | 17061 | 4146 | 961086 | 2013-04-15 21:46 | 2013-04-15 23:50 | 124 | 11kV | 70218 | 1006 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zone 1850 Bass Hill 11kv Panel 3 CB Tripped on A phase IOC, Timed, EFI. Field EFI's: S35437, S47459, S7582. Signals 11kv Trip. At LB 49711 Fault Indicator operated. Relays: A+B O/C Detection, Earth Fault Detection. Possible lightning strike near 17 wendy ave as reported by customer. Dop found bat near AB 1782. See 961783, 961786, 961790, 961086,961090. | April | 2013 | 2013Q4 | 2013 | ZN1850:PA3 | ZN1850:PA32 | ZN01850/000032 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-04-15 | N | 69.7992 | N | 8 | N | N | 1.1101 | 39.4971 | 51313.2433
[7 empty] | 16688 | 1137 | 961097 | 2013-04-15 23:12 | 2013-04-16 00:10 | 58 | 11kV | 174 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 135470 Single phase DOLF : 10 Amp Excluded OMS 961097 | April | 2013 | 2013Q4 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | UG | Not Veg | 2013-04-15 | N | 58 | N | 8 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 16895 | 2841 | 961100 | 2013-04-15 23:40 | 2013-04-16 01:05 | 85 | 11kV | 170 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 135471 Single phase DOLF : 10 Amp Excluded OMS 961100 | April | 2013 | 2013Q4 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | UG | Not Veg | 2013-04-15 | N | 85 | N | 8 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 18339 | 17781 | 961151 | 2013-04-16 08:29 | 2013-04-16 09:25 | 56 | 11kV | 56 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Section of Zn12650 West Gosford Pa1 @PT11343 Horticulture Lackersteen C phase HV D/O fuse blown. BBLAS 20Amp Remarks: Cph lightning arrester blown at PT11343. Will require replacement by subs See 962213 exclude 961151 | April | 2013 | 2013Q4 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-04-16 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 18362 | 17999 | 961161 | 2013-04-16 08:43 | 2013-04-16 10:10 | 87 | 11kV | 87 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 135476 Single phase DOLF : 10 Amp arrestor cut away by dop. Excluded OMS 961161 | April | 2013 | 2013Q4 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2013-04-16 | N | 87 | N | 4 | N | N | 1.1101 | 39.4971 | 63.577
[7 empty] | 17399 | 7952 | 962421 | 2013-04-16 16:39 | 2013-04-16 18:07 | 88 | 11kV | 8395 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 135484 2 fault operations 3 phase Earth fault | April | 2013 | 2013Q4 | 2013 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2013-04-16 | N | 87.4479 | N | 4 | N | N | 1.1101 | 39.4971 | 6134.8184
[7 empty] | 18552 | 20363 | 961440 | 2013-04-16 17:19 | 2013-04-16 22:50 | 331 | 11kV | 3411 | 21 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 135486 1 fault operation 3 phase (DOLF : 10 Amp) Eath fault defective surge arrestor at N Strachan sub 73062. Note Bow Reg RAGCB tripped on closing back sub dolf. Excluded OMS 961440 | April | 2013 | 2013Q4 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2013-04-16 | N | 162.4286 | N | 4 | N | N | 1.1101 | 39.4971 | 2492.6582
[7 empty] | 17092 | 4349 | 961936 | 2013-04-18 08:14 | 2013-04-18 09:30 | 76 | 11kV | 5168 | 68 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 47841 - Roadside HV fuse (63K). HV fuse element fatigued and failed. ME: 962336. GIS ME: 961988, 961991, 961948. Withdrawn: 961936, 961977. | April | 2013 | 2013Q4 | 2013 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Not Veg | 2013-04-18 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 3776.622
[7 empty] | 17125 | 4617 | 962009 | 2013-04-18 09:25 | 2013-04-18 13:40 | 255 | 11kV | 1275 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135501 Single phase DOLF : 10 Amp open dt lf 74337 for repairs Excluded oms962009 and 961916 | April | 2013 | 2013Q4 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-04-18 | N | 255 | N | 4 | N | N | 1.1101 | 39.4971 | 931.7324
[7 empty] | 16710 | 1275 | 962391 | 2013-04-18 03:46 | 2013-04-18 17:10 | 804 | 11kV | 164752 | 1223 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | LID 135500 2 fault operations B & C phase Overcurrent Cable box fault pole KS-60071 | April | 2013 | 2013Q4 | 2013 | 229:34989 | 233:82815 | ZN00233/082815 | PORT STEPHENS | Unknown | Not Veg | 2013-04-18 | N | 134.7114 | N | 4 | N | N | 1.1101 | 39.4971 | 120395.9022
[7 empty] | 17682 | 11345 | 962256 | 2013-04-18 16:56 | 2013-04-18 18:20 | 84 | 11kV | 65700 | 954 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At ZN3472 Sefton 11kv Panel 15 CB tripped on: 11kv trip, group earth, I.O.C, B & C phase SEL, Lockout and timer, EFI, Fault check relay. Field EFI's: S.5741, EFI @ Carlingford Rd East Guelph St defective, EFI @ Carlingford Rd near Clapham Rd defective. Cause: UGOH fault short circuit - phase to earth. Section of feeder between S5741 to S8241 to S6040 to AB888 (refer DMA). LV parallels - USL. 3844, 11663, 14588. See 962481 962483 962256 962262(GIS error) 962263(GIS error) 962276(GIS error) 962281(GIS error) | April | 2013 | 2013Q4 | 2013 | ZN3472:PA15 | ZN35900:PA2 | ZN35900/000002 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2013-04-18 | N | 68.8679 | N | 4 | N | N | 1.1101 | 39.4971 | 48011.6222
[7 empty] | 16593 | 585 | 962318 | 2013-04-19 07:28 | 2013-04-19 12:20 | 292 | 11kV | 292 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | LID 135524 B & C phase : DOLF 10 Amp Replaced fuse & carriers. Excluded OMS 962318 | April | 2013 | 2013Q4 | 2013 | 232:11460 | 232:11460 | ZN00232/011460 | PORT STEPHENS | OH | Not Veg | 2013-04-19 | N | 292 | N | 2 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 17989 | 14142 | 962515 | 2013-04-19 12:57 | 2013-04-19 19:15 | 378 | 11kV | 35622 | 185 | HV | Fire (non-electrical) | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Wind | N | AtZn14144 Wamberal 11kv feeder Pa10 opened by AOp, due to HV down causing grass fires in Brush Rd Wamberal. Note: 11kv O/H mains on ground. SEL Failed to operate. TPE to investigate Abnormal:DMA section of Feeder S48880 to broken away UGOH; Closed LB40900; Opened SwBS18764 Entrance Serpentine No.2; Closed REC44059 Cause: Bushfire Remarks: HV in brush rd, down. Section of 11kv fdr from S18802/B to S18803/B tee PT12460, tee S18826, tee S48880, tee PT14484, tee PT13671, tee PT12109. See 965400,1 exclude 962552 | April | 2013 | 2013Q4 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2013-04-19 | N | 192.5514 | N | 2 | N | N | 1.1101 | 39.4971 | 26031.5069
[7 empty] | 18436 | 18963 | 962750 | 2013-04-20 04:03 | 2013-04-20 09:00 | 297 | 11kV | 63837 | 641 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | At ZN9037 Miranda, Panel 7 "Bates Drive" Feeder tripped on Relays: C Phase IOC. Signals: 11kv Trip. Cause: Pole top fire o/s 85 Rival St Kareela. Repaired by mains. See 963261 963263 excl. 962750 962751 962753 962754 | April | 2013 | 2013Q4 | 2013 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2013-04-20 | N | 99.5897 | N | 7 | N | N | 1.1101 | 39.4971 | 46650.1967
[7 empty] | 17429 | 8166 | 962843 | 2013-04-20 11:26 | 2013-04-20 12:30 | 64 | 11kV | 20928 | 327 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | REC - 22381- Lane Cove Walter Tripped on: O/C Trip, IOC Trip, Lockout Section of 11kv Fdr exiting Pnl 14 labelled "S.16938 & S.17022 - Walana Mona" fd. @ Mona Vale Zone. Tree Branch on Mains adjacent USL 20431 | April | 2013 | 2013Q4 | 2013 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2013-04-20 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 15293.5651
[7 empty] | 17841 | 12641 | 962809 | 2013-04-20 10:00 | 2013-04-20 13:25 | 205 | 11kV | 22423 | 198 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 135532 Overcurrent Faulty lightning arrestor on recloser 74441 Excluded OMS 962809 | April | 2013 | 2013Q4 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2013-04-20 | N | 113.2475 | N | 7 | N | N | 1.1101 | 39.4971 | 16386.067
[7 empty] | 16705 | 1249 | 962889 | 2013-04-20 12:52 | 2013-04-20 13:40 | 48 | 11kV | 2832 | 59 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Rain Heavy | N | LID 135534 C phase DOLF : 31 Amp Dead Possum Volts = 248 Amps = 70/100/190 Excluded OMS 962889, 962892 | April | 2013 | 2013Q4 | 2013 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | OH | Not Veg | 2013-04-20 | N | 48 | N | 7 | N | N | 1.1101 | 39.4971 | 2069.5421
[7 empty] | 17463 | 8431 | 962937 | 2013-04-20 15:05 | 2013-04-20 15:34 | 29 | 11kV | 40397 | 1393 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 135535 1 fault operation B & C phase Overcurrent Tree branch across 11kV OHM near ABS 43311 Excluded oms 962937, 962938 | April | 2013 | 2013Q4 | 2013 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Veg | 2013-04-20 | N | 29 | N | 7 | N | N | 1.1101 | 39.4971 | 29520.9361
[7 empty] | 17180 | 5553 | 962921 | 2013-04-20 14:19 | 2013-04-20 16:00 | 101 | 11kV | 243376 | 3064 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S35500 Top Ryde Panel 28L Tripped and Locked out on A and C phase Timed O/C Reclose Timer Lockout 11kV Trip. Cause: Tree branch fell on 11kV feeder. 962948 963474 962947 962946 962932 962930 962929 962928 963476 962923 962922 962921 962933 963471 | April | 2013 | 2013Q4 | 2013 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Veg | 2013-04-20 | N | 79.4308 | N | 7 | N | N | 1.1101 | 39.4971 | 177852.0024
[7 empty] | 17634 | 10605 | 962951 | 2013-04-20 15:33 | 2013-04-20 17:35 | 122 | 11kV | 122 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Rain Heavy | N | LID 135536 B & C phase DOLF : 5 Amp LVF B phase replaced 100amps. Customer service cut away and capped. Pole came down. Excluded oms 962951 | April | 2013 | 2013Q4 | 2013 | 235:2121 | 235:8684 | ZN00235/008684 | NEWCASTLE | Unknown | Not Veg | 2013-04-20 | N | 122 | N | 7 | N | N | 1.1101 | 39.4971 | 89.154
[7 empty] | 17259 | 6621 | 963122 | 2013-04-21 15:17 | 2013-04-21 16:35 | 78 | 11kV | 78 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135540 A phase DOLF : 10 Amp Excluded OMS 963122 | April | 2013 | 2013Q4 | 2013 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | UG | Not Veg | 2013-04-21 | N | 78 | N | 1 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 16933 | 3139 | 963438 | 2013-04-22 12:34 | 2013-04-22 15:30 | 176 | 11kV | 4172 | 112 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 135547 Reports of a backhoe and mains down at sub 73227 | April | 2013 | 2013Q4 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-04-22 | N | 37.25 | N | 3 | N | N | 1.1101 | 39.4971 | 3048.7745
[7 empty] | 17542 | 9071 | 963589 | 2013-04-22 19:20 | 2013-04-22 20:40 | 80 | 11kV | 69640 | 1689 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At ZN9700 Kirrawee, 11kv Feeder Panel #23 "S9819 Talara Kingsway" Tripped on Bazler Relay 50TN (Instantaneous earth fault over-current) 51C (Time delayed phase overcurrent) EFI. Cause: Possum on UGOH adj 41 Ellesmere Rd. See 964172 964173 964176 963596 963598 963600 963601 963597 exclude 963599 963606 963589 963590 | April | 2013 | 2013Q4 | 2013 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2013-04-22 | N | 41.2315 | N | 3 | N | N | 1.1101 | 39.4971 | 50890.858
[7 empty] | 18487 | 19743 | 963614 | 2013-04-22 23:35 | 2013-04-23 00:50 | 75 | 11kV | 58650 | 782 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN 342 Paddington 11kv panel 35 "s4371 Clement Waratah" Feeder Tripped on Earth Fault, EFI Signals:11kv trip, zone earth, no.4 group earth. Field EFI's: nil. Cause: U/G Fault. Suspect U/G cable fault between ZN 342 Paddington to S4371 "Clement Waratah" SW/A to S1681 "New South Rushcutters" SW/F. Dop restored power from SW/B S2317 to S4371 See 964533 exclude 963614 | April | 2013 | 2013Q4 | 2013 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2013-04-22 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 42859.6901
[7 empty] | 16772 | 1811 | 963619 | 2013-04-23 05:30 | 2013-04-23 09:16 | 226 | 11kV | 1808 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT13835 Cullens Wongari footpath HDO fuse operated Cause: Fuse fatigue See OMS 964062 963619 | April | 2013 | 2013Q4 | 2013 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2013-04-23 | N | 226 | N | 6 | N | N | 1.1101 | 39.4971 | 1321.2331
[7 empty] | 16825 | 2185 | 963621 | 2013-04-23 06:25 | 2013-04-23 09:29 | 184 | 11kV | 290080 | 1580 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135550 B & C phase Overcurrent; Earth fault | April | 2013 | 2013Q4 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2013-04-23 | N | 183.5949 | N | 6 | N | N | 1.1101 | 39.4971 | 211981.9081
[7 empty] | 17046 | 4001 | 963616 | 2013-04-23 02:52 | 2013-04-23 10:16 | 444 | 11kV | 12885 | 97 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Pa1 Recloser 61364 Brieses peats 0.4 Tripped and locked out on O/C Cause: Large tree in 11kV OH + 33kV 720 FDR Tree bought down OH See OMS 964124 964126 963616 | April | 2013 | 2013Q4 | 2013 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2013-04-23 | N | 132.8351 | N | 6 | N | N | 1.1101 | 39.4971 | 9415.978
[7 empty] | 18513 | 19987 | 963623 | 2013-04-23 06:44 | 2013-04-23 12:50 | 366 | 11kV | 10458 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135551 Earth fault broke OHM at pole FO-70301 | April | 2013 | 2013Q4 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-04-23 | N | 186.75 | N | 6 | N | N | 1.1101 | 39.4971 | 7642.3979
[7 empty] | 16847 | 2314 | 963961 | 2013-04-23 17:52 | 2013-04-23 19:39 | 107 | 11kV | 128204 | 1399 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah Nth, Panel 17 Fdr CB tripped on B and C phase IOC, with 11kV trip signal. | April | 2013 | 2013Q4 | 2013 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Veg | 2013-04-23 | N | 91.6397 | N | 6 | N | N | 1.1101 | 39.4971 | 93687.7018
[7 empty] | 16845 | 2311 | 964027 | 2013-04-23 18:54 | 2013-04-23 23:00 | 246 | 11kV | 2984 | 44 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 135568 BROKEN CROSS ARM AT POLE WB-72921. Excluded OMS REPORT NO 963974. | April | 2013 | 2013Q4 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-04-23 | N | 67.8182 | N | 6 | N | N | 1.1101 | 39.4971 | 2180.6192
[7 empty] | 16697 | 1218 | 963996 | 2013-04-24 07:16 | 2013-04-24 07:55 | 39 | 11kV | 23595 | 605 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn.3154 St Ives, Panel 13 Fdr CB tripped on A and B phase IOC and timed OC, 11kV trip. Tree branch on OH mains O/S 20 Clissold St. Tree branch removed and voltage checked at S.4728 - OK | April | 2013 | 2013Q4 | 2013 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | OH | Veg | 2013-04-24 | N | 39 | N | 5 | N | N | 1.1101 | 39.4971 | 17242.5301
[7 empty] | 16657 | 976 | 963989 | 2013-04-24 02:15 | 2013-04-24 09:40 | 445 | 11kV | 33968 | 126 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135569 2 fault operations 11Kv OHM down to S-50978 Excluded OMS 963989 | April | 2013 | 2013Q4 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-04-24 | N | 269.5873 | N | 5 | N | N | 1.1101 | 39.4971 | 24822.8125
[7 empty] | 17301 | 7102 | 963993 | 2013-04-24 07:01 | 2013-04-24 13:50 | 409 | 11kV | 409 | 1 | HV | Equipment Failed in Service | Equipment Failure | Feeder/Distributor U/G | Unplanned | Unselected | N | At CP.587 Princes GEC, tee off tripped on B phase HV fuse OQFRN 71 amp. Cause: U/G cable fault. HV B phase fuse striker pin snapped, TX switch did not trip. 11kv feeder from S897 "Chisolm Princes (SW/B) to S3863 "Melissa St" (SW/A) via CP 587 "Princes GEC" and including TX at "S3768 Princes GEC" is Isolated and Earthed. MG connected to customers board. T/Con to inspect RMI after test. See 964480 exclude 963993 | April | 2013 | 2013Q4 | 2013 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | UG | Not Veg | 2013-04-24 | N | 409 | N | 5 | N | N | 1.1101 | 39.4971 | 298.8851
[7 empty] | 16830 | 2211 | 964359 | 2013-04-24 21:28 | 2013-04-24 22:22 | 53.9167 | 11kV | 7335.85 | 194 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 135579 UG cable fault Excluded OMS 964359 | April | 2013 | 2013Q4 | 2013 | 208:71 | 257:81994 | ZN00257/081994 | NEWCASTLE | UG | Not Veg | 2013-04-24 | N | 37.8137 | N | 5 | N | N | 1.1101 | 39.4971 | 5360.8228
[7 empty] | 18143 | 16042 | 964358 | 2013-04-24 21:29 | 2013-04-24 22:23 | 54 | 11kV | 432 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn14891 Wyong Pa12 @PT13819 Yarramlong Maitland 1.5 Footpath 11kv 16Amp HVDO fuse operated Cause: Fuse Fatigue Remarks: Possible fuse fatigue. Nothing found. DOp could not read MDI See 966253 exclude 964358 | April | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-04-24 | N | 54 | N | 5 | N | N | 1.1101 | 39.4971 | 315.6929
[7 empty] | 18062 | 15437 | 964628 | 2013-04-26 12:05 | 2013-04-26 12:09 | 4 | 11kV | 10128 | 2532 | HV | Staff Operation | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | At Zn116 Leichhardt, 11KV CB Panel 50 'S.2670 Wisdom Young' feeder TRIPPED on: Relays: Earth fault, EFI Signals: 11kv trip Field EFI's: S2670, S15, S35778, S5770, S2561, S3822 Abnormal: SW/B Closed @ S5770 Boyce St West. SW/B Open @ S3822 Glebe Point Rd Remarks: Staff error - details below. At S.3822 Glebe Point Rd, Dop closed fdr SW/B onto an earthed feeder. Related jobs: #965539, 964628, 965530 | April | 2013 | 2013Q4 | 2013 | ZN116:PA50 | ZN116:PA25 | ZN00116/000025 | INNER WEST | UG | Not Veg | 2013-04-26 | N | 4 | N | 5 | N | N | 1.1101 | 39.4971 | 7401.2437
[7 empty] | 17984 | 14130 | 964617 | 2013-04-26 11:51 | 2013-04-26 14:47 | 176 | 11kV | 60428 | 1587 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 135589 2 fault operations A & B phase Overcurrent Excluded OMS 963617, 964624, 964645 | April | 2013 | 2013Q4 | 2013 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | OH | Not Veg | 2013-04-26 | N | 38.0769 | N | 5 | N | N | 1.1101 | 39.4971 | 44159.0001
[7 empty] | 18540 | 20255 | 964666 | 2013-04-26 13:40 | 2013-04-26 16:00 | 140 | 11kV | 102117 | 1023 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills Panel 43 tripped on Relays: O/C and E?F Trip. EFI. Cause; UG cable fault Between S3205 and S5296 to S6712 See OMS 965096 965097 965098 964666 | April | 2013 | 2013Q4 | 2013 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | UG | Not Veg | 2013-04-26 | N | 99.8211 | N | 5 | N | N | 1.1101 | 39.4971 | 74624.0917
[7 empty] | 16765 | 1737 | 964761 | 2013-04-26 17:30 | 2013-04-26 20:02 | 152 | 11kV | 1216 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT14145 Kowoong Noamunga the B Phase fuse was found open Cause: B phase HDO assmebly broken See 966268 exclude 964761,7 | April | 2013 | 2013Q4 | 2013 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2013-04-26 | N | 152 | N | 5 | N | N | 1.1101 | 39.4971 | 888.6169
[7 empty] | 17422 | 8134 | 965132 | 2013-04-26 22:35 | 2013-04-27 00:54 | 139 | 11kV | 95564 | 817 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 135592 3 fault operations A phase Earth fault, Overcurent Possum at UGOH MQ-10137 Excluded OMS 964799 | April | 2013 | 2013Q4 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2013-04-26 | N | 116.9694 | N | 5 | N | N | 1.1101 | 39.4971 | 69835.3525
[7 empty] | 17965 | 13808 | 964805 | 2013-04-27 01:06 | 2013-04-27 02:40 | 93.7667 | 11kV | 11908.3667 | 127 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 10215 Edgbaston Penshurst - Footpath side HDO (50A). Fuse failed in service and operated. ME: 964806 Withdrawn: 964805 | April | 2013 | 2013Q4 | 2013 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2013-04-27 | N | 93.7667 | N | 6 | N | N | 1.1101 | 39.4971 | 8702.2831
[7 empty] | 18215 | 16731 | 964813 | 2013-04-27 07:09 | 2013-04-27 08:25 | 76.1167 | 11kV | 2131.2667 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135594 A & B phase DOLF : 20 Amp cursory patrol carried out by dop no cause found CC1: 22-"Refer to SOp" | April | 2013 | 2013Q4 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2013-04-27 | N | 76.1167 | N | 6 | N | N | 1.1101 | 39.4971 | 1557.4668
[7 empty] | 16677 | 1101 | 965207 | 2013-04-27 09:40 | 2013-04-27 11:04 | 84 | 11kV | 84935 | 1117 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135596 2 fault operation A & C phase Overcurrent cursory patrol by dop no cause found dq Excluded OMS 964846 | April | 2013 | 2013Q4 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2013-04-27 | N | 76.0385 | N | 6 | N | N | 1.1101 | 39.4971 | 62067.9928
[7 empty] | 16570 | 469 | 964870 | 2013-04-27 12:04 | 2013-04-27 14:00 | 116 | 11kV | 6148 | 53 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 9692 Ellis St - Centre Phase HDO. Fuse failed in service and operated. ME: 965112 Withdrawn: 964870 | April | 2013 | 2013Q4 | 2013 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2013-04-27 | N | 116 | N | 6 | N | N | 1.1101 | 39.4971 | 4492.7771
[7 empty] | 18191 | 16522 | 964933 | 2013-04-27 20:32 | 2013-04-27 21:56 | 84 | 11kV | 17165 | 205 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S35335 Riyal North Shore Hospital Panel 14 51C, EFI. Cable Fault: Between S5174 to S5172 to S829 See OMS 965102 964933 | April | 2013 | 2013Q4 | 2013 | ZN35335:PA14 | ZN35335:PA14 | ZN35335/000014 | LANE COVE | UG | Not Veg | 2013-04-27 | N | 83.7317 | N | 6 | N | N | 1.1101 | 39.4971 | 12543.6757
[7 empty] | 17389 | 7865 | 964945 | 2013-04-27 21:14 | 2013-04-27 22:00 | 46 | 11kV | 3634 | 79 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | @PT48408 St Georges Lakala the roadside HV 3A Fuse operated Cause: Fuse Fatigue See 966276 GIS 966278 Exclude 964945,8,9 | April | 2013 | 2013Q4 | 2013 | ZN12580:PA16 | ZN12580:PA8 | ZN12580/000008 | CENTRAL COAST | OH | Not Veg | 2013-04-27 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 2655.62
[7 empty] | 18310 | 17534 | 965031 | 2013-04-28 15:35 | 2013-04-28 16:27 | 52 | 11kV | 78638 | 1666 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10999 Kogarah - Pnl 4 - trip/reclose/trip, 50 T A B & C, Field EFI. 11kV UGOH to S 10063 failed in service. ME: 965118 RS: 965119, 120 Withdrawn: 965031, 032, 033, 037 | April | 2013 | 2013Q4 | 2013 | ZN10999:PA4 | ZN10999:PA4 | ZN10999/000004 | GEORGES RIVER | Unknown | Unknown | 2013-04-28 | N | 47.2017 | N | 2 | N | N | 1.1101 | 39.4971 | 57466.331
[7 empty] | 17744 | 11911 | 965064 | 2013-04-28 22:16 | 2013-04-28 23:08 | 51.7167 | 11kV | 26582.3667 | 514 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | Unselected | N | Zn14891 Wyong Pa20 "Warnervale West Railway" fdr tripped Relays: A & B phase overcurrent, EFI Signals: 11kv trip EFI: S18534 S18246 Remarks: Possum came into contact with 11kv mains at Recloser 45070 Sparks rd. OK to energise, however the DOp recommends inspection by overhead in the morning See 965064 Exclude 965065,7 | April | 2013 | 2013Q4 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2013-04-28 | N | 51.7167 | N | 2 | N | N | 1.1101 | 39.4971 | 19425.6095
[7 empty] | 17295 | 7034 | 965305 | 2013-04-29 13:24 | 2013-04-29 15:05 | 101 | 11kV | 38634 | 658 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9252 Jannali - Pnl 3 - Trip/reclose/trip, A phase IOC, Lockout, timer, EFI. Suspect fault between S 9034 to LB 46625 to AB 35837 tee S 9781. ME: 966025 RS: 966026 Withdrawn: 965305 | April | 2013 | 2013Q4 | 2013 | ZN9252:PA3 | ZN9252:PA28 | ZN09252/000028 | SUTHERLAND | UG | Not Veg | 2013-04-29 | N | 58.7143 | N | 2 | N | N | 1.1101 | 39.4971 | 28232.5877
[7 empty] | 16704 | 1248 | 965464 | 2013-04-29 17:28 | 2013-04-30 01:25 | 477 | 11kV | 10335 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135607 3 fault operations Earth fault Wire off pin at CF-80029 | April | 2013 | 2013Q4 | 2013 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2013-04-29 | N | 313.1818 | N | 2 | N | N | 1.1101 | 39.4971 | 7552.5132
[7 empty] | 16680 | 1118 | 965544 | 2013-04-30 10:41 | 2013-04-30 12:01 | 80 | 11kV | 156279 | 2027 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn12570 Avoca Pa37L fdr tripped Signals: 11kv trip Relays: Bph IC, EFI EFI: S18439 S49066 S18135 Contractors found digging adjacent to UGOH below S18135 Townsend Avoca Bowling. Contractor error caused failure See 966304,6 Exclude 965544 | April | 2013 | 2013Q4 | 2013 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | UG | Not Veg | 2013-04-30 | N | 77.0987 | N | 2 | N | N | 1.1101 | 39.4971 | 114204.0837
[7 empty] | 18039 | 14934 | 965868 | 2013-04-30 18:40 | 2013-04-30 19:45 | 65 | 11kV | 585 | 9 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 135624 Crossarm hanging off Pole AK 32138 Excluded OMS 965894 | April | 2013 | 2013Q4 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-04-30 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 427.5007
[7 empty] | 17188 | 5725 | 965998 | 2013-05-01 09:00 | 2013-05-01 11:00 | 120 | 11kV | 10440 | 87 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | No Weather Impact | N | LID 135635 See Outage Request 32000. Customers at Northminster Way sub not notified of outage by Lend Lease (Contractor), as per request. Planned outage report #135634 for customers at Hadleigh Rd sub. Excluded OMS 965998 | May | 2013 | 2013Q4 | 2013 | 239:82128 | 239:82128 | ZN00239/082128 | LAKE MACQUARIE | UG | Not Veg | 2013-05-01 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 7629.2441
[7 empty] | 17513 | 8913 | 966528 | 2013-05-01 19:34 | 2013-05-01 20:58 | 84 | 11kV | 106848 | 1272 | HV | Animal Possum | Animal | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 135637 2 fault operations Overcurrent G. Woodland reported explosion at ELB 2444. DOP found possum across Bph. Fdr opened to allow DOP to remove possum from equipment. Daylight inspection required LA's may be damaged. Excludes OMS 966529 restore time corrected percontrol room report | May | 2013 | 2013Q4 | 2013 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2013-05-01 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 78081.3669
[7 empty] | 18246 | 17050 | 966348 | 2013-05-01 17:36 | 2013-05-01 22:30 | 294 | 11kV | 4116 | 14 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135638 A phase 11kV tapping off at Line DOLF 42863 Excluded OMS 966348 | May | 2013 | 2013Q4 | 2013 | 503:48011 | 508:82576 | ZN00508/082576 | MAITLAND | OH | Not Veg | 2013-05-01 | N | 294 | N | 3 | N | N | 1.1101 | 39.4971 | 3007.8514
[7 empty] | 17248 | 6524 | 966903 | 2013-05-02 19:35 | 2013-05-02 20:55 | 80 | 11kV | 1360 | 17 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135654 Section isolated to repair broken DOLF dropper at sub 21810. Excluded OMS 966903. | May | 2013 | 2013Q4 | 2013 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2013-05-02 | N | 80 | N | 1 | N | N | 1.1101 | 39.4971 | 993.8479
[7 empty] | 16991 | 3508 | 967099 | 2013-05-03 11:30 | 2013-05-03 14:45 | 195 | 11kV | 390 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135668 B phase No blown fuse cable connecting to DOLF had burnt off. Excluded OMS # 967099. | May | 2013 | 2013Q4 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-05-03 | N | 195 | N | 3 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 17768 | 12072 | 967162 | 2013-05-03 14:22 | 2013-05-03 16:40 | 138 | 11kV | 120940 | 1191 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | @zn12610 Long Jetty Pa17 fdr tripped and locked out Relays: OC and EF, Timing, LO, FC, EFI Signals:11kv trip EFI's: S14943 Cause: ABC Cable fault between USL40219 and AB40218, Fault in bundled ABC in tee off to PT13061. Secondary problems were a burnt bond near tree to PT11020 and another burnt bond @ USL40219 See 972969,71,2,3 Exclude 967162,77,95 | May | 2013 | 2013Q4 | 2013 | ZN12610:PA17 | ZN12610:PA17 | ZN12610/000017 | CENTRAL COAST | OH | Not Veg | 2013-05-03 | N | 101.5449 | N | 3 | N | N | 1.1101 | 39.4971 | 88379.3849
[7 empty] | 18190 | 16495 | 967220 | 2013-05-03 17:03 | 2013-05-03 22:43 | 340 | 11kV | 73316 | 233 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 135669 3 fault operations C phase Fault in UGM to Sw 90369 Blown tapping at pole JU-30050 PWCL Sw 91144 C phase O/C | May | 2013 | 2013Q4 | 2013 | 203:8089 | 204:82703 | ZN00204/082703 | NEWCASTLE | UG | Not Veg | 2013-05-03 | N | 314.6609 | N | 3 | N | N | 1.1101 | 39.4971 | 53577.1703
[7 empty] | 17798 | 12378 | 967368 | 2013-05-05 00:34 | 2013-05-05 10:15 | 581 | 11kV | 5810 | 10 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | Ex Zn14144 Wamberal Pa10 @PT11568 Milina Matcham 0.3 Footpath Phase 16A HDO fuse operated Relays: EFI Signals: Tx2 Group Earth No Field EFI's Remarks: Possum committed Harakiri See 967558 Exclude 967368,9,71,82 | May | 2013 | 2013Q4 | 2013 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2013-05-05 | N | 581 | N | 3 | N | N | 1.1101 | 39.4971 | 4245.7766
[7 empty] | 17433 | 8192 | 967439 | 2013-05-05 15:24 | 2013-05-05 15:41 | 17 | 11kV | 1411 | 83 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At recloser 24722 tripped; earth fault Trip 1, C phase OC, earth fault. Lockout. Suspect 11kV fault in new joint works. Recloser 24722 tripped on energising new work from LB.63021 | May | 2013 | 2013Q4 | 2013 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | UG | Not Veg | 2013-05-05 | N | 17 | N | 3 | N | N | 1.1101 | 39.4971 | 1031.1172
[7 empty] | 17853 | 12733 | 967484 | 2013-05-05 21:45 | 2013-05-05 22:28 | 43 | 11kV | 33454 | 778 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S80 Chatswood Panel 27 tripped on A and C phase IOC and Fault Check with EFI. At S5582 Moriaty Pacific SW/B side of RMI failed See OMS 967685 967684 967484 967485 | May | 2013 | 2013Q4 | 2013 | ZN80:PA27 | ZN80:PA27 | ZN00080/000027 | WILLOUGHBY | UG | Not Veg | 2013-05-05 | N | 43 | N | 3 | N | N | 1.1101 | 39.4971 | 24447.1965
[7 empty] | 17023 | 3850 | 967495 | 2013-05-06 05:24 | 2013-05-06 07:15 | 111 | 11kV | 179791 | 2046 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 398 Dulwich Hill - Pnl 16 - A phase IOC, Timed OC, EFIs. Underground cable fault between S2023, S1823 tee 1499. ME: 968924 RS: 968927 Withdrawn: 967495, 967497 | May | 2013 | 2013Q4 | 2013 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2013-05-06 | N | 87.8744 | N | 6 | N | N | 1.1101 | 39.4971 | 131385.9599
[7 empty] | 16990 | 3501 | 967537 | 2013-05-06 12:40 | 2013-05-06 15:05 | 145 | 11kV | 580 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 135684 A phase BROKEN HV DOLF BASE. Excluded OMS REPORT NO 967537 | May | 2013 | 2013Q4 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-05-06 | N | 145 | N | 6 | N | N | 1.1101 | 39.4971 | 423.8469
[7 empty] | 16740 | 1530 | 967511 | 2013-05-06 06:57 | 2013-05-06 16:31 | 574.3667 | 11kV | 4020.5667 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | No LID report found Blown 11kV bond feeding into Essential Energy's area CE customers effected. | May | 2013 | 2013Q4 | 2013 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2013-05-06 | N | 574.3667 | N | 6 | N | N | 1.1101 | 39.4971 | 2938.1115
[7 empty] | 17868 | 12860 | 967896 | 2013-05-06 18:00 | 2013-05-06 18:35 | 35 | 11kV | 70 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135688 A phase BROKEN LIVE LINE LEAD. Excluded OMS REPORT NO 967901. | May | 2013 | 2013Q4 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-05-06 | N | 35 | N | 6 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 18431 | 18937 | 968955 | 2013-05-06 18:13 | 2013-05-06 18:55 | 42 | 11kV | 34544 | 1052 | HV | Animal Flying Fox | Animal | DC PT | Unplanned | Wind | N | ZN 9550 Gwawley Bay - Pnl 43 - A & B phase Overcurrent. Dead bat found near PT 9483. 11kV bond burnt off on tee to PT 9483. ME: 968955 RS: 968956 Withdrawn: 967925, 967924, 967922 | May | 2013 | 2013Q4 | 2013 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2013-05-06 | N | 32.8365 | N | 6 | N | N | 1.1101 | 39.4971 | 25243.7363
[7 empty] | 18288 | 17358 | 967933 | 2013-05-06 19:45 | 2013-05-06 20:15 | 30 | 11kV | 30 | 1 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 135689 A & B phase DOLF : 16 Amp GALAH ON SUB. Excluded OMS REPORT NO 967933. | May | 2013 | 2013Q4 | 2013 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2013-05-06 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 16748 | 1581 | 968368 | 2013-05-07 17:00 | 2013-05-07 17:50 | 50 | 11kV | 20763 | 441 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.711 Blackwattle bay Pnl.15 tripped on earth fault, EFI UG cable fault between Pnl.15 ex Blackwattle Bay and Sw A @ S7527 Jones Mary Anne and Sw F @ S7026 Murray Pyrmont see 968929 968928 | May | 2013 | 2013Q4 | 2013 | ZN711:PA15 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2013-05-07 | N | 47.0816 | N | 2 | N | N | 1.1101 | 39.4971 | 15172.988
[7 empty] | 18372 | 18107 | 968419 | 2013-05-07 23:40 | 2013-05-08 00:36 | 56 | 11kV | 4088 | 73 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 135702 2 fault operations 3 phase Overcurrent Probable conductor clash Excluded OMS 968419 & 968420 | May | 2013 | 2013Q4 | 2013 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2013-05-07 | N | 56 | N | 2 | N | N | 1.1101 | 39.4971 | 2987.3898
[7 empty] | 17827 | 12533 | 975214 | 2013-05-08 01:12 | 2013-05-08 07:30 | 378 | 11kV | 170344 | 1683 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S5868 Gore Hill Panel 30 tripped on B phase OC and Earth fault, EFI and Fault Check relay Cause: Suspect UG fault S8527 to S5172 See OMS 975214 975216 975217 | May | 2013 | 2013Q4 | 2013 | ZN5868:PA30 | ZN5868:PA30 | ZN05868/000030 | LANE COVE | UG | Not Veg | 2013-05-08 | N | 101.2145 | N | 4 | N | N | 1.1101 | 39.4971 | 124482.3709
[7 empty] | 18382 | 18256 | 968441 | 2013-05-08 05:56 | 2013-05-08 08:25 | 148.8 | 11kV | 148.8 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | S 10914 Harslett Water Board - Roadside HDO (40K). One phase down on High voltage supply due to fuse failure because of fatigue. CC1: 22-"Refer to SOp" FRC1: 329-"High Voltage Fuse - Requires replacement" | May | 2013 | 2013Q4 | 2013 |  |  |  | GEORGES RIVER | OH | Not Veg | 2013-05-08 | N | 148.8 | N | 4 | N | N | 1.1101 | 39.4971 | 108.7387
[7 empty] | 16997 | 3538 | 968618 | 2013-05-08 10:50 | 2013-05-08 11:40 | 50 | 11kV | 900 | 18 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135712 Section of 11kv OHM isolated to repair stranding wires near pole WB-84610. Excluded OMS No. 968618 | May | 2013 | 2013Q4 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-05-08 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 657.6935
[7 empty] | 17003 | 3599 | 968433 | 2013-05-08 05:00 | 2013-05-08 13:30 | 510 | 11kV | 62220 | 122 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 135704 Three pases off pins pole IV-10720 Subs 12710 & 21597 held in LV parrallel | May | 2013 | 2013Q4 | 2013 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2013-05-08 | N | 510 | N | 4 | N | N | 1.1101 | 39.4971 | 45468.5408
[7 empty] | 17038 | 3965 | 968918 | 2013-05-09 07:32 | 2013-05-09 08:48 | 76 | 11kV | 48866 | 851 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12660 Woy Woy 11kV VCB Pa16 "St Huberts" fdr tripped on: Relays: Earth Fault, EFI EFI's: S14604 S11459 S11458 Signals: 11kv trip Remarks: Suspect UG Fault between S11458 Nautilus Attunga S11242 Salacia Helmsman See 969339,41,3 Exclude 968918,30,2 | May | 2013 | 2013Q4 | 2013 | ZN12660:PA16 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | UG | Not Veg | 2013-05-09 | N | 57.4219 | N | 3 | N | N | 1.1101 | 39.4971 | 35709.8315
[7 empty] | 18147 | 16062 | 968943 | 2013-05-09 08:25 | 2013-05-09 09:29 | 64 | 11kV | 104838 | 1686 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135717 11kV system abnormal due to SI 32341. Customers off Fdrs 48031 & 48033 interrupted. Excluded OMS No. 968944+968943+968946+968953 | May | 2013 | 2013Q4 | 2013 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2013-05-09 | N | 62.1815 | N | 3 | N | N | 1.1101 | 39.4971 | 76612.5182
[7 empty] | 17297 | 7085 | 969207 | 2013-05-09 15:29 | 2013-05-09 16:45 | 76 | 11kV | 70832 | 932 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | See DNMS Log. @ Zn 2196 Milperra, 11KV feeder panel No.18 "S.4859 Lachlan Cant" TRIPPED on: 11kv trip, IOC, B & C phase Remarks: tree/branch on OH mains. Tree branch Eldridge Rd near Mons. Related jobs: #969207, 970011 | May | 2013 | 2013Q4 | 2013 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-05-09 | N | 76 | N | 3 | N | N | 1.1101 | 39.4971 | 51761.9364
[7 empty] | 18153 | 16104 | 969622 | 2013-05-10 19:43 | 2013-05-10 23:05 | 202 | 11kV | 202 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135742 Single phase DOLF : 10 Amp Excluded OMS 969622 | May | 2013 | 2013Q4 | 2013 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | UG | Not Veg | 2013-05-10 | N | 202 | N | 1 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 17776 | 12134 | 969741 | 2013-05-11 12:07 | 2013-05-11 13:23 | 76 | 11kV | 156169 | 2125 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | ZN 180 Mosman - Pnl 41 - Ourimbah Cowles - 11kv Fdr Tripped Signals: 11kv Trip, GE, ZE Relays: EF, Sealing contacts, EFI, FC Field EFI': 8299, 4071, 3587, 2242, 6762, 4069, 2055 See OMS job, construction site in Mowbray Place. UG Cable damaged by contractor. See OMS 970522 | May | 2013 | 2013Q4 | 2013 | ZN180:PA41 | ZN180:PA41 | ZN00180/000041 | WILLOUGHBY | UG | Not Veg | 2013-05-11 | N | 73.4913 | N | 1 | N | N | 1.1101 | 39.4971 | 114123.699
[7 empty] | 16906 | 2949 | 970034 | 2013-05-13 01:02 | 2013-05-13 01:22 | 20 | 11kV | 28920 | 1446 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | tripped while trying to restored pnl.18 - closed onto fault | May | 2013 | 2013Q4 | 2013 | ZN2602:PA41 | ZN2602:PA41 | ZN02602/000041 | RANDWICK | Unknown | Not Veg | 2013-05-13 | N | 20 | N | 2 | N | N | 1.1101 | 39.4971 | 21133.883
[7 empty] | 17252 | 6560 | 969962 | 2013-05-12 23:37 | 2013-05-13 01:39 | 122 | 11kV | 112598 | 1213 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2602 Clovelly Zone Pnl.18 tripped on Earth Fault EFI F/C Field EFIs: S3663 3230 3439 6846 *S1290 did not operate as reset pin was stuck up* UG cable fault in conduits bear S1298 Milford Avoca - see 970033 for interruption to P41 - tripped while trying to restore Pnl.18. see 970031 970033 970034 | May | 2013 | 2013Q4 | 2013 | ZN2602:PA18 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | UG | Not Veg | 2013-05-12 | N | 92.8261 | N | 1 | N | N | 1.1101 | 39.4971 | 82283.2973
[7 empty] | 17426 | 8154 | 970307 | 2013-05-13 14:36 | 2013-05-13 17:00 | 144 | 11kV | 14249 | 172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn 690 Campsie - Pnl 27 - Earth fault, Fault check, EFIs. Underground fault. Could not phase at Sub 7885 and Sub 49897. DOp checked phase rotation. ME: 972734 RS: 972735 Withdrawn: 970307 | May | 2013 | 2013Q4 | 2013 | ZN690:PA27 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-05-13 | N | 82.843 | N | 2 | N | N | 1.1101 | 39.4971 | 10412.7489
[7 empty] | 18174 | 16350 | 970458 | 2013-05-14 07:22 | 2013-05-14 10:20 | 178 | 11kV | 102757 | 1732 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | zn12650 West Gosford Pa13 "AB44151" 11kV CB has tripped Signals: 11kV trip Relays: Timed A,B,C EFI, SEF, LO and timing relay EFI's: Cnr racecourse and faunce, S14116 S8117 S12869 S14215 S14568 Cause: Tree OS 103 Carrington St brough down OH See 971313,4 Exclude 970458,62,6,515,30 | May | 2013 | 2013Q4 | 2013 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2013-05-14 | N | 59.3285 | N | 3 | N | N | 1.1101 | 39.4971 | 75091.7848
[7 empty] | 17366 | 7611 | 970468 | 2013-05-14 07:43 | 2013-05-14 14:15 | 392.3167 | 11kV | 2353.9 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135769 A phase DOLF : 20 Amp Wire down to sub 52780. This sub already isolated on 8/4/2013. Pulling down mains to this sub, mains removed from pole HS-53203. CC1: 22-"Refer to SOp" FRC1: 329-"High Voltage Fuse - Requires replacement" | May | 2013 | 2013Q4 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2013-05-14 | N | 392.3167 | N | 3 | N | N | 1.1101 | 39.4971 | 1720.1607
[7 empty] | 16653 | 955 | 970669 | 2013-05-14 16:15 | 2013-05-14 17:00 | 45 | 11kV | 45 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135771 reported fluctuating supply Sub isolated to check connections Excluded OMS 970669 | May | 2013 | 2013Q4 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-05-14 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 18423 | 18853 | 971225 | 2013-05-15 13:07 | 2013-05-15 16:25 | 198 | 11kV | 112549 | 1332 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 15001 Brookvale - Pnl 18 - Pine Pittwater - 11kv CB Trip Relays: EF, EFI, Fault Check Signals: 11kv Trip EFI's: 16312, 17044 System Config Adnormal Underground fault between S.17044 Pine Federal Sw/B to S.16837 Federal Consul Sw/B to S.16905 Federal Consul Sw/A. Water main near Sub 16905 Consul Federal may have been damaged due to cable trench full of water. See OMS 971386,225 Exclude: 971093,085 CC1: 22-"Refer to SOp" FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | May | 2013 | 2013Q4 | 2013 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | UG | Not Veg | 2013-05-15 | N | 84.4962 | N | 2 | N | N | 1.1101 | 39.4971 | 82247.4896
[7 empty] | 16524 | 125 | 971197 | 2013-05-15 17:29 | 2013-05-15 23:05 | 336 | 11kV | 672 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 135783 Sub isolated to repair broken C phase LV connection Excluded OMS 971197 | May | 2013 | 2013Q4 | 2013 | 510:48164 | 508:82574 | ZN00508/082574 | PORT STEPHENS | UG | Not Veg | 2013-05-15 | N | 336 | N | 2 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 18411 | 18693 | 971427 | 2013-05-16 12:23 | 2013-05-16 12:40 | 17.3833 | 11kV | 208.6 | 12 | HV | Equipment Failed in Service | Equipment Failure | OTHER - REFER COMMENTS | Unplanned | Unselected | N | LID 135794 reported by pole inspector, Sw 61230 Earth wire broken in ground adj to pole. OMS# 135794. | May | 2013 | 2013Q4 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | Unknown | Not Veg | 2013-05-16 | N | 17.3833 | N | 2 | N | N | 1.1101 | 39.4971 | 152.4387
[7 empty] | 17196 | 5867 | 971616 | 2013-05-16 22:06 | 2013-05-17 01:10 | 183.8833 | 11kV | 1838.8333 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135795 A phase DOLF : 31 Amp | May | 2013 | 2013Q4 | 2013 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2013-05-16 | N | 183.8833 | N | 2 | N | N | 1.1101 | 39.4971 | 1343.7652
[7 empty] | 16889 | 2718 | 971622 | 2013-05-17 00:54 | 2013-05-17 02:10 | 76 | 11kV | 39064 | 514 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn14891 Wyong Pa20 fdr tripped on B&C ph O/C Cause: not ascertained. mains to patrol in daylight no recloser. (Great idea!) See 671670 exclude 671622 | May | 2013 | 2013Q4 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2013-05-17 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 28546.819
[7 empty] | 18397 | 18412 | 971763 | 2013-05-17 11:54 | 2013-05-17 13:10 | 76 | 11kV | 152 | 2 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Wind | N | LID 135809 A phase DOLF : 16 Amp Fuse bound open but not blown. Suspect shaken open by wind. Excluded OMS # 971763 | May | 2013 | 2013Q4 | 2013 | 225:33670 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | UG | Not Veg | 2013-05-17 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 16880 | 2564 | 971778 | 2013-05-17 12:23 | 2013-05-17 13:36 | 73 | 11kV | 53001 | 777 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 4 tripped on A and C phase IOC and Timed O/C Cause: Tree branch falling through mains. 973914 973918 973919 971778 | May | 2013 | 2013Q4 | 2013 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Veg | 2013-05-17 | N | 68.2124 | N | 6 | N | N | 1.1101 | 39.4971 | 38731.5675
[7 empty] | 16935 | 3143 | 971788 | 2013-05-17 12:44 | 2013-05-17 14:50 | 126 | 11kV | 1008 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135810 A phase DOLF : 20 Amp Excluded OMS 971788 | May | 2013 | 2013Q4 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2013-05-17 | N | 126 | N | 6 | N | N | 1.1101 | 39.4971 | 736.6167
[7 empty] | 17031 | 3936 | 971855 | 2013-05-17 14:44 | 2013-05-17 16:21 | 97 | 11kV | 192448 | 1984 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 135811 2 fault operations Overcurrent Tree branch on mains near sub 15100. Excluded OMS 971855. | May | 2013 | 2013Q4 | 2013 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2013-05-17 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 140635.3221
[7 empty] | 18401 | 18478 | 971983 | 2013-05-17 22:36 | 2013-05-18 08:44 | 608 | 11kV | 49248 | 81 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Zn.342 Paddington Pnl.15 tripped on IT Receive - @ S5277 OTC Gordon: ITR/Send, A & C phase differential Abnormal: DMA(15/2/13) AP's issued 30/4/13 D/R #31391 - 11kV feeder from S5277 to S2246 for cable replacement and repairs. Sw B @ S5853 Closed. @ S5277 11kv/415V TX #2 failed. Due to difficulty of TX replacement due to basement sub, subs attempted to transfer the existing OOS TX #3 associated with existing DMA, to replace defective TX #2. Delays in getting hygenist onite delayed restoration. | May | 2013 | 2013Q4 | 2013 | ZN342:PA15 | ZN342:PA24 | ZN00342/000024 | WOOLLAHRA | UG | Not Veg | 2013-05-17 | N | 608 | N | 6 | N | N | 1.1101 | 39.4971 | 35988.9858
[7 empty] | 18511 | 19979 | 972095 | 2013-05-18 18:24 | 2013-05-18 19:30 | 66 | 11kV | 8151.6 | 125 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12640 Umina Zone Section of Pa16 fdr @PT13148 40A footath HVDO failed Cause: Fuse Fatigue See 972094 GIS 972995 Exclude 972094 | May | 2013 | 2013Q4 | 2013 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2013-05-18 | N | 65.2128 | N | 1 | N | N | 1.1101 | 39.4971 | 5956.9488
[7 empty] | 18065 | 15457 | 972124 | 2013-05-19 08:14 | 2013-05-19 09:25 | 71 | 11kV | 142 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 135823 A phase DOLF : 10 Amp BIRD ON SUB. Excluded OMS REPORT NO 972124 & 972128. | May | 2013 | 2013Q4 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-05-19 | N | 71 | N | 4 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 18268 | 17194 | 972114 | 2013-05-19 07:24 | 2013-05-19 10:30 | 186 | 11kV | 7440 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135824 3 phase fuse/switch : 80 Amp FOUND WITH A-PHASE BLOWN,RELOADED, FOUND B PHASE AND C PHASE HV FUSES BLOWN.INTERRCONNECTED SUB. see report # 135849 | May | 2013 | 2013Q4 | 2013 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | UG | Not Veg | 2013-05-19 | N | 186 | N | 4 | N | N | 1.1101 | 39.4971 | 5436.9326
[7 empty] | 17866 | 12850 | 972212 | 2013-05-19 21:40 | 2013-05-19 22:30 | 50 | 11kV | 3550 | 71 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135848 no protection operation LV sub fuses opened to repair OHM Excluded oms # 972212 | May | 2013 | 2013Q4 | 2013 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2013-05-19 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 2594.2353
[7 empty] | 18395 | 18393 | 972222 | 2013-05-19 21:52 | 2013-05-19 23:46 | 114 | 11kV | 3676 | 34 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1290 Leightonfield Zn P10 'Christina Wood' fdr tripped on E/F, EFI. EFI @ S5539 Remarks: UG fault. S1290 Leightonfield P10 to S1206 Christina Wood Related jobs: #972222, 973233 | May | 2013 | 2013Q4 | 2013 | ZN1290:PA10 | ZN1290:PA10 | ZN01290/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-05-19 | N | 108.1176 | N | 4 | N | N | 1.1101 | 39.4971 | 2686.3124
[7 empty] | 17664 | 10965 | 972228 | 2013-05-20 01:56 | 2013-05-20 03:15 | 79 | 11kV | 2481 | 36 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | @Zn14143 Somersby Pa21 fdr tripped on ABC O/C relay, EFI EFI's S18108 S18052 S18270 S18849 S14902 S14956 See 973008,9,10 Exclude 972228 | May | 2013 | 2013Q4 | 2013 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2013-05-20 | N | 68.9167 | N | 4 | N | N | 1.1101 | 39.4971 | 1813.0416
[7 empty] | 16690 | 1140 | 972308 | 2013-05-20 08:59 | 2013-05-20 10:50 | 111 | 11kV | 111 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135853 DOLF : 16 Amp Volts 244/252/252 Amps 50/5/5 Excluded OMS 972308 | May | 2013 | 2013Q4 | 2013 | 238:34147 | 532:83298 | ZN00532/083298 | MAITLAND | UG | Not Veg | 2013-05-20 | N | 111 | N | 4 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 18080 | 15586 | 972687 | 2013-05-20 20:34 | 2013-05-20 21:28 | 53.7333 | 11kV | 5856.9333 | 109 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | PT 9001 Tara Robvic - Centre and Roadside fuses (50A). Possum on Tx caused HDO failure. ME: 972686 Withdrawn: 972687 CC1: 22-"Refer to SOp" | May | 2013 | 2013Q4 | 2013 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2013-05-20 | N | 53.7333 | N | 4 | N | N | 1.1101 | 39.4971 | 4280.0741
[7 empty] | 16633 | 857 | 972693 | 2013-05-20 22:08 | 2013-05-20 22:43 | 35 | 11kV | 19495 | 557 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Unselected | N | At S4545 Meadowbank Panel 29 tripped on Relays: EFI, O/C+EF(Basler Relay) Signals 11kV trip, ZE, Tx2 GE possum across LB 61231 See OMS 975136 972693 972696 972695 | May | 2013 | 2013Q4 | 2013 | ZN4545:PA24 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2013-05-20 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 14246.371
[7 empty] | 16885 | 2633 | 972765 | 2013-05-21 02:04 | 2013-05-21 04:00 | 116 | 11kV | 146072 | 1617 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 10 - Trip/reclose/trip, A & C phase IOC, timing and lockout, EFIs. HV UGOH (pole CR 01964) above S 48179 is defective. UGOH fault short circuit. ME: 972765 RS: 972767, 972766 Withdrawn: 972704, 972705 | May | 2013 | 2013Q4 | 2013 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | Unknown | Unknown | 2013-05-21 | N | 90.3352 | N | 4 | N | N | 1.1101 | 39.4971 | 106745.1092
[7 empty] | 16891 | 2772 | 972769 | 2013-05-21 08:40 | 2013-05-21 09:56 | 76 | 11kV | 106592 | 1481 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S187 Crwos Nest Panel 17 tripped on Earth Fault and EFI. Cause: Cable damaged by contractor S1033 SW/B to S1391 SW/B to S3496 SW/B See OMS 976054 976055 972769 | May | 2013 | 2013Q4 | 2013 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2013-05-21 | N | 71.973 | N | 4 | N | N | 1.1101 | 39.4971 | 77894.2897
[7 empty] | 17501 | 8844 | 972792 | 2013-05-21 09:18 | 2013-05-21 11:08 | 110 | 11kV | 18300 | 170 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn12580 Erina Pa7 fdr tripped on Relays: Aph IOC, EF, Time, EFI Signals: No Signals EFI's: No Field EFI's operated.l Cause: UG Cable fault between S18675 to S18072 to LB42550 See 973203,5 Exclude 972792,802,19 | May | 2013 | 2013Q4 | 2013 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | UG | Not Veg | 2013-05-21 | N | 107.6471 | N | 4 | N | N | 1.1101 | 39.4971 | 13373.1002
[7 empty] | 17321 | 7280 | 973102 | 2013-05-21 17:03 | 2013-05-22 01:10 | 487 | 11kV | 9018 | 117 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | Unselected | N | LID 135866 2 fault operations Earth fault Truck hit pole JS- 70237. Broke crossarm JS-70073 Excluded OMS 973102 & 973116 | May | 2013 | 2013Q4 | 2013 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2013-05-21 | N | 77.0769 | N | 4 | N | N | 1.1101 | 39.4971 | 6590.0884
[7 empty] | 18034 | 14844 | 973589 | 2013-05-22 18:35 | 2013-05-22 19:37 | 62 | 11kV | 79546 | 1283 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | Zn9252 Jannali Panell 4 "Vesta Glenelg" tripped, reclosed and tripped on Relays: A phase instantaneous, timed O/C, Timing relay and Lockout relay Signals: 11kv trip, Zone earth and Tx3 Group earth Field EFI's: Nil Remarks: tree/branch on OH mains. Dop remove tree branch from 11kv O/H mains o/s 8 Tudar Rd Jannali. Feeders restored. Related jobs: #973605, 973602, 973594, 973592, 973589, 976120 | May | 2013 | 2013Q4 | 2013 | ZN9252:PA4 | ZN9252:PA30 | ZN09252/000030 | SUTHERLAND | OH | Veg | 2013-05-22 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 58129.8706
[7 empty] | 17949 | 13619 | 973634 | 2013-05-22 21:28 | 2013-05-22 23:12 | 104 | 11kV | 313520 | 3282 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ZN3922 Drummoyne - 11kv Panel No.29 "Sub 8351 Wise Ln Norman" tripped. Relays: e/fault, fault check. Signals: efi, 11kv trip, zone earth Field EFI's: S8351, S4019, S4732 Remarks: UG fault. Fault between Sub 4732 Rosser St to Sub 1511 Hyam Reynolds. (Suspect multiple parallels during outage. Though not indicated on report) Related jobs: #973649, 973643, 973641, 973640, 973639, 973636, 973634, 975747, 975755, 975762, 975764, 975757, 975750, 975741, 975693, 975692 | May | 2013 | 2013Q4 | 2013 | ZN3922:PA29 | ZN3922:PA29 | ZN03922/000029 | INNER WEST | UG | Not Veg | 2013-05-22 | N | 95.5271 | N | 3 | N | N | 1.1101 | 39.4971 | 229111.1687
[7 empty] | 17852 | 12727 | 973565 | 2013-05-22 17:39 | 2013-05-23 01:57 | 498 | 11kV | 23658 | 119 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 135883 1 fault operation B & C phase Overcurrent Broken xarms at pole AK-72692. Excluded OMS 973565 | May | 2013 | 2013Q4 | 2013 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2013-05-22 | N | 198.8067 | N | 3 | N | N | 1.1101 | 39.4971 | 17288.5686
[7 empty] | 18402 | 18487 | 973659 | 2013-05-23 02:20 | 2013-05-23 03:40 | 80 | 11kV | 61305 | 772 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12570 Avoca Section of Pa29 "Bensville" fdr @RE44982 Bensville tripped on O/C Cause: Not ascertained. Lineworker to patrol See 973737,8 exclude 973659 | May | 2013 | 2013Q4 | 2013 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2013-05-23 | N | 79.4106 | N | 6 | N | N | 1.1101 | 39.4971 | 44799.8858
[7 empty] | 16873 | 2507 | 973657 | 2013-05-23 01:30 | 2013-05-23 07:39 | 369 | 11kV | 171146 | 816 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 135884 3 fault operations Faulty LA's at pole MQ-10137. Excluded OMS 973657 & 973661. | May | 2013 | 2013Q4 | 2013 | 231:8415 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2013-05-23 | N | 209.7377 | N | 6 | N | N | 1.1101 | 39.4971 | 125068.4488
[7 empty] | 18358 | 17898 | 973871 | 2013-05-23 11:55 | 2013-05-23 12:05 | 10 | 11kV | 30 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 135885 Single phase Kite in mains | May | 2013 | 2013Q4 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-05-23 | N | 10 | N | 6 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 18144 | 16051 | 973929 | 2013-05-23 13:03 | 2013-05-23 13:36 | 33 | 11kV | 51697 | 1598 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 15011 - Beacon Hill - Pnl 2 "S16011 Alambie rd 252" - CB Trip Relays: C Phase timmed, Timming, Lockout Field EFI's: Nil Signals: 11kv Trip Bat Adj to AB 26245. LK 22823 HR Connection See OMS 975014 Exclude 973929,931,943,957 | May | 2013 | 2013Q4 | 2013 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2013-05-23 | N | 32.3511 | N | 6 | N | N | 1.1101 | 39.4971 | 37778.6428
[7 empty] | 16564 | 389 | 973785 | 2013-05-23 12:00 | 2013-05-23 16:00 | 240 | 11kV | 8640 | 36 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12650 Section Pa12L @USL44673 interrupted for safety to allow SES tro remove falling tree near PT14644 See 976418 exclude 973785 | May | 2013 | 2013Q4 | 2013 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Veg | 2013-05-23 | N | 240 | N | 6 | N | N | 1.1101 | 39.4971 | 6313.8572
[7 empty] | 17010 | 3676 | 974003 | 2013-05-23 14:27 | 2013-05-23 20:44 | 377 | 11kV | 35061 | 93 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 135887 3 phase Sensitive Earth FAult wire snapped mid span down at pole 8E50018 dq Excluded OMS 974003 | May | 2013 | 2013Q4 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-05-23 | N | 377 | N | 6 | N | N | 1.1101 | 39.4971 | 25621.5447
[7 empty] | 16971 | 3357 | 974195 | 2013-05-24 01:24 | 2013-05-24 02:30 | 66 | 11kV | 726 | 11 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Ex Zn14144 Wamberal Section of Pa5 @PT11330 Hastings Yeramba roadside & middle phase 20A HDO fuses operated cause: lightning/surge arrestor. supply restored by lv// link 36951 See 976778 exclude 974195 | May | 2013 | 2013Q4 | 2013 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2013-05-24 | N | 66 | N | 2 | N | N | 1.1101 | 39.4971 | 530.5394
[7 empty] | 17861 | 12810 | 974577 | 2013-05-24 18:53 | 2013-05-25 00:45 | 352 | 11kV | 160619 | 1899 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S129 Hunters Hill Pa8 tripped on E/F, EFI, frame leakage #1 Tx Group earth and 11kV Trip. Abnormal Switching: S86 SW/B closed S7564 SW/A open OH wires down Due tree adjacent PT1170. Suspect secondary UG fault between S3403 and S1782. See OMS 975469 975470 975471 975472 974577 974581 974593 | May | 2013 | 2013Q4 | 2013 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Veg | 2013-05-24 | N | 84.5808 | N | 2 | N | N | 1.1101 | 39.4971 | 117375.6277
[7 empty] | 17528 | 9005 | 974633 | 2013-05-25 02:08 | 2013-05-25 03:30 | 82 | 11kV | 104289 | 1790 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 135897 2 fault operations 3 phase Earth fault Trip & L/O after car hit pole JU-31979. HV into LV. Excluded OMS No.974633. | May | 2013 | 2013Q4 | 2013 | 256:80647 | 256:80647 | ZN00256/080647 | NEWCASTLE | OH | Not Veg | 2013-05-25 | N | 58.262 | N | 3 | N | N | 1.1101 | 39.4971 | 76211.3252
[7 empty] | 17529 | 9006 | 974679 | 2013-05-25 09:25 | 2013-05-25 10:46 | 80.9833 | 11kV | 10576.95 | 132 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 135902 A phase DOLF DOLF carrier contact burnt. | May | 2013 | 2013Q4 | 2013 | 256:80647 | 256:80647 | ZN00256/080647 | NEWCASTLE | OH | Not Veg | 2013-05-25 | N | 80.1284 | N | 3 | N | N | 1.1101 | 39.4971 | 7729.3231
[7 empty] | 17991 | 14159 | 974652 | 2013-05-25 07:22 | 2013-05-25 11:35 | 253 | 11kV | 61604 | 368 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135898 - 1 fault operation B & C phase Earth fault LID 135901 - 1 fault operation B & C phase Earth fault Network abnormal - black pinned open ABS 40246 since 8/3/13 Blown L/A UGOH pole FS-82403, burnt off Bph tapping at ABS 41400 Note - Please fit animal covers on UGOH FS-82403, birds in varying stages of decayfound at base of pole. | May | 2013 | 2013Q4 | 2013 | 504:48029 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2013-05-25 | N | 167.4022 | N | 3 | N | N | 1.1101 | 39.4971 | 45018.3862
[7 empty] | 16556 | 359 | 974793 | 2013-05-26 00:20 | 2013-05-26 02:35 | 135 | 11kV | 372330 | 2758 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12660 Wiy Wiy Pa14 fdr tripped on: relays: Cph time Overcurrent Signals: 11kv trip ABNORMAL: S48927SwB Closed S11242SwA Open ; AB43079 Closed Open Bonda Below S49324 Cause: Cause not ascertained. Feeder patrolled clear See 978099,103,5,6,7 Exclude 974793,4,5,6,7,8 | May | 2013 | 2013Q4 | 2013 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2013-05-26 | N | 135 | N | 2 | N | N | 1.1101 | 39.4971 | 272087.7821
[7 empty] | 18201 | 16612 | 974944 | 2013-05-26 23:47 | 2013-05-27 03:20 | 213 | 11kV | 48244 | 423 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ez Zn13000 Lake Munmorah Section of Pa10 @IR40178 Elizabeth Bay Anothony tripped on: Cause: OH down See 975127,8,9Exclude 974944 | May | 2013 | 2013Q4 | 2013 | ZN13000:PA10 | ZN13000:PA10 | ZN13000/000010 | CENTRAL COAST | OH | Not Veg | 2013-05-26 | N | 114.052 | N | 2 | N | N | 1.1101 | 39.4971 | 35255.2922
[7 empty] | 17051 | 4038 | 974956 | 2013-05-27 07:41 | 2013-05-27 09:30 | 109 | 11kV | 545 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | S.7127 - Princes Alexander - A Phase OEFMA75A HV Fuse Blown Cause Not Ascertained Related OMS:975516, 974956,959,979 | May | 2013 | 2013Q4 | 2013 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | OH | Veg | 2013-05-27 | N | 109 | N | 2 | N | N | 1.1101 | 39.4971 | 398.2699
[7 empty] | 17717 | 11688 | 975377 | 2013-05-27 16:54 | 2013-05-27 20:00 | 186 | 11kV | 86878 | 2167 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | @Zn12610 Long Jetty Pa22 "Shelly Primary School" fdr tripped on AB phase IOC reclose t/d cuase: Underslung links - USL @ S40269 failed See 975542,3 Exclude 975377,8,426 | May | 2013 | 2013Q4 | 2013 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Not Veg | 2013-05-27 | N | 40.0914 | N | 2 | N | N | 1.1101 | 39.4971 | 63487.8799
[7 empty] | 18219 | 16744 | 975641 | 2013-05-28 12:23 | 2013-05-28 13:08 | 45 | 11kV | 8688 | 204 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At S35500 Top Ryde Pa14 tripped Relays; Earth Fault with EFI. Signals: 11kV Trip, Zone Earth and Tx2 Group Earth. Cause; Ausgrid contractor drilling hit 11kV cable between S.8 Animal Genetics. and S7888 Csiro Richardson No1. See OMS 978682 978684 975641 | May | 2013 | 2013Q4 | 2013 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2013-05-28 | N | 42.5882 | N | 3 | N | N | 1.1101 | 39.4971 | 6348.9341
[7 empty] | 17825 | 12526 | 975848 | 2013-05-28 17:58 | 2013-05-28 19:30 | 92 | 11kV | 736 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 135926 B phase dist fuse : 100 Amp Fuse Fatigued. Tx Volts: 244V Load Aph - 13A, Bph - 42A, Cph - 38A Excluded OMS No. 975848 + 975861 | May | 2013 | 2013Q4 | 2013 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2013-05-28 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 537.8471
[7 empty] | 18305 | 17522 | 975870 | 2013-05-28 20:25 | 2013-05-28 23:20 | 175 | 11kV | 4725 | 27 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 135927 Section of 11kV isolated to repair broken crossarm at pole JP-90639 and low mains. | May | 2013 | 2013Q4 | 2013 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2013-05-28 | N | 175 | N | 3 | N | N | 1.1101 | 39.4971 | 3452.8906
[7 empty] | 17212 | 6062 | 976225 | 2013-05-29 19:08 | 2013-05-29 20:06 | 58 | 11kV | 2030 | 35 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale section of Pa12 @PT48816 Wolseley Mcdonagh, footpath HDO fuse blown ( 63K ABB pro link batch 1004) due to fuse fatigue See 977045 GIS 977047 Exclude 976225,6,31,3 | May | 2013 | 2013Q4 | 2013 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2013-05-29 | N | 58 | N | 1 | N | N | 1.1101 | 39.4971 | 1483.4641
[7 empty] | 16631 | 851 | 976248 | 2013-05-30 00:27 | 2013-05-30 02:20 | 112.5333 | 11kV | 4838.9333 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135942 A & B phase DOLF : 15 Amp | May | 2013 | 2013Q4 | 2013 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2013-05-30 | N | 112.5333 | N | 7 | N | N | 1.1101 | 39.4971 | 3536.1498
[7 empty] | 17441 | 8230 | 976254 | 2013-05-30 01:18 | 2013-05-30 02:55 | 97 | 11kV | 7857 | 81 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12610 Long Jetty section of Pa22 @PT13976 Grandview Liddell had a blown fuse foot path side. 31.5A HDO. Cause not ascertained. See 977059 exclude 9760254,5 | May | 2013 | 2013Q4 | 2013 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Veg | 2013-05-30 | N | 97 | N | 7 | N | N | 1.1101 | 39.4971 | 5741.6639
[7 empty] | 17684 | 11389 | 976259 | 2013-05-30 04:13 | 2013-05-30 05:39 | 86 | 11kV | 36448 | 437 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S80 Chatswood Panel 28 tripped with the following relays Earth Fault, EFI and Fault Check. Suspect UG cable fault between S83736 Mobray Sydney SW? B and S3199 Archer Albert SW/A to S1845 Holland St SW/B See OMS 978669 978671 976259 | May | 2013 | 2013Q4 | 2013 | ZN80:PA28 | ZN80:PA28 | ZN00080/000028 | WILLOUGHBY | UG | Not Veg | 2013-05-30 | N | 83.405 | N | 7 | N | N | 1.1101 | 39.4971 | 26635.1234
[7 empty] | 16728 | 1404 | 976406 | 2013-05-30 10:51 | 2013-05-30 13:00 | 128.75 | 11kV | 515 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 135948 A & C phase HV MAIN ON X-ARM AT SUB 3924 . | May | 2013 | 2013Q4 | 2013 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-05-30 | N | 128.75 | N | 7 | N | N | 1.1101 | 39.4971 | 376.3468
[7 empty] | 16678 | 1103 | 976884 | 2013-05-30 18:31 | 2013-05-30 21:20 | 169 | 11kV | 1014 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135960 B phase DOLF : 20 Amp. | May | 2013 | 2013Q4 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2013-05-30 | N | 169 | N | 7 | N | N | 1.1101 | 39.4971 | 741.0013
[7 empty] | 17896 | 13092 | 976909 | 2013-05-30 22:02 | 2013-05-31 04:30 | 388 | 11kV | 193460 | 1199 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 135961 2 fault operations Earth fault MVA pole JV-10941. Pole broken. HV into LV. Excluded OMS 976909 | May | 2013 | 2013Q4 | 2013 | 221:11900 | 221:11900 | ZN00221/011900 | LAKE MACQUARIE | OH | Not Veg | 2013-05-30 | N | 161.3511 | N | 7 | N | N | 1.1101 | 39.4971 | 141374.8619
[7 empty] | 17629 | 10512 | 976924 | 2013-05-31 04:59 | 2013-05-31 06:30 | 91 | 11kV | 6825 | 75 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | PT12780 Wyuna Branga Cph Fuse HDO Broken Cause: Insulator failed See 978127 Exclude 976924 | May | 2013 | 2013Q4 | 2013 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2013-05-31 | N | 91 | N | 2 | N | N | 1.1101 | 39.4971 | 4987.5087
[7 empty] | 17146 | 4928 | 978685 | 2013-05-30 19:24 | 2013-05-31 09:20 | 836 | 11kV | 100554 | 698 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | ZN 10995 Riverwood - Pnl 8 - Trip/reclose/trip, C phase IOC, Timed OC, lockout and timing relay. Vehicle hit pole in Boundary Road and brought down 11kV and 415V. 11kV reinstated at 21:13 and 21:16. LV distributors reinstated at various times as mains cut away and paralleled. For S 10977 see 978688. For S 10681 see 978687. For S 10113 see 978691. For S 10674 which overloaded because it was in parallel with S 10185 see 978705. ME: 978685. Rest Steps: 978687, 688, 689, 691. Associated: 978705. see below... | May | 2013 | 2013Q4 | 2013 | ZN10995:PA8 | ZN10995:PA8 | ZN10995/000008 | GEORGES RIVER | OH | Not Veg | 2013-05-30 | N | 144.0602 | N | 7 | N | N | 1.1101 | 39.4971 | 73481.8974
[7 empty] | 17522 | 8972 | 987740 | 2013-05-31 19:19 | 2013-05-31 20:44 | 85 | 11kV | 850 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone Section of Pa12 @Autolink 44773 Chandlers ceter phase had operated Cause: not ascertained. Wyong mains to patrol feeder beyond auto links in daylight also refer to 987441, 978141 and 977265 | May | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-05-31 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 621.1549
[7 empty] | 16927 | 3081 | 977287 | 2013-06-01 06:43 | 2013-06-01 09:00 | 137 | 11kV | 411 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135973 A phase 11kV llc burnt off OHM Excluded oms 977287 | June | 2013 | 2013Q4 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-06-01 | N | 137 | N | 4 | N | N | 1.1101 | 39.4971 | 300.3467
[7 empty] | 18539 | 20218 | 977321 | 2013-06-01 10:28 | 2013-06-01 11:27 | 59.1167 | 11kV | 2637.3833 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135975 B phase DOLF : 40 Amp Operator did not have a 40 A fuse available. Fuse replaced with a 31.5. FS M'Brook please arrange to have the fuse replaced w/ the appropriate fuse asap. dq cause not ascertained. Excluded OMS 977321 | June | 2013 | 2013Q4 | 2013 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | UG | Not Veg | 2013-06-01 | N | 56.1145 | N | 4 | N | N | 1.1101 | 39.4971 | 1927.322
[7 empty] | 16884 | 2626 | 977387 | 2013-06-01 17:40 | 2013-06-01 20:10 | 150 | 11kV | 150 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135979 Single phase Cable from DOLF to LLC had failed. Excluded OMS 977387 | June | 2013 | 2013Q4 | 2013 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2013-06-01 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 16509 | 72 | 977418 | 2013-06-01 22:13 | 2013-06-01 23:59 | 106 | 11kV | 1908 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | Ex Zn14891 Wyong Zone Section of Pa20 @PT14967 Burlington Holloway 0.9 Footpath side HV fuse carrier defective/replaced See 978366 exclude 977418 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2013-06-01 | N | 106 | N | 4 | N | N | 1.1101 | 39.4971 | 1394.3101
[7 empty] | 17459 | 8397 | 977475 | 2013-06-02 10:18 | 2013-06-02 11:26 | 68 | 11kV | 77792 | 1144 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | ZN.15012 - Killarney - Pnl 8 "Forestville" - Fdr Tripped, Reclosed, Tripped and Locked out Relays: A and C Phase Timed and IOC, reclosed timing, lockout relay Signals: 11kv Trip PT.15429 isolated and in LV// Palm frond contact mains in Tyalla Ave Exclude OMS 977477,490,496,500 | June | 2013 | 2013Q4 | 2013 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2013-06-02 | N | 68 | N | 9 | N | N | 1.1101 | 39.4971 | 56848.0991
[7 empty] | 17639 | 10678 | 977498 | 2013-06-02 10:42 | 2013-06-02 12:25 | 103 | 11kV | 43957 | 487 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At S1673 Turramurra Panel 9 Tripped on Relays: EFI and C phase IOC. Cause: Fault Locked on section of 11kV feeder from S7484 Adventist Hospital No3 to S50162 Adventist Hospital No7. See OMS 978096 978101 978102 977498 | June | 2013 | 2013Q4 | 2013 | ZN1673:PA9 | ZN1673:PA9 | ZN01673/000009 | KU-RING-GAI | UG | Not Veg | 2013-06-02 | N | 90.2608 | N | 9 | N | N | 1.1101 | 39.4971 | 32122.4791
[7 empty] | 18272 | 17212 | 977555 | 2013-06-02 11:40 | 2013-06-02 13:50 | 130 | 11kV | 51880 | 491 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn14891 Wyong Zone Pa16 'Wadalba' fdr tripped on: Relays: SEF Signals: 11kv trip EFI's: nil Cause: OH down. Weather related LV// USL 30783 See 978457,60 Exclude 977555,68,70,3,82,9,94 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA1 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2013-06-02 | N | 105.6619 | N | 9 | N | N | 1.1101 | 39.4971 | 37912.3738
[7 empty] | 17427 | 8157 | 977549 | 2013-06-02 11:35 | 2013-06-02 14:20 | 165 | 11kV | 51420 | 333 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong Zone Pa12 'Yarramalong fdr' @TCAT 14085 Yarramalong Boyds 0.2 Tripped on Cph O/C trip Cause: Cause not ascertained. DOp found no cause after detailed patrol See 978412,3,5 Exclude 977549 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-06-02 | N | 154.4144 | N | 9 | N | N | 1.1101 | 39.4971 | 37576.2194
[7 empty] | 18179 | 16395 | 977714 | 2013-06-02 15:26 | 2013-06-02 15:50 | 24 | 11kV | 624 | 26 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale Section of Pa24R 'the burns rd' @AB42102 DOp interrupted supply to allow Linesman and SES to freely remove tree from 11kv mains in Palmdale rd. Ourimbah adjacent to USL43859. See 978524 Exclude 977714,6 | June | 2013 | 2013Q4 | 2013 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2013-06-02 | N | 24 | N | 9 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 17087 | 4322 | 977862 | 2013-06-02 13:00 | 2013-06-02 16:10 | 190 | 11kV | 190 | 1 | HV | 3rd Party Action | 3rd Party Impact | Fuse | Unplanned | Rain Heavy | N | S 10914 Harslett Water Board - A & C phase HDO's (40A). Suspect that customer has installed a new pump that does not grade with the HV fuses. Fuses have been known to blow before on more than one occasion, usually recorded as cause not ascertained. Further investigation necessary. | June | 2013 | 2013Q4 | 2013 |  |  |  | GEORGES RIVER | OH | Not Veg | 2013-06-02 | N | 190 | N | 9 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 17282 | 6893 | 978085 | 2013-06-02 17:07 | 2013-06-02 17:11 | 4 | 11kV | 7440 | 1860 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | IR62774 - Kentwell Pittwater - Tripped on O/C Ex Pnl 9 "USL23364 ETC" Fdr from ZN.15008 Harbord Suspect O/L Trip - Incorrect Load Readings on Pnl 9 and or IR62774. Previously Reported. | June | 2013 | 2013Q4 | 2013 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2013-06-02 | N | 4 | N | 9 | N | N | 1.1101 | 39.4971 | 5436.9326
[7 empty] | 16519 | 103 | 977612 | 2013-06-02 17:35 | 2013-06-02 17:53 | 18 | 11kV | 1836 | 102 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14892 Charmhaven Zone Pa3 DOp interrupted HV into PT11198 to allow Linesman to remove tree laying on 11kv mains See 978527 exclude 977749 | June | 2013 | 2013Q4 | 2013 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Veg | 2013-06-02 | N | 18 | N | 9 | N | N | 1.1101 | 39.4971 | 1341.6946
[7 empty] | 18391 | 18330 | 977794 | 2013-06-02 21:19 | 2013-06-03 06:56 | 577 | 11kV | 461433 | 2190 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 135981 2 fault operations B phase Overcurrent; Sensitive Earth Fault Possum found across arrestors at Sw 1552. HV conductor broke between poles OR-30278 & OR-30515. HV into LV. EMSo reported no damage at residences. Tapping also found blown at pole OR-30313. Excluded OMS 977794 | June | 2013 | 2013Q4 | 2013 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2013-06-02 | N | 210.7 | N | 9 | N | N | 1.1101 | 39.4971 | 337201.6264
[7 empty] | 16950 | 3262 | 978357 | 2013-06-03 09:00 | 2013-06-03 09:25 | 25 | 11kV | 5300 | 212 | HV | Staff Other | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 135984 Planned job SI 32903 customers not notified | June | 2013 | 2013Q4 | 2013 | 239:82132 | 239:82132 | ZN00239/082132 | LAKE MACQUARIE | OH | Not Veg | 2013-06-03 | N | 25 | N | 6 | N | N | 1.1101 | 39.4971 | 3873.0837
[7 empty] | 17638 | 10677 | 977885 | 2013-06-03 09:06 | 2013-06-03 12:10 | 184 | 11kV | 736 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 135987 A phase burnt off llc Excluded oms 977885 | June | 2013 | 2013Q4 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2013-06-03 | N | 184 | N | 6 | N | N | 1.1101 | 39.4971 | 537.8471
[7 empty] | 17261 | 6650 | 977935 | 2013-06-03 06:09 | 2013-06-03 12:45 | 396 | 11kV | 2772 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cable End Box | Unplanned | No Weather Impact | N | At S7127 Princes Alexander, A Phase 75A OEFMA HV fuse operated Remarks: End box fault. Dist #2 restored @ 1025 via LV// links 16749 & 16659 Related jobs: #977825, 978522, 977935, 978523 | June | 2013 | 2013Q4 | 2013 | ZN3472:PA34 | ZN3472:PA34 | ZN03472/000034 | CUMBERLAND | UG | Not Veg | 2013-06-03 | N | 396 | N | 6 | N | N | 1.1101 | 39.4971 | 2025.6958
[7 empty] | 18017 | 14556 | 978082 | 2013-06-03 13:39 | 2013-06-03 15:51 | 132 | 11kV | 120516 | 913 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S80 Chatswood Pa25 Tripped reclosed tripped and locked out on IOC, Fault check, EFI Signals:11kV trip, Zone Earth No11 Group Earth. Cause: 11kV UG fault from Zn80 Chatswood to S3451 Murray Ralston. See OMS 979071 978082 978150 | June | 2013 | 2013Q4 | 2013 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | UG | Not Veg | 2013-06-03 | N | 132 | N | 6 | N | N | 1.1101 | 39.4971 | 88069.5382
[7 empty] | 17430 | 8174 | 978261 | 2013-06-03 18:41 | 2013-06-03 19:05 | 24 | 11kV | 7032 | 293 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn13000 Lake Munmorah Section of Pa2L @AB40027 burnt off bond at load side or northern side. See 978533 exclude 978261 | June | 2013 | 2013Q4 | 2013 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Not Veg | 2013-06-03 | N | 24 | N | 6 | N | N | 1.1101 | 39.4971 | 5138.7782
[7 empty] | 18073 | 15544 | 978278 | 2013-06-03 19:20 | 2013-06-03 20:50 | 90 | 11kV | 450 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | @PT14152 Toomey Maidens Brush interrupted for safety reasons. @AB44297 defective and glowing on one phase. To isolate AB44297, PT14152 was interrupted. PT s non LV//. Lineworkers have bonded through AB44297 See 978543 Exclude 978278 | June | 2013 | 2013Q4 | 2013 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2013-06-03 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 16778 | 1880 | 978408 | 2013-06-04 09:11 | 2013-06-04 10:40 | 89 | 11kV | 89 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 135996 Single phase DOLF : 10 Amp excluded OMS 978408 | June | 2013 | 2013Q4 | 2013 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | UG | Not Veg | 2013-06-04 | N | 89 | N | 7 | N | N | 1.1101 | 39.4971 | 65.0386
[7 empty] | 18456 | 19148 | 978558 | 2013-06-04 11:32 | 2013-06-04 12:34 | 62 | 11kV | 86040 | 1458 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn2835 Burwood Panel 16 'Vernon Redmyre' tripped on: Relays: Earth fault, fault check and EFI Signals: Zone earth, Tx4 group earth and 11kv trip EFI's: S2035, S2073, S3340 Remarks: ASP contractor Connect Engineering damaged UG cable near Sub 3340 Redmyre Raw. Terry Harris advised SCR where he cable had been hit. Dop Burchell isolated and earthed issued Jointers A/P. Jointers will fix today for network security. Related jobs: #978558, 978987, 978986 | June | 2013 | 2013Q4 | 2013 | ZN2835:PA16 | ZN2835:PA16 | ZN02835/000016 | STRATHFIELD | UG | Not Veg | 2013-06-04 | N | 59.0123 | N | 7 | N | N | 1.1101 | 39.4971 | 62875.4942
[7 empty] | 17732 | 11832 | 978652 | 2013-06-04 12:59 | 2013-06-04 14:03 | 64 | 11kV | 22784 | 356 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa5 @RE45101 Jilliby Dunks off Pa5 Wyong Feeder tripped on SEL & Locked out ABNORMAL: During Reconnect Swtiching. Pa5 & Pa19 in parallel at S18164 SwB for D&R 315317 Cause: Protection Malfunction. SEL appears to have oparated incorreclty during reconnect switching of another section of feeder See 979105 exclude 978652,9 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-06-04 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 16649.8752
[7 empty] | 17702 | 11552 | 978754 | 2013-06-04 15:16 | 2013-06-04 16:45 | 89 | 11kV | 202688 | 2325 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2635 Epping Panel 10 tripped reclosed tripped and locked out on Relays: Earth Fault, Fault check, EFI, Timing and lockout Signals: 11kV trip No1 Group earth and zone Earth. See OMS 979430 979432 979431 978798 979451 798747 | June | 2013 | 2013Q4 | 2013 | ZN2635:PA10 | ZN2635:PA58 | ZN02635/000058 | PARRAMATTA | UG | Not Veg | 2013-06-04 | N | 87.1776 | N | 7 | N | N | 1.1101 | 39.4971 | 148118.4121
[7 empty] | 18242 | 17000 | 978751 | 2013-06-04 15:22 | 2013-06-04 18:14 | 172.4167 | 11kV | 299.9667 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 136003 A phase DOLF : 10 Amp Cause suspect Cockatoo contacted HV. Excluded OMS 978951 | June | 2013 | 2013Q4 | 2013 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2013-06-04 | N | 149.9833 | N | 7 | N | N | 1.1101 | 39.4971 | 219.2068
[7 empty] | 16585 | 557 | 978746 | 2013-06-04 15:18 | 2013-06-04 19:40 | 262 | 11kV | 1572 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Ex Zn12580 Erina secion of Pa16 @PT18289 Terrigal Chetwynd 0.2 Aph TX hv fuse blown (120EFMA75Amp) due to transformer failure. Suspect 1000kVA transformer deective. Restored by LV Parallel. Customer on restricted supply. See 979315 exclude 978746,73,86 | June | 2013 | 2013Q4 | 2013 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | UG | Not Veg | 2013-06-04 | N | 262 | N | 7 | N | N | 1.1101 | 39.4971 | 1148.7712
[7 empty] | 17417 | 8104 | 978342 | 2013-06-04 07:52 | 2013-06-04 22:20 | 868 | 11kV | 32426 | 62 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S.5916 Bank Bowman - Low volts due to defective transformer Aggreko generator connected @ 1630 to LV board - work permits issued to T-Con & Jointer to replace defective TX. Permits cancelled & planned interruption @ 2215 to disconnect generator and TX replaced with LV board restored @ 2220 see 979413 979411 | June | 2013 | 2013Q4 | 2013 | ZN711:PA33 | ZN7481:PA9 | ZN07481/000009 | SYDNEY | UG | Not Veg | 2013-06-04 | N | 523 | N | 7 | N | N | 1.1101 | 39.4971 | 23695.9644
[7 empty] | 17508 | 8877 | 979438 | 2013-06-06 11:06 | 2013-06-06 11:51 | 45 | 11kV | 15255 | 339 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 136021 B phase Bph incoming link burnt up at Sw 42048 Bridgeman Rd RAGCB. Excluded OMS 979438 | June | 2013 | 2013Q4 | 2013 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2013-06-06 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 11147.9041
[7 empty] | 18449 | 19106 | 979593 | 2013-06-06 15:13 | 2013-06-06 17:03 | 109.7167 | 11kV | 66076.7167 | 790 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 136028 1 fault operation Sensitive Earth Fault UGOH blown outside Tarro zone.UGOH blown outside Tarro zone. Excluded OMS 979648 & 979593 | June | 2013 | 2013Q4 | 2013 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | Unknown | Unknown | 2013-06-06 | N | 83.6414 | N | 3 | N | N | 1.1101 | 39.4971 | 48286.9156
[7 empty] | 18116 | 15882 | 979037 | 2013-06-06 11:51 | 2013-06-06 20:10 | 499 | 11kV | 46407 | 93 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 10164 Banksia Short - Centre Phase HDO. HDO defective and PT 10164. Supply restored via 4 LV// links. Only one customer phoned in to report outage. Event did not roll up to the Control room, who were notified at approx 17:44. Volts recorded at 211v, so no disturbance may have been noticed. Extended outage time. ME: 979739. Withdrawn: 979037. | June | 2013 | 2013Q4 | 2013 | ZN10996:PA9 | ZN10998:PA8 | ZN10998/000008 | BAYSIDE | OH | Not Veg | 2013-06-06 | N | 499 | N | 3 | N | N | 1.1101 | 39.4971 | 33912.8668
[7 empty] | 18413 | 18723 | 979730 | 2013-06-07 07:40 | 2013-06-07 09:35 | 115 | 11kV | 4485 | 39 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136034 2 fault operations Earth fault HV Trans leads fail sub 71181 Sub 71181supported by LV interconection. Excluded OMS 979730 Job for NS at Thompson st. sucked into this switching on creation. | June | 2013 | 2013Q4 | 2013 | 812:19066 | 801:74117 | ZN00801/074117 | MUSWELLBROOK | OH | Not Veg | 2013-06-07 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 3277.5057
[7 empty] | 18471 | 19389 | 979713 | 2013-06-07 07:15 | 2013-06-07 10:59 | 224 | 11kV | 91922 | 723 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S.3154 St Ives, Panel 22 Fdr CB tripped, reclosed and locked out on C ph. timed OC, SEF relay, lockout and timing relays, Zone earth, 11kV trip. 11kV wire down in Ayres Rd near Carissa Ave, St Ives. Also a second fault on feeder was tree branch on teee to PT.1338 | June | 2013 | 2013Q4 | 2013 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Not Veg | 2013-06-07 | N | 127.1397 | N | 5 | N | N | 1.1101 | 39.4971 | 67173.8864
[7 empty] | 16693 | 1168 | 979797 | 2013-06-07 09:38 | 2013-06-07 11:25 | 107 | 11kV | 535 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136035 Broken LL lead Excluded OMS 979797 | June | 2013 | 2013Q4 | 2013 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-06-07 | N | 107 | N | 5 | N | N | 1.1101 | 39.4971 | 390.9622
[7 empty] | 18208 | 16672 | 979808 | 2013-06-07 09:50 | 2013-06-07 12:50 | 180 | 11kV | 7710 | 65 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 136039 2 Fault operations Sensitive Earth Fault Excavator dropped trees on mains "twice" near pole EO-50168. Excluded OMS 979808 & 979855 | June | 2013 | 2013Q4 | 2013 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2013-06-07 | N | 118.6154 | N | 5 | N | N | 1.1101 | 39.4971 | 5634.2406
[7 empty] | 16755 | 1656 | 981118 | 2013-06-07 17:35 | 2013-06-07 18:31 | 56 | 11kV | 3336 | 139 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 136045 Fdr interrupted to repair faulty ABS 539 | June | 2013 | 2013Q4 | 2013 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2013-06-07 | N | 24 | N | 5 | N | N | 1.1101 | 39.4971 | 2437.8504
[7 empty] | 17805 | 12445 | 981632 | 2013-06-08 11:44 | 2013-06-08 15:30 | 226 | 11kV | 1210 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 136047 B phase DOLF : 10 Amp B Phase 10A Line DOLF blown. Replaced at 1304hrs. B Phase 10A Mullee sub DOLF 70161 blown. Blown LAs at sub replaced also. Excluded OMS No. 980315 | June | 2013 | 2013Q4 | 2013 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-06-08 | N | 201.6667 | N | 1 | N | N | 1.1101 | 39.4971 | 884.2323
[7 empty] | 18010 | 14328 | 981031 | 2013-06-09 04:35 | 2013-06-09 12:30 | 475 | 11kV | 69115 | 238 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Ex Zn12610 Long Jetty section of Pa16 From LB40284to AB40285 interrupted by DOp after truck hit and split pole Cause: Interrupted by DOp after truck hit pole to allow emergency replacement See 981529,31 Exclude 981031,2,3 | June | 2013 | 2013Q4 | 2013 | ZN12610:PA16 | ZN12610:PA16 | ZN12610/000016 | CENTRAL COAST | OH | Not Veg | 2013-06-09 | N | 290.3992 | N | 1 | N | N | 1.1101 | 39.4971 | 50507.2035
[7 empty] | 17367 | 7631 | 981299 | 2013-06-10 02:09 | 2013-06-10 03:20 | 71 | 11kV | 4828 | 68 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 10120 Samuel Forrest - Centre Phase HDO operated. HV fuse failed in service. ME: 981510. Withdrawn: 981299, 981301. | June | 2013 | 2013Q4 | 2013 | ZN10995:PA6 | ZN10995:PA6 | ZN10995/000006 | GEORGES RIVER | OH | Not Veg | 2013-06-10 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 3528.16
[7 empty] | 17442 | 8234 | 981325 | 2013-06-10 08:54 | 2013-06-10 10:50 | 116 | 11kV | 116 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136055 Single phase DOLF : 10 Amp Excluded OMD 981325 Tx Volts: 246V | June | 2013 | 2013Q4 | 2013 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-06-10 | N | 116 | N | 3 | N | N | 1.1101 | 39.4971 | 84.7694
[7 empty] | 18060 | 15427 | 981407 | 2013-06-10 15:05 | 2013-06-10 19:57 | 292 | 11kV | 166650 | 1152 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136057 2 fault operations 3 phase Overcurrent; Sensitive Earth Fault PROT OVERCURRENT ,SEF PERMIT ISSUED TO REPAIR FALLEN MAINS Excluded OMS 981407, 981408, 981409, 981410, 981423 | June | 2013 | 2013Q4 | 2013 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2013-06-10 | N | 144.6615 | N | 3 | N | N | 1.1101 | 39.4971 | 121782.9047
[7 empty] | 17828 | 12534 | 981499 | 2013-06-11 08:21 | 2013-06-11 10:43 | 142 | 11kV | 1420 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 @Auto link CP44773 Chandlers opened Cause: not ascertained Remarks: DOp suspects autolink mechanism is suspect and requires investigation/overhaul See 982083 exclude 9814999,501,93 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-06-11 | N | 142 | N | 2 | N | N | 1.1101 | 39.4971 | 1037.6941
[7 empty] | 18533 | 20166 | 981853 | 2013-06-11 17:01 | 2013-06-11 20:20 | 199 | 11kV | 3980 | 20 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 136065 C phase DOLF : 16 Amp sub isolated to replace 3 x arrester Excluded oms 981853 | June | 2013 | 2013Q4 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-06-11 | N | 199 | N | 2 | N | N | 1.1101 | 39.4971 | 2908.4666
[7 empty] | 18124 | 15928 | 981914 | 2013-06-12 01:12 | 2013-06-12 02:55 | 103 | 11kV | 127974 | 1321 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn14891 Wyong Pa8 "Betty Anne Green" etc fdr tripped on: Relays: Earth Fault, EFI Signals: 11kV trip Tx1 Group Earth Field EFI's: Nil Cause: Suspect UG cable fault from S14690:B to S14691:B to S14689:A. The EFI @ S14690 Betty Anne Green did not operate. T/CON/TPE to check See 982157,9,60,1 Exclude 981914 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | UG | Not Veg | 2013-06-12 | N | 96.8766 | N | 7 | N | N | 1.1101 | 39.4971 | 93519.6246
[7 empty] | 16726 | 1385 | 982153 | 2013-06-12 12:44 | 2013-06-12 14:50 | 126 | 11kV | 903 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 136082 Single phase DOLF : 10 Amp - 982460 LID 136082 Single phase DOLF : 10 Amp - 982462 | June | 2013 | 2013Q4 | 2013 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-06-12 | N | 112.875 | N | 7 | N | N | 1.1101 | 39.4971 | 659.8858
[7 empty] | 16651 | 949 | 982283 | 2013-06-12 14:37 | 2013-06-12 16:50 | 133 | 11kV | 2527 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 136085 A phase DOLF : 10 Amp Excluded OMS 982257 | June | 2013 | 2013Q4 | 2013 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-06-12 | N | 133 | N | 7 | N | N | 1.1101 | 39.4971 | 1846.6571
[7 empty] | 18241 | 16990 | 982471 | 2013-06-12 17:50 | 2013-06-12 23:00 | 310 | 11kV | 2760 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 136090 3 phase section isolated to repair outgoing link Hunter Vale swer sub Excluded oms 982306 | June | 2013 | 2013Q4 | 2013 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2013-06-12 | N | 172.5 | N | 7 | N | N | 1.1101 | 39.4971 | 2016.9266
[7 empty] | 17047 | 4002 | 982400 | 2013-06-12 22:17 | 2013-06-12 23:25 | 68 | 11kV | 102068 | 1501 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | @Zn12580 Erina Pa10 Erina High fdr tripped on A&C Phase IOC EFI Field EFI's: Down to S1489 S14190:B Cause:animals/birds Remarks:possum on UGOH to S18013 removed by DOp See 982487 exclude 982400 | June | 2013 | 2013Q4 | 2013 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Not Veg | 2013-06-12 | N | 68 | N | 7 | N | N | 1.1101 | 39.4971 | 74588.2839
[7 empty] | 17464 | 8435 | 982404 | 2013-06-13 00:50 | 2013-06-13 02:21 | 91 | 11kV | 83447 | 917 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.3155 Double Bay Pnl.19 - tripped on A phase O/C EFI fault check All field EFI's down to S5354 Sw B UG fault in section of feeder from S5354 Sw B to S480 Sw R (N/O) | June | 2013 | 2013Q4 | 2013 | ZN3155:PA19 | ZN3155:PA19 | ZN03155/000019 | WOOLLAHRA | UG | Not Veg | 2013-06-13 | N | 91 | N | 4 | N | N | 1.1101 | 39.4971 | 60980.6063
[7 empty] | 17721 | 11730 | 982367 | 2013-06-12 18:31 | 2013-06-13 03:18 | 527 | 11kV | 60011 | 217 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Rain Light | N | LID 136088 Pelican into mains pole GQ-47489. Section isolated to repair mains Excluded OMS982367 & 982383 | June | 2013 | 2013Q4 | 2013 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-06-12 | N | 276.5484 | N | 7 | N | N | 1.1101 | 39.4971 | 43854.2688
[7 empty] | 18265 | 17167 | 982086 | 2013-06-12 11:09 | 2013-06-13 09:30 | 1341 | 11kV | 10998 | 158 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 136087 3 phase Overcurrent; Earth fault SECTION ISOLATED TO REPAIR MAINS AND SUB 53033 Excluded OMS 982087 & 982115 | June | 2013 | 2013Q4 | 2013 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2013-06-12 | N | 69.6076 | N | 7 | N | N | 1.1101 | 39.4971 | 8037.014
[7 empty] | 17619 | 10287 | 982558 | 2013-06-13 10:55 | 2013-06-13 13:05 | 130 | 11kV | 130 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 136096 A phase DOLF : 10 Amp Excluded OMS 982558 | June | 2013 | 2013Q4 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-06-13 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 17055 | 4053 | 982617 | 2013-06-13 12:28 | 2013-06-13 13:17 | 49 | 11kV | 12045 | 275 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Zn.188 Zetland Pnl.25 tripped on A & B phase O/C and fault check EFIs @ S3457 6702 & 1639 At S6894 Mentore Queen Sw A end box failed see 983505 983503 | June | 2013 | 2013Q4 | 2013 | ZN188:PA25 | ZN188:PA13 | ZN00188/000013 | SYDNEY | Unknown | Not Veg | 2013-06-13 | N | 43.8 | N | 4 | N | N | 1.1101 | 39.4971 | 8802.1307
[7 empty] | 18021 | 14585 | 982820 | 2013-06-13 19:47 | 2013-06-14 03:00 | 433 | 11kV | 88048 | 705 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN 9900 Menai - Pnl 19 - Trip/reclose/trip, C phase overcurrent, Lockout and timing relay. Large tree brought down 2 spans of 11kV mains outside 188 Prices Cct, Woronora. Section of feeder from ABS 35364 on. ME: 982949. Rest Step: 982950. Withdrawn: 982820, 982822, 982826, 982829, 982833, 982841. | June | 2013 | 2013Q4 | 2013 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | OH | Veg | 2013-06-13 | N | 124.8908 | N | 4 | N | N | 1.1101 | 39.4971 | 64342.8814
[7 empty] | 18263 | 17149 | 983024 | 2013-06-14 12:20 | 2013-06-14 12:44 | 24.2 | 11kV | 8905.6 | 368 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Zone Section of Pa1 "Grants Rd" @IR61340 George Bloodtree 0..2 to the extent of the feeder,was interrupted by DOp. Remarks: Remove tree of 11lv feedre adjacent PT11225 George Downes Bloodtree | June | 2013 | 2013Q4 | 2013 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-06-14 | N | 24.2 | N | 2 | N | N | 1.1101 | 39.4971 | 6507.9498
[7 empty] | 17856 | 12754 | 983193 | 2013-06-14 20:56 | 2013-06-14 22:48 | 112 | 11kV | 672 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridege section of Pa4 'Kulnurra' fdr @PT13661 Peats ridge ross 0.3 footpath phase 16A HDO fuse operated Cause: Fuse fatigue. Batch No.2579 See 984007 exclude 983193 | June | 2013 | 2013Q4 | 2013 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2013-06-14 | N | 112 | N | 2 | N | N | 1.1101 | 39.4971 | 491.0778
[7 empty] | 18266 | 17168 | 983222 | 2013-06-15 09:27 | 2013-06-15 12:40 | 193 | 11kV | 6281 | 63 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136113 2 fault operations A phase Overcurrent OH 11kV cable failed at pole 9N-40002 and wrapped around the other 2 phases. Excluded OMS 983222, 983224, 983232 | June | 2013 | 2013Q4 | 2013 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-06-15 | N | 99.6984 | N | 2 | N | N | 1.1101 | 39.4971 | 4589.9695
[7 empty] | 18192 | 16529 | 983329 | 2013-06-15 23:54 | 2013-06-16 01:04 | 70 | 11kV | 132923 | 1931 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12610 Long Jetty 11kv Pa10 "Wamberal" fdr - tripped, reclosed and locked out Relays: IOC, EFI, Fault Check, Timing & Lockout Signals: 11kV trip, Zone Earth EFI's: Nil ABNORMAL:LB50381 closed (5A7) and LB42922 open (3D9) Cause: UG Fault remarks: 11kV UG fault from Zn12610 Pa10 to LB45183. Note: LB45183 is defective and can not be opened or closed fully See 984125,7 Exclude 983329 | June | 2013 | 2013Q4 | 2013 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | UG | Not Veg | 2013-06-15 | N | 68.8364 | N | 2 | N | N | 1.1101 | 39.4971 | 97136.2078
[7 empty] | 18140 | 16019 | 983538 | 2013-06-17 01:59 | 2013-06-17 03:15 | 76 | 11kV | 15813 | 212 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S630 Mascot - Pnl.32 tripped on B phase OC, EF,EFI 11kV UG cable fault from S2200 Champion plugs to S7926 Bourke Rd 77 to S7067 EC of NSW Burrows see 983538 983541 | June | 2013 | 2013Q4 | 2013 | ZN630:PA32 | ZN630:PA18 | ZN00630/000018 | BAYSIDE | UG | Not Veg | 2013-06-17 | N | 74.5896 | N | 2 | N | N | 1.1101 | 39.4971 | 11555.674
[7 empty] | 17199 | 5878 | 983760 | 2013-06-17 14:22 | 2013-06-17 17:00 | 158 | 11kV | 632 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136125 Broken Live Line Clamp Excluded OMS 983760 | June | 2013 | 2013Q4 | 2013 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-06-17 | N | 158 | N | 2 | N | N | 1.1101 | 39.4971 | 461.847
[7 empty] | 18097 | 15774 | 984143 | 2013-06-18 13:41 | 2013-06-18 15:27 | 106 | 11kV | 161143 | 2838 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.342 Paddington Pnl.26 tripped on: B phase O/C Right hand Side, EFI RHS Field EFIs: S6899, S5746, S166, S35521 *operation of EFI @ S35521 delayed restoration, possibly operated from previous failure UG cable fault to be located between S166 Sw A to S35521 Sw A see 984389 984390 984393 984392 GIS: 984147 | June | 2013 | 2013Q4 | 2013 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2013-06-18 | N | 56.7805 | N | 2 | N | N | 1.1101 | 39.4971 | 117758.5515
[7 empty] | 17711 | 11650 | 984293 | 2013-06-18 21:32 | 2013-06-18 23:00 | 87.5167 | 11kV | 875.1667 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 136139 A phase DOLF : 31 Amp Blown Line DOLF | June | 2013 | 2013Q4 | 2013 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2013-06-18 | N | 87.5167 | N | 2 | N | N | 1.1101 | 39.4971 | 639.546
[7 empty] | 17225 | 6238 | 984342 | 2013-06-19 08:08 | 2013-06-19 09:26 | 78 | 11kV | 6942 | 89 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.384 Camperdown - Panel 4 tripped on Earth Fault & EFI UG cable fault to S5759 see 984790 GIS 984791 | June | 2013 | 2013Q4 | 2013 | ZN384:PA4 | ZN384:PA4 | ZN00384/000004 | SYDNEY | UG | Not Veg | 2013-06-19 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 5073.0088
[7 empty] | 17256 | 6597 | 984394 | 2013-06-19 09:24 | 2013-06-19 10:58 | 94 | 11kV | 74008 | 889 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | ZN.35500 - Top Ryde - Pnl 16 "Top Ryde Aux & Lane Cove Goulding" Tripped on: Relays:Instantaneous OC AB phase. Signals:11kv trip, Battery Charger A defect, Tx 3 415v no volt, Change over inoperative, AC supply fail. Cause:Tree branch on OH Mains Tree branch on Cnr Kulgoa and Blaxland Rd. See 2nd 984972 Exclude 984 394,406,402,396,414 | June | 2013 | 2013Q4 | 2013 | ZN4545:PA24 | ZN35500:PA16 | ZN35500/000016 | RYDE | OH | Veg | 2013-06-19 | N | 83.2486 | N | 4 | N | N | 1.1101 | 39.4971 | 54082.8635
[7 empty] | 18105 | 15831 | 984432 | 2013-06-19 10:18 | 2013-06-19 15:21 | 303 | 11kV | 11715 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Light | N | ZN.12650 - West Gosford - Ex 11kV Pnl 1 "Dog Trap Rd" Fdr - Recloser 44853 'Ourimbah Bumble' Tripped, Reclosed,Tripped & Locked-Out Signals : CP44853 - EF trip, SEF trip, CP Open Cause:Tree/Branch brough down O/H HV & LV. See OMS 985138,141,142 Exclude 984432,444 | June | 2013 | 2013Q4 | 2013 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-06-19 | N | 266.25 | N | 4 | N | N | 1.1101 | 39.4971 | 8560.9765
[7 empty] | 18459 | 19174 | 984550 | 2013-06-19 13:42 | 2013-06-19 19:40 | 358.2333 | 11kV | 4657.0333 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136150 3 Phase fault BURNT OFF TAPPING AT POLE JR-42441 SECTION ISOLATED FOR REPAIR OF 3 X HV TAPPINGS AND REPLACE 2 X DISCS CC1: 06-"Urgent - O.H Mains - No others" FRC1: 300-"Specify details by voice" | June | 2013 | 2013Q4 | 2013 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2013-06-19 | N | 358.2333 | N | 4 | N | N | 1.1101 | 39.4971 | 3403.2226
[7 empty] | 18521 | 20056 | 984716 | 2013-06-20 07:40 | 2013-06-20 09:24 | 104 | 11kV | 208 | 2 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | S7327 Centenary Institute RPA - 11kV RMI No 1 - Tripped on Low Gas - Sub has parallel trip coils RMI needs to be replaced | June | 2013 | 2013Q4 | 2013 | ZN384:PA42 | ZN2568:PA6 | ZN02568/000006 | SYDNEY | Unknown | Not Veg | 2013-06-20 | N | 104 | N | 3 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 16934 | 3141 | 984924 | 2013-06-20 16:25 | 2013-06-20 20:45 | 260 | 11kV | 7540 | 29 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 136168 Section isolated to repair broken insulator/crossarm pole IR-62463 found on fdr patrol. Excluded OMS 985000 & 984924 | June | 2013 | 2013Q4 | 2013 | 238:34141 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2013-06-20 | N | 260 | N | 3 | N | N | 1.1101 | 39.4971 | 5510.0096
[7 empty] | 18407 | 18549 | 985034 | 2013-06-20 17:40 | 2013-06-20 22:15 | 275 | 11kV | 275 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136170 Broken LL Lead | June | 2013 | 2013Q4 | 2013 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2013-06-20 | N | 275 | N | 3 | N | N | 1.1101 | 39.4971 | 200.9619
[7 empty] | 18206 | 16647 | 985091 | 2013-06-21 07:45 | 2013-06-21 16:28 | 523 | 11kV | 37413 | 553 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 5 - Earth Fault, Fault check, Zone earth, Group 2 earth, Field EFIs. 11kV feeder fault between S 1301 and S 49897. Extended outage for S 49897 and S 7885 due to restoration via LV//. ME: 986589. Rest Steps: 986592, 986593, 986595. Withdrawn: 985091, 985100, 985119, 985120. | June | 2013 | 2013Q4 | 2013 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-06-21 | N | 67.6546 | N | 2 | N | N | 1.1101 | 39.4971 | 27340.3169
[7 empty] | 17963 | 13766 | 985436 | 2013-06-22 00:37 | 2013-06-22 02:10 | 93 | 11kV | 1860 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136186 A phase DOLF : 16 Amp Excluded OMS 985436 | June | 2013 | 2013Q4 | 2013 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | UG | Not Veg | 2013-06-22 | N | 93 | N | 1 | N | N | 1.1101 | 39.4971 | 1359.2331
[7 empty] | 16686 | 1127 | 985413 | 2013-06-21 18:18 | 2013-06-22 02:55 | 517 | 11kV | 517 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136187 A phase DOLF : 10 Amp Excluded OMS 985413, 985438 | June | 2013 | 2013Q4 | 2013 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | UG | Not Veg | 2013-06-21 | N | 517 | N | 2 | N | N | 1.1101 | 39.4971 | 377.8084
[7 empty] | 17340 | 7387 | 985642 | 2013-06-23 09:37 | 2013-06-23 10:45 | 68 | 11kV | 680 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14891 Wyong Section of Pa12 @Autolink 44773 c phase (footpath side) tripped ABRNORMAL: REC49506 Spring rd (PR 1/C7) closed ; AB43646 (PR 1/D5) open LB40899(PR 1/D3) closed; LB40546 (PR 1/C2) open See D&R 315858 Cause: not ascertained Remarks: Autolink 44773 has several times recently as per DOp information See 985959 exclude 985642,4,7,61 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-06-23 | N | 68 | N | 8 | N | N | 1.1101 | 39.4971 | 496.9239
[7 empty] | 16921 | 3047 | 985648 | 2013-06-23 09:47 | 2013-06-23 11:05 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136203 Single phase DOLF : 3 Amp Excluded OMS 985464 | June | 2013 | 2013Q4 | 2013 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | UG | Not Veg | 2013-06-23 | N | 78 | N | 8 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 17413 | 8072 | 985694 | 2013-06-23 11:39 | 2013-06-23 14:03 | 144 | 11kV | 278539 | 2319 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Rain Heavy | N | @Zn3922 Drummoyne - 11kv Panel No.5 "Sub 36165, Sub 2401, Sub 1528" feeder tripped Relays: C phase timed O/C, EFI fault check Signals: 11kv trip, No.1 Group earth, Zone earth Field EFI's: Sub 36465, Sub 7583, Sub 7681, Sub 7682, Sub 7683 Remarks: End box fault. Suspect Flash over Related jobs: #985694, 985709, 985703, 986555, 986569, 986564, 986568 | June | 2013 | 2013Q4 | 2013 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | Unknown | Not Veg | 2013-06-23 | N | 120.1117 | N | 8 | N | N | 1.1101 | 39.4971 | 203548.0857
[7 empty] | 17622 | 10336 | 985723 | 2013-06-23 14:30 | 2013-06-23 15:03 | 33 | 11kV | 55803 | 1691 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.901 Surry Hills Pnl.13 tripped on Earth Fault, EFI UG cable fault - front line feeder fault from Panel 13 to S3157 Cooper Young Sw/A. Pit cover blown off nr Goodlett Lane | June | 2013 | 2013Q4 | 2013 | ZN901:PA13 | ZN901:PA31 | ZN00901/000031 | SYDNEY | UG | Not Veg | 2013-06-23 | N | 33 | N | 8 | N | N | 1.1101 | 39.4971 | 40779.1865
[7 empty] | 16886 | 2666 | 985674 | 2013-06-23 10:53 | 2013-06-23 15:18 | 265.5 | 11kV | 68009.5 | 526 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 136207 1 fault operation A & C phase Overcurrent Note A/R OFF for SI 32962 Bird at pole SI-91330 - blown disc insulators Excluded OMS 985674 & 985685 | June | 2013 | 2013Q4 | 2013 | 513:48052 | 513:83503 | ZN00513/083503 | SINGLETON | OH | Not Veg | 2013-06-23 | N | 129.2956 | N | 8 | N | N | 1.1101 | 39.4971 | 49699.3367
[7 empty] | 16822 | 2171 | 985715 | 2013-06-23 13:12 | 2013-06-23 17:28 | 256 | 11kV | 209229 | 1504 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Heavy | N | LID 136205 2 fault operations A phase Earth fault L/A blown at UGOH pole IT-91764 replaced. Excluded oms 985715 | June | 2013 | 2013Q4 | 2013 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | OH | Not Veg | 2013-06-23 | N | 139.115 | N | 8 | N | N | 1.1101 | 39.4971 | 152898.382
[7 empty] | 18558 | 20405 | 985777 | 2013-06-23 17:02 | 2013-06-23 17:38 | 36 | 11kV | 26892 | 747 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN.15011 - Beacon Hill - Section of 11kV Fdr ex pnl 2. USL21320 has bond burnt off Centre phase bond burnt off @ USL 21320 (Zone Side) Exclude 985770,777,782,787 | June | 2013 | 2013Q4 | 2013 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2013-06-23 | N | 36 | N | 8 | N | N | 1.1101 | 39.4971 | 19651.8804
[7 empty] | 18336 | 17761 | 986561 | 2013-06-23 17:33 | 2013-06-23 17:38 | 5 | 11kV | 5960 | 1192 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Rain Light | N | Zn.15008 - Harbord - ex Pnl PL, Rec 62774 "Kentwell Pittwater" has tripped Relays: OC, Battery Bad, Warning, Lockout Failed on energising During Fault restoration recloser tripped with SEL and REC non auto. Suspect faulty current reading indicates higher than feeder load. | June | 2013 | 2013Q4 | 2013 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2013-06-23 | N | 5 | N | 8 | N | N | 1.1101 | 39.4971 | 4355.3922
[7 empty] | 18114 | 15873 | 985870 | 2013-06-24 04:04 | 2013-06-24 05:20 | 76 | 11kV | 111796 | 1934 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | ZN 9700 Kirrawee - Pnl 11 - Trip/reclose/trip, B phase Earth leakage, fault check, Group Earth, Field EFIs. Transformer failure at PT 9432 Auburn Forest. 2 blown HDOs. Supply restored via LV//. ME: 985957. Rest Step: 985958. Withdrawn: 985970, 985871. | June | 2013 | 2013Q4 | 2013 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | OH | Not Veg | 2013-06-24 | N | 57.8056 | N | 3 | N | N | 1.1101 | 39.4971 | 81697.2194
[7 empty] | 18209 | 16681 | 986187 | 2013-06-24 13:12 | 2013-06-24 15:40 | 148 | 11kV | 309703 | 2370 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 Meadowbank 11kV panel 41 tripped Relays: Earth fault, EFI, Fault Check Signals: 11kV trip, No3 Group Earth, Zone Earth Cause: Cable fault from S35110 to S8530 to S7890 tee S2810 See OMS 990333 990335 990334 986187 | June | 2013 | 2013Q4 | 2013 | ZN4545:PA41 | ZN4545:PA29 | ZN04545/000029 | RYDE | UG | Not Veg | 2013-06-24 | N | 130.6764 | N | 3 | N | N | 1.1101 | 39.4971 | 226321.8177
[7 empty] | 18199 | 16594 | 986400 | 2013-06-24 19:27 | 2013-06-24 20:05 | 38 | 11kV | 35128 | 1137 | HV | Overload | Utility Process Issue | U/G Cable | Unplanned | Rain Heavy | N | Zn.711 Blackwattle Bay Pnl.21 tripped on A phase O/C Cross zone circulating current -tripped during cross zone switching to relieve load on highly loaded Panel 21 @ Blackwattle Bay Could not switch within Blackwattle Bay due to defective interconnecting panels. see 986550 986551 | June | 2013 | 2013Q4 | 2013 | ZN711:PA21 | ZN188:PA43 | ZN00188/000043 | SYDNEY | UG | Not Veg | 2013-06-24 | N | 30.8953 | N | 3 | N | N | 1.1101 | 39.4971 | 25670.5063
[7 empty] | 17036 | 3963 | 986432 | 2013-06-25 00:23 | 2013-06-25 03:40 | 197 | 11kV | 77616 | 1808 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | ZN 9037 Miranda - Pnl 8 - Opened for safety. At PT 9458, large tree brought down overhead mains adjacent to PT and an LV// was found to be in. Its removal delayed the restoration time. AOp opened distributor for safety reasons. Minor part of distributor will be restored upon completion of repairs. ME: 987580. Rest Steps: 987581, 987582. Withdrawn: 986432. | June | 2013 | 2013Q4 | 2013 | ZN9037:PA8 | ZN9037:PA8 | ZN09037/000008 | SUTHERLAND | OH | Veg | 2013-06-25 | N | 42.9292 | N | 7 | N | N | 1.1101 | 39.4971 | 56719.4835
[7 empty] | 17791 | 12348 | 986440 | 2013-06-25 01:31 | 2013-06-25 06:30 | 299 | 11kV | 365823 | 1682 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 10994 Mortdale - Pnl 4 - A phase IOC, Earth fault, Timing, Lockout, EFIs. Suspected underground fault from Lk 30139 to LB 31013 to S 10621. ME: 987768. Rest Steps: 987769, 987771. Withdrawn: 986440. | June | 2013 | 2013Q4 | 2013 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | UG | Not Veg | 2013-06-25 | N | 217.4929 | N | 7 | N | N | 1.1101 | 39.4971 | 267332.6584
[7 empty] | 18178 | 16385 | 986530 | 2013-06-25 09:13 | 2013-06-25 10:32 | 79 | 11kV | 107237 | 1715 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | At Zone 2196 Milperra 11kv Panel 25 'Sub 4684 Turvey River' Tripped out: Relays: A,B,C phase IOC Signals: 11kv trip Remarks: weather related. Feeder patrolled, no problem found Related jobs: #986530, 986546, 987186, 987188, 987184 | June | 2013 | 2013Q4 | 2013 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-06-25 | N | 62.5289 | N | 7 | N | N | 1.1101 | 39.4971 | 78365.6366
[7 empty] | 18132 | 15970 | 986685 | 2013-06-25 12:23 | 2013-06-25 13:20 | 57 | 11kV | 1197 | 21 | HV | Vandalism | 3rd Party Impact | U/G Cable | Unplanned | Rain Light | N | ZN 9301 Kurnell - Pnl 13 - B phase Timed OC, Fault check, Lockout and timing relays, Field EFIs. At S 9011, copper theif stripped out LV board then attempted to remove HV cables. Whoops.... ME: 987546. Withdrawn: 986685. | June | 2013 | 2013Q4 | 2013 | ZN9301:PA13 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | UG | Not Veg | 2013-06-25 | N | 57 | N | 7 | N | N | 1.1101 | 39.4971 | 874.7323
[7 empty] | 17224 | 6237 | 986709 | 2013-06-25 12:48 | 2013-06-25 13:45 | 57 | 11kV | 60849 | 1636 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12580 Erina 11kvPa4 labelled "PT Frederick/Springfield" tripped,reclosed & locked out Relays: Right Lef: Earth fault, EFI Signals: 11kv trip, Zone Earth, Group 1 Earth Cause: UG Fault. Fronline fdr fault form Pa14 to AB4891 to LK42184 to LK40353 See 988236,9 Exclude 986709 | June | 2013 | 2013Q4 | 2013 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | UG | Not Veg | 2013-06-25 | N | 37.1938 | N | 7 | N | N | 1.1101 | 39.4971 | 44466.6545
[7 empty] | 17495 | 8775 | 986904 | 2013-06-25 16:53 | 2013-06-25 19:36 | 163 | 11kV | 14018 | 86 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S47576 Pritchard Yarrara 400A fuse blown on A and B phase of distribiutor 1 At S47576 Pritchard Yarrara 400A fuse blown on A B and C phase of distributor 2. Cause: LV parallel failure - Dop found links 18393 and 2813 in See OMS 987073 976094 | June | 2013 | 2013Q4 | 2013 | ZN965:PA47 | ZN965:PA47 | ZN00965/000047 | HORNSBY | OH | Veg | 2013-06-25 | N | 163 | N | 7 | N | N | 1.1101 | 39.4971 | 10243.9409
[7 empty] | 17871 | 12874 | 986991 | 2013-06-25 22:38 | 2013-06-25 23:20 | 42 | 11kV | 2604 | 62 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136232 C phase DOLF : 20 Amp 247V. 110A, 140A, 150A. Excluded oms 986991/3 | June | 2013 | 2013Q4 | 2013 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | UG | Not Veg | 2013-06-25 | N | 42 | N | 7 | N | N | 1.1101 | 39.4971 | 1902.9264
[7 empty] | 18284 | 17315 | 987034 | 2013-06-26 07:32 | 2013-06-26 11:05 | 213 | 11kV | 302211 | 3058 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | ZN 10994 Mortdale - Pnl 2L - SEL left trip. 11kV bond burnt off at PT 10283. Lots of calls came in after the fact and have been withdrawn as they had power restored and were simply ringing up to inform us that the power was out before. ME: 988059. Rest Steps: 988061, 4, 5, 6. Withdrawn: 987034, 5, 9, 987130, 2, 987272, 987301. | June | 2013 | 2013Q4 | 2013 | ZN10994:PA2 | ZN10994:PA2 | ZN10994/000002 | GEORGES RIVER | OH | Not Veg | 2013-06-26 | N | 98.8264 | N | 4 | N | N | 1.1101 | 39.4971 | 220846.8851
[7 empty] | 17510 | 8896 | 987367 | 2013-06-26 14:52 | 2013-06-26 16:44 | 112 | 11kV | 67167 | 708 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 6 tripped on Earth Fault, EFI, fault check and 11kV trip Cause: Suspect UG feeder fault between S4648 Baronga Wallaonga to S4650 Wallaong Combe Tee PT2318 Glouchester Ave See OMS 990313 990316 990315 987367 | June | 2013 | 2013Q4 | 2013 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2013-06-26 | N | 94.8686 | N | 4 | N | N | 1.1101 | 39.4971 | 49083.6625
[7 empty] | 17876 | 12910 | 987460 | 2013-06-26 19:28 | 2013-06-26 20:40 | 72 | 11kV | 720 | 10 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone section of Pa12 "yarramalong fdr" Recloser upstream did not operate so autolink should not have operated live. Protection malfunction See 989065 exclue 987460,1,2 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-06-26 | N | 72 | N | 4 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 18171 | 16340 | 987407 | 2013-06-26 16:29 | 2013-06-26 21:10 | 281 | 11kV | 562 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 136243 A phase burnt off bond at dolf Excluded oms 987407 | June | 2013 | 2013Q4 | 2013 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2013-06-26 | N | 281 | N | 4 | N | N | 1.1101 | 39.4971 | 410.693
[7 empty] | 16611 | 731 | 987905 | 2013-06-27 17:51 | 2013-06-27 21:05 | 194.5 | 11kV | 1167 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 136252 C phase DOLF : 20 Amp Please patrol. Access very difficult due to wet weather. CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | June | 2013 | 2013Q4 | 2013 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2013-06-27 | N | 194.5 | N | 1 | N | N | 1.1101 | 39.4971 | 852.8092
[7 empty] | 17292 | 7012 | 987949 | 2013-06-28 02:22 | 2013-06-28 04:40 | 138 | 11kV | 224573 | 2369 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Zn12610 Long Jetty 11kv fdr #24 "Wamberal" tripped reclosed tripped & locked out Relays: Recloser lockout relay, A&B Phase Inst. O/C trip Signals: 11kv trip, 11kv Open Abnormal: AB43617 closed, LB45184 open due to Pa10 front line fdr fault Remarks: B or centre phase to AB41974 load side failed LV// USL 35565, 18923, 35571 ,388266, 35475, 35471 Switching Tag @AB44580 See 989145,6,7,8,9 Exclude 987949,50,1 | June | 2013 | 2013Q4 | 2013 | ZN12610:PA24 | ZN12610:PA24 | ZN12610/000024 | CENTRAL COAST | OH | Not Veg | 2013-06-28 | N | 94.7965 | N | 6 | N | N | 1.1101 | 39.4971 | 164111.3246
[7 empty] | 17584 | 9727 | 987989 | 2013-06-28 08:12 | 2013-06-28 09:28 | 76 | 11kV | 108908 | 1433 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S1193 Lindfield Panel 15 tripped on Relays: A Phase IOC with EFI Signals: 11kV trip Tx 2 Group Earth Abnormal Switching: SW/D Closed at S312 SW/A open at S35523 Cause; 11kV Feeder fault between Pa15 to S3420 to S591 See OMS 990294 987989 988010 | June | 2013 | 2013Q4 | 2013 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | UG | Not Veg | 2013-06-28 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 79586.7542
[7 empty] | 17986 | 14135 | 987959 | 2013-06-28 06:31 | 2013-06-28 10:30 | 239 | 11kV | 2390 | 10 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 'cedar northcott' fdr beyond CP 44773 auto link defective previously emailed Engineering officer 4th occurence. See 989161 exclude 987959,70 | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-06-28 | N | 239 | N | 6 | N | N | 1.1101 | 39.4971 | 1746.5415
[7 empty] | 18109 | 15850 | 988146 | 2013-06-28 11:32 | 2013-06-28 14:15 | 163 | 11kV | 125270 | 865 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Heavy | N | At ZN2196 Milperra Panel 25 The Turvey River fdr tripped on Basler Relay 50TB. Bph timed O/L Remarks: Air break switch - detail below. AB 179 failed on Bph post insulator Related jobs: #989018, 988161, 988146, 988156, 989022, 989023 | June | 2013 | 2013Q4 | 2013 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-06-28 | N | 144.8208 | N | 6 | N | N | 1.1101 | 39.4971 | 91543.6212
[7 empty] | 18314 | 17584 | 988300 | 2013-06-28 15:53 | 2013-06-28 17:45 | 112 | 11kV | 112 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 136264 A phase DOLF : 10 Amp Excluded OMS 988300 | June | 2013 | 2013Q4 | 2013 |  |  |  |  | UG | Not Veg | 2013-06-28 | N | 112 | N | 6 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 18360 | 17935 | 988345 | 2013-06-28 14:21 | 2013-06-28 18:10 | 229 | 11kV | 243 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | ZN 9700 Kirrawee - Rec 35006 - Opened for Safety Reasons. AOp opened Recloser to allow HV fuse replacement at PT 9463 and subsequent replacement of B phase surge arrestor. ME: 988944. Rest Step: 988945. Withdrawn: 988345. | June | 2013 | 2013Q4 | 2013 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2013-06-28 | N | 121.5 | N | 6 | N | N | 1.1101 | 39.4971 | 177.5772
[7 empty] | 17446 | 8289 | 988397 | 2013-06-29 01:51 | 2013-06-29 02:46 | 55 | 11kV | 110 | 2 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | @Zn2310 Punchbowl Panel 23 "S.48156 Roseland Ave #2" tripped with the following: Relays: translay flag Signal: 11kv trip, Zone earth, Group Earth Field EFI's: S48156 Relays @ S2321 Roselands Ave: Translay Flag Remarks: UG fault. Suspected underground feeder fault from S48156 Roseland Av #2 (sw/B) to S2321 Roselands Av (#1 HV CB) Related jobs: #989293, 988397 | June | 2013 | 2013Q4 | 2013 | ZN2310:PA23 | ZN2310:PA9 | ZN02310/000009 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-06-29 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 17567 | 9530 | 988497 | 2013-06-29 11:19 | 2013-06-29 12:20 | 61 | 11kV | 25315 | 415 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12650 West Gosford Section of Pa13 'The Hanlan st fdr' from USL40339 to S18118 to S18689 centre phase bond found burnt off. See 989164 exclude 988497 | June | 2013 | 2013Q4 | 2013 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2013-06-29 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 18499.4553
[7 empty] | 17997 | 14184 | 988569 | 2013-06-29 15:32 | 2013-06-29 18:05 | 153 | 11kV | 153 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Light | N | LID 136268 A phase DOLF : 10 Amp Excluded OMS 988569 | June | 2013 | 2013Q4 | 2013 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2013-06-29 | N | 153 | N | 3 | N | N | 1.1101 | 39.4971 | 111.8079
[7 empty] | 17305 | 7129 | 988707 | 2013-06-30 10:47 | 2013-06-30 11:40 | 53.15 | 11kV | 531.5 | 10 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone Section of Pa12 'yarramalong' @Autolink 44773 Cph tripped Cph roadside fuse failed. Autolink 44773 protection operated numerous times within a week CC1: 22-"Refer to SOp" | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-06-30 | N | 53.15 | N | 3 | N | N | 1.1101 | 39.4971 | 388.4045
[7 empty] | 16959 | 3309 | 988747 | 2013-06-30 13:06 | 2013-06-30 14:02 | 56 | 11kV | 114176 | 2107 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | LID 136273 Tapping open at JU-71084 Excluded OMS 988747 | June | 2013 | 2013Q4 | 2013 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2013-06-30 | N | 54.1889 | N | 3 | N | N | 1.1101 | 39.4971 | 83436.4532
[7 empty] | 17985 | 14134 | 988754 | 2013-06-30 13:32 | 2013-06-30 15:10 | 98.4 | 11kV | 984 | 10 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone Section of Pa12 'yarramalong' @Autolink 44773 Cph tripped Cph roadside fuse failed. Autolink 44773 protection operated numerous times within a week. 20Amps HV drop out fuse used to replace suspect autolink element. Please investigate | June | 2013 | 2013Q4 | 2013 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-06-30 | N | 98.4 | N | 3 | N | N | 1.1101 | 39.4971 | 719.0782
[7 empty] | 15671 | 10714 | 989378 | 2013-07-01 19:16 | 2013-07-01 20:32 | 76 | 11kV | 11520 | 171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Erina Zone 11kv Pa7 "S18765 Entrance Ernest 0.2 & AB41037" tripped with the following: Relays: Earth Fault Relay EFI Signals: Nil EFI's: S18675 S18072 S18751 S18047 S18193 S18191 Remarks: Suspected UG cable fault between S18193 Erina Fair Chiller Sw/A to S18191 Erina Fair Food Hall Sw/B Note: EFI's at subs 18193 & 18191 Dropped upon resotring supply after the fault was isolated. They need to be tested and/or replaced See 990566,7 Exclude 989378 | July | 2013 | 2014Q1 | 2014 | ZN12580:PA7 | ZN12580:PA7 | ZN12580/000007 | CENTRAL COAST | UG | Not Veg | 2013-07-01 | N | 67.3684 | N | 1 | N | N | 1.1101 | 39.4971 | 8418.4762
[7 empty] | 16420 | 19437 | 989401 | 2013-07-02 03:00 | 2013-07-02 07:45 | 285 | 11kV | 159463 | 848 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn12600 Lisarow Pa13 "Brush rd" feeder tripped on SEF Cause: OH Down Remarks: One Bay of 11kv mains down on ground near PT12227 Brush Ourimbah 0.1 Section of feeder from AB44456 to S14776 Old Farm Shirley SwB tee to PT14372 Shirley Coraki tee to PT 12227 Brush Ourimbah 1.4 See 990642,4,8,9 Exclude 989401,14 | July | 2013 | 2014Q1 | 2014 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2013-07-02 | N | 188.046 | N | 2 | N | N | 1.1101 | 39.4971 | 116530.857
[7 empty] | 15602 | 9629 | 989738 | 2013-07-02 14:47 | 2013-07-02 16:38 | 111 | 11kV | 64798 | 1068 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2835 Burwood Zn P29 tripped on it receive At S570 telecom burwood hv cb tripped on tx2 b/c phase diff, it send Remarks: protection failure. At S570 telecom burwood from sw b to hv cb tee no2 tx Related jobs: #989738, 989742, 989751, 991865, 991869, 991859, 991855 | July | 2013 | 2014Q1 | 2014 | ZN2835:PA29 | ZN2835:PA29 | ZN02835/000029 | BURWOOD | UG | Not Veg | 2013-07-02 | N | 60.6723 | N | 2 | N | N | 1.1101 | 39.4971 | 47352.4672
[7 empty] | 16480 | 20259 | 990179 | 2013-07-03 12:11 | 2013-07-03 14:45 | 154 | 11kV | 51464 | 723 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn.3154 - St Ives - Pnl 22 "S.7962 Mona Vale Link" Fdr Tripped Relays: A Phase Inst, Timing, Lockout Signals: 11kV Trip Branch dropped on HV mains in ayers rd tripping fdr. PT1798 found in LV// resulting in LV mains burning down See OMS 990546 & 990547 Exclude 990179,180,184 | July | 2013 | 2014Q1 | 2014 | ZN3154:PA22 | ZN3154:PA22 | ZN03154/000022 | KU-RING-GAI | OH | Veg | 2013-07-03 | N | 71.1812 | N | 1 | N | N | 1.1101 | 39.4971 | 37608.3733
[7 empty] | 15943 | 13634 | 990635 | 2013-07-04 12:42 | 2013-07-04 16:07 | 205 | 11kV | 103234 | 1072 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 136316 2 fault operations B & C phase Earth fault, Overcurrent tree on OHM at pole JU-90065 Excluded OMS No 990635. | July | 2013 | 2014Q1 | 2014 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2013-07-04 | N | 96.3004 | N | 3 | N | N | 1.1101 | 39.4971 | 75440.3623
[7 empty] | 15469 | 8126 | 990583 | 2013-07-04 11:34 | 2013-07-04 20:04 | 510 | 11kV | 134642 | 2025 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | @Zn12570 Avoca Pa37L "Avoca Beach" fdr tripped on Relays: Bph IOC and EI Signals:11kv trip EFI's: S18349 S49066 Cause: UGOH short circuit Remarks:11kv UGOH failed in Avoca Drive oppposite the Avoca Bowling Club. Section of feeder from S49066 to S18135 to AB44670 tee to PT18112. See 994695,7,8 Exclude 990583,96,646,838 | July | 2013 | 2014Q1 | 2014 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | Unknown | Unknown | 2013-07-04 | N | 66.4899 | N | 3 | N | N | 1.1101 | 39.4971 | 98392.4023
[7 empty] | 15714 | 11084 | 990786 | 2013-07-04 17:08 | 2013-07-04 22:00 | 291.8167 | 11kV | 448.1167 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 136318 Single phase DOLF : 10 Amp LA's blown Excluded OMS 990786 | July | 2013 | 2014Q1 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-07-04 | N | 224.0583 | N | 3 | N | N | 1.1101 | 39.4971 | 327.4704
[7 empty] | 16490 | 20347 | 990857 | 2013-07-05 00:32 | 2013-07-05 01:05 | 33 | 11kV | 48786 | 1549 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @ S2196 MILPERRA PANEL 5 'S8696 MARIGOLD AMOUR NO 4' feeder tripped on Relays - SEF, Lockout Signals - 11KV trip Remarks: Bond. 11KV Bond Burnt off footpath side of AB 2800 Related jobs: #990857, 991746, 991747 | July | 2013 | 2014Q1 | 2014 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-07-05 | N | 31.4952 | N | 6 | N | N | 1.1101 | 39.4971 | 35651.3699
[7 empty] | 15512 | 8600 | 990858 | 2013-07-05 00:47 | 2013-07-05 02:20 | 93 | 11kV | 88867 | 1141 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15012 Killarney, Panel 8 Fdr CB tripped, reclosed tripped and locked out on earth fault, reclose, lockout, fault check, frame leakage, efi. 11kv TRIP, zONE EARTH. Field efi's down at S.16789, S.16846. 11kV UG cable fault beyond S.17136 Sw B | July | 2013 | 2014Q1 | 2014 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | UG | Not Veg | 2013-07-05 | N | 77.8852 | N | 6 | N | N | 1.1101 | 39.4971 | 64941.3825
[7 empty] | 16096 | 15975 | 990861 | 2013-07-05 06:07 | 2013-07-05 08:00 | 113 | 11kV | 5989 | 53 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ Zn188 Zetland Pnl.31 gave signals: Zone Earth, Group Earth - EFi relay. Field EFI's: S386 S35946 S7723 S6894 S1639(x2) @ S1639 Dunning Cres - 11kV CB and No.2 Tx 415V ACB tripped on translay IT/S, EFIs Abnormals: Pa 25 @ Zetland to Sw A @ S3457 O/O/S (CB replacement) - Sw C @ S386 Closed UG cable fault between Sw B @ S6702, Sw A @ S123 and 11kV CB @ S1639 | July | 2013 | 2014Q1 | 2014 | ZN188:PA25 | ZN188:PA25 | ZN00188/000025 | SYDNEY | UG | Not Veg | 2013-07-05 | N | 113 | N | 6 | N | N | 1.1101 | 39.4971 | 4376.5846
[7 empty] | 15524 | 8748 | 990879 | 2013-07-05 08:05 | 2013-07-05 09:30 | 85 | 11kV | 340 | 4 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 136320 B & C phase DOLF : 10 Amp Pelicans hit mains adjacent pole HR-95402 Excluded OMS 990879 & 990886 | July | 2013 | 2014Q1 | 2014 | 503:48017 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2013-07-05 | N | 85 | N | 6 | N | N | 1.1101 | 39.4971 | 248.462
[7 empty] | 16471 | 20170 | 991199 | 2013-07-05 16:59 | 2013-07-05 18:35 | 96 | 11kV | 11712 | 122 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @PT1975 Drone St Foot Path HDO Bond HR Remarks: @PT 1975 Drone St Foot Path side HDO top bond HR customers restored via LV// links 11600 & 16557 & N/O dist No2 @ Sub 8932 Drone Hebe. Related jobs: #991199, 991740 | July | 2013 | 2014Q1 | 2014 | ZN1285:PA27 | ZN1285:PA27 | ZN01285/000027 | STRATHFIELD | OH | Not Veg | 2013-07-05 | N | 96 | N | 6 | N | N | 1.1101 | 39.4971 | 8558.7842
[7 empty] | 16102 | 16010 | 991226 | 2013-07-05 19:09 | 2013-07-05 20:42 | 93 | 11kV | 47849 | 531 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Zn2632 Epping 11kV Panel 3 tripped on Relays: Earth leakage, fault check and EFI Cause not ascertained. 993444 993447 993446 991226 | July | 2013 | 2014Q1 | 2014 | ZN2635:PA3 | ZN2635:PA32 | ZN02635/000032 | RYDE | OH | Veg | 2013-07-05 | N | 90.1111 | N | 6 | N | N | 1.1101 | 39.4971 | 34966.6379
[7 empty] | 16183 | 16906 | 991268 | 2013-07-06 02:32 | 2013-07-06 03:56 | 84 | 11kV | 145152 | 1728 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ ZN 9118 CRONULLA 11kv VCB panel 6 "S-9508 Croyden Kingsway No.2" feeder tripped on: Relays: Earth Fault, EFI, Ceiling Contactor Field EFI's: Nil Signals: 11kv trip zone earth, No.1 Tx group earth Remarks: UG fault. Suspect 11kv feeder fault from ZN9118 Cronulla panel 6 to S-9508 Croydon Kingsway No.2 SW-A Related jobs: #991268, 991756 | July | 2013 | 2014Q1 | 2014 | ZN9118:PA6 | ZN9118:PA6 | ZN09118/000006 | SUTHERLAND | UG | Not Veg | 2013-07-06 | N | 84 | N | 7 | N | N | 1.1101 | 39.4971 | 106072.8003
[7 empty] | 15003 | 2887 | 991270 | 2013-07-06 05:45 | 2013-07-06 10:55 | 310 | 11kV | 1240 | 4 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 136333 A phase DOLF : 10 Amp Dead possum on pole. Volts = 243V, I = 17A Excluded OMS 991270 | July | 2013 | 2014Q1 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-07-06 | N | 310 | N | 7 | N | N | 1.1101 | 39.4971 | 906.1554
[7 empty] | 16406 | 19226 | 991407 | 2013-07-06 12:55 | 2013-07-06 14:00 | 65 | 11kV | 130 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 136335 B & C phase DOLF : 31 Amp Cockatoo dead at sub Excluded OMS 991407 | July | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-07-06 | N | 65 | N | 7 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 16275 | 17725 | 991404 | 2013-07-06 12:42 | 2013-07-06 17:15 | 273 | 11kV | 32326 | 305 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At Castle Cove Panel 46 tripped Relays: Translay and frame leakage Signals: 11kV trip. S35317 Stirling Victoria burnt to the ground see OMS 992942 992963 992944 992945 991404 991414 | July | 2013 | 2014Q1 | 2014 | ZN3425:PA46 | ZN3425:PA46 | ZN03425/000046 | WILLOUGHBY | UG | Not Veg | 2013-07-06 | N | 105.9869 | N | 7 | N | N | 1.1101 | 39.4971 | 23622.8873
[7 empty] | 15178 | 4404 | 991487 | 2013-07-06 18:59 | 2013-07-06 23:12 | 253 | 11kV | 151478 | 1084 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Pa44 Haldane Health feeder tripped and reclosed then tripped on Relay: E/F, SEF, Timing relay lockout and fault check. Cause: Possum across 11kV UGOH Colah RD East Of Gray St. Also Bond Burnt off at UGOH below LB2694 See OMS 992757 992761 992762 992763 99276 992768 991487 991493 991489 991510 991511 | July | 2013 | 2014Q1 | 2014 | ZN847:PA44 | ZN847:PA44 | ZN00847/000044 | HORNSBY | OH | Not Veg | 2013-07-06 | N | 139.7399 | N | 7 | N | N | 1.1101 | 39.4971 | 110695.6546
[7 empty] | 16009 | 14719 | 991436 | 2013-07-06 14:39 | 2013-07-06 23:30 | 531 | 11kV | 9926 | 149 | HV | 3rd Party Vehicle | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | Unselected | N | CP.46935 - Position Open At CP.46935 Ironbark Kirk 0.8 (ex panel 3 'Mangrove Mountain' Fdr) CB opened, reclosed and then locked out. Relays: IOC Car hit pole between L 40558, LB 40554 and Rec 46895 Wise Ferry Ironbark. PT 13138 Wise Ferry Lombarde 0.4 isolated to repaird LV distributor wires at site. See OMS 992792,801,800,806 Exclude 991436,440 | July | 2013 | 2014Q1 | 2014 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2013-07-06 | N | 66.6174 | N | 7 | N | N | 1.1101 | 39.4971 | 7253.628
[7 empty] | 16372 | 18753 | 991507 | 2013-07-06 23:05 | 2013-07-07 00:35 | 90 | 11kV | 12690 | 141 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 136336 A phase DOLF Fuse not blown but burnt up due to faulty fuse assembly. Fuse & assembly replaced. Excluded OMS No's 991507 & 991513. | July | 2013 | 2014Q1 | 2014 | 264:81238 | 264:81238 | ZN00264/081238 | PORT STEPHENS | OH | Not Veg | 2013-07-06 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 9273.4777
[7 empty] | 16383 | 18891 | 991517 | 2013-07-07 03:53 | 2013-07-07 04:47 | 54 | 11kV | 97632 | 1808 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 690 Campsie Panel 18 "Canterbury Hospital" feeder tripped on: Relays: Earth Fault, EFI Signals: 11kv trip Tx 3 Group Earth Field EFI's: Nil Remarks: UG fault. Suspect UG cable fault from Sub 690 Campsie panel 18 to Sub 690 Campsie panel 13 to Sub 1346 Canterbury Hospital Related jobs: #991767, 991517 | July | 2013 | 2014Q1 | 2014 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-07-07 | N | 54 | N | 5 | N | N | 1.1101 | 39.4971 | 71346.5859
[7 empty] | 15104 | 3781 | 991601 | 2013-07-07 13:45 | 2013-07-07 15:50 | 125 | 11kV | 125 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136339 Single phase DOLF : 10 Amp Tx Volts: 254V Excluded OMS No. 991601 | July | 2013 | 2014Q1 | 2014 | 807:74179 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2013-07-07 | N | 125 | N | 5 | N | N | 1.1101 | 39.4971 | 91.3463
[7 empty] | 15387 | 7292 | 991641 | 2013-07-07 18:55 | 2013-07-07 21:50 | 175 | 11kV | 119439 | 2124 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | Unselected | N | At S.15005 Belrose, Panewl 12 Fdr CB tripped on SEL. Branch on mains caused bond to burn off at link 21843 | July | 2013 | 2014Q1 | 2014 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Veg | 2013-07-07 | N | 56.2331 | N | 5 | N | N | 1.1101 | 39.4971 | 87282.4983
[7 empty] | 15690 | 10932 | 991628 | 2013-07-07 18:20 | 2013-07-07 23:13 | 293 | 11kV | 39681 | 251 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136340 3 fault operations C phase Earth fault 11kV OHM down between poles FU-33128 & FU-33131. Excluded OMS No. 991628 | July | 2013 | 2014Q1 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-07-07 | N | 158.0916 | N | 5 | N | N | 1.1101 | 39.4971 | 28997.7044
[7 empty] | 15123 | 3900 | 991687 | 2013-07-08 06:24 | 2013-07-08 07:17 | 53 | 11kV | 14724 | 283 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN5868 Gore 11kV panel 10 tripped Relays: Earth Fault, EFI and Fault check Cause: 11kV UG fault from S47276 Reserve Charlotta to S3727 McLachan Marden 991730 991732 911687 | July | 2013 | 2014Q1 | 2014 | ZN5868:PA10 | ZN5868:PA10 | ZN05868/000010 | WILLOUGHBY | UG | Not Veg | 2013-07-08 | N | 52.0283 | N | 2 | N | N | 1.1101 | 39.4971 | 10759.8649
[7 empty] | 15556 | 8975 | 991660 | 2013-07-07 23:10 | 2013-07-08 12:09 | 779 | 11kV | 1603 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | ZN.12630 - Peats Ridge - Pnl 2 labelled gunderman section of 11kv interrupted by DOp from LB43534 to N/O LB45074 11kV on X arm Interrupted for Safety Reasons See OMS 993184, 993200 | July | 2013 | 2014Q1 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2013-07-07 | N | 320.6 | N | 5 | N | N | 1.1101 | 39.4971 | 1171.4251
[7 empty] | 15056 | 3297 | 991882 | 2013-07-08 11:26 | 2013-07-08 14:58 | 212 | 11kV | 19928 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 136347 1 fault operation Tree fell on mains at Glass Sub 43589. Sensitive Earth Fault | July | 2013 | 2014Q1 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-07-08 | N | 212 | N | 2 | N | N | 1.1101 | 39.4971 | 14562.7946
[7 empty] | 16461 | 20069 | 992201 | 2013-07-09 08:37 | 2013-07-09 11:35 | 178 | 11kV | 356 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136363 C phase DOLF : 31 Amp Excluded OMS 992201 | July | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | UG | Not Veg | 2013-07-09 | N | 178 | N | 4 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 15619 | 9889 | 992384 | 2013-07-09 11:50 | 2013-07-09 12:00 | 10 | 11kV | 12770 | 1277 | HV | Staff Operation | Utility Process Issue | Air Break Switch | Unplanned | No Weather Impact | N | LID 136361 Operator error M0353 & SI 33699 not correctly coordinated. Load broken at ABS 63705 232/3 F9 | July | 2013 | 2014Q1 | 2014 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2013-07-09 | N | 10 | N | 4 | N | N | 1.1101 | 39.4971 | 9331.9393
[7 empty] | 15725 | 11344 | 992509 | 2013-07-09 15:18 | 2013-07-09 17:10 | 112 | 11kV | 70890 | 670 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Section of 11kv feeder ex panel 27 @ Zn 1068 Lidcombe, from Sub 524 Beatrice Street the 11kv CB 'C' has tripped Relays: A and C timed OC and inst, EFI Field EFI's: 7177, 4468, 5204 Remarks: UG fault. Suspected UG fault between Sw/B @ Sub 35204 Manchester the crescent to Sw/A @ Sub 5792 Walters Mona tee Sw/A @ Sub 2603 Crescent Alice No.1 Related jobs: #992532, 992528, 992521, 992509, 992733, 992736, 992712, 992716, 992765 | July | 2013 | 2014Q1 | 2014 | ZN1068:PA27 | ZN1068:PA27 | ZN01068/000027 | CUMBERLAND | UG | Not Veg | 2013-07-09 | N | 105.806 | N | 4 | N | N | 1.1101 | 39.4971 | 51804.3211
[7 empty] | 16122 | 16168 | 992613 | 2013-07-09 18:20 | 2013-07-10 10:20 | 960 | 11kV | 99874 | 299 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Light | N | At S.931 Darlinghurst #1 tx group earth, #4 tx group earth 11kv trip Panel 24 the Burrahpore Corfu fdr. Tripped on inter trip receive. Remarks: Transformer failure. At S1323 Domain Parking Station sub flooded, 415v LV No1 TX ACB failure and protection equipment operation failure. Section of feeder from S6850 Cathederal Col to and including No1 11kv/415V Transformer @ S1323 domain Parking Station ISOLATED and EARTHED ONLY. Related jobs: #992749, 992628, 993438, 992613, 993436, 993439, 993435, 993434 | July | 2013 | 2014Q1 | 2014 | ZN931:PA24 | ZN931:PA24 | ZN00931/000024 | SYDNEY | UG | Not Veg | 2013-07-09 | N | 334.0268 | N | 4 | N | N | 1.1101 | 39.4971 | 72984.9734
[7 empty] | 14883 | 1771 | 993166 | 2013-07-11 09:59 | 2013-07-11 12:06 | 127 | 11kV | 2540 | 20 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | LID 136395 C phase DOLF : 10 Amp contractor dug up LV mains Excluded OMS 993166 | July | 2013 | 2014Q1 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2013-07-11 | N | 127 | N | 1 | N | N | 1.1101 | 39.4971 | 1856.1571
[7 empty] | 15355 | 6855 | 993684 | 2013-07-12 10:37 | 2013-07-12 14:45 | 248 | 11kV | 105186 | 1348 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | At ZN1193 Lindfield 11kV Panel 12 tripped reclosed and lockedout on Relays: A B and C phase of distributor IOC and EFI. Signals: 11kV Trip and No2 Group Earth Cause: Broken cross arm O/S 56 Stanhope St Near PT2268 See OMS 994609 613 615 614 612 993785 993684 | July | 2013 | 2014Q1 | 2014 | ZN1193:PA12 | ZN1193:PA12 | ZN01193/000012 | KU-RING-GAI | OH | Not Veg | 2013-07-12 | N | 78.0312 | N | 3 | N | N | 1.1101 | 39.4971 | 76866.8263
[7 empty] | 15655 | 10514 | 993801 | 2013-07-12 13:53 | 2013-07-12 16:50 | 177 | 11kV | 177 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136410 Single phase Cable failure on one of the 11kV live line connectors. No protection operated. Excluded OMS # 993801. | July | 2013 | 2014Q1 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-07-12 | N | 177 | N | 3 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 15125 | 3929 | 993935 | 2013-07-13 01:39 | 2013-07-13 02:57 | 78 | 11kV | 25422 | 362 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At S2635 Panel 18 tripped with and IT Receive At S1870 Waterloo Macquarie No4 SW/A tripped on T13 Relay (Possible Tx Bz Relay) with and IT send. Cause: 11kV feeder from S49212 Herring Waterloo to S1870 Waterloo Macquarie No4 tee to No3 Tx at S1870 to S3477 Cottonwood waterloo possible Tx Bz Trip. See OMS 994588 994589 993935 993936 | July | 2013 | 2014Q1 | 2014 | ZN2635:PA18 | ZN2635:PA39 | ZN02635/000039 | RYDE | UG | Not Veg | 2013-07-13 | N | 70.2265 | N | 2 | N | N | 1.1101 | 39.4971 | 18577.6478
[7 empty] | 15302 | 6450 | 993931 | 2013-07-12 23:20 | 2013-07-13 06:05 | 405 | 11kV | 12960 | 32 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 136411 car into pole AK-60033, no protection operation, section isolated to make repairs Excluded OMS 993931, 993938, 993940, 993941 | July | 2013 | 2014Q1 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-07-12 | N | 405 | N | 3 | N | N | 1.1101 | 39.4971 | 9470.7857
[7 empty] | 16439 | 19838 | 993942 | 2013-07-13 03:35 | 2013-07-14 01:55 | 1340 | 11kV | 27282 | 78 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Recloser 1014 Suakin Drive tripped and locked out on Earth fault. At Mosman Zone Zone Earth, #3 Tx Group Earth. UG cable fault in tee to S.2113 | July | 2013 | 2014Q1 | 2014 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | UG | Not Veg | 2013-07-13 | N | 349.7692 | N | 2 | N | N | 1.1101 | 39.4971 | 19936.8809
[7 empty] | 15739 | 11476 | 994168 | 2013-07-14 12:27 | 2013-07-14 13:27 | 60 | 11kV | 81838 | 1368 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 136418 2 fault operations 3 phase Instantaneous Overcurrent Excluded OMS 994168, 994171, 994172, 994174, 994175, 994176 | July | 2013 | 2014Q1 | 2014 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | Unknown | Unknown | 2013-07-14 | N | 59.8231 | N | 1 | N | N | 1.1101 | 39.4971 | 59804.7966
[7 empty] | 15159 | 4216 | 994766 | 2013-07-15 19:45 | 2013-07-15 20:44 | 59 | 11kV | 36639 | 621 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn.690 Campsie - Pnl.10 tripped on A phase overcurrent Field EFis: CP571, S6622 S47528 S2634 S4309 UG cable fault between S4309 and S2892 (N/O) Isolated fault and restored supply. S8056 and 1688 were in LV parallel see 995535 994767 | July | 2013 | 2014Q1 | 2014 | ZN690:PA10 | ZN690:PA10 | ZN00690/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-07-15 | N | 59 | N | 1 | N | N | 1.1101 | 39.4971 | 26774.7005
[7 empty] | 16172 | 16721 | 994794 | 2013-07-16 06:28 | 2013-07-16 07:10 | 42 | 11kV | 43638 | 1039 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ZN 1290 Leightonfield - 11kv Panel No.12 "Sub 3043 Miller Bil No.1 "feeder tripped, reclosed and locked out. Relays: A phase timed O/C Reclosing relsy, locking relay s Signals: 11kv trip Field EFI's: Nil Remarks: Animals/Birds. Bat on 11kv Mains adjacent LB407 Related jobs: 994794, 994795, 995054 | July | 2013 | 2014Q1 | 2014 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-07-16 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 31889.3633
[7 empty] | 16178 | 16824 | 994861 | 2013-07-16 09:50 | 2013-07-16 11:00 | 70 | 11kV | 1120 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136t432 11kV OHM between poles KR-40065 & KR-40066 AT 4.3 Mtrs. Subs interrupted for repairs Excluded OMS 994861 & 994862 | July | 2013 | 2014Q1 | 2014 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2013-07-16 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 14752 | 511 | 994889 | 2013-07-16 09:41 | 2013-07-16 13:30 | 229 | 11kV | 458 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 136433 A phase DOLF : 10 Amp LAs blown at sub 72698. TX Volts: 248V Excluded OMS No. 994889 | July | 2013 | 2014Q1 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2013-07-16 | N | 229 | N | 4 | N | N | 1.1101 | 39.4971 | 334.6929
[7 empty] | 15696 | 10984 | 995284 | 2013-07-16 23:05 | 2013-07-17 09:31 | 626 | 11kV | 218474 | 349 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.15014 - Mona Vale - Pnl 12 'S.16154 Minmai Rd' Fdr Relays: EFI, Fault Check Signals: ZE @CP24701 'Scotland Island' SW6000 Tripped C Phase 90A Kemxo HV Fuse All field EFIs Operated, Field EFIs on Scotland Island:S16614 UG Fault Water Transport Required. Attend AM Wed 17/07 Section of fdr from S.16614'Richard Cecil' SW/B to S.15526 'Thompson Elsie' SW/A CC1: 22-"Refer to SOp" | July | 2013 | 2014Q1 | 2014 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2013-07-16 | N | 626 | N | 4 | N | N | 1.1101 | 39.4971 | 159654.3553
[7 empty] | 15702 | 11017 | 996227 | 2013-07-17 12:02 | 2013-07-17 12:07 | 5 | 11kV | 10735 | 2147 | HV | Staff Other | Utility Process Issue | O/H Link | Unplanned | Unselected | N | At Zn14891 Wyong Pa10 fdr tripped Relays: A & B ph OC, EFI Signals: 11kv trip Signals: 11kv trip EFI's: S14857 Cause: Loadbreak Switch Remarks: Whilst Linesman was checking locking mechanism. AB flicker has come in contact with footpath side temp bond causing a flashover. All workers were on the ground at time. | July | 2013 | 2014Q1 | 2014 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2013-07-17 | N | 5 | N | 2 | N | N | 1.1101 | 39.4971 | 7844.8214
[7 empty] | 14806 | 992 | 995640 | 2013-07-17 17:25 | 2013-07-17 19:23 | 118 | 11kV | 87638 | 811 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.1285 Greenacre Park Panel 10 The East Tce/South Tce fdr tripped on B ph timed O/L EFI, fault check, sealing contact field efi's down at Subs 4109, 35231, 1924, 3978, 3708 Remarks: UG fault. Suspect cable fault between S3707 and S7020 Related jobs: #995640, 996928, 996927 | July | 2013 | 2014Q1 | 2014 | ZN1285:PA10 | ZN1285:PA10 | ZN01285/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-07-17 | N | 108.0617 | N | 2 | N | N | 1.1101 | 39.4971 | 64043.2655
[7 empty] | 15235 | 5475 | 995783 | 2013-07-18 09:17 | 2013-07-18 10:49 | 92 | 11kV | 80316 | 873 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136459 2 fault operations Earth fault; Overcurrent Excluded OMS 995783; 995787; 995792 | July | 2013 | 2014Q1 | 2014 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | OH | Veg | 2013-07-18 | N | 92 | N | 4 | N | N | 1.1101 | 39.4971 | 58692.5639
[7 empty] | 15911 | 13250 | 995779 | 2013-07-18 09:45 | 2013-07-18 11:42 | 117 | 11kV | 53422 | 462 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136463 2 fault operations C phase Overcurrent fdr patrolled in area of reported explostion in Aberdeen St no cause found dq Excluded oms 995779 | July | 2013 | 2014Q1 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-07-18 | N | 115.632 | N | 4 | N | N | 1.1101 | 39.4971 | 39039.2219
[7 empty] | 15309 | 6506 | 995909 | 2013-07-18 12:14 | 2013-07-18 16:30 | 256 | 11kV | 164917 | 2707 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 136467 Faulty UG main between pole JT-80970 - sub 58188 - CB60 2 fault operations Earth fault Excluded OMS 995909 | July | 2013 | 2014Q1 | 2014 | 240:34835 | 240:34849 | ZN00240/034849 | NEWCASTLE | UG | Not Veg | 2013-07-18 | N | 60.9224 | N | 4 | N | N | 1.1101 | 39.4971 | 120516.4794
[7 empty] | 15574 | 9148 | 996080 | 2013-07-18 18:15 | 2013-07-18 18:48 | 33 | 11kV | 41594 | 1978 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @Zn12650 West Gosford Pa12 fdr tripped and reclosed Relay:aPh overcurrent, Lockout, Reclose Signals: 11kv trip Cause: Bond HV bond burnt off on zone side of AB43065 See 996246,7 Exclude 996080,1,4,90 | July | 2013 | 2014Q1 | 2014 | ZN12650:PA12 | ZN12650:PA12 | ZN12650/000012 | CENTRAL COAST | OH | Not Veg | 2013-07-18 | N | 21.0283 | N | 4 | N | N | 1.1101 | 39.4971 | 30395.6684
[7 empty] | 15570 | 9114 | 996211 | 2013-07-19 10:32 | 2013-07-19 11:30 | 58 | 11kV | 348 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Section of Pa3 At PT11630 Wise Ferry Fairymeade roadside 16 Amp HDO operated Cause: Fuse Fatigue. Dop replaced roadside HDO See 996926 Exclude 996211,24 | July | 2013 | 2014Q1 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2013-07-19 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 254.3081
[7 empty] | 14763 | 558 | 996338 | 2013-07-19 13:58 | 2013-07-19 14:59 | 61 | 11kV | 72346 | 1186 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136483 2 fault operations A & B phases Overcurrent reports of flash at pole IV-70074, ok on arrival. Excluded OMS 996338 | July | 2013 | 2014Q1 | 2014 | 225:33676 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Veg | 2013-07-19 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 52868.323
[7 empty] | 15184 | 4433 | 996319 | 2013-07-19 13:37 | 2013-07-19 16:20 | 163 | 11kV | 74230 | 626 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S.262 Marrickville Panel 20 (S.6398 Smith Victoria Feeder) tripped. Relays: EF, F/C, EFI Signals: 11kv trip, TX4 GE, ZE Field EFI's: S6398, S6943, S3054, S7364 Remarks: UG cable damaged by contractors. O/S No.4 Perry St by Emmanuel Gilanos. Ph 0425241816. UG Fault between S.7364 Brompton Rich (Sw/B) to S.7071 Jabez Denby (Sw/D) tee to S.2648 Browns Newington Related jobs: #996337, 996330, 996328, 996326, 996319, 997166, 997168, 997169, 997162, 997143 | July | 2013 | 2014Q1 | 2014 | ZN262:PA20 | ZN262:PA20 | ZN00262/000020 | INNER WEST | UG | Not Veg | 2013-07-19 | N | 118.5783 | N | 6 | N | N | 1.1101 | 39.4971 | 54245.0946
[7 empty] | 16262 | 17585 | 996444 | 2013-07-19 19:23 | 2013-07-19 21:45 | 142.5 | 11kV | 3990 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136485 A & B phase DOLF : 20 Amp | July | 2013 | 2014Q1 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2013-07-19 | N | 142.5 | N | 6 | N | N | 1.1101 | 39.4971 | 2915.7743
[7 empty] | 15249 | 5646 | 996430 | 2013-07-19 17:46 | 2013-07-19 23:55 | 368.7167 | 11kV | 114791.0167 | 1346 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn.36300 Balgowlah North Pnl 17 ' Balgowlah North Aux No.2' tripped on: Relays: B+C phase IOC Signals: 11kvTrip EFI's: nil Bat into 11kV mains brought 1 phase down between S.17039 Condamine Kooralia SW/B to AB 26238 tee to S.16320 Kenneth Pitt. See 1011237,40,1,3 Exclude 996430,904 | July | 2013 | 2014Q1 | 2014 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2013-07-19 | N | 85.2831 | N | 6 | N | N | 1.1101 | 39.4971 | 83885.8892
[7 empty] | 14854 | 1454 | 996458 | 2013-07-19 22:18 | 2013-07-20 | 102 | 11kV | 306 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136486 Single phase DOLF : 16 Amp | July | 2013 | 2014Q1 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2013-07-19 | N | 102 | N | 6 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 16166 | 16649 | 997055 | 2013-07-20 07:41 | 2013-07-20 08:40 | 59 | 11kV | 8799 | 157 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 136492 3 fault operations B & C phase Overcurrent UG Fault suspected at Joint 26 @ 70 Wattle Ponds Rd Singleton. Adj to SP SI-60513. Excluded OMS 996783 | July | 2013 | 2014Q1 | 2014 | 523:33511 | 523:33511 | ZN00523/033511 | SINGLETON | UG | Not Veg | 2013-07-20 | N | 56.0446 | N | 6 | N | N | 1.1101 | 39.4971 | 6430.0497
[7 empty] | 15830 | 12448 | 996521 | 2013-07-20 04:20 | 2013-07-20 11:02 | 402 | 11kV | 402 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 136498 Single phase DOLF : 10 Amp Lightning Strike. Excluded OMS 996522 | July | 2013 | 2014Q1 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-07-20 | N | 402 | N | 6 | N | N | 1.1101 | 39.4971 | 293.7697
[7 empty] | 14731 | 300 | 996530 | 2013-07-20 10:28 | 2013-07-20 14:45 | 257 | 11kV | 257 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 136500 HV Dropper has come out of Dolf & hanging from mains. No Protection Operation Excluded OMS 996530 | July | 2013 | 2014Q1 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-07-20 | N | 257 | N | 6 | N | N | 1.1101 | 39.4971 | 187.808
[7 empty] | 15407 | 7503 | 996518 | 2013-07-20 09:56 | 2013-07-20 15:40 | 344 | 11kV | 344 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 136501 Single phase DOLF : 10 Amp LF 75374 blew when sub fuse closed. Excluded OMS 996518 | July | 2013 | 2014Q1 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2013-07-20 | N | 344 | N | 6 | N | N | 1.1101 | 39.4971 | 251.3851
[7 empty] | 15718 | 11123 | 996481 | 2013-07-20 04:20 | 2013-07-20 16:00 | 700 | 11kV | 700 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Electrical Storm | N | LID 136494 Single phase DOLF Tx and all hardware damaged. Replace all. Contractor to make LV safe. Excluded OMS 996481 | July | 2013 | 2014Q1 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-07-20 | N | 700 | N | 6 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 15864 | 12820 | 996599 | 2013-07-20 18:14 | 2013-07-20 23:08 | 294 | 11kV | 24473 | 157 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 136503 2 fault operations 3 phase Overcurrent tree on mains @ pole ER-62802 section isolated for repair Excluded OMS 996618 | July | 2013 | 2014Q1 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2013-07-20 | N | 155.879 | N | 6 | N | N | 1.1101 | 39.4971 | 17884.1466
[7 empty] | 15764 | 11739 | 996700 | 2013-07-21 14:08 | 2013-07-21 16:55 | 167 | 11kV | 22209 | 263 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | ZN.15013 - Terry Hills - Recloser 1126 'Mona Vale Rd' of Pnl 10 Mona Vale Alumuna Fdr Tripped on O/C & Locked Out o/s #26 Ingleside rd Terry Hills. Large Branch removed by mains. | July | 2013 | 2014Q1 | 2014 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2013-07-21 | N | 84.4449 | N | 1 | N | N | 1.1101 | 39.4971 | 16229.6821
[7 empty] | 14713 | 150 | 996802 | 2013-07-22 05:30 | 2013-07-22 06:25 | 55 | 11kV | 220 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136510 C phase DOLF : 10 Amp Excluded OMS 996802 | July | 2013 | 2014Q1 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2013-07-22 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 14920 | 2064 | 997076 | 2013-07-22 13:34 | 2013-07-22 13:47 | 13 | 11kV | 494 | 38 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 136513 Section isolated to repair x-arm pole LI-51086 Emerg switching M0375 | July | 2013 | 2014Q1 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-07-22 | N | 13 | N | 4 | N | N | 1.1101 | 39.4971 | 361.0006
[7 empty] | 15187 | 4454 | 997177 | 2013-07-22 15:30 | 2013-07-22 17:46 | 136 | 11kV | 8568 | 63 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 136514 section isolated to replace x-arm on pole SI-90163. Note ABS 40740 faulty won't open Excluded OMS 997177 | July | 2013 | 2014Q1 | 2014 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2013-07-22 | N | 136 | N | 4 | N | N | 1.1101 | 39.4971 | 6261.2417
[7 empty] | 15175 | 4355 | 997164 | 2013-07-22 15:12 | 2013-07-22 19:52 | 280.1833 | 11kV | 502.6167 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136515 C phase Broken Live Line lead Excluded OMS 997164 | July | 2013 | 2014Q1 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-07-22 | N | 251.3083 | N | 4 | N | N | 1.1101 | 39.4971 | 367.2974
[7 empty] | 15172 | 4334 | 997570 | 2013-07-23 15:07 | 2013-07-23 17:32 | 145 | 11kV | 17308 | 278 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14892 Charmhaven Pa5 tripped on Relays: 51N (Timed Earth Fault), EFI, Fault CHeck Reclose, Fault Check Lockout Signals: CB5 11kv trip EFI's: S14804 S18365 S14758 S14416 Cause:Suspect UG Fault between HV UGOH & S14019 Freeway Tooheys. See 997814,7,8,20 2nd 997821 Exclude 997570,5 | July | 2013 | 2014Q1 | 2014 | ZN14892:PA5 | ZN14892:PA5 | ZN14892/000005 | CENTRAL COAST | UG | Not Veg | 2013-07-23 | N | 62.259 | N | 4 | N | N | 1.1101 | 39.4971 | 12648.1759
[7 empty] | 15882 | 12941 | 997637 | 2013-07-23 16:37 | 2013-07-23 18:05 | 88 | 11kV | 81798 | 1168 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn12660 Woy Woy Pa14 fdr tripped on relays: 11kv trip, Aph Time OC, Aph IOC signals:11kc cb 14 trip Remarks: Vehicle hit pole. Cross arm HV broken corner Rawson st & Woy Woy rd, Woy Woy See 997854,5,6,7 Exclude 997637,45,9,51,3 | July | 2013 | 2014Q1 | 2014 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2013-07-23 | N | 70.0325 | N | 4 | N | N | 1.1101 | 39.4971 | 59775.5658
[7 empty] | 16086 | 15878 | 997648 | 2013-07-23 16:52 | 2013-07-23 18:10 | 78 | 11kV | 390 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136526 A & B phase DOLF : 16 Amp replaced 16A fuses, Note Syst diag & LID 20A fuses Excluded OMS 997648 | July | 2013 | 2014Q1 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | UG | Not Veg | 2013-07-23 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 15478 | 8219 | 997684 | 2013-07-23 18:17 | 2013-07-23 19:51 | 94 | 11kV | 120707 | 4321 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Sub 3922 Drummoyne Panel No.11 "Thornley Victoria" opened on Earth fault. EFI's operated @ Subs 35633, 7738 Abnormal: N/O Open SW B @ sub 3874 PMG Balmain closed. Sw A @ Sub 1511 Hyam Reynolds Open. See DMA. Remarks: UG cable fault sub 7738 to Sub 2872 to Sub 499979 to sub 3874. See also interruption Panel No 29. | July | 2013 | 2014Q1 | 2014 | ZN3922:PA29 | ZN3922:PA29 | ZN03922/000029 | INNER WEST | UG | Not Veg | 2013-07-23 | N | 27.935 | N | 4 | N | N | 1.1101 | 39.4971 | 88209.1153
[7 empty] | 15653 | 10502 | 998107 | 2013-07-24 16:06 | 2013-07-24 19:15 | 189 | 11kV | 18900 | 100 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At PT1900 Richardson Court LV Readings 246v, 308v, 246v possible internal/winding fault. Section of Panel No 3 "Mars Virginius etc" feeder ex Sub 1287 Revesby Remarks: Trasformer failure. Tap Change had been done on Tx yesterday. Possible internal fault. Neutral connections looks ok. Pt 1900 Isolated on LV only. Related jobs: #998179, 998107, 998398 | July | 2013 | 2014Q1 | 2014 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-07-24 | N | 189 | N | 1 | N | N | 1.1101 | 39.4971 | 13811.5625
[7 empty] | 15755 | 11678 | 998231 | 2013-07-25 08:24 | 2013-07-25 10:12 | 108 | 11kV | 31148 | 315 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 136546 2 fault operations C phase Earth fault Contractor hit cable at Crown Plaza Isolated 37672 to 37179 TAP left Excluded OMS 998231 | July | 2013 | 2014Q1 | 2014 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | UG | Not Veg | 2013-07-25 | N | 98.8825 | N | 1 | N | N | 1.1101 | 39.4971 | 22762.0397
[7 empty] | 16260 | 17547 | 998918 | 2013-07-27 01:08 | 2013-07-27 03:30 | 142 | 11kV | 67166 | 473 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex Zn10993 Hurstville North AB31113 Contact HR connection. See OMS 1000773 998920 998921 998919 998918 | July | 2013 | 2014Q1 | 2014 | ZN10993:PA12 | ZN10993:PA35 | ZN10993/000035 | GEORGES RIVER | OH | Not Veg | 2013-07-27 | N | 142 | N | 2 | N | N | 1.1101 | 39.4971 | 49082.9317
[7 empty] | 15402 | 7468 | 998981 | 2013-07-27 10:15 | 2013-07-27 12:00 | 105 | 11kV | 229145 | 3538 | HV | Arcing | Equipment Failure | Insulator | Unplanned | Unselected | N | At Zn 1285 Greenacre Park Panel 24 "Merideth Rickard" feeder has tripped. Signals: 11kv trip, GE Relays: Micom P122 - Trip led, alarm led, EFI led EF Led EFI's: S50, s8618, s7247, s48478, s4398, s36196 Abnormal: Sw/A closed @ Sub 48478 Brancourt Marion. IS 1452 open and defective (Bonds tied back) Remarks: flashover/arcing. Arcing @ IS 1452 | July | 2013 | 2014Q1 | 2014 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-07-27 | N | 64.7668 | N | 2 | N | N | 1.1101 | 39.4971 | 167452.4074
[7 empty] | 15961 | 13960 | 999758 | 2013-07-28 10:05 | 2013-07-28 15:26 | 321 | 11kV | 22149 | 69 | HV | 3rd Party Vehicle | 3rd Party Impact | Cross arm | Unplanned | Unselected | N | LID 136571 BROKEN X-ARM FOUND AT POLE FT-63130 WHILST SWITCHING (SI 32709)28/07/2013.CUSTOMER ADVISED CAR HIT POLE ON 27/07/2013 SEE UPO/REPORT 136564.POLE HAS BEEN DAMAGED PLEASE ARRANGE FOR POLE INSPECTION ASAP. | July | 2013 | 2014Q1 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-07-28 | N | 321 | N | 4 | N | N | 1.1101 | 39.4971 | 16185.8359
[7 empty] | 15320 | 6585 | 999217 | 2013-07-28 18:51 | 2013-07-28 19:40 | 49 | 11kV | 98 | 2 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 136573 B phase DOLF : 10 Amp pelican into 11 kV mains Excluded oms 999217 | July | 2013 | 2014Q1 | 2014 | 213:33773 | 213:33773 | ZN00213/033773 | NEWCASTLE | OH | Not Veg | 2013-07-28 | N | 49 | N | 4 | N | N | 1.1101 | 39.4971 | 71.6155
[7 empty] | 15202 | 4661 | 999190 | 2013-07-28 16:43 | 2013-07-28 20:30 | 227 | 11kV | 24970 | 110 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S.16434 Whale Beach Morella, the B phase HV fuse failed - lack of grading between OQFRN HV 40 amp fuse and 400 amp LV fuse. LV OH Wires down O/S 245 Whale Beach RD CC1: 22-"Refer to SOp" | July | 2013 | 2014Q1 | 2014 | ZN15010:PA1 | ZN15010:PA24 | ZN15010/000024 | NORTHERN BEACHES | OH | Not Veg | 2013-07-28 | N | 227 | N | 4 | N | N | 1.1101 | 39.4971 | 18247.3395
[7 empty] | 15719 | 11140 | 999235 | 2013-07-28 20:08 | 2013-07-28 20:50 | 42 | 11kV | 84 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136574 A phase DOLF : 10 Amp Excluded OMS 999235 also refer to 999686 | July | 2013 | 2014Q1 | 2014 | 213:33773 | 213:33773 | ZN00213/033773 | NEWCASTLE | UG | Not Veg | 2013-07-28 | N | 42 | N | 4 | N | N | 1.1101 | 39.4971 | 61.3847
[7 empty] | 16207 | 17117 | 999463 | 2013-07-29 00:08 | 2013-07-29 01:22 | 74 | 11kV | 168480 | 2716 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S35500 Top Ryde Panel 24 Tripped on Relays - 24R Basler BE1 851, 51N, Inverse Time, O/C, EF and EFI. No field EFI;s Operated. Cause not ascertained for outage Mains to Patrol. See OMS 999463 999465 999466 | July | 2013 | 2014Q1 | 2014 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Veg | 2013-07-29 | N | 62.0324 | N | 3 | N | N | 1.1101 | 39.4971 | 123120.2147
[7 empty] | 15994 | 14528 | 999275 | 2013-07-29 07:15 | 2013-07-29 17:50 | 635 | 11kV | 19698 | 157 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 136585 1 fault operation Sensitive Earth Fault 11KV BUNDLE TOUCHING POLE FR-22104 CAUSING POLE FIRE AND LOSS OFF FEEDER. Excluded OMS REPORT NO 999275. | July | 2013 | 2014Q1 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2013-07-29 | N | 125.465 | N | 3 | N | N | 1.1101 | 39.4971 | 14394.7174
[7 empty] | 14834 | 1271 | 999539 | 2013-07-29 17:00 | 2013-07-29 19:00 | 120 | 11kV | 240 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136587 Broken LL lead | July | 2013 | 2014Q1 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-07-29 | N | 120 | N | 3 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 15920 | 13325 | 999707 | 2013-07-30 09:55 | 2013-07-30 13:50 | 235 | 11kV | 150304 | 1330 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15006 Dee Why West, 11kV Fdr CB Panel 13 tripped on OC (Minor Alarm LED, Trip LED, Fault Check, 11kV trip. Field efi's down at S.47595 and S.15777Suspect UF fault on 11kV feeder from Sw B @ S.16618 and SW B @ S.15777 tee S.16255. Open bond caused by fault current after the tee to PT.15330 | July | 2013 | 2014Q1 | 2014 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | UG | Not Veg | 2013-07-30 | N | 113.0105 | N | 2 | N | N | 1.1101 | 39.4971 | 109837.73
[7 empty] | 15103 | 3727 | 999947 | 2013-07-30 15:40 | 2013-07-30 19:25 | 225 | 11kV | 6300 | 28 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 136596 Section isolated for repairs Excavator hit feeder near pole KS-90229 Section isolated for repairs Excluded OMS 999763, 999948, 999947 | July | 2013 | 2014Q1 | 2014 | 229:34986 | 229:34986 | ZN00229/034986 | PORT STEPHENS | OH | Not Veg | 2013-07-30 | N | 225 | N | 2 | N | N | 1.1101 | 39.4971 | 4603.8542
[7 empty] | 15527 | 8774 | 1000147 | 2013-07-31 09:35 | 2013-07-31 10:58 | 83 | 11kV | 4067 | 49 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S6931 St Johns End 400A fuse blown on B and C phase of distributor 2. UG Cable fault in Street light standard o/s 159 St johns Rd Gordon. At S3654 St Johns Bushlands B phase HVDO fuse operated. - Found in Parallel with Above Sub. -Likely Fuses didnt grade See OMS 1000729 1000922 1000153 1000147 1000129 1000119 | July | 2013 | 2014Q1 | 2014 | ZN195:PA28 | ZN195:PA28 | ZN00195/000028 | KU-RING-GAI | UG | Not Veg | 2013-07-31 | N | 83 | N | 3 | N | N | 1.1101 | 39.4971 | 2972.0436
[7 empty] | 15881 | 12937 | 1000488 | 2013-07-31 19:59 | 2013-07-31 22:51 | 172 | 11kV | 1548 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | 'B' phase fuse on PT blown also refer to 1000488 | July | 2013 | 2014Q1 | 2014 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2013-07-31 | N | 172 | N | 3 | N | N | 1.1101 | 39.4971 | 1131.2327
[7 empty] | 15518 | 8673 | 1000498 | 2013-07-31 22:30 | 2013-08-01 00:45 | 135 | 11kV | 135 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Rdige section of Pa5 @PT18371 Bushells Peats Bph HVDO fuse operated type BBLAS 20Amp Cause: Apparent Fuse fatigu. Supply resotred via LV// link box 30406. DOp has replaced HV fuse and removed LV// See 1000761 exclude 1000498 | July | 2013 | 2014Q1 | 2014 | ZN12630:PA5 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2013-07-31 | N | 135 | N | 3 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 16417 | 19413 | 1002663 | 2013-08-02 21:50 | 2013-08-02 23:14 | 84 | 11kV | 88316 | 1291 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10995 Riverwood - Pnl 12 - Trip/reclose/trip, A & C phase IOC and timed O/C, timing and lockout, EFI, Field EFIs. 11kV UGOH failed (centre phase) below S 48434. ME: 1002663. Rest Step: 1002665. Withdrawn: 1001157, 58, 59, 60, 61. | August | 2013 | 2014Q1 | 2014 | ZN10995:PA12 | ZN10995:PA12 | ZN10995/000012 | GEORGES RIVER | Unknown | Unknown | 2013-08-02 | N | 68.409 | N | 1 | N | N | 1.1101 | 39.4971 | 64538.7279
[7 empty] | 16363 | 18695 | 1001188 | 2013-08-03 07:59 | 2013-08-03 09:39 | 100 | 11kV | 3570 | 42 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | @Zn262 Marrickville Panel 13 "Lillian Fitz" fdr tripped on:- Relays: Earth fault and EFI Signals: 11kv trip, Tx4 group and Zn earths EFIs: S7116, S46850 Remarks: Marrickville council contractors damaged 11kv UG conductor on cnr of Edinburgh and Smidmore St's. Jointing crew advised of fault location between S46850 Fitzroy Edinburgh and S4399 Chapel Fitz tee to S7069 E.O.I No2 Related jobs: #1001188, 1001194, 1001609, 1001610 | August | 2013 | 2014Q1 | 2014 | ZN262:PA13 | ZN262:PA13 | ZN00262/000013 | INNER WEST | UG | Not Veg | 2013-08-03 | N | 85 | N | 1 | N | N | 1.1101 | 39.4971 | 2608.8507
[7 empty] | 16422 | 19465 | 1001345 | 2013-08-04 15:43 | 2013-08-04 16:42 | 59 | 11kV | 66181 | 1229 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S195 Pennant Hills Panel 9 tripped on B phase timed Earth fault S5284 Rosedale Khartoum to S5248 Rosedale Edwards Cause: 1001526 1001527 1001345/347 | August | 2013 | 2014Q1 | 2014 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2013-08-04 | N | 53.8495 | N | 3 | N | N | 1.1101 | 39.4971 | 48363.1228
[7 empty] | 15859 | 12764 | 1001350 | 2013-08-04 16:06 | 2013-08-04 17:15 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136632 B phase DOLF : 31 Amp NO APPARENT CAUSE. VOLTS = 250 LOAD A=30 B=32 C= 33. Excluded OMS REPORT NO 1001350. | August | 2013 | 2014Q1 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | UG | Not Veg | 2013-08-04 | N | 69 | N | 3 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 14859 | 1519 | 1001377 | 2013-08-04 21:56 | 2013-08-04 23:11 | 75.2 | 11kV | 8196.8 | 109 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex Zn 35500 Top Ryde Panel 18 PT1656 Cutler Edmundon Centre Phase HVDO fuse operated EFI's - ZN35500, S5352 and S7410 Cause: Possum found at the base of PT1656. See OMS 1001378 1001377 | August | 2013 | 2014Q1 | 2014 | ZN35500:PA18 | ZN35500:PA18 | ZN35500/000018 | RYDE | OH | Not Veg | 2013-08-04 | N | 75.2 | N | 3 | N | N | 1.1101 | 39.4971 | 5989.9797
[7 empty] | 16003 | 14651 | 1001804 | 2013-08-06 07:44 | 2013-08-06 07:57 | 13 | 11kV | 9001 | 877 | HV | Fire (non-electrical) | Adverse Weather/Environment | Pole | Unplanned | Unselected | N | ZN 10996 Rockdale - Pnl 10 - Opened for safety reasons. AB 30119 on fire. Pnl 10 interrupted by Operator to safely open AB 30119. ME: 1002610. Rest Step: 1002611. Withdrawn: 1001790, 1001804. | August | 2013 | 2014Q1 | 2014 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2013-08-06 | N | 10.2634 | N | 3 | N | N | 1.1101 | 39.4971 | 6577.6653
[7 empty] | 15223 | 4995 | 1002152 | 2013-08-06 15:59 | 2013-08-06 17:00 | 61 | 11kV | 1708 | 28 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of Pa13 @PT13114 Narara Creek Manns - 11kv Roadside 31.5 Amp dropout fuse operated See 1002330 Exclude 1002152 | August | 2013 | 2014Q1 | 2014 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Not Veg | 2013-08-06 | N | 61 | N | 3 | N | N | 1.1101 | 39.4971 | 1248.156
[7 empty] | 15112 | 3854 | 1002239 | 2013-08-06 19:34 | 2013-08-06 20:13 | 39 | 11kV | 36711 | 1313 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 269 Waverley - Pnl 9 - C phase timed O/C, Zone earth, group earth, field EFIs. At S 185 Birriga Road - Sw/E tripped - C phase O/C. Suspect UG fault between S 2188, S 183 and S 185. DOp was switching for a job when UG fault occurred. ME: 1002445. Rest Step: 1002447. Withdrawn: 1002239. | August | 2013 | 2014Q1 | 2014 | ZN269:PA9 | ZN36100:PA6 | ZN36100/000006 | WAVERLEY | UG | Not Veg | 2013-08-06 | N | 27.9596 | N | 3 | N | N | 1.1101 | 39.4971 | 26827.316
[7 empty] | 15802 | 12138 | 1002256 | 2013-08-07 01:26 | 2013-08-07 02:29 | 63 | 11kV | 49014 | 778 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn12570 Avoca Pa34 "Terrigal" fdr tripped, reclosed, tripped and locked out on: Relays-50T B&C Signals: 11kv trip EFI: Nil Cause: Tree Branch on OH Mains DOp removed tree branch from 11kv mains in Francis st between LK43139 and PT18531 Scenic Francis | August | 2013 | 2014Q1 | 2014 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2013-08-07 | N | 63 | N | 2 | N | N | 1.1101 | 39.4971 | 35817.9855
[7 empty] | 15256 | 5776 | 1002383 | 2013-08-07 11:50 | 2013-08-07 12:55 | 65 | 11kV | 1586 | 28 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.1290 Leightonfield Panel 16 (S4286 Christina Rd fdr) tripped. Relays: O/C Spaj.Relay No.4, lock-out, EFI Signals: ZE, No.3 GE Field EFI's: S.4286 Remarks: suspect UG fault between S.4286 Christina Related jobs: #1002383, 1002688, 1002687, 1002686 | August | 2013 | 2014Q1 | 2014 | ZN1290:PA16 | ZN1290:PA16 | ZN01290/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-08-07 | N | 56.6429 | N | 2 | N | N | 1.1101 | 39.4971 | 1159.002
[7 empty] | 15044 | 3135 | 1002975 | 2013-08-08 18:15 | 2013-08-08 21:27 | 192.0333 | 11kV | 26333.5333 | 147 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | S 10374 Chuter Florence - C phase HDO (40A). Fuse failed in service. ME: 1002976. ME GIS error: 1002998. Withdrawn: 10029785. | August | 2013 | 2014Q1 | 2014 | ZN10997:PA1 | ZN10997:PA1 | ZN10997/000001 | BAYSIDE | OH | Not Veg | 2013-08-08 | N | 179.1397 | N | 1 | N | N | 1.1101 | 39.4971 | 19243.7695
[7 empty] | 15530 | 8795 | 1003347 | 2013-08-09 21:55 | 2013-08-09 23:53 | 118.2 | 11kV | 12488.1 | 106 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | CP 35946 Burubi Av - 11kV Tee - Centre phase (40A). Possible Underground fault or UGOH fault. Mains to inspect with DOp in Daylight. ME: 1003348. ME GIS error: 1003354, 5. Withdrawn: 1003347, 49, 50, 53. CC1: 22-"Refer to SOp" | August | 2013 | 2014Q1 | 2014 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | UG | Not Veg | 2013-08-09 | N | 117.8123 | N | 1 | N | N | 1.1101 | 39.4971 | 9125.9351
[7 empty] | 14795 | 911 | 1003398 | 2013-08-10 09:24 | 2013-08-10 12:25 | 181 | 11kV | 724 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136692 B phase Live Line Clamp Replace burnt off LV Tx lead | August | 2013 | 2014Q1 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-08-10 | N | 181 | N | 2 | N | N | 1.1101 | 39.4971 | 529.0778
[7 empty] | 16330 | 18287 | 1003529 | 2013-08-11 10:25 | 2013-08-11 13:27 | 182 | 11kV | 309764 | 2152 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S15008 Harbord Panel 5 Tripped reclosed tripped and locked out on Signa;ls 11kV trip and Battery defect Cause: report of explosion at PT15656 the Drive - PT OK Suspect UG fault See OMS 1005326 1005328 1005332 1003529 1003537 1003535 1003536 | August | 2013 | 2014Q1 | 2014 | ZN15008:PA5 | ZN15008:PA5 | ZN15008/000005 | NORTHERN BEACHES | UG | Not Veg | 2013-08-11 | N | 143.9424 | N | 2 | N | N | 1.1101 | 39.4971 | 226366.3947
[7 empty] | 15038 | 3104 | 1003595 | 2013-08-11 22:11 | 2013-08-11 23:00 | 49 | 11kV | 41503 | 847 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 136700 2 fault operations A & B phase Overcurrent branch on ohm at pole is-62348. | August | 2013 | 2014Q1 | 2014 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Veg | 2013-08-11 | N | 49 | N | 2 | N | N | 1.1101 | 39.4971 | 30329.1683
[7 empty] | 16163 | 16607 | 1003825 | 2013-08-12 12:21 | 2013-08-12 13:16 | 55 | 11kV | 30745 | 559 | HV | Arcing | Equipment Failure | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN 10994 Mortdale - Pnl 14 - B & C phase O/C. Sw/B closed at S 10685. Sw/A open at S 49372. Sarking from roof contacted 11kV overhead at 69 Boundary Road. ME: 1009307. Withdrawn: 1003825, 1003897. | August | 2013 | 2014Q1 | 2014 | ZN10994:PA14 | ZN10994:PA14 | ZN10994/000014 | GEORGES RIVER | OH | Not Veg | 2013-08-12 | N | 55 | N | 18 | N | N | 1.1101 | 39.4971 | 22467.5392
[7 empty] | 15689 | 10919 | 1003853 | 2013-08-12 12:31 | 2013-08-12 13:23 | 52 | 11kV | 101452 | 1951 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | @Zn12650 West Gosford 11kv Pa20 "Cantral Moore" fdr tripped on A & B phase overcurrent Signals: 11kv trip EFI's: nil Cause: tree/branch on OH Mains. Made Safe and restored supply | August | 2013 | 2014Q1 | 2014 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Veg | 2013-08-12 | N | 52 | N | 18 | N | N | 1.1101 | 39.4971 | 74138.1293
[7 empty] | 14761 | 549 | 1003688 | 2013-08-12 13:01 | 2013-08-12 14:28 | 87 | 11kV | 186093 | 2139 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 9700 Kirrawee - Pnl 17 - Trip/reclose/trip, A & C phase IOC, timer, lockout. Branch on mains near PT 9543. ME: 1005011. Withdrawn: 1003688, 1003890. | August | 2013 | 2014Q1 | 2014 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Veg | 2013-08-12 | N | 87 | N | 18 | N | N | 1.1101 | 39.4971 | 135991.2756
[7 empty] | 16397 | 19152 | 1003816 | 2013-08-12 12:04 | 2013-08-12 14:37 | 153 | 11kV | 179157 | 1258 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | @Zn 1287 Revesby - 11kv Panel 17 labelled "S.5036 Hinemoa St" tripped: Signals: 11kv trip Relays: A phase timed and instantaneous overcurrent. Field EFI's Remarks: weather related. High winds. 11kv on the ground near PT441 Lehn Rd. Related jobs: #1003816, 1005296, 1005295, 1004141 | August | 2013 | 2014Q1 | 2014 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-08-12 | N | 142.4141 | N | 18 | N | N | 1.1101 | 39.4971 | 130922.6514
[7 empty] | 15912 | 13260 | 1003992 | 2013-08-12 13:33 | 2013-08-12 15:24 | 111 | 11kV | 8450 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At Zn15013 Terrey Hills Panel 8 Tripped Reclosed tripped and locked out out Relays: C phase O.C and IOC, Earth Fault, Lockout, Fault Check with EFI Signals: Zone Earth, No2 Group Earth and 11kV trip. Cause: Tree branch contact See OMS 1005401 1005403 1005407 | August | 2013 | 2014Q1 | 2014 | ZN15013:PA8 | ZN15013:PA8 | ZN15013/000008 | NORTHERN BEACHES | OH | Veg | 2013-08-12 | N | 86.2245 | N | 18 | N | N | 1.1101 | 39.4971 | 6175.0108
[7 empty] | 15825 | 12387 | 1004094 | 2013-08-12 14:02 | 2013-08-12 15:41 | 99 | 11kV | 73359 | 741 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Recloser 46113 Fiddens Wharf Coronga Tripped on O/C Trip Section of Panel 30 Pymble Cause: Tree branch removed from OH mains O/S 48 Beaumont Rd See OMS 1004594 1004098 1004111 1004387 1004119 1004094 | August | 2013 | 2014Q1 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2013-08-12 | N | 99 | N | 18 | N | N | 1.1101 | 39.4971 | 53608.5935
[7 empty] | 15557 | 8976 | 1003819 | 2013-08-12 12:09 | 2013-08-12 15:43 | 214 | 11kV | 38315 | 194 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" fdr 11kv REC45013 Gunderman tripped on overcurrent Cause: Weather related. Suspect high winds See 1004421,670,1,3 | August | 2013 | 2014Q1 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2013-08-12 | N | 197.5 | N | 18 | N | N | 1.1101 | 39.4971 | 27999.4719
[7 empty] | 15305 | 6483 | 1004312 | 2013-08-12 15:14 | 2013-08-12 16:43 | 89 | 11kV | 23496 | 264 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At CP1126 Mona Vale Rd (ex Pa10 Terrey Hills ) tripped and locked out on Overcurrent Cause: Tree branch onb OH near PT15031 See OMS 1004257 1004297 1004312 CC1: 22-"Refer to SOp" | August | 2013 | 2014Q1 | 2014 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2013-08-12 | N | 89 | N | 18 | N | N | 1.1101 | 39.4971 | 17170.1838
[7 empty] | 15893 | 13114 | 1003861 | 2013-08-12 12:45 | 2013-08-12 16:50 | 245 | 11kV | 28910 | 118 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | Ex ZN 9245 Engadine - Pnl 8 - AB 35002 bond open circuit. 11kV bond broke off at AB 35002 Roadside phase. Restored from LB 35535. ME: 1005213. Withdrawn: 1003861. | August | 2013 | 2014Q1 | 2014 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2013-08-12 | N | 245 | N | 18 | N | N | 1.1101 | 39.4971 | 21126.5753
[7 empty] | 15995 | 14554 | 1004426 | 2013-08-12 17:01 | 2013-08-12 17:38 | 37 | 11kV | 25649 | 1601 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12570 Avoca 11kv Pa22 "Davies Wilima" fdr tripped and relcosed on A and B phase overcurrent Also 11kv recloser 46529 Davistown Mundora triped on overcurrent Cause: Tree branch on OH mains. Branch on mains at LK42408. TPE to check grading. See 1004763,4 Exclude 1004426 | August | 2013 | 2014Q1 | 2014 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2013-08-12 | N | 16.0206 | N | 18 | N | N | 1.1101 | 39.4971 | 18743.5327
[7 empty] | 16031 | 15100 | 1004161 | 2013-08-12 14:32 | 2013-08-12 17:50 | 198 | 11kV | 107940 | 1680 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12610 Long Jetty section of 11kv pa22 "Long Hetty" fdr @ Intellirupter 61951 Swadling Oaks 0.1 tripped on A phase overcurrent, Lockout Cause: @ Underslung links LK43077 A phase collapsed into LV See 1004716 exclude 1004161 | August | 2013 | 2014Q1 | 2014 | ZN12610:PA22 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2013-08-12 | N | 64.25 | N | 18 | N | N | 1.1101 | 39.4971 | 78879.3683
[7 empty] | 16292 | 17910 | 1004112 | 2013-08-12 14:13 | 2013-08-12 18:05 | 232 | 11kV | 3941 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 136713 Wires down beyond link 5321 | August | 2013 | 2014Q1 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-08-12 | N | 39.0198 | N | 18 | N | N | 1.1101 | 39.4971 | 2879.9666
[7 empty] | 15767 | 11777 | 1004389 | 2013-08-12 16:32 | 2013-08-12 18:22 | 110 | 11kV | 126070 | 1734 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | @Zn12570 Avoca 11kv Pa24 "Woodifield Wladron" Tripped on: Earth Fault, lockout and timing Signals:11kv trip and EFI EFI's: S126664 ABNORMAL: AB44523 closed and AB44522 open (defective) Cause: Tree branch brought down OH. Made safe and restored supply See 1004747,8,50 exclude 1004389 | August | 2013 | 2014Q1 | 2014 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2013-08-12 | N | 72.7047 | N | 18 | N | N | 1.1101 | 39.4971 | 92128.2376
[7 empty] | 15218 | 4927 | 1003923 | 2013-08-12 13:12 | 2013-08-12 20:25 | 433 | 11kV | 428126 | 1565 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | @Zn1850 Bass Hill: 11kv Panel 13 labelled "S4312 Edgar Marion" tripped on: Signals: 11kv trip, Tx 3 group earth and Zone earth Relays: A phase timed overcurrent, earth fault, EFI Field EFI's: S4312, S4434, S8894, S4345 Remarks: tree/branch brought down OH. 1st high voltage into LV mains in Manahan St near AB41. 2nd Bond off at AB140. 3rd LV//'s in fuses blown. | August | 2013 | 2014Q1 | 2014 | ZN1850:PA13 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-08-12 | N | 273.5629 | N | 18 | N | N | 1.1101 | 39.4971 | 312861.8532
[7 empty] | 14736 | 340 | 1004510 | 2013-08-12 19:22 | 2013-08-12 20:49 | 87 | 11kV | 100284 | 1201 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn12690 Berkely Vale Pa19 fdr tripped Relays: A & B phase IOC pa19R Signals: IOC Trip Cause: not ascertained See 1004874,5 Exclude 1004510,7,42 | August | 2013 | 2014Q1 | 2014 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2013-08-12 | N | 83.5004 | N | 18 | N | N | 1.1101 | 39.4971 | 73284.5893
[7 empty] | 16313 | 18137 | 1003843 | 2013-08-12 12:27 | 2013-08-12 21:40 | 553 | 11kV | 10924 | 40 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 136712 2 fault operations C phase Earth fault Cph-E 47Amp Excluded OMS 1003843 | August | 2013 | 2014Q1 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-08-12 | N | 273.1 | N | 18 | N | N | 1.1101 | 39.4971 | 7982.937
[7 empty] | 15910 | 13247 | 1004546 | 2013-08-12 20:35 | 2013-08-12 22:40 | 125.25 | 11kV | 3882.75 | 31 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa2 @CP43285 interrupted by DOp to allow tree branch remvoal form OH Weather related. Tree branch on OH near PT13863 See 1004551 exclude 1004546,50 | August | 2013 | 2014Q1 | 2014 | ZN12630:PA2 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2013-08-12 | N | 125.25 | N | 18 | N | N | 1.1101 | 39.4971 | 2837.3992
[7 empty] | 16474 | 20189 | 1004896 | 2013-08-13 09:37 | 2013-08-13 13:05 | 208 | 11kV | 624 | 3 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 136723 B phase DOLF : 10 Amp Possum found at bottom of pole. 3 x 11kV arrestors replaced Excluded OMS 1004697 & 1004896 | August | 2013 | 2014Q1 | 2014 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2013-08-13 | N | 208 | N | 8 | N | N | 1.1101 | 39.4971 | 456.0008
[7 empty] | 15131 | 3993 | 1004869 | 2013-08-13 12:05 | 2013-08-13 13:05 | 60 | 11kV | 13680 | 228 | HV | Vandalism | 3rd Party Impact | O/H Link | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of Pa1 @CP47849 Reservoir Beckford 0.5 Bph HV link 47848Y was found open with a branch stuck in it. Cause: Phantom Operator. 3 young (12-14 yr olds) on motor bikes road off when DOp McPherson approached heading EAST in bush behind CP47849. There was signs of rocks & branches having been thrown at CP. See 1005291 exclude 1004857,69,70,3,81,3,5,8,9,91,3,4,9 | August | 2013 | 2014Q1 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-08-13 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 9996.9405
[7 empty] | 16070 | 15641 | 1004563 | 2013-08-12 21:33 | 2013-08-13 14:40 | 1026.9833 | 11kV | 6161.9 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Ex ZN12660 Woy Woy section of Pa14 @RE45093 Wondabyne tripped on overcurrent Cause: Oh down. Difficult access. Gosford mains repaired and restored supply. | August | 2013 | 2014Q1 | 2014 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2013-08-12 | N | 1026.9833 | N | 18 | N | N | 1.1101 | 39.4971 | 4502.9348
[7 empty] | 14952 | 2285 | 1004713 | 2013-08-13 09:40 | 2013-08-13 15:20 | 340 | 11kV | 17340 | 51 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 136724/02 Broken king pin, 11kV main on pole KT-40826. Isolated for repairs Excluded report 136700 | August | 2013 | 2014Q1 | 2014 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2013-08-13 | N | 340 | N | 8 | N | N | 1.1101 | 39.4971 | 12671.5606
[7 empty] | 14838 | 1294 | 1004951 | 2013-08-13 14:02 | 2013-08-13 15:50 | 108 | 11kV | 21168 | 196 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT62839 Harold Lowry, Roadside HDO operated 63.5k Remarks: Fuse fatigue. Suspect S48759 Dist 3 was in parallel at that time. | August | 2013 | 2014Q1 | 2014 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-08-13 | N | 108 | N | 8 | N | N | 1.1101 | 39.4971 | 15468.95
[7 empty] | 15683 | 10809 | 1004954 | 2013-08-13 14:05 | 2013-08-13 16:57 | 172 | 11kV | 52902 | 531 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn340 Botany Pnl.8 feeder tripped on Earth Fault and EFI Field EFIs: S2496 S3409 Underground feeder fault from S3409 Sw B to S8559 Sw A tee S2120, S784 & S3138. Due to LV //'s, LV conductors on ground and bonds burnt off from various locations see 1005682 1005684 1005688 1005689 | August | 2013 | 2014Q1 | 2014 | ZN340:PA8 | ZN340:PA8 | ZN00340/000008 | BAYSIDE | UG | Not Veg | 2013-08-13 | N | 99.6271 | N | 8 | N | N | 1.1101 | 39.4971 | 38659.2213
[7 empty] | 14835 | 1272 | 1005069 | 2013-08-13 17:24 | 2013-08-13 18:30 | 65.6333 | 11kV | 16867.7667 | 257 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 136729 isolated to repair pin off x-arm at pole DR-40029 | August | 2013 | 2014Q1 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-08-13 | N | 65.6333 | N | 8 | N | N | 1.1101 | 39.4971 | 12326.4664
[7 empty] | 15106 | 3808 | 1004920 | 2013-08-13 13:34 | 2013-08-13 18:55 | 321 | 11kV | 85774 | 744 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 136726/7 fire & broken pole at ABS 74977 related to report 136727. system abnormal. ABS 74173 closed & ABS 74963 (DMA) OPEN. | August | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-08-13 | N | 115.2876 | N | 8 | N | N | 1.1101 | 39.4971 | 62681.1093
[7 empty] | 15963 | 13988 | 1005099 | 2013-08-13 19:28 | 2013-08-13 21:10 | 102 | 11kV | 64424 | 913 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At Zn80 Chatswood Panel 25 tripped on Relays: C phase O/C+E/F, Fault check, EI and Lockout UGOH Short circuit See OMS 1005439 1005442 1005443 1005099 1005100 1005104 | August | 2013 | 2014Q1 | 2014 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | Unknown | Unknown | 2013-08-13 | N | 70.563 | N | 8 | N | N | 1.1101 | 39.4971 | 47079.159
[7 empty] | 15629 | 10097 | 1005203 | 2013-08-14 08:30 | 2013-08-14 08:50 | 20 | 11kV | 1020 | 51 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 136747 Sub isolated to install Gen for emerg SI M0409 to replace pole KT-40826 | August | 2013 | 2014Q1 | 2014 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2013-08-14 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 745.3859
[7 empty] | 15265 | 5893 | 1005122 | 2013-08-14 08:18 | 2013-08-14 11:25 | 187 | 11kV | 1122 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 136741 B phase DOLF : 20 Amp Excluded OMS 1005182 | August | 2013 | 2014Q1 | 2014 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2013-08-14 | N | 187 | N | 4 | N | N | 1.1101 | 39.4971 | 819.9245
[7 empty] | 15630 | 10098 | 1005539 | 2013-08-14 16:20 | 2013-08-14 16:40 | 20 | 11kV | 1020 | 51 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 136746 Sub isolated to remove Gen for emerg SI M0409 to replace pole KT-40826. also refer OMS 1005203 | August | 2013 | 2014Q1 | 2014 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2013-08-14 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 745.3859
[7 empty] | 15673 | 10717 | 1005607 | 2013-08-14 22:16 | 2013-08-14 23:26 | 70 | 11kV | 153858 | 2715 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | at s.35500 tOP rYDE, pANEL 24 fDR cb TRIPPED ON (24r) A and B phase OC, efi, 11kV trip, #2 Tx group earth. Field efi's down at S.61646, S.49445, S.5739, S.36042. Possum on UG/OH at S.6304 | August | 2013 | 2014Q1 | 2014 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2013-08-14 | N | 56.6696 | N | 4 | N | N | 1.1101 | 39.4971 | 112434.8884
[7 empty] | 15431 | 7821 | 1005620 | 2013-08-15 08:15 | 2013-08-15 09:00 | 45 | 11kV | 45 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136749 Burnt Live Line Clamp Excluded Oms 1005620 | August | 2013 | 2014Q1 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-08-15 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 16347 | 18518 | 1005906 | 2013-08-15 14:30 | 2013-08-15 14:57 | 27 | 11kV | 28827 | 1119 | HV | Arcing | Equipment Failure | DC Transformer | Unplanned | Unselected | N | ZN 10997 Sans Souci - Pnl 1 - Opened for safety. S 10374 was out under test Access permit. On energisation there was arcing on the Transformer tails and endbox. DOp then contacted AOp and asked for the feeder to be deenergised. S 10462 and S 10374 were in // with S 46995 for the permit and were restored at the same time. ME: 1007207. Rest Step: 1007208. Withdrawn: 1005900, 6. | August | 2013 | 2014Q1 | 2014 | ZN10997:PA1 | ZN10997:PA1 | ZN10997/000001 | BAYSIDE | UG | Not Veg | 2013-08-15 | N | 25.7614 | N | 5 | N | N | 1.1101 | 39.4971 | 21065.9213
[7 empty] | 14860 | 1532 | 1006064 | 2013-08-15 16:32 | 2013-08-15 16:43 | 11 | 11kV | 17776 | 1616 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | At S.15002 Narrabeen Panel 6 and Panel 8 tripped on SEL operation. Staff error whilst switching | August | 2013 | 2014Q1 | 2014 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | Unknown | Not Veg | 2013-08-15 | N | 11 | N | 5 | N | N | 1.1101 | 39.4971 | 12990.1765
[7 empty] | 14816 | 1089 | 1006063 | 2013-08-15 16:32 | 2013-08-15 16:43 | 11 | 11kV | 8987 | 817 | HV | Staff Operation | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.15002 Narrabeen Panel 6 and Panel 8 tripped on SEL operation. Staff error whilst switching | August | 2013 | 2014Q1 | 2014 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Not Veg | 2013-08-15 | N | 11 | N | 5 | N | N | 1.1101 | 39.4971 | 6567.4345
[7 empty] | 16350 | 18538 | 1006023 | 2013-08-15 23:21 | 2013-08-16 00:39 | 78 | 11kV | 43273 | 643 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12570 section of Pa33 @IR50407 the scenic bounty tripped, reclosed, tripped, reclosed, tripped, reclosed, tripped & locked out on overcurrent Cause: not ascertained See 1006087,8,9 exclude 1006023 | August | 2013 | 2014Q1 | 2014 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2013-08-15 | N | 67.2986 | N | 5 | N | N | 1.1101 | 39.4971 | 31622.6321
[7 empty] | 15037 | 3100 | 1006059 | 2013-08-16 08:08 | 2013-08-16 08:17 | 9 | 11kV | 35946 | 3994 | HV | Staff Other | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | LID 136758 1 fault operation Busbar protection Staff drilling pannel vibrated VAA relay. BGN, TA-1A, TA-3A, TA-3B,TA-3B, TM-3A, TM-3B. | August | 2013 | 2014Q1 | 2014 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | Unknown | Not Veg | 2013-08-16 | N | 9 | N | 4 | N | N | 1.1101 | 39.4971 | 26268.2766
[7 empty] | 14871 | 1688 | 1006664 | 2013-08-16 08:19 | 2013-08-16 08:24 | 5 | 11kV | 19970 | 3994 | HV | Staff Other | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | LID 136760 1 fault operation Busbar protection Same Fdrs tripped again see #136759. OMS 1006656 BGN, TA-1A, TA-3A, TA-3B,TA-3B, TM-3A, TM-3B. | August | 2013 | 2014Q1 | 2014 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | Unknown | Not Veg | 2013-08-16 | N | 5 | N | 4 | N | N | 1.1101 | 39.4971 | 14593.487
[7 empty] | 15324 | 6596 | 1006270 | 2013-08-16 14:12 | 2013-08-16 17:55 | 223 | 11kV | 177891 | 1308 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn Revesby 11kv Panel 5 labelled "S6360 Davies Banks No3" Tripped/reclosed/tripped on signals 11kv trip, TX 3 group earth, Zone earth. Relays EFI, fault check, feeder reclose lockout. Field EFIs: S6360, S6525, S709, S4954 Remarks: UG Fault. Between LB 3262 and swA at S4663 Queensbury Court. | August | 2013 | 2014Q1 | 2014 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-08-16 | N | 136.0023 | N | 4 | N | N | 1.1101 | 39.4971 | 129997.4959
[7 empty] | 16149 | 16473 | 1003503 | 2013-08-10 23:52 | 2013-08-16 18:55 | 8343 | 11kV | 51823 | 50 | HV | 3rd Party Action | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | Zn3288 City South 43/44E and 43/44F feeders tripped on - Buchholz Abnormal: 43/44D feeder out of service defective Flooding - burst water main in Harris St corner Ultimo Rd causing S5556 UTS Merino Boulevarde sub to flood. see 1006709 1006703 # 1006718 - LV dist in street flooded | August | 2013 | 2014Q1 | 2014 | ZN3288:PA43 44DEF | ZN3288:PA43 44DEF | ZN03288/43 44DEF | SYDNEY | UG | Not Veg | 2013-08-10 | N | 1036.46 | N | 2 | N | N | 1.1101 | 39.4971 | 37870.7199
[7 empty] | 15987 | 14463 | 1006376 | 2013-08-16 18:22 | 2013-08-16 18:55 | 33.3667 | 11kV | 1501.5 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136768 A & B phase DOLF : 16 Ammp Excluded OMS 1006376; 1006384 & 1006385 CC1: 22-"Refer to SOp" | August | 2013 | 2014Q1 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2013-08-16 | N | 33.3667 | N | 4 | N | N | 1.1101 | 39.4971 | 1097.2519
[7 empty] | 15155 | 4181 | 1006402 | 2013-08-17 01:59 | 2013-08-17 04:00 | 121 | 11kV | 10406 | 86 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 9995 Novara Pavia - Centre phase HDO (31.5A). Centre phase HDO failed in service. ME: 1006762. Withdrawn: 100402, 3, 4, 5. | August | 2013 | 2014Q1 | 2014 | ZN9252:PA9 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Not Veg | 2013-08-17 | N | 121 | N | 7 | N | N | 1.1101 | 39.4971 | 7604.3979
[7 empty] | 14737 | 345 | 1006779 | 2013-08-17 08:30 | 2013-08-17 12:45 | 255 | 11kV | 2805 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Planned LID 136769 | August | 2013 | 2014Q1 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2013-08-17 | N | 255 | N | 7 | N | N | 1.1101 | 39.4971 | 2049.8113
[7 empty] | 16251 | 17526 | 1006465 | 2013-08-17 13:43 | 2013-08-17 15:30 | 107 | 11kV | 107 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 136775 11kV Dropper pulled out of top of DOLF. No Protection operated. Excluded OMS # 1006465 | August | 2013 | 2014Q1 | 2014 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2013-08-17 | N | 107 | N | 7 | N | N | 1.1101 | 39.4971 | 78.1924
[7 empty] | 16357 | 18647 | 1006698 | 2013-08-17 17:05 | 2013-08-17 18:45 | 100 | 11kV | 200 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | LID 136777 Isolate to replace xarm at pole NB-40348. Excluded oms 1006481 | August | 2013 | 2014Q1 | 2014 | 232:11453 | 232:11453 | ZN00232/011453 | PORT STEPHENS | OH | Not Veg | 2013-08-17 | N | 100 | N | 7 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 15029 | 3055 | 1006477 | 2013-08-17 14:28 | 2013-08-17 20:05 | 337 | 11kV | 6740 | 20 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 136780 isolate to repair broken strands on OHM & LV wires down. Excluded OMS #1006476/7 | August | 2013 | 2014Q1 | 2014 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2013-08-17 | N | 337 | N | 7 | N | N | 1.1101 | 39.4971 | 4925.3932
[7 empty] | 16120 | 16160 | 1006518 | 2013-08-17 18:33 | 2013-08-17 21:00 | 147 | 11kV | 294 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 136779 A & C phase DOLF : 10 Amp Blown line fuses. Possible wind of Wildlife. Please patrol. V= 248, 248, 250 A= 5, 7, 5 Excluded OMS # 1006518. | August | 2013 | 2014Q1 | 2014 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2013-08-17 | N | 147 | N | 7 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 16340 | 18436 | 1006714 | 2013-08-17 21:08 | 2013-08-17 22:25 | 77 | 11kV | 6237 | 81 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind | N | LID 136781 isolate to repair insulators at ABS 9077 | August | 2013 | 2014Q1 | 2014 | 203:8088 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Not Veg | 2013-08-17 | N | 77 | N | 7 | N | N | 1.1101 | 39.4971 | 4557.8156
[7 empty] | 15981 | 14275 | 1006536 | 2013-08-18 03:50 | 2013-08-18 04:30 | 40 | 11kV | 2160 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136782 A phase DOLF : 20 Amp Excluded OMS 1006536 & 1006537 | August | 2013 | 2014Q1 | 2014 | 210:8676 | 210:83474 | ZN00210/083474 | NEWCASTLE | UG | Not Veg | 2013-08-18 | N | 40 | N | 2 | N | N | 1.1101 | 39.4971 | 1578.4643
[7 empty] | 14755 | 524 | 1006628 | 2013-08-18 20:32 | 2013-08-18 21:34 | 62 | 11kV | 83072 | 1396 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Burnt bond at corner of Horning and Condamine Sts, manly Vale. cause Panel 17 ex S.36300 Balgowlah Nth to trip on SEL | August | 2013 | 2014Q1 | 2014 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2013-08-18 | N | 59.5072 | N | 2 | N | N | 1.1101 | 39.4971 | 60706.5674
[7 empty] | 15957 | 13874 | 1006710 | 2013-08-19 09:03 | 2013-08-19 10:41 | 98.5333 | 11kV | 963.1167 | 14 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 136789 C phase DOLF : 31 Amp Fuse fatigued. Volts = 250, 250, 250. | August | 2013 | 2014Q1 | 2014 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2013-08-19 | N | 68.794 | N | 5 | N | N | 1.1101 | 39.4971 | 703.8173
[7 empty] | 15247 | 5630 | 1006764 | 2013-08-19 10:13 | 2013-08-19 12:15 | 122 | 11kV | 122 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | N | LID 136791 C phase DOLF : 10 Amp Tx Volts: 242V Excluded OMS No. 1006764 | August | 2013 | 2014Q1 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-08-19 | N | 122 | N | 5 | N | N | 1.1101 | 39.4971 | 89.154
[7 empty] | 16211 | 17130 | 1006871 | 2013-08-19 12:30 | 2013-08-19 15:00 | 150 | 11kV | 1950 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 136794 Single phase DOLF : 20 Amp Excluded OMS 1006896 | August | 2013 | 2014Q1 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-08-19 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 1425.0025
[7 empty] | 15868 | 12861 | 1006877 | 2013-08-19 12:36 | 2013-08-19 15:50 | 194 | 11kV | 4656 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 136795 Three phase fdr patrolled nothing found feeder restored in sections 11kV feeder fault passed 42011. | August | 2013 | 2014Q1 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-08-19 | N | 194 | N | 5 | N | N | 1.1101 | 39.4971 | 3402.4675
[7 empty] | 15687 | 10874 | 1007062 | 2013-08-19 14:32 | 2013-08-19 19:05 | 273 | 11kV | 1365 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 136796 SECTION ISOLATED TO REPAIR BURNT OFF TAPPING AT SUB 54364 Excluded OMS1006938 | August | 2013 | 2014Q1 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-08-19 | N | 273 | N | 5 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 15894 | 13115 | 1007262 | 2013-08-20 11:37 | 2013-08-20 12:20 | 43 | 11kV | 903 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 23 Opened due to unknown cause No Protection Relays Operated No Alarms Recieved (RTU is test for telecontrol Work) Cause Not ascertained for outage TPE to investigate | August | 2013 | 2014Q1 | 2014 | ZN8000:PA23 | ZN35500:PA19 | ZN35500/000019 | RYDE | OH | Veg | 2013-08-20 | N | 43 | N | 2 | N | N | 1.1101 | 39.4971 | 659.8858
[7 empty] | 15406 | 7499 | 1007443 | 2013-08-20 18:15 | 2013-08-20 19:26 | 71 | 11kV | 95512 | 1432 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S3425 Castle Cove Panel 30 Gibbes Eastern Valley Tripped and reclosed on C phase IOC and Timed Timing and Lockout 11kV Trip Cause: Bond Burnt off at AB2856 See OMS 1007609 1007610 1007443 1007464 | August | 2013 | 2014Q1 | 2014 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | WILLOUGHBY | OH | Not Veg | 2013-08-20 | N | 66.6983 | N | 2 | N | N | 1.1101 | 39.4971 | 69797.3525
[7 empty] | 15542 | 8887 | 1007500 | 2013-08-21 04:41 | 2013-08-21 06:25 | 104 | 11kV | 108674 | 1236 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14891 Wyong Pa9 tripped, reclosed, tripped and locked out on: Relays-A & C phase IOC, Reclose timer, Lock out, EFI, Earth Fault Check, Tx1 Earth Fault Check, Prohibition relay on frame leakage panel Signals: 11kv trip EFI: S18620 S14753, O/HMenagle rd 2 off, S14366 S14551 S14700 S18099 S18222 Cause: UG Fault between S18223/SwA and S14607/Sw6664 See 1007670,2,3,4 Exclude 1007500 | August | 2013 | 2014Q1 | 2014 | ZN14891:PA9 | ZN14891:PA9 | ZN14891/000009 | CENTRAL COAST | UG | Not Veg | 2013-08-21 | N | 87.9239 | N | 1 | N | N | 1.1101 | 39.4971 | 79415.7539
[7 empty] | 14927 | 2119 | 1008401 | 2013-08-22 20:21 | 2013-08-22 21:23 | 62 | 11kV | 77128 | 1244 | HV | Overload | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At S1610 Homebush Bay Panel #11 RAS Showring North Feeder tripped on o/c trip-G1-A-B-C phase fault 11kv trip Remarks: overload. x-zone switching feeder tripped on o/c Related jobs: #1008401, 1008473 | August | 2013 | 2014Q1 | 2014 | ZN1610:PA11 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2013-08-22 | N | 62 | N | 1 | N | N | 1.1101 | 39.4971 | 56362.8675
[7 empty] | 15264 | 5889 | 1008416 | 2013-08-23 02:05 | 2013-08-23 04:43 | 158 | 11kV | 82318 | 521 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136832 3 fault operations Earth fault Daylight patrol required | August | 2013 | 2014Q1 | 2014 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2013-08-23 | N | 158 | N | 6 | N | N | 1.1101 | 39.4971 | 60155.5664
[7 empty] | 15332 | 6644 | 1008481 | 2013-08-23 09:35 | 2013-08-23 10:14 | 39 | 11kV | 428.1 | 11 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 2466 Flemington Panel No.26 "Edwin Flack Uhrig, Uhrig Carter No.5 "Feeder opened on Earth fault Zone Earth, No.1 Group Earth" EFIs operated @ Subs 48512, 35058, 35391,35433, 35434 Remarks: 11KV UG cable fault from S2466 Flemington Panel No.1 to Sub 35434 Uhrig Carter No.4 to Sub 49740 Centenary Park No.1 Related jobs: #1008481, 1008484, 1008486, 1009371 | August | 2013 | 2014Q1 | 2014 | ZN2466:PA26 | ZN2466:PA18 | ZN02466/000018 | PARRAMATTA | UG | Not Veg | 2013-08-23 | N | 38.9182 | N | 6 | N | N | 1.1101 | 39.4971 | 312.8429
[7 empty] | 15897 | 13159 | 1008476 | 2013-08-23 09:19 | 2013-08-23 10:34 | 75 | 11kV | 83577 | 1243 | HV | Vegetation Blow/Fall In | Vegetation | DC Transformer | Unplanned | Unselected | N | @Zn12580 Erina 11kv CB 1 tripped on Relays: Overcurrent 50T AB (A&B phase IOC trip) Signals: 11kv trip Cause: Tree branh found on Tx tank at PT11929 Elfin Hill Avoca See 1009931,4,5 Exclude 1008476,89 | August | 2013 | 2014Q1 | 2014 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Veg | 2013-08-23 | N | 67.2381 | N | 6 | N | N | 1.1101 | 39.4971 | 61075.6065
[7 empty] | 16061 | 15472 | 1010035 | 2013-08-23 11:28 | 2013-08-23 12:58 | 90 | 11kV | 150576 | 1721 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn14892 Charmahven Pa19 tripped, reclosed, tripped and locked out on Relays: overcurrent, EFI, Earht Fault, Timing Relay, Lockout, fault check, tx @B fault checj Signlas: 11k trip EFI's: Nil Cause: UG fdr from Zn14892:Pa19 to S14809/SwA See 1010035 exclude 1008578 | August | 2013 | 2014Q1 | 2014 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | UG | Not Veg | 2013-08-23 | N | 87.4933 | N | 6 | N | N | 1.1101 | 39.4971 | 110036.4996
[7 empty] | 14887 | 1793 | 1008519 | 2013-08-23 12:30 | 2013-08-23 13:15 | 45 | 11kV | 270 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136843 burnt off tapping at pole 9N-20109 off Bureen Rd | August | 2013 | 2014Q1 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-08-23 | N | 45 | N | 6 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 15042 | 3126 | 1008645 | 2013-08-23 15:25 | 2013-08-23 18:40 | 195 | 11kV | 1950 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 136849 B phase BURNT OFF LIVE LINE LEAD TO DOLF. Excluded OMS REPORT NO 1008645. | August | 2013 | 2014Q1 | 2014 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2013-08-23 | N | 195 | N | 6 | N | N | 1.1101 | 39.4971 | 1425.0025
[7 empty] | 15140 | 4060 | 1008805 | 2013-08-24 04:08 | 2013-08-24 05:28 | 80 | 11kV | 65870 | 825 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 1 - EFL, EFC, EFI. 11kV UG cable fault from S 9195 to S 9143 to S 9413. ME: 1009210. Withdrawn: 1008805. | August | 2013 | 2014Q1 | 2014 | ZN9550:PA1 | ZN9550:PA1 | ZN09550/000001 | SUTHERLAND | UG | Not Veg | 2013-08-24 | N | 79.8424 | N | 2 | N | N | 1.1101 | 39.4971 | 48135.8532
[7 empty] | 15913 | 13265 | 1009703 | 2013-08-24 18:48 | 2013-08-24 22:10 | 202 | 11kV | 202 | 1 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At CP1352MWS+DB Victoria Rd 80A HDO Operated Cause: Animals/Birds - Possum | August | 2013 | 2014Q1 | 2014 |  |  |  | HORNSBY | OH | Not Veg | 2013-08-24 | N | 202 | N | 2 | N | N | 1.1101 | 39.4971 | 147.6156
[7 empty] | 15121 | 3898 | 1008972 | 2013-08-25 06:12 | 2013-08-25 07:30 | 78 | 11kV | 79626 | 1298 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.1164 Rose Bay Pnl.27 - tripped on Earth Fault Field EFIs: S471 4482 6392 8897 UG cable fault from S8897 (Sw B) to S521 (Sw A) to S6259 (Sw A) to S8377 (Sw B) see 1009131 1009132 | August | 2013 | 2014Q1 | 2014 | ZN1164:PA27 | ZN36100:PA5 | ZN36100/000005 | WOOLLAHRA | UG | Not Veg | 2013-08-25 | N | 61.3451 | N | 2 | N | N | 1.1101 | 39.4971 | 58188.3322
[7 empty] | 15519 | 8680 | 1009043 | 2013-08-25 14:46 | 2013-08-25 15:48 | 62 | 11kV | 24389 | 527 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S35500 Top Ryde Panel 31 11kV feeder tripped on A and B IOC with EFI Alarms Tx3 Group Earth Cause: 1kV UGOH to S5372 Plassey Delhi Failed 1009835 1009837 1009838 1009043 | August | 2013 | 2014Q1 | 2014 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | Unknown | Unknown | 2013-08-25 | N | 46.2789 | N | 2 | N | N | 1.1101 | 39.4971 | 17822.7618
[7 empty] | 15093 | 3621 | 1009434 | 2013-08-26 22:47 | 2013-08-26 23:53 | 65.9167 | 11kV | 66048.5 | 1002 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | ZN 9245 Engadine - Pnl 11 - Tripped, Earth Fault, Field EFIs. Possum fried at PT 9527. Roadside phase HDO operated (31.5A). ME: 1009434. Withdrawn: 1009435, 6. | August | 2013 | 2014Q1 | 2014 | ZN9245:PA11 | ZN9245:PA4 | ZN09245/000004 | SUTHERLAND | OH | Not Veg | 2013-08-26 | N | 65.9167 | N | 1 | N | N | 1.1101 | 39.4971 | 48266.2957
[7 empty] | 15170 | 4282 | 1009472 | 2013-08-27 08:39 | 2013-08-27 10:27 | 108 | 11kV | 1404 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At PT16098 Tumburra St left phase 31.5amp HDO blown Cause: Fuse blown cause unknown. 1009921 1009511 1009472 1009491 1009496 | August | 2013 | 2014Q1 | 2014 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2013-08-27 | N | 108 | N | 3 | N | N | 1.1101 | 39.4971 | 1026.0018
[7 empty] | 15971 | 14166 | 1009500 | 2013-08-27 09:28 | 2013-08-27 11:15 | 107 | 11kV | 214 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Ex Zn12660 Woy Woy section of Pa14 @PT12575 Woy Woy Corowa roadside 16 amp HDO fuse operated Cause: Lightning/Surge arrestor found to be defective. Was cutaway to restore PT12575 See seperate interruption on RE48036 Rawson Woy Woy - 1011695 also refer to 1009500 | August | 2013 | 2014Q1 | 2014 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2013-08-27 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 15959 | 13943 | 1009782 | 2013-08-27 21:13 | 2013-08-27 22:10 | 57 | 11kV | 57 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136881 A & B phase DOLF : 16 Amp Excluded oms 1009782 | August | 2013 | 2014Q1 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | UG | Not Veg | 2013-08-27 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 41.6539
[7 empty] | 15609 | 9729 | 1009788 | 2013-08-28 03:51 | 2013-08-28 05:22 | 91 | 11kV | 6825 | 75 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | At S16038 Riverview Rd 400A fuse blown on B bphase of distributor 2 House Fire at 75 River Rd Avalon Beach | August | 2013 | 2014Q1 | 2014 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | Unknown | Not Veg | 2013-08-28 | N | 91 | N | 2 | N | N | 1.1101 | 39.4971 | 4987.5087
[7 empty] | 15839 | 12530 | 1010110 | 2013-08-28 15:07 | 2013-08-28 16:40 | 93 | 11kV | 1581 | 17 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136888 B phase DOLF : 20 Amp birds at sub 53452. blew sub DOLF (10A) and Spur DOLF 40799 Excluded oms 1010110 | August | 2013 | 2014Q1 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2013-08-28 | N | 93 | N | 2 | N | N | 1.1101 | 39.4971 | 1155.3482
[7 empty] | 15022 | 2999 | 1010210 | 2013-08-29 00:55 | 2013-08-29 06:35 | 340 | 11kV | 25500 | 75 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12570 Avoca section of Pa34 @ PT12844 Hillcrest Scenic C phase HDO fuse blown due to fuse fatigue. batch 443 See 1010646 exclude 1010210 | August | 2013 | 2014Q1 | 2014 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2013-08-29 | N | 340 | N | 2 | N | N | 1.1101 | 39.4971 | 18634.6479
[7 empty] | 15363 | 6965 | 1010221 | 2013-08-29 06:58 | 2013-08-29 08:59 | 121 | 11kV | 98489 | 1551 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2196 Milperra Panel #5 "Marigold Armour #4 FDR" tripped ontime earth fault lockout fault check Signals - 11kv trip zone earth #2 Group earth Remarks: UG fault. Suspect 11kv UG fault between S8990 Bracher Park to S8011 Truscott batchelor tee S7097 Marco Childs Related jobs: #1016221, 1011641, 1011639, 1011638 | August | 2013 | 2014Q1 | 2014 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-08-29 | N | 63.5003 | N | 2 | N | N | 1.1101 | 39.4971 | 71972.8563
[7 empty] | 15365 | 6970 | 1010598 | 2013-08-30 06:49 | 2013-08-30 07:33 | 44 | 11kV | 25000 | 696 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 901 Surry Hillls - Pnl 8 - Earth Fault, Field EFIs. 11kV feeder fault from S 4067 to S 35617 to S 63. ME: 1011276. Rest Step: 1011279, 80. Withdrawn: 1010598. | August | 2013 | 2014Q1 | 2014 | ZN901:PA8 | ZN7900:PA12 | ZN07900/000012 | SYDNEY | UG | Not Veg | 2013-08-30 | N | 35.9195 | N | 3 | N | N | 1.1101 | 39.4971 | 18269.2626
[7 empty] | 15615 | 9804 | 1010778 | 2013-08-30 13:48 | 2013-08-30 16:00 | 132 | 11kV | 1452 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @Sub 4100 Beresford Coventry A phase HV 90amp siba fuse blown. Remarks: Cause not ascertained. Related jobs: #1010778, 1010817, 1011654 | August | 2013 | 2014Q1 | 2014 | ZN2835:PA41 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | OH | Veg | 2013-08-30 | N | 132 | N | 3 | N | N | 1.1101 | 39.4971 | 1061.0788
[7 empty] | 15848 | 12673 | 1010878 | 2013-08-30 20:52 | 2013-08-30 23:00 | 128.2667 | 11kV | 256.5333 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 136906 Single phase DOLF : 3 Amp Replaced 1 burnt up DOLF carrier and both DOLF fuses CC1: 22-"Refer to SOp" | August | 2013 | 2014Q1 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2013-08-30 | N | 128.2667 | N | 3 | N | N | 1.1101 | 39.4971 | 187.467
[7 empty] | 15797 | 12105 | 1010903 | 2013-08-31 08:04 | 2013-08-31 09:00 | 56 | 11kV | 37464 | 669 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12570 Avoca section of pa24 @Tee off to LB42022 in fdr towards PT11831 bond burnt off See 1011201 exclude 1010903 | August | 2013 | 2014Q1 | 2014 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2013-08-31 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 27377.5862
[7 empty] | 16456 | 20014 | 1010938 | 2013-08-31 10:00 | 2013-08-31 11:20 | 80 | 11kV | 7891 | 1097 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn13000 Lake Munmorah section of Pa11 @RE45092 Mannering Park tripped and reclosed @PT12304 Campbell Vales 31.5 k footpath HDO fatigued operation See 1011210,2 Exclude 1010937,8 | August | 2013 | 2014Q1 | 2014 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2013-08-31 | N | 7.1933 | N | 4 | N | N | 1.1101 | 39.4971 | 5766.5101
[7 empty] | 15640 | 10212 | 1010984 | 2013-08-31 14:04 | 2013-08-31 14:52 | 48 | 11kV | 1392 | 29 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 136909 2 fault operation B & C phase Overcurrent Customer cutting tree 10 Casson Ave, brought down 11kV mains between poles IV-30840 & IV-37063. Excluded OMS 1010984, 1010985, 1011001. | August | 2013 | 2014Q1 | 2014 | 206:34437 | 206:34437 | ZN00206/034437 | LAKE MACQUARIE | OH | Veg | 2013-08-31 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 1017.2325
[7 empty] | 15228 | 5231 | 1011039 | 2013-08-31 18:59 | 2013-08-31 21:35 | 156 | 11kV | 144036 | 1517 | HV | Arcing | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9252 Jannali - Pnl 9 - Trip/reclose/trip, A phase timed OC, C phase IOC, reclose timing relay, lockout relay. Section of feeder from LB35331 to PT 9362 had a flashover. ME: 1011214. Rest Steps: 1011215, 7. Withdrawn: 1011039, 40, 44, 45, 46. | August | 2013 | 2014Q1 | 2014 | ZN9252:PA9 | ZN9252:PA21 | ZN09252/000021 | SUTHERLAND | OH | Not Veg | 2013-08-31 | N | 94.9479 | N | 4 | N | N | 1.1101 | 39.4971 | 105257.2605
[7 empty] | 15050 | 3226 | 1011051 | 2013-09-01 02:49 | 2013-09-01 03:30 | 41 | 11kV | 5452 | 272 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 136912 11kV UGOH fault pole JU-24270 Sw 72 trip & reclose then Fdr de-energised for safety please patrol feeder | September | 2013 | 2014Q1 | 2014 | 208:72 | 257:81999 | ZN00257/081999 | NEWCASTLE | Unknown | Unknown | 2013-09-01 | N | 20.0441 | N | 1 | N | N | 1.1101 | 39.4971 | 3984.1608
[7 empty] | 15077 | 3456 | 1011148 | 2013-09-02 06:54 | 2013-09-02 08:30 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136919 Single phase DOLF : 10 Amp | September | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | UG | Not Veg | 2013-09-02 | N | 96 | N | 2 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 16156 | 16562 | 1011479 | 2013-09-02 06:00 | 2013-09-02 11:35 | 335 | 11kV | 64619 | 602 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136917 2 fault operations 3 phase Overcurrent; Earth fault section isolated for repairs to sub 71391 & 72963 fdr restored | September | 2013 | 2014Q1 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-09-02 | N | 107.3405 | N | 2 | N | N | 1.1101 | 39.4971 | 47221.6593
[7 empty] | 16306 | 18065 | 1011996 | 2013-09-03 08:00 | 2013-09-03 08:30 | 30 | 11kV | 1800 | 60 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | LID 136926 3 phase isolation DOPS and Desk 2 received paperwork for job to proceed A Morton called Desk 3 advising the switching had been cancelled days before. Supply was restored as fast as possible. No protection operations. | September | 2013 | 2014Q1 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | Unknown | Not Veg | 2013-09-03 | N | 30 | N | 1 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 15571 | 9140 | 1012205 | 2013-09-04 13:24 | 2013-09-04 14:13 | 49 | 11kV | 5709 | 123 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.630 Mascot - Panel 33 tripped on Earth Fault, EFI UG cable fault between S6359 and S35659 see 1012367 1012370 1012371 | September | 2013 | 2014Q1 | 2014 | ZN630:PA33 | ZN630:PA33 | ZN00630/000033 | SYDNEY | UG | Not Veg | 2013-09-04 | N | 46.4146 | N | 4 | N | N | 1.1101 | 39.4971 | 4171.9688
[7 empty] | 15660 | 10546 | 1012156 | 2013-09-04 13:09 | 2013-09-04 14:40 | 91 | 11kV | 647 | 467 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 136946 SW 50139 OPENED AT 1309 & CLOSED AT 1310 FOR EMERGENCY ISOLATION FROM 11KV LINKS 2169.SEE SI- M0443. ## complete restoration 1440hrs ALSO SEE UPO/REPORT NO 136944. Excluded OMS REPORT NO 1012193 & 1012192. | September | 2013 | 2014Q1 | 2014 | 240:34852 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2013-09-04 | N | 1.3854 | N | 4 | N | N | 1.1101 | 39.4971 | 472.8085
[7 empty] | 15766 | 11764 | 1012330 | 2013-09-04 18:39 | 2013-09-04 20:15 | 96 | 11kV | 16032 | 167 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | S 48982 Wolli Creek Oswell - Interrupted by DOp. Section of Fdr from S 10143 to S 10577 to S 10004 to AB 31145 isolated. Vehicle ran into kiosk. ME: 1012571. ME GIS: 1012334. Withdrawn: 1012331. Georges River: 1012324, 1012330. | September | 2013 | 2014Q1 | 2014 | ZN10990:PA1 | ZN10998:PA3 | ZN10998/000003 | BAYSIDE | Unknown | Not Veg | 2013-09-04 | N | 96 | N | 4 | N | N | 1.1101 | 39.4971 | 11715.7127
[7 empty] | 15768 | 11778 | 1012366 | 2013-09-05 06:49 | 2013-09-05 07:17 | 28 | 11kV | 69496 | 2482 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn12570 Pa24 tripped on Basler relay 1.2.1=51A (overcurrent), trip LED Auto reclose relay - trip LED Signals: 11kv trip ABNORMAL: AB44523 is closed. LB45057 is open for further work. Cause: Tree/branch on OH mains adjacent to PT13664 the scenic hill outside 559 scenic rd, Avoca Beach. Branch cleared by DOp, mains not damaged See 1012756 exclude 366,8,72,4 | September | 2013 | 2014Q1 | 2014 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2013-09-05 | N | 28 | N | 2 | N | N | 1.1101 | 39.4971 | 50785.627
[7 empty] | 15136 | 4037 | 1012351 | 2013-09-04 23:02 | 2013-09-05 08:25 | 563 | 11kV | 1689 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136952 B phase DOLF : 20 Amp Also 33kv fdr 730 at AWABA tripped same time unplanned outage report # 136951 share same poles | September | 2013 | 2014Q1 | 2014 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2013-09-04 | N | 563 | N | 4 | N | N | 1.1101 | 39.4971 | 1234.2714
[7 empty] | 16334 | 18342 | 1012643 | 2013-09-05 15:06 | 2013-09-05 17:25 | 139 | 11kV | 163935 | 1687 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 398 Dulwich Hill - Pnl 15 - C phase IOC, Earth Fault, Field EFI's. Feeder fault from S 2583 to S 8972 tee S 5067. ME: 1012797. Rest Steps: 101279, 800. Withdrawn: 1012643. | September | 2013 | 2014Q1 | 2014 | ZN398:PA15 | ZN398:PA15 | ZN00398/000015 | INNER WEST | UG | Not Veg | 2013-09-05 | N | 97.1755 | N | 2 | N | N | 1.1101 | 39.4971 | 119798.8627
[7 empty] | 15789 | 11994 | 1012735 | 2013-09-06 02:38 | 2013-09-06 08:45 | 367 | 11kV | 52481 | 143 | HV | Overload LV Parallel | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | @PT2272 Norfolk Water A phase 31.5amp hdo blown Remarks: Fuse failure. Suspect overload. Planning to investigate. Suspect S46871 Dist 1 was in parallel at the time. | September | 2013 | 2014Q1 | 2014 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-09-06 | N | 367 | N | 4 | N | N | 1.1101 | 39.4971 | 38351.5669
[7 empty] | 14757 | 534 | 1012880 | 2013-09-06 12:33 | 2013-09-06 15:00 | 147 | 11kV | 44425 | 371 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 136968 2 fault operations C phase Earth fault Cablt fault at Abernethy Home sub 24391 | September | 2013 | 2014Q1 | 2014 | 504:48029 | 522:83124 | ZN00522/083124 | CESSNOCK | UG | Not Veg | 2013-09-06 | N | 119.7439 | N | 4 | N | N | 1.1101 | 39.4971 | 32464.4797
[7 empty] | 15480 | 8251 | 1012958 | 2013-09-06 15:53 | 2013-09-06 17:40 | 107 | 11kV | 214 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136970 Single phase DOLF : 10 Amp Excluded OMS 1012958 | September | 2013 | 2014Q1 | 2014 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | UG | Not Veg | 2013-09-06 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 15053 | 3276 | 1013001 | 2013-09-06 19:21 | 2013-09-06 20:15 | 53.9167 | 11kV | 2048.8333 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136972 A phase DOLF : 20 Amp Volts = 248V, Load 40A/ph Excluded OMS 1013004 | September | 2013 | 2014Q1 | 2014 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | UG | Not Veg | 2013-09-06 | N | 53.9167 | N | 4 | N | N | 1.1101 | 39.4971 | 1497.227
[7 empty] | 15552 | 8946 | 1013077 | 2013-09-07 12:50 | 2013-09-07 16:15 | 205 | 11kV | 7790 | 38 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | @PT14102 Roselands Tupentine: All phases interrupted @1545 to carry out repairs Centre Phase termination disc above HV drop out fuse has shattered. Termination insulators replaced on all phases. See 1013077 exclude 1013068 | September | 2013 | 2014Q1 | 2014 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2013-09-07 | N | 205 | N | 1 | N | N | 1.1101 | 39.4971 | 5692.7022
[7 empty] | 15165 | 4252 | 1013192 | 2013-09-08 19:00 | 2013-09-08 19:08 | 8 | 11kV | 1000 | 125 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 136979 3 phase ABS 74783 burning-up.Fdr dipped to try to close ABS fully. ABS unable to be closed successfully & left OPEN. Sw 74477 closed to restore supply to customers beyond faulty ABS. Excluded OMS# 1013192,3,4&5. | September | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-09-08 | N | 8 | N | 2 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 15761 | 11695 | 1013204 | 2013-09-08 20:35 | 2013-09-09 03:45 | 430 | 11kV | 51410 | 454 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 4 - Trip/reclose/trip, B & C phase OC. AB 35304 had caught fire and dropped one phase into the LV. ME: 1013326. Rest Step: 1013329. Withdrawn: 1013204, 05, 06, 07, 08, 12, 14. | September | 2013 | 2014Q1 | 2014 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | OH | Not Veg | 2013-09-08 | N | 113.2379 | N | 2 | N | N | 1.1101 | 39.4971 | 37568.9117
[7 empty] | 15036 | 3098 | 1013255 | 2013-09-09 09:00 | 2013-09-09 09:20 | 20 | 11kV | 20 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 136981 B phase DOLF : 10 Amp Excluded OMS 1013255 | September | 2013 | 2014Q1 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-09-09 | N | 20 | N | 3 | N | N | 1.1101 | 39.4971 | 14.6154
[7 empty] | 15669 | 10693 | 1013532 | 2013-09-09 15:16 | 2013-09-09 16:01 | 45 | 11kV | 34785 | 773 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.7481 Darling Harbour - Pnl.12 tripped on: EF Right EFIs: S8365 35288 4081 36188 CP512 UG cable fault from CP512 Harris William Henry to S8893 Pyrmont St No2 | September | 2013 | 2014Q1 | 2014 | ZN7481:PA12 | ZN7481:PA12 | ZN07481/000012 | SYDNEY | UG | Not Veg | 2013-09-09 | N | 45 | N | 3 | N | N | 1.1101 | 39.4971 | 25419.852
[7 empty] | 15255 | 5772 | 1013629 | 2013-09-09 21:44 | 2013-09-09 22:26 | 42 | 11kV | 9705 | 244 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.931 Darlinghurst Pnl.26 tripped on: Earth Fault EFI Field EFI @ S7948 only - EFI @ S8491 Appears defective UG cable fault between S7948 and S7519. see 1014620 1014621 | September | 2013 | 2014Q1 | 2014 | ZN931:PA26 | ZN931:PA26 | ZN00931/000026 | SYDNEY | UG | Not Veg | 2013-09-09 | N | 39.7746 | N | 3 | N | N | 1.1101 | 39.4971 | 7092.1278
[7 empty] | 16354 | 18615 | 1013632 | 2013-09-10 01:25 | 2013-09-10 02:23 | 58 | 11kV | 8968 | 181 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.931 Darlinghurst Pnl.26 tripped on Earth Fault Abnormal: S7948 (Sw A) OPEN - S6144 (Sw D) CLOSED - S7519 (Sw B) OPEN Cause not ascertained - suspect developing cable fault see 1014625 1014625 | September | 2013 | 2014Q1 | 2014 | ZN931:PA26 | ZN931:PA26 | ZN00931/000026 | SYDNEY | UG | Not Veg | 2013-09-10 | N | 49.547 | N | 10 | N | N | 1.1101 | 39.4971 | 6553.5499
[7 empty] | 14724 | 245 | 1013642 | 2013-09-10 08:30 | 2013-09-10 09:00 | 30 | 11kV | 450 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 136993 3 phase DOLF : 20 Amp excluded OMS 1013642 | September | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2013-09-10 | N | 30 | N | 10 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 15793 | 12037 | 1013815 | 2013-09-10 11:23 | 2013-09-10 12:54 | 91 | 11kV | 14924 | 164 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Ex Panel No.4L "Sub 47361 Galston Aux No.1" feeder from Zn35370 Galston. Recloser 428 Bayfield - Tripped, reclosed and locked out. Cause not Ascertained. OMS No. 1013815, 1013977 | September | 2013 | 2014Q1 | 2014 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-09-10 | N | 91 | N | 10 | N | N | 1.1101 | 39.4971 | 10906.019
[7 empty] | 14787 | 836 | 1013747 | 2013-09-10 10:23 | 2013-09-10 13:25 | 182 | 11kV | 4456 | 118 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 136990 2 fault operations A phase Overcurrent, Earth fault | September | 2013 | 2014Q1 | 2014 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2013-09-10 | N | 37.7627 | N | 10 | N | N | 1.1101 | 39.4971 | 3256.3134
[7 empty] | 15782 | 11929 | 1013846 | 2013-09-10 11:12 | 2013-09-10 13:35 | 143 | 11kV | 73962 | 1134 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At ZN1673 Turramurra Panel 18 Tripped on B and C phase Timed O/C Feeder Patrolled By DOp - LV mains found down beyond CP1840 See OMS 1014231 1014233 | September | 2013 | 2014Q1 | 2014 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Not Veg | 2013-09-10 | N | 65.2222 | N | 10 | N | N | 1.1101 | 39.4971 | 54049.2481
[7 empty] | 15828 | 12437 | 1013689 | 2013-09-10 09:17 | 2013-09-10 15:40 | 383 | 11kV | 102880 | 1265 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 136986 2 fault operations A phase Earth fault Tree on mains at sub 43672 pole down Excluded oms 1013689, 1013710 & 1013734 | September | 2013 | 2014Q1 | 2014 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2013-09-10 | N | 81.3281 | N | 10 | N | N | 1.1101 | 39.4971 | 75181.6696
[7 empty] | 16425 | 19511 | 1013890 | 2013-09-10 13:27 | 2013-09-10 17:35 | 248 | 11kV | 104351 | 1627 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | ZN 9245 Engadine - Pnl 4 - A & C phase OC and IOC, timing, lockout, EFIs. Broken King bolt on a HV crossarm caused wire to clash together. Crossarm repaired 10/9/13, 17:30. S 46983 Dist 1 interrupted for safety. ME: 1014217. Rest Steps: 1014218, 20. Withdrawn: 1014004. | September | 2013 | 2014Q1 | 2014 | ZN9245:PA4 | ZN9245:PA19 | ZN09245/000019 | SUTHERLAND | OH | Not Veg | 2013-09-10 | N | 64.1371 | N | 10 | N | N | 1.1101 | 39.4971 | 76256.633
[7 empty] | 15877 | 12904 | 1014068 | 2013-09-10 16:51 | 2013-09-10 18:10 | 79 | 11kV | 1738 | 22 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12610 Long Jetty section of Pa20 @PT50360 Bellevue Tumbi 63K HDO footpath side fuse failed due to fatigue See 1014279 exclude 1014068 | September | 2013 | 2014Q1 | 2014 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2013-09-10 | N | 79 | N | 10 | N | N | 1.1101 | 39.4971 | 1270.0791
[7 empty] | 14769 | 588 | 1014066 | 2013-09-10 16:47 | 2013-09-10 19:20 | 153 | 11kV | 10404 | 68 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At S6287 Church Addis TX1 A phase HV fuse Operated Cause: Tx1 suspected failure. See OMS 1018557 1014066 | September | 2013 | 2014Q1 | 2014 | ZN4545:PA17 | ZN4545:PA2 | ZN04545/000002 | RYDE | UG | Not Veg | 2013-09-10 | N | 153 | N | 10 | N | N | 1.1101 | 39.4971 | 7602.9363
[7 empty] | 16000 | 14622 | 1013930 | 2013-09-10 14:03 | 2013-09-10 21:30 | 447 | 11kV | 91856 | 663 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Recloser 46116 Lancaster Andrew Tripped and Reclosed pn OC and IOC Cause: Section of Panel 25 Meadowbank Park See OMS 1013930 1015784 1015786 1015785 Tree branch on OH mains in Winbourne St | September | 2013 | 2014Q1 | 2014 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Veg | 2013-09-10 | N | 138.546 | N | 10 | N | N | 1.1101 | 39.4971 | 67125.6555
[7 empty] | 16361 | 18669 | 1014728 | 2013-09-11 01:22 | 2013-09-11 11:40 | 618 | 11kV | 25428 | 83 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At R.24722 Forest Crozier tripped on SEF. Section of panel 10 'Forest Way Dawes' 11kV feeder. Feeder patrolled, cause not ascertained. OMS No: 1014728, 1014158, 1014162. | September | 2013 | 2014Q1 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2013-09-11 | N | 306.3614 | N | 4 | N | N | 1.1101 | 39.4971 | 18582.0324
[7 empty] | 14993 | 2790 | 1014356 | 2013-09-11 12:00 | 2013-09-11 14:00 | 120 | 11kV | 1080 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137014 B phase sub isolated to repair broken dropper to tx at sub 51276. | September | 2013 | 2014Q1 | 2014 | 523:33501 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-09-11 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 16004 | 14653 | 1014225 | 2013-09-11 08:49 | 2013-09-11 15:05 | 376 | 11kV | 67092 | 374 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 @IR50630 Yarramalong tripped, reclosed, tripped and locked out Relays: A&C phase overcurrent Abnormal: IR48813 Yarramalong Boyds 3.7 and T/Cat 48814 Yarramalong Boyds 3.8 bypassed Cause: Tree/branch on OH Mains. Large tree branch on mains near PT13249 Yarramalong Bumble 1.5 See 1014649,51,2,3 Exclude 1014225,35 | September | 2013 | 2014Q1 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-09-11 | N | 179.3904 | N | 4 | N | N | 1.1101 | 39.4971 | 49028.8547
[7 empty] | 15021 | 2989 | 1014559 | 2013-09-11 18:56 | 2013-09-11 21:40 | 164 | 11kV | 16564 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale section of Pa26R between LB44761 to RE44947 interrupted by DOp for safety to allow linesman to repair CCT pin insulators and remove tree in close proximity Tree branch dislodged HV CCT SEe 1014671 exclude 1014559 | September | 2013 | 2014Q1 | 2014 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2013-09-11 | N | 164 | N | 4 | N | N | 1.1101 | 39.4971 | 12104.4826
[7 empty] | 15509 | 8569 | 1014589 | 2013-09-12 01:59 | 2013-09-12 04:00 | 121 | 11kV | 29285 | 341 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 1648 Enfield - Pnl 21 - Translay, EFI, Field EFI. 11kV UG cable fault from S 6831 to S 962 tee S 3400. S 3400 is a non paralleling sub that was reinstated by the use of their own on site generator. ME: 1014639. Rest Steps: 1014640, 1. Withdrawn: 1014589, 92. | September | 2013 | 2014Q1 | 2014 | ZN1648:PA21 | ZN4853:PA12 | ZN04853/000012 | STRATHFIELD | UG | Not Veg | 2013-09-12 | N | 85.8798 | N | 3 | N | N | 1.1101 | 39.4971 | 21400.6142
[7 empty] | 15603 | 9681 | 1014614 | 2013-09-12 07:44 | 2013-09-12 11:30 | 226 | 11kV | 5508 | 49 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137017 ISOLATED FDR TO OPERATE LIVE LINE CLAMP ON STEEL MAINS AT SUB 50837 Excluded OMS 1014614 & 1014618 | September | 2013 | 2014Q1 | 2014 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2013-09-12 | N | 112.4082 | N | 3 | N | N | 1.1101 | 39.4971 | 4025.0839
[7 empty] | 16254 | 17536 | 1014764 | 2013-09-12 12:43 | 2013-09-12 13:46 | 63 | 11kV | 34302 | 556 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.7900 Campbell St - Pnl.9 tripped on Earth Fault, EFI Field EFIs: S8554, S3381 UG cable fault between S3381 and S7525. see 1015623 1015624 1015625 | September | 2013 | 2014Q1 | 2014 | ZN7900:PA9 | ZN7900:PA9 | ZN07900/000009 | SYDNEY | UG | Not Veg | 2013-09-12 | N | 61.6942 | N | 3 | N | N | 1.1101 | 39.4971 | 25066.8899
[7 empty] | 15417 | 7647 | 1015114 | 2013-09-13 12:16 | 2013-09-13 14:50 | 154 | 11kV | 52476 | 539 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 5 - Earth fault, Field EFIs, Fault check. UG cable struck by contractors in Harp St Nr Alfred St. Section of feeder from S 91717 to S3326 tee S828 to S2894. ME: 1015641. Rest Steps: 1015642, 5. Withdrawn: 1015114, 20. | September | 2013 | 2014Q1 | 2014 | ZN690:PA5 | ZN690:PA5 | ZN00690/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-09-13 | N | 97.3581 | N | 1 | N | N | 1.1101 | 39.4971 | 38347.913
[7 empty] | 15280 | 6235 | 1015307 | 2013-09-14 02:40 | 2013-09-14 06:15 | 215 | 11kV | 43673 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137041 6 fault operations A & B phase Overcurrent Removed tree branch pole GW-11020 Excluded OMS 1015307 | September | 2013 | 2014Q1 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2013-09-14 | N | 137.7697 | N | 6 | N | N | 1.1101 | 39.4971 | 31914.9403
[7 empty] | 14799 | 943 | 1015344 | 2013-09-14 07:09 | 2013-09-14 08:34 | 85.4833 | 11kV | 1709.6667 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 137044 B phase DOLF : 40 Amp | September | 2013 | 2014Q1 | 2014 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2013-09-14 | N | 85.4833 | N | 6 | N | N | 1.1101 | 39.4971 | 1249.374
[7 empty] | 15084 | 3534 | 1015303 | 2013-09-14 01:57 | 2013-09-14 09:50 | 473 | 11kV | 17539 | 76 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Unselected | N | Zn12600 Lisarow 11kv fdr Pa5 "Pacific Parsons" trippe on Earht Fault, EFI Cause lightning. surge arrestor blown UGOH to S14059 See 1015674,5 exclude 1015303 | September | 2013 | 2014Q1 | 2014 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | OH | Not Veg | 2013-09-14 | N | 230.7763 | N | 6 | N | N | 1.1101 | 39.4971 | 12816.9839
[7 empty] | 14802 | 952 | 1015396 | 2013-09-14 11:11 | 2013-09-14 11:20 | 9 | 11kV | 648 | 72 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa13 @RE44547 Defective. Will not close fully, requires maintenance PT14523 Interrupted for safety to close Air Break Switch. See 1015684 exclude 1015396,7,8 | September | 2013 | 2014Q1 | 2014 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2013-09-14 | N | 9 | N | 6 | N | N | 1.1101 | 39.4971 | 473.5393
[7 empty] | 16448 | 19925 | 1016547 | 2013-09-14 00:35 | 2013-09-14 12:20 | 705 | 11kV | 239072 | 897 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 137048 4 fault operations Earth fault Faulty TX due to lightening strike. Delay in restoration also created by CB tripping free (3X) during fault restotation attempts. Emailled to MBrook Tech services DQ Excluded OMS 1015300 | September | 2013 | 2014Q1 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | UG | Not Veg | 2013-09-14 | N | 266.524 | N | 6 | N | N | 1.1101 | 39.4971 | 174706.7662
[7 empty] | 16374 | 18780 | 1015371 | 2013-09-14 08:41 | 2013-09-14 14:00 | 319 | 11kV | 638 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137051 A & C phase DOLF : 10 Amp Replaced Line (Lightning) Arresters Excluded OMS 1015371 | September | 2013 | 2014Q1 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-09-14 | N | 319 | N | 6 | N | N | 1.1101 | 39.4971 | 466.2316
[7 empty] | 15068 | 3412 | 1015504 | 2013-09-15 04:06 | 2013-09-15 06:40 | 154 | 11kV | 11550 | 75 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12640 Umina section of Pa8 @PT13705 Heath Araluen cnetre phase HVDO found broken See 1015696 exclude 1015504,5,9 | September | 2013 | 2014Q1 | 2014 | ZN12640:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2013-09-15 | N | 154 | N | 4 | N | N | 1.1101 | 39.4971 | 8440.3993
[7 empty] | 15969 | 14104 | 1015516 | 2013-09-15 08:36 | 2013-09-15 10:00 | 84 | 11kV | 588 | 7 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137058 B phase DOLF : 10 Amp B PHASE LINE FUSE BLOWN AS WELL AS SAME PHASE ON S51507. BIRD FOUND ON TX. Excluded OMS 1015516 | September | 2013 | 2014Q1 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-09-15 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 429.6931
[7 empty] | 15639 | 10176 | 1015571 | 2013-09-15 16:03 | 2013-09-15 16:58 | 55 | 11kV | 155705 | 2831 | HV | Arcing | Equipment Failure | DC PT | Unplanned | Unselected | N | At Zn80 Chatswood 11kV feeder tripped on Relays: B and C phase Timed O/C Cause: Appears a flashover occurred at PT628 Ronald Osbourne. 4 Witnesses pinpointed the problem, No Bird, possum or tree branch found. Feeder restored sucessfully No auto close on this feeder. See OMS 1015571 1015574 1015575 1015576 1015571 | September | 2013 | 2014Q1 | 2014 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Not Veg | 2013-09-15 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 113784.6215
[7 empty] | 15664 | 10616 | 1015582 | 2013-09-15 16:53 | 2013-09-15 17:23 | 30 | 11kV | 51390 | 1713 | HV | Animal Bird | Animal | Bond | Unplanned | Unselected | N | At S.2196 Milperra Panel 25 The Turvey River Fdr. Tripped on Reyrolle Electronic Relay 50 TAB. A and B ph IOC. 11kv Trip alarm Remarks: Magpie flew onto 11kv corner pole bonding. No auto reclose on this feeder. pole cnr Bishop and Mackenzie | September | 2013 | 2014Q1 | 2014 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-09-15 | N | 30 | N | 4 | N | N | 1.1101 | 39.4971 | 37554.2963
[7 empty] | 15409 | 7508 | 1015608 | 2013-09-16 02:31 | 2013-09-16 04:57 | 146 | 11kV | 42996 | 312 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 136060 2 fault operations 3 phase Instantaneous Earth fault Cessnock on call attended no cause found however full patrol in daylight requied. DQ Excluded oms1015608 | September | 2013 | 2014Q1 | 2014 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2013-09-16 | N | 137.8077 | N | 9 | N | N | 1.1101 | 39.4971 | 31420.2086
[7 empty] | 15613 | 9782 | 1015618 | 2013-09-16 07:12 | 2013-09-16 10:00 | 168 | 11kV | 1176 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137064 B phase DOLF: 10 Amp 247V A - 42A, B - 8A, C - 6A Excluded oms 1015618 | September | 2013 | 2014Q1 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | UG | Not Veg | 2013-09-16 | N | 168 | N | 9 | N | N | 1.1101 | 39.4971 | 859.3861
[7 empty] | 15914 | 13278 | 1016002 | 2013-09-16 15:30 | 2013-09-16 16:10 | 40 | 11kV | 2800 | 70 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 137067 C phase CAr hit pole. Wire Off Pin at BI-40513 No Protection operation Excluded OMS # 1016002 | September | 2013 | 2014Q1 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-09-16 | N | 40 | N | 9 | N | N | 1.1101 | 39.4971 | 2046.1574
[7 empty] | 15110 | 3852 | 1015926 | 2013-09-16 13:44 | 2013-09-16 16:15 | 151 | 11kV | 88794 | 1156 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN180 Mosman Panel 23 'S1899 Harbour Mosman' tripped on C phase timed O/C, EFI, Fault Check. Field EFI: S6694. 11kV UG Fault from S6694 Brady Ourimbah No.1 to S2781 Spit Bickell to S2415 Killarney Mitchell Tee S3089 Bay Bickell. OMS Numbers: 1015926, 1016257, 1016259. | September | 2013 | 2014Q1 | 2014 | ZN180:PA23 | ZN180:PA23 | ZN00180/000023 | MOSMAN | UG | Not Veg | 2013-09-16 | N | 76.8114 | N | 9 | N | N | 1.1101 | 39.4971 | 64888.0362
[7 empty] | 16083 | 15799 | 1016088 | 2013-09-16 18:42 | 2013-09-16 19:40 | 58.25 | 11kV | 24115.5 | 414 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Light | N | At Sub 35800 Bankstown 11kv Fdr Pnl 18 'S47787 Gibson Atkinson' tripped on: IOC Field EFI's Nil Remarks: tree/branch on oH mains. o/s 2 Enterprise Ave Padstow | September | 2013 | 2014Q1 | 2014 | ZN35800:PA18 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-09-16 | N | 58.25 | N | 9 | N | N | 1.1101 | 39.4971 | 17622.8961
[7 empty] | 15441 | 7880 | 1016107 | 2013-09-16 19:42 | 2013-09-16 20:40 | 58.75 | 11kV | 23617.5 | 402 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 137070 3 fault operations B & C phase Overcurrent Branch fell through mains 1 span from recloser. 2100A phase to phase fault. | September | 2013 | 2014Q1 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2013-09-16 | N | 58.75 | N | 9 | N | N | 1.1101 | 39.4971 | 17258.9724
[7 empty] | 15861 | 12771 | 1016116 | 2013-09-16 20:15 | 2013-09-16 22:45 | 150 | 11kV | 150 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | 11kV/250V Fong sub 52830 interupted to enable repairs Refer to LID 137068 Austar Kitchener RAGCB not back on until x arm at Pole FT-60035 repaired - refer to OMS 1016331 Excluded OMS #1016116 | September | 2013 | 2014Q1 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-09-16 | N | 150 | N | 9 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 14702 | 46 | 1016160 | 2013-09-16 22:29 | 2013-09-17 00:21 | 111.7 | 11kV | 145433.4 | 1302 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At S345 Hornsby Panel 21 tripped reclosed tripped and locked out on Relays: C phase O/C , Reclose timer and lockout Cause: Tree branch on OHGO/S 49 Manor Rd. Se eOMS 1016160 1016162 1016171 | September | 2013 | 2014Q1 | 2014 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2013-09-16 | N | 111.7 | N | 9 | N | N | 1.1101 | 39.4971 | 106278.4392
[7 empty] | 15476 | 8188 | 1016753 | 2013-09-17 10:38 | 2013-09-17 12:25 | 107 | 11kV | 642 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 137081 B phase DOLF : 40 Amp LINE FUSE BLOWN. REPORTED TO DEPOT. NO OMS REPORT. | September | 2013 | 2014Q1 | 2014 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2013-09-17 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 469.1547
[7 empty] | 15976 | 14233 | 1016506 | 2013-09-17 12:05 | 2013-09-17 13:40 | 95 | 11kV | 1615 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 from AB41276 to LK40077 cause: LV mains dropped and required retensioing near AB4393 HV taken out for sefty See 1016750 exclude 1016506 | September | 2013 | 2014Q1 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-09-17 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 1180.1944
[7 empty] | 15806 | 12156 | 1016733 | 2013-09-17 14:30 | 2013-09-17 16:20 | 110 | 11kV | 770 | 7 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 137082 Isolation for emergency repairs Broken strands on conductor near pole JP-95063. | September | 2013 | 2014Q1 | 2014 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2013-09-17 | N | 110 | N | 4 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 15450 | 7938 | 1016177 | 2013-09-16 23:39 | 2013-09-17 20:50 | 1271 | 11kV | 155683 | 689 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | CP3282 Alberta Ave tripped on Panel 11 Tree branch brought OH down (HV and LV) See OMS 1020488 1020486 1016210 1016177 | September | 2013 | 2014Q1 | 2014 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2013-09-16 | N | 225.955 | N | 9 | N | N | 1.1101 | 39.4971 | 113768.5445
[7 empty] | 16442 | 19890 | 1016665 | 2013-09-17 20:22 | 2013-09-17 21:30 | 68.2167 | 11kV | 6617.0167 | 97 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex ZN12620 Noraville section of Pa8 @PT11147 Noella Natuna 31.5k HDO operated from fuse fatigue See 1016663 exclude 1016665 | September | 2013 | 2014Q1 | 2014 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2013-09-17 | N | 68.2167 | N | 4 | N | N | 1.1101 | 39.4971 | 4835.5206
[7 empty] | 15620 | 9949 | 1016675 | 2013-09-18 02:20 | 2013-09-18 03:47 | 86.8667 | 11kV | 121179 | 1395 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN36300 Balgowlah North Panel 17 'S46665 Balgowlah North AUX No 2' feeder tripped on A & A phase IOC, EFI, Fault Check. Field EFIs operated at S46665, S48110, S62663, S46775, S16797, CP20901, S17039, S16320. S15107. Feeder patrolled by DOp. Cause not ascertained. | September | 2013 | 2014Q1 | 2014 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Veg | 2013-09-18 | N | 86.8667 | N | 3 | N | N | 1.1101 | 39.4971 | 88554.039
[7 empty] | 14751 | 507 | 1016679 | 2013-09-18 06:20 | 2013-09-18 09:45 | 204.9667 | 11kV | 2254.6333 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137090 B & C phase DOLF : 10 Amp Found 10A fuses in-service. Replaced with 5A fuses as per system diagram. CC1: 22-"Refer to SOp" | September | 2013 | 2014Q1 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Veg | 2013-09-18 | N | 204.9667 | N | 3 | N | N | 1.1101 | 39.4971 | 1647.6195
[7 empty] | 14730 | 299 | 1017034 | 2013-09-18 15:53 | 2013-09-18 20:50 | 297 | 11kV | 891 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137098 11Kv Dropper broken at top of DOLF. No protection operation Excluded oms # 1017034 | September | 2013 | 2014Q1 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2013-09-18 | N | 297 | N | 3 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 14720 | 227 | 1017111 | 2013-09-19 06:07 | 2013-09-19 09:26 | 199 | 11kV | 14692 | 83 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn15005 Belrose section of Panel 10 fro Rec 24722 Forest Crozier tripped on: SEL trip and lock out, no SCADA control. Cause not ascertained. Reference OMS Numbers: 1017561, 1017567, 1017569, 1017572, 1017573, 1017111, 1017178 | September | 2013 | 2014Q1 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2013-09-19 | N | 177.012 | N | 4 | N | N | 1.1101 | 39.4971 | 10736.4803
[7 empty] | 15233 | 5317 | 1017451 | 2013-09-19 17:17 | 2013-09-19 17:50 | 33 | 11kV | 528 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137116 B phase Live line connector cable failed at joint near DOLF. Open circuit only no protection operation. Excluded OMS # 1017451. | September | 2013 | 2014Q1 | 2014 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2013-09-19 | N | 33 | N | 4 | N | N | 1.1101 | 39.4971 | 385.8468
[7 empty] | 15712 | 11063 | 1017487 | 2013-09-19 20:09 | 2013-09-19 21:12 | 63 | 11kV | 40549 | 659 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.35600 Kingsford Pnl.12L tripped on: Earth Fault, 12L frame leakage Field EFIs: S.61470 S2917 S36076 S36064 UG cable fault between S36064 (Sw B ) to S4155 (Sw A) to S3040 (Sw B ) to S4622 (Sw B) see 1017521 1017522 1017523 | September | 2013 | 2014Q1 | 2014 | ZN35600:PA12 | ZN35600:PA12 | ZN35600/000012 | RANDWICK | UG | Not Veg | 2013-09-19 | N | 61.5311 | N | 4 | N | N | 1.1101 | 39.4971 | 29632.0132
[7 empty] | 15811 | 12238 | 1017459 | 2013-09-19 17:24 | 2013-09-19 21:40 | 255.9 | 11kV | 13562.7 | 53 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137115 C phase DOLF : 31 Amp LV OHM came down at PT. Dropper to Tx damaged and repaired. Volts 242 Amps 81-48-85 | September | 2013 | 2014Q1 | 2014 | 239:82133 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Not Veg | 2013-09-19 | N | 255.9 | N | 4 | N | N | 1.1101 | 39.4971 | 9911.2211
[7 empty] | 15108 | 3819 | 1017618 | 2013-09-20 11:08 | 2013-09-20 12:12 | 64 | 11kV | 5568 | 87 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 137121 B Phase B phase 11kV link 15345 broke when operating for SI 35041. Customers interrupted to replace link. Excluded OMS No. 1017618 | September | 2013 | 2014Q1 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2013-09-20 | N | 64 | N | 6 | N | N | 1.1101 | 39.4971 | 4068.9302
[7 empty] | 15360 | 6911 | 1017615 | 2013-09-20 10:57 | 2013-09-20 12:55 | 118 | 11kV | 77644 | 658 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2568 St Peters Pnl.22 tripped on Earth Fault, Fault Check EFI Field EFIs: S93, S5200 S1446 UG cable fault between S1445 Sw B and S2091 Sw A | September | 2013 | 2014Q1 | 2014 | ZN2568:PA22 | ZN2568:PA22 | ZN02568/000022 | INNER WEST | UG | Not Veg | 2013-09-20 | N | 118 | N | 6 | N | N | 1.1101 | 39.4971 | 56739.9451
[7 empty] | 14975 | 2599 | 1017676 | 2013-09-20 12:44 | 2013-09-20 14:25 | 101 | 11kV | 303 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137124 B phase Faulty live line clamp lead at sub. Excluded OMS 1017676 | September | 2013 | 2014Q1 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-09-20 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 221.4235
[7 empty] | 15837 | 12499 | 1017663 | 2013-09-20 12:06 | 2013-09-20 15:00 | 174 | 11kV | 2262 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 137125 Single phase DOLF : 20 Amp Both fuses blew. Conductor strand worked loose and short circuited to the adjoining phase at ploe 8H-80079. Excluded OMS # 1017663. | September | 2013 | 2014Q1 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-09-20 | N | 174 | N | 6 | N | N | 1.1101 | 39.4971 | 1653.0029
[7 empty] | 15982 | 14304 | 1017814 | 2013-09-20 17:49 | 2013-09-20 19:52 | 123 | 11kV | 130251 | 1163 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 9900 Menai - Pnl 8 - B phase EF, EFI, LO, timer, Field EFIs. UG fault between S 9341 and S 9174. Suspect tree tripped feeder initially near the river crossing and that initiated a secondary fault on the underground cable. All EFIs operated, the lines showed up clear, but the UG fault occurred halfway along the feeder. ME: 1018150 Rest Steps: 1018152, 3. Withdrawn: 1017814, 6. | September | 2013 | 2014Q1 | 2014 | ZN9900:PA8 | ZN9900:PA8 | ZN09900/000008 | SUTHERLAND | OH | Veg | 2013-09-20 | N | 111.9957 | N | 6 | N | N | 1.1101 | 39.4971 | 95183.589
[7 empty] | 15964 | 14010 | 1017827 | 2013-09-20 18:53 | 2013-09-20 21:15 | 142 | 11kV | 10934 | 77 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At PT155 Dernancourt Flanders road side HV fuse blown, 1.5K asea brown boveri. Batch no.3126 Remarks: vehicle hit pole. | September | 2013 | 2014Q1 | 2014 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-09-20 | N | 142 | N | 6 | N | N | 1.1101 | 39.4971 | 7990.2447
[7 empty] | 15541 | 8875 | 1017870 | 2013-09-21 09:13 | 2013-09-21 10:33 | 80 | 11kV | 25360 | 317 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137130 3 phase Overcurrent, Earth fault Removed Branch. Moonan Close pole GW-50256 | September | 2013 | 2014Q1 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2013-09-21 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 18532.34
[7 empty] | 15180 | 4420 | 1017931 | 2013-09-21 14:50 | 2013-09-21 15:55 | 65 | 11kV | 1040 | 16 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137132 B phase Incoming 11kV OH conductor fell away and dropped onto the top of trees at sub 51480. Supply was interrupted to this and surrounding subs to carry out repairs and make safe. No protection operated. Excluded OMS # 1017931. | September | 2013 | 2014Q1 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2013-09-21 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 15191 | 4487 | 1017920 | 2013-09-21 13:43 | 2013-09-21 17:33 | 229.95 | 11kV | 1097.55 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 137134 B phase DOLF : 16 Amp Operator said fuse showed signs of corrosion. CASS # 879076. Excluded OMS # 1017920. | September | 2013 | 2014Q1 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2013-09-21 | N | 219.51 | N | 3 | N | N | 1.1101 | 39.4971 | 802.0572
[7 empty] | 14900 | 1945 | 1018001 | 2013-09-22 09:26 | 2013-09-22 10:09 | 43 | 11kV | 73659 | 1713 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S2196 Milperra Panel #25 "Turvey River" fdr tripped on A+B IOC 11kv trip Remarks: animals/birds. Corner Bishop & Mackenzie St Revesby Magpie flew into high Related jobs: #1018001, 118002, 1018127 | September | 2013 | 2014Q1 | 2014 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-09-22 | N | 43 | N | 2 | N | N | 1.1101 | 39.4971 | 53827.8246
[7 empty] | 15950 | 13692 | 1018072 | 2013-09-22 19:58 | 2013-09-22 21:10 | 72 | 11kV | 8496 | 118 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | Adnormal switching for duration: SW D closed at S15133 Manly Swimming pools. Panel 11 open at zone and under A/P. Main event at ZN15009 Manly Zone panel 7 'Birkley Raglan' tripped on reclosed on. Tripped on Relays: Overcurrent B phase, lock out relay, timing relay, EFI, fault check and Tx3 fault check relay. - refer to OMS 1018640 for T&R on Panel 7 Interruption cause by possum on PT16409 Herbert Francis. OMS Numbers: 1018640, 1018656 1018072, 1018073, 1018075, 1018076. | September | 2013 | 2014Q1 | 2014 | ZN15009:PA7 | ZN15009:PA7 | ZN15009/000007 | NORTHERN BEACHES | OH | Not Veg | 2013-09-22 | N | 72 | N | 2 | N | N | 1.1101 | 39.4971 | 6208.6262
[7 empty] | 15479 | 8249 | 1018103 | 2013-09-23 08:01 | 2013-09-23 10:10 | 129 | 11kV | 7716 | 129 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 137139 Motor Vehicle Accident Excluded OMS 1018103 | September | 2013 | 2014Q1 | 2014 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2013-09-23 | N | 59.814 | N | 4 | N | N | 1.1101 | 39.4971 | 5638.6252
[7 empty] | 15268 | 5930 | 1018598 | 2013-09-23 09:02 | 2013-09-23 14:36 | 334 | 11kV | 120546 | 371 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 137141 2 fault operations 3 phase Overcurrent CAR HIT POLE IQ-41558, PATTERSON RD WOODVILLE. Excluded OMS 1018146 | September | 2013 | 2014Q1 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2013-09-23 | N | 324.9218 | N | 4 | N | N | 1.1101 | 39.4971 | 88091.4613
[7 empty] | 14941 | 2188 | 1018385 | 2013-09-23 13:53 | 2013-09-23 15:30 | 97 | 11kV | 1066.6167 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | @S4100 Beresford Coventry A & B Phase 90A HV Fuse operated. EX panel 41 'S1616 Manson Rd Etc" feeder from S2835 Burwood Remarks: Cause not ascertained. | September | 2013 | 2014Q1 | 2014 | ZN2835:PA41 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2013-09-23 | N | 96.9652 | N | 4 | N | N | 1.1101 | 39.4971 | 779.452
[7 empty] | 15589 | 9413 | 1018424 | 2013-09-23 15:15 | 2013-09-23 19:05 | 230 | 11kV | 9386 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa2 @RE44945 Lower Mangrove has tripped and locked out. Relays: A & C phase OC See 1018650,2,3 GIS 1018448 Exclude 1018424 | September | 2013 | 2014Q1 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2013-09-23 | N | 173.8148 | N | 4 | N | N | 1.1101 | 39.4971 | 6859.012
[7 empty] | 15610 | 9736 | 1018528 | 2013-09-24 06:49 | 2013-09-24 07:45 | 56 | 11kV | 336 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa5 HDO found blown. Could not find a cause. No readings taken as it was a termite pole See 1018912 exclude 1018528 | September | 2013 | 2014Q1 | 2014 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2013-09-24 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 245.5389
[7 empty] | 15973 | 14177 | 1018526 | 2013-09-24 06:28 | 2013-09-24 16:00 | 572 | 11kV | 802 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 137149 B phase HV fuse : 80 Amp Faulty trans Excluded OMS# 1018526. | September | 2013 | 2014Q1 | 2014 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | UG | Not Veg | 2013-09-24 | N | 267.3333 | N | 4 | N | N | 1.1101 | 39.4971 | 586.0779
[7 empty] | 16147 | 16466 | 1018802 | 2013-09-24 15:47 | 2013-09-24 16:40 | 53 | 11kV | 1113 | 21 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2635 Epping Pa64 feeder tripped on Relays Basler - IOC + Earth Fault 11kV feeder fault fro m Zn2635 Epping Pa64 to S35789 Culloden Taranto. | September | 2013 | 2014Q1 | 2014 | ZN2635:PA64 | ZN2635:PA64 | ZN02635/000064 | RYDE | UG | Not Veg | 2013-09-24 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 813.3476
[7 empty] | 16201 | 17080 | 1018791 | 2013-09-24 15:37 | 2013-09-24 18:10 | 153 | 11kV | 1683 | 11 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S.6371 Beauchamp Mcpherson - 90Amp "A" phase fuse blown on Transformer #2 Transformer failure - repeated outages | September | 2013 | 2014Q1 | 2014 | ZN1788:PA11 | ZN35700:PA10 | ZN35700/000010 | BAYSIDE | UG | Not Veg | 2013-09-24 | N | 153 | N | 4 | N | N | 1.1101 | 39.4971 | 1229.8868
[7 empty] | 14885 | 1776 | 1018877 | 2013-09-25 01:37 | 2013-09-25 04:15 | 158 | 11kV | 3318 | 21 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | At PT1297 Charltons Bay 31.5A HVDO fuse blown Cause: Tx at PT1297 defective. also refer to 1018877 | September | 2013 | 2014Q1 | 2014 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2013-09-25 | N | 158 | N | 8 | N | N | 1.1101 | 39.4971 | 2424.6965
[7 empty] | 15886 | 13001 | 1018943 | 2013-09-25 08:30 | 2013-09-25 09:32 | 62 | 11kV | 4898 | 79 | HV | Staff Other | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | LID 137157 Refer Disconect and Reconnect Request 25934, switching did start but after a few customer calls it was confirned no customers beyond Sw 47688 were notified of the interruption. Supply was restored to customers as soon as possible. No protection operations. | September | 2013 | 2014Q1 | 2014 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | Unknown | Not Veg | 2013-09-25 | N | 62 | N | 8 | N | N | 1.1101 | 39.4971 | 3579.3139
[7 empty] | 14824 | 1162 | 1018900 | 2013-09-25 07:24 | 2013-09-25 10:15 | 171 | 11kV | 684 | 4 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137161 B phase DOLF : 10 Amp POSSUM ON TX TANK Excluded OMS 1018904 | September | 2013 | 2014Q1 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-09-25 | N | 171 | N | 8 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 16382 | 18888 | 1019340 | 2013-09-25 15:02 | 2013-09-25 15:06 | 4 | 11kV | 868 | 217 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN180 Mosman panel 23 'Brady Ourimbah, etc.' tripped on: - A & C phase IOC, A & C phase timed, EFI and Fault Check. Section of feeder between S6694 Brady Ourimbah No1, S2781 Spit Bickell, S2415 Killarney Mitchell and tee S3089 Bay Bickell defect and OOS. After reconnect #323831 A/P signed off and cancelled. DOp closed SW/B at S6694 Brady Ourimbah No1 and Panel 23 tripped. New tester and jointer issued. | September | 2013 | 2014Q1 | 2014 | ZN180:PA23 | ZN180:PA23 | ZN00180/000023 | MOSMAN | UG | Not Veg | 2013-09-25 | N | 4 | N | 8 | N | N | 1.1101 | 39.4971 | 634.3088
[7 empty] | 15732 | 11391 | 1019186 | 2013-09-25 15:37 | 2013-09-25 16:49 | 72 | 11kV | 83196 | 1540 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.188 Zetland Pnl.41 tripped on: Timed O/C, EFI , Fault Check Field EFIs: S8838 & S35352 UG cable fault from S35352 to S1321 (Sw B) to S1321 (Sw C) See 1019325 1019326 GIS: 1019327 1019197 | September | 2013 | 2014Q1 | 2014 | ZN188:PA41 | ZN2602:PA42 | ZN02602/000042 | RANDWICK | UG | Not Veg | 2013-09-25 | N | 54.0234 | N | 8 | N | N | 1.1101 | 39.4971 | 60797.1829
[7 empty] | 15197 | 4579 | 1019357 | 2013-09-25 14:30 | 2013-09-25 18:30 | 240 | 11kV | 720 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 137169 Conductor on crossarm | September | 2013 | 2014Q1 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-09-25 | N | 240 | N | 8 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 15169 | 4280 | 1019261 | 2013-09-25 19:19 | 2013-09-25 20:40 | 81 | 11kV | 69041 | 1110 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn195 Pymble Panel 29 tripped on Relays: Earth Fault with fault check Cause: Suspect Cable fault between S4021, S35489, S46905 tee PT1846 See OMS 1020451 1020453 1020455 1019261 | September | 2013 | 2014Q1 | 2014 | ZN195:PA29 | ZN195:PA29 | ZN00195/000029 | KU-RING-GAI | UG | Not Veg | 2013-09-25 | N | 62.1991 | N | 8 | N | N | 1.1101 | 39.4971 | 50453.1264
[7 empty] | 16054 | 15460 | 1019281 | 2013-09-25 23:05 | 2013-09-26 02:10 | 185 | 11kV | 280483 | 1648 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137171 Rec N/A due to TFB fdr patrolled to advice for suburban/rural fdr Excluded oms 1019281 | September | 2013 | 2014Q1 | 2014 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2013-09-25 | N | 170.196 | N | 8 | N | N | 1.1101 | 39.4971 | 204968.7036
[7 empty] | 16215 | 17229 | 1019370 | 2013-09-26 09:27 | 2013-09-26 10:47 | 80 | 11kV | 114080 | 1426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137175 1 Fault operations, Overcurrent, Sensitive Earth Fault The feeder was patrolled, no cuase found and sw 50319 closed successfully | September | 2013 | 2014Q1 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2013-09-26 | N | 80 | N | 21 | Y | Y | 1.1101 | 39.4971 | 83366.2992
[7 empty] | 16390 | 18997 | 1019403 | 2013-09-26 11:03 | 2013-09-26 11:43 | 40.3333 | 11kV | 2460.3333 | 61 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @PT13115 Mangrove Narara Valley roadside side 31.5 HV fuse has blown Tree branch on OH mains See 1019405 exclude 1019403,10 | September | 2013 | 2014Q1 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-09-26 | N | 40.3333 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1797.939
[7 empty] | 16184 | 16914 | 1019437 | 2013-09-26 11:44 | 2013-09-26 12:28 | 44 | 11kV | 70100 | 1707 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | @Zn12600 Lisarow Pa9 fdr tripped Relays: A Phase Instantaneous and Timed Overcurrent Signals: 11kv trip EFI: Nil Cause: Weather related See 1020313,5 exclude 1019437 | September | 2013 | 2014Q1 | 2014 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2013-09-26 | N | 41.0662 | N | 21 | Y | Y | 1.1101 | 39.4971 | 51227.0124
[7 empty] | 16284 | 17850 | 1019423 | 2013-09-26 11:24 | 2013-09-26 12:30 | 66 | 11kV | 4422 | 67 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Ex Zn12630 Peats Ridge section of Pa3 @RE45035 Mangrove Mountain has tripped Relays: B & C phase OC, IOC and EF Cause: weather related | September | 2013 | 2014Q1 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-09-26 | N | 66 | N | 21 | Y | Y | 1.1101 | 39.4971 | 3231.4672
[7 empty] | 15693 | 10961 | 1019390 | 2013-09-26 10:33 | 2013-09-26 12:50 | 137 | 11kV | 37162 | 324 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Recloser 22381 Lane Cove Walter (ZN15014 Mona Vale Zone ex panel 14 'S17022 Walana Mona, etc.') CB tripped and locked out on: - Earth Fault trip. 11kV fault in UG section of feeder from LB 21568 to SW/A at S16061 Walker McCarrs tee to S16178 McCarrs Creek. OMS Numbers: 1020340, 1020341, 1019390 | September | 2013 | 2014Q1 | 2014 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | UG | Not Veg | 2013-09-26 | N | 114.6975 | N | 21 | Y | Y | 1.1101 | 39.4971 | 27156.8935
[7 empty] | 15421 | 7693 | 1019478 | 2013-09-26 12:13 | 2013-09-26 13:01 | 48 | 11kV | 1728 | 36 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | @Zn14143 Somersby Pa21 fdr tripped Relays: A and B phase Overcurrent Signals: 11kv trip Cause: Weather related. Tree found near links 44185 (Sht 3 B6) | September | 2013 | 2014Q1 | 2014 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2013-09-26 | N | 48 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1262.7714
[7 empty] | 16115 | 16109 | 1019524 | 2013-09-26 12:36 | 2013-09-26 13:40 | 64 | 11kV | 68424 | 1082 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S129 Hunters Hill Panel 9 Tripped and reclosed Tripped and locked out on Relays: A and C phase Timed O/C, B phase IOC and Timing relay Field EFI'S: Nil Cause: likely Tree branch from wind. DOp patrolled and nothing found See OMS 1020205 1020208 | September | 2013 | 2014Q1 | 2014 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Veg | 2013-09-26 | N | 63.2384 | N | 21 | Y | Y | 1.1101 | 39.4971 | 50002.241
[7 empty] | 15559 | 8985 | 1019471 | 2013-09-26 12:10 | 2013-09-26 13:52 | 102 | 11kV | 6182 | 73 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Ex Zn12630 Peats Ridge section of Pa2 @RE45013 Gunderman has tripped ABNORMAL: Job #323368 between LK 42515 and LK45074 closed. PT's 13625 and PT14273 are interrupted as part of planned outage Relays: A and B phase Overcurrent, LO Cause: Weather related. Strong Wind See 1020325,6,8 exclude 1019471 | September | 2013 | 2014Q1 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2013-09-26 | N | 84.6849 | N | 21 | Y | Y | 1.1101 | 39.4971 | 4517.6233
[7 empty] | 16171 | 16720 | 1019552 | 2013-09-26 12:48 | 2013-09-26 14:02 | 74 | 11kV | 97310 | 1315 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Sub 116 Leichhardt Panel No.44 "Carlisle St, Leichhardt Aux No.1" feeder tripped on: Relays: A,B & C phases IOC Field EFI's: Nil Remarks: tree branch contact - other. A large tree has fallen down in a park near Manning St Rozelle. It appears that it has hit the mains on the way down | September | 2013 | 2014Q1 | 2014 | ZN116:PA44 | ZN116:PA31 | ZN00116/000031 | INNER WEST | OH | Veg | 2013-09-26 | N | 74 | N | 21 | Y | Y | 1.1101 | 39.4971 | 71111.2778
[7 empty] | 15439 | 7859 | 1019719 | 2013-09-26 12:49 | 2013-09-26 14:09 | 80 | 11kV | 12800 | 160 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137184 A & B phase Instantaneous Overcurrent tree on mains at pole FR-44816 Excluded OMS 1019715 | September | 2013 | 2014Q1 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2013-09-26 | N | 80 | N | 21 | Y | Y | 1.1101 | 39.4971 | 9353.8625
[7 empty] | 15996 | 14558 | 1019714 | 2013-09-26 13:30 | 2013-09-26 14:18 | 48 | 11kV | 37584 | 783 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S80 Chatswood Panel 31 Tripped reclosed tripped and locked out on Relays: A phase IOC/Lockout and Timing Cause: Tree branch removed O/S 31 Beconsfield Rd. See OMS 1019714 1019746 CC1: 22-"Refer to SOp" | September | 2013 | 2014Q1 | 2014 | ZN80:PA31 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2013-09-26 | N | 48 | N | 21 | Y | Y | 1.1101 | 39.4971 | 27465.2787
[7 empty] | 15182 | 4422 | 1019678 | 2013-09-26 13:16 | 2013-09-26 15:14 | 118 | 11kV | 70934 | 617 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Recloser 1622 Eastern Arterial (ZN3154 St Ives ex panel 16 'S7413 Lynbara Shinfield') CB tripped and locked out on Overcurrent. Fault indicator at tee to PT1624 Davidson Park Lookout was down. Tree/ branch brough down 11kV wires between LB3238 and LB62189. Mains to repair immediately. OMS Numbers: 1020171, 1020167, 1019678 | September | 2013 | 2014Q1 | 2014 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Veg | 2013-09-26 | N | 114.966 | N | 21 | Y | Y | 1.1101 | 39.4971 | 51836.475
[7 empty] | 15538 | 8860 | 1019583 | 2013-09-26 12:55 | 2013-09-26 15:55 | 180 | 11kV | 274100 | 1816 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137188 1 fault operation A phase Instantaneous Overcurrent Reclose off for Bush Fire Excluded OMS 1019583 | September | 2013 | 2014Q1 | 2014 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2013-09-26 | N | 150.9361 | N | 21 | Y | Y | 1.1101 | 39.4971 | 200304.1954
[7 empty] | 16173 | 16740 | 1019597 | 2013-09-26 13:02 | 2013-09-26 16:30 | 208 | 11kV | 282767.3333 | 2707 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Wind | N | LID 137194 1 fault operation Overcurrent TV antenna on OHM near pole JT-81241. | September | 2013 | 2014Q1 | 2014 | 240:34835 | 240:34849 | ZN00240/034849 | NEWCASTLE | OH | Not Veg | 2013-09-26 | N | 104.4578 | N | 21 | Y | Y | 1.1101 | 39.4971 | 206638.027
[7 empty] | 14794 | 900 | 1019650 | 2013-09-26 13:06 | 2013-09-26 17:00 | 234 | 11kV | 8190 | 35 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 137187 3 fault operations A phase Earth fault wires down at pole FM-90091 | September | 2013 | 2014Q1 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-09-26 | N | 234 | N | 21 | Y | Y | 1.1101 | 39.4971 | 5985.0104
[7 empty] | 15925 | 13389 | 1019486 | 2013-09-26 12:19 | 2013-09-26 17:10 | 291 | 11kV | 30831 | 375 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 has tripped Relays: A & C phase Overcurrent, OL Cause: Tree/Branch brought down OH Tree outside 1086 Yarramalong rd, Yarramalong See 1020376,80 Exclude 1019486,99,814,8 | September | 2013 | 2014Q1 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-09-26 | N | 82.216 | N | 21 | Y | Y | 1.1101 | 39.4971 | 22530.3854
[7 empty] | 14848 | 1347 | 1019853 | 2013-09-26 16:15 | 2013-09-26 17:10 | 55 | 11kV | 55 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 137195 Broken tail from LLC to DOLF | September | 2013 | 2014Q1 | 2014 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2013-09-26 | N | 55 | N | 21 | Y | Y | 1.1101 | 39.4971 | 40.1924
[7 empty] | 14996 | 2835 | 1019872 | 2013-09-26 15:03 | 2013-09-26 17:30 | 147 | 11kV | 1911 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137211 Single phase DOLF : 10 Amp fdr patrolled nothing found fuses restored all ok Excluded oms1019872 CC1: 22-"Refer to SOp" | September | 2013 | 2014Q1 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-09-26 | N | 147 | N | 21 | Y | Y | 1.1101 | 39.4971 | 1396.5024
[7 empty] | 15466 | 8092 | 1020047 | 2013-09-26 19:35 | 2013-09-26 21:42 | 127 | 11kV | 85836 | 1426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137200 1 fault operation Sensitive Earth Fault; Overcurrent Second outage today, fdr patrolled & no cause found. Detailed patrol required from Sw 50319 to Sw 50354 Excluded OMS 10020047, 1020061 | September | 2013 | 2014Q1 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2013-09-26 | N | 60.1935 | N | 21 | Y | Y | 1.1101 | 39.4971 | 62726.4171
[7 empty] | 15326 | 6604 | 1020305 | 2013-09-26 13:03 | 2013-09-26 22:20 | 557 | 11kV | 924827.6667 | 3686 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 137199 1 fault operation C phase Overcurrent Cable fault & HV mains down between JU-31498 & JU-30355. Excluded OMS 1019551. | September | 2013 | 2014Q1 | 2014 | 203:8086 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2013-09-26 | N | 250.9028 | N | 21 | Y | Y | 1.1101 | 39.4971 | 675836.781
[7 empty] | 15960 | 13950 | 1019532 | 2013-09-26 12:38 | 2013-09-27 00:15 | 697 | 11kV | 120191.6167 | 695 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137197 2 fault operations 3 phase Earth fault Tree brought mains down between poles JU-31032 & JU-36224. HV into LV. Excluded OMS 1019532, 1019791, 1019937, 1020093, 1020096, 1020098, 1020103 | September | 2013 | 2014Q1 | 2014 | 203:8090 | 204:82699 | ZN00204/082699 | NEWCASTLE | OH | Veg | 2013-09-26 | N | 172.9376 | N | 21 | Y | Y | 1.1101 | 39.4971 | 87832.4884
[7 empty] | 15795 | 12081 | 1020089 | 2013-09-27 01:26 | 2013-09-27 02:16 | 50 | 11kV | 48555 | 1368 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | At S15005 Belrose 11kV panel 6 'Davidson Park' feeder tripped and reclosed on B and C phase overcurrent, reclose timing and lockout. CP24831 Lockwood Peacock tripped reclosed and locked out on IOC abd OC. Field EFIs operated: S16965 and S48656. Cause of interuption animals/birds at UGOH to S15665 Hakea Av. Reference OMS numbers: 1020504, 1020502, 1020089 | September | 2013 | 2014Q1 | 2014 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-09-27 | N | 35.4934 | N | 5 | N | N | 1.1101 | 39.4971 | 35482.5619
[7 empty] | 14877 | 1744 | 1020091 | 2013-09-27 01:21 | 2013-09-27 02:38 | 77 | 11kV | 20328 | 264 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa11 Norah Head @RE45050 Magenta recloser tripped reclsoed and locked out on IOC and OC See 1020454 exclude 1020091 | September | 2013 | 2014Q1 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2013-09-27 | N | 77 | N | 5 | N | N | 1.1101 | 39.4971 | 14855.1028
[7 empty] | 15424 | 7716 | 1020097 | 2013-09-27 08:30 | 2013-09-27 10:50 | 140 | 11kV | 224 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137207 B phase EMERG SWITCHING DUE TO LLC FAILING AND NO LL CREW AVAILABLE. | September | 2013 | 2014Q1 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2013-09-27 | N | 56 | N | 5 | N | N | 1.1101 | 39.4971 | 163.6926
[7 empty] | 15675 | 10749 | 1020191 | 2013-09-27 10:06 | 2013-09-27 12:30 | 144 | 11kV | 288 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 137209 C phase DOLF : 16 Amp NO CAUSE FOUND. FUSE CARRIER REPLACED. | September | 2013 | 2014Q1 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2013-09-27 | N | 144 | N | 5 | N | N | 1.1101 | 39.4971 | 210.4619
[7 empty] | 15632 | 10127 | 1020424 | 2013-09-27 12:00 | 2013-09-27 15:25 | 205 | 11kV | 7995 | 39 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Ex Zn12570 Avoca Zone section of Pa29 Btwn AB44619 - USL44276 interrupted by DOp to allow lineworker to carry out repairs to USL41506 ABNORMAL: Empire Bay Zone 11kv network switched away. Empire Bay Pa8 & Pa4 fed via AB43452. USL44969 Open AB41812 Closed. Fed from Avoca Pa40 See 1021012 exclude 1020424 | September | 2013 | 2014Q1 | 2014 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2013-09-27 | N | 205 | N | 5 | N | N | 1.1101 | 39.4971 | 5842.5102
[7 empty] | 14924 | 2088 | 1020647 | 2013-09-28 10:21 | 2013-09-28 11:35 | 74 | 11kV | 8498.6 | 115 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At S.1743 the #1 Tx 63 amp OEFMA 11kV fuses failed in service | September | 2013 | 2014Q1 | 2014 | ZN180:PA9 | ZN180:PA9 | ZN00180/000009 | MOSMAN | OH | Not Veg | 2013-09-28 | N | 73.9009 | N | 5 | N | N | 1.1101 | 39.4971 | 6210.5262
[7 empty] | 16153 | 16498 | 1020695 | 2013-09-28 13:13 | 2013-09-28 14:06 | 53 | 11kV | 44891 | 847 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S35370 Galston Panel 8 tripped reclosed tripped and lockedout on Relays: B and C phase IOC, EFI, Reclose relay, Lock out relay Cause: Tree branch on feeder tee to PT739 | September | 2013 | 2014Q1 | 2014 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-09-28 | N | 53 | N | 5 | N | N | 1.1101 | 39.4971 | 32805.0187
[7 empty] | 15548 | 8914 | 1020700 | 2013-09-28 13:43 | 2013-09-28 16:30 | 167 | 11kV | 12201 | 83 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 24722 tripped and locked out on SEL. Two phases of OH wires on crossarm between LB.63021 and AB.20623 tee to PT.15159 | September | 2013 | 2014Q1 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-09-28 | N | 147 | N | 5 | N | N | 1.1101 | 39.4971 | 8916.1309
[7 empty] | 16164 | 16611 | 1020713 | 2013-09-28 14:04 | 2013-09-28 17:08 | 184 | 11kV | 212552 | 1361 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn13000 Lake Munmorah section of Pa7 CP45061 Chain Valley Bay Mulloway tripped on SEF EFI Cause: Bond burnt off at AB43823 See 1021083,4 exclude 1020713 | September | 2013 | 2014Q1 | 2014 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2013-09-28 | N | 156.1734 | N | 5 | N | N | 1.1101 | 39.4971 | 155326.7324
[7 empty] | 16119 | 16154 | 1020773 | 2013-09-28 20:08 | 2013-09-28 21:25 | 77 | 11kV | 26173 | 407 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Zn14891 Wyong Pa14R fdr tripped on Relays: Bassler 51AB EFI, TX2 E/F check EFI:S14799,S14630 Signals:11kv trip Abnormal: RE45181 bypassed via AB closed Cause: Possum found at base of pole at AB44731. Please inspect UGOH pole WY2634 outside 95 Gavenlock rd Tuggerah See 1021161,2,3,4 Exclude 1020773,4,5 | September | 2013 | 2014Q1 | 2014 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Not Veg | 2013-09-28 | N | 64.3071 | N | 5 | N | N | 1.1101 | 39.4971 | 19126.4564
[7 empty] | 15099 | 3689 | 1020855 | 2013-09-29 13:04 | 2013-09-29 13:55 | 51 | 11kV | 2754 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT477 Nelson Tryon roadside 11kV drop out fuse operated Cause: Fuse fatigue See OMS 1022890 1020855 1020859 | September | 2013 | 2014Q1 | 2014 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Not Veg | 2013-09-29 | N | 51 | N | 5 | N | N | 1.1101 | 39.4971 | 2012.542
[7 empty] | 15759 | 11686 | 1020852 | 2013-09-29 14:40 | 2013-09-29 15:15 | 35 | 11kV | 1015 | 29 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa16 Btw AB44422-USL43026 Cause: interrupted for safety reasons. To remove branch from HV mains in Bruce Crescent See 1021185 exclude 1020868 | September | 2013 | 2014Q1 | 2014 | ZN14891:PA16 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Veg | 2013-09-29 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 741.7321
[7 empty] | 15209 | 4713 | 1020891 | 2013-09-29 19:06 | 2013-09-29 21:04 | 118.45 | 11kV | 114291.1 | 1172 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137224 1 fault operation B & C phase Overcurrent Excluded OMS 1020891, 1020899, 1020900, 1020901 & 1020902 | September | 2013 | 2014Q1 | 2014 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Veg | 2013-09-29 | N | 97.518 | N | 5 | N | N | 1.1101 | 39.4971 | 83520.5649
[7 empty] | 15801 | 12137 | 1020905 | 2013-09-29 20:18 | 2013-09-29 21:51 | 93 | 11kV | 38090 | 414 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @Zn12570 Avoca Pa26 fdr tripped on B&C Phase IOC Alarms: 11kv trip Cause: not ascertained All OH patrolled except beyond LB48409. OH Mains to patrol in daylight See 1021187,8 exclude 1020905 | September | 2013 | 2014Q1 | 2014 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Veg | 2013-09-29 | N | 92.0048 | N | 5 | N | N | 1.1101 | 39.4971 | 27835.0485
[7 empty] | 15430 | 7794 | 1020787 | 2013-09-29 03:25 | 2013-09-29 22:50 | 1165 | 11kV | 76627 | 1157 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | Z.7900 Campbell St - Pnl.6 tripped on: A, B & C phase O/C, Earth Fault, Fault Check and EFI. Field EFIs: S8528 S7187 S48719 S61473 S61532 & S4430 Abnormal: Feeder defective from S4067 to S63 to S35617 (Surry Hills Sht 1 C5) S4430 Richard Coll (Sw B) CLOSED S35617 - Collins Riley (Sw A) OPEN S35617 Collins Riley destroyed by fire see 1020950 1020952 1020951 | September | 2013 | 2014Q1 | 2014 | ZN7900:PA6 | ZN7900:PA6 | ZN07900/000006 | SYDNEY | UG | Not Veg | 2013-09-29 | N | 66.229 | N | 5 | N | N | 1.1101 | 39.4971 | 55996.7515
[7 empty] | 16011 | 14728 | 1020954 | 2013-09-30 08:03 | 2013-09-30 10:15 | 132 | 11kV | 395.55 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | EX Zn12630 Peats Ridge section of Pa5 @PT14263 Wiseman Ferry North Expressway Bphase 20A HVDO Cause: Fuse Fatigue See 1021424 GIS 1020954 | September | 2013 | 2014Q1 | 2014 | ZN12630:PA5 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2013-09-30 | N | 131.85 | N | 6 | N | N | 1.1101 | 39.4971 | 289.0563
[7 empty] | 16216 | 17230 | 1020981 | 2013-09-30 08:56 | 2013-09-30 10:32 | 96 | 11kV | 136896 | 1426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137226 3 fault operations Sensitive Earth Fault; Overcurrent | September | 2013 | 2014Q1 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2013-09-30 | N | 96 | N | 6 | N | N | 1.1101 | 39.4971 | 100039.5591
[7 empty] | 16182 | 16903 | 1021166 | 2013-09-30 12:44 | 2013-09-30 14:25 | 101 | 11kV | 303 | 3 | HV | Animal Insect | Animal | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa3 @PT18535 Waratah Wisferry 3.0 HV fuse found operated. Wasp nest found inside HV fuse tube causing tracking and burning melting fuse wedge See 1021444 exclude 1021166 | September | 2013 | 2014Q1 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2013-09-30 | N | 101 | N | 6 | N | N | 1.1101 | 39.4971 | 221.4235
[7 empty] | 16099 | 15987 | 1021192 | 2013-09-30 13:35 | 2013-09-30 15:45 | 130 | 11kV | 1690 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 137232 No Protection operation Crossarm failure at Pole CS-60082 | September | 2013 | 2014Q1 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-09-30 | N | 130 | N | 6 | N | N | 1.1101 | 39.4971 | 1235.0022
[7 empty] | 16101 | 16004 | 1021310 | 2013-09-30 16:15 | 2013-09-30 17:09 | 54 | 11kV | 66582 | 1233 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S35800 Bankstown Panel #1 "Gow Gibson" fdr tripped on B & C phase IOC 11kv trip Remarks: animals/birds. Crow into hv cnr Irvine St & herbert St Bankstown | September | 2013 | 2014Q1 | 2014 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-09-30 | N | 54 | N | 6 | N | N | 1.1101 | 39.4971 | 48656.1618
[7 empty] | 16142 | 16421 | 1021385 | 2013-09-30 23:21 | 2013-10-01 00:30 | 69 | 11kV | 5658 | 82 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137234 B phase DOLF : 31 Amp Possum Excluded OMS 1021385 & 1021386 | September | 2013 | 2014Q1 | 2014 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2013-09-30 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 4134.6995
[7 empty] | 14978 | 2627 | 1021396 | 2013-10-01 09:10 | 2013-10-01 11:40 | 150 | 11kV | 150 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 137245 Broken LL dropper Excluded OMS 1021396 | October | 2013 | 2014Q2 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-10-01 | N | 150 | N | 40 | Y | Y | 1.1101 | 39.4971 | 109.6156
[7 empty] | 16356 | 18627 | 1021515 | 2013-10-01 09:56 | 2013-10-01 12:30 | 154 | 11kV | 3907 | 847 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S35370 Galston Section of Panel 8 fromCP554 Arcadia Rosscommon tripped and reclosed on C and B phase Overcurrent Cause: Tree branch brought down OH mains O/S 33 and 40 Cobar Rd See OMS 1023467 1023469 1021515 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-10-01 | N | 4.6128 | N | 40 | Y | Y | 1.1101 | 39.4971 | 2855.1204
[7 empty] | 16265 | 17620 | 1021604 | 2013-10-01 12:32 | 2013-10-01 12:50 | 18 | 11kV | 7542 | 419 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Zn35370 Galston Panel 8 CP554 Arcadia Roddcommon tripped on B and Cphase O/C Cause: Tree on OH mains Near Cobah Rd. Second tree branch iin same street. After restoration of previous fault tree fell again See OMS 1023611 1021604 1021634 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-10-01 | N | 18 | N | 40 | Y | Y | 1.1101 | 39.4971 | 5511.4711
[7 empty] | 16213 | 17172 | 1021592 | 2013-10-01 12:00 | 2013-10-01 13:10 | 70 | 11kV | 350 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 137249 Split xarm helicopter patrol. Emergency Job No Protection Operation | October | 2013 | 2014Q2 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2013-10-01 | N | 70 | N | 40 | Y | Y | 1.1101 | 39.4971 | 255.7697
[7 empty] | 16068 | 15638 | 1021798 | 2013-10-01 12:29 | 2013-10-01 13:25 | 56 | 11kV | 8344 | 149 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12630 Peats Ridge section of Pa3 @RE46935 Ironbark Kirks tripped reclosed , tripped and locked out on Overcurrent, Instantaneous Overcurrent Cause: Tree Branch removed off Overhead near PT13226 Kirks Ironbark 0.4 See 1022471 exclude 1021798 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 56 | N | 40 | Y | Y | 1.1101 | 39.4971 | 6097.5491
[7 empty] | 15149 | 4157 | 1021566 | 2013-10-01 13:15 | 2013-10-01 13:44 | 29 | 11kV | 232 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 137250 A phase Broken LL clamp | October | 2013 | 2014Q2 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2013-10-01 | N | 29 | N | 40 | Y | Y | 1.1101 | 39.4971 | 169.5388
[7 empty] | 16457 | 20023 | 1021622 | 2013-10-01 12:07 | 2013-10-01 13:56 | 109 | 11kV | 50288 | 602 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S35370 Galston Pa4 Tripped on B and C phase IOC Cause: Tree branch on OH See OMS 1023458 1023460 1021601 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-10-01 | N | 83.5349 | N | 40 | Y | Y | 1.1101 | 39.4971 | 36748.9872
[7 empty] | 15087 | 3541 | 1021662 | 2013-10-01 12:32 | 2013-10-01 13:58 | 86 | 11kV | 27864 | 324 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Recloser 22381 tripped on IOC and OC; weather related - Tree branch on ground with burn marks | October | 2013 | 2014Q2 | 2014 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2013-10-01 | N | 86 | N | 40 | Y | Y | 1.1101 | 39.4971 | 20362.1894
[7 empty] | 15166 | 4261 | 1021520 | 2013-10-01 10:09 | 2013-10-01 14:20 | 251 | 11kV | 11785 | 67 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa3 @RE45035 Mangrove Mountain on SEL Cause: Tree Branch brought overhead down near LK40940. Overhead have repaired See 1022448,9 Exclude 1021520,75 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 175.8955 | N | 40 | Y | Y | 1.1101 | 39.4971 | 8612.1304
[7 empty] | 16244 | 17495 | 1022367 | 2013-10-01 12:24 | 2013-10-01 14:36 | 132 | 11kV | 95437 | 1038 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID 137247 3 fault operations Earth fault faulty section of UGM between Sw 36080 & Sw 55116 isolated see report # 137255 Excluded OMS # 1021632 | October | 2013 | 2014Q2 | 2014 | 216:10729 | 216:10729 | ZN00216/010729 | LAKE MACQUARIE | UG | Not Veg | 2013-10-01 | N | 91.9432 | N | 40 | Y | Y | 1.1101 | 39.4971 | 69742.5447
[7 empty] | 16454 | 19983 | 1022371 | 2013-10-01 14:02 | 2013-10-01 15:10 | 68 | 11kV | 9774 | 1005 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | LID 137255 1 fault operation A phase Overcurrent; Earth fault Related to OMS 1022367 UG cable fault on fdr 10729. Attempted backfeed | October | 2013 | 2014Q2 | 2014 | 216:10729 | 216:10729 | ZN00216/010729 | LAKE MACQUARIE | UG | Not Veg | 2013-10-01 | N | 9.7254 | N | 40 | Y | Y | 1.1101 | 39.4971 | 7142.5509
[7 empty] | 16376 | 18810 | 1021835 | 2013-10-01 13:18 | 2013-10-01 15:25 | 127.0833 | 11kV | 14106.25 | 111 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12640 Umina section of Pa7 @PT13802 Augusta the Esplanade fotpath HVDO assembly broken. Subs have repaired See 1021835 exclude 1021985 | October | 2013 | 2014Q2 | 2014 | ZN12640:PA7 | ZN12640:PA7 | ZN12640/000007 | CENTRAL COAST | OH | Not Veg | 2013-10-01 | N | 127.0833 | N | 40 | Y | Y | 1.1101 | 39.4971 | 10308.4314
[7 empty] | 16344 | 18480 | 1021701 | 2013-10-01 12:43 | 2013-10-01 15:40 | 177 | 11kV | 420552 | 2376 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12610 Long Jetty Pa11 tripped and locked out Abnormal: Auto Reclose on Pa11 was N/A Relays: B and C phase IOC EFI Earht Fault check Signals: 11kv trip EI's: All down to S14377 Large tree blown onto 11kv mains o/s 38 Yimbala st. removed by SES | October | 2013 | 2014Q2 | 2014 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 177 | N | 40 | Y | Y | 1.1101 | 39.4971 | 307326.9974
[7 empty] | 16137 | 16348 | 1021495 | 2013-10-01 09:27 | 2013-10-01 15:55 | 388 | 11kV | 7460 | 30 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137254 1 fault operation Sing;le phase Sensitive Earth Fault Wires down at pole 8E-70010. Excluded OMS No.1021495 & 1021653 | October | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-10-01 | N | 248.6667 | N | 40 | Y | Y | 1.1101 | 39.4971 | 5451.548
[7 empty] | 15788 | 11991 | 1021603 | 2013-10-01 12:08 | 2013-10-01 16:20 | 252 | 11kV | 101638 | 581 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Section of Pa2 ex Galston Zone CP3280 Hunt Ave Tripped Cause: Tree on Mains o/s 59 Quarry Rd. Tree on OH mains. Abnormal Switching: CP62157 Closed with CP2270 Open (D&R - 321385, Note Pa 10L to CP2270 Planned Interruption) See OMS 1023428 1023429 1023430 1021607 1021603 1021645 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2013-10-01 | N | 174.9363 | N | 40 | Y | Y | 1.1101 | 39.4971 | 74274.0526
[7 empty] | 15535 | 8848 | 1021907 | 2013-10-01 13:49 | 2013-10-01 16:20 | 151 | 11kV | 67902 | 865 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Zn1673 Turramurra Panel 13 tripped on B and C phase IOC Cause: Tree branch brough down OG wires between S4715 Boundary Chifley and S7920 Grosvenor Fisher tee PT1976 Barton Chifley See OMS 1022899 1022901 1022902 1021907 | October | 2013 | 2014Q2 | 2014 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Veg | 2013-10-01 | N | 78.4994 | N | 40 | Y | Y | 1.1101 | 39.4971 | 49620.7788
[7 empty] | 14889 | 1823 | 1021888 | 2013-10-01 13:46 | 2013-10-01 16:24 | 157.9833 | 11kV | 13112.6167 | 83 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Recloser 24722 tripped and locked out - weather related CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2013-10-01 | N | 157.9833 | N | 40 | Y | Y | 1.1101 | 39.4971 | 9582.3135
[7 empty] | 14890 | 1852 | 1021697 | 2013-10-01 12:40 | 2013-10-01 16:50 | 250 | 11kV | 118914 | 685 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 137262 C phase Overcurrent wire off pin at pole AI-20080. near sub 46583. Excluded oms 1021697, 1022084, 1021711 | October | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-10-01 | N | 173.5971 | N | 40 | Y | Y | 1.1101 | 39.4971 | 86898.8438
[7 empty] | 16229 | 17371 | 1021709 | 2013-10-01 12:43 | 2013-10-01 17:10 | 267 | 11kV | 156832 | 2170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12610 Long Jetty Zone Pa22 fdr tripped and loced out on Relays: A and B phase IOC EFI reclose timing and lockout flags Signals: 11kv trip EFI: Down to S14998 Large tree branch blown onto 11kv mains bringing down wires See 1023766,7 exclude 1021709,39 | October | 2013 | 2014Q2 | 2014 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 72.2728 | N | 40 | Y | Y | 1.1101 | 39.4971 | 114608.1998
[7 empty] | 15376 | 7138 | 1021997 | 2013-10-01 15:48 | 2013-10-01 17:10 | 82 | 11kV | 28474 | 557 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S1193 Lindfield Panel 25 Tripped on A and B phase IOC with EFI Cause: Tree branch on OH mains in Hill St Cnr Victoria Rd LB3221 defective and will not close. See OMS 1022420 1022422 1021997 | October | 2013 | 2014Q2 | 2014 | ZN1193:PA25 | ZN1193:PA25 | ZN01193/000025 | KU-RING-GAI | OH | Veg | 2013-10-01 | N | 51.1203 | N | 40 | Y | Y | 1.1101 | 39.4971 | 20807.9594
[7 empty] | 15834 | 12482 | 1021643 | 2013-10-01 12:26 | 2013-10-01 17:22 | 296 | 11kV | 131476 | 1156 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137252 Sensitive Earth Fault wires down near sub 52167, pole RU-23313. tripped fdr Sw 48039. Excluded oms 1021643, 1021944, 1022155, 1022540, 1022543, 1022542, 1022547 | October | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-10-01 | N | 113.7336 | N | 40 | Y | Y | 1.1101 | 39.4971 | 96078.7829
[7 empty] | 14709 | 119 | 1021600 | 2013-10-01 13:23 | 2013-10-01 17:29 | 246 | 11kV | 738 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | 11KV DROPPER BROKEN OFF TOP OF DOLF AT SUB 54130. MAITLAND FIELD STAFF ON SITE AND ARE ORGANISING REPAIRS. SUB ISOLATED. also refer to 1021600 and 1021850 | October | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-10-01 | N | 246 | N | 40 | Y | Y | 1.1101 | 39.4971 | 539.3086
[7 empty] | 15415 | 7586 | 1021790 | 2013-10-01 12:51 | 2013-10-01 17:50 | 299 | 11kV | 50804 | 271 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137264/03 1 fault operation Earth fault OHEW broke off pole BK-70058 Excluded OMS 1021790 & 1021993 | October | 2013 | 2014Q2 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2013-10-01 | N | 187.4686 | N | 40 | Y | Y | 1.1101 | 39.4971 | 37126.0647
[7 empty] | 14818 | 1099 | 1021738 | 2013-10-01 12:41 | 2013-10-01 18:00 | 319 | 11kV | 250312 | 1201 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12690 Berkeley Vale Pa19 fdr tripped and locked out on Relays: B C phase IOC Signals: 11kv trip Cause: tree/branch brought down OH. Tree blown onto 11kv mains bringing wires down adjacent to AB42130 See 1022526,7,8 Exclude 1021695 | October | 2013 | 2014Q2 | 2014 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 208.4197 | N | 40 | Y | Y | 1.1101 | 39.4971 | 182920.6266
[7 empty] | 15922 | 13356 | 1021731 | 2013-10-01 12:42 | 2013-10-01 18:32 | 350 | 11kV | 34258 | 129 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12600 Lisarow section of Pa2 @RE41020 Wattle Tree Rd North tripped on Overcurrent, Earth Fault Cause: Tree Brought down 11kv OH in watle tree rd near LB45186. Linesman have repaired. See 1022648,950,1,2 Exclude 1021731,3,91,2110 | October | 2013 | 2014Q2 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 265.5659 | N | 40 | Y | Y | 1.1101 | 39.4971 | 25034.736
[7 empty] | 15952 | 13703 | 1021585 | 2013-10-01 11:49 | 2013-10-01 18:42 | 413 | 11kV | 5782 | 14 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137256 3 fault operations A & B phase Overcurrent Wires down at pole AK-63118. Excluded OMS No. 1021585 | October | 2013 | 2014Q2 | 2014 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Not Veg | 2013-10-01 | N | 413 | N | 40 | Y | Y | 1.1101 | 39.4971 | 4225.3151
[7 empty] | 14726 | 273 | 1022215 | 2013-10-01 17:45 | 2013-10-01 19:00 | 75 | 11kV | 6225 | 83 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 137263 section isolated to repair insulators at pole OS-20527 Excluded oms # 1022232 | October | 2013 | 2014Q2 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2013-10-01 | N | 75 | N | 40 | Y | Y | 1.1101 | 39.4971 | 4549.0464
[7 empty] | 16025 | 14919 | 1022056 | 2013-10-01 15:28 | 2013-10-01 20:15 | 287 | 11kV | 23122 | 118 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137258 1 fault operation Earth fault wires down at pole JT-10104 Excluded oms # 1022056 | October | 2013 | 2014Q2 | 2014 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2013-10-01 | N | 195.9492 | N | 40 | Y | Y | 1.1101 | 39.4971 | 16896.8756
[7 empty] | 15370 | 7042 | 1021674 | 2013-10-01 12:33 | 2013-10-01 20:17 | 464 | 11kV | 7888 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12650 West Gosford section of Pa1 @RE45010 Palmgrove tripped on SEF IOC Cause: OH Down. 1 Bay of 11kv Overhead down near PT48497. Overhead have repaired. See 1021674 Exclude 1021706,95,828,935,2238 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 464 | N | 40 | Y | Y | 1.1101 | 39.4971 | 5764.3177
[7 empty] | 16075 | 15725 | 1021886 | 2013-10-01 13:40 | 2013-10-01 20:22 | 402 | 11kV | 13306 | 70 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137257 1 fault operation single phase Sensitive Earth Fault Wires down at 11kV links 43254. Excluded OMS No. 1021585 + 1022130, also refer to OMS 1022607 | October | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-10-01 | N | 190.0857 | N | 40 | Y | Y | 1.1101 | 39.4971 | 9723.6323
[7 empty] | 15231 | 5265 | 1021948 | 2013-10-01 13:13 | 2013-10-01 21:10 | 477.4667 | 11kV | 84428.0667 | 1152 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137259 Sensitive Earth Fault mains down beyond Spur 40495. Excluded oms 1021822, 1021948, 1022140 | October | 2013 | 2014Q2 | 2014 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2013-10-01 | N | 73.2883 | N | 40 | Y | Y | 1.1101 | 39.4971 | 61697.5409
[7 empty] | 15188 | 4455 | 1022190 | 2013-10-01 17:20 | 2013-10-01 22:50 | 330 | 11kV | 49958 | 170 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 137267 A phase LLC Broken lead to DOLF 51719 Elderslie Bridge sub. Excluded OMS 1022190 | October | 2013 | 2014Q2 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-10-01 | N | 293.8706 | N | 40 | Y | Y | 1.1101 | 39.4971 | 36507.8329
[7 empty] | 15537 | 8854 | 1022266 | 2013-10-01 21:45 | 2013-10-01 23:10 | 85 | 11kV | 1190 | 14 | HV | Equipment Failed in Service | Equipment Failure | 3rd Party Asset | Unplanned | Previous Storm | N | LID 137266 3 phase No protection operations. Section isolated to secure hurdles that fell into mains at pole JS-12417. Excluded OMS # 1022266 | October | 2013 | 2014Q2 | 2014 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | Unknown | Not Veg | 2013-10-01 | N | 85 | N | 40 | Y | Y | 1.1101 | 39.4971 | 869.6169
[7 empty] | 15199 | 4613 | 1022289 | 2013-10-01 21:07 | 2013-10-01 23:50 | 163 | 11kV | 489 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 137269 A phase DOLF : 10 Amp Volts = 245, amps = 20 Excluded OMS # 1022289. | October | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2013-10-01 | N | 163 | N | 40 | Y | Y | 1.1101 | 39.4971 | 357.3468
[7 empty] | 14714 | 155 | 1021714 | 2013-10-01 12:27 | 2013-10-02 00:15 | 708 | 11kV | 126415 | 689 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S2400 Berowra Panel section pof Pa11 CP3282 Alberta Ave Tripped Cause: Tree branch brought down OH between AB1093 and IS2336 tee PT1516 and PT2350 See OMS 1022983 1022986 1022988 1022989 | October | 2013 | 2014Q2 | 2014 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2013-10-01 | N | 183.4761 | N | 40 | Y | Y | 1.1101 | 39.4971 | 92380.3534
[7 empty] | 15748 | 11636 | 1021747 | 2013-10-01 12:42 | 2013-10-02 02:00 | 798 | 11kV | 11172 | 14 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | Ex Zn14891 Wyong section of Pa5 @Autolink 44788 tripped. OH down. Mains to repair and broken crossarm See 1022512 for feeder T&R exclude 1021747,78,831,2284,8 | October | 2013 | 2014Q2 | 2014 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-10-01 | N | 798 | N | 40 | Y | Y | 1.1101 | 39.4971 | 8164.1681
[7 empty] | 16391 | 19026 | 1021676 | 2013-10-01 12:39 | 2013-10-02 09:00 | 1221 | 11kV | 27497 | 37 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn14891 Wyong Zone section of Pa12 @RE46228 Ravensdale tripped on SEL Cause: Tree branch brought down OH. 11kv beyond USL42868 DOwned. Cut away made safe by linesman. to be restrung Wed AM. Interrupted fdr from AB43959 @ 900 to allow repairs. see seperate interuption report. See 1023764,5 Exclude 1021676,817 | October | 2013 | 2014Q2 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 743.1622 | N | 40 | Y | Y | 1.1101 | 39.4971 | 20093.9966
[7 empty] | 15151 | 4169 | 1023792 | 2013-10-02 09:00 | 2013-10-02 12:10 | 190 | 11kV | 3230 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 @AB43959 interupted to allow repairs to fallen 11kv OH mains beyond USL42868 Cause: tree branch brought down OH earlier incident See 1023764. Genuine outage overlap | October | 2013 | 2014Q2 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-10-02 | N | 190 | N | 5 | N | N | 1.1101 | 39.4971 | 2360.3887
[7 empty] | 15843 | 12612 | 1021715 | 2013-10-01 12:28 | 2013-10-02 13:50 | 1522 | 11kV | 105566 | 231 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge Pa1 section of Pa1 @RE44995 Kulnura tripped and locked out on overcurrent and Instantaneous overcurrent Cause: Storm. Multiple 11kv wires down See 1023751,3,4,5,6,7 Exclude 1021688,704,15,808,885 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2013-10-01 | N | 456.9957 | N | 40 | Y | Y | 1.1101 | 39.4971 | 77144.5191
[7 empty] | 15499 | 8439 | 1021636 | 2013-10-01 12:25 | 2013-10-02 14:35 | 1570 | 11kV | 780218 | 567 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn12630 Peats Ridge Pa2 tripped and reclosed and locked out on A phase timed and EFI Cause: Storm. Multiple HV Mains Down See 1023732,3,4,5,6,7,8,40,41 Exclude 1021636,734,857,2307 Rookie error 1023714,9,20,1,2,3,4,5,6 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2013-10-01 | N | 1376.0459 | N | 40 | Y | Y | 1.1101 | 39.4971 | 570160.3019
[7 empty] | 15433 | 7837 | 1022747 | 2013-10-02 15:30 | 2013-10-02 16:30 | 60 | 11kV | 2580 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14144 Wamberal section of Pa2 between LB41249 to LB40235 tee PT11284 PT18002 interrupted by DOp to allow linesman to remove tree branch from 11kv CCT mains in Oak Rd Matcham Tree branch on 11kv and LV Mains See 1024704,18 Exclude 1022747,9 | October | 2013 | 2014Q2 | 2014 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2013-10-02 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 1885.3879
[7 empty] | 14995 | 2822 | 1022722 | 2013-10-02 15:17 | 2013-10-02 16:45 | 88 | 11kV | 3696 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 1022722 A phase Outage to repair Aph OHM off insulator & cross arm at pole EU-94049. | October | 2013 | 2014Q2 | 2014 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2013-10-02 | N | 88 | N | 5 | N | N | 1.1101 | 39.4971 | 2700.9278
[7 empty] | 15988 | 14482 | 1021744 | 2013-10-01 12:52 | 2013-10-02 17:13 | 1701 | 11kV | 442547 | 732 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn14143 Somersby 11kv Pa17 fdr tripped on Relays: B & C phase Overcurrent Tx2 fault check EFI: Nil Signals: 11kv trip Cause: tree branch brought down OH. found at Bar point removed by Linemsan See 1023783,4,5,6,7,8 exclude 1021744,59,837,2269 | October | 2013 | 2014Q2 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2013-10-01 | N | 604.5724 | N | 40 | Y | Y | 1.1101 | 39.4971 | 323400.2947
[7 empty] | 16195 | 16984 | 1022713 | 2013-10-02 14:22 | 2013-10-02 17:40 | 198 | 11kV | 9382 | 49 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge sectionof Pa1 AB44188 to radial section of fdr interrupted by DOp to allow Linemans to remove tree from HV mains in Kyola Rd mangrove Dam. Cause: Tree/branch on OH Mains. Linemans and DOp removed tree from HV mains in Kyola rd See 1024694,6 Exclude 1022713,25 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-10-02 | N | 191.4694 | N | 5 | N | N | 1.1101 | 39.4971 | 6856.0889
[7 empty] | 15455 | 7983 | 1022810 | 2013-10-02 22:51 | 2013-10-03 00:11 | 80 | 11kV | 136720 | 1709 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | ZN 9252 Jannali - Pnl 2 - Trip/reclose/trip, A phase IOC, timing, lockout, EFI, Field EFIs. Fresh dead possum smoking at the base of PT 9538 Westaward School. ME: 1022810. Withdrawn: 1022812. | October | 2013 | 2014Q2 | 2014 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2013-10-02 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 99910.9434
[7 empty] | 14899 | 1938 | 1022836 | 2013-10-03 07:21 | 2013-10-03 07:45 | 24 | 11kV | 24 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137289 A phase DOLF : 10 Amp Excluded OMS 1022836 | October | 2013 | 2014Q2 | 2014 |  |  |  |  | UG | Not Veg | 2013-10-03 | N | 24 | N | 9 | N | N | 1.1101 | 39.4971 | 17.5385
[7 empty] | 14847 | 1345 | 1022829 | 2013-10-03 06:45 | 2013-10-03 08:05 | 80 | 11kV | 1600 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137291 A phase DOLF : 10 Amp Excluded OMS 1022829 | October | 2013 | 2014Q2 | 2014 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | UG | Not Veg | 2013-10-03 | N | 80 | N | 9 | N | N | 1.1101 | 39.4971 | 1169.2328
[7 empty] | 14710 | 130 | 1022883 | 2013-10-03 08:55 | 2013-10-03 11:02 | 127 | 11kV | 12227 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137294 3 fault operations 3 phase Overcurrent tree branch on mains beyond ABS 42110. Excluded OMS# 1022883 | October | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-10-03 | N | 108.2035 | N | 9 | N | N | 1.1101 | 39.4971 | 8935.131
[7 empty] | 15642 | 10267 | 1023118 | 2013-10-03 12:38 | 2013-10-03 13:49 | 71 | 11kV | 192595 | 2729 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12570 Avoca Zone Pa40 "Davistown" fdr tripped on Signals: 11kv trip Relays: Open/Reclose lockout relay, target 1.2.1 Bph overcurrent ABNORMAL:AB41812 closed RE44982 Bensville Open AB43452 Closed Empire Bay Pa4 Open AB40459 closed EMpire Bay Pa8 Open Cause: tree branch on mains adjacent USL43963 Pomona rd off wards Hill rd See 1024732,5 Exclude 1023118,23,28,47,51,212,32 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2013-10-03 | N | 70.5735 | N | 9 | N | N | 1.1101 | 39.4971 | 140742.7454
[7 empty] | 14776 | 690 | 1023013 | 2013-10-03 11:48 | 2013-10-03 15:05 | 197 | 11kV | 70369 | 685 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 137306 A phase Overcurrent broken insulators at pole AI-90271 between ABS 74980 & 74513. Excluded oms 1023013, 1023222 | October | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-10-03 | N | 102.7285 | N | 9 | N | N | 1.1101 | 39.4971 | 51423.5897
[7 empty] | 14919 | 2063 | 1023162 | 2013-10-03 13:02 | 2013-10-03 15:33 | 150.65 | 11kV | 1205.2 | 8 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | LID 137305 A Phase Line 10A Line DOLF tripped during storms | October | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-10-03 | N | 150.65 | N | 9 | N | N | 1.1101 | 39.4971 | 880.7246
[7 empty] | 15697 | 10992 | 1023151 | 2013-10-03 12:55 | 2013-10-03 15:40 | 165 | 11kV | 24420 | 148 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Ex Zn12570 section of Pa22 @PT13769 Warilda Davistown centre phase HV drop out fuse operated BBLAS 31.5K Cause: Surge arrestor blown. Cut away and PT13769 return to service See 1024742 exclude 1023151,1023212,1023232 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2013-10-03 | N | 165 | N | 9 | N | N | 1.1101 | 39.4971 | 17845.4157
[7 empty] | 14884 | 1772 | 1023264 | 2013-10-03 15:12 | 2013-10-03 17:00 | 108 | 11kV | 540 | 5 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137310 B Phase 40A Line DOLF - tripped during storm Set start time to customer call time | October | 2013 | 2014Q2 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2013-10-03 | N | 108 | N | 9 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 15395 | 7393 | 1023065 | 2013-10-03 12:09 | 2013-10-03 17:15 | 306 | 11kV | 94206 | 1237 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | At Sub 35800 Bankstown Panel 6 "S46101 Bankstown Aux No.1" feeder tripped on: Relays: Earth fault and EFI Signals: 11kv trip, Tx11 Group Earth Field EFI's Abnormal: Sw B @ S6674 Stuart Fairford is closed., LB 1794 is opened. SwB @ Sub 5519 Banks davies is closed, sw A @ S35222 Cahors Arab is opened. Remarks: Lightning/ Surge arrestor. Arrestor at PT2876 Stuart Arab failed. | October | 2013 | 2014Q2 | 2014 | ZN35800:PA6 | ZN35800:PA6 | ZN35800/000006 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-10-03 | N | 76.1568 | N | 9 | N | N | 1.1101 | 39.4971 | 68842.9662
[7 empty] | 15403 | 7470 | 1024243 | 2013-10-04 12:50 | 2013-10-04 13:15 | 25 | 11kV | 175 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Previous Storm | N | LID 137327 3 phase LOOSE X-arm pole WT-20058 | October | 2013 | 2014Q2 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2013-10-04 | N | 25 | N | 3 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 15031 | 3069 | 1023673 | 2013-10-04 16:10 | 2013-10-04 17:34 | 84 | 11kV | 7560 | 90 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137330 1 fault operation 3 phase Overcurrent tree on mains at pole GR-27431 near sub 43933 | October | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | CESSNOCK | OH | Veg | 2013-10-04 | N | 84 | N | 3 | N | N | 1.1101 | 39.4971 | 5524.625
[7 empty] | 16250 | 17524 | 1023883 | 2013-10-05 16:38 | 2013-10-05 17:43 | 65 | 11kV | 40803 | 643 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S.901 Surry Hills - Pnl.1 tripped on: Earth Fault , EFI Field EFIs: S35797, S48601, S8517 Underground Cable fault from S8517 to S35440 | October | 2013 | 2014Q2 | 2014 | ZN901:PA1 | ZN188:PA4 | ZN00188/000004 | SYDNEY | UG | Not Veg | 2013-10-05 | N | 63.4572 | N | 2 | N | N | 1.1101 | 39.4971 | 29817.6289
[7 empty] | 16440 | 19865 | 1023882 | 2013-10-05 19:17 | 2013-10-05 19:31 | 14 | 11kV | 770 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At ZN35370 Galston Section of 11kV ex Panel 10L between SW/B at S35228 to sw/B at S35655 supply manually interrupted Tree branch on Mains See OMS 1023901/900/899/1027283 1023882 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2013-10-05 | N | 14 | N | 2 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 15227 | 5190 | 1023797 | 2013-10-04 22:01 | 2013-10-05 20:30 | 1349 | 11kV | 29323 | 83 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | ZN15005 Belrose Zone section of PA 10 'Forestway Dawes'. Recloser 24722 Forest Crozier tripped on SEF. Cause not ascertained. Possible surge arrestor issue or Recloser 24722 Forest Crozier SEL relay faulty. OMS numbers: 1024502, 1023895, 1024515, 1024508, 1024506, 1024505 1023797, 1023895 | October | 2013 | 2014Q2 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-10-04 | N | 353.2892 | N | 3 | N | N | 1.1101 | 39.4971 | 21428.3835
[7 empty] | 15720 | 11156 | 1023913 | 2013-10-06 03:14 | 2013-10-06 12:32 | 558 | 11kV | 110646 | 1570 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | @Zn13000 Lake Munmorah Pa11 Lake Munmorah Aux tripped, reclosed and locked out on B/C phase, lockout relay, EFI Cause: Possum on UGOH to S12357 Lakeside Leisure Kamila. HV bond off link 40165. Broken ties on feeder See 1024748,9,50 Exclude 1023913,4 | October | 2013 | 2014Q2 | 2014 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Not Veg | 2013-10-06 | N | 70.4752 | N | 4 | N | N | 1.1101 | 39.4971 | 80856.8333
[7 empty] | 15312 | 6545 | 1023979 | 2013-10-06 15:53 | 2013-10-06 17:09 | 76 | 11kV | 49911 | 681 | HV | Wind Blown Debris | Adverse Weather/Environment | UGOH | Unplanned | Unselected | N | ZN 10996 Rockdale - Pnl 4 - Trip/reclose, A & C phase IOC, A phase timed, Earth leakage, timing, lockout, EFI, Field EFIs. UGOH short circuit when plastic blown onto UGOH. ME: 1024439. ME GIS: 1023992. Rest Steps: 1024439, 42. Withdrawn: 1023979, 81, 82, 85. | October | 2013 | 2014Q2 | 2014 | ZN10996:PA4 | ZN10998:PA25 | ZN10998/000025 | BAYSIDE | OH | Veg | 2013-10-06 | N | 73.2907 | N | 4 | N | N | 1.1101 | 39.4971 | 36473.4867
[7 empty] | 16253 | 17531 | 1024006 | 2013-10-06 18:31 | 2013-10-06 19:52 | 81 | 11kV | 71115 | 1073 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14892 Charmhaven Zone 11kV Pa21 tripped on Relays: Pa21 fdr panel- Overcurrent 1.2.1 Taret 51n, Fault check, SEF Tx2 Protection Panel: 11kv fault check Signals: EFI,11kv Trip EFI's S14501 S14236(failed to operate) Cause: 11kv UG fdr fault from S14501 to S14461 to S14577 to S14576 See 1025633,5,6,7 exclude 1024006 | October | 2013 | 2014Q2 | 2014 | ZN14892:PA21 | ZN14892:PA21 | ZN14892/000021 | CENTRAL COAST | UG | Not Veg | 2013-10-06 | N | 66.2768 | N | 4 | N | N | 1.1101 | 39.4971 | 51968.7445
[7 empty] | 16498 | 20404 | 1024008 | 2013-10-06 18:37 | 2013-10-06 20:35 | 118 | 11kV | 2242 | 19 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12640 Umina Zone section of Pa1 @PT14643 Shoalhaven Dulkara Roadside HDO found broken and open circuit. Requires replacement. Cutout required. also refer to 1024008 | October | 2013 | 2014Q2 | 2014 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2013-10-06 | N | 118 | N | 4 | N | N | 1.1101 | 39.4971 | 1638.3875
[7 empty] | 15270 | 6000 | 1024040 | 2013-10-07 03:52 | 2013-10-07 05:06 | 74 | 11kV | 58955 | 818 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137333 2 fault operations A & B phase Overcurrent Excluded OMS 1024040 51AB leg 1. No fault found | October | 2013 | 2014Q2 | 2014 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2013-10-07 | N | 72.0721 | N | 2 | N | N | 1.1101 | 39.4971 | 43082.5751
[7 empty] | 15558 | 8981 | 1024124 | 2013-10-07 17:42 | 2013-10-07 18:20 | 38 | 11kV | 2964 | 78 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | Ex Zn14892 section of Pa3 @PT12656 Oceanview Gilbert, Roadside HV drop out 40A fuse operated. EFI:Zn14892 Charmhaven Pa3, S12298 Cause: Bird flew into PT12656 See 1024125 exclude 1024124 | October | 2013 | 2014Q2 | 2014 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2013-10-07 | N | 38 | N | 2 | N | N | 1.1101 | 39.4971 | 2166.0038
[7 empty] | 16428 | 19571 | 1024142 | 2013-10-08 04:07 | 2013-10-08 05:39 | 92 | 11kV | 12420 | 135 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137334 Burnt dropper at transformer | October | 2013 | 2014Q2 | 2014 | 222:2018 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2013-10-08 | N | 92 | N | 7 | N | N | 1.1101 | 39.4971 | 9076.1697
[7 empty] | 16024 | 14916 | 1024141 | 2013-10-08 01:45 | 2013-10-08 07:20 | 335 | 11kV | 157768 | 1290 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 36 - A phase IOC, Earth Fault, Fault Check, Field EFIs. Underground cable failed in service. Delay restoring S 3557 due to sub vandalism. ME: 1024423. Rest Steps: 1024424, 5, 6, 7. Withdrawn: 1024141. | October | 2013 | 2014Q2 | 2014 | ZN690:PA36 | ZN690:PA36 | ZN00690/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-10-08 | N | 122.3008 | N | 7 | N | N | 1.1101 | 39.4971 | 115292.201
[7 empty] | 14786 | 806 | 1024358 | 2013-10-08 12:47 | 2013-10-08 13:00 | 13 | 11kV | 24648 | 1896 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At S.15005 Belrose, Panel 2 Fdr CB tripped on SEF. Centre phase flicker blade on N/O AB.20287 failed to open when operating | October | 2013 | 2014Q2 | 2014 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Not Veg | 2013-10-08 | N | 13 | N | 7 | N | N | 1.1101 | 39.4971 | 18012.0314
[7 empty] | 16433 | 19701 | 1024360 | 2013-10-08 12:47 | 2013-10-08 13:00 | 13 | 11kV | 14872 | 1144 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At S.15005 Belrose, Panel 2 Fdr CB tripped on SEF. Centre phase flicker blade on N/O AB.20287 failed to open when operating | October | 2013 | 2014Q2 | 2014 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2013-10-08 | N | 13 | N | 7 | N | N | 1.1101 | 39.4971 | 10868.019
[7 empty] | 16169 | 16683 | 1024530 | 2013-10-08 16:34 | 2013-10-08 17:32 | 58 | 11kV | 33988 | 586 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale section of Pa19 @Pole BV1515 below HV LK41116 bond burnt off See 1027077 exclude 1024530 | October | 2013 | 2014Q2 | 2014 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2013-10-08 | N | 58 | N | 7 | N | N | 1.1101 | 39.4971 | 24837.4279
[7 empty] | 16270 | 17663 | 1024480 | 2013-10-08 15:08 | 2013-10-08 21:25 | 377 | 11kV | 2996 | 28 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137343 A & B phase DOLF : 20 Amp Replaced arresters at UGOH poles HS 74038 & HS 74039 Excluded OMS 1024480 & 1024561 | October | 2013 | 2014Q2 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2013-10-08 | N | 107 | N | 7 | N | N | 1.1101 | 39.4971 | 2189.3884
[7 empty] | 15676 | 10755 | 1024572 | 2013-10-08 17:27 | 2013-10-08 23:40 | 373 | 11kV | 6281 | 32 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137344 2 fault operations Sensitive Earth Fault Mains down between poles WB 90001 & WB 91947 Narone Creek Rd Excluded OMS 1024572 | October | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-10-08 | N | 196.2812 | N | 7 | N | N | 1.1101 | 39.4971 | 4589.9695
[7 empty] | 15934 | 13458 | 1024631 | 2013-10-09 04:39 | 2013-10-09 06:08 | 89 | 11kV | 137994 | 1820 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 25 - C phase OC, IOC, Fault Check, EFI. Section of Underground feeder failed in service. Section from Campsie Pnl 25 to S 1976 to S 3773 to S 3834. ME: 1025352. Rest Steps: 1025354, 5. Withdrawn: 1024631. | October | 2013 | 2014Q2 | 2014 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-10-09 | N | 75.8209 | N | 2 | N | N | 1.1101 | 39.4971 | 100841.9451
[7 empty] | 15372 | 7082 | 1024936 | 2013-10-09 14:40 | 2013-10-09 15:16 | 36 | 11kV | 61668 | 1713 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @Zn2196 Milperra 11kv Pnl 25 "Turvey River" feeder tripped on A and B phase overcurrent. Signals: 11kv trip Field EFI's: S4684 and S4276 Remarks: Animals/birds. Bird flew into mains at cnr. Mackenzie and Bishop st in Revesby. Repeat outage, urgent attention required. | October | 2013 | 2014Q2 | 2014 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-10-09 | N | 36 | N | 2 | N | N | 1.1101 | 39.4971 | 45065.1555
[7 empty] | 15240 | 5528 | 1025109 | 2013-10-10 08:03 | 2013-10-10 09:50 | 107.05 | 11kV | 11668.45 | 109 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 137371 A phase DOLF : 31 Amp Aph DOLF carrier top contact burnt up suspect DOLF mount contacts. DOLF replaced & 3 sets interconnecting LV links closed for support. Refered to Field Services Maitland | October | 2013 | 2014Q2 | 2014 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2013-10-10 | N | 107.05 | N | 12 | N | N | 1.1101 | 39.4971 | 8526.9591
[7 empty] | 15505 | 8524 | 1025162 | 2013-10-10 10:06 | 2013-10-10 13:00 | 174 | 11kV | 68296 | 913 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Hot >35C | N | At S80 Chatswood Panel 25 tripped reclosed tripped and locked out on Relays: C phase O/C, Earth Fault, EFI, Reclose and Lockout Signals: 11kV trip, Zone Earth, Tx11 Group Earth Cause: Crane in 11kV outside 39 Mindarie St Lane Cove between ZB3012 to SWA at S5353 Mobray Cumberland to SWB at S47085 Willandra Mowbray tee S5510 Epping Moore See OMS 1027313 1027316 1027315 1025162 | October | 2013 | 2014Q2 | 2014 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Not Veg | 2013-10-10 | N | 74.8039 | N | 12 | N | N | 1.1101 | 39.4971 | 49908.7024
[7 empty] | 15711 | 11054 | 1025277 | 2013-10-10 12:35 | 2013-10-10 13:29 | 54 | 11kV | 29753 | 572 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137374 1 fault operation A phase A/R function off for TFB Tree branch on mains adjacent pole IT-70057 Carrington St , West Wallsend Excluded OMS 1025277, 1025287, 1025295 | October | 2013 | 2014Q2 | 2014 | 213:33777 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Veg | 2013-10-10 | N | 52.0157 | N | 12 | N | N | 1.1101 | 39.4971 | 21742.6148
[7 empty] | 16076 | 15727 | 1025301 | 2013-10-10 13:37 | 2013-10-10 14:15 | 38 | 11kV | 2090 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | Ex Zn12690 Berkeley Vale section of Pa12 @PT48611 Boyce Warner, Middle Phase 63A BB HDO operated Cause: fuse fatigue DOp reports fuse pulled away from crimp See 1027057 exclude 1025301 | October | 2013 | 2014Q2 | 2014 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Not Veg | 2013-10-10 | N | 38 | N | 12 | N | N | 1.1101 | 39.4971 | 1527.3104
[7 empty] | 15028 | 3045 | 1025300 | 2013-10-10 13:18 | 2013-10-10 14:50 | 92 | 11kV | 1380 | 15 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 137377 HV DROPPER BURNED OFF DOLF | October | 2013 | 2014Q2 | 2014 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | OH | Not Veg | 2013-10-10 | N | 92 | N | 12 | N | N | 1.1101 | 39.4971 | 1008.4633
[7 empty] | 15196 | 4565 | 1025417 | 2013-10-10 16:14 | 2013-10-10 17:15 | 61 | 11kV | 81569 | 1421 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | ZN 9118 Cronulla - Pnl 22 - Trip/reclose/trip, Earth Fault, timing, lockout, Field EFIs. Suspect cable fault between S 9180 and S 9305. ME: 1025663. Rest Step: 1025664. Withdrawn: 1025417. | October | 2013 | 2014Q2 | 2014 | ZN9118:PA22 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | UG | Not Veg | 2013-10-10 | N | 57.4025 | N | 12 | N | N | 1.1101 | 39.4971 | 59608.2193
[7 empty] | 16022 | 14901 | 1025357 | 2013-10-10 14:49 | 2013-10-10 17:24 | 155 | 11kV | 94630 | 1074 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | At Zn 15001 Brookvale ZN PA6 'Windourne Rd 36' tripped. Zone relays: IOC (50T B), EFI, FC. DC EFI's indicated at S16892, S15189, 16948, S16027, S16636, S16816, S50675, S16933. In section of 11kV feeder ex Brookvale Zn Panel 6L between SW/B S16933 Burne Mooramba and SW/B S17046 Francis Lewis the UGOH on tee off to S16278 Mooramba Rd 19 flashed over. UGOH fault short circuit. OMS numbers: 1025743, 1025744, 1025357, 1025358, 1025357 | October | 2013 | 2014Q2 | 2014 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | Unknown | Unknown | 2013-10-10 | N | 88.1099 | N | 12 | N | N | 1.1101 | 39.4971 | 69152.8129
[7 empty] | 15873 | 12885 | 1025466 | 2013-10-10 19:14 | 2013-10-10 21:20 | 126 | 11kV | 67884 | 1423 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137379 1 fault operation Sensitive Earth Fault NOTE: Third trip in 2 weeks. Daylight patrol required. Excluded OMS 1025466 & 1025467 | October | 2013 | 2014Q2 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2013-10-10 | N | 47.7048 | N | 12 | N | N | 1.1101 | 39.4971 | 49607.625
[7 empty] | 15203 | 4662 | 1025332 | 2013-10-10 14:00 | 2013-10-10 23:29 | 569 | 11kV | 6028 | 12 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Hot >35C | N | At Sub 4100 Beresford Coventry H.V (HRC B Phase, 90Amp) Tx Sw tripped off Transformer Remarks: Transformer found to have a HR joint on B phase connection due to loose connections. Direct Distributors supply maintained by generators durings outages | October | 2013 | 2014Q2 | 2014 | ZN2835:PA41 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2013-10-10 | N | 502.3333 | N | 12 | N | N | 1.1101 | 39.4971 | 4405.0846
[7 empty] | 16132 | 16293 | 1025487 | 2013-10-10 20:26 | 2013-10-10 23:35 | 189 | 11kV | 161582 | 2061 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn 2835 Burwood Zone 11kv C/B Pnl 23 'Sub 3007 Wentworth Hornsey' tripped on Relays: Earth fault, Fault check, EFI Signals: Group earth Tx2, 11kv trip Field EFI's: S3007, S48182 Remarks: 11kv underground feeder fault from Sw/B S48182 Oxford Norwood to Sw/B at Sub 2764 wynne Ave to Sw/A at Sub 136 Sym Ave | October | 2013 | 2014Q2 | 2014 | ZN2835:PA23 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2013-10-10 | N | 78.3998 | N | 12 | N | N | 1.1101 | 39.4971 | 118079.3597
[7 empty] | 15594 | 9500 | 1025508 | 2013-10-10 22:01 | 2013-10-10 23:35 | 94 | 11kV | 196676 | 3278 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At Zn2835 Burwood, 11kv Panel 10 'Russell Wentworth' tripped on earth fault with fault check. Signals: Tx2 GE, 11kv trip and efi Field EFI's: Nil Abnormal: Sw/A closed at S294 Angel rd, with Sw/A openat S136 Sym Ave (defective fdr) Sw/A closed at S324 newton Rd, with Sw/A open at S2011 merley Rd (defective RMI at S4100) Remarks: UG fault between Zn2835 pnl10 to S3315. Note: Abnormal switching after fault on Pnl 23 at Zn2835 | October | 2013 | 2014Q2 | 2014 | ZN2835:PA10 | ZN2835:PA10 | ZN02835/000010 | BURWOOD | UG | Not Veg | 2013-10-10 | N | 59.9988 | N | 12 | N | N | 1.1101 | 39.4971 | 143725.0198
[7 empty] | 15783 | 11938 | 1025522 | 2013-10-10 23:06 | 2013-10-10 23:49 | 43 | 11kV | 13803 | 321 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Wind Strong | N | At Zn35800 Bankstown 11kv Panel 16 'Canterbury Fair' tripped on IOC and earth fault. Alarms; EFI and 11kv trip Field EFI's operated at S5149, S4115 and S5412 Remarks: Tree/branch on OH mains. Dop removed branch from mains at 58 Hoskins Ave adj AB 2487. No after hours access to S5112 (did not reset efi) | October | 2013 | 2014Q2 | 2014 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-10-10 | N | 43 | N | 12 | N | N | 1.1101 | 39.4971 | 10086.8253
[7 empty] | 16296 | 17968 | 1025546 | 2013-10-11 02:01 | 2013-10-11 03:40 | 99 | 11kV | 197604 | 1996 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Wind | N | At Zn36300 Balgowlah North Panel 3 'S17119 Jackson White' tripped on relays: 3 phase IOC and EFI. Field EFIs - Nil. DOp patrolled feeder and found possum dead on LB 61276. | October | 2013 | 2014Q2 | 2014 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2013-10-11 | N | 99 | N | 15 | N | N | 1.1101 | 39.4971 | 144403.1749
[7 empty] | 15584 | 9298 | 1025543 | 2013-10-11 01:25 | 2013-10-11 05:50 | 265 | 11kV | 20670 | 78 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | Ex Zn12620 Noraville section of pa13 @PT11211 View Point Main HDO bond burnt off roadside See 1027146 exclude 1025543 | October | 2013 | 2014Q2 | 2014 | ZN12620:PA13 | ZN12620:PA13 | ZN12620/000013 | CENTRAL COAST | OH | Not Veg | 2013-10-11 | N | 265 | N | 15 | N | N | 1.1101 | 39.4971 | 15105.0263
[7 empty] | 16355 | 18619 | 1025548 | 2013-10-11 02:18 | 2013-10-11 08:15 | 357 | 11kV | 48506 | 414 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn12570 Avoca Pa26 tripped on Cph IOC EFI Alarms: 11kv trip Abnormal: AB40413 closed w/ LB41272 & AB44153 Open. But Wamberal Pa1 also out. restored according to Wamberal outage report Cause not ascertained. DOp patrolled feeder up to LB48409. DOp Baldwin patrolled nothing found. See 1028657,9 exclude 1025548,62,7158,61 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Veg | 2013-10-11 | N | 117.1643 | N | 15 | N | N | 1.1101 | 39.4971 | 35446.7541
[7 empty] | 16345 | 18488 | 1025660 | 2013-10-11 09:25 | 2013-10-11 09:53 | 28 | 11kV | 1428 | 51 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137384 EMERGENCY SI M0500.LOW 11KV MAINS BETWEEN POLES GU-54312 & GU-54331. | October | 2013 | 2014Q2 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-10-11 | N | 28 | N | 15 | N | N | 1.1101 | 39.4971 | 1043.5403
[7 empty] | 16090 | 15913 | 1025537 | 2013-10-11 00:06 | 2013-10-11 12:38 | 752 | 11kV | 379234 | 1179 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn14144 Wamberal Pa1 tripped and reclosed & locked out on EFI, LO, Timer, A&B IOC Alarms: Tx2 GE Cause: Tree/Branch brought down OH in Dover Rd Adjacent USL 40416 (2 spans 11kv cut away and safe above USL40416) also LV mains isolated at PT13683 and PT12114 (HV into LV) See 1027101,3,4,5,6,7 Exclude 1025537,8,41,54,6,8,9,614 | October | 2013 | 2014Q2 | 2014 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Veg | 2013-10-11 | N | 321.6573 | N | 15 | N | N | 1.1101 | 39.4971 | 277133.0217
[7 empty] | 16268 | 17632 | 1025823 | 2013-10-11 12:55 | 2013-10-11 13:35 | 40 | 11kV | 65600 | 1640 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S1673 Turramurra Panel 11 Tripped reclosed tripped and locke dout on Relays: A and B phase Overcurrent Cause: Tree branch on OH mains in commenarra parkway near Evans St Turramurra South | October | 2013 | 2014Q2 | 2014 | ZN1673:PA11 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2013-10-11 | N | 40 | N | 15 | N | N | 1.1101 | 39.4971 | 47938.5451
[7 empty] | 16491 | 20349 | 1025763 | 2013-10-11 11:48 | 2013-10-11 13:40 | 112 | 11kV | 13776 | 123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of pa10 Between USL40139 to LB45068 interrupted for safety remove tree from 11kv fdr Tree in contact with 11kv. Interrupted for safety to remove trees See 1027352 exclude 1025763 | October | 2013 | 2014Q2 | 2014 | ZN14891:PA10 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Veg | 2013-10-11 | N | 112 | N | 15 | N | N | 1.1101 | 39.4971 | 10067.0945
[7 empty] | 15091 | 3578 | 1025551 | 2013-10-11 04:35 | 2013-10-11 14:56 | 621 | 11kV | 78819 | 515 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn14891 Wyong 11kv Pa20 fdr tripped on A&B overcurrent Cause: Tree/branch brought down OH corner Hue Hue & Sparkes rds See 1027318,23,4,5 Exclude 1025551,60,640 | October | 2013 | 2014Q2 | 2014 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2013-10-11 | N | 153.0466 | N | 15 | N | N | 1.1101 | 39.4971 | 57598.6004
[7 empty] | 16199 | 17062 | 1025941 | 2013-10-11 14:50 | 2013-10-11 16:25 | 95 | 11kV | 79206 | 1039 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 137387 3 fault operations Earth fault UG cable fault between Sw 36080 & Sw 55116. Excluded OMS 1025941 | October | 2013 | 2014Q2 | 2014 | 216:10729 | 216:10729 | ZN00216/010729 | LAKE MACQUARIE | UG | Not Veg | 2013-10-11 | N | 76.2329 | N | 15 | N | N | 1.1101 | 39.4971 | 57881.4086
[7 empty] | 14880 | 1759 | 1025580 | 2013-10-11 07:06 | 2013-10-11 16:50 | 584 | 11kV | 1168 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa2 @PT11214 Morgan Pacific 1.5 Middle Phase 20K HDO operated See fuse failure at crimp See 1027346 exclude 1025580 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA2 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-10-11 | N | 584 | N | 15 | N | N | 1.1101 | 39.4971 | 853.5399
[7 empty] | 16312 | 18116 | 1025848 | 2013-10-11 16:51 | 2013-10-11 18:41 | 110 | 11kV | 11880 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of Pa1 @RE44602 Ourimbah Ck Rd Interrupted for safety reasons. To remove branch from HV mains btw PT13621 & PT13622 | October | 2013 | 2014Q2 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-10-11 | N | 110 | N | 15 | N | N | 1.1101 | 39.4971 | 8681.5536
[7 empty] | 16478 | 20252 | 1027578 | 2013-10-11 16:15 | 2013-10-11 19:45 | 210 | 11kV | 40740 | 194 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 137390 EMERGENCY ISOLATION TO REPLACE POLE IP-82880. SEE SI.M0502 | October | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2013-10-11 | N | 210 | N | 15 | N | N | 1.1101 | 39.4971 | 29771.5904
[7 empty] | 14997 | 2851 | 1026026 | 2013-10-11 19:00 | 2013-10-11 22:00 | 180 | 11kV | 12600 | 70 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 137388 Isolate to replace faulty insulators See S.I. M503A Excluded OMS 1026026 | October | 2013 | 2014Q2 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2013-10-11 | N | 180 | N | 15 | N | N | 1.1101 | 39.4971 | 9207.7084
[7 empty] | 16208 | 17121 | 1026044 | 2013-10-11 21:24 | 2013-10-11 22:25 | 61 | 11kV | 671 | 11 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137389 Isolate to repair wire off pin at pole IT-22039 | October | 2013 | 2014Q2 | 2014 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2013-10-11 | N | 61 | N | 15 | N | N | 1.1101 | 39.4971 | 490.347
[7 empty] | 15506 | 8529 | 1026046 | 2013-10-11 21:37 | 2013-10-11 22:30 | 53 | 11kV | 91425 | 1725 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex S 10995 Riverwood - AB 31327 - Footphath phase contact went high resistance. Air Break Switch went High resistance. Opened and warning tagged. ME: 1026879. ME GIS: 1026049. Withdrawn: 1026046, 47, 48, 50 | October | 2013 | 2014Q2 | 2014 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2013-10-11 | N | 53 | N | 15 | N | N | 1.1101 | 39.4971 | 66810.6934
[7 empty] | 15488 | 8288 | 1025821 | 2013-10-12 09:01 | 2013-10-12 10:28 | 87 | 11kV | 5321 | 171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.384 Camperdown Pnl.36 - Tripped on: B phase Overcurrent, Timing, EFI Field EFIs: S1306, S48306 UG cable fault between S48306 (Sw B) to S2497 (Sw A) to S486 (Sw A) to S8985 (Sw A) to S2472 (Sw D) see 1026889 1026892 | October | 2013 | 2014Q2 | 2014 | ZN384:PA36 | ZN384:PA81 | ZN00384/000081 | SYDNEY | UG | Not Veg | 2013-10-12 | N | 31.117 | N | 4 | N | N | 1.1101 | 39.4971 | 3888.4299
[7 empty] | 14922 | 2078 | 1026072 | 2013-10-12 02:57 | 2013-10-12 10:50 | 473 | 11kV | 76271 | 1450 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 137399 1 fault operation Earth fault Replaced L/A UGOH pole JS-50358 Old Punt Rd. Excluded OMS 1026072 | October | 2013 | 2014Q2 | 2014 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | Unknown | Unknown | 2013-10-12 | N | 52.6007 | N | 4 | N | N | 1.1101 | 39.4971 | 55736.5972
[7 empty] | 15667 | 10643 | 1026206 | 2013-10-12 23:34 | 2013-10-13 00:22 | 48 | 11kV | 128688 | 2681 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | Unselected | N | @Zn12620 Noraville Pa1 fdr tripped on Relays:Left Leg A&B phase Overcurrent, EFI Signals: 11kv trip Cause: Possum frying @ Top of RE41873 See 1026206 exclude 1026209 | October | 2013 | 2014Q2 | 2014 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2013-10-12 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 94041.3947
[7 empty] | 16012 | 14761 | 1026200 | 2013-10-12 22:15 | 2013-10-13 02:00 | 225 | 11kV | 325648 | 2288 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 10999 Kogarah - Pnl 29 - Earth fault, EFI, Field EFIs. Suspect underground cable fault from S 10866 Parker Railway to AB 30029. DOp unable to open USL 30797 due to height to determine which section of UG is faulty. ME: 1027040. Rest Step: 1027042. Withdrawn: 1026200. | October | 2013 | 2014Q2 | 2014 | ZN10999:PA29 | ZN10999:PA29 | ZN10999/000029 | BAYSIDE | UG | Not Veg | 2013-10-12 | N | 142.3287 | N | 4 | N | N | 1.1101 | 39.4971 | 237973.9534
[7 empty] | 15279 | 6223 | 1026306 | 2013-10-13 12:24 | 2013-10-13 13:13 | 49 | 11kV | 45896 | 1350 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 137417 2 fault operations 3 phase Overcurrent remove tree branch pole IV-30911. Excluded OMS 1026306 | October | 2013 | 2014Q2 | 2014 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Veg | 2013-10-13 | Y | 33.997 | N | 14 | N | Y | 1.1101 | 39.4971 | 33539.4431
[7 empty] | 16152 | 16496 | 1026308 | 2013-10-13 12:30 | 2013-10-13 14:02 | 92 | 11kV | 75440 | 820 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | At S35370 Galston - Panel 4 Tripped Abnormal switching - CP555 ArcadiaClosed and AB 275 Open and Defective Cause: Tree branch on 11kV mains O/S 24 Mansfield Rd See OMS 1026957 1026340/346/351/358/422/410/367/349/339 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-10-13 | Y | 92 | N | 14 | N | Y | 1.1101 | 39.4971 | 55129.3269
[7 empty] | 15631 | 10125 | 1026375 | 2013-10-13 13:22 | 2013-10-13 14:04 | 42 | 11kV | 22531 | 549 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | Wind | Y | Zn14891 Wyong Pa20 Warnervale West Railway fdr tripped on SEF ABNORMAL: RE45070 closed with LK43114 open (defective on Pa16) CP45203 Butt Gas Generator Open Cause: @LK43350 fottpath bond off after branch on mains See 1027439 exclude 1026375 | October | 2013 | 2014Q2 | 2014 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2013-10-13 | N | 41.0401 | N | 14 | N | N | 1.1101 | 39.4971 | 16464.9902
[7 empty] | 14929 | 2132 | 1026276 | 2013-10-13 13:19 | 2013-10-13 14:08 | 49 | 11kV | 49 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Bond | Unplanned | Wind | Y | LID 137425 Live line clamp burned off - also refer to OMS 1026276 | October | 2013 | 2014Q2 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-10-13 | N | 49 | N | 14 | N | N | 1.1101 | 39.4971 | 35.8078
[7 empty] | 15746 | 11610 | 1026314 | 2013-10-13 12:28 | 2013-10-13 14:29 | 121 | 11kV | 137214 | 1134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | At S16373 Turramurra Panel 18 Tripped on B and C phase IOC Cause not ascertained for outage - Wind storm at the time of interruption See OMS 1026314 1026354 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2013-10-13 | Y | 121 | N | 14 | N | Y | 1.1101 | 39.4971 | 100271.9441
[7 empty] | 14829 | 1237 | 1026331 | 2013-10-13 12:44 | 2013-10-13 14:29 | 105 | 11kV | 4935 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 137423 1 Fault operations, overcurrent. Full Patrol by J Dallen - no cause found | October | 2013 | 2014Q2 | 2014 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2013-10-13 | Y | 105 | N | 14 | N | Y | 1.1101 | 39.4971 | 3606.3524
[7 empty] | 16035 | 15139 | 1026316 | 2013-10-13 12:45 | 2013-10-13 14:49 | 124 | 11kV | 35288 | 1503 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | LID 137418 1 fault operation Earth fault Also see report 137412, Fdr was feeding part of Fdr 82133 as CB 82133 was not closing. Excluded OMS 1026316 | October | 2013 | 2014Q2 | 2014 | 239:82129 | 239:82129 | ZN00239/082129 | LAKE MACQUARIE | OH | Veg | 2013-10-13 | Y | 23.4784 | N | 14 | N | Y | 1.1101 | 39.4971 | 25787.4296
[7 empty] | 16160 | 16596 | 1026275 | 2013-10-13 11:57 | 2013-10-13 16:00 | 243 | 11kV | 34340 | 491 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | @Zn14891 Wyong Pa16 tripped on Cphase timed overcurrent, reclose timer, lockout and earth fault check Signals:Tx2 Group Earth and EFI Cause: Tree branch brought down OH. Wires down at 275 Bruce Cres, Wallarah between USL43026 and USL43114 mains to repair with DOp See 1027372,5 exclude 1026275 | October | 2013 | 2014Q2 | 2014 | ZN14891:PA16 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Veg | 2013-10-13 | N | 69.9389 | N | 14 | N | N | 1.1101 | 39.4971 | 25094.6591
[7 empty] | 15025 | 3018 | 1026444 | 2013-10-13 13:46 | 2013-10-13 16:01 | 135 | 11kV | 31185 | 231 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex Zn12630 Peats Ridge section of Pa1 Grants Rd @RE44995 Kulnura tripped and reclosed and locke dout on ABC Phase overcurrent. Tree branch on Mains. | October | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-10-13 | N | 135 | N | 14 | N | N | 1.1101 | 39.4971 | 22789.0782
[7 empty] | 15327 | 6605 | 1026215 | 2013-10-13 04:14 | 2013-10-13 16:30 | 736.4833 | 11kV | 22830.9833 | 31 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Wind | Y | At Auto Link 2013 (Ex Panel 18 berowra Waters) 16A fuse blown. Cause: Possum found at the base of auto links BYpass ABS to restore supply. See OMS 1026215 7061 7056 7052 1026222 1026228 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2013-10-13 | Y | 736.4833 | N | 14 | N | Y | 1.1101 | 39.4971 | 16684.2092
[7 empty] | 15311 | 6541 | 1026247 | 2013-10-13 10:28 | 2013-10-13 17:20 | 412 | 11kV | 581059 | 1635 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | LID 137412 2 fault operationsA phase Earth fault TFB. Problems closing Sw 82133. Fdr patrolled/sectionalised no fault found. Excluded OMS 1026247 | October | 2013 | 2014Q2 | 2014 | 239:82133 | 239:82133 | ZN00239/082133 | LAKE MACQUARIE | OH | Veg | 2013-10-13 | Y | 355.3878 | N | 14 | N | Y | 1.1101 | 39.4971 | 424620.7789
[7 empty] | 16017 | 14868 | 1026479 | 2013-10-13 12:28 | 2013-10-13 18:10 | 342 | 11kV | 11196 | 53 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | Y | At S35736 Meadowbank Park interrupted from CP337 Cause: Above section interruption interrupted to isolate pole PA63922 on fire See OMS 1027112 1026479 1026508 1026519 1026500 | October | 2013 | 2014Q2 | 2014 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Not Veg | 2013-10-13 | N | 211.2453 | N | 14 | N | N | 1.1101 | 39.4971 | 8181.7066
[7 empty] | 16282 | 17825 | 1026559 | 2013-10-13 17:40 | 2013-10-13 18:30 | 50 | 11kV | 800 | 16 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind | Y | LID 137426 Interruption to repair 11kV OHM off pin at pole JS-50242. Less than 4m above ground. Evidence of vehicle contacting pole. Excluded OMS No. 1026559 | October | 2013 | 2014Q2 | 2014 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | OH | Not Veg | 2013-10-13 | N | 50 | N | 14 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 15292 | 6343 | 1026259 | 2013-10-13 11:27 | 2013-10-13 18:35 | 427.7 | 11kV | 23523.5 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 137428 1 Fault operations - single Phase Tree on Mains - MN-82901 | October | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-10-13 | Y | 427.7 | N | 14 | N | Y | 1.1101 | 39.4971 | 17190.28
[7 empty] | 15323 | 6595 | 1026291 | 2013-10-13 12:18 | 2013-10-13 19:05 | 407 | 11kV | 73225 | 1721 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At S15005 Belrose Zone Panel 8 "French's Forest" fdr tripped on relays: earth fault, SEL, EFI, Fault Check. Field EFIs tripped: S46711, S46712 Tree/ branch brought down several bays of 11kV and 415V mains in Burraloo St French's Forest. OMS numbers: 1027086, 1027087, 1026291, 1026341 | October | 2013 | 2014Q2 | 2014 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | OH | Veg | 2013-10-13 | N | 42.5479 | N | 14 | N | N | 1.1101 | 39.4971 | 53510.6702
[7 empty] | 15017 | 2953 | 1026595 | 2013-10-13 18:37 | 2013-10-13 20:03 | 86 | 11kV | 192576 | 2418 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Hot >35C | Y | LID 137429 1 fault operation B phase Earth fault Excluded OMS 1026595 | October | 2013 | 2014Q2 | 2014 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | UG | Not Veg | 2013-10-13 | Y | 79.6427 | N | 14 | N | Y | 1.1101 | 39.4971 | 140728.8608
[7 empty] | 15281 | 6236 | 1026614 | 2013-10-13 19:13 | 2013-10-13 21:00 | 107 | 11kV | 26984 | 263 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 137432 Overcurrent; Earth fault No cause found Excluded OMS 1026614 | October | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-10-13 | N | 102.6008 | N | 14 | N | N | 1.1101 | 39.4971 | 19719.1113
[7 empty] | 15061 | 3327 | 1026646 | 2013-10-13 20:13 | 2013-10-13 21:35 | 82 | 11kV | 69933 | 1191 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 137431 1 fault operation 3 phase Overcurrent Tappings blown off at UGOH JU_61528. Excluded oms 1026646. | October | 2013 | 2014Q2 | 2014 | 202:34245 | 202:34245 | ZN00202/034245 | NEWCASTLE | OH | Not Veg | 2013-10-13 | Y | 58.7179 | N | 14 | N | Y | 1.1101 | 39.4971 | 51104.9737
[7 empty] | 14715 | 166 | 1027424 | 2013-10-13 20:09 | 2013-10-13 21:38 | 89 | 11kV | 70755 | 795 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 137433 1 fault operation C phase Overcurrent Fdr patrolled and closed OK. TFB. | October | 2013 | 2014Q2 | 2014 | 258:80791 | 258:80791 | ZN00258/080791 | NEWCASTLE | OH | Veg | 2013-10-13 | Y | 89 | N | 14 | N | Y | 1.1101 | 39.4971 | 51705.6671
[7 empty] | 16015 | 14795 | 1026658 | 2013-10-13 20:26 | 2013-10-13 21:40 | 74 | 11kV | 64010 | 865 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Wind | Y | At S1673 Turramurra Panel 13 tripped on Relays: IOC A and B phase Signals: 11kV trip, Protection Trip, IOC A + B phase Cause: Tree brancg at UGOH in Grosvenor Near Barton St DOp Cleared Tree | October | 2013 | 2014Q2 | 2014 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Veg | 2013-10-13 | Y | 74 | N | 14 | N | Y | 1.1101 | 39.4971 | 46776.62
[7 empty] | 15933 | 13442 | 1026604 | 2013-10-13 18:49 | 2013-10-13 22:48 | 239 | 11kV | 73467 | 310 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 137434 1 Fault operations, overcurrent, feeder patrolled and no cause found also refer to 102277704, 1027705, 1027706 and 1027710 Excluded 1026604 | October | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-10-13 | N | 236.9903 | N | 14 | N | N | 1.1101 | 39.4971 | 53687.5167
[7 empty] | 16006 | 14690 | 1026623 | 2013-10-13 19:34 | 2013-10-13 23:00 | 206.1 | 11kV | 3091.5 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 137437 A & C phase DOLF : 20 Amp Branch found across mains. Excluded OMS No. 1026638 | October | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2013-10-13 | N | 206.1 | N | 14 | N | N | 1.1101 | 39.4971 | 2259.177
[7 empty] | 16379 | 18833 | 1026701 | 2013-10-13 22:05 | 2013-10-13 23:02 | 57 | 11kV | 46854 | 822 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 137439 1 fault operation A & B phase Overcurrent | October | 2013 | 2014Q2 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2013-10-13 | Y | 57 | N | 14 | N | Y | 1.1101 | 39.4971 | 34239.5212
[7 empty] | 15283 | 6264 | 1026666 | 2013-10-13 20:39 | 2013-10-13 23:36 | 177 | 11kV | 43542 | 246 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | At Recloser 421 Crosslands Rd Tripped reclosed tripped and locked out on overload trip Cause: Tree branch across 11kV at #4 Megan Rd Galston See OMS 1026666 1026691 1026664 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2013-10-13 | Y | 177 | N | 14 | N | Y | 1.1101 | 39.4971 | 31819.2093
[7 empty] | 15477 | 8202 | 1026708 | 2013-10-13 22:22 | 2013-10-14 00:10 | 107.6833 | 11kV | 3338.1833 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 137436 B & C phase DOLF : 40 Amp Please patrol feeder CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | October | 2013 | 2014Q2 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2013-10-13 | Y | 107.6833 | N | 14 | N | Y | 1.1101 | 39.4971 | 2439.4459
[7 empty] | 15481 | 8254 | 1026755 | 2013-10-13 23:30 | 2013-10-14 00:13 | 43 | 11kV | 43172 | 1004 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | @Zn12570 Avoca section of Pa21 LB49826 fdr from CP41397 Karalta rd tripped reclosed and locked out on OC Cause: tree/branch on OH Mains near AB44656 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA21 | ZN12580:PA2 | ZN12580/000002 | CENTRAL COAST | OH | Veg | 2013-10-13 | N | 43 | N | 14 | N | N | 1.1101 | 39.4971 | 31548.8242
[7 empty] | 14861 | 1534 | 1026400 | 2013-10-13 14:21 | 2013-10-14 00:30 | 609 | 11kV | 90132 | 148 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 137440 3 phase dist fuse : 400 Amp Tree branch fell on LV OHM on Cct 58344. 11kV isolated to work on LV beneath. | October | 2013 | 2014Q2 | 2014 | 238:34136 | 238:34136 | ZN00238/034136 | MAITLAND | OH | Veg | 2013-10-13 | Y | 609 | N | 14 | N | Y | 1.1101 | 39.4971 | 65865.8072
[7 empty] | 15454 | 7967 | 1026746 | 2013-10-13 23:23 | 2013-10-14 01:15 | 111.9 | 11kV | 5818.8 | 52 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Wind Storm | Y | At PT1809 Billyard Young Road side and middle phase HV DOPF blown Cause: Suspect TC failure at PT1809 supply restore via lv parallel See OMS 1026747 1026754 1026746 1026759 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | UG | Not Veg | 2013-10-13 | Y | 111.9 | N | 14 | N | Y | 1.1101 | 39.4971 | 4252.2074
[7 empty] | 15531 | 8799 | 1027757 | 2013-10-13 20:57 | 2013-10-14 01:25 | 268 | 11kV | 95824 | 360 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 137442 1 fault operation Fdr patrolled No fault found. Excluded OMS No. 1026678 | October | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Veg | 2013-10-13 | Y | 266.1778 | N | 14 | N | Y | 1.1101 | 39.4971 | 70025.3529
[7 empty] | 16114 | 16102 | 1026799 | 2013-10-14 01:09 | 2013-10-14 01:50 | 41 | 11kV | 3485 | 85 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Ex Zn14144 Wamberal section of Pa7 @PT11286 Bluebell DILL 50Amp roadside HDO fuse blown due to Possum also refer to 1026799 | October | 2013 | 2014Q2 | 2014 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Not Veg | 2013-10-14 | N | 41 | N | 8 | N | N | 1.1101 | 39.4971 | 2546.7352
[7 empty] | 16060 | 15467 | 1026770 | 2013-10-13 23:55 | 2013-10-14 02:09 | 134 | 11kV | 117442 | 965 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | At S1287 Revesby P4 the Tower Condon fdr tripped reclosed and locked out on B/C phase IOC Remarks: cause not ascertained | October | 2013 | 2014Q2 | 2014 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-10-13 | N | 121.7016 | N | 14 | N | N | 1.1101 | 39.4971 | 85823.1496
[7 empty] | 15119 | 3893 | 1026679 | 2013-10-13 20:58 | 2013-10-14 02:30 | 332 | 11kV | 332 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 137449 Single phase DOLF : 10 Amp Replcae faulty Tx. Excluded OMS 1026679 | October | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2013-10-13 | N | 332 | N | 14 | N | N | 1.1101 | 39.4971 | 242.6158
[7 empty] | 15190 | 4478 | 1026704 | 2013-10-13 22:17 | 2013-10-14 03:28 | 311 | 11kV | 622 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 137451 Single phase DOLF : 5 Amp Replaced 5A line DOLF and 5A sub DOLF. Sub DOLF blew when line was re-energized. Excluded OMS No. 1026704 | October | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-10-13 | N | 311 | N | 14 | N | N | 1.1101 | 39.4971 | 454.5393
[7 empty] | 15080 | 3498 | 1026632 | 2013-10-13 19:55 | 2013-10-14 04:45 | 530 | 11kV | 40579 | 161 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 137450 3 fault operations 11kV OHM found on ground near Moon Mountain sub 52384. Excluded OMS 1026632; | October | 2013 | 2014Q2 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2013-10-13 | Y | 252.0435 | N | 14 | N | Y | 1.1101 | 39.4971 | 29653.9363
[7 empty] | 15491 | 8320 | 1026627 | 2013-10-13 19:44 | 2013-10-14 06:10 | 626 | 11kV | 42147 | 230 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 137435 Single phase DOLF : 16 Amp Wire across Rd at pole MK-70001. Excluded OMS No. 1026627, 1026692, 1026639, 1026756. | October | 2013 | 2014Q2 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2013-10-13 | Y | 183.2478 | N | 14 | N | Y | 1.1101 | 39.4971 | 30799.7845
[7 empty] | 16257 | 17539 | 1026816 | 2013-10-14 04:59 | 2013-10-14 06:35 | 96 | 11kV | 113325 | 1238 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | @Zn12620 Noraville Pa8 tripped on Relays: A phase Overcurrent Signals: 11kv trip Cause: Tree branch contact - other Tree Branch with burn marks found near PT11747 Ulana Sunrise See 1027457,8 Exclude 1026816 | October | 2013 | 2014Q2 | 2014 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Veg | 2013-10-14 | N | 91.5388 | N | 8 | N | N | 1.1101 | 39.4971 | 82814.5675
[7 empty] | 16273 | 17704 | 1026696 | 2013-10-14 00:19 | 2013-10-14 06:55 | 396 | 11kV | 54103 | 778 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | @Zn12570 Avoca Pa34 fdr tripped and reclosed on A/B IOC Cause: Tree on 11kv near AB43862 bond burnt off in tee to PT12827 table top scenic See 1027394,6 Exclude 1026800,21 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2013-10-14 | N | 69.5411 | N | 8 | N | N | 1.1101 | 39.4971 | 39536.8766
[7 empty] | 16349 | 18537 | 1026828 | 2013-10-14 06:18 | 2013-10-14 10:15 | 237 | 11kV | 237 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 137452 No cause found not storm conditions also refer to 1026828 | October | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-10-14 | N | 237 | N | 8 | N | N | 1.1101 | 39.4971 | 173.1926
[7 empty] | 15681 | 10783 | 1027099 | 2013-10-14 10:23 | 2013-10-14 11:12 | 49 | 11kV | 65954 | 1346 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | At S15014 Mona Vale Zone Panel 9 'S17121, etc' tripped on relays: SEL. Field EFI's - Nil. Interruptions occurred on the 14/10/13 and 15/10/13. Cause of interruptions due to diagram error. Control room diagrams showed job across panels 7 and 22 but they were actually across 9 and 22. SEL for panel 9 was not made N/A. OMS numbers: 1028106, 1028108, 1027099, 1027566, 1027570, 1027646, 1027571, 1027573 | October | 2013 | 2014Q2 | 2014 | ZN15014:PA9 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | Unknown | Not Veg | 2013-10-14 | N | 49 | N | 8 | N | N | 1.1101 | 39.4971 | 48197.2379
[7 empty] | 15945 | 13658 | 1027645 | 2013-10-14 12:55 | 2013-10-14 16:10 | 195 | 11kV | 3510 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa13 @USL44274 tee to PT18068, PT14182, PT18076 interrupted by DOp in Cutrock area Lineworker and DOp isolated, trim branch and restored supply | October | 2013 | 2014Q2 | 2014 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2013-10-14 | N | 195 | N | 8 | N | N | 1.1101 | 39.4971 | 2565.0045
[7 empty] | 16230 | 17377 | 1027244 | 2013-10-14 10:00 | 2013-10-14 17:45 | 465 | 11kV | 1395 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | @Zn1287 Revesby Panel 4 'Tower Condon' section of feeder from LB 63570 to PT2313 St George Heathcote interrupted due to wired down. Remarks: Interrupted for safety reasons. 2 phases of CCT 11kv O/H beyond LB 63570 brough down by tree branch. Lineworkers to reinstate. PT2313 St George Heathcote is non paralleling. Location from customer call is 202 ST GEORGE CRES, SANDY POINT, 2172 | October | 2013 | 2014Q2 | 2014 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | SUTHERLAND | OH | Veg | 2013-10-14 | N | 465 | N | 8 | N | N | 1.1101 | 39.4971 | 1019.4249
[7 empty] | 15217 | 4926 | 1026805 | 2013-10-13 14:05 | 2013-10-14 19:50 | 1785 | 11kV | 119987 | 93 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Wind | Y | LID 137420 2 fault operations Sensitive Earth Fault Fire caused by water board assets Excluded OMS 1026430 & 1026451 | October | 2013 | 2014Q2 | 2014 | 231:8405 | 230:81438 | ZN00230/081438 | PORT STEPHENS | Unknown | Not Veg | 2013-10-13 | Y | 1290.1828 | N | 14 | N | Y | 1.1101 | 39.4971 | 87682.9606
[7 empty] | 16424 | 19487 | 1027526 | 2013-10-14 20:34 | 2013-10-14 21:01 | 27 | 11kV | 41526 | 1538 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At ZN15011 Beacon Hill Zone Panel 10 'French's Hurdis, Rodborough Rd' feeder tripped. Relays - Panel 10R - A and C phase overcurrent. Switching adnormal at the time of interruption - Rec 24721 Oxford Dreadnought closed, Rec 24722 Forst Crozier open. Possum made contact with 11kV mains at UGOH to S15247 Brooker Avenue. OMS numbers: 1027577, 1027528, 1027532, 1027526 | October | 2013 | 2014Q2 | 2014 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-10-14 | N | 27 | N | 8 | N | N | 1.1101 | 39.4971 | 30345.976
[7 empty] | 14904 | 1960 | 1027545 | 2013-10-15 05:19 | 2013-10-15 07:52 | 153 | 11kV | 32115 | 217 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CP555 Arcadia Park Tripped on SEF. Cause not ascertained mains to patrol. See OMS 1029611 1026914 1029615 1029619 1027546 1027545 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-10-15 | N | 147.9954 | N | 7 | N | N | 1.1101 | 39.4971 | 23468.6948
[7 empty] | 15276 | 6145 | 1027566 | 2013-10-15 07:36 | 2013-10-15 08:01 | 25 | 11kV | 33550 | 1342 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | At S15014 Mona Vale Zone Panel 9 'S17121, etc' tripped on relays: SEL. Field EFI's - Nil. Interruptions occurred on the 14/10/13 and 15/10/13. Cause of interruptions due to diagram error. Control room diagrams showed job across panels 7 and 22 but they were actually across 9 and 22. SEL for panel 9 was not made N/A. OMS numbers: 1028106, 1028108, 1027099, 1027566, 1027570, 1027646, 1027571, 1027573 | October | 2013 | 2014Q2 | 2014 | ZN15014:PA9 | ZN15014:PA8 | ZN15014/000008 | NORTHERN BEACHES | Unknown | Not Veg | 2013-10-15 | N | 25 | N | 7 | N | N | 1.1101 | 39.4971 | 24517.3504
[7 empty] | 15908 | 13238 | 1027579 | 2013-10-15 08:06 | 2013-10-15 09:33 | 87 | 11kV | 115960 | 1345 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 137458 4 fault operations B phase Overcurrent; Earth fault fault in section 33611/42881/42966 Excluded oms # 1027579 | October | 2013 | 2014Q2 | 2014 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | UG | Not Veg | 2013-10-15 | N | 86.2156 | N | 7 | N | N | 1.1101 | 39.4971 | 84740.1478
[7 empty] | 15129 | 3981 | 1027614 | 2013-10-15 07:50 | 2013-10-15 09:58 | 128 | 11kV | 512 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137462 interrupt to repair HV connection at sub 53503. Excluded oms 1027614 | October | 2013 | 2014Q2 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-10-15 | N | 128 | N | 7 | N | N | 1.1101 | 39.4971 | 374.1545
[7 empty] | 15707 | 11041 | 1027840 | 2013-10-15 13:26 | 2013-10-15 13:46 | 20 | 11kV | 500 | 25 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137472 interrupt to repair broken HV tapping at pole 9M-10074 near sub 70579. | October | 2013 | 2014Q2 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2013-10-15 | N | 20 | N | 7 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 15872 | 12880 | 1027950 | 2013-10-15 16:00 | 2013-10-15 17:18 | 78 | 11kV | 270 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137473 C phase HV dropper rubbing on crossarm reported. LL Clamps siezed at sub 51072. 11kV section isolated to repair. Excluded OMS No. 1027950 | October | 2013 | 2014Q2 | 2014 | 523:33508 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Not Veg | 2013-10-15 | N | 54 | N | 7 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 16283 | 17837 | 1028005 | 2013-10-15 18:59 | 2013-10-15 19:45 | 46 | 11kV | 3588 | 78 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14892 section of Pa3 Relays: EFI No1 Group Earth, fault check EFI's S12298 @PT12656 Oceanview Gilbert roadside HDO 31.5Amp operated Flashover on exposed conductor between HDO and Las by bird requires plastic insulating caps fitted, referred to subs in OMS See 1028006 exclude 1028005 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2013-10-15 | N | 46 | N | 7 | N | N | 1.1101 | 39.4971 | 2622.0046
[7 empty] | 16021 | 14900 | 1028041 | 2013-10-16 06:40 | 2013-10-16 08:10 | 90 | 11kV | 83340 | 926 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137476 no protection operation tapping off at abs 7851 Sw 2123 opened to arrange fdr Excluded oms # 1028041 | October | 2013 | 2014Q2 | 2014 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2013-10-16 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 60902.4139
[7 empty] | 14902 | 1957 | 1028044 | 2013-10-16 06:47 | 2013-10-16 08:15 | 88 | 11kV | 176 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137477 B phase DOLF : 16 Amp Excluded OMS 1028044 | October | 2013 | 2014Q2 | 2014 | 256:80632 | 256:80632 | ZN00256/080632 | LAKE MACQUARIE | UG | Not Veg | 2013-10-16 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 128.6156
[7 empty] | 15485 | 8277 | 1028644 | 2013-10-16 15:35 | 2013-10-16 16:05 | 30 | 11kV | 720 | 24 | HV | Staff Other | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 137491 Moss Sub 51521 connected to de-energised phase under AP on SI 35742. Customer had no supply when RSI was completed. Section isolated to rectify problem. | October | 2013 | 2014Q2 | 2014 | 523:33501 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-10-16 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 16435 | 19713 | 1028270 | 2013-10-16 12:24 | 2013-10-16 16:15 | 231 | 11kV | 89805 | 643 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Wind | N | LID 137490 2 fault operations A & C phase Overcurrent Public cut down tree that fell on mains between poles HS-42561 & HS-42560. Excluded OMS No. 1028270, 1028279, 1028332 | October | 2013 | 2014Q2 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2013-10-16 | N | 139.6656 | N | 6 | N | N | 1.1101 | 39.4971 | 65626.8452
[7 empty] | 15645 | 10304 | 1028411 | 2013-10-16 15:55 | 2013-10-16 17:15 | 80 | 11kV | 18840 | 241 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | Ex Zn12660 Woy Woy section of Pa14 11kv fdr between AB40639 to LB43375 to AB43306 to LK41730 isolated with interruption to PT's for emergency repairs damaged insulators in taylor st See 1028537,8 Exclude 1028411 | October | 2013 | 2014Q2 | 2014 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2013-10-16 | N | 78.1743 | N | 6 | N | N | 1.1101 | 39.4971 | 13767.7163
[7 empty] | 15658 | 10532 | 1028285 | 2013-10-16 12:45 | 2013-10-16 18:00 | 315 | 11kV | 187762 | 1479 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | LID 137487 2 fault operations Cust drove star picket into cable 6 Cleveland St, Edgeworth. Hit HV cable from 58170 & LV cable Cct 58176. Excluded oms # 1028285 | October | 2013 | 2014Q2 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | UG | Not Veg | 2013-10-16 | N | 126.952 | N | 6 | N | N | 1.1101 | 39.4971 | 137210.9316
[7 empty] | 14793 | 899 | 1028607 | 2013-10-17 09:25 | 2013-10-17 11:12 | 107 | 11kV | 27937 | 263 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137508 1 Fault operations Overcurrent Total Fire Ban, Reclose Function Off, full line patrol done to SW 74456, no fault found, also refer to 1028607 | October | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-10-17 | N | 106.2243 | N | 39 | Y | Y | 1.1101 | 39.4971 | 20415.5356
[7 empty] | 15791 | 12014 | 1028647 | 2013-10-17 10:18 | 2013-10-17 12:10 | 112 | 11kV | 59269 | 752 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137496 3 fault operations tree on mains at pole VP-20064 Excluded oms 1028647 | October | 2013 | 2014Q2 | 2014 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Veg | 2013-10-17 | N | 78.8152 | N | 39 | Y | Y | 1.1101 | 39.4971 | 43312.0371
[7 empty] | 14792 | 883 | 1028809 | 2013-10-17 12:34 | 2013-10-17 13:06 | 32.15 | 11kV | 3890.15 | 121 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 137507 Safety Reasons | October | 2013 | 2014Q2 | 2014 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2013-10-17 | N | 32.15 | N | 39 | Y | Y | 1.1101 | 39.4971 | 2842.8069
[7 empty] | 14694 | 7 | 1028778 | 2013-10-17 12:07 | 2013-10-17 13:16 | 68.8 | 11kV | 41142.4 | 598 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | At ZN3154 St Ives Zone, Panel 13 'S4609 Nambucca Burns' feeder tripped on B and C phase O/C and IOC. DOp removed tree branch from PT1438 Morris Zelda. | October | 2013 | 2014Q2 | 2014 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | OH | Veg | 2013-10-17 | N | 68.8 | N | 39 | Y | Y | 1.1101 | 39.4971 | 30065.6524
[7 empty] | 16437 | 19820 | 1028691 | 2013-10-17 10:53 | 2013-10-17 13:55 | 181.85 | 11kV | 8910.65 | 49 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Hot >35C | N | At S16222 Hudson Hansford, distributor 1, C phase 400A fuse blown. 11kV centre phase OQFRN 40A HV fuse operated. Possible branch blown onto LV mains during hot and windy conditions. HV fuse appears not to have graded with LV fuse. Also striker pin did not operate to trip Tx. OMS numbers: 1028692, 1028695 CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | ZN15004:PA5 | ZN15004:PA5 | ZN15004/000005 | NORTHERN BEACHES | OH | Veg | 2013-10-17 | N | 181.85 | N | 39 | Y | Y | 1.1101 | 39.4971 | 6511.6402
[7 empty] | 16121 | 16167 | 1028540 | 2013-10-17 08:29 | 2013-10-17 14:00 | 331 | 11kV | 89538 | 823 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137495 1 fault operation C phase Overcurrent; Earth fault tree on mains past 11kv links 16639 TFB fdr on one shot | October | 2013 | 2014Q2 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2013-10-17 | N | 108.7947 | N | 39 | Y | Y | 1.1101 | 39.4971 | 65431.7295
[7 empty] | 16241 | 17480 | 1028814 | 2013-10-17 12:39 | 2013-10-17 14:10 | 91 | 11kV | 98671 | 1233 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Hot >35C | N | At Zn35800 Bankstown Zone 11kv Panel 1 "Sub 35208 Gow Gibson' C/B tripped on: Relays: Earth fault on OC and E/F relay, EFI Signals: 11kv trip Remarks: Open circuit HV bond was found open circuit on HVUG pole cnr of Irvine Ave and Northam St repaired by mains. | October | 2013 | 2014Q2 | 2014 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-10-17 | N | 80.0251 | N | 39 | Y | Y | 1.1101 | 39.4971 | 72105.8565
[7 empty] | 16327 | 18264 | 1028864 | 2013-10-17 13:08 | 2013-10-17 14:50 | 102 | 11kV | 3642 | 298 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137510 Tree in mains at pole HV-10121 also refer to 1028864 and 1029504 | October | 2013 | 2014Q2 | 2014 | 239:82131 | 239:82131 | ZN00239/082131 | LAKE MACQUARIE | OH | Veg | 2013-10-17 | N | 12.2215 | N | 39 | Y | Y | 1.1101 | 39.4971 | 2661.4662
[7 empty] | 16104 | 16037 | 1028753 | 2013-10-17 11:45 | 2013-10-17 14:56 | 191 | 11kV | 268167 | 1815 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137503 1 Fault operations - no cause found also refer to 1028753 Patrol Requested | October | 2013 | 2014Q2 | 2014 | 224:80332 | 270:83590 | ZN00270/083590 | LAKE MACQUARIE | OH | Veg | 2013-10-17 | N | 147.7504 | N | 39 | Y | Y | 1.1101 | 39.4971 | 195968.534
[7 empty] | 14866 | 1607 | 1028794 | 2013-10-17 14:28 | 2013-10-17 14:58 | 30 | 11kV | 14430 | 481 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137515 1 Fault operations,Overcurrent. No Cause Found Multiple trip and recloses for this feeder today CC1: 06-"Urgent - O.H Mains - No others" | October | 2013 | 2014Q2 | 2014 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2013-10-17 | N | 30 | N | 39 | Y | Y | 1.1101 | 39.4971 | 10545.0184
[7 empty] | 15316 | 6561 | 1028954 | 2013-10-17 14:07 | 2013-10-17 15:13 | 66 | 11kV | 83886 | 1271 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | ZN12650 West Gosford 11kv fdr Pa3 tripped/reclosed/locked out Relays: A&B phase IOC, Reclosing, Timing, Lockout Cause: not ascetained. Wind Strom at time of failure. DOp patrolled all clear See 1029714,5 exclude 1028954 | October | 2013 | 2014Q2 | 2014 | ZN12650:PA3 | ZN12650:PA3 | ZN12650/000003 | CENTRAL COAST | OH | Veg | 2013-10-17 | N | 66 | N | 39 | Y | Y | 1.1101 | 39.4971 | 61301.4146
[7 empty] | 14911 | 1994 | 1029048 | 2013-10-17 15:05 | 2013-10-17 15:20 | 14.9667 | 11kV | 1062.6333 | 71 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12570 Avoca Zone section of Pa33 IR44797 Bouddi tripped to lockout (x2) Relays: OC trip Cause: Branch removed of Overhead main near PT13385 The scenic Grahame 0.3 by DOp | October | 2013 | 2014Q2 | 2014 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2013-10-17 | N | 14.9667 | N | 39 | Y | Y | 1.1101 | 39.4971 | 776.5411
[7 empty] | 14990 | 2719 | 1028701 | 2013-10-17 13:39 | 2013-10-17 15:25 | 106 | 11kV | 195676 | 1846 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137514 2 fault operations A phase Overcurrent Tree fell on mains at pole NB-50233. | October | 2013 | 2014Q2 | 2014 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | OH | Veg | 2013-10-17 | N | 106 | N | 39 | Y | Y | 1.1101 | 39.4971 | 142994.2493
[7 empty] | 16151 | 16493 | 1028890 | 2013-10-17 13:42 | 2013-10-17 15:37 | 115 | 11kV | 154445 | 1343 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S2400 Berowra Panel 22 Tripped on O/C Cause: Tree branch on OH near AB1143 | October | 2013 | 2014Q2 | 2014 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Veg | 2013-10-17 | N | 115 | N | 39 | Y | Y | 1.1101 | 39.4971 | 112863.8506
[7 empty] | 14791 | 879 | 1028921 | 2013-10-17 13:50 | 2013-10-17 15:37 | 107 | 11kV | 34347 | 321 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137517 1 Fault operations single phase, overcurrent Strong Wind | October | 2013 | 2014Q2 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2013-10-17 | N | 107 | N | 39 | Y | Y | 1.1101 | 39.4971 | 25099.7745
[7 empty] | 15446 | 7912 | 1028825 | 2013-10-17 12:30 | 2013-10-17 15:45 | 195 | 11kV | 390 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137521 Trees growing into Mains, Clashing Mains isolated for Tree Trimming | October | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-10-17 | N | 195 | N | 39 | Y | Y | 1.1101 | 39.4971 | 285.0005
[7 empty] | 15551 | 8943 | 1028743 | 2013-10-17 11:36 | 2013-10-17 15:49 | 253.1167 | 11kV | 58822.6833 | 594 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 10990 Arncliffe - Pnl 5 - Trip/reclose/trip, A phase IOC and OC, Timing, lockout. Branch on 11kV in Burrows near Eden. LV// were in place during outage and are included as restoration steps. ME: 1028743. Rest Steps: 1029478, 80, 81. RS GIS: 1029032. Withdrawn: 1028750, 51, 55, 58, 74, 96, 1029030, 31, 32. | October | 2013 | 2014Q2 | 2014 | ZN10990:PA5 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | OH | Veg | 2013-10-17 | N | 99.0281 | N | 39 | Y | Y | 1.1101 | 39.4971 | 42985.882
[7 empty] | 16426 | 19532 | 1029020 | 2013-10-17 14:47 | 2013-10-17 16:49 | 122 | 11kV | 71980 | 590 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137518 2 fault operations A & B phase Instantaneous Overcurrent Trees on mains at poles JS-37036 & JS-37083. | October | 2013 | 2014Q2 | 2014 | 264:81238 | 264:81238 | ZN00264/081238 | PORT STEPHENS | OH | Veg | 2013-10-17 | N | 122 | N | 39 | Y | Y | 1.1101 | 39.4971 | 52600.8609
[7 empty] | 16109 | 16059 | 1028953 | 2013-10-17 14:06 | 2013-10-17 16:53 | 167 | 11kV | 174797 | 1285 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 10995 Riverwood - Pnl 13 - Trip/reclose/trip, A phase IOC and timed OC, timing, lockout. Tree branch on 11kV OH mains adjacent AB 31153. ME: 1029465. Rest Step: 1029466. RS GIS: 1029037. Withdrawn: 1028953. | October | 2013 | 2014Q2 | 2014 | ZN10995:PA13 | ZN10995:PA13 | ZN10995/000013 | GEORGES RIVER | OH | Veg | 2013-10-17 | N | 136.0288 | N | 39 | Y | Y | 1.1101 | 39.4971 | 127736.492
[7 empty] | 16472 | 20175 | 1028768 | 2013-10-17 15:51 | 2013-10-17 17:25 | 94 | 11kV | 103686 | 1404 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn12600 Lisarow Pa3 tripped Relays: Aph overcurrent Cause: Overhead patrolled clear. DOp found evidence of tree contact near PT13717 Berry Head Green Oaks. The recloser for this panel is now normally N/A even though major section of mains Overhead. thus delaying restoration See 1029755,8 GIS 1029172 Exclude 1028768,9707 | October | 2013 | 2014Q2 | 2014 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2013-10-17 | N | 73.8504 | N | 39 | Y | Y | 1.1101 | 39.4971 | 75770.6706
[7 empty] | 15111 | 3853 | 1029007 | 2013-10-17 14:36 | 2013-10-17 17:32 | 176 | 11kV | 141614 | 1075 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S847 Hornsby Panel 22 Tripped on C phase IOC and Timed O/C Cause: Tree in Spedding St Hornsby Heights See OMS 1029696 1029638 1029638 1029025 1029011 | October | 2013 | 2014Q2 | 2014 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Veg | 2013-10-17 | N | 131.734 | N | 39 | Y | Y | 1.1101 | 39.4971 | 103487.3343
[7 empty] | 15284 | 6265 | 1029223 | 2013-10-17 16:46 | 2013-10-17 17:56 | 70 | 11kV | 51870 | 741 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Section of Pa30 ex Zn195 Pymble CP46113 - Fidden Warf Coronga Tripped Cause Not ascertained for outage - suspect tree branch based on high wind Outage Times Checked against DNMS load trend | October | 2013 | 2014Q2 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2013-10-17 | N | 70 | N | 39 | Y | Y | 1.1101 | 39.4971 | 37905.0661
[7 empty] | 16029 | 14949 | 1029245 | 2013-10-17 17:08 | 2013-10-17 18:04 | 56.3833 | 11kV | 63825.9333 | 1132 | HV | Vegetation Blow/Fall In | Vegetation | Unselected | Unplanned | Wind | N | At ZN3154 St Ives Zone panel 5 'S4263 The Collins Killeaton' feeder tripped on C phase IOC and timed OL. Large tree fell onto 11kV mains infront of 8 Awatea St. Reference OMS numbers: 1029245, 1029265, 1029278 | October | 2013 | 2014Q2 | 2014 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2013-10-17 | N | 56.3833 | N | 39 | Y | Y | 1.1101 | 39.4971 | 46642.1095
[7 empty] | 14953 | 2296 | 1029241 | 2013-10-17 17:02 | 2013-10-17 18:10 | 68 | 11kV | 50928 | 1154 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | LID 137529 3 fault operations B & C phase Overcurrent; Earth fault UG cable fault between Sw 28418 & Sw 24530 Excluded OMS 1029241 | October | 2013 | 2014Q2 | 2014 | 213:33770 | 213:33770 | ZN00213/033770 | NEWCASTLE | UG | Not Veg | 2013-10-17 | N | 44.1317 | N | 39 | Y | Y | 1.1101 | 39.4971 | 37216.6803
[7 empty] | 15666 | 10642 | 1029214 | 2013-10-17 16:48 | 2013-10-17 18:12 | 84 | 11kV | 126168 | 1502 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12580 Erina Pa10 tripped Relays: A&C phase ins, A phase timed overcurrent, EFI EFI's: S13682 S12866 S14189 S18183 Cause: DOp removed tree branch lodged on UGOH above S14225, no damage to UGOH | October | 2013 | 2014Q2 | 2014 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2013-10-17 | N | 84 | N | 39 | Y | Y | 1.1101 | 39.4971 | 92199.8531
[7 empty] | 14840 | 1298 | 1029069 | 2013-10-17 15:14 | 2013-10-17 18:20 | 185.5167 | 11kV | 29311.6333 | 158 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137526 burnt off tapping beyond 11kV Links 16639 - Trees blown onto mains | October | 2013 | 2014Q2 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2013-10-17 | N | 185.5167 | N | 39 | Y | Y | 1.1101 | 39.4971 | 21420.0771
[7 empty] | 15627 | 10081 | 1029137 | 2013-10-17 17:12 | 2013-10-17 18:20 | 68 | 11kV | 272 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 137522 Cph HV dropper burnt off, Cph LV Connection burnt up | October | 2013 | 2014Q2 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2013-10-17 | N | 68 | N | 39 | Y | Y | 1.1101 | 39.4971 | 198.7696
[7 empty] | 15758 | 11685 | 1029002 | 2013-10-17 14:37 | 2013-10-17 18:48 | 251 | 11kV | 153591 | 787 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137520 1 fault operation A & B phase Instantaneous Overcurrent Grass fire at Ray Terrace sub and tree on mains at pole JS-30978. Excluded OMS 1029002 + 1029129 | October | 2013 | 2014Q2 | 2014 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2013-10-17 | N | 195.1601 | N | 39 | Y | Y | 1.1101 | 39.4971 | 112239.7726
[7 empty] | 15727 | 11363 | 1029298 | 2013-10-17 17:50 | 2013-10-17 18:53 | 63.1667 | 11kV | 1263.3333 | 20 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | Hot >35C | N | LID 137527 Burnt down stay pole JS-60136. Section isolated to cut away stay | October | 2013 | 2014Q2 | 2014 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Veg | 2013-10-17 | N | 63.1667 | N | 39 | Y | Y | 1.1101 | 39.4971 | 923.2067
[7 empty] | 14855 | 1481 | 1029052 | 2013-10-17 15:02 | 2013-10-17 19:26 | 263.9167 | 11kV | 120430.45 | 1135 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S1673 Turramurra Pa18 Tripped on B and C phase IOC Cause not ascertained for outage | October | 2013 | 2014Q2 | 2014 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2013-10-17 | N | 106.1061 | N | 39 | Y | Y | 1.1101 | 39.4971 | 88007.0208
[7 empty] | 16444 | 19906 | 1029284 | 2013-10-17 17:35 | 2013-10-17 20:00 | 145 | 11kV | 10645 | 113 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 137519 1 Fault operations. Pole mounted RAGCB, Sensitive Earth Fault HV Wires down near Godgrey sub 17346. Cuased Fire. Reported to JD | October | 2013 | 2014Q2 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2013-10-17 | N | 94.2035 | N | 39 | Y | Y | 1.1101 | 39.4971 | 7779.052
[7 empty] | 14944 | 2201 | 1029551 | 2013-10-17 20:00 | 2013-10-17 20:30 | 30 | 11kV | 180 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137523 Fuse: 40 Amp Line DOLF Tree fell and brushed mains - no location provided | October | 2013 | 2014Q2 | 2014 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2013-10-17 | N | 30 | N | 39 | Y | Y | 1.1101 | 39.4971 | 131.5387
[7 empty] | 14886 | 1787 | 1029130 | 2013-10-17 16:45 | 2013-10-17 21:15 | 270 | 11kV | 13500 | 50 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | LID 137525 Bph dropper to links 27638 broken also refer to OMS 1029130 | October | 2013 | 2014Q2 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-10-17 | N | 270 | N | 39 | Y | Y | 1.1101 | 39.4971 | 9865.4018
[7 empty] | 14707 | 101 | 1029407 | 2013-10-18 00:30 | 2013-10-18 01:35 | 65 | 11kV | 1040 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137534 Isolate to repair 11kV tapping Excluded OMS-1029407 | October | 2013 | 2014Q2 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-10-18 | N | 65 | N | 11 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 15582 | 9274 | 1029334 | 2013-10-17 18:56 | 2013-10-18 02:10 | 434 | 11kV | 5642 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137535 Fuse Size: 16 Amp Line DOLF also refer to 1029334 - Fdr patrolled before reclose | October | 2013 | 2014Q2 | 2014 | 802:82225 | 802:82225 | ZN00802/082225 | MID-WESTERN REGIONAL | OH | Veg | 2013-10-17 | N | 434 | N | 39 | Y | Y | 1.1101 | 39.4971 | 4123.0072
[7 empty] | 15010 | 2908 | 1029256 | 2013-10-17 17:05 | 2013-10-18 02:50 | 585 | 11kV | 28665 | 49 | HV | Fire (non-electrical) | Adverse Weather/Environment | Cross arm | Unplanned | Wind | N | LID 137536 replace burnt crossarm at HS-50060 | October | 2013 | 2014Q2 | 2014 | 229:34986 | 229:34986 | ZN00229/034986 | PORT STEPHENS | OH | Not Veg | 2013-10-17 | N | 585 | N | 39 | Y | Y | 1.1101 | 39.4971 | 20947.5365
[7 empty] | 15105 | 3792 | 1030293 | 2013-10-17 19:35 | 2013-10-18 04:40 | 545 | 11kV | 4360 | 8 | HV | Fire (non-electrical) | Adverse Weather/Environment | Cross arm | Unplanned | Hot >35C | N | LID 137530 33kV x-arm fire pole JS-90042 33kV fdr TM3 & 11kV fdr isolated for repair | October | 2013 | 2014Q2 | 2014 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2013-10-17 | N | 545 | N | 39 | Y | Y | 1.1101 | 39.4971 | 3186.1594
[7 empty] | 15238 | 5502 | 1029411 | 2013-10-18 01:21 | 2013-10-18 06:18 | 297 | 11kV | 103554 | 1294 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 137533 3 fault operations A & B phase Overcurrent; Earth fault Cable melted up pole below UGOH Excluded oms-1029411/13/14 | October | 2013 | 2014Q2 | 2014 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | UG | Not Veg | 2013-10-18 | N | 80.0263 | N | 11 | N | N | 1.1101 | 39.4971 | 75674.2089
[7 empty] | 16128 | 16242 | 1029419 | 2013-10-18 05:07 | 2013-10-18 07:46 | 159 | 11kV | 34338 | 218 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Interrupted S35370 Galston Zone section of panel 8 'LB497, etc' 11kV feederRec.555 Arcadia Park open on: SEL. Cause not ascertained. OH mains to patrol. OMS numbers: 1030888, 1030897, 1029419, 1029420 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-10-18 | N | 157.5138 | N | 11 | N | N | 1.1101 | 39.4971 | 25093.1976
[7 empty] | 14956 | 2336 | 1029409 | 2013-10-18 00:50 | 2013-10-18 07:56 | 425.9333 | 11kV | 43019.2667 | 101 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At PT634 Somerville Camiri 11kV footpath phase HDO blown Suspect PT634 is defective See OMS 1029467 1029415 1029409 | October | 2013 | 2014Q2 | 2014 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | UG | Not Veg | 2013-10-18 | N | 425.9333 | N | 11 | N | N | 1.1101 | 39.4971 | 31437.2112
[7 empty] | 14767 | 584 | 1029500 | 2013-10-18 08:50 | 2013-10-18 09:33 | 43 | 11kV | 430 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 137539 11KV MAIN FOUND OFF X-ARM POLE SI-80293. THIS PROBLEM RELATES TO OUTAGES ON FDR 33508 ON 17/10/2013. | October | 2013 | 2014Q2 | 2014 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2013-10-18 | N | 43 | N | 11 | N | N | 1.1101 | 39.4971 | 314.2313
[7 empty] | 16196 | 17028 | 1029331 | 2013-10-17 18:41 | 2013-10-18 10:27 | 946 | 11kV | 554852 | 594 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn13000 Lake Munmorah 11kv fdr pa1 tripped Relays: IOC B&C phase, EFI ABNORMAL: All 11kv reclosing made non-auto by AOp prior to this failur due to bushfir in region Cause: Extensive fire damage - LONG delays until staff can access damaged areas to asses extent of damage. See 1030455,7 Exclude 1029331 | October | 2013 | 2014Q2 | 2014 | ZN13000:PA1 | ZN13000:PA1 | ZN13000/000001 | CENTRAL COAST | OH | Veg | 2013-10-17 | N | 934.0943 | N | 39 | Y | Y | 1.1101 | 39.4971 | 405469.4762
[7 empty] | 16317 | 18154 | 1029622 | 2013-10-18 10:49 | 2013-10-18 12:24 | 95 | 11kV | 6962 | 110 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn874 Concord Zn: 11kv Pnl12 'Sub 2834' C/B tripped on; Relays: Translay, intertrip receive. Signals: 11kv trip, Group Earth, Zone Earth. At Sub 5417 Hospital Road tripped on: Relays: Translay, Intertrip send. Signals: nil. No field EFI's Remarks: UG fault. 11kv underground feeder fault from Zn874 Concord 'Panel 12' to Sw/a at Sub 2834 Nurrawarra Curra | October | 2013 | 2014Q2 | 2014 | ZN874:PA12 | ZN874:PA12 | ZN00874/000012 | CANADA BAY | UG | Not Veg | 2013-10-18 | N | 63.2909 | N | 11 | N | N | 1.1101 | 39.4971 | 5087.6243
[7 empty] | 16307 | 18088 | 1029405 | 2013-10-17 19:50 | 2013-10-18 14:35 | 1125 | 11kV | 33750 | 30 | HV | Fire (non-electrical) | Adverse Weather/Environment | Pole | Unplanned | Hot >35C | N | LID 137531 Isolated for pole fires along Richardson Rd between ABS 1480 & LF 43997 | October | 2013 | 2014Q2 | 2014 | 229:34983 | 233:82818 | ZN00233/082818 | PORT STEPHENS | OH | Not Veg | 2013-10-17 | N | 1125 | N | 39 | Y | Y | 1.1101 | 39.4971 | 24663.5045
[7 empty] | 15443 | 7886 | 1029757 | 2013-10-18 13:33 | 2013-10-18 15:19 | 106 | 11kV | 169914 | 1695 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | At S195 Pymble Zone panel 9 'S47348 Pacific Cecil' feeder tripped. Suspect underground 11kV feeder fault between S5428, S47190 and S2542. OMS numbers: 1030579, 1030581, 1029757, 1029767, 1029776, 1029780, 1029784, 1029785, 1029787, 1029791, 1029797 | October | 2013 | 2014Q2 | 2014 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2013-10-18 | N | 100.2442 | N | 11 | N | N | 1.1101 | 39.4971 | 124168.1396
[7 empty] | 14857 | 1493 | 1029656 | 2013-10-18 12:15 | 2013-10-18 15:35 | 200 | 11kV | 1000 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137544 C phase DOLF : 10 Amp 11KV MAIN INTO LOW VOLTAGE AT POLE AG-80438. | October | 2013 | 2014Q2 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-10-18 | N | 200 | N | 11 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 15386 | 7273 | 1029737 | 2013-10-18 13:02 | 2013-10-18 16:48 | 226 | 11kV | 309168 | 1368 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Hot >35C | N | Ex Zn13000 Lake Munmorah section of Pa7 RE45061Chain Valley Bay Molloway tripped on OC & IOC ABNORMAL: AB44265 Closed, LB41810 Open, RE45061 recloser made Non Auto due to Bushfires Cause: RFS dropped water bucket onto 11kv OH Mains in Finlay Ave Chain Valley Bay See 1030462 exclude 1029737 | October | 2013 | 2014Q2 | 2014 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2013-10-18 | N | 226 | N | 11 | N | N | 1.1101 | 39.4971 | 225930.8555
[7 empty] | 15427 | 7765 | 1029717 | 2013-10-18 12:34 | 2013-10-18 18:44 | 370 | 11kV | 150111 | 1022 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S847 Hornsby Zone panel 47 'LB2901, etc' 11kV feeder tripped, reclosed abd locked out on: C phase O/C, E/F, EFI, F/C, LO, Timer. Field EFI operated at S4843. 11kV OH wires down in Peter Close. OMS numbers: 1030846, 1029847, 1030850, 1030852, 1029717, 1029750, 1029705 | October | 2013 | 2014Q2 | 2014 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2013-10-18 | N | 146.8796 | N | 11 | N | N | 1.1101 | 39.4971 | 109696.6913
[7 empty] | 15016 | 2944 | 1029417 | 2013-10-18 04:40 | 2013-10-18 20:40 | 960 | 11kV | 5760 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | LID 137537 Isolate to repair burnt LV crossarm at sub 5417. SI. M0511 Excluded oms-1029417. | October | 2013 | 2014Q2 | 2014 | 265:81651 | 265:81651 | ZN00265/081651 | PORT STEPHENS | OH | Not Veg | 2013-10-18 | N | 960 | N | 11 | N | N | 1.1101 | 39.4971 | 4209.2381
[7 empty] | 16496 | 20385 | 1029974 | 2013-10-19 11:40 | 2013-10-19 13:05 | 85 | 11kV | 7140 | 84 | HV | Bushfire | Adverse Weather/Environment | DC PT | Unplanned | Unselected | N | Ex Zn13000 Lake Munmorah section of Pa2L @USL44854 to extent of fdr interrupted by DOp to replace PT earth grids (safety reasons) | October | 2013 | 2014Q2 | 2014 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Veg | 2013-10-19 | N | 85 | N | 3 | N | N | 1.1101 | 39.4971 | 5217.7014
[7 empty] | 16495 | 20383 | 1029388 | 2013-10-17 17:42 | 2013-10-19 15:40 | 2758 | 11kV | 103937 | 110 | HV | Bushfire | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | Zn13000 Lake Munmorah 11kv fdr Pa4 tripped and locked out Relays: IOC A&B Phase reclose, lockout ABNORMAL All 11kv reclosing made non-auto by AOP prior to this failure due to bushfire region Cause: Weather related Bushfire damaged mains See 1030438,9,40,2 exclude 1029388,498,902 | October | 2013 | 2014Q2 | 2014 | ZN13000:PA4 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Veg | 2013-10-17 | N | 944.8818 | N | 39 | Y | Y | 1.1101 | 39.4971 | 75954.094
[7 empty] | 15152 | 4171 | 1030014 | 2013-10-19 15:22 | 2013-10-19 16:35 | 72.75 | 11kV | 3710.25 | 51 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137557 A Phase DOLF : 32 Amp CC1: 22-"Refer to SOp" | October | 2013 | 2014Q2 | 2014 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2013-10-19 | N | 72.75 | N | 3 | N | N | 1.1101 | 39.4971 | 2711.3413
[7 empty] | 15473 | 8169 | 1030056 | 2013-10-19 21:54 | 2013-10-20 00:14 | 140 | 11kV | 9660 | 69 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 137562 A & B phase Nil protection see previous report 137560. Wire off pin mains clashed at sub 50935 Dalwood west sub. Excluded oms 1030056## | October | 2013 | 2014Q2 | 2014 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2013-10-19 | N | 140 | N | 3 | N | N | 1.1101 | 39.4971 | 7059.2431
[7 empty] | 15462 | 8058 | 1030058 | 2013-10-20 01:22 | 2013-10-20 08:52 | 450 | 11kV | 2250 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137563 B & C phase DOLF : 20 Amp Due to a customer locking a gate and restricting access, the line patrol was not done immediately, but did commence at daylight when the customer was awake and allowed access. The Operator on site did point out we needed better access, for the short term the customer provided a phone number. There was a small grass fire near blown line dolf 's 40830, the line patrol could not provide any reason for the blown fuses or the grass fire. | October | 2013 | 2014Q2 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2013-10-20 | N | 450 | N | 2 | N | N | 1.1101 | 39.4971 | 1644.2336
[7 empty] | 14747 | 427 | 1030163 | 2013-10-20 21:00 | 2013-10-21 01:20 | 260 | 11kV | 20280 | 78 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 137567 Section isolated for emergency repairs at UGOH IV-40265 | October | 2013 | 2014Q2 | 2014 | 225:33679 | 270:83586 | ZN00270/083586 | LAKE MACQUARIE | Unknown | Unknown | 2013-10-20 | N | 260 | N | 2 | N | N | 1.1101 | 39.4971 | 14820.0258
[7 empty] | 15871 | 12873 | 1030255 | 2013-10-21 09:05 | 2013-10-21 10:47 | 102 | 11kV | 154892 | 1706 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S.2196 Milperra Panel 25 'Turvey River' 11kv feeder tripped on; A & B IOC Alarms: 11kv trip Remarks: Bird flew into HV mains - Cnr Mackenzie & Bishop. Repeated outage - ocured on 9/10/13, 22/09/13, 15/09/13, 28/06/13, 25/06/13 | October | 2013 | 2014Q2 | 2014 | ZN2196:PA25 | ZN35800:PA18 | ZN35800/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-10-21 | N | 90.7925 | N | 6 | N | N | 1.1101 | 39.4971 | 113190.5051
[7 empty] | 16469 | 20154 | 1030310 | 2013-10-21 09:55 | 2013-10-21 13:10 | 195 | 11kV | 5316 | 49 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137577 1 fault operation Earth fault Tree brought down OHM on spur beyond pole 8L-10304 off Wybong Rd, A/R non auto due to TFB Excluded OMS 1030310 | October | 2013 | 2014Q2 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2013-10-21 | N | 108.4898 | N | 6 | N | N | 1.1101 | 39.4971 | 3884.776
[7 empty] | 15634 | 10139 | 1030640 | 2013-10-21 16:13 | 2013-10-21 17:26 | 72.95 | 11kV | 56453.4333 | 1227 | HV | Animal Bird | Animal | O/H Conductor ABC | Unplanned | Hot >35C | N | ZN 9037 Miranda - Pnl 16 - Trip/reclose/trip, Earth fault, lockout, timing. Magpie found across footpath and centre phase on 11kV OH near PT 9220 Raglan Wyralla. Removed by DOp. S 9404 moved off panel 16 for works. ME: 1034174. ME GIS: 1030658. Withdrawn: 1030640, 54, 67. | October | 2013 | 2014Q2 | 2014 | ZN9037:PA16 | ZN9037:PA16 | ZN09037/000016 | SUTHERLAND | OH | Not Veg | 2013-10-21 | N | 46.0093 | N | 6 | N | N | 1.1101 | 39.4971 | 41254.504
[7 empty] | 16427 | 19540 | 1030615 | 2013-10-21 15:50 | 2013-10-21 17:36 | 106 | 11kV | 52788 | 498 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Zn1287 Revesby, Ex Panel No.17 labelled 'S.5036 Hinemoa St' feeder, roadside phase contact not making on AB2943. Remarks: air break switch. AB2943 roadside phase contact not making. AB2943 very loose. | October | 2013 | 2014Q2 | 2014 | ZN1287:PA17 | ZN1287:PA17 | ZN01287/000017 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-10-21 | N | 106 | N | 6 | N | N | 1.1101 | 39.4971 | 38575.9134
[7 empty] | 15970 | 14109 | 1030723 | 2013-10-21 19:17 | 2013-10-21 20:49 | 92 | 11kV | 12749 | 142 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137582 1 fault operation Overcurrent The operators cleared a tree away from the 11kV line near pole GR-65614 Wollombi Rd x Ravensfield Rd. This tree will require further trimming to get correct clearances. Whilst the line was patrolled as good as possible it is recommended the line be further patrolled in the daylight. Reclose function was off at Sw 43029 due to the total fire ban conditions. Excluded OMS 1030723 & 1030732 | October | 2013 | 2014Q2 | 2014 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Veg | 2013-10-21 | N | 89.7817 | N | 6 | N | N | 1.1101 | 39.4971 | 9316.5932
[7 empty] | 15420 | 7684 | 1030865 | 2013-10-21 22:37 | 2013-10-21 23:40 | 63 | 11kV | 189 | 3 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Ex Zn14892 Charmhaven section of Pa6 @AB41862-AB40891-AB44111 Interrupted for safety reasons. Car hit pole. Pole needed to be reraked and retied | October | 2013 | 2014Q2 | 2014 | ZN14892:PA6 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | OH | Not Veg | 2013-10-21 | N | 63 | N | 6 | N | N | 1.1101 | 39.4971 | 138.1156
[7 empty] | 16319 | 18210 | 1030742 | 2013-10-22 01:43 | 2013-10-22 03:15 | 92 | 11kV | 94639 | 1078 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S4545 Meadowbank Zone panel 42 'S2910' feeder tripped, reclosed, tripped and locked out on: time O/C, Earth Fault, Fault Check, L/O Field EFI's operated at: S2910, S4056, S4333, S7676, 7896. Field EFI's operated after first manual reclose attempt: S2910, S4056. UG fault between S4056 Gaza Victoria to S4333 Station Dunmore to AB49868. OMS numbers: 1031019, 1031022, 1030742 | October | 2013 | 2014Q2 | 2014 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | UG | Not Veg | 2013-10-22 | N | 87.7913 | N | 3 | N | N | 1.1101 | 39.4971 | 69159.3898
[7 empty] | 14797 | 913 | 1030744 | 2013-10-22 02:01 | 2013-10-22 04:10 | 129 | 11kV | 6966 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137583 B phase DOLF : 40 Amp | October | 2013 | 2014Q2 | 2014 | 261:81876 | 261:81876 | ZN00261/081876 | LAKE MACQUARIE | UG | Not Veg | 2013-10-22 | N | 129 | N | 3 | N | N | 1.1101 | 39.4971 | 5090.5473
[7 empty] | 14777 | 696 | 1031065 | 2013-10-22 15:39 | 2013-10-22 17:32 | 113 | 11kV | 132222 | 1284 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 1648 Enfield - Pnl 15 - C phase IOC, EFI, Field EFIs. Underground cable fault between S 3658 and S 2087. ME: 1031241. Rest Step: 1031242. Withdrawn: 1031065. | October | 2013 | 2014Q2 | 2014 | ZN1648:PA15 | ZN4853:PA2 | ZN04853/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-10-22 | N | 102.9766 | N | 3 | N | N | 1.1101 | 39.4971 | 96623.9377
[7 empty] | 15659 | 10542 | 1031245 | 2013-10-23 08:09 | 2013-10-23 12:55 | 286 | 11kV | 198322 | 1444 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At Zn116 Leichhardt P34 Balmain Derby fdr tripped on C phase IOC, EFI. EFI's at S47278, S4829, S35899, S35932 Remarks: UGOH fault short circuit. 11kv fdr from S35932 Balmain Piper No1 to S2359 Henry Lill tee Pt1862 Lilyfield Trev LV network found in LV// | October | 2013 | 2014Q2 | 2014 | ZN116:PA34 | ZN116:PA12 | ZN00116/000012 | INNER WEST | Unknown | Unknown | 2013-10-23 | N | 137.3421 | N | 6 | N | N | 1.1101 | 39.4971 | 144927.8681
[7 empty] | 16146 | 16451 | 1031599 | 2013-10-23 16:00 | 2013-10-23 18:40 | 160 | 11kV | 2560 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 137609 Interrupted supply to repair link 27638 - also refer to OMS 1032179 and 1032180 which are referred to in this LID re repairing tapping at pole SF40438 | October | 2013 | 2014Q2 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-10-23 | N | 160 | N | 6 | N | N | 1.1101 | 39.4971 | 1870.7725
[7 empty] | 15073 | 3426 | 1031691 | 2013-10-23 16:30 | 2013-10-23 18:40 | 130 | 11kV | 3390 | 33 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 137609 Interrupted supply to repair tapping at pole SF-40438 also refer to 1032178 for record re USL27638 | October | 2013 | 2014Q2 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2013-10-23 | N | 102.7273 | N | 6 | N | N | 1.1101 | 39.4971 | 2477.312
[7 empty] | 16038 | 15282 | 1031471 | 2013-10-23 11:47 | 2013-10-23 19:27 | 460 | 11kV | 150121 | 381 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 137606 3 Fault operations Broken Live Line lead on sub 26870 B phase welded to C Phase at the top of the DOLF Note information provided by T45983, LID mentions fire beyond ABS 3282, john advised Ausgrid have no assets near where the fire was, and the fire played no part in this event. It was hot and windy. | October | 2013 | 2014Q2 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-10-23 | N | 394.0184 | N | 6 | N | N | 1.1101 | 39.4971 | 109703.999
[7 empty] | 16403 | 19191 | 1031876 | 2013-10-24 09:20 | 2013-10-24 10:40 | 80 | 11kV | 160 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Hot >35C | N | LID 137614 Voltage Leaking on Pole | October | 2013 | 2014Q2 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2013-10-24 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 15359 | 6910 | 1031663 | 2013-10-23 16:03 | 2013-10-24 13:30 | 1287 | 11kV | 263305 | 1300 | HV | Bushfire | Adverse Weather/Environment | Pole | Unplanned | Wind | N | LID 137611 Feeder isolated for poles on fire at redhead road | October | 2013 | 2014Q2 | 2014 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2013-10-23 | N | 202.5423 | N | 6 | N | N | 1.1101 | 39.4971 | 192415.5278
[7 empty] | 16277 | 17734 | 1032426 | 2013-10-24 12:30 | 2013-10-24 13:38 | 68 | 11kV | 680 | 10 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 @AB40983 interrupted by DOp for safety reasons. To allow Overhead mains to repair CCT which had come off insulators | October | 2013 | 2014Q2 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2013-10-24 | N | 68 | N | 4 | N | N | 1.1101 | 39.4971 | 496.9239
[7 empty] | 15057 | 3300 | 1031801 | 2013-10-24 07:50 | 2013-10-24 14:05 | 375 | 11kV | 375 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 137618 Live Line Clamp broken refer also to OMS 1031801 | October | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2013-10-24 | N | 375 | N | 4 | N | N | 1.1101 | 39.4971 | 274.0389
[7 empty] | 16052 | 15426 | 1031351 | 2013-10-23 10:23 | 2013-10-24 22:09 | 2146 | 11kV | 23336 | 62 | HV | Bushfire | Adverse Weather/Environment | Bond | Unplanned | Wind | N | LID 137610 3 Fault operations, Overcurrent Burnt Off tapping repaired at Pole IT 21703 Optus Stockrington sub burnt down Suggested Fire began between subs 25223 and 54677 | October | 2013 | 2014Q2 | 2014 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2013-10-23 | N | 376.3871 | N | 6 | N | N | 1.1101 | 39.4971 | 17053.2605
[7 empty] | 15204 | 4672 | 1032240 | 2013-10-24 19:22 | 2013-10-24 23:20 | 238 | 11kV | 293 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137621 C phase Broken HV lead DOLF to Tx at sub 70493 Subs isolated from LL clamps pole 7L-80415 Volts = 243V Excluded OMS 1032240 | October | 2013 | 2014Q2 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2013-10-24 | N | 146.5 | N | 4 | N | N | 1.1101 | 39.4971 | 214.1158
[7 empty] | 15816 | 12285 | 1032265 | 2013-10-25 01:48 | 2013-10-25 07:15 | 327 | 11kV | 71286 | 218 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of 11kV feeder ex ZN35370 Cp555 Arcadia Park Tripped on SEL Abnormal Switching CP555 CLosed AB275 Open and Defective Cause: SEL defective | October | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2013-10-25 | N | 327 | N | 4 | N | N | 1.1101 | 39.4971 | 52093.7062
[7 empty] | 16002 | 14650 | 1032390 | 2013-10-25 10:10 | 2013-10-25 11:45 | 95 | 11kV | 27245 | 299 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn14143 Somersby Pa10 fdr tripped on B&Cphase IOC 11kv trip Cause: Adjacent AB40488 workmen reported to DOp seeing branch hit & fall thru HV Mains. Note: Pa10 Spring Charging does not indicate in control room. Also could not be closed using SCADA in Control Room or Somersby. Cloased by DOp in Zone Manually See 1032997,3000,1 Exclude 1032390 | October | 2013 | 2014Q2 | 2014 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Veg | 2013-10-25 | N | 91.1204 | N | 4 | N | N | 1.1101 | 39.4971 | 19909.8424
[7 empty] | 15916 | 13291 | 1032612 | 2013-10-25 16:50 | 2013-10-25 18:35 | 105 | 11kV | 1365 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 137633 interrupt supple to fix wire off pin and replace x-arm at P: FN-10226. near sub 51133. | October | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-10-25 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 16368 | 18727 | 1032671 | 2013-10-25 21:20 | 2013-10-26 00:20 | 180 | 11kV | 180 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 137634 Broken LL Lead Excluded OMS 1032671 | October | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2013-10-25 | N | 180 | N | 4 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 16227 | 17332 | 1032723 | 2013-10-26 12:00 | 2013-10-26 15:20 | 200 | 11kV | 20800 | 104 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 137638/01& 02 11kV OHM isolated to repair broken 33kV crossarm at pole HR-61029. Outage to Fdr 30028 to repair broken 33kV crossarm on pole HR-61029. CB 30028 opened at 1107hrs. | October | 2013 | 2014Q2 | 2014 | 502:48010 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2013-10-26 | N | 200 | N | 1 | N | N | 1.1101 | 39.4971 | 15200.0265
[7 empty] | 15880 | 12929 | 1032814 | 2013-10-27 07:53 | 2013-10-27 11:12 | 199 | 11kV | 1393 | 7 | HV | Animal Bird | Animal | Insulator | Unplanned | Unselected | N | PT11501 Kirks Ironbark 1.0 the footpath side HDO has blown (31.5) 11kv bushings on tank has flashed over after animal contact. Shroud has completely burnt away. Requires inspection/repair. See 1033049 exclude 1032814 | October | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2013-10-27 | N | 199 | N | 4 | N | N | 1.1101 | 39.4971 | 1017.9633
[7 empty] | 16290 | 17892 | 1032866 | 2013-10-27 13:59 | 2013-10-27 16:02 | 123 | 11kV | 184641 | 1791 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN15010 Careel Bay, Panel 7 "S16539 Barrenjoey Eastbourne" 11kV feeder tripped on: EF, EFI, F/C. Field EFI's operated: S16539, CP24706, S46683, S16540, S16542, S16335, S17032, S16543, S16544, S16545, S16361, S15234. Note: Protection malfunction as S47668 EFI did not operate. UG fault between S47668 Crescent Old Barrenjoey (SW/B) and S16720 Old Barrenjoey Sanders (SW/A). OMS numbers: 1033053, 1033058, 1033071, 1032866, 1032867, 1032868 | October | 2013 | 2014Q2 | 2014 | ZN15010:PA7 | ZN15010:PA30 | ZN15010/000030 | NORTHERN BEACHES | UG | Not Veg | 2013-10-27 | N | 103.0938 | N | 4 | N | N | 1.1101 | 39.4971 | 134930.1968
[7 empty] | 15245 | 5581 | 1032825 | 2013-10-27 09:41 | 2013-10-27 17:00 | 439 | 11kV | 19044 | 798 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137643 1 fault operation Sensitive Earth fault tree into mains at pole IU-30038 targets = NC 1 & 3, SEF Check, Aux R1, BGN Excluded oms # 1032825 | October | 2013 | 2014Q2 | 2014 | 216:10724 | 216:10724 | ZN00216/010724 | LAKE MACQUARIE | OH | Veg | 2013-10-27 | N | 23.8647 | N | 4 | N | N | 1.1101 | 39.4971 | 13916.7935
[7 empty] | 16399 | 19155 | 1032917 | 2013-10-27 22:48 | 2013-10-28 00:50 | 122 | 11kV | 227066 | 2023 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | 11KV Panel 44 labelled "S.2156 & S.47860" @ ZN116 Leichardt tripped on: Relays: A & B phase timed O/C, EFI Signals: Group earth Tx2 & Tx4, 11kv trip Field EFI's: S47860, S6088, S8311, S1540 & @ UGOH to S1436 Abnormal: N/O Sw/A closed @ S1488 Mary Church. Open SwA @ S2359 Henry Lil. See DMA: defective UGOH @ PT.1862 Lillyfield Trev Remarks: Possible possums. Mains to patrol in the morning sections of 11kv overhead feeder to S1436 Callan Park No.1 | October | 2013 | 2014Q2 | 2014 | ZN116:PA34 | ZN116:PA12 | ZN00116/000012 | INNER WEST | OH | Not Veg | 2013-10-27 | N | 112.2422 | N | 4 | N | N | 1.1101 | 39.4971 | 165933.1355
[7 empty] | 16342 | 18445 | 1032921 | 2013-10-28 00:15 | 2013-10-28 01:45 | 90 | 11kV | 179820 | 1998 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At Zn36300 Balgowlah North Zone, panel 3 "S17119, etc" tripped on: A and C phased timed O/C, EFI, Fault Check. No field EFI's operated. Cause not ascertained. OH mains crew to patrol feeder. | October | 2013 | 2014Q2 | 2014 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Veg | 2013-10-28 | N | 90 | N | 5 | N | N | 1.1101 | 39.4971 | 131407.1522
[7 empty] | 16206 | 17116 | 1032923 | 2013-10-28 04:57 | 2013-10-28 06:15 | 78 | 11kV | 51796 | 1426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137648 2 fault operations Overcurrent; Sensitive Earth Fault fdr patrolled by DOp. No fault found. Excluded OMS 1032923. | October | 2013 | 2014Q2 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2013-10-28 | N | 36.3226 | N | 5 | N | N | 1.1101 | 39.4971 | 37850.9891
[7 empty] | 15606 | 9691 | 1033160 | 2013-10-28 10:56 | 2013-10-28 12:25 | 89 | 11kV | 8898.35 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | Rain Light | N | PT 61229 Mulyan Yamba - Centre phase HDO (63A). Cause not ascertained. DOp unable to read MDI. ME: 1033160. ME GIS: 1033177. | October | 2013 | 2014Q2 | 2014 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Veg | 2013-10-28 | N | 88.9835 | N | 5 | N | N | 1.1101 | 39.4971 | 6502.6517
[7 empty] | 15381 | 7201 | 1033399 | 2013-10-28 17:42 | 2013-10-28 19:20 | 98 | 11kV | 48484 | 949 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 137656 2 fault operations 3 phase Earth fault CB 58 Broadmedow tripped and L/O on: E/F, suspect ug cable fault dq Excluded oms 1033399 | October | 2013 | 2014Q2 | 2014 | 208:58 | 257:81987 | ZN00257/081987 | NEWCASTLE | UG | Not Veg | 2013-10-28 | N | 51.0896 | N | 5 | N | N | 1.1101 | 39.4971 | 35430.6772
[7 empty] | 16082 | 15783 | 1033435 | 2013-10-28 22:18 | 2013-10-29 00:40 | 142 | 11kV | 6390 | 45 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137657 B phase DOLF : 20 Amp Found dead birds at base of pole Volts = 242V, Loads = 110A, 15A, 85A Excluded OMS 1033435 | October | 2013 | 2014Q2 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2013-10-28 | N | 142 | N | 5 | N | N | 1.1101 | 39.4971 | 4669.6235
[7 empty] | 14699 | 33 | 1035238 | 2013-10-29 02:47 | 2013-10-29 04:12 | 85 | 11kV | 100555 | 1183 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | 1kV Panel 4 Labelled LB2929 Pennant Hills Tripped and reclosed on A and C phase IOC, A and C phase timed overload, timing relay, lockout relay EFI. Possum found on GV UGOH below LB486 and removed. | October | 2013 | 2014Q2 | 2014 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | OH | Not Veg | 2013-10-29 | N | 85 | N | 33 | Y | Y | 1.1101 | 39.4971 | 73482.6281
[7 empty] | 16014 | 14778 | 1033438 | 2013-10-29 03:00 | 2013-10-29 04:34 | 94 | 11kV | 157920 | 1680 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9700 Kirrawee - Pnl 23 - B & C phase IOC. Possum cleared from HV mains. Corner of Sylvania and Bunarba near PT 9295. OH mains to inspect in the daylight. ME: 1033438. Withdrawn: 1033439. | October | 2013 | 2014Q2 | 2014 | ZN9700:PA23 | ZN9700:PA23 | ZN09700/000023 | SUTHERLAND | OH | Not Veg | 2013-10-29 | N | 94 | N | 33 | Y | Y | 1.1101 | 39.4971 | 115403.2781
[7 empty] | 16080 | 15753 | 1033510 | 2013-10-29 09:09 | 2013-10-29 12:35 | 206 | 11kV | 206 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137670 Single phase DOLF : 10 Amp Excluded OMS 1033510 | October | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-10-29 | N | 206 | N | 33 | Y | Y | 1.1101 | 39.4971 | 150.5387
[7 empty] | 14901 | 1951 | 1033672 | 2013-10-29 12:11 | 2013-10-29 12:55 | 44.15 | 11kV | 1412.8 | 32 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex n12630 Peats Ridge section of Pa1 "Grants Rd" AB44109 was opened for safety Tree Branch on 11kv near PT13322 George Downes Kyola | October | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-10-29 | N | 44.15 | N | 33 | Y | Y | 1.1101 | 39.4971 | 1032.4326
[7 empty] | 16220 | 17253 | 1033778 | 2013-10-29 13:13 | 2013-10-29 13:47 | 33.5833 | 11kV | 41307.5 | 1230 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S2635 Epping PA57 feeder tripped reclosed tripped and locked oout on IOC A and B phase Cause: Tree branch on mains adjacent to AB523 See OMS 1033778 1033825 1033803 | October | 2013 | 2014Q2 | 2014 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | OH | Veg | 2013-10-29 | N | 33.5833 | N | 33 | Y | Y | 1.1101 | 39.4971 | 30186.3026
[7 empty] | 15523 | 8734 | 1033839 | 2013-10-29 13:19 | 2013-10-29 14:40 | 81 | 11kV | 42117 | 742 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | N | At S3425 Castle Cove Panel 28 tripped and reclose don B and C phase IOC and Timed lockout Cause: 2 crossarms broken and head of pole split See OMS 1035921 1035924 1035929 1033839 1033948 | October | 2013 | 2014Q2 | 2014 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Not Veg | 2013-10-29 | N | 56.7615 | N | 33 | Y | Y | 1.1101 | 39.4971 | 30777.8614
[7 empty] | 15821 | 12347 | 1036334 | 2013-10-29 13:39 | 2013-10-29 15:14 | 95 | 11kV | 39330 | 414 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | @Zn12570 Avoca Pa26 fdr tripped on Relays: Bphase IOC, EFI Signals: 11kv trip Cause: weather related. possible lightning strike See 1036334,5 exclude 1033857 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2013-10-29 | N | 95 | N | 33 | Y | Y | 1.1101 | 39.4971 | 28741.204
[7 empty] | 15278 | 6194 | 1033799 | 2013-10-29 13:10 | 2013-10-29 15:20 | 130 | 11kV | 1820 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 137693 Single phase DOLF : 10 Amp | October | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2013-10-29 | N | 130 | N | 33 | Y | Y | 1.1101 | 39.4971 | 1330.0023
[7 empty] | 16272 | 17687 | 1033987 | 2013-10-29 14:10 | 2013-10-29 15:31 | 81 | 11kV | 136845 | 1913 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn12640 Umina Pa2 fdr tripped, reclosed, tripped & locked out Relays: BC phase O/C, lock out Signals: 11kv trip Cause: tree/branch on OH Mains Near AB43157 See 1036341,2,3,4 Exclude 1033987 | October | 2013 | 2014Q2 | 2014 | ZN12640:PA2 | ZN12640:PA2 | ZN12640/000002 | CENTRAL COAST | OH | Veg | 2013-10-29 | N | 71.5342 | N | 33 | Y | Y | 1.1101 | 39.4971 | 100002.2898
[7 empty] | 14991 | 2749 | 1033961 | 2013-10-29 14:06 | 2013-10-29 15:37 | 91 | 11kV | 369187 | 4057 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Circuit Breaker | Unplanned | Wind | N | ZN 10995 Riverwood - Pnl 2 - trip/reclose/trip, A phase IOC, OC, timing, lockout. Cause not ascertained. Possible branch because of the strong winds. ME: 1035289. Withdrawn: Seriously heaps. | October | 2013 | 2014Q2 | 2014 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | Unknown | Unknown | 2013-10-29 | N | 91 | N | 33 | Y | Y | 1.1101 | 39.4971 | 269790.9704
[7 empty] | 15656 | 10521 | 1033797 | 2013-10-29 13:20 | 2013-10-29 16:00 | 160 | 11kV | 2960 | 35 | HV | Vegetation Blow/Fall In | Vegetation | Feeder/Distributor O/H | Unplanned | Wind | N | At S3472 Sefton Panel #18 Chisholm Marjorie Fdr tripped on: C phase IOC and timed O/L Remarks: weather related. Large tree branch brought down on HV phase onto LV mains in Bellona Ave Regents Park | October | 2013 | 2014Q2 | 2014 | ZN3472:PA18 | ZN3472:PA18 | ZN03472/000018 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-10-29 | N | 84.5714 | N | 33 | Y | Y | 1.1101 | 39.4971 | 2163.0807
[7 empty] | 14954 | 2326 | 1035478 | 2013-10-29 13:50 | 2013-10-29 16:55 | 185 | 11kV | 555 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 137691 3 phase subs isolated to repair broken fuse arm | October | 2013 | 2014Q2 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2013-10-29 | N | 185 | N | 33 | Y | Y | 1.1101 | 39.4971 | 405.5776
[7 empty] | 16141 | 16410 | 1033992 | 2013-10-29 14:13 | 2013-10-29 17:00 | 167 | 11kV | 12728 | 174 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137680 2 fault operations B phase mains down near sub51092 section isolated for repair Excluded oms 1033992 | October | 2013 | 2014Q2 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2013-10-29 | N | 73.1494 | N | 33 | Y | Y | 1.1101 | 39.4971 | 9301.247
[7 empty] | 14980 | 2634 | 1033854 | 2013-10-29 14:21 | 2013-10-29 17:25 | 184 | 11kV | 110953 | 1820 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S1287 Revesby Panel 15 The Ashmead Ave Fdr tripped on C ph IOC and timed O/L. Reclose timing and lockout Remarks: weather related. Large tree blown down onto 11kv mains cnr. Burns and Kennedy Rds Picnic Point. | October | 2013 | 2014Q2 | 2014 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Veg | 2013-10-29 | N | 60.9632 | N | 33 | Y | Y | 1.1101 | 39.4971 | 81081.1798
[7 empty] | 15185 | 4438 | 1034502 | 2013-10-29 16:01 | 2013-10-29 17:50 | 109 | 11kV | 8720 | 80 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | ExZn12640 Umina section of Pa18 @PT13537 Crystal Diamond roadside pase 40A HDO fuse operated Cause: Weather relatd. Lightning also refer to Trip and reclose on CP45090 - OMS 1036351 at 1600 | October | 2013 | 2014Q2 | 2014 | ZN12640:PA18 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Not Veg | 2013-10-29 | N | 109 | N | 33 | Y | Y | 1.1101 | 39.4971 | 6372.3188
[7 empty] | 15735 | 11431 | 1034407 | 2013-10-29 15:48 | 2013-10-29 18:15 | 147 | 11kV | 1029 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Ex Zn13000 Lake Munmorah section of Pa4 @PT14250 Kanangra Orana roadside HDO operated 31.5 Amps Cause: Lightning/Surge Arrestor exploded during storm. Linesman repaired | October | 2013 | 2014Q2 | 2014 | ZN13000:PA4 | ZN13000:PA4 | ZN13000/000004 | CENTRAL COAST | OH | Not Veg | 2013-10-29 | N | 147 | N | 33 | Y | Y | 1.1101 | 39.4971 | 751.9628
[7 empty] | 15803 | 12139 | 1034693 | 2013-10-29 17:44 | 2013-10-29 18:41 | 57 | 11kV | 28842 | 506 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | Zn12570 Avoca Pa34 "Terrigal" Fdr tripped and reclosed on Relays: B,C phase IOC Signals: 11kv trip ABNORMAL:LB41002 open, LB45088 Open, Open bonds (defective), AB44119 closed, S18705/SwB Clsoed Cause: Burnt Branch found by DOp below Mains corner lake shore See 1036360 exclude 1034693,720 | October | 2013 | 2014Q2 | 2014 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2013-10-29 | N | 57 | N | 33 | Y | Y | 1.1101 | 39.4971 | 21076.8829
[7 empty] | 15678 | 10777 | 1034292 | 2013-10-29 15:20 | 2013-10-29 19:10 | 230 | 11kV | 9430 | 41 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137695 B & C phase DOLF : 20 Amp High voltage into low voltage near S.16810 Vine st. due to tree on mains. Excluded OMS 1034346. | October | 2013 | 2014Q2 | 2014 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 230 | N | 33 | Y | Y | 1.1101 | 39.4971 | 6891.1659
[7 empty] | 16158 | 16592 | 1034250 | 2013-10-29 15:19 | 2013-10-29 19:12 | 233 | 11kV | 140013 | 789 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | ZN 9900 Menai - Pnl 12 - Trip/reclose/trip, A phase IOC, SEL, lockout, timing, reclose. 11kV overhead down near Ocean Rd, Illawong. Linesmen have repaired. ME: 1035271. Rest Step: 1035273. Withdrawn: 1034250, 347. | October | 2013 | 2014Q2 | 2014 | ZN9900:PA12 | ZN9900:PA12 | ZN09900/000012 | SUTHERLAND | OH | Not Veg | 2013-10-29 | N | 177.4563 | N | 33 | Y | Y | 1.1101 | 39.4971 | 102317.3707
[7 empty] | 15924 | 13375 | 1034224 | 2013-10-29 15:01 | 2013-10-29 20:25 | 324 | 11kV | 182277 | 1596 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137715 2 fault operations 3 phase Overcurrent; Earth fault 11kV surge arrestor failed on ugoh to sub 23477 Excluded oms 1034224 | October | 2013 | 2014Q2 | 2014 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2013-10-29 | N | 114.2086 | N | 33 | Y | Y | 1.1101 | 39.4971 | 133202.6553
[7 empty] | 15751 | 11646 | 1034747 | 2013-10-29 18:23 | 2013-10-29 21:15 | 172 | 11kV | 688 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 137703 C phase DOLF : 10 Amp REPLACED 3 X FUSES Excluded OMS 1034747 | October | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2013-10-29 | N | 172 | N | 33 | Y | Y | 1.1101 | 39.4971 | 502.7701
[7 empty] | 14872 | 1699 | 1034341 | 2013-10-29 15:24 | 2013-10-29 21:42 | 378 | 11kV | 83160 | 220 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137712 3 fault operations 3 phase Overcurrent branch on OHM in Lisadell Rd removed by dop dq | October | 2013 | 2014Q2 | 2014 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 378 | N | 33 | Y | Y | 1.1101 | 39.4971 | 60770.8752
[7 empty] | 15018 | 2978 | 1034349 | 2013-10-29 15:33 | 2013-10-29 23:15 | 462 | 11kV | 345576 | 748 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137718 3 phase Overcurrent tree removed from 11kV mains adj sub 16231 Ash st. | October | 2013 | 2014Q2 | 2014 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 462 | N | 33 | Y | Y | 1.1101 | 39.4971 | 252536.748
[7 empty] | 15929 | 13411 | 1034700 | 2013-10-29 17:51 | 2013-10-29 23:20 | 329 | 11kV | 113520 | 390 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 137717 A phase burnt off bond on 11kV ohm. nil protection Excluded oms 1034700 | October | 2013 | 2014Q2 | 2014 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | OH | Not Veg | 2013-10-29 | N | 291.0769 | N | 33 | Y | Y | 1.1101 | 39.4971 | 82957.0677
[7 empty] | 14931 | 2135 | 1034884 | 2013-10-29 22:35 | 2013-10-29 23:43 | 68 | 11kV | 14960 | 220 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137709 3 fault operations 3 phase Earth fault tree removed off 11kV OHM | October | 2013 | 2014Q2 | 2014 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 68 | N | 33 | Y | Y | 1.1101 | 39.4971 | 10932.3268
[7 empty] | 15000 | 2873 | 1034291 | 2013-10-29 15:19 | 2013-10-30 00:11 | 532 | 11kV | 10108 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137714 5 fault operations 3 phase Overcurrent tree on 11kV OHM Excluded oms 1034291 | October | 2013 | 2014Q2 | 2014 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 532 | N | 33 | Y | Y | 1.1101 | 39.4971 | 7386.6283
[7 empty] | 15090 | 3577 | 1034115 | 2013-10-29 14:36 | 2013-10-30 00:30 | 594 | 11kV | 212650 | 1582 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 137681 3 fault operations A & B phase Overcurrent | October | 2013 | 2014Q2 | 2014 | 503:48017 | 532:83300 | ZN00532/083300 | MAITLAND | OH | Veg | 2013-10-29 | N | 134.4185 | N | 33 | Y | Y | 1.1101 | 39.4971 | 155398.3479
[7 empty] | 15356 | 6874 | 1034083 | 2013-10-29 14:34 | 2013-10-30 01:00 | 626.3667 | 11kV | 81427.6667 | 130 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | PT 10367 Gladstone Dunmore - B phase HDO (31.5A). B phase bond burnt at PT 10367. Oatley mains temporarily repaired. | October | 2013 | 2014Q2 | 2014 | ZN10999:PA12 | ZN10999:PA12 | ZN10999/000012 | BAYSIDE | OH | Not Veg | 2013-10-29 | N | 626.3667 | N | 33 | Y | Y | 1.1101 | 39.4971 | 59504.9371
[7 empty] | 14964 | 2449 | 1034901 | 2013-10-30 00:43 | 2013-10-30 01:48 | 65 | 11kV | 129870 | 1998 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Unselected | N | At S.36300 Balgowlah Nth, 11kV Panel 3 Fdr CB tripped on A,B and C phase IOC, 11kV trip, efi. No Field efi's operated. Possum at LB.61276 | October | 2013 | 2014Q2 | 2014 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2013-10-30 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 94905.1655
[7 empty] | 15638 | 10175 | 1034290 | 2013-10-29 15:14 | 2013-10-30 03:35 | 741 | 11kV | 352545 | 847 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137722 2 fault operations 3 phase Earth Fault; Overcurrent Prot 1.2.1 51 ABC 51N Tree into mains tee to sub 10023 Excluded OMS 1034290 | October | 2013 | 2014Q2 | 2014 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 416.2279 | N | 33 | Y | Y | 1.1101 | 39.4971 | 257629.4877
[7 empty] | 15290 | 6339 | 1034198 | 2013-10-29 14:44 | 2013-10-30 15:20 | 1476 | 11kV | 159520 | 306 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137692 3 phase Wires down and damaged arms after FQ-95123 Excluded OMS 1034198, 1034876, 1034300 | October | 2013 | 2014Q2 | 2014 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2013-10-29 | N | 521.3072 | N | 33 | Y | Y | 1.1101 | 39.4971 | 116572.511
[7 empty] | 15507 | 8557 | 1034167 | 2013-10-29 14:46 | 2013-10-30 15:50 | 1504 | 11kV | 133653 | 371 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137711 3 fault operations 3 phase OvercurrentTree on mains near S.52828 Redman. Tree on mains near S50541 College Entrance. Excluded OMS 1034167 | October | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 360.2507 | N | 33 | Y | Y | 1.1101 | 39.4971 | 97669.6703
[7 empty] | 16155 | 16536 | 1034264 | 2013-10-29 15:39 | 2013-10-30 15:55 | 1456 | 11kV | 24328 | 43 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 137707 Wire found live on ground:15 Amp DOLF at 4788. Large tree fell on 11kV mains along Italia Rd @ pole KQ10053. Mains down from KQ10006 to KQ40030. Damage from KQ10136 to ABS47258. Pole @ sub15518 split full length.Despatch arranging customers installations checked HV may have contacted mains @ sub15518 & possibly @ sub25736 & sub5735.Most staff near 16 hour cap & Maitland mgt advised site was made safe & they would start repairs 5am on 30th. 1 fuse blew but further down line all 3 phases on ground | October | 2013 | 2014Q2 | 2014 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2013-10-29 | N | 565.7674 | N | 33 | Y | Y | 1.1101 | 39.4971 | 17778.1848
[7 empty] | 16001 | 14643 | 1035592 | 2013-10-29 14:42 | 2013-10-30 16:05 | 1523 | 11kV | 55895 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 137699 Tree on mains after 40764 PROT EF 57 AMPS TREE ON MAINS POLE 8V-80107 SECTION ISOLATED FOR REPAIR Excluded OMS 1034120 | October | 2013 | 2014Q2 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2013-10-29 | N | 553.4158 | N | 33 | Y | Y | 1.1101 | 39.4971 | 40846.4174
[7 empty] | 15271 | 6001 | 1036020 | 2013-10-30 18:50 | 2013-10-30 19:08 | 18 | 11kV | 72 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 137747 B phase NO OMS number staff found 11kV conductor broken off the insulator and lying on an 11kV cross arm near sub 26097. A modiewark detected 2kV at the base of the pole. No protection operated. | October | 2013 | 2014Q2 | 2014 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2013-10-30 | N | 18 | N | 3 | N | N | 1.1101 | 39.4971 | 52.6155
[7 empty] | 15857 | 12756 | 1036025 | 2013-10-30 16:56 | 2013-10-30 19:10 | 134 | 11kV | 2010 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137745 B & C phase DOLF : 20 Amp 11kV mains twisted together near sub 20021 blowing the line fuses. Excluded OMS # 1035411 | October | 2013 | 2014Q2 | 2014 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2013-10-30 | N | 134 | N | 3 | N | N | 1.1101 | 39.4971 | 1468.8487
[7 empty] | 15242 | 5545 | 1035459 | 2013-10-31 00:39 | 2013-10-31 02:10 | 91 | 11kV | 2366 | 26 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | At PT1868 Hall Wylds HV fuse blown Cuase: Possum at PT1868 | October | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2013-10-31 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 1729.003
[7 empty] | 16500 | 20435 | 1035649 | 2013-10-31 03:03 | 2013-10-31 04:52 | 109 | 11kV | 99389 | 1219 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At Zn 15005 Belrose, 11kV Panel 4 Fdr CB tripped and reclosed on OC. Recloser 21801 tripped on OC {Investigation into suspected lack of grading}. Bond burnt off at UG/OH between LB.24314 and S.16021 | October | 2013 | 2014Q2 | 2014 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2013-10-31 | N | 81.5332 | N | 6 | N | N | 1.1101 | 39.4971 | 72630.5497
[7 empty] | 14753 | 513 | 1035571 | 2013-10-31 12:00 | 2013-10-31 13:07 | 67 | 11kV | 67 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137760 A phase DOLF : 10 Amp | October | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2013-10-31 | N | 67 | N | 6 | N | N | 1.1101 | 39.4971 | 48.9616
[7 empty] | 15742 | 11582 | 1036034 | 2013-10-31 16:50 | 2013-10-31 18:40 | 110 | 11kV | 1870 | 17 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137763 Feeder taken out for safety to cut away section of OH cable from Fdr 48048 Branxton. Section was already isolated 29/10/13 after major storm. | October | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-10-31 | N | 110 | N | 6 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 15442 | 7885 | 1036000 | 2013-10-31 23:40 | 2013-11-01 00:33 | 53 | 11kV | 14181 | 268 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S3425 Castle Cove Panel 8 tripped on Earth Fault EFI and Fault CHeck. Cause: UG cable fault between S6947 and S249 See OMS 1038472 1038476 | October | 2013 | 2014Q2 | 2014 | ZN3425:PA8 | ZN3425:PA8 | ZN03425/000008 | WILLOUGHBY | UG | Not Veg | 2013-10-31 | N | 52.9142 | N | 6 | N | N | 1.1101 | 39.4971 | 10363.0565
[7 empty] | 16351 | 18539 | 1036003 | 2013-11-01 01:12 | 2013-11-01 01:54 | 42 | 11kV | 5082 | 121 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12570 Avoca section of Pa37L "Avoca Beach" fdr @PT13192 Avoca Ascot footpath side phase 31.5A HDO blew Cause: Possum came into contact with 11kc mains at PT13192 See 1038022 Exclude 1036003 | November | 2013 | 2014Q2 | 2014 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2013-11-01 | N | 42 | N | 3 | N | N | 1.1101 | 39.4971 | 3713.7757
[7 empty] | 16243 | 17491 | 1036004 | 2013-11-01 05:07 | 2013-11-01 05:37 | 30 | 11kV | 59940 | 1998 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Unselected | N | At ZN36300 Balgowlah North, Panel 3 "S17119 Jackson White, etc" feeder tripped on: IOC A,B and C phase. Possum came in contact with 11kV mains at surge diverters at LB 61276. Appears shroud missing. Mains to check for damage and possible replacement of shroud. Exclude OMS 1036052 | November | 2013 | 2014Q2 | 2014 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Not Veg | 2013-11-01 | N | 30 | N | 3 | N | N | 1.1101 | 39.4971 | 43802.3841
[7 empty] | 15729 | 11372 | 1035880 | 2013-10-31 15:22 | 2013-11-01 07:00 | 938 | 11kV | 5282 | 19 | HV | 3rd Party Vehicle | 3rd Party Impact | DC Not Transformer | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of Pa10 @S13511 Baker Donnison Kiosk hit by Vehicle, LV Board dmgd.HV RMI dmgd + TX leaking oil DOp interupted and isolated S13511 remotely All Dists dead into substation. Jointers LV// 11kv fdr isolated+earthed from S18165 Donnison Workcover to S12306 Comm bank Mann to S18440 Baker Georgiana via S13511 See 1037698,9,700,1 Exclude 1035880,7,91,4,909 | October | 2013 | 2014Q2 | 2014 | ZN12650:PA10 | ZN12650:PA10 | ZN12650/000010 | CENTRAL COAST | Unknown | Not Veg | 2013-10-31 | N | 278 | N | 6 | N | N | 1.1101 | 39.4971 | 3859.9298
[7 empty] | 16053 | 15430 | 1036107 | 2013-11-01 11:05 | 2013-11-01 12:05 | 60 | 11kV | 60 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 137776 C phase DOLF : 10 Amp Fuse Fatigue Excluded OMS 1036107 | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-11-01 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 15246 | 5602 | 1036386 | 2013-11-02 01:26 | 2013-11-02 03:20 | 114 | 11kV | 205799 | 2408 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 137781 1 fault operation B & C phase Overcurrent faulty ugoh pole JU-64939 left isolated Excluded oms # 1036386 | November | 2013 | 2014Q2 | 2014 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | Unknown | Unknown | 2013-11-02 | N | 85.4647 | N | 1 | N | N | 1.1101 | 39.4971 | 150391.8392
[7 empty] | 14932 | 2141 | 1036587 | 2013-11-03 11:49 | 2013-11-03 17:07 | 318 | 11kV | 8616 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 137790 1 fault operation Reclose was non auto at Sw 42032 due to it being a bush fire day and recorded defects on the line. Line patrolled - no cause found. Excluded OMS # 1036587. | November | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-11-03 | N | 187.3043 | N | 4 | N | N | 1.1101 | 39.4971 | 6296.3187
[7 empty] | 14945 | 2220 | 1036650 | 2013-11-03 16:25 | 2013-11-03 17:40 | 75 | 11kV | 225 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | Ex Zn12690 Berkeley Vale section of Pa3 11kv fdr @PT14432 Wyong Glenning footpath side 20 Amp HV fuse blown BB Batch #3493: Defective in crimp Cause: Fuse Fatigue. See 1038057 exclude 1036650 | November | 2013 | 2014Q2 | 2014 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Not Veg | 2013-11-03 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 15100 | 3697 | 1036709 | 2013-11-03 18:16 | 2013-11-03 19:25 | 69 | 11kV | 2346 | 34 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 137792 Section isolated to relace broken 11kV x-arm on pole MW-70005 Excluded OMS 1036709 | November | 2013 | 2014Q2 | 2014 | 229:34995 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Not Veg | 2013-11-03 | N | 69 | N | 4 | N | N | 1.1101 | 39.4971 | 1714.3876
[7 empty] | 15769 | 11788 | 1036581 | 2013-11-03 11:32 | 2013-11-04 02:05 | 873 | 11kV | 32379 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 137789 2 fault operations C phase Earth fault ohm down past 22k links 40764 repairs complete Excluded OMS # 1036581. | November | 2013 | 2014Q2 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2013-11-03 | N | 320.5842 | N | 4 | N | N | 1.1101 | 39.4971 | 23661.6182
[7 empty] | 16333 | 18313 | 1037027 | 2013-11-04 12:00 | 2013-11-04 13:02 | 62 | 11kV | 64430 | 1111 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | Zn.1788 matraville Pnl.8 - feeder tripped on : E/F, EFI Field EFIs: S1170 7934 807 35502 UG cable fault from S35502 to S1345 to S1146 - Cable laying contractor hit cable in Raglan St Malabar | November | 2013 | 2014Q2 | 2014 | ZN1788:PA8 | ZN1788:PA61 | ZN01788/000061 | RANDWICK | UG | Not Veg | 2013-11-04 | N | 57.9928 | N | 5 | N | N | 1.1101 | 39.4971 | 47083.5436
[7 empty] | 15853 | 12720 | 1037016 | 2013-11-04 11:50 | 2013-11-04 17:00 | 310 | 11kV | 20150 | 65 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 137797 3 phase isolation See also LID report 137797/ OMS 1037380, which records an earlier trip and reclose and earth fault. Car hit pole GS-83311 breaking both cross ams and one 11kv main part fell but was still above the low voltage, no 11k/V / LV contact. | November | 2013 | 2014Q2 | 2014 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2013-11-04 | N | 310 | N | 5 | N | N | 1.1101 | 39.4971 | 14725.0257
[7 empty] | 15097 | 3684 | 1037238 | 2013-11-04 15:47 | 2013-11-04 17:03 | 76 | 11kV | 76 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137801 Single phase DOLF : 3 Amp Excluded OMS 1037238 | November | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | UG | Not Veg | 2013-11-04 | N | 76 | N | 5 | N | N | 1.1101 | 39.4971 | 55.5386
[7 empty] | 14698 | 24 | 1037326 | 2013-11-04 18:04 | 2013-11-04 22:15 | 251 | 11kV | 98691 | 733 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 10994 Mortdale - Pnl 11 - Trip/reclose/trip, Earth fault, lockout, EFI. Suspecte underground fault between 11kV UGOH and S 10706. ME: 1037611. Rest Steps: 1037612, 3, 4, 8, 9. Rest Step GIS: 1037329. Withdrawn: 1037326, 1037347, 8. | November | 2013 | 2014Q2 | 2014 | ZN10994:PA11 | ZN10994:PA11 | ZN10994/000011 | GEORGES RIVER | UG | Not Veg | 2013-11-04 | N | 134.6398 | N | 5 | N | N | 1.1101 | 39.4971 | 72120.4719
[7 empty] | 15289 | 6335 | 1037366 | 2013-11-05 02:25 | 2013-11-05 03:20 | 55 | 11kV | 2310 | 42 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137803 B phase DOLF : 31 Amp Possum on sub Volts = 245, Loads = 47A, 167A, 23A Excluded OMS 1037366 & 1037367 | November | 2013 | 2014Q2 | 2014 | 217:33612 | 217:33612 | ZN00217/033612 | LAKE MACQUARIE | OH | Not Veg | 2013-11-05 | N | 55 | N | 2 | N | N | 1.1101 | 39.4971 | 1688.0799
[7 empty] | 14839 | 1297 | 1037379 | 2013-11-05 07:44 | 2013-11-05 09:25 | 101 | 11kV | 165795 | 2376 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @Zn12610 Long Jetty Pa11 "The Lucinda Ave" fdr tripped on SEF Cause: 11kv bond found burnt at UGOH Western end of Lucinda Ave and R/S bond found open at USL41198 See 1038431,3,6 Exclude 1037379,446 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-05 | N | 69.779 | N | 2 | N | N | 1.1101 | 39.4971 | 121158.0959
[7 empty] | 16377 | 18816 | 1037349 | 2013-11-04 20:15 | 2013-11-05 12:50 | 995 | 11kV | 137657 | 1369 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137802 2 fault operations Single phase Earth fault 11kV mains down beyond pole HQ-83801 | November | 2013 | 2014Q2 | 2014 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2013-11-04 | N | 100.553 | N | 5 | N | N | 1.1101 | 39.4971 | 100595.6754
[7 empty] | 15709 | 11046 | 1046928 | 2013-11-06 07:27 | 2013-11-06 07:44 | 17 | 11kV | 19193 | 1129 | HV | Staff Operation | Utility Process Issue | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | During switching in conjunction with D&R 325208; Recloser 21802 was closed and on opening Links 23755 Recloser 21818 tripped on SEL. Note Wallboard was NOT correctly plugged for defective sectionbetween S.16021 and LB.24314 | November | 2013 | 2014Q2 | 2014 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-11-06 | N | 17 | N | 6 | N | N | 1.1101 | 39.4971 | 14025.6783
[7 empty] | 15124 | 3919 | 1037818 | 2013-11-06 08:38 | 2013-11-06 08:52 | 14 | 11kV | 2506 | 179 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 137822 1 fault operation B phase Earth fault LA Blown at UGOH pole FQ-33173 during DSI 36319. Emergency SI attached to SI 36319. | November | 2013 | 2014Q2 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-11-06 | N | 14 | N | 6 | N | N | 1.1101 | 39.4971 | 1831.3109
[7 empty] | 16329 | 18275 | 1037876 | 2013-11-06 09:58 | 2013-11-06 11:05 | 67 | 11kV | 60970 | 910 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 6 - Earth Fault, EFI, Fault Check, Field EFIs. Underground feeder fault between S 4436 to S 35383 to S 3347. ME: 1038282. Withdrawn: 1037876. | November | 2013 | 2014Q2 | 2014 | ZN690:PA6 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-11-06 | N | 67 | N | 6 | N | N | 1.1101 | 39.4971 | 44555.0777
[7 empty] | 15771 | 11823 | 1038074 | 2013-11-06 15:56 | 2013-11-06 16:14 | 18 | 11kV | 74265 | 4192 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | Unselected | N | Zn12610 Long Jetty Pa17&Pa20 tripped on SEL. 11kv trip ABNORMAL: Section of Fdr out of service (Pa11) See 1038431. AB44476 TO AB43314 tee PT13685 with LB45159 closed. LB61289 closed with USL41198 open & defective Cause: Staff Error SEL Left Auto on reconnect Pa17&Pa20 @ Long Jetty. After defective USL41198 being returned to service See 1038470 Excliude 1038074,6,80,94,114,6,8 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | Unknown | Not Veg | 2013-11-06 | N | 17.7159 | N | 6 | N | N | 1.1101 | 39.4971 | 54270.6716
[7 empty] | 15888 | 13041 | 1038058 | 2013-11-06 15:32 | 2013-11-06 16:33 | 61 | 11kV | 610 | 10 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2635 11kv fdr Pa6 "S7740 Herring Talavera" Tripped on: Timed Earth Fault EFI Fault check Alarms: Zone Earth No1 Tx Group Earth EFI's: Nil Cause: UG Fault on frontline feeder from Pa6 | November | 2013 | 2014Q2 | 2014 | ZN2635:PA6 | ZN2635:PA33 | ZN02635/000033 | RYDE | UG | Not Veg | 2013-11-06 | N | 61 | N | 6 | N | N | 1.1101 | 39.4971 | 445.77
[7 empty] | 16203 | 17089 | 1038488 | 2013-11-06 23:20 | 2013-11-06 23:24 | 4 | 11kV | 376 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of pa1 @IR61364 Brieses Peats 0.4 tripped and reclosed on; Relays: Overcurrent Signals: Nil Cause not ascertained. | November | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2013-11-06 | N | 4 | N | 6 | N | N | 1.1101 | 39.4971 | 274.7697
[7 empty] | 16400 | 19156 | 1038227 | 2013-11-07 07:01 | 2013-11-07 08:10 | 69 | 11kV | 10390 | 156 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1610 Homebush Bay 11kv fdr Pnl 20 'S1310 Coal St' tripped on: Earth fault EFI Field EFI's Nil Remarks: UG fault. Front Line fdr from Pnl 20 Homebush Bay to Sub 1320 Coal St | November | 2013 | 2014Q2 | 2014 | ZN1610:PA17 | ZN1610:PA17 | ZN01610/000017 | PARRAMATTA | UG | Not Veg | 2013-11-07 | N | 66.6026 | N | 4 | N | N | 1.1101 | 39.4971 | 7592.7055
[7 empty] | 16447 | 19912 | 1038388 | 2013-11-07 11:53 | 2013-11-07 14:25 | 152 | 11kV | 2128 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S787 Thomas Johnson 63A HVDO fuse operated. Cause not ascertained for outage see OMS 1039656 1038441 1038473 1038388 | November | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-11-07 | N | 152 | N | 4 | N | N | 1.1101 | 39.4971 | 1555.0796
[7 empty] | 14743 | 391 | 1038697 | 2013-11-07 14:20 | 2013-11-07 14:55 | 35 | 11kV | 70 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa1 Feeder beyond LB45201 interrupted to cut away blown lightning surge arrestor on UGOH adjacent S14077 | November | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Not Veg | 2013-11-07 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 51.1539
[7 empty] | 15461 | 8051 | 1038600 | 2013-11-07 17:30 | 2013-11-07 22:15 | 285 | 11kV | 1140 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 137842 No protection operations. Section isolated to repair wire off pin pole JR-25519. OMS 108600 | November | 2013 | 2014Q2 | 2014 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Not Veg | 2013-11-07 | N | 285 | N | 4 | N | N | 1.1101 | 39.4971 | 833.0784
[7 empty] | 14826 | 1191 | 1038737 | 2013-11-08 09:50 | 2013-11-08 10:28 | 38 | 11kV | 114 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Hot >35C | N | LID 137858 C phase DOLF : 10 Amp Tx Volts = 248V Excluded OMS No. 1038737 | November | 2013 | 2014Q2 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | UG | Not Veg | 2013-11-08 | N | 38 | N | 4 | N | N | 1.1101 | 39.4971 | 83.3078
[7 empty] | 15048 | 3165 | 1039036 | 2013-11-08 22:11 | 2013-11-08 22:55 | 44 | 11kV | 50424 | 1146 | HV | Arcing | Equipment Failure | Insulator | Unplanned | Unselected | N | At S965 Pennant hills Panel 11 tripped on SEF. Cause: Dop found arcing orn closed at AB307 | November | 2013 | 2014Q2 | 2014 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Not Veg | 2013-11-08 | N | 44 | N | 4 | N | N | 1.1101 | 39.4971 | 36848.3719
[7 empty] | 15876 | 12893 | 1039054 | 2013-11-09 00:45 | 2013-11-09 04:20 | 215 | 11kV | 11610 | 54 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137860 1 fault operation Sensitive Earth Fault possum on sub pole 70292 Excluded oms 1039054 | November | 2013 | 2014Q2 | 2014 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Not Veg | 2013-11-09 | N | 215 | N | 10 | N | N | 1.1101 | 39.4971 | 8484.2456
[7 empty] | 15780 | 11905 | 1038643 | 2013-11-08 03:30 | 2013-11-09 08:45 | 1755 | 11kV | 7020 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | @S3537 Marigold Byrne C phase 75A OEFMA HV Fuse operated. Remarks: Transformer tail defective. At Sub 3537 Marigold Byrne it appears as the Tx tails have failed and is a compound endbox. Section of feeder from Sub 4991 Marigold Amour No.2 to CP1394 Marigold Mil tee to Sub 2802 Marigold ML No.1 tee to PT 1858 Marigold WB Pump. | November | 2013 | 2014Q2 | 2014 | ZN2196:PA13 | ZN2196:PA13 | ZN02196/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-11-08 | N | 1755 | N | 4 | N | N | 1.1101 | 39.4971 | 5130.0089
[7 empty] | 15892 | 13112 | 1039061 | 2013-11-09 02:36 | 2013-11-09 09:30 | 414 | 11kV | 5321 | 1191 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | ZN 9245 Engadine - Pnl 8 - Trip/reclose, A phase timed OC, Lockout, EFI, Field EFIs. At PT 9014 Darangan Princes - 2 x HDO fuses operated. Possum blew up at PT 9014, damaging middle phase HDO assembly. ME: 1039850. Rest Step: 1039852. Withdrawn: 1039060, 1. | November | 2013 | 2014Q2 | 2014 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2013-11-09 | N | 4.4677 | N | 10 | N | N | 1.1101 | 39.4971 | 3888.4299
[7 empty] | 16255 | 17537 | 1039086 | 2013-11-09 10:16 | 2013-11-09 11:41 | 85 | 11kV | 108869 | 1289 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S129 Hunters Hill Pa12 Labelled Serius Lane Tripped on Earth Fault EFI, Frame Leakage and Fault Check. Cause: 11kV section of feeder from S8182 SW/A to S8023 SW/B UG cable fault See OMS 1041033 1041032 | November | 2013 | 2014Q2 | 2014 | ZN129:PA12 | ZN129:PA56 | ZN00129/000056 | LANE COVE | UG | Not Veg | 2013-11-09 | N | 84.46 | N | 10 | N | N | 1.1101 | 39.4971 | 79558.2541
[7 empty] | 15411 | 7555 | 1039042 | 2013-11-08 22:39 | 2013-11-09 12:35 | 836 | 11kV | 274810 | 2155 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn14891 Wyong Pa10 "Wyongah" fdr tripped on Relays: A7BPhase O/C, EFI, Fault Check Signals: 11kv trip EFI's: Operated down to and including S18445 ABNORMAL: IT40118 Murrawal Kilpa 0.2 SEL & REC N/A & Made Non tripping @ interlliruptor Cause: Vehicl hit pole. Section of 11kv OH isolated from LB45068 to LB41468 tee PT's 11813,13098,13606 See 1039821,4,5,6 Exclude 1039042,4,5,51,2,3 | November | 2013 | 2014Q2 | 2014 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2013-11-08 | N | 127.522 | N | 4 | N | N | 1.1101 | 39.4971 | 200823.0425
[7 empty] | 14803 | 979 | 1039140 | 2013-11-09 15:17 | 2013-11-09 16:50 | 93 | 11kV | 5580 | 60 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT11265 The Entrance Whalan the footpath side HDO (31.5) was found blown Cause: Fuse Fatigue See 1039857 GIS 1039140 Exclude 1039136,45 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2013-11-09 | N | 93 | N | 10 | N | N | 1.1101 | 39.4971 | 4077.6994
[7 empty] | 15063 | 3335 | 1039124 | 2013-11-09 15:30 | 2013-11-09 16:50 | 80 | 11kV | 160 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 137868 A phase Burnt off LLC oms 1039124 | November | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-11-09 | N | 80 | N | 10 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 15941 | 13612 | 1040079 | 2013-11-09 18:05 | 2013-11-09 19:00 | 55 | 11kV | 6826 | 2830 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At Sub 1285 Greenacre Park: Panel 31 "Anzac Dominion etc" opened and reclosed on: Relays: A phase IOC, Lockout & Timing Relay. Signals: 11kv trip, Zn Earth, Grp Earth Abnormal: AB 2481 closed , AB704 open and defectivie Remarks: fuse failure. Blown HDO Fuse @ PT1576. Fuse size: 31.5K (B phase) | November | 2013 | 2014Q2 | 2014 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-11-09 | N | 2.412 | N | 10 | N | N | 1.1101 | 39.4971 | 4988.2395
[7 empty] | 16375 | 18793 | 1039167 | 2013-11-09 18:09 | 2013-11-09 19:28 | 79 | 11kV | 52181 | 713 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Wind | N | ZN 10993 Hurstville North - Pnl 7 - Trip/reclose/trip, OC, timing, reclose, EFI, Field EFIs. (EFI at S 10944 had suspect operation). 11kV underground feeder fault between S 10275 and S 10944. ME: 1039831. Rest Step: 1039835. Withdrawn: 1039167. | November | 2013 | 2014Q2 | 2014 | ZN10993:PA7 | ZN10993:PA33 | ZN10993/000033 | GEORGES RIVER | UG | Not Veg | 2013-11-09 | N | 73.1851 | N | 10 | N | N | 1.1101 | 39.4971 | 38132.3357
[7 empty] | 15741 | 11530 | 1039166 | 2013-11-09 18:04 | 2013-11-09 20:17 | 133 | 11kV | 178990 | 1846 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Electrical Storm | N | LID 137870 2 fault operations A phase Overcurrent after initial fault CB tripped free on 4 attempts to close. no fault found repairs arranged for CB. Excluded oms# 1039166 | November | 2013 | 2014Q2 | 2014 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | Unknown | Not Veg | 2013-11-09 | N | 96.961 | N | 10 | N | N | 1.1101 | 39.4971 | 130800.6127
[7 empty] | 16386 | 18933 | 1039134 | 2013-11-09 15:10 | 2013-11-09 22:05 | 415 | 11kV | 114593 | 1497 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 137865 1 fault operation B phase Overcurrent; Earth fault reclose off for total fire ban faulty ugoh at pole IV-67209 repairs complete Excluded oms # 1039134; 1039143; 1039152 | November | 2013 | 2014Q2 | 2014 | 206:34434 | 206:34434 | ZN00206/034434 | LAKE MACQUARIE | Unknown | Unknown | 2013-11-09 | N | 76.5484 | N | 10 | N | N | 1.1101 | 39.4971 | 83741.1845
[7 empty] | 15948 | 13677 | 1039205 | 2013-11-09 23:46 | 2013-11-10 01:46 | 120 | 11kV | 192096 | 2143 | HV | Animal Bird | Animal | UGOH | Unplanned | Unselected | N | ZN 10999 Kogarah - Pnl 22 - Trip/reclose/trip, A & B phase IOC, EFI, Fault Check, Lock out, Field EFIs. Section of Feeder from S 10929 to USL 30484 tee S 10978 isolated. Birds nest on UGOH near S 10929 has caused flash over. ME: 1039934. Rest Steps: 1039935, 7. Withdrawn: 1039205, 7. | November | 2013 | 2014Q2 | 2014 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | OH | Not Veg | 2013-11-09 | N | 89.6388 | N | 10 | N | N | 1.1101 | 39.4971 | 140378.0909
[7 empty] | 14712 | 145 | 1040045 | 2013-11-10 03:12 | 2013-11-10 04:25 | 73 | 11kV | 73 | 1 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 137875 3 Phase isolation 11kV fdr 18146 Newdell interupted due to 33kv pole about to fall into 11kV see LID report 137874 | November | 2013 | 2014Q2 | 2014 |  |  |  | MUSWELLBROOK | OH | Not Veg | 2013-11-10 | N | 73 | N | 10 | N | N | 1.1101 | 39.4971 | 53.3462
[7 empty] | 16189 | 16949 | 1039228 | 2013-11-10 03:42 | 2013-11-10 04:50 | 68 | 11kV | 3876 | 57 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137876 A & B phase DOLF : 40 Amp possum on tx Excluded oms 1039228 | November | 2013 | 2014Q2 | 2014 | 225:33679 | 270:83586 | ZN00270/083586 | LAKE MACQUARIE | OH | Not Veg | 2013-11-10 | N | 68 | N | 10 | N | N | 1.1101 | 39.4971 | 2832.4665
[7 empty] | 15448 | 7922 | 1039240 | 2013-11-10 05:22 | 2013-11-10 08:00 | 158 | 11kV | 474 | 3 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 137877 B phase DOLF : 10 Amp Possum. Excluded OMS # 1039240. | November | 2013 | 2014Q2 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2013-11-10 | N | 158 | N | 10 | N | N | 1.1101 | 39.4971 | 346.3852
[7 empty] | 15447 | 7920 | 1039266 | 2013-11-10 08:05 | 2013-11-10 09:45 | 100 | 11kV | 100 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 137879 Single phase DOLF : 10 Amp VOLTS 242 LOAD 41AMPS Excluded OMS 1039266 | November | 2013 | 2014Q2 | 2014 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | UG | Not Veg | 2013-11-10 | N | 100 | N | 10 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 16411 | 19287 | 1039284 | 2013-11-10 08:40 | 2013-11-10 10:40 | 120 | 11kV | 17681 | 307 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser CP428 Bayfield Rd tripped on overcurrent Recloser CP555 Arcadia Park Tripped on Overcurrent Cause: Tree on mains outside 23 Bay St Galston See 1049153 also OMS 1041543 1041546 1039285 1039284 | November | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-11-10 | N | 57.5928 | N | 10 | N | N | 1.1101 | 39.4971 | 12920.7533
[7 empty] | 15646 | 10339 | 1040086 | 2013-11-10 10:08 | 2013-11-10 10:45 | 37 | 11kV | 34389 | 1317 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | At Sub 1285 Greenacre Park panel 19 "Hume Rook etc" feeder tripped and locked out on: Relays: SEF, EFI, Timing relay and Lockout Relay. Signals: 11kv trip, Tx3 Group Earth. Field EFI's: Nil Remarks: Transformer failure. Dop reports that footpath side HDO had operated explosively @ PT1686 Bower St. | November | 2013 | 2014Q2 | 2014 | ZN1285:PA19 | ZN35900:PA1 | ZN35900/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-11-10 | N | 26.1116 | N | 10 | N | N | 1.1101 | 39.4971 | 25130.4669
[7 empty] | 15315 | 6559 | 1039395 | 2013-11-10 12:11 | 2013-11-10 17:30 | 319 | 11kV | 166705 | 1615 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S.15002 Narrabeen, Panel 6 Fdr CB tripped, reclosed and tripped on Earth Fault, Timing, Lockout, Fault Check, efi, Fault Check relay#2 Tx. Field efi's down at S.16441, S.16903 and S.16839. 11kV OH down at corner Narrabeen Park and Hunter St, Narrabeen. | November | 2013 | 2014Q2 | 2014 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-11-10 | N | 103.2229 | N | 10 | N | N | 1.1101 | 39.4971 | 121823.097
[7 empty] | 15662 | 10601 | 1039473 | 2013-11-10 18:22 | 2013-11-10 18:40 | 18 | 11kV | 10998 | 2171 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | @Zn14143 Somersby Pa10 "Somersby East" fdr tripped on A&Cphase overcurrent also Pa12 "Phillips Gindurra" fdr tripped on A&Cphase overcurrent Signals: 11kv trip & group Earth ABNORMAL: LB45416 closed and LB44475 open (3f6) AB44696 closed and AB44527 open Cause: other - details provided SAO325905 HV feeder alteration. Circiut Breakers tripped on closing at AB44527 between Pa10 and Pa12 (incorrect phasing). See 1039880 exclude 1039473 | November | 2013 | 2014Q2 | 2014 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | Unknown | Not Veg | 2013-11-10 | N | 5.0659 | N | 10 | N | N | 1.1101 | 39.4971 | 8037.014
[7 empty] | 14957 | 2357 | 1039524 | 2013-11-10 22:18 | 2013-11-11 00:05 | 107 | 11kV | 11574 | 126 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 137886 4 fault operations 3 phase Overcurrent branch on ohm pole hw-50032 Excluded oms 1039524 | November | 2013 | 2014Q2 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2013-11-10 | N | 91.8571 | N | 10 | N | N | 1.1101 | 39.4971 | 8457.9378
[7 empty] | 15319 | 6575 | 1039554 | 2013-11-11 05:28 | 2013-11-11 08:20 | 172 | 11kV | 11868 | 69 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Heavy | N | LID137894 DOLF fuse holder broke and had to be replaced, no fuse blew. Excluded OMS 1039554 | November | 2013 | 2014Q2 | 2014 | 223:14398 | 223:14398 | ZN00223/014398 | LAKE MACQUARIE | OH | Not Veg | 2013-11-11 | N | 172 | N | 4 | N | N | 1.1101 | 39.4971 | 8672.7844
[7 empty] | 15179 | 4412 | 1039571 | 2013-11-11 06:48 | 2013-11-11 08:35 | 107 | 11kV | 105823 | 989 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of Panel 18 ex Berowra Zone lost supply Cause: Centre phase of AB2257 burnt off See OMS 1040652 1039571 1039575 | November | 2013 | 2014Q2 | 2014 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2013-11-11 | N | 107 | N | 4 | N | N | 1.1101 | 39.4971 | 77332.3271
[7 empty] | 14723 | 239 | 1039534 | 2013-11-10 23:54 | 2013-11-11 09:35 | 581 | 11kV | 2905 | 5 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Rain Wind Storm | N | LID 137892 B & C phase DOLF : 10 Amp Matt Hammel suspected in the heavy rain and some wind in the morning it appears tree branches had come into contact at the sub. Excluded OMS # 1039534. | November | 2013 | 2014Q2 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2013-11-10 | N | 581 | N | 10 | N | N | 1.1101 | 39.4971 | 2122.8883
[7 empty] | 15377 | 7144 | 1039537 | 2013-11-11 03:52 | 2013-11-11 09:44 | 352 | 11kV | 37409 | 212 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | LID 137887 4 fault operations A & C phase Instantaneous Overcurrent section isolated to repair x-arm at pole BK-40087 Excluded oms 1039537 | November | 2013 | 2014Q2 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2013-11-11 | N | 176.4575 | N | 4 | N | N | 1.1101 | 39.4971 | 27337.3938
[7 empty] | 15236 | 5478 | 1039779 | 2013-11-11 10:12 | 2013-11-11 11:56 | 104 | 11kV | 59184 | 594 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Zn35370 Galston 11kv fdr Pa4 "Galston Aux No1" tripped on Relays: C phase overcurrent ABNORMAL: AB2295 open and defective, LB473 Closed, LB62158 Closed, RE555 Open? Cause: Trees on 11kv Overhead fdr adjacent PT2214 Mansfield End See 1046297,8 Exclude 1039779 | November | 2013 | 2014Q2 | 2014 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-11-11 | N | 99.6364 | N | 4 | N | N | 1.1101 | 39.4971 | 43249.9216
[7 empty] | 15954 | 13745 | 1040245 | 2013-11-12 08:00 | 2013-11-12 09:15 | 75 | 11kV | 150 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137915 C phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 |  |  |  |  | UG | Not Veg | 2013-11-12 | N | 75 | N | 25 | Y | Y | 1.1101 | 39.4971 | 109.6156
[7 empty] | 16124 | 16186 | 1040256 | 2013-11-12 07:15 | 2013-11-12 09:45 | 150 | 11kV | 450 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 137925 C phase DOLF | November | 2013 | 2014Q2 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2013-11-12 | N | 150 | N | 25 | Y | Y | 1.1101 | 39.4971 | 328.8467
[7 empty] | 14692 | 3 | 1041371 | 2013-11-12 08:13 | 2013-11-12 09:54 | 101 | 11kV | 69425 | 731 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn14143 Somersby Pa17 'Somersby Falls' fdr tripped on: Relays: SEL Signals: Tx2 Group Earth EFI's: Nil Cause: Footpath side bond burnt off at first UGOH out of Pa17 See 1041371,3,4,5 Exclude 1040288 | November | 2013 | 2014Q2 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-11-12 | N | 94.9726 | N | 25 | Y | Y | 1.1101 | 39.4971 | 50733.7423
[7 empty] | 15067 | 3395 | 1040291 | 2013-11-12 08:00 | 2013-11-12 10:05 | 125 | 11kV | 1750 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 137923 C Phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2013-11-12 | N | 125 | N | 25 | Y | Y | 1.1101 | 39.4971 | 1278.8484
[7 empty] | 15078 | 3467 | 1040295 | 2013-11-12 08:00 | 2013-11-12 10:10 | 130 | 11kV | 910 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 137920 B & C phase DOLF : 20 Amp | November | 2013 | 2014Q2 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2013-11-12 | N | 130 | N | 25 | Y | Y | 1.1101 | 39.4971 | 665.0012
[7 empty] | 15404 | 7478 | 1040280 | 2013-11-12 08:04 | 2013-11-12 10:30 | 146 | 11kV | 146 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137918 A phase DOLF : 10 Amp Excluded OMS 1040280 | November | 2013 | 2014Q2 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-11-12 | N | 146 | N | 25 | Y | Y | 1.1101 | 39.4971 | 106.6925
[7 empty] | 14706 | 100 | 1040383 | 2013-11-12 08:20 | 2013-11-12 11:05 | 165 | 11kV | 165 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137927 Single phase DOLF : 5 Amp | November | 2013 | 2014Q2 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 165 | N | 25 | Y | Y | 1.1101 | 39.4971 | 120.5771
[7 empty] | 16194 | 16974 | 1040392 | 2013-11-12 09:57 | 2013-11-12 11:15 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137924 Single phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 78 | N | 25 | Y | Y | 1.1101 | 39.4971 | 114.0002
[7 empty] | 15457 | 7987 | 1040325 | 2013-11-12 09:53 | 2013-11-12 11:35 | 102 | 11kV | 510 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137930 A phase DOLF : 10 Amp Dropper lead and surge arrestor damaged. Excluded OMS 1040325 | November | 2013 | 2014Q2 | 2014 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Not Veg | 2013-11-12 | N | 102 | N | 25 | Y | Y | 1.1101 | 39.4971 | 372.693
[7 empty] | 14852 | 1419 | 1040434 | 2013-11-12 10:30 | 2013-11-12 11:40 | 70 | 11kV | 210 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137931 Single phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 70 | N | 25 | Y | Y | 1.1101 | 39.4971 | 153.4618
[7 empty] | 15458 | 7990 | 1040265 | 2013-11-12 08:39 | 2013-11-12 13:38 | 299 | 11kV | 35460 | 311 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137937 3 phase fault FAULT ISOLATED TO RAGCB 74433 (ARRESTORS) | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-11-12 | N | 114.0193 | N | 25 | Y | Y | 1.1101 | 39.4971 | 25913.1221
[7 empty] | 15567 | 9086 | 1040361 | 2013-11-12 09:16 | 2013-11-12 14:45 | 329 | 11kV | 19881 | 285 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137929 3 phase Sensitive Earth Fault sub 51306 isolated for replacement fdr restored. LA's blown at Sub 51306 Manwarring | November | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2013-11-12 | N | 69.7579 | N | 25 | Y | Y | 1.1101 | 39.4971 | 14528.4484
[7 empty] | 15463 | 8061 | 1040526 | 2013-11-12 12:27 | 2013-11-12 15:35 | 188 | 11kV | 49120 | 283 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 137941 2 fault operations Earth fault No cause found. Storm conditions. Excluded OMS 1040526 | November | 2013 | 2014Q2 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2013-11-12 | N | 173.5689 | N | 25 | Y | Y | 1.1101 | 39.4971 | 35895.4472
[7 empty] | 15663 | 10611 | 1040503 | 2013-11-12 12:03 | 2013-11-12 17:00 | 297 | 11kV | 1188 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | N | no further information available refer to 1040503 | November | 2013 | 2014Q2 | 2014 | 813:89062 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2013-11-12 | N | 297 | N | 25 | Y | Y | 1.1101 | 39.4971 | 868.1554
[7 empty] | 15701 | 11004 | 1040518 | 2013-11-12 12:30 | 2013-11-12 17:00 | 270 | 11kV | 1350 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137948 A & B phase DOLF : 10 Amp Excluded OMS 1040518 | November | 2013 | 2014Q2 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 270 | N | 25 | Y | Y | 1.1101 | 39.4971 | 986.5402
[7 empty] | 16081 | 15782 | 1040552 | 2013-11-12 12:59 | 2013-11-12 17:10 | 251 | 11kV | 251 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137947 A & B phase DOLF : 3 Amp Excluded OMS 1040552 Volts = 251 | November | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 251 | N | 25 | Y | Y | 1.1101 | 39.4971 | 183.4234
[7 empty] | 15400 | 7448 | 1040542 | 2013-11-12 12:03 | 2013-11-12 17:15 | 312 | 11kV | 312 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137946 A & B phase DOLF : 10 Amp 10A DOLF 100A LVF Volts 240 | November | 2013 | 2014Q2 | 2014 | 803:74010 | 813:89058 | ZN00813/089058 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 312 | N | 25 | Y | Y | 1.1101 | 39.4971 | 228.0004
[7 empty] | 14939 | 2173 | 1040450 | 2013-11-12 14:45 | 2013-11-12 17:30 | 165 | 11kV | 330 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137945 A phase DOLF : 10 Amp Volts = 247 Excluded OMS 1040630 | November | 2013 | 2014Q2 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 165 | N | 25 | Y | Y | 1.1101 | 39.4971 | 241.1543
[7 empty] | 15013 | 2927 | 1040585 | 2013-11-12 12:20 | 2013-11-12 19:10 | 410 | 11kV | 9840 | 24 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 137939 car hit pole HQ-61513 - Maitlandvale Rd Excluded oms 1040587 | November | 2013 | 2014Q2 | 2014 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2013-11-12 | N | 410 | N | 25 | Y | Y | 1.1101 | 39.4971 | 7190.7818
[7 empty] | 15553 | 8951 | 1040728 | 2013-11-12 18:55 | 2013-11-12 19:55 | 60 | 11kV | 180 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137944 A phase DOLF : 10 Amp Excluded OMS 1040728 | November | 2013 | 2014Q2 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2013-11-12 | N | 60 | N | 25 | Y | Y | 1.1101 | 39.4971 | 131.5387
[7 empty] | 16311 | 18114 | 1040492 | 2013-11-12 10:59 | 2013-11-12 20:42 | 583 | 11kV | 30907 | 85 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 137974 3 fault operations Earth fault poles split from lightening. Excluded OMS 1040492 | November | 2013 | 2014Q2 | 2014 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2013-11-12 | N | 363.6118 | N | 25 | Y | Y | 1.1101 | 39.4971 | 22585.924
[7 empty] | 15321 | 6587 | 1040734 | 2013-11-12 19:17 | 2013-11-12 22:16 | 179 | 11kV | 179 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 137952 A & B phase DOLF : 10 Amp One LA had been replaced OK earlier tonight and restored . HV fuses blew again at later time. Excluded OMS 1040734 | November | 2013 | 2014Q2 | 2014 | 803:74010 | 813:89058 | ZN00813/089058 | UPPER HUNTER | OH | Not Veg | 2013-11-12 | N | 179 | N | 25 | Y | Y | 1.1101 | 39.4971 | 130.8079
[7 empty] | 15560 | 8994 | 1040741 | 2013-11-12 19:57 | 2013-11-12 23:20 | 203 | 11kV | 406 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 137954 A & B phase DOLF : 10 Amp Excluded OMS 1040741 | November | 2013 | 2014Q2 | 2014 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 203 | N | 25 | Y | Y | 1.1101 | 39.4971 | 296.6928
[7 empty] | 16493 | 20369 | 1040746 | 2013-11-12 20:27 | 2013-11-13 08:45 | 738 | 11kV | 738 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 137964 Single phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 803:74010 | 813:89058 | ZN00813/089058 | UPPER HUNTER | UG | Not Veg | 2013-11-12 | N | 738 | N | 25 | Y | Y | 1.1101 | 39.4971 | 539.3086
[7 empty] | 15955 | 13775 | 1040787 | 2013-11-13 07:24 | 2013-11-13 09:00 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 137962 Single phase DOLF : 10 Amp Excluded OMS 1040787 | November | 2013 | 2014Q2 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | UG | Not Veg | 2013-11-13 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 15546 | 8905 | 1040729 | 2013-11-12 19:11 | 2013-11-13 09:10 | 839 | 11kV | 839 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 137950 Broken LL lead Excluded OMS 1040729 | November | 2013 | 2014Q2 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2013-11-12 | N | 839 | N | 25 | Y | Y | 1.1101 | 39.4971 | 613.1165
[7 empty] | 15012 | 2924 | 1040896 | 2013-11-13 09:50 | 2013-11-13 11:30 | 100 | 11kV | 100 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 137968 Trees growing into mains Excluded OMS 1040896. | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-11-13 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 14846 | 1325 | 1041181 | 2013-11-13 17:15 | 2013-11-13 20:45 | 210 | 11kV | 5460 | 26 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 137976 No protection operation fdr isolated for repairs to faulty pole. Excluded OMS 1041181 | November | 2013 | 2014Q2 | 2014 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2013-11-13 | N | 210 | N | 5 | N | N | 1.1101 | 39.4971 | 3990.007
[7 empty] | 15373 | 7115 | 1041236 | 2013-11-13 21:26 | 2013-11-13 23:50 | 144 | 11kV | 127872 | 888 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Section of feeder ex Darlinghurst Panel 25 - @ S1565 McElhorne St - HV CB tripped on #2 Tx side (CC B ph34E Intertrip send relay) @ S104 Woolloomooloo - HV CB tripped on #1 Tx side (receive relay) Suspect Transformer failure @ S1565 see 1041267 1041239 | November | 2013 | 2014Q2 | 2014 | ZN931:PA25 | ZN931:PA25 | ZN00931/000025 | SYDNEY | UG | Not Veg | 2013-11-13 | N | 144 | N | 5 | N | N | 1.1101 | 39.4971 | 93445.086
[7 empty] | 15927 | 13403 | 1041232 | 2013-11-13 20:47 | 2013-11-14 03:45 | 418 | 11kV | 198840 | 1648 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 137977 2 fault operations B phase Earth Fualt; Overcurrent 11kV OHM down near pole HR-91892 & tapping off at 11kV Links 41267 Excluded oms 1041232, 1041233 & 1041244 | November | 2013 | 2014Q2 | 2014 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2013-11-13 | N | 120.6553 | N | 5 | N | N | 1.1101 | 39.4971 | 145306.4072
[7 empty] | 14905 | 1961 | 1041352 | 2013-11-14 10:16 | 2013-11-14 10:52 | 36 | 11kV | 39888 | 1108 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At Zn195 Pymble S4021 Tripped on Earth Fault EFUI and Signals: Zone Earth - Group Earth Cause: Contaractor Hit Underground cable with crowbar Trunk section | November | 2013 | 2014Q2 | 2014 | ZN195:PA29 | ZN195:PA29 | ZN00195/000029 | KU-RING-GAI | UG | Not Veg | 2013-11-14 | N | 36 | N | 4 | N | N | 1.1101 | 39.4971 | 29148.9739
[7 empty] | 14728 | 284 | 1043006 | 2013-11-14 13:55 | 2013-11-14 14:55 | 60 | 11kV | 480 | 8 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 137995 Broken crossarm at pole AI 90222 | November | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-11-14 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 15762 | 11700 | 1041471 | 2013-11-14 13:42 | 2013-11-14 17:30 | 228 | 11kV | 45506 | 294 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 137994 2 fault operations B phase Earth fault; Overcurrent Car into pole HR 61831 NEH x Cessnock Rd Excluded OMS 1041482,1041495 | November | 2013 | 2014Q2 | 2014 | 501:48118 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2013-11-14 | N | 154.7823 | N | 4 | N | N | 1.1101 | 39.4971 | 33254.4426
[7 empty] | 14979 | 2629 | 1041625 | 2013-11-14 21:00 | 2013-11-14 22:45 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 137997 A phase DOLF : 10 Amp Wasp nest caused DOLF carrier to burn. Carrier & fuse replaced. Excluded OMS # 1041625 | November | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2013-11-14 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 15596 | 9518 | 1041800 | 2013-11-15 12:27 | 2013-11-15 14:30 | 123 | 11kV | 24525 | 279 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | ZN 10996 Rockdale - Pnl 20 - C phase IOC and Timed OC, Timing, Lockout, EFI, Field EFIs. Vehicle hit pole causing 11kV OH mains to clash and trip feeder. S 10726 was in LV// and overloaded A phase on Dist 1. ME: 1042796. Rest Step: 1042798. Withdrawn: 1042769, 1041800. | November | 2013 | 2014Q2 | 2014 | ZN10996:PA20 | ZN10998:PA24 | ZN10998/000024 | BAYSIDE | OH | Not Veg | 2013-11-15 | N | 87.9032 | N | 13 | N | N | 1.1101 | 39.4971 | 17922.1466
[7 empty] | 15221 | 4982 | 1041697 | 2013-11-15 09:00 | 2013-11-15 18:30 | 570 | 11kV | 1140 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138008 A phase DOLF : 10 Amp Excluded OMS 1041697 | November | 2013 | 2014Q2 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-11-15 | N | 570 | N | 13 | N | N | 1.1101 | 39.4971 | 833.0784
[7 empty] | 14898 | 1914 | 1041921 | 2013-11-15 18:29 | 2013-11-15 20:00 | 91 | 11kV | 1001 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138010 B phase DOLF : 10 Amp Excluded OMS 1041921 | November | 2013 | 2014Q2 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2013-11-15 | N | 91 | N | 13 | N | N | 1.1101 | 39.4971 | 731.5013
[7 empty] | 16168 | 16677 | 1041962 | 2013-11-15 22:00 | 2013-11-15 23:11 | 71 | 11kV | 81224 | 1144 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At S.15012 Killarney, Panel 8 Fdr CB tripped on A and C phase IOC, earth fault, reclose timer and lockout relays, fault check and ef with 11kV trip and Zone earth. AB.22077 which is normally open is common to both Panel 4 and Panel 8 Also refer to OMS 1042678 | November | 2013 | 2014Q2 | 2014 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Veg | 2013-11-15 | N | 71 | N | 13 | N | N | 1.1101 | 39.4971 | 59356.1035
[7 empty] | 15035 | 3094 | 1041969 | 2013-11-15 22:12 | 2013-11-15 23:45 | 93 | 11kV | 59613 | 641 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN 9037 Miranda - Pnl 7 - Trip/reclose/trip, A & C phase IOC, EFI. Weather related. Lightning in area. Mains to patrol in daylight. | November | 2013 | 2014Q2 | 2014 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Veg | 2013-11-15 | N | 93 | N | 13 | N | N | 1.1101 | 39.4971 | 43563.4221
[7 empty] | 16341 | 18443 | 1041956 | 2013-11-15 21:53 | 2013-11-15 23:46 | 113 | 11kV | 319790 | 2830 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At S80 Chatswood Panel 32 tripped on A and C phase O/C EFI and Earth leakage Cause: Severe rain and lightning See OMS 1041956 1041960 1041967 | November | 2013 | 2014Q2 | 2014 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Veg | 2013-11-15 | N | 113 | N | 13 | N | N | 1.1101 | 39.4971 | 233693.0998
[7 empty] | 15126 | 3957 | 1041961 | 2013-11-15 22:00 | 2013-11-15 23:47 | 107 | 11kV | 78041 | 741 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | At ZN3425 Castle Cove panel 28 'Eastern Valley Smith' feeder tripped on: A, B & C phase IOC & reclose time delay L/O EFI. DOp patrolled and found nothing. OMS numbers: 1043224, 1043225, 1043226, 1041961 | November | 2013 | 2014Q2 | 2014 | ZN3425:PA28 | ZN3425:PA28 | ZN03425/000028 | WILLOUGHBY | OH | Veg | 2013-11-15 | N | 105.3185 | N | 13 | N | N | 1.1101 | 39.4971 | 57030.061
[7 empty] | 14701 | 43 | 1041978 | 2013-11-15 22:27 | 2013-11-16 00:15 | 108 | 11kV | 194806 | 1895 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At S.15005 Belrose Panel 2 Fdr CB tripped on "2L" Panel :- efi and fault check "2R" Panel:- efi, fault check, B and C phase timed OC plus 11kV trip, zone earth. Lightning storm at the time of occurrence | November | 2013 | 2014Q2 | 2014 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Veg | 2013-11-15 | N | 102.8 | N | 13 | N | N | 1.1101 | 39.4971 | 142358.479
[7 empty] | 15295 | 6357 | 1041981 | 2013-11-15 22:32 | 2013-11-16 00:46 | 134 | 11kV | 78168 | 762 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At Zn180 Mosman panel 17 tripped on: A phase IOC and C phase IOC and EFI. At Rec 10414 Suakin Drive relay operations at recloser: overcurrent trip and lock out. Lightning storm weather conditions. Rec 1014 Suakin Drive may not grade with Mosman Zone panel 17 protection. OMS numbers: 1043777, 1042780, 1041981 | November | 2013 | 2014Q2 | 2014 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Veg | 2013-11-15 | N | 102.5827 | N | 13 | N | N | 1.1101 | 39.4971 | 57122.8688
[7 empty] | 15616 | 9810 | 1041945 | 2013-11-15 21:00 | 2013-11-16 00:50 | 230 | 11kV | 690 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138011 A & B phase : 10 Amp A ph LF 3507 blew when DOLFs replaced 10A. C ph LVF replaced 100A. Also see report 138010 OMS 1043033 Excluded OMS # 1041945. | November | 2013 | 2014Q2 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | UG | Not Veg | 2013-11-15 | N | 230 | N | 13 | N | N | 1.1101 | 39.4971 | 504.2316
[7 empty] | 15286 | 6282 | 1041987 | 2013-11-15 22:46 | 2013-11-16 02:45 | 239 | 11kV | 333405 | 1395 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | ZN 9700 Kirrawee - Pnl 24 - Trip/reclose/trip, A phase IOC, EFI, Lockout, Timing, Field EFIs. Tree branch on mains at 116 Waratah St. | November | 2013 | 2014Q2 | 2014 | ZN9700:PA24 | ZN9700:PA24 | ZN09700/000024 | SUTHERLAND | OH | Veg | 2013-11-15 | N | 239 | N | 13 | N | N | 1.1101 | 39.4971 | 243642.5402
[7 empty] | 15962 | 13972 | 1041970 | 2013-11-15 22:52 | 2013-11-16 03:45 | 293 | 11kV | 264964 | 963 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Lightning | N | ZN 9252 Jannali - Pnl 2 - Trip/reclose/trip/trip, A & C phase IOC, Lockout, timer, EFI, Field EFIs. Insulator failed between AB 35806 and AB 35892. Outage greater then 4 hours because of the dark and rainy environment and the location of the fault. ME: 1043141. Rest Step: 1043142. Withdrawn: 1041970, 1042014. | November | 2013 | 2014Q2 | 2014 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2013-11-15 | N | 275.1443 | N | 13 | N | N | 1.1101 | 39.4971 | 193627.8761
[7 empty] | 15947 | 13674 | 1042039 | 2013-11-16 00:45 | 2013-11-16 03:55 | 190 | 11kV | 542575 | 3026 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | @Zn12610 Long Jetty Pa20 "matcham st" 11kv fdr tripped, reclosed & locked out on EFI, Overcurrent B & C phase, Sensitive Earth Fault Alarms: Tx3 Group Earth, Zone Earth, 11kv trip ABNORMAL: LB61289 closed with LB43314 Open Cause: Bond centre phase open circuit at Pole BV4022 See 1043555,6,7,8,9 Exclude 1042039,41,5,7,8 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 179.3044 | N | 14 | N | N | 1.1101 | 39.4971 | 396497.8067
[7 empty] | 14775 | 679 | 1042007 | 2013-11-15 23:04 | 2013-11-16 04:32 | 328 | 11kV | 769160 | 2345 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Rain Wind Storm | N | ZN 10997 Sans Souci - Pnl 2 - Trip/reclose/trip, IOC and EFI. Suspect lightning strike at AB 30656. See interruption for Kogarah Pnl 38. | November | 2013 | 2014Q2 | 2014 | ZN10997:PA2 | ZN10997:PA2 | ZN10997/000002 | BAYSIDE | OH | Not Veg | 2013-11-15 | N | 328 | N | 13 | N | N | 1.1101 | 39.4971 | 562079.4416
[7 empty] | 15350 | 6805 | 1042050 | 2013-11-16 01:01 | 2013-11-16 06:35 | 334 | 11kV | 190806 | 1175 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Wind Storm | N | Zn12570 Avoca Pa25 "Hillcrest st" 11kv fdr tripped reclosed & locked out on; LO, EFI, Aph, E/F, Trip ABNORMAL: S18075/SwB Closed, LB45088 Open Cause: Failed UGOH on section of fdr from S18705/SwA to USL43253 to AB41184 to LB41423 tee PT11424 See 1043748,50,1,2,3,8 Exclude 1042050,80 | November | 2013 | 2014Q2 | 2014 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | Unknown | Unknown | 2013-11-16 | N | 162.3881 | N | 14 | N | N | 1.1101 | 39.4971 | 139435.397
[7 empty] | 15604 | 9685 | 1042063 | 2013-11-16 02:18 | 2013-11-16 07:30 | 312 | 11kV | 44616 | 143 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | Section of 11kV feeder Pa32R ex Chatswood, Bond burnt off roadside in tee off to PT628 Ronald Osbourne. See OMS1043744 1042063 | November | 2013 | 2014Q2 | 2014 | ZN80:PA32 | ZN80:PA32 | ZN00080/000032 | LANE COVE | OH | Not Veg | 2013-11-16 | N | 312 | N | 14 | N | N | 1.1101 | 39.4971 | 32604.0569
[7 empty] | 15641 | 10235 | 1042122 | 2013-11-16 08:41 | 2013-11-16 09:50 | 69 | 11kV | 75822 | 1575 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | @PT14423 Soldiers Point Budgeree Lightning arrestor struck by lightning 2nd event @Zn12620 Noraville 11kv fdr pa11 "Norah Head" tripped on SEF PT Lightning Arrestors damaged. PT Isolated high and low and placed in LV// See 1043997 2nd event 1043998,9,4000,1,2 Exclude 1042122,45,53,62 | November | 2013 | 2014Q2 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 48.141 | N | 14 | N | N | 1.1101 | 39.4971 | 55408.4812
[7 empty] | 15410 | 7543 | 1042188 | 2013-11-16 05:00 | 2013-11-16 09:55 | 295 | 11kV | 4720 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn12600 Lisarow section of Pa2 btw LK41935 to AB41934 tee PT47611, PT12365 interrupted to allow overhead mains to remove tree from CCT in addition found burnt up bonds on pole WL73288. DMA created See 1043812 Exclude 1042130,88 | November | 2013 | 2014Q2 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2013-11-16 | N | 295 | N | 14 | N | N | 1.1101 | 39.4971 | 3449.2368
[7 empty] | 16408 | 19262 | 1042145 | 2013-11-16 07:18 | 2013-11-16 10:15 | 177 | 11kV | 10443 | 59 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Customers report Low Volts due to damaged lightning arrestor. Restored on 2nd Event OMS#1043998 Zn12620 Pa11 trip. @PT14423 Soldiers Point Budgeree Lightning arrestor struck by lightning See 1043997 2nd event 1043998,9,4000,1,2 Exclude 1042122,45,53,62 | November | 2013 | 2014Q2 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 177 | N | 14 | N | N | 1.1101 | 39.4971 | 7631.4364
[7 empty] | 14925 | 2092 | 1042170 | 2013-11-16 10:44 | 2013-11-16 13:01 | 137 | 11kV | 177237 | 1438 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn12570 Avoca 11kv fdr Pa39 "north Avoca" tripped and locked out Relays: SEL, EFI, E/F EFI's: S14134 S18035 S48327 Cause: Lightning Multiple lightning strikes on feeder at PT13619 Ocean Tranway and PT13546 Coast Scenic isolated high and low and placed in LV// by DOp See 1043720,3,4 Exclude 1042170 | November | 2013 | 2014Q2 | 2014 | ZN12570:PA39 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 123.2524 | N | 14 | N | N | 1.1101 | 39.4971 | 129519.572
[7 empty] | 15445 | 7895 | 1042245 | 2013-11-16 09:58 | 2013-11-16 13:30 | 212 | 11kV | 3392 | 16 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn14144 Wamberal section of pa10 Relays: EFI EFI's: S18824 S18802 S18826 S4888 S18825 Cause: lightning Sever lightning at time of a failure, HDO replaced at PT18766 all supply restored See 1044090 exclude 1042215,46 @PT18766 Matcham Entrance Footpath HDO operated 20 Amp | November | 2013 | 2014Q2 | 2014 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 212 | N | 14 | N | N | 1.1101 | 39.4971 | 2478.7736
[7 empty] | 14830 | 1255 | 1042273 | 2013-11-16 12:00 | 2013-11-16 15:40 | 220 | 11kV | 220 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138026 A phase DOLF : 10 Amp Excluded OMS 1042273 | November | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | UG | Not Veg | 2013-11-16 | N | 220 | N | 14 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 15366 | 6973 | 1042313 | 2013-11-16 13:39 | 2013-11-16 16:15 | 156 | 11kV | 3432 | 22 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Previous Storm | N | Ex Zn12610 Long Jetty section of Pa22 "shelly beach" @PT12360 Swalding Oaks A phase 31.5k HDO blown Cuase: Lightning See 1044120 exclude 1042313,26 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA22 | ZN12610:PA22 | ZN12610/000022 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 156 | N | 14 | N | N | 1.1101 | 39.4971 | 2508.0044
[7 empty] | 15980 | 14238 | 1042786 | 2013-11-16 14:00 | 2013-11-16 16:25 | 145 | 11kV | 145 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 138023 3 phase nil oms no cause found suspect lightning from previous storm. Note: 3474 Powercoal RAVCB has been on the system abs for 12 months, the control box is rusting off the pole and is in need of attention ASAP per P Swan. dq | November | 2013 | 2014Q2 | 2014 |  |  |  | LAKE MACQUARIE | OH | Not Veg | 2013-11-16 | N | 145 | N | 14 | N | N | 1.1101 | 39.4971 | 105.9617
[7 empty] | 16093 | 15960 | 1044168 | 2013-11-16 15:10 | 2013-11-16 16:30 | 80 | 11kV | 1280 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | Ex Zn12600 Lisarow sectrion of a2 BtW USL41935 to AB41934 tee PT12365 & PT47611 Cause: 11kv bonds on pole WL73288 burned off, section of feeder interrupted for repairs | November | 2013 | 2014Q2 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2013-11-16 | N | 80 | N | 14 | N | N | 1.1101 | 39.4971 | 935.3862
[7 empty] | 15563 | 9074 | 1042287 | 2013-11-16 12:34 | 2013-11-16 21:20 | 526 | 11kV | 36956 | 681 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S5868 Gore Hill Panel 22 interrupted for safety At S8809 Herbert Frederick No2 Tx Fuse switch operated. Cause: At S8809 LV board on fire See OMS 1043762 1043763 1042287 1042298 | November | 2013 | 2014Q2 | 2014 | ZN5868:PA22 | ZN5868:PA22 | ZN05868/000022 | WILLOUGHBY | UG | Not Veg | 2013-11-16 | N | 54.2673 | N | 14 | N | N | 1.1101 | 39.4971 | 27006.3548
[7 empty] | 14790 | 877 | 1042399 | 2013-11-16 23:31 | 2013-11-17 00:46 | 75 | 11kV | 81805 | 1187 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn.3155 Duoble bay Pnl.17 - tripped on: 17R A phase IOC, E/F, F/C UG cable fault from Pnl.17 to S35410 (Sw B ) to S5782 (Sw A) to S480 (Sw D ) | November | 2013 | 2014Q2 | 2014 | ZN3155:PA17 | ZN3155:PA17 | ZN03155/000017 | WOOLLAHRA | UG | Not Veg | 2013-11-16 | N | 68.9174 | N | 14 | N | N | 1.1101 | 39.4971 | 59780.6812
[7 empty] | 15487 | 8283 | 1042401 | 2013-11-17 01:18 | 2013-11-17 02:36 | 78 | 11kV | 143958 | 1904 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn180 Mosman panel 21 'Shadforth Hamlet etc' 11kV feeder tripped on: A & C IOC,EFI, F/C. UG cable fault between Zn180 Mosman panel 21, S325 Gerrard Winnie SW/A and S2989 Shadforth Hamlet. OMS numbers: 1042805, 1042401. | November | 2013 | 2014Q2 | 2014 | ZN180:PA21 | ZN180:PA21 | ZN00180/000021 | MOSMAN | UG | Not Veg | 2013-11-17 | N | 75.6082 | N | 4 | N | N | 1.1101 | 39.4971 | 105200.2604
[7 empty] | 14971 | 2546 | 1042405 | 2013-11-17 02:39 | 2013-11-17 05:20 | 161 | 11kV | 158456 | 1237 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn12620 Noraville Pa8 "Manoa Ave" 11kv fdr tripped on Earth Fault, Earth Fault Indicator Alarms: Nil Cause: Not ascertained. OH mains to patrol in daylight See 1044208,9,10,11 Exclude 1042405 | November | 2013 | 2014Q2 | 2014 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Veg | 2013-11-17 | N | 128.097 | N | 4 | N | N | 1.1101 | 39.4971 | 115794.9711
[7 empty] | 15703 | 11025 | 1042477 | 2013-11-17 09:57 | 2013-11-17 13:30 | 213 | 11kV | 13419 | 63 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At CP342 Redlan Raglan Sw/C has tripped on two phases. UG fault between CP342 Redlan Raglan and S5737 Lane M46 Raglan. S5737 Lane M46 Raglan distributor 4 was still alive as LV // was found in and S5737 distributor 4 fuses blown. OMS numbers: 1042747, 1042490, 1042477 | November | 2013 | 2014Q2 | 2014 | ZN180:PA10 | ZN180:PA10 | ZN00180/000010 | MOSMAN | UG | Not Veg | 2013-11-17 | N | 213 | N | 4 | N | N | 1.1101 | 39.4971 | 9806.2094
[7 empty] | 15522 | 8733 | 1042562 | 2013-11-17 17:18 | 2013-11-17 20:50 | 212 | 11kV | 5206 | 50 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn12650 West Gosford section of Pa1 "Dog trap rd" fdr @RE44603 Footes Rd tripped on overcurrent Cause: Tree/branch brought down OH Noraville lineworker repaired overhead mains at 106 Footes rd See 1044223,5 exclude 1042562,8 | November | 2013 | 2014Q2 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-11-17 | N | 104.12 | N | 4 | N | N | 1.1101 | 39.4971 | 3804.3912
[7 empty] | 14742 | 387 | 1042835 | 2013-11-18 01:15 | 2013-11-18 02:55 | 100 | 11kV | 9900 | 99 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | LID 138037 3 Phase No protection operations. Isolation to replace insulator at pole IV-30230. See report 138038/ OMS 1042834. SI M0572. Excluded OMS # 1042623 | November | 2013 | 2014Q2 | 2014 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Not Veg | 2013-11-18 | N | 100 | N | 11 | N | N | 1.1101 | 39.4971 | 7234.628
[7 empty] | 15113 | 3856 | 1042652 | 2013-11-18 06:21 | 2013-11-18 07:27 | 66 | 11kV | 37129 | 621 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn.340 Botany - pnl.2 tripped on short translay (overcurrent) Field EFIs: @ Zone Pnl.2 through to S35536 Suspect cable fault between S35536 to S8860 to S4530 See 1043432 1043434 1043435 | November | 2013 | 2014Q2 | 2014 | ZN340:PA2 | ZN340:PA45 | ZN00340/000045 | BAYSIDE | UG | Not Veg | 2013-11-18 | N | 59.789 | N | 11 | N | N | 1.1101 | 39.4971 | 27132.7781
[7 empty] | 16410 | 19274 | 1042689 | 2013-11-18 07:53 | 2013-11-18 09:06 | 73 | 11kV | 42340 | 580 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | ZN 9301 Kurnell - Section of Pnl 8 - Bond open circuit. Bond went open circuit at AB 35165. Customers received low volts. ME: 1044262. Withdrawn: 1042689. | November | 2013 | 2014Q2 | 2014 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2013-11-18 | N | 73 | N | 11 | N | N | 1.1101 | 39.4971 | 30940.8232
[7 empty] | 15470 | 8140 | 1042795 | 2013-11-18 08:55 | 2013-11-18 09:06 | 11 | 11kV | 2695 | 245 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | ZN 9301 Kurnell - Pnl 15 - SEL right, Field EFI. Open circuit bond at AB 35165 on Pnl 8. When trying to restore through Sw. B at S 9724, the SEL operated and dumped the panel. ME: 1044261. Withdrawn: 1042795. | November | 2013 | 2014Q2 | 2014 | ZN9301:PA15 | ZN9534:PA11 | ZN09534/000011 | SUTHERLAND | OH | Not Veg | 2013-11-18 | N | 11 | N | 11 | N | N | 1.1101 | 39.4971 | 1969.4265
[7 empty] | 15250 | 5649 | 1042753 | 2013-11-18 08:37 | 2013-11-18 09:45 | 68 | 11kV | 68612 | 1009 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn12580 Erina section of Pa14 @IR62391 Wells Brougham tripped and reclosed and tripped on overcurrent Cause: Tree branch on 11kv adjacent LB42181 removed by DOp See 1042753 exclude 1042757,82 | November | 2013 | 2014Q2 | 2014 | ZN12580:PA14 | ZN12580:PA14 | ZN12580/000014 | CENTRAL COAST | OH | Veg | 2013-11-18 | N | 68 | N | 11 | N | N | 1.1101 | 39.4971 | 50139.6259
[7 empty] | 15336 | 6701 | 1042863 | 2013-11-18 10:06 | 2013-11-18 11:10 | 64 | 11kV | 211 | 148 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | @Zn12690 Berkeley Vale Pa26R, EFI operated Alarms: Tx12 GE, TX13 GE @RE44947 Gavenlock rd tripped and reclosed on IOC, OC @PT14761 Pacific Old Tuggerah 1.1 B phase HDO 16K operated Cause: tree/branch on OH Mains at PT14761 See 1044265,6 Exclude 1042863 | November | 2013 | 2014Q2 | 2014 | ZN12690:PA26 | ZN12690:PA26 | ZN12690/000026 | CENTRAL COAST | OH | Veg | 2013-11-18 | N | 1.4257 | N | 11 | N | N | 1.1101 | 39.4971 | 154.1926
[7 empty] | 15459 | 8031 | 1042637 | 2013-11-18 02:14 | 2013-11-18 11:15 | 541 | 11kV | 45809 | 161 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Heavy | N | LID 138040 3 fault operations 3 phase Earth fault pole fire sub 70929 Excluded OMS 1042637 & 1042659 | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-11-18 | N | 284.528 | N | 11 | N | N | 1.1101 | 39.4971 | 33475.8661
[7 empty] | 15148 | 4152 | 1042212 | 2013-11-18 01:38 | 2013-11-18 11:45 | 607 | 11kV | 238367 | 1585 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn12660 Woy Woy Pa6 "Davistown" fdr CB has tripped Relays: Aph IOC and timed OC, Cphase timed OC, timing, LO and EFI Signals: 11kv trip EFI's" S18272 ABNORMAL: AB40471 is closed, LB62073 is open (part of empire bay contingency swotch) Cause: Tree @ Henderson has brought down 2 bays of OH near AB41139 See 1044239,40,1,2 Exclude 1042598,636,45,6 | November | 2013 | 2014Q2 | 2014 | ZN36200:PA11 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Veg | 2013-11-18 | N | 150.3893 | N | 11 | N | N | 1.1101 | 39.4971 | 174191.573
[7 empty] | 16240 | 17477 | 1043059 | 2013-11-18 13:08 | 2013-11-18 14:54 | 106.0333 | 11kV | 8270.6 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser CP3280 Hunt Ave tripped and locked out on C phase O/C Cause: Branch removed from 11kV OH near AB3340 by DOp See OMS 1043046 1043059 | November | 2013 | 2014Q2 | 2014 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2013-11-18 | N | 106.0333 | N | 11 | N | N | 1.1101 | 39.4971 | 6043.9105
[7 empty] | 16464 | 20115 | 1042844 | 2013-11-18 09:58 | 2013-11-18 17:30 | 452 | 11kV | 9908 | 129 | HV | O/H Conductor Wind Related | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa2 @RE41020 Wattle tree rd nth tripped & locked out on EF trip Cause: OH cables twisted together. Tree on 11kv low voltage contacted HV EMSO notified PT12383 damaged See 1044259,60 exclude 1042844 | November | 2013 | 2014Q2 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2013-11-18 | N | 76.8062 | N | 11 | N | N | 1.1101 | 39.4971 | 7240.4742
[7 empty] | 15034 | 3082 | 1043315 | 2013-11-18 17:38 | 2013-11-18 19:15 | 97 | 11kV | 485 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138046 Single phase DOLF : 10 Amp Excluded OMS 1043315 | November | 2013 | 2014Q2 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | UG | Not Veg | 2013-11-18 | N | 97 | N | 11 | N | N | 1.1101 | 39.4971 | 354.4237
[7 empty] | 16185 | 16918 | 1043722 | 2013-11-19 13:42 | 2013-11-19 17:25 | 223 | 11kV | 123957 | 1966 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | @Zn12660 Woy Woy Pa16 "St Hubart" fdr tripped Relays: Earth Fault and EFI Signals: 11kv trip EFI's: S14604 S11459 S11458 S11242 S48128 S48927 Abnormal: S48927SwB Closed, LB62073 Opened, Empire Bay Pa11L & Pa1L Opened, AB43303 Closed Cause: Car hit PT12604 pole snapping 11kv cross arms. Section of fdr from AB43575 to LB62073 tee PT12604 is isolated. Car details: Red Hold UTE rego XUZ751 Driver Shane Orenshaw of 5 Sorrento Rd EMpire Bay. Sen Const UNGER of Gosford See 1044772,3 Exclude 1043722,5,7,42,93 | November | 2013 | 2014Q2 | 2014 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-19 | N | 63.0504 | N | 1 | N | N | 1.1101 | 39.4971 | 90584.1195
[7 empty] | 15385 | 7248 | 1043934 | 2013-11-20 03:26 | 2013-11-20 05:36 | 130 | 11kV | 279110 | 2147 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn36300 Balgowlah North Pa19 "Hayes Condamine" fdr tripped on Basler #50 O/C Cause: DOp patrolled nothing identified mains to patrol in daylight See 1043934 Exclude 1043935 | November | 2013 | 2014Q2 | 2014 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Veg | 2013-11-20 | N | 130 | N | 4 | N | N | 1.1101 | 39.4971 | 203965.3556
[7 empty] | 14963 | 2428 | 1044024 | 2013-11-20 10:00 | 2013-11-20 11:15 | 75 | 11kV | 150 | 2 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 138067 3 phase Trees growing into mains SECTION ISOLATED TO POLE MD-90772 | November | 2013 | 2014Q2 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2013-11-20 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 14718 | 209 | 1044176 | 2013-11-20 12:19 | 2013-11-20 13:29 | 70.55 | 11kV | 3809.7 | 54 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 138068 tree on fdr near sub 16317 section isolated to remove | November | 2013 | 2014Q2 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2013-11-20 | N | 70.55 | N | 4 | N | N | 1.1101 | 39.4971 | 2784.0164
[7 empty] | 16419 | 19425 | 1044123 | 2013-11-20 11:48 | 2013-11-20 14:50 | 182 | 11kV | 1638 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa3 @PT13210 Waratah Borrisbrook foot path side HDO 16A fuse failed. Cause: Fuse Fatigue Exclude 1045288, 1044123,96 | November | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2013-11-20 | N | 182 | N | 4 | N | N | 1.1101 | 39.4971 | 1197.0021
[7 empty] | 15412 | 7557 | 1044428 | 2013-11-21 01:14 | 2013-11-21 03:20 | 126 | 11kV | 6426 | 51 | HV | Animal Possum | Animal | Fuse | Unplanned | Unselected | N | Ex Zn12640 Umina section of Pa13 @PT12210 Yarrabin Monash 11kv HDO 31.5K cewntre & roadside phase fuse bown Cause: Possum on PT See 1045295 Exclude 1044428,30 | November | 2013 | 2014Q2 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2013-11-21 | N | 126 | N | 5 | N | N | 1.1101 | 39.4971 | 4695.9313
[7 empty] | 16276 | 17731 | 1044443 | 2013-11-21 07:18 | 2013-11-21 08:25 | 67 | 11kV | 42612 | 636 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 72 Five Dock Panel No.22 "Wolseley Parra etc" feeder opened on earth fault with EFI. Zone earth, No.3 Group earth, 11kv trip. EFIs operted @ NIL Remarks: UG fault. 11kv ug fault from Sub 72 Five Dock Panel No.22 to Sub 6318 Wolseley Parra tee Sub 5972 Parramatta Croydon | November | 2013 | 2014Q2 | 2014 | ZN72:PA22 | ZN35555:PA20 | ZN35555/000020 | INNER WEST | UG | Not Veg | 2013-11-21 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 31139.5928
[7 empty] | 16030 | 15025 | 1044859 | 2013-11-21 21:49 | 2013-11-21 23:20 | 91 | 11kV | 17742 | 205 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138091 1 fault operation 3 phase Earth fault See also LID ## 138089 & 138090 (previous T&Rs).Fdr patrolled. No cause found. Excluded OMS No. 1044859 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2013-11-21 | N | 86.5463 | N | 5 | N | N | 1.1101 | 39.4971 | 12965.3303
[7 empty] | 14734 | 329 | 1044868 | 2013-11-21 22:25 | 2013-11-22 02:00 | 215 | 11kV | 1505 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138103 B phase DOLF : 20 Amp Excluded OMS 1044868 | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-11-21 | N | 215 | N | 5 | N | N | 1.1101 | 39.4971 | 1099.8096
[7 empty] | 16077 | 15730 | 1044884 | 2013-11-22 01:47 | 2013-11-22 03:15 | 88 | 11kV | 9152 | 104 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 138108 A & B phase DOLF Compound filled UGOH failed. Excluded oms 1044884 | November | 2013 | 2014Q2 | 2014 | 205:12206 | 205:12206 | ZN00205/012206 | NEWCASTLE | Unknown | Unknown | 2013-11-22 | N | 88 | N | 37 | Y | Y | 1.1101 | 39.4971 | 6688.0117
[7 empty] | 15089 | 3575 | 1044862 | 2013-11-21 22:15 | 2013-11-22 05:19 | 424 | 11kV | 194769 | 685 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 138102 2 fault operations C phase Overcurrent Excluded OMS 1044862 | November | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-11-21 | N | 284.3343 | N | 5 | N | N | 1.1101 | 39.4971 | 142331.4405
[7 empty] | 15568 | 9107 | 1044894 | 2013-11-22 06:40 | 2013-11-22 08:20 | 100 | 11kV | 500 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | Blown DOLF - no further information available | November | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2013-11-22 | N | 100 | N | 37 | Y | Y | 1.1101 | 39.4971 | 365.3853
[7 empty] | 15733 | 11394 | 1044909 | 2013-11-22 07:11 | 2013-11-22 08:40 | 89 | 11kV | 77170 | 995 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | At ZN2196 Milperra Zone 11kv Pnl 18 '4859 Lachlan Cant' tripped on: Relays: B Phase Overcurrent, EFI, Fault check Signals: G/E, Z/E, 11kv trip Note: G/E, Z/E at Bass Hill Abnormal: Close @ Sw/D @ Sub 6601 Edgar Llma, Open @ Sw/A @ Sub 8573 Remarks: Lightening strike caused feeder to trip. Pnl 1 @ Bankstown tripped at the same time common point of connection is AB 608. | November | 2013 | 2014Q2 | 2014 | ZN2196:PA18 | ZN2196:PA18 | ZN02196/000018 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-11-22 | N | 77.5578 | N | 37 | Y | Y | 1.1101 | 39.4971 | 56393.5599
[7 empty] | 15471 | 8156 | 1044911 | 2013-11-22 07:11 | 2013-11-22 08:52 | 101 | 11kV | 107816 | 1232 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | At Zn35800 Bankstown, 11kv Pnl 1L 'Sub 35208 GOW GIBSON' fdr C/B tripped on: Relays: 50T abc (IOC), 50Tm (E/F0, EFI Signals: 11kv trip Note: G/E, Z/E at Bass Hill Remarks: Lightening strike caused feeder to trip. Pnl 1 @ Bankstown tripped at the same time common point of connection is AB 608 | November | 2013 | 2014Q2 | 2014 | ZN35800:PA1 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-11-22 | N | 87.513 | N | 37 | Y | Y | 1.1101 | 39.4971 | 78788.7528
[7 empty] | 14858 | 1506 | 1044942 | 2013-11-22 08:09 | 2013-11-22 08:58 | 49 | 11kV | 37975 | 775 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Zn.12640 Umina Pnl.16 tripped on EFi, IOC C phase Lightning - mains to patrol | November | 2013 | 2014Q2 | 2014 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Veg | 2013-11-22 | N | 49 | N | 37 | Y | Y | 1.1101 | 39.4971 | 27751.0099
[7 empty] | 15694 | 10971 | 1044933 | 2013-11-22 07:58 | 2013-11-22 09:38 | 100 | 11kV | 700 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 138122 A & B phase DOLF : 16 Amp Excluded OMS 1044933 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2013-11-22 | N | 100 | N | 37 | Y | Y | 1.1101 | 39.4971 | 511.5394
[7 empty] | 14820 | 1108 | 1044927 | 2013-11-22 07:46 | 2013-11-22 10:40 | 174 | 11kV | 348 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138126 Single phase DOLF : 10 Amp Excluded OMS 1044927 | November | 2013 | 2014Q2 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2013-11-22 | N | 174 | N | 37 | Y | Y | 1.1101 | 39.4971 | 254.3081
[7 empty] | 14721 | 230 | 1044912 | 2013-11-22 07:20 | 2013-11-22 11:00 | 220 | 11kV | 3300 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138136 B phase DOLF : 10 Amp Excluded OMS 1044912 | November | 2013 | 2014Q2 | 2014 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2013-11-22 | N | 220 | N | 37 | Y | Y | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 14750 | 497 | 1045073 | 2013-11-22 10:10 | 2013-11-22 11:00 | 50 | 11kV | 100 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138134 Single phase DOLF : 10 Amp replaced 2 x HDO's (fuses) Excluded OMS1045073 | November | 2013 | 2014Q2 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | UG | Not Veg | 2013-11-22 | N | 50 | N | 37 | Y | Y | 1.1101 | 39.4971 | 73.0771
[7 empty] | 16007 | 14701 | 1045045 | 2013-11-22 09:45 | 2013-11-22 11:20 | 95 | 11kV | 285 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138137 Single phase DOLF : 10 Amp Excluded OMS 1045045 | November | 2013 | 2014Q2 | 2014 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | UG | Not Veg | 2013-11-22 | N | 95 | N | 37 | Y | Y | 1.1101 | 39.4971 | 208.2696
[7 empty] | 15906 | 13216 | 1044963 | 2013-11-22 09:04 | 2013-11-22 12:05 | 181 | 11kV | 53371.6 | 297 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | Zn.14143 Sommersby - Pnl.10 tripped on IOC all phases Lightning strike to surge arrestor @ HV UGOH below S46875 see 1045988 1045990 1045991 1045989 | November | 2013 | 2014Q2 | 2014 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Not Veg | 2013-11-22 | N | 179.7024 | N | 37 | Y | Y | 1.1101 | 39.4971 | 39002.3911
[7 empty] | 15611 | 9741 | 1045014 | 2013-11-22 09:27 | 2013-11-22 12:15 | 168 | 11kV | 1512 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | PT13210 Warratah Burnsbrook - 11kV HDO footpath side operated lightning | November | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-11-22 | N | 168 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1104.925
[7 empty] | 14693 | 4 | 1045026 | 2013-11-22 09:09 | 2013-11-22 12:15 | 186 | 11kV | 12090 | 65 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138140 3 phase DOLF Excluded OMS 1045026 | November | 2013 | 2014Q2 | 2014 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | UG | Not Veg | 2013-11-22 | N | 186 | N | 37 | Y | Y | 1.1101 | 39.4971 | 8835.0154
[7 empty] | 16475 | 20211 | 1044971 | 2013-11-22 08:55 | 2013-11-22 12:30 | 215 | 11kV | 12255 | 57 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Lightning | N | PT11873 Venice Como -Center phase HDO blown On restoration volts - 249, 249 & 296 Interrutped again @ 1200 - fault transformer winding restored via LV // see 1045984 1045985 | November | 2013 | 2014Q2 | 2014 | ZN12640:PA8 | ZN12640:PA8 | ZN12640/000008 | CENTRAL COAST | UG | Not Veg | 2013-11-22 | N | 215 | N | 37 | Y | Y | 1.1101 | 39.4971 | 8955.5925
[7 empty] | 14800 | 944 | 1045109 | 2013-11-22 11:07 | 2013-11-22 12:50 | 103 | 11kV | 103 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138145 Single phase DOLF : 10 Amp Excluded OMS 1045109 | November | 2013 | 2014Q2 | 2014 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | UG | Not Veg | 2013-11-22 | N | 103 | N | 37 | Y | Y | 1.1101 | 39.4971 | 75.2694
[7 empty] | 15207 | 4704 | 1045115 | 2013-11-22 11:13 | 2013-11-22 13:10 | 117 | 11kV | 1287 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | PT13137 Wise Ferry Lilli 0.3 - 11kV HDO fuse blown footpath side lightning | November | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-11-22 | N | 117 | N | 37 | Y | Y | 1.1101 | 39.4971 | 940.5016
[7 empty] | 15722 | 11197 | 1045085 | 2013-11-22 10:23 | 2013-11-22 13:39 | 196 | 11kV | 16856 | 86 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 138150 C phase DOLF : 31 Amp Faulty arrester cut away at sub 2159. | November | 2013 | 2014Q2 | 2014 | 256:80638 | 256:80638 | ZN00256/080638 | NEWCASTLE | OH | Not Veg | 2013-11-22 | N | 196 | N | 37 | Y | Y | 1.1101 | 39.4971 | 12317.8676
[7 empty] | 15005 | 2892 | 1047082 | 2013-11-22 13:33 | 2013-11-22 13:39 | 6 | 11kV | 5586 | 931 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 138151 1 fault operation 3 phase Sensitive Earth Fault Sub with faulty arresters backfed. | November | 2013 | 2014Q2 | 2014 | 256:80638 | 256:80638 | ZN00256/080638 | NEWCASTLE | OH | Not Veg | 2013-11-22 | N | 6 | N | 37 | Y | Y | 1.1101 | 39.4971 | 4082.084
[7 empty] | 15033 | 3079 | 1045054 | 2013-11-22 09:55 | 2013-11-22 14:15 | 260 | 11kV | 4160 | 16 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Unselected | N | PT14213 Soldieers Victoria - 11kV centre phase HDO blown Lightning strikes in area | November | 2013 | 2014Q2 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-22 | N | 260 | N | 37 | Y | Y | 1.1101 | 39.4971 | 3040.0053
[7 empty] | 16193 | 16971 | 1045037 | 2013-11-22 09:26 | 2013-11-22 15:50 | 384 | 11kV | 59728 | 162 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 138132 C phase ABS 8705 & tappings pole JU-33968 damaged by lightning. Also see report 138131. Excluded OMS # 1045012 | November | 2013 | 2014Q2 | 2014 | 203:8086 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2013-11-22 | N | 368.6914 | N | 37 | Y | Y | 1.1101 | 39.4971 | 43647.4607
[7 empty] | 15181 | 4421 | 1045321 | 2013-11-22 14:48 | 2013-11-22 16:13 | 85 | 11kV | 14157 | 198 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138157 1 fault operation C phase Earth fault Reclose was switched off for emergency works beyond ABS 47780. Please patrol Feeder. Excluded OMS No. 1045321 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2013-11-22 | N | 71.5 | N | 37 | Y | Y | 1.1101 | 39.4971 | 10345.518
[7 empty] | 16468 | 20148 | 1045394 | 2013-11-22 15:57 | 2013-11-22 17:00 | 63 | 11kV | 2268 | 36 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Lightning | N | PT9395 Anzac Highway - DOp found 2 x HDOs blown Restored via LV // Interrupted at same time as Pnl.3 and Pnl.15 @ Engadine zone | November | 2013 | 2014Q2 | 2014 | ZN9245:PA15 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | OH | Not Veg | 2013-11-22 | N | 63 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1657.3875
[7 empty] | 15436 | 7854 | 1045320 | 2013-11-22 14:51 | 2013-11-22 17:00 | 129 | 11kV | 129 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138154 B Phase No protection operations. B ph DOLF found arcing. Carrier welded shut & arcing stopped when trying to remove. Please investigate ASAP. Excluded OMS 1045320. | November | 2013 | 2014Q2 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | UG | Not Veg | 2013-11-22 | N | 129 | N | 37 | Y | Y | 1.1101 | 39.4971 | 94.2694
[7 empty] | 14828 | 1233 | 1045422 | 2013-11-22 16:16 | 2013-11-22 17:10 | 54 | 11kV | 15390 | 285 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | REC 41845 North Erina tripped on OC trip and lockout tree branch on mains outside 210 Wattle Tree Rd Holgate | November | 2013 | 2014Q2 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2013-11-22 | N | 54 | N | 37 | Y | Y | 1.1101 | 39.4971 | 11246.5581
[7 empty] | 14856 | 1486 | 1047631 | 2013-11-22 16:07 | 2013-11-22 17:20 | 73 | 11kV | 1606 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138167 B & C phase DOLF : 16 Amp Excluded OMS 1045406 & 1045420 | November | 2013 | 2014Q2 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2013-11-22 | N | 73 | N | 37 | Y | Y | 1.1101 | 39.4971 | 1173.6174
[7 empty] | 15174 | 4348 | 1045383 | 2013-11-22 15:51 | 2013-11-22 17:40 | 109 | 11kV | 1308 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138169 Single phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-11-22 | N | 109 | N | 37 | Y | Y | 1.1101 | 39.4971 | 955.8478
[7 empty] | 16338 | 18384 | 1044889 | 2013-11-22 04:46 | 2013-11-22 18:00 | 794 | 11kV | 33917 | 205 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 138109 Earth fault section isolated beyond abs 47780 to repair pole AL-80078 Excluded oms 1044889 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2013-11-22 | N | 165.4488 | N | 37 | Y | Y | 1.1101 | 39.4971 | 24785.5432
[7 empty] | 15974 | 14221 | 1044960 | 2013-11-22 08:39 | 2013-11-22 18:20 | 581 | 11kV | 7091 | 18 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | Ex Zn14891 Wyong Pnl.8 - @ PT14351 Valley Prestons 0.6 - Footpath phase HVDO operated @PT13658 Valley Prestons 0.5 - Footpath phase HVDO operated Lightning arrestors / HV fuses replaced by subs under limited operating procedures . HV feeder isolated from LK42275 @ 16:40 see 1046022 1046021 1046023 | November | 2013 | 2014Q2 | 2014 | ZN14891:PA8 | ZN14891:PA8 | ZN14891/000008 | CENTRAL COAST | OH | Not Veg | 2013-11-22 | N | 393.9444 | N | 37 | Y | Y | 1.1101 | 39.4971 | 5181.8937
[7 empty] | 15208 | 4707 | 1045436 | 2013-11-22 16:31 | 2013-11-22 18:30 | 119 | 11kV | 238 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138171 C phase DOLF : 10 Amp Excluded OMS 1045436 | November | 2013 | 2014Q2 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2013-11-22 | N | 119 | N | 37 | Y | Y | 1.1101 | 39.4971 | 173.9234
[7 empty] | 15397 | 7426 | 1045202 | 2013-11-22 13:09 | 2013-11-22 18:35 | 326 | 11kV | 606896 | 2551 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | N | Zn.12610 long Jetty Pnl.17 - tripped on SEF Abnormal: LB45159 CLOSED - LB45161 OPEN - LB43314 OPEN - PT13685 in LV// Bond burnt @ AB42561 repaired - AB42560 welded shut not repaired see 1046028 1046031 1046029 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA11 | ZN12610:PA11 | ZN12610/000011 | CENTRAL COAST | OH | Not Veg | 2013-11-22 | N | 237.9051 | N | 37 | Y | Y | 1.1101 | 39.4971 | 443501.6964
[7 empty] | 15958 | 13941 | 1045526 | 2013-11-22 18:46 | 2013-11-22 19:53 | 67 | 11kV | 67 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138173 Single phase DOLF : 10 Amp Excluded OMS 1045526 | November | 2013 | 2014Q2 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2013-11-22 | N | 67 | N | 37 | Y | Y | 1.1101 | 39.4971 | 48.9616
[7 empty] | 16231 | 17378 | 1045540 | 2013-11-22 19:10 | 2013-11-22 20:00 | 50 | 11kV | 3300 | 77 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn.630 mascot pnl.40 - tripped on A phase overcurrent Field EFIs: S5377 S1629 S3709 Cable fault between S3076 to S2457. East subs note no EFI @ S3076 see 1046330 1046331 1046332 | November | 2013 | 2014Q2 | 2014 | ZN630:PA40 | ZN630:PA40 | ZN00630/000040 | SYDNEY | UG | Not Veg | 2013-11-22 | N | 42.8571 | N | 37 | Y | Y | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 15717 | 11121 | 1047641 | 2013-11-22 16:34 | 2013-11-22 20:02 | 208 | 11kV | 416 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138174 B phase DOLF : 10 Amp Excluded OMS 1045439 | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-11-22 | N | 208 | N | 37 | Y | Y | 1.1101 | 39.4971 | 304.0005
[7 empty] | 16389 | 18977 | 1045448 | 2013-11-22 15:00 | 2013-11-22 20:03 | 303 | 11kV | 171958 | 685 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Electrical Storm | N | LID 138165 1 fault operation c phase DOLF : 10 Amp at sub 72097 Overcurrent Bushfire defective Fdr. Reclose NA. DOLF found blown at Segenhoe st sub 72097. Excluded OMS No. 1045448 | November | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | UG | Not Veg | 2013-11-22 | N | 251.0336 | N | 37 | Y | Y | 1.1101 | 39.4971 | 125661.8345
[7 empty] | 15734 | 11429 | 1045489 | 2013-11-22 17:30 | 2013-11-22 21:03 | 213 | 11kV | 30885 | 145 | HV | Staff Other | Utility Process Issue | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 138158 No protection operations. Section isolated to replace 33kV insulators at poles JV-20798 & 99. Excluded OMS # 1045489 | November | 2013 | 2014Q2 | 2014 | 221:11895 | 221:11895 | ZN00221/011895 | LAKE MACQUARIE | OH | Not Veg | 2013-11-22 | N | 213 | N | 37 | Y | Y | 1.1101 | 39.4971 | 22569.847
[7 empty] | 14711 | 131 | 1045533 | 2013-11-22 18:55 | 2013-11-22 22:10 | 195 | 11kV | 390 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138176 3 phase DOLF : 10 Amp Excluded OMS 1045533 | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-11-22 | N | 195 | N | 37 | Y | Y | 1.1101 | 39.4971 | 285.0005
[7 empty] | 14732 | 315 | 1045574 | 2013-11-22 22:04 | 2013-11-23 02:25 | 261 | 11kV | 2871 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138177 A Phase DOLF : 20 Amp Excluded OMS 1045574 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2013-11-22 | N | 261 | N | 37 | Y | Y | 1.1101 | 39.4971 | 2098.0421
[7 empty] | 16388 | 18971 | 1045595 | 2013-11-23 03:52 | 2013-11-23 04:20 | 28 | 11kV | 2604 | 93 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Light | N | LID 138178 C phase DOLF : 31 Amp Excluded OMS 1045595 | November | 2013 | 2014Q2 | 2014 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | UG | Not Veg | 2013-11-23 | N | 28 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1902.9264
[7 empty] | 15521 | 8719 | 1045603 | 2013-11-23 06:49 | 2013-11-23 07:50 | 61 | 11kV | 1952 | 32 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138188 C phase DOLF : 20 Amp Excluded OMS 1045603 | November | 2013 | 2014Q2 | 2014 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | UG | Not Veg | 2013-11-23 | N | 61 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1426.464
[7 empty] | 16405 | 19207 | 1045628 | 2013-11-23 08:30 | 2013-11-23 08:39 | 9 | 11kV | 6822 | 758 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn.12650 West Gosford Pnl.10 tripped on C phase O/C and EFI Abnormal: S11609 Sw 1753 CLOSED - S47762 Sw A OPEN Branch on 11kV outside 82/84 Donnison Rd Palm Fronds | November | 2013 | 2014Q2 | 2014 | ZN12650:PA10 | ZN12650:PA10 | ZN12650/000010 | CENTRAL COAST | OH | Veg | 2013-11-23 | N | 9 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4985.3164
[7 empty] | 15918 | 13318 | 1045615 | 2013-11-23 08:00 | 2013-11-23 09:15 | 75 | 11kV | 2925 | 39 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138199 A & C phase DOLF : 20 Amp Excluded OMS 1045630 | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-11-23 | N | 75 | N | 35 | Y | Y | 1.1101 | 39.4971 | 2137.5037
[7 empty] | 15993 | 14520 | 1045606 | 2013-11-23 07:02 | 2013-11-23 09:38 | 156 | 11kV | 31980 | 205 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 138198 2 fault operations A & C phase Earth fault LIGHTENING HIT POLE AL-80081,2 BROKEN 11KV PINS. | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2013-11-23 | N | 156 | N | 35 | Y | Y | 1.1101 | 39.4971 | 23370.0407
[7 empty] | 15046 | 3159 | 1045618 | 2013-11-23 08:20 | 2013-11-23 10:15 | 115 | 11kV | 1610 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138230 A & B phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2013-11-23 | N | 115 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1176.5405
[7 empty] | 15529 | 8784 | 1045621 | 2013-11-23 08:00 | 2013-11-23 11:00 | 180 | 11kV | 1800 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138231 3 phase DOLF : 20 Amp and LID 138226 A phase DOLF : 10 Amp (for sub 70027:11kV) CC1: 06-"Urgent - O.H Mains - No others" | November | 2013 | 2014Q2 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2013-11-23 | N | 180 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 15040 | 3115 | 1045633 | 2013-11-23 08:30 | 2013-11-23 11:30 | 180 | 11kV | 360 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138229 B phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2013-11-23 | N | 180 | N | 35 | Y | Y | 1.1101 | 39.4971 | 263.0774
[7 empty] | 14827 | 1230 | 1045659 | 2013-11-23 10:00 | 2013-11-23 12:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138227 A phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-11-23 | N | 120 | N | 35 | Y | Y | 1.1101 | 39.4971 | 87.6925
[7 empty] | 14873 | 1703 | 1045663 | 2013-11-23 12:04 | 2013-11-23 13:14 | 70 | 11kV | 141400 | 2020 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Zn.965 Pennant Hills - Pnl.3 tripped on A phase timed O/C and EFI Lightning at time of interruption - DOp patrolled no damage | November | 2013 | 2014Q2 | 2014 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2013-11-23 | N | 70 | N | 35 | Y | Y | 1.1101 | 39.4971 | 103330.9494
[7 empty] | 14695 | 17 | 1045681 | 2013-11-23 10:51 | 2013-11-23 14:26 | 215 | 11kV | 430 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138234 Single phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2013-11-23 | N | 215 | N | 35 | Y | Y | 1.1101 | 39.4971 | 314.2313
[7 empty] | 15195 | 4551 | 1045746 | 2013-11-23 13:06 | 2013-11-23 14:34 | 88.2167 | 11kV | 4675.4833 | 53 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138236 A & B phase DOLF : 20 Amp CC1: 06-"Urgent - O.H Mains - No others" | November | 2013 | 2014Q2 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2013-11-23 | N | 88.2167 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3416.7053
[7 empty] | 15382 | 7210 | 1045724 | 2013-11-23 12:30 | 2013-11-23 14:35 | 125 | 11kV | 170125 | 1361 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Zn.1673 Turramurra - Pnl.18 tripped on A, B & C phase IOC Lightning at time - patrolled nothing found | November | 2013 | 2014Q2 | 2014 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2013-11-23 | N | 125 | N | 35 | Y | Y | 1.1101 | 39.4971 | 124322.3322
[7 empty] | 15902 | 13191 | 1045783 | 2013-11-23 14:09 | 2013-11-23 14:48 | 39 | 11kV | 26715 | 685 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138222 1 fault operation C phase Overcurrent A/R for bushfire season | November | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2013-11-23 | N | 39 | N | 35 | Y | Y | 1.1101 | 39.4971 | 19522.534
[7 empty] | 15465 | 8085 | 1045703 | 2013-11-23 11:47 | 2013-11-23 15:00 | 193 | 11kV | 18721 | 97 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138217 A & C phase Earth fault; Overcurrent | November | 2013 | 2014Q2 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2013-11-23 | N | 193 | N | 35 | Y | Y | 1.1101 | 39.4971 | 13680.7546
[7 empty] | 16336 | 18357 | 1045725 | 2013-11-23 12:25 | 2013-11-23 16:04 | 219 | 11kV | 31494 | 150 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 138243 1 fault operation A phase Overcurrent | November | 2013 | 2014Q2 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2013-11-23 | N | 209.96 | N | 35 | Y | Y | 1.1101 | 39.4971 | 23014.8863
[7 empty] | 15514 | 8604 | 1045675 | 2013-11-23 12:10 | 2013-11-23 16:25 | 255 | 11kV | 4845 | 19 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | PT12035 Erina Valley Ports 0.5 - Interrupted by DOp Trees brought down CCT in Erina Valley Rd feeder from USL 42282 to PT12035 CC1: 22-"Refer to SOp" | November | 2013 | 2014Q2 | 2014 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Veg | 2013-11-23 | N | 255 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3540.5831
[7 empty] | 16450 | 19932 | 1045807 | 2013-11-23 14:49 | 2013-11-23 16:35 | 106.0833 | 11kV | 4985.9167 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138241 3 Phase DOLF : 40 Amp | November | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2013-11-23 | N | 106.0833 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3643.5608
[7 empty] | 14801 | 947 | 1045836 | 2013-11-23 15:55 | 2013-11-23 17:00 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138239 A phase DOLF : 10 Amp Excluded OMS 1045839 | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-11-23 | N | 65 | N | 35 | Y | Y | 1.1101 | 39.4971 | 95.0002
[7 empty] | 15269 | 5931 | 1045671 | 2013-11-23 12:12 | 2013-11-23 17:27 | 315 | 11kV | 29996 | 96 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 138245 A & B phase Overcurrent 11 kV mains down at pole WT 30051 Excluded OMS 1045671 | November | 2013 | 2014Q2 | 2014 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2013-11-23 | N | 312.4583 | N | 35 | Y | Y | 1.1101 | 39.4971 | 21920.1921
[7 empty] | 15186 | 4443 | 1045648 | 2013-11-23 09:25 | 2013-11-23 17:37 | 492 | 11kV | 1476 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Insulator | Unplanned | Lightning | N | no further information available also refer to 1045648 | November | 2013 | 2014Q2 | 2014 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2013-11-23 | N | 492 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1078.6173
[7 empty] | 15142 | 4077 | 1045829 | 2013-11-23 15:41 | 2013-11-23 18:00 | 139 | 11kV | 1668 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138280 A phase DOLF : 31 Amp LA's OK. Had incorrect DOLF fuse size installed. Excluded OMS No. 1045829 | November | 2013 | 2014Q2 | 2014 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | UG | Not Veg | 2013-11-23 | N | 139 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1218.9252
[7 empty] | 15564 | 9078 | 1045857 | 2013-11-23 15:30 | 2013-11-23 18:15 | 165 | 11kV | 980 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 138223 Isolated subs 27095 & 11252 to repair 33kV tapping above. blown 33kV tapping pole HW-70793. See report 138203 | November | 2013 | 2014Q2 | 2014 | 243:80074 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Not Veg | 2013-11-23 | N | 163.3333 | N | 35 | Y | Y | 1.1101 | 39.4971 | 716.1551
[7 empty] | 16135 | 16345 | 1045865 | 2013-11-23 17:30 | 2013-11-23 18:20 | 50 | 11kV | 100 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138237 Single phase DOLF : Excluded OMS 1045865 | November | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | UG | Not Veg | 2013-11-23 | N | 50 | N | 35 | Y | Y | 1.1101 | 39.4971 | 73.0771
[7 empty] | 16414 | 19365 | 1045727 | 2013-11-23 11:03 | 2013-11-23 18:45 | 462 | 11kV | 412269 | 1338 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | Ex Zn.12600 Lisarow Pnl.9 - REC 47607 Toomeys Rd tripped on Earth Fault Defective lightning arrestors between LK44339 and AB44074 - Defective LB45039 has also been repaired Extended outage also due to lisarow zone tripping @ 11:05 see 1046007 see 1046008 1046011 | November | 2013 | 2014Q2 | 2014 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2013-11-23 | N | 308.1233 | N | 35 | Y | Y | 1.1101 | 39.4971 | 301274.0253
[7 empty] | 15133 | 4011 | 1046911 | 2013-11-23 15:59 | 2013-11-23 18:45 | 166 | 11kV | 8964 | 54 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 138254 1 fault operation Broken cross arm at pole 8J-80098 Note: all calls associated with this job are attached to OMS 1045828, as the feeder was not closed in OMS, thus when the second incident happened - see LID 138262, the calls for the second incident grouped with this first incident | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-11-23 | N | 166 | N | 35 | Y | Y | 1.1101 | 39.4971 | 6550.6268
[7 empty] | 14759 | 541 | 1045599 | 2013-11-23 15:40 | 2013-11-23 19:00 | 200.4833 | 11kV | 200.4833 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138251 Single phase DOLF : 10 Amp CC1: 06-"Urgent - O.H Mains - No others" | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2013-11-23 | N | 200.4833 | N | 35 | Y | Y | 1.1101 | 39.4971 | 146.5073
[7 empty] | 15340 | 6742 | 1045794 | 2013-11-23 14:21 | 2013-11-23 19:50 | 329.3667 | 11kV | 5928.6 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138253 A & B phase DOLF : 10 Amp | November | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-11-23 | N | 329.3667 | N | 35 | Y | Y | 1.1101 | 39.4971 | 4332.446
[7 empty] | 14961 | 2414 | 1045871 | 2013-11-23 18:15 | 2013-11-23 20:58 | 163 | 11kV | 474.3333 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138248 A phase DOLF : 31 Amp Excluded OMS 1045871 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-11-23 | N | 158.1111 | N | 35 | Y | Y | 1.1101 | 39.4971 | 346.6288
[7 empty] | 14837 | 1289 | 1045631 | 2013-11-23 11:25 | 2013-11-23 21:00 | 575 | 11kV | 10285 | 26 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 138244 1 fault operation Burnt off bond adjacent to ABS 61103 Blown arrestors at various subs Excluded OMS 1045631 | November | 2013 | 2014Q2 | 2014 | 501:48122 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2013-11-23 | N | 395.5769 | N | 35 | Y | Y | 1.1101 | 39.4971 | 7515.9746
[7 empty] | 14987 | 2676 | 1045849 | 2013-11-23 16:24 | 2013-11-23 21:15 | 291 | 11kV | 4365 | 15 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 138255 Blown arrestors at sub 59018 Excluded OMS 1045873 | November | 2013 | 2014Q2 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-11-23 | N | 291 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3189.8133
[7 empty] | 16133 | 16299 | 1045744 | 2013-11-23 13:03 | 2013-11-23 22:40 | 577.4833 | 11kV | 7507.2833 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138258 A & B Phase DOLF : 10 Amp CC1: 22-"Refer to SOp" | November | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2013-11-23 | N | 577.4833 | N | 35 | Y | Y | 1.1101 | 39.4971 | 5486.1012
[7 empty] | 15041 | 3118 | 1045816 | 2013-11-23 18:37 | 2013-11-24 01:45 | 428 | 11kV | 154843 | 2105 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 138246 Intellirupter 4968 Fishermans Bay UGOH near ABS 19254 | November | 2013 | 2014Q2 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | Unknown | Unknown | 2013-11-23 | N | 73.5596 | N | 35 | Y | Y | 1.1101 | 39.4971 | 113154.6973
[7 empty] | 16321 | 18227 | 1045927 | 2013-11-24 04:41 | 2013-11-24 05:58 | 77 | 11kV | 12915 | 171 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2635 Epping - Pnl.55 tripped on EFI, C phase No.1 timmed O/C, C phase No.2 timmed O/C UG cable fault from S49503 to S5702 to S4626 see 1046155 1045154 | November | 2013 | 2014Q2 | 2014 | ZN2635:PA55 | ZN2635:PA55 | ZN02635/000055 | PARRAMATTA | UG | Not Veg | 2013-11-24 | N | 75.5263 | N | 11 | N | N | 1.1101 | 39.4971 | 9437.9011
[7 empty] | 15277 | 6177 | 1045803 | 2013-11-23 14:41 | 2013-11-24 08:15 | 1054 | 11kV | 3162 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 138266 Single phase DOLF : 10 Amp Excluded OMS 1045880 & 1045803 | November | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2013-11-23 | N | 1054 | N | 35 | Y | Y | 1.1101 | 39.4971 | 2310.6963
[7 empty] | 15147 | 4143 | 1045937 | 2013-11-24 07:09 | 2013-11-24 09:00 | 111 | 11kV | 111 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | LID 138267 Single phase DOLF : 10 Amp Broken DOLF Excluded OMS 1045937 | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-11-24 | N | 111 | N | 11 | N | N | 1.1101 | 39.4971 | 81.1155
[7 empty] | 15162 | 4234 | 1045828 | 2013-11-23 19:00 | 2013-11-24 12:15 | 1035 | 11kV | 58033 | 263 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 138262 2 fault operations 3 phase Overcurrent Pole 9K-50109 damaged. Excluded OMS 1045828, 1045920, 1045935, 1045942, 1045945. | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-11-23 | N | 220.6578 | N | 35 | Y | Y | 1.1101 | 39.4971 | 42408.8047
[7 empty] | 14867 | 1636 | 1046018 | 2013-11-24 11:31 | 2013-11-24 12:20 | 49 | 11kV | 49 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138272 Single phase DOLF : 10 Amp Tx Volts 245V Excluded OMS 1046018 | November | 2013 | 2014Q2 | 2014 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2013-11-24 | N | 49 | N | 11 | N | N | 1.1101 | 39.4971 | 35.8078
[7 empty] | 15928 | 13410 | 1045943 | 2013-11-24 07:54 | 2013-11-24 13:20 | 326 | 11kV | 326 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138269 A & C phase DOLF : 10 Amp Excluded OMS 1045943 | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | UG | Not Veg | 2013-11-24 | N | 326 | N | 11 | N | N | 1.1101 | 39.4971 | 238.2312
[7 empty] | 16486 | 20310 | 1046030 | 2013-11-24 12:07 | 2013-11-24 15:30 | 203 | 11kV | 203 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138278 Single phase DOLF : 10 Amp Excluded OMS 1046030 | November | 2013 | 2014Q2 | 2014 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | UG | Not Veg | 2013-11-24 | N | 203 | N | 11 | N | N | 1.1101 | 39.4971 | 148.3464
[7 empty] | 15887 | 13032 | 1045966 | 2013-11-24 09:14 | 2013-11-24 18:22 | 548 | 11kV | 772 | 33 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 138274 1 fault operation Single phase DOLF : 3 Amp Overcurrent Giants Creek RAGCB tripped (faulty TX) at 1400hrs after replacing DOLF & LAs. Replaced defective Tx. Excluded OMS 1045966 | November | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | UG | Not Veg | 2013-11-24 | N | 23.3939 | N | 11 | N | N | 1.1101 | 39.4971 | 564.1548
[7 empty] | 16200 | 17077 | 1046002 | 2013-11-24 10:59 | 2013-11-24 19:00 | 481 | 11kV | 1443 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 138281 A phase Repair Aph burnt off t-off to LL clamps at pole 8M-60051. Excluded OMS No. 1046002 | November | 2013 | 2014Q2 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2013-11-24 | N | 481 | N | 11 | N | N | 1.1101 | 39.4971 | 1054.5018
[7 empty] | 16034 | 15136 | 1046069 | 2013-11-24 14:15 | 2013-11-24 19:00 | 285 | 11kV | 855 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138283 Single phase DOLF : 5 Amp Excluded OMS 1046069 | November | 2013 | 2014Q2 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-11-24 | N | 285 | N | 11 | N | N | 1.1101 | 39.4971 | 624.8088
[7 empty] | 16459 | 20062 | 1046056 | 2013-11-24 13:05 | 2013-11-24 20:07 | 422 | 11kV | 1266 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138285 B phase DOLF : 3 Amp Excluded OMS 1046056 | November | 2013 | 2014Q2 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | UG | Not Veg | 2013-11-24 | N | 422 | N | 11 | N | N | 1.1101 | 39.4971 | 925.1555
[7 empty] | 15544 | 8893 | 1046121 | 2013-11-24 19:18 | 2013-11-24 21:30 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138286 C phase DOLF : 10 Amp Excluded OMS 1046121 | November | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | UG | Not Veg | 2013-11-24 | N | 132 | N | 11 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 15618 | 9881 | 1045732 | 2013-11-24 12:44 | 2013-11-24 23:00 | 616 | 11kV | 616 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138263 Line DOLF : 10 Amp Could not access fuse until flooding subsided Excluded OMS 1045732 | November | 2013 | 2014Q2 | 2014 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2013-11-24 | N | 616 | N | 11 | N | N | 1.1101 | 39.4971 | 450.1546
[7 empty] | 15139 | 4059 | 1046410 | 2013-11-25 12:47 | 2013-11-25 15:14 | 147 | 11kV | 271438 | 2713 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S.15011 Beacon Hill, Panel 2 Fdr CB tripped on A phase IOC and Timed OC, C phase IOC, efi, 11kV trip signal. UG/OH adjacent AB.25229 failed | November | 2013 | 2014Q2 | 2014 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | Unknown | Unknown | 2013-11-25 | N | 100.0509 | N | 11 | N | N | 1.1101 | 39.4971 | 198358.8843
[7 empty] | 15745 | 11596 | 1046486 | 2013-11-25 14:00 | 2013-11-25 15:17 | 77 | 11kV | 87943 | 1217 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | At S965 Pennant Hills Panel No 15 Tripped reclosed tripped and locked out on Earth Fault, A phase Inst and Timed O/C, Timing and lockout relays with EFI. Zone Earth No2 Group Earth aand 11kV trip Cause: Lightning hit tree coming down on OH Near AB192 to S1567 See OMS 1046937 1046486 | November | 2013 | 2014Q2 | 2014 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Veg | 2013-11-25 | N | 72.2621 | N | 11 | N | N | 1.1101 | 39.4971 | 64266.1505
[7 empty] | 15575 | 9150 | 1046456 | 2013-11-25 13:33 | 2013-11-25 15:40 | 127 | 11kV | 159272 | 1651 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138300 3 phase Overcurrent Feeder restored in sections. No fault found. Can not confirm if reclose worked correctly. | November | 2013 | 2014Q2 | 2014 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2013-11-25 | N | 96.47 | N | 11 | N | N | 1.1101 | 39.4971 | 116391.2799
[7 empty] | 16483 | 20276 | 1046428 | 2013-11-25 13:05 | 2013-11-25 16:21 | 196 | 11kV | 392 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 138302 Fuse size: 16 Amp replaced HV arrestors also refer to OMS 1046428 | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2013-11-25 | N | 196 | N | 11 | N | N | 1.1101 | 39.4971 | 286.462
[7 empty] | 15520 | 8709 | 1046547 | 2013-11-25 15:02 | 2013-11-25 16:44 | 102 | 11kV | 46923 | 691 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Rain Light | N | At S4545 Meadowbank Panel 6 Tripped Cause: Possum on 11kV OH adjacent to PT1714 Anzac Orchard HDO damaged at PT1714 and requires replacement 1046835 1046837 1046838 1046839 1046547 | November | 2013 | 2014Q2 | 2014 | ZN4545:PA6 | ZN4545:PA6 | ZN04545/000006 | RYDE | OH | Not Veg | 2013-11-25 | N | 67.9059 | N | 11 | N | N | 1.1101 | 39.4971 | 34289.9444
[7 empty] | 15384 | 7244 | 1046599 | 2013-11-25 16:02 | 2013-11-25 16:49 | 47 | 11kV | 46436 | 988 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn398 Dulwich Hill Pnl.11 feeder open circuit on one phase to S6625 Norton Queen No protection operation Abnormal: Pnl.11 @ Dulwich Hill OPEN - S6625 Norton Queen SwA OPEN - Pnl.13 @ Dulwich Hill CLOSED While restoring Pnl.11 from S6625 SwA after planned CB replacement. Suspect RMI @S6625 is defective or open circuit cable from Pnl.11 to S6625 | November | 2013 | 2014Q2 | 2014 | ZN398:PA11 | ZN398:PA11 | ZN00398/000011 | INNER WEST | UG | Not Veg | 2013-11-25 | N | 47 | N | 11 | N | N | 1.1101 | 39.4971 | 33934.0592
[7 empty] | 14974 | 2588 | 1046647 | 2013-11-25 16:59 | 2013-11-25 17:33 | 34 | 11kV | 8670 | 255 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Heavy | N | Zn12610 Long Jetty section of Pa2 "Bateau Bay" 11kv feeder from USL 40263 to AB41760 interupted Cause: interrupted to repair Bond at centre phase USL 40263 See 1046915 exclude 1046647 | November | 2013 | 2014Q2 | 2014 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2013-11-25 | N | 34 | N | 11 | N | N | 1.1101 | 39.4971 | 6335.7803
[7 empty] | 15216 | 4878 | 1046487 | 2013-11-25 14:05 | 2013-11-25 22:00 | 475 | 11kV | 259406 | 1877 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hills Panel 42 Tripped on Earth Fault and EFI, Zone Earth, No2 Group Earth and 11kV Trip. Abnormal Switching: Panel 29 was under Access D&R 326189, SW/B closed at S5402 Cause: UG Cable Fault between S4513 SW/B - S48294 SW/A - CP1352 See OMS 1047276 1047279 1047280 1047290 1046487 1046490 1046602 1046721 | November | 2013 | 2014Q2 | 2014 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | UG | Not Veg | 2013-11-25 | N | 138.2025 | N | 11 | N | N | 1.1101 | 39.4971 | 189566.2536
[7 empty] | 15098 | 3688 | 1046734 | 2013-11-25 21:29 | 2013-11-25 22:08 | 39 | 11kV | 50544 | 1296 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn.9550 Gwawley Bay - Pnl.3 tripped on A & B phase IOC Bat into mains at 2 Harrow Road - Oatley mains to inspect | November | 2013 | 2014Q2 | 2014 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | OH | Not Veg | 2013-11-25 | N | 39 | N | 11 | N | N | 1.1101 | 39.4971 | 36936.0644
[7 empty] | 16234 | 17414 | 1049392 | 2013-11-25 23:06 | 2013-11-26 01:08 | 122 | 11kV | 13054 | 107 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Last part of LID 138306 5 fault operations B phase Earth fault Mains down between poles IQ-41141 & IQ-41142 Excluded OMS # 1046744. | November | 2013 | 2014Q2 | 2014 | 501:48123 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2013-11-25 | N | 122 | N | 11 | N | N | 1.1101 | 39.4971 | 9539.4782
[7 empty] | 14909 | 1977 | 1046744 | 2013-11-25 23:06 | 2013-11-26 07:20 | 494 | 11kV | 155021 | 1069 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 138306 5 fault operations B phase Earth fault Mains down between poles IQ-41141 & IQ-41142 Excluded OMS # 1046744. | November | 2013 | 2014Q2 | 2014 | 501:48123 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2013-11-25 | N | 145.015 | N | 11 | N | N | 1.1101 | 39.4971 | 113284.7745
[7 empty] | 15027 | 3044 | 1046769 | 2013-11-26 11:00 | 2013-11-26 12:10 | 70 | 11kV | 140 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138320 Fuse: 10 Amp | November | 2013 | 2014Q2 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2013-11-26 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 14836 | 1281 | 1047042 | 2013-11-26 13:02 | 2013-11-26 15:09 | 127 | 11kV | 116750 | 1068 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12690 Berkeley Vale tripped, reclosed & locked out: Relays: B&Cphase IOC trip, Auto Reclose Flag, Lock out Flag Signals: 11kv trip EFI's: nil Cause: Not ascertained. DOp patrolled feeder, no cause found See 1047329,30,2,3,4 Exclude 1047042,56,8,79 | November | 2013 | 2014Q2 | 2014 | ZN12690:PA12 | ZN12690:PA12 | ZN12690/000012 | CENTRAL COAST | OH | Veg | 2013-11-26 | N | 109.3165 | N | 3 | N | N | 1.1101 | 39.4971 | 85317.4565
[7 empty] | 16328 | 18272 | 1047163 | 2013-11-26 16:00 | 2013-11-26 17:55 | 115 | 11kV | 5405 | 47 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 138325 B & C phase DOLF : 10 Amp Sub 26169. DOLF carrier broke when closing in fuse cartridge. Insulator broke in two. Blackout required to repair. No OMS No for initial sub job at 26169. Crow caused fuses to blow. | November | 2013 | 2014Q2 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2013-11-26 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 3949.8146
[7 empty] | 16245 | 17507 | 1047244 | 2013-11-27 07:31 | 2013-11-27 08:45 | 74 | 11kV | 38604 | 690 | HV | Staff Operation | Utility Process Issue | Recloser / Sectionaliser | Unplanned | No Weather Impact | N | Recloser 3282 Alberta Ave Tripped and locked out ib SEL. Cause: During Switching SEL at REC3282 was left auto 1048451 1048453 1047244 | November | 2013 | 2014Q2 | 2014 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2013-11-27 | N | 55.9478 | N | 7 | N | N | 1.1101 | 39.4971 | 28210.6646
[7 empty] | 15489 | 8305 | 1047308 | 2013-11-27 08:41 | 2013-11-27 10:20 | 99 | 11kV | 396 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 138338 Fuse: 16 Amp fatigued fuse reading as left 248V, @ 6A, 25A, 38A also refer to OMS 1047308 | November | 2013 | 2014Q2 | 2014 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Not Veg | 2013-11-27 | N | 99 | N | 7 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 15899 | 13162 | 1047499 | 2013-11-27 11:56 | 2013-11-27 12:45 | 49 | 11kV | 50274 | 1026 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2602 Clovelly Pnl.8 - tripped on E/F. EFC, EFI UG cable fault from S35539 Sw B to S8812 Sw A see 1048258 1048261 1048259 | November | 2013 | 2014Q2 | 2014 | ZN2602:PA8 | ZN2602:PA46 | ZN02602/000046 | WAVERLEY | UG | Not Veg | 2013-11-27 | N | 49 | N | 7 | N | N | 1.1101 | 39.4971 | 36738.7564
[7 empty] | 14722 | 234 | 1047480 | 2013-11-27 11:30 | 2013-11-27 13:45 | 135 | 11kV | 270 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138343 Fuse: 10 Amp Line Dolf, no cause found - not storm conditions also refer to 1047480 | November | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2013-11-27 | N | 135 | N | 7 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 15232 | 5280 | 1047391 | 2013-11-27 09:53 | 2013-11-27 14:30 | 277 | 11kV | 554 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Cause not ascertained - 2 customer affected | November | 2013 | 2014Q2 | 2014 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-11-27 | N | 277 | N | 7 | N | N | 1.1101 | 39.4971 | 404.8469
[7 empty] | 14725 | 258 | 1047673 | 2013-11-27 15:54 | 2013-11-27 18:35 | 161 | 11kV | 161 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 138347 also refer to 1047673 | November | 2013 | 2014Q2 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2013-11-27 | N | 161 | N | 7 | N | N | 1.1101 | 39.4971 | 117.6541
[7 empty] | 15753 | 11666 | 1047715 | 2013-11-27 17:34 | 2013-11-27 18:40 | 66 | 11kV | 86516 | 1478 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S847 Hornsby Panel 36 tripped on Relays: B phase Earth Fault, Fault Check ans EFI Cause: UG Cable fault from S1992 Waitara Alexandra to S4383 Patterson Romsey to S4426 Park Alexandria 1048501 1048503 1048505 1047715 1047718 1047720 | November | 2013 | 2014Q2 | 2014 | ZN847:PA36 | ZN847:PA36 | ZN00847/000036 | HORNSBY | UG | Not Veg | 2013-11-27 | N | 58.5359 | N | 7 | N | N | 1.1101 | 39.4971 | 63223.341
[7 empty] | 16271 | 17664 | 1047758 | 2013-11-28 02:28 | 2013-11-28 03:34 | 66 | 11kV | 109296 | 1656 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.16194 Manly Hospital #1, Sw 'B" tripped on A and C phase OC. Field efi's down at S.16136 and S.16721. Dead possum found at UG/OH pole in Addison Rd west of Darley RD. | November | 2013 | 2014Q2 | 2014 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | OH | Not Veg | 2013-11-28 | N | 66 | N | 7 | N | N | 1.1101 | 39.4971 | 79870.2931
[7 empty] | 15692 | 10956 | 1047806 | 2013-11-28 08:10 | 2013-11-28 09:15 | 65 | 11kV | 260 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138351 A & B phase DOLF : 16 Amp Operator said the fuses blew while mine staff were attempting to start up some large electrical equipment but was unsure if this was just a coincidence. Excluded OMS 1047806 | November | 2013 | 2014Q2 | 2014 | 511:29872 | 511:29872 | ZN00511/029872 | MAITLAND | UG | Not Veg | 2013-11-28 | N | 65 | N | 7 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 16106 | 16044 | 1047997 | 2013-11-28 12:22 | 2013-11-28 13:37 | 75 | 11kV | 49500 | 660 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.3154 St Ives; Panel 12 Fdr CB tripped on C phase IOC and timed OC, timing and lockout. Field efi down at S.4112. Trees in vicinity of PT240 require trimming | November | 2013 | 2014Q2 | 2014 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2013-11-28 | N | 75 | N | 7 | N | N | 1.1101 | 39.4971 | 36173.14
[7 empty] | 15498 | 8429 | 1048140 | 2013-11-28 16:56 | 2013-11-28 17:02 | 6 | 11kV | 6366 | 1061 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | At S8000 Macquarie Park Panel 4 feeder tripped on SEF. At S35500 Top Ryde Panel 27 Tripped on SEF Arcing Horn remained closed at AB372 upon restoration ofi section of feedeer between CP372 to AB1901 to S2004 DAROS 327518) See OMS 1048140/144/147 | November | 2013 | 2014Q2 | 2014 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Not Veg | 2013-11-28 | N | 6 | N | 7 | N | N | 1.1101 | 39.4971 | 4652.085
[7 empty] | 15241 | 5544 | 1048124 | 2013-11-28 16:48 | 2013-11-28 17:20 | 31.7333 | 11kV | 1999.2 | 63 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12620 Noraville section of Pa10 "AB42638" @PT49312 Buff Pt Kobada 63K middle HDO fuse operated and opened Suspect Fuse Fatigue. 11kv HDO 63Amp cartridge See 1048128 exclude 1048124,32 | November | 2013 | 2014Q2 | 2014 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2013-11-28 | N | 31.7333 | N | 7 | N | N | 1.1101 | 39.4971 | 1460.9564
[7 empty] | 15437 | 7855 | 1048110 | 2013-11-28 16:57 | 2013-11-28 19:00 | 123 | 11kV | 246 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138362 B phase DOLF : 20 Amp Excluded OMS 1048110 | November | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-11-28 | N | 123 | N | 7 | N | N | 1.1101 | 39.4971 | 179.7695
[7 empty] | 15867 | 12840 | 1048184 | 2013-11-28 20:16 | 2013-11-29 00:45 | 269 | 11kV | 269 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138364 A phase DOLF : 10 Amp Excluded OMS 1048184 | November | 2013 | 2014Q2 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | UG | Not Veg | 2013-11-28 | N | 269 | N | 7 | N | N | 1.1101 | 39.4971 | 196.5773
[7 empty] | 15889 | 13043 | 1048200 | 2013-11-29 02:11 | 2013-11-29 02:56 | 45 | 11kV | 40770 | 906 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn80 Chatswood Pane;l 25 tripped and reclosed on Relays: A and C phase IOC and A and B phase O/C lockout and Timing. Cause: tree branch fell on OH mains O/S 72 Gordon St. See OMS 1048200 1048201 | November | 2013 | 2014Q2 | 2014 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Veg | 2013-11-29 | N | 45 | N | 5 | N | N | 1.1101 | 39.4971 | 29793.5135
[7 empty] | 16316 | 18153 | 1048210 | 2013-11-29 06:20 | 2013-11-29 09:40 | 200 | 11kV | 23600 | 118 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Rain Heavy | N | Ex Zn12630 section of Pa5 @RE46803 Wise Ferry Dog Trap 0.1 tripped on: C Phase to earth Phase protection trip @PT49111 Wise Ferry Dog trap 0.7 HDO's C phase 16Amp Dist 17a 5a 53 Amps 246v 249v 249v Suspect Tx @PT13865 Wise Ferry Dog trap C phase HDO 16Amp. Switching tag at PT isolated Cause: PT13865 Wise Ferry Dog trap HDO's failed to hold on restoration. Restored via LV// Links 17015 0942. See 1049391 exclude 1048210,21,52 | November | 2013 | 2014Q2 | 2014 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | UG | Not Veg | 2013-11-29 | N | 200 | N | 5 | N | N | 1.1101 | 39.4971 | 17246.1839
[7 empty] | 15705 | 11028 | 1048202 | 2013-11-29 02:47 | 2013-11-29 10:38 | 471 | 11kV | 29470 | 92 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 138365 3 fault operations Earth fault Wire off pin Excluded OMS 1048202 | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2013-11-29 | N | 320.3261 | N | 5 | N | N | 1.1101 | 39.4971 | 21535.8068
[7 empty] | 14948 | 2238 | 1048555 | 2013-11-29 15:20 | 2013-11-29 16:55 | 95 | 11kV | 24320 | 256 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 138374 REPLACE XARM POLE IU-10496 Excluded OMS 1048555 | November | 2013 | 2014Q2 | 2014 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2013-11-29 | N | 95 | N | 5 | N | N | 1.1101 | 39.4971 | 17772.3387
[7 empty] | 15858 | 12758 | 1048582 | 2013-11-29 16:00 | 2013-11-29 18:00 | 120 | 11kV | 120 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 138373 Repaired dropper to Transformer Excluded OMS 1048582 | November | 2013 | 2014Q2 | 2014 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2013-11-29 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 15895 | 13135 | 1048662 | 2013-11-30 02:25 | 2013-11-30 03:30 | 65 | 11kV | 23400 | 360 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 138377 3 fault operations B & C phase Earth fault; Overcurrent Possum found at ugoh JU-17068 | November | 2013 | 2014Q2 | 2014 | 210:8675 | 210:83472 | ZN00210/083472 | NEWCASTLE | OH | Not Veg | 2013-11-30 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 17100.0298
[7 empty] | 16453 | 19968 | 1048671 | 2013-11-30 06:51 | 2013-11-30 07:50 | 59 | 11kV | 885 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 138380 A phase DOLF : 16 Amp Excluded OMS 1048676 | November | 2013 | 2014Q2 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2013-11-30 | N | 59 | N | 6 | N | N | 1.1101 | 39.4971 | 646.7319
[7 empty] | 16066 | 15535 | 1048660 | 2013-11-30 01:08 | 2013-11-30 09:10 | 482 | 11kV | 1928 | 4 | HV | Animal Possum | Animal | Fuse | Unplanned | Rain Light | N | Zn14143 Somersby Pa17 "Somersby alls" @PT13459 Wise Ferry Howes 16amp HDO blown on foot path side Cause: Animals/Birds Possum found at base of PT13459 Wise Ferry Howes See 1049463 exclude 1048660 | November | 2013 | 2014Q2 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-11-30 | N | 482 | N | 6 | N | N | 1.1101 | 39.4971 | 1408.9255
[7 empty] | 16413 | 19332 | 1048656 | 2013-11-30 00:16 | 2013-11-30 10:05 | 589 | 11kV | 2356 | 4 | HV | Animal Possum | Animal | DC PT | Unplanned | Rain Light | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" @PT14603 Dog trap Beckford 0.6 16.5 Amp HDO blown on roadside Cause: Possum found at base of PT14603 Dog Trap Beckford 0.6 See 1049461 exclude 1048656,721 | November | 2013 | 2014Q2 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2013-11-30 | N | 589 | N | 6 | N | N | 1.1101 | 39.4971 | 1721.6953
[7 empty] | 15930 | 13425 | 1048690 | 2013-11-30 07:44 | 2013-11-30 10:10 | 146.0333 | 11kV | 1022.2333 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138383 A phase DOLF : 20 Amp | November | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2013-11-30 | N | 146.0333 | N | 6 | N | N | 1.1101 | 39.4971 | 747.018
[7 empty] | 15413 | 7573 | 1048668 | 2013-11-30 05:46 | 2013-11-30 14:00 | 494 | 11kV | 152748 | 902 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 10994 Mortdale - Pnl 19L - Trip/reclose/trip, C phase OC & EF, EFI, lockout, timing, Field EFIs. Suspect underground fault between S 10082, S 10207 and USL 30648. ME: 1049664. Rest Steps: 1049665, 6. Withdrawn: 1048668. | November | 2013 | 2014Q2 | 2014 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | UG | Not Veg | 2013-11-30 | N | 169.3437 | N | 6 | N | N | 1.1101 | 39.4971 | 111623.7331
[7 empty] | 16443 | 19893 | 1048826 | 2013-12-01 06:32 | 2013-12-01 07:45 | 73 | 11kV | 1241 | 17 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa10 @PT14424 South Tacoma Raymond 0.8 11kv 31.5 Amp Roadside Dropout fuse operated Cause: Fuse Fatigue See 1049472 exclude 1048826 | December | 2013 | 2014Q2 | 2014 | ZN14891:PA10 | ZN14891:PA10 | ZN14891/000010 | CENTRAL COAST | OH | Not Veg | 2013-12-01 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 906.8862
[7 empty] | 14934 | 2147 | 1048847 | 2013-12-01 08:45 | 2013-12-01 12:10 | 205 | 11kV | 820 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138391 C phase DOLF : 16 Amp Excluded OMS 1048847 | December | 2013 | 2014Q2 | 2014 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | UG | Not Veg | 2013-12-01 | N | 205 | N | 4 | N | N | 1.1101 | 39.4971 | 599.2318
[7 empty] | 15636 | 10142 | 1048928 | 2013-12-01 19:50 | 2013-12-01 20:26 | 36 | 11kV | 57456 | 1596 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S80 Chatswood Panel 37 Tripped on Relays: A and C phase O/C and EFi Signals: 11kV Trip Cause: Bird flew into mains. See OMS 1048917 1048928 1048931 | December | 2013 | 2014Q2 | 2014 | ZN80:PA37 | ZN80:PA37 | ZN00080/000037 | LANE COVE | OH | Not Veg | 2013-12-01 | N | 36 | N | 4 | N | N | 1.1101 | 39.4971 | 41987.1501
[7 empty] | 15045 | 3152 | 1048929 | 2013-12-01 20:16 | 2013-12-01 20:55 | 39 | 11kV | 3469.5 | 91 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | tHE FOOTPATH AND ROADSIDE PHASE FUSE ASSEMBLY FRACTURED | December | 2013 | 2014Q2 | 2014 | ZN15002:PA4 | ZN15002:PA4 | ZN15002/000004 | NORTHERN BEACHES | OH | Not Veg | 2013-12-01 | N | 38.1264 | N | 4 | N | N | 1.1101 | 39.4971 | 2535.4083
[7 empty] | 15023 | 3007 | 1049298 | 2013-12-02 17:21 | 2013-12-02 18:25 | 64 | 11kV | 256 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138407 C phase DOLF : 10 Amp Excluded OMS 1049298 | December | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2013-12-02 | N | 64 | N | 2 | N | N | 1.1101 | 39.4971 | 187.0772
[7 empty] | 15533 | 8841 | 1049342 | 2013-12-03 03:09 | 2013-12-03 04:33 | 84 | 11kV | 43511 | 638 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9900 Menai - Pnl 2 - Earth Fault, EFI, Fault Check, Field EFIs. 11kV feeder fault from S 9024 to S 9175. Defective EFI at S 9024. Panel 19 tripped while trying to restore Pnl 2. ME: 1049950. Rest Step: 1049951. Withdrawn: 1049342. | December | 2013 | 2014Q2 | 2014 | ZN9900:PA2 | ZN9900:PA2 | ZN09900/000002 | SUTHERLAND | UG | Not Veg | 2013-12-03 | N | 68.1991 | N | 3 | N | N | 1.1101 | 39.4971 | 31796.5554
[7 empty] | 16116 | 16115 | 1049708 | 2013-12-03 16:22 | 2013-12-03 18:04 | 102 | 11kV | 77668 | 790 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138423 Earth fault Reclose Function Off on Fdr 2120 for planned outage. Excluded OMS # 1049708 | December | 2013 | 2014Q2 | 2014 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Veg | 2013-12-03 | N | 98.3139 | N | 3 | N | N | 1.1101 | 39.4971 | 56757.4836
[7 empty] | 15827 | 12417 | 1048945 | 2013-12-02 05:42 | 2013-12-03 20:30 | 2328 | 11kV | 778400 | 350 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Beyond CP.24701 Scotland Island (Sw 6000) tripped on C phase 90Amp HV fuse efi. Section of UG cable failed between CP.24701 and S.16614 tee S.16615 refer to 1051679, 1051681, 1051682, 1051683 and 1051684 | December | 2013 | 2014Q2 | 2014 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2013-12-02 | N | 2224 | N | 2 | N | N | 1.1101 | 39.4971 | 568831.7611
[7 empty] | 16261 | 17559 | 1049775 | 2013-12-03 23:43 | 2013-12-04 03:10 | 207 | 11kV | 217554 | 1597 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.15014 Mona Vale, Panel 5 Fdr CB tripped on A & C phase OC, efi, Earth Fault, EF check, 11kV trip, Zone Earth. Field efi's down at S.16608, S.49874, S.15389, S.15186, S.16739, S.16942, S.16410, S.16847, S.16956, S.16957, and S.49907. UG/OH damaged to S.16413 due to possum | December | 2013 | 2014Q2 | 2014 | ZN15014:PA5 | ZN15014:PA5 | ZN15014/000005 | NORTHERN BEACHES | OH | Not Veg | 2013-12-03 | N | 136.2267 | N | 3 | N | N | 1.1101 | 39.4971 | 158982.0464
[7 empty] | 16055 | 15462 | 1049777 | 2013-12-04 01:09 | 2013-12-04 03:30 | 141 | 11kV | 199582 | 1736 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Unselected | N | At S.15008 Harbord, Panel 10 Fdr CB tripped, reclosed and locked out on B and C phase OC, timer and lockout relays. No field efi's operated. | December | 2013 | 2014Q2 | 2014 | ZN15008:PA10 | ZN15008:PA10 | ZN15008/000010 | NORTHERN BEACHES | OH | Veg | 2013-12-04 | N | 114.9666 | N | 4 | N | N | 1.1101 | 39.4971 | 145848.6389
[7 empty] | 14933 | 2143 | 1050020 | 2013-12-04 12:06 | 2013-12-04 13:40 | 94 | 11kV | 53866 | 1426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138441 1 fault operation Sensitive Earth Fault; Overcurrent Excluded OMS 1050020 | December | 2013 | 2014Q2 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2013-12-04 | N | 37.7742 | N | 4 | N | N | 1.1101 | 39.4971 | 39363.684
[7 empty] | 16281 | 17823 | 1050265 | 2013-12-04 20:47 | 2013-12-04 23:40 | 173 | 11kV | 1903 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1752 Quarry Eloura Reserve Fuse fatigue See OMS 1052111 1050265 1050266 1050267 | December | 2013 | 2014Q2 | 2014 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2013-12-04 | N | 173 | N | 4 | N | N | 1.1101 | 39.4971 | 1390.6563
[7 empty] | 15688 | 10912 | 1050246 | 2013-12-04 19:37 | 2013-12-05 00:50 | 313 | 11kV | 121590 | 1144 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 138446 2 fault operations A & B phase Overcurrent Car hit pole HS-72458 - Mulbring st x Pokolbin st Kurri ,Broken x-arm. Excluded Oms report no 1050264. | December | 2013 | 2014Q2 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2013-12-04 | N | 106.285 | N | 4 | N | N | 1.1101 | 39.4971 | 88854.3857
[7 empty] | 15081 | 3503 | 1050288 | 2013-12-05 04:01 | 2013-12-05 06:50 | 169 | 11kV | 4225 | 25 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | Y | Ex Zn12650 West Gosford section of Pa6L @PT12037 Manns Dell Raodside phase 50A HDO fuse operated Fuse Fatigue ABB 0237 Batch See 1051857 exclude 1050288 | December | 2013 | 2014Q2 | 2014 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2013-12-05 | Y | 169 | N | 9 | N | Y | 1.1101 | 39.4971 | 3087.5054
[7 empty] | 15127 | 3969 | 1050295 | 2013-12-05 06:27 | 2013-12-05 08:15 | 108 | 11kV | 108 | 1 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | Y | LID 138452 10A DOLF tripped due to possum | December | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2013-12-05 | N | 108 | N | 9 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 15484 | 8264 | 1052642 | 2013-12-05 08:22 | 2013-12-05 08:43 | 21 | 11kV | 798 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | LID 138455/02 1 Fault operation 3 phase Overcurrent During SI 36988 Sw 42148 opened at 0822hrs. Same time as 33kV Sw 32038 Tripped & Reclosed. See OMS 1052639 | December | 2013 | 2014Q2 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Veg | 2013-12-05 | N | 21 | N | 9 | N | N | 1.1101 | 39.4971 | 583.1549
[7 empty] | 15685 | 10855 | 1051165 | 2013-12-05 15:55 | 2013-12-05 16:07 | 12 | 11kV | 7716 | 643 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | DNMS load trend shows no load at CP50407 @ 15:17 3rd Zn12570 Avoca Pa33 tripped 1st 1052662 2nd 1052664 3rd 1052666,8,70 Exclude 1050758,801,1091,111,65 | December | 2013 | 2014Q2 | 2014 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 12 | N | 9 | N | Y | 1.1101 | 39.4971 | 5638.6252
[7 empty] | 16380 | 18879 | 1050976 | 2013-12-05 15:44 | 2013-12-05 17:35 | 111 | 11kV | 9657 | 87 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind | Y | LID 138469 3 phase ABS 40037 FOUND OPEN (NO LOCK AT SITE) Excluded OMS 1050951 | December | 2013 | 2014Q2 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2013-12-05 | N | 111 | N | 9 | N | N | 1.1101 | 39.4971 | 7057.0508
[7 empty] | 14881 | 1760 | 1050646 | 2013-12-05 14:37 | 2013-12-05 17:35 | 178 | 11kV | 33412 | 194 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | Ex Zn12630 Peats Ridge section of Pa2 RE45013 Gunderman tripped and locked out Cause: weather related. WInd Storm See 1051932,4,5 Exclude 1050646 | December | 2013 | 2014Q2 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 172.2268 | N | 9 | N | Y | 1.1101 | 39.4971 | 24416.5041
[7 empty] | 15818 | 12294 | 1050907 | 2013-12-05 15:27 | 2013-12-05 17:38 | 131 | 11kV | 8562 | 222 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 138478 1 fault operation Earth fault Tree into OHM at pole SI 90484 Excluded OMS 1050884 & 1051233 | December | 2013 | 2014Q2 | 2014 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2013-12-05 | Y | 38.5676 | N | 9 | N | Y | 1.1101 | 39.4971 | 6256.8571
[7 empty] | 15832 | 12466 | 1050743 | 2013-12-05 15:08 | 2013-12-05 18:10 | 182 | 11kV | 209116 | 1223 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | ZN 9700 Kirrawee - Pnl 15 - Trip/reclose/trip, A & C phase IOC, A phase timed OC. Tree branch on 11kV OH in Serpentine St near Gore St. ME: 1053760. Rest Step: 1053761. Withdrawn: 1050743. | December | 2013 | 2014Q2 | 2014 | ZN9700:PA15 | ZN9700:PA15 | ZN09700/000015 | SUTHERLAND | OH | Veg | 2013-12-05 | N | 170.9861 | N | 9 | N | N | 1.1101 | 39.4971 | 152815.8049
[7 empty] | 14782 | 767 | 1050908 | 2013-12-05 15:46 | 2013-12-05 18:20 | 154 | 11kV | 462 | 3 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Bond | Unplanned | Wind | Y | LID 138477 Live line lead hanging - during strong winds. Live line clamp repaired | December | 2013 | 2014Q2 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2013-12-05 | Y | 154 | N | 9 | N | Y | 1.1101 | 39.4971 | 337.616
[7 empty] | 14983 | 2667 | 1050749 | 2013-12-05 15:51 | 2013-12-05 18:25 | 154 | 11kV | 23458 | 227 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Tree brought down 11kV OH in Chareroi RD | December | 2013 | 2014Q2 | 2014 | ZN15005:PA12 | ZN15005:PA12 | ZN15005/000012 | NORTHERN BEACHES | OH | Veg | 2013-12-05 | N | 103.3392 | N | 9 | N | N | 1.1101 | 39.4971 | 17142.4145
[7 empty] | 16482 | 20272 | 1053167 | 2013-12-05 15:15 | 2013-12-05 18:27 | 192 | 11kV | 106469 | 1108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Wind Strong | Y | ZN 10994 Mortdale - Pnl 10L - Trip/reclose/trip, B & C phase timed OC, timing, Lockout. Tree branch on 11kV OH near PT 10408 Forest River. Secondary Event HV bond off below AB 31019. ME: 1053167. Rest Step: 1053170. Withdrawn: 1050757. | December | 2013 | 2014Q2 | 2014 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2013-12-05 | N | 96.0912 | N | 9 | N | N | 1.1101 | 39.4971 | 77804.4049
[7 empty] | 15167 | 4270 | 1050768 | 2013-12-05 15:11 | 2013-12-05 18:40 | 209 | 11kV | 33123 | 1507 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | Wind Strong | Y | ZN 10991 Blakehurst - Pnl 1 - Trip/reclose, C phase Timed OC. Severe Wind. Suspect tree branch on mains. 11kV bond burnt off due to fault beyond bond as secondary event. ME: 1053159. Secondary: 1053160. Withdrawn: 1050768, 982. | December | 2013 | 2014Q2 | 2014 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Veg | 2013-12-05 | N | 21.9794 | N | 9 | N | N | 1.1101 | 39.4971 | 24205.3114
[7 empty] | 15272 | 6034 | 1050801 | 2013-12-05 16:07 | 2013-12-05 18:43 | 156 | 11kV | 207941 | 1580 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Zn12570 Avoca zone VCB Pa33 "McMasters Beach" fdr tripped on: Relays: SEl EFI's: nil Signals: 11kv trip Cause: weather related. DOp patrolled nothing found 1st 1052662 2nd 1052664 3rd 1052666,8,70 Exclude 1050758,801,1091,111,65 | December | 2013 | 2014Q2 | 2014 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 131.6082 | N | 9 | N | Y | 1.1101 | 39.4971 | 151957.1496
[7 empty] | 14892 | 1872 | 1051321 | 2013-12-05 17:13 | 2013-12-05 19:11 | 118 | 11kV | 68983 | 781 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 138480 1 fault operation B & C phase Sensitive Earth Fault; Earth fault; Overcurrent Excluded 1051321 | December | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-12-05 | Y | 88.3265 | N | 9 | N | Y | 1.1101 | 39.4971 | 50410.7417
[7 empty] | 15291 | 6342 | 1051124 | 2013-12-05 16:20 | 2013-12-05 19:48 | 208 | 11kV | 22751 | 149 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 138468 3 fault operations Tree brought down mains between poles MG-97045 & MG-97046. Excluded OMS 1051124 | December | 2013 | 2014Q2 | 2014 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2013-12-05 | Y | 152.6913 | N | 9 | N | Y | 1.1101 | 39.4971 | 16625.7598
[7 empty] | 16305 | 18064 | 1051137 | 2013-12-05 17:17 | 2013-12-05 19:52 | 155 | 11kV | 74565 | 489 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Zn14891 wYONG 11KV vcb PA20 "wARNERVALE wEST rAILWAY" FDR TRIPPED rELAYS: BASSLER 51 A+B phase EFI's: nil SIgnals: 11kv trip Cause: tree found on ground DU414 mountain rd beyond PT11897 See 1052846,8 exclude 1051332 | December | 2013 | 2014Q2 | 2014 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 152.4847 | N | 9 | N | Y | 1.1101 | 39.4971 | 54489.9027
[7 empty] | 16393 | 19069 | 1050649 | 2013-12-05 14:55 | 2013-12-05 19:56 | 301 | 11kV | 187228 | 1258 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | Y | At S965 Pennant hills panel 15 tripped reclosed trip[edd and locked out on A phase Time Overcurrent +A phase IOC Cause: 11kV down outside Cheltenham Railstation an sutherland Rd. See OMS 1055656 1055660 1055661 1055659 1050678 1050686/726/825/399 NOTE: Based on customer calls suspect PT2383 was in parallel with Pa15 at the time of interruption | December | 2013 | 2014Q2 | 2014 | ZN965:PA15 | ZN965:PA15 | ZN00965/000015 | HORNSBY | OH | Not Veg | 2013-12-05 | Y | 148.8299 | N | 9 | N | Y | 1.1101 | 39.4971 | 136820.7001
[7 empty] | 15248 | 5637 | 1050842 | 2013-12-05 15:27 | 2013-12-05 20:30 | 303 | 11kV | 217657 | 885 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | Y | At Zn1673, 11kV Pnl 13 "King Eastern" feeder tripped on A phase IOC. Field efi's: Pnl 13 to S4715. Tree branch contact. Hv welded together at 33 Holt Ave. Mains isolated. | December | 2013 | 2014Q2 | 2014 | ZN1673:PA13 | ZN1673:PA13 | ZN01673/000013 | KU-RING-GAI | OH | Veg | 2013-12-05 | N | 245.9401 | N | 9 | N | N | 1.1101 | 39.4971 | 159057.3158
[7 empty] | 14842 | 1310 | 1051209 | 2013-12-05 16:37 | 2013-12-05 21:23 | 286 | 11kV | 6292 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 138475 2 fault operations 11KV MAINS ON GROUND AT POLE GU-24364. Excluded OMS REPORT NO 1051209. | December | 2013 | 2014Q2 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-12-05 | Y | 286 | N | 9 | N | Y | 1.1101 | 39.4971 | 4598.008
[7 empty] | 16337 | 18379 | 1051217 | 2013-12-05 16:38 | 2013-12-05 21:40 | 302 | 11kV | 62130 | 645 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Wind | Y | LID 138479 2 fault operations A & C phase Overcurrent Roof from adjacent temp building blown onto OHM Excluded OMS 1051217 | December | 2013 | 2014Q2 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2013-12-05 | Y | 96.3256 | N | 9 | N | Y | 1.1101 | 39.4971 | 45402.7715
[7 empty] | 15650 | 10451 | 1051540 | 2013-12-05 19:25 | 2013-12-05 22:06 | 161 | 11kV | 84893 | 781 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 138481 1 fault operation B & C phase Sensitive Earth Fault; Earth fault; Overcurrent Excluded 1051540 | December | 2013 | 2014Q2 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2013-12-05 | Y | 108.6978 | N | 9 | N | Y | 1.1101 | 39.4971 | 62037.3005
[7 empty] | 16148 | 16468 | 1051166 | 2013-12-05 16:30 | 2013-12-05 22:26 | 356 | 11kV | 267997 | 1244 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 138472 2 fault operations B phase Earth fault 11KV MAIN DOWN AT POLE FS 92760.11KV INTO L/VOLTAGE. Excluded OMS REPORT NO 1051176. | December | 2013 | 2014Q2 | 2014 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2013-12-05 | Y | 215.4317 | N | 9 | N | Y | 1.1101 | 39.4971 | 195844.303
[7 empty] | 15164 | 4244 | 1051031 | 2013-12-05 16:00 | 2013-12-05 22:40 | 400 | 11kV | 9491 | 50 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Ex Zn12650 sectin of Pa1 "Dog trap rd" fdr @RE44603 Footes Rd tripped and locked out Cause: Tree/Branch brought down OH. Between Links 44332 to AB42214 See 1051980,2 exclude 1051031 | December | 2013 | 2014Q2 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 189.82 | N | 9 | N | Y | 1.1101 | 39.4971 | 6935.7429
[7 empty] | 15798 | 12108 | 1050680 | 2013-12-05 14:57 | 2013-12-05 23:05 | 488 | 11kV | 90885 | 623 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Zn14891 Wyong Zone section of Pa12 "cedar northcot" fdr tripped @IR48813 Yarramalong Boyds 3.7 (no scada) ABNORMAL: section of 11kv fdr isolated for work from AB43957 to AB43601 peats ridge 1C* with LB45195 closed Cause: tree/branch brought down OH. Reww near PT11058 FInns Springs See 1052717,21 Exclude 1050667,80,98,1182 | December | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 145.8828 | N | 9 | N | Y | 1.1101 | 39.4971 | 66416.0773
[7 empty] | 15845 | 12635 | 1051548 | 2013-12-05 18:09 | 2013-12-05 23:20 | 311 | 11kV | 33277 | 107 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | Y | LID 138484 1 fault operation B & C phase Earth fault Broken pole HS 82569 Buchanan Rd Excluded OMS 1051602 | December | 2013 | 2014Q2 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2013-12-05 | Y | 311 | N | 9 | N | Y | 1.1101 | 39.4971 | 24317.8501
[7 empty] | 15777 | 11885 | 1050912 | 2013-12-05 15:46 | 2013-12-05 23:30 | 464 | 11kV | 39440 | 85 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | Section of Panel 2 Galston High School feeder B phase Live line connector burnt off above PT2118 Carters Hunt Cause: Lineworker assisted and restored supply. See OMS 1050912 1053842 | December | 2013 | 2014Q2 | 2014 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Not Veg | 2013-12-05 | Y | 464 | N | 9 | N | Y | 1.1101 | 39.4971 | 28821.5887
[7 empty] | 15850 | 12680 | 1051418 | 2013-12-05 17:51 | 2013-12-05 23:38 | 347 | 11kV | 38373 | 751 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 138471 No protection operation, Fdr isolated because tree on main at pole VP-20742. Excluded OMS 1051418 | December | 2013 | 2014Q2 | 2014 | 243:80084 | 243:80084 | ZN00243/080084 | LAKE MACQUARIE | OH | Not Veg | 2013-12-05 | Y | 51.0959 | N | 9 | N | Y | 1.1101 | 39.4971 | 28041.8566
[7 empty] | 14783 | 768 | 1051142 | 2013-12-05 16:28 | 2013-12-06 00:47 | 499 | 11kV | 88445 | 344 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | Y | LID 138470 2 fault operations A phase Earth Fault; Overcurrent A phase O/C & E/F, Timed O/C & Timed E/F. Tree branch damage HV xarms at & near sub 14305. Excluded OMS 1051142 | December | 2013 | 2014Q2 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2013-12-05 | Y | 257.1076 | N | 9 | N | Y | 1.1101 | 39.4971 | 64632.9973
[7 empty] | 15749 | 11637 | 1051159 | 2013-12-05 16:31 | 2013-12-06 00:53 | 502 | 11kV | 237696 | 1151 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 138473 2 fault operations B & C phase Overcurrent TREE ON POLE GT-14294 ELLALONG ST KEARSLEY. Excluded OMS REPORT NO 1051159. | December | 2013 | 2014Q2 | 2014 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2013-12-05 | Y | 206.5126 | N | 9 | N | Y | 1.1101 | 39.4971 | 173701.226
[7 empty] | 15143 | 4082 | 1050921 | 2013-12-05 16:00 | 2013-12-06 01:50 | 590 | 11kV | 45350 | 790 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | Y | LID 138467 No protection operation Fdr off loaded due to pole IU-20097 falling over. Excluded OMS 1050921 | December | 2013 | 2014Q2 | 2014 | 216:10728 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Not Veg | 2013-12-05 | Y | 57.4051 | N | 9 | N | Y | 1.1101 | 39.4971 | 33140.4424
[7 empty] | 14717 | 172 | 1051133 | 2013-12-05 16:24 | 2013-12-06 02:59 | 635 | 11kV | 89614 | 1294 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 138474 TREE FLATTENED 4 SPAN OFF 11KV MAINS AND TX 888. Excluded OMS 1051133. | December | 2013 | 2014Q2 | 2014 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Veg | 2013-12-05 | Y | 69.2535 | N | 9 | N | Y | 1.1101 | 39.4971 | 65487.268
[7 empty] | 14729 | 289 | 1051613 | 2013-12-05 23:00 | 2013-12-06 03:00 | 240 | 11kV | 8880 | 37 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | Y | LID 148804 no protection operation section isolated for emergency repairs at ABS 16214 Excluded OMS 1051613 | December | 2013 | 2014Q2 | 2014 | 229:34983 | 233:82818 | ZN00233/082818 | PORT STEPHENS | OH | Not Veg | 2013-12-05 | N | 240 | N | 9 | N | N | 1.1101 | 39.4971 | 6489.2421
[7 empty] | 15094 | 3623 | 1051641 | 2013-12-06 04:16 | 2013-12-06 05:40 | 84 | 11kV | 110460 | 1315 | HV | Animal Possum | Animal | UGOH | Unplanned | Previous Storm | N | At Zn116 Leichhardt, 11kv Pnl1 #44 "Carlisle and Leichhardt aux" feeder tripped on E/F and C phase overcurrent. Signals: 11kv trip and efi Field EFI's: Pnl44R to Sub 1540 Remarks: animals/birds. Possum on ugoh in Moodie street | December | 2013 | 2014Q2 | 2014 | ZN116:PA44 | ZN116:PA31 | ZN00116/000031 | INNER WEST | OH | Not Veg | 2013-12-06 | N | 84 | N | 10 | N | N | 1.1101 | 39.4971 | 80720.91
[7 empty] | 15239 | 5518 | 1051645 | 2013-12-06 05:06 | 2013-12-06 06:15 | 69 | 11kV | 1311 | 19 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Ex Zn12660 Woy Woy section of Pa10R "Ocean Breach rd" PT13428 Parkes Bay Brisbane rodaside phase 16A hDO fuse operated due to possum also refer to 1051645 | December | 2013 | 2014Q2 | 2014 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | OH | Not Veg | 2013-12-06 | N | 69 | N | 10 | N | N | 1.1101 | 39.4971 | 958.0401
[7 empty] | 15695 | 10980 | 1051659 | 2013-12-06 06:18 | 2013-12-06 09:00 | 162 | 11kV | 11016 | 68 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 138487 2 fault operations Overcurrent Hot air balloon contacted mains at pole DR-70243, off Wollombi Rd South of Singleton St, Broke. Excluded OMS 1051659 and 1051660. | December | 2013 | 2014Q2 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-12-06 | N | 162 | N | 10 | N | N | 1.1101 | 39.4971 | 8050.1679
[7 empty] | 15665 | 10636 | 1051699 | 2013-12-06 07:48 | 2013-12-06 09:45 | 117 | 11kV | 208429 | 1881 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1610 Homebush Bay Panel 13 'Holker Jamieson No.2" feeder has tripped. Relays: B phase and Neutral Inst and OC Signals: 11kv trip EFIs: S7637, 4595, 4596, 4817 Remarks: UG fault. Suspected UG fault between Sw/B @ Sub 4817 Newington Nurmi and Sw/A @ Sub 4818 Ali Newington | December | 2013 | 2014Q2 | 2014 | ZN1610:PA13 | ZN1610:PA13 | ZN01610/000013 | PARRAMATTA | UG | Not Veg | 2013-12-06 | N | 110.8075 | N | 10 | N | N | 1.1101 | 39.4971 | 152313.7656
[7 empty] | 16473 | 20176 | 1051709 | 2013-12-06 08:13 | 2013-12-06 10:15 | 122 | 11kV | 442.75 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138491 C phase DOLF : 10 Amp Excluded OMS 1051709 | December | 2013 | 2014Q2 | 2014 | 238:34141 | 264:81240 | ZN00264/081240 | MAITLAND | UG | Not Veg | 2013-12-06 | N | 110.6875 | N | 10 | N | N | 1.1101 | 39.4971 | 323.5486
[7 empty] | 14985 | 2673 | 1051096 | 2013-12-05 16:23 | 2013-12-06 11:40 | 1157 | 11kV | 43393 | 139 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 138500 1 fault operation Sensitive Earth FAult Tree into mains beyond Links 2389 Excluded OMS 1051096 | December | 2013 | 2014Q2 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2013-12-05 | Y | 312.1799 | N | 9 | N | Y | 1.1101 | 39.4971 | 31710.3245
[7 empty] | 15257 | 5777 | 1051828 | 2013-12-06 10:25 | 2013-12-06 12:30 | 125 | 11kV | 16873 | 539 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 138495 Pollice report car hit pole FT-33121. Crossarm broken, OHM on pole Fdr 48031 de-energised as pole was alive (240V). Excluded OMS No. 1051828 | December | 2013 | 2014Q2 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-12-06 | N | 31.3043 | N | 10 | N | N | 1.1101 | 39.4971 | 12330.2907
[7 empty] | 15168 | 4276 | 1051110 | 2013-12-05 16:10 | 2013-12-06 13:40 | 1290 | 11kV | 42703 | 94 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Ez Zn12630 Peats Ridge section of Pa1 "Grants Rd" fdr @RE61364 Brieses Peats 0.4 tripped on SEF, O/C trip Cause: Tree brought down 11kv O?H near LB61387 See 1052826,30,1 Exclude 1051052,110 | December | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2013-12-05 | Y | 454.2872 | N | 9 | N | Y | 1.1101 | 39.4971 | 31206.0929
[7 empty] | 16247 | 17513 | 1052058 | 2013-12-06 13:36 | 2013-12-06 14:41 | 65 | 11kV | 89925 | 1476 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Zn14891 Wyong Pa5 tripped on SEL Air Break Switch footpath contact high resistance See 1052914,5 LV// 1052930 Exclude 1052058,61,109 | December | 2013 | 2014Q2 | 2014 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2013-12-06 | N | 60.9248 | N | 10 | N | N | 1.1101 | 39.4971 | 65714.5377
[7 empty] | 15222 | 4983 | 1051538 | 2013-12-05 15:25 | 2013-12-06 17:05 | 1540 | 11kV | 25775 | 17 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Section of panel 8 Galston Picnic reserve feeder at S35370 Galston Recloser 560 Tripped Cause: Tree branch on OH mains - Cause Tree removed from 11kV CCT See OMS 1055692 1055694 1055695 1055704 1055699 1051550 1051538 1051577 1051580 | December | 2013 | 2014Q2 | 2014 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2013-12-05 | Y | 1516.1765 | N | 9 | N | Y | 1.1101 | 39.4971 | 18835.6098
[7 empty] | 16221 | 17288 | 1053132 | 2013-12-06 15:35 | 2013-12-06 18:36 | 181 | 11kV | 113668 | 628 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.1788 Matraville Pnl.8 tripped on : C phase timed and EFI Field EFIs: S35502 7934 1170 note: 807 EFI did not work Abnormal: S1146 Sw B CLOSED Sw A OPEN - S2640 Sw B CLOSED - S1345 Sw A OPEN (for previous UG cable fault) Section of feeder from S35502 to S1345 tee S1146 was defective and on the DMA ready for service with D/R # 328900. When DOp closed Sw B @ S35502 feeder failed 30 seconds later. | December | 2013 | 2014Q2 | 2014 | ZN1788:PA8 | ZN1788:PA61 | ZN01788/000061 | RANDWICK | UG | Not Veg | 2013-12-06 | N | 181 | N | 10 | N | N | 1.1101 | 39.4971 | 83065.2218
[7 empty] | 15601 | 9602 | 1052226 | 2013-12-06 20:13 | 2013-12-06 22:40 | 147 | 11kV | 294 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138505 Single phase DOLF : 10 Amp Excluded OMS 1052226 | December | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2013-12-06 | N | 147 | N | 10 | N | N | 1.1101 | 39.4971 | 214.8465
[7 empty] | 14864 | 1567 | 1052243 | 2013-12-06 23:19 | 2013-12-07 01:15 | 116 | 11kV | 6380 | 55 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 138506/02 B phase DOLF : 31 Amp Possum at LF 13263 Excluded OMS 1052243 | December | 2013 | 2014Q2 | 2014 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2013-12-06 | N | 116 | N | 10 | N | N | 1.1101 | 39.4971 | 4662.3158
[7 empty] | 15362 | 6962 | 1052286 | 2013-12-07 09:26 | 2013-12-07 11:12 | 106 | 11kV | 186978 | 1842 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12610 Long Jetty Pa10 "Wamberal" fdr tripped, reclosed, tripped & locked out on Relays: Aphase O/C, IOC, EFI Signals: 11kv trip EFI's: Nil Cause: 11kv UG frontline feeder fault from Zn12610 Long Jetty Pa10 to LB45183 See 1052976,7 Exclude 1052286,92 | December | 2013 | 2014Q2 | 2014 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | UG | Not Veg | 2013-12-07 | N | 101.5081 | N | 2 | N | N | 1.1101 | 39.4971 | 136638.0075
[7 empty] | 16190 | 16965 | 1052344 | 2013-12-07 16:41 | 2013-12-07 18:16 | 95 | 11kV | 49780 | 524 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S35370 Galston Panel 10 tripped reclosed tripped and locked out Cause: Tree on Tee Off to PT2103 - Branch on 11kV OH See OMS 1054017 1052344 1052362 1052363 | December | 2013 | 2014Q2 | 2014 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2013-12-07 | N | 95 | N | 2 | N | N | 1.1101 | 39.4971 | 36377.7557
[7 empty] | 16174 | 16750 | 1052410 | 2013-12-08 05:37 | 2013-12-08 06:41 | 64 | 11kV | 41344 | 646 | HV | Vegetation Blow/Fall In | Vegetation | Air Break Switch | Unplanned | Unselected | N | Zn12600 Lisarow Pa1 "Dog trap Gully" fdr tripped on: Relays: B&Cphase IOC, Timing & Lockout relays Signals: 11kv trip EFI's: Nil ABNORMAL: S14059/SwD closed LK41285 opened Cause: Tree bark on LK44092 Pa1 did not reclose as CB shot through See 1053001 exclude 1052410 | December | 2013 | 2014Q2 | 2014 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2013-12-08 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 30212.9758
[7 empty] | 15699 | 10994 | 1052491 | 2013-12-08 16:34 | 2013-12-08 18:20 | 106 | 11kV | 954 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138520 C phase Fuse switch : 80 Amp (oli filled) Excluded OMS 1052491 & 1052492 | December | 2013 | 2014Q2 | 2014 | 208:56 | 257:81997 | ZN00257/081997 | NEWCASTLE | UG | Not Veg | 2013-12-08 | N | 106 | N | 4 | N | N | 1.1101 | 39.4971 | 697.1551
[7 empty] | 15607 | 9702 | 1052526 | 2013-12-08 22:59 | 2013-12-08 23:50 | 51 | 11kV | 2091 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138524 A phase DOLF : 31 Amp Excluded OMS 1052526 , 1052527 & 1052529 | December | 2013 | 2014Q2 | 2014 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | UG | Not Veg | 2013-12-08 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 1528.0411
[7 empty] | 15475 | 8186 | 1052528 | 2013-12-08 23:01 | 2013-12-09 01:26 | 145 | 11kV | 3770 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138525 A & B phase DOLF : 10 Amp Excluded OMS 1052528 | December | 2013 | 2014Q2 | 2014 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2013-12-08 | N | 145 | N | 4 | N | N | 1.1101 | 39.4971 | 2755.0048
[7 empty] | 15075 | 3435 | 1052546 | 2013-12-09 07:12 | 2013-12-09 08:30 | 78 | 11kV | 1014 | 13 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | Unselected | N | LID 138527 A phase DOLF : 31 Amp 3.15 fuse elements installed previous day Excluded oms # 1052546 | December | 2013 | 2014Q2 | 2014 | 203:8086 | 204:82697 | ZN00204/082697 | NEWCASTLE | OH | Not Veg | 2013-12-09 | N | 78 | N | 7 | N | N | 1.1101 | 39.4971 | 741.0013
[7 empty] | 15060 | 3315 | 1052538 | 2013-12-09 06:28 | 2013-12-09 08:48 | 140 | 11kV | 11678 | 150 | HV | Animal Bird | Animal | Insulator | Unplanned | Unselected | N | LID 138526 Earth fault; Overcurrent Wire off pin insulator & 2 dead Magpies. Excluded OMS # 1052538 | December | 2013 | 2014Q2 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2013-12-09 | N | 77.8533 | N | 7 | N | N | 1.1101 | 39.4971 | 8533.938
[7 empty] | 15623 | 9982 | 1052598 | 2013-12-09 09:04 | 2013-12-09 10:10 | 66 | 11kV | 58003 | 913 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 6 - A phase IOC and Timed OC, EL, EFI, FC. Suspect UG fault between Pnl 6 @ Campsie and S 3030. (Note Hazemeyer RMI). ME: 1053824. Rest Step: 1053825. Withdrawn: 1052598. | December | 2013 | 2014Q2 | 2014 | ZN690:PA6 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-12-09 | N | 63.5301 | N | 7 | N | N | 1.1101 | 39.4971 | 42386.8816
[7 empty] | 16362 | 18670 | 1052798 | 2013-12-09 12:52 | 2013-12-09 13:53 | 61 | 11kV | 33611 | 551 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | AT UNDERSLUNG LINK 23523 THE CENTRE PHASE LINK BURNT | December | 2013 | 2014Q2 | 2014 | ZN15014:PA19 | ZN15014:PA19 | ZN15014/000019 | NORTHERN BEACHES | OH | Not Veg | 2013-12-09 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 24561.9274
[7 empty] | 15951 | 13699 | 1052775 | 2013-12-09 12:10 | 2013-12-09 14:45 | 155 | 11kV | 16190 | 203 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 138534 Car hit pole. No Protection Operation LV ABC Stripped on S. 27696. Repaired after HV put back into service. Excluded OMS # 1052775 | December | 2013 | 2014Q2 | 2014 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | OH | Not Veg | 2013-12-09 | N | 79.7537 | N | 7 | N | N | 1.1101 | 39.4971 | 11831.1745
[7 empty] | 15532 | 8823 | 1052645 | 2013-12-09 16:20 | 2013-12-09 18:00 | 100 | 11kV | 600 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 138536 Stay wire leaning on 11Kv dropper | December | 2013 | 2014Q2 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2013-12-09 | N | 100 | N | 7 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 14789 | 869 | 1053106 | 2013-12-09 21:24 | 2013-12-09 22:25 | 61 | 11kV | 8174 | 134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138538 B Phase DOLF : 20 Amp Excluded OMS 1053106, 1053110, 1053112 & 1053113 | December | 2013 | 2014Q2 | 2014 | 202:34260 | 202:34260 | ZN00202/034260 | NEWCASTLE | UG | Not Veg | 2013-12-09 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 5973.3181
[7 empty] | 15840 | 12535 | 1053115 | 2013-12-10 00:43 | 2013-12-10 07:00 | 377 | 11kV | 8356 | 460 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14891 Wyong sectin of Pa12 @RE48838 Yarramalong Maitland 1.2 tripped and reclosed on overload Autolinks 44778 roadside phase found operated Dop patrolled nothing found See 1053306,10 Exclude 1053115,20,7 | December | 2013 | 2014Q2 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-12-10 | N | 18.1652 | N | 6 | N | N | 1.1101 | 39.4971 | 6106.3183
[7 empty] | 16367 | 18719 | 1053437 | 2013-12-10 12:55 | 2013-12-10 14:29 | 94 | 11kV | 5076 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138553 1 Fault operations, No cause found, not storm conditions | December | 2013 | 2014Q2 | 2014 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2013-12-10 | N | 94 | N | 6 | N | N | 1.1101 | 39.4971 | 3709.3911
[7 empty] | 15744 | 11589 | 1053396 | 2013-12-10 12:08 | 2013-12-10 15:08 | 180 | 11kV | 173160 | 962 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138551 1 Fault operations, no cause found, not storm conditions | December | 2013 | 2014Q2 | 2014 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Veg | 2013-12-10 | N | 180 | N | 6 | N | N | 1.1101 | 39.4971 | 126540.2206
[7 empty] | 15807 | 12159 | 1053471 | 2013-12-10 14:04 | 2013-12-10 15:17 | 73 | 11kV | 40223 | 551 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.901 Surry Hills - Pnl.19 tripped on C phase O/C & EFI Abnormal Switching: S1916 Sw B OPEN - S7864 Sw A CLOSED UG cable fault front line section of feeder | December | 2013 | 2014Q2 | 2014 | ZN901:PA19 | ZN901:PA31 | ZN00901/000031 | SYDNEY | UG | Not Veg | 2013-12-10 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 29393.782
[7 empty] | 15229 | 5253 | 1053643 | 2013-12-10 19:59 | 2013-12-10 22:59 | 180 | 11kV | 540 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 138556 Isolated to repair live line clamp to DOLF refer to OMS 1053643 | December | 2013 | 2014Q2 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2013-12-10 | N | 180 | N | 6 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 14778 | 733 | 1053655 | 2013-12-10 22:04 | 2013-12-11 00:20 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138557 Fuse: 10 Amp No cause found, not storm conditions, also refer to 1053655 | December | 2013 | 2014Q2 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2013-12-10 | N | 136 | N | 6 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 15354 | 6843 | 1053661 | 2013-12-11 02:47 | 2013-12-11 05:34 | 167 | 11kV | 78874 | 507 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone section of Pa12 @IR50630 Yarramalong Chandlers 0.1 tripped and reclosed, trpped and locked out Cause: Dop patrolled the feeder thoroughly but could not find a cause See 1054473,5,6 Exclude 1053661,2,3,5,6,7 | December | 2013 | 2014Q2 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-12-11 | N | 155.57 | N | 5 | N | N | 1.1101 | 39.4971 | 57638.7928
[7 empty] | 14764 | 563 | 1053660 | 2013-12-11 00:46 | 2013-12-11 10:15 | 569 | 11kV | 19915 | 35 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12570 section of Pa22 @PT11569 Broad Weston B phase 31.5Amp HDO Blown Cause: Fuse Fatigue. Isolated and restored See 1054283 exclude 1053660,94 | December | 2013 | 2014Q2 | 2014 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2013-12-11 | N | 569 | N | 5 | N | N | 1.1101 | 39.4971 | 14553.2946
[7 empty] | 15901 | 13180 | 1053993 | 2013-12-11 13:08 | 2013-12-11 14:22 | 74 | 11kV | 101816 | 1380 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ZN116 Leichhardt 11kv Panel #34 labelled "S.47278 Balmain derby" tripped on: Relays: A phase IOC EFI Signals: 11kv trip Field EFI's: S47278, S4829, S35899, S35932, S2359, S4205 Remarks: UG fault. Section of 11kv feeder from Sub 4205 Cambell Perry SW B to Sub 1488 Mary Church SW A | December | 2013 | 2014Q2 | 2014 | ZN116:PA34 | ZN116:PA12 | ZN00116/000012 | INNER WEST | UG | Not Veg | 2013-12-11 | N | 73.7797 | N | 5 | N | N | 1.1101 | 39.4971 | 74404.1297
[7 empty] | 15004 | 2889 | 1054103 | 2013-12-11 16:20 | 2013-12-11 17:00 | 40 | 11kV | 720 | 18 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 138570 burnt tapping to sub 71945 | December | 2013 | 2014Q2 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2013-12-11 | N | 40 | N | 5 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 15710 | 11050 | 1054186 | 2013-12-11 23:08 | 2013-12-12 01:51 | 163 | 11kV | 79862 | 507 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone section of Pa12 @IR50630 Yarramalong Chandlers 0.1 tripped and locked out Cause: Mains to conduct a thorough patrol due to irregular tripping without cause See 1054486,9,90 Exclude 1054186 | December | 2013 | 2014Q2 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2013-12-11 | N | 157.5187 | N | 5 | N | N | 1.1101 | 39.4971 | 58360.7941
[7 empty] | 15293 | 6354 | 1054189 | 2013-12-12 00:54 | 2013-12-12 07:00 | 366 | 11kV | 247692 | 725 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9301 Kurnell - Pnl 8 - Earth Fault, timing, lockout, Field EFIs. 11kV wire on the ground between AB35903 and AB35123. ME: 1054302. Secondary: 1054303. Withdrawn: 1054189, 98. | December | 2013 | 2014Q2 | 2014 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2013-12-12 | N | 341.6441 | N | 4 | N | N | 1.1101 | 39.4971 | 181006.0079
[7 empty] | 15434 | 7845 | 1054242 | 2013-12-12 08:55 | 2013-12-12 12:50 | 235 | 11kV | 705 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138585 Fuse size : 16 Amp alsp refer to 1054242 no cause found not storm conditions | December | 2013 | 2014Q2 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2013-12-12 | N | 235 | N | 4 | N | N | 1.1101 | 39.4971 | 515.1932
[7 empty] | 15138 | 4046 | 1054440 | 2013-12-12 12:20 | 2013-12-12 13:20 | 60 | 11kV | 840 | 14 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 148803 emergency switching to replace pole MG-30462 no protection operation SI m0621 | December | 2013 | 2014Q2 | 2014 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Not Veg | 2013-12-12 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 15322 | 6592 | 1054634 | 2013-12-12 16:10 | 2013-12-12 16:45 | 34.7667 | 11kV | 1077.7667 | 31 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 138588 Interrupt to repair wire off pin at pole GR-80296 | December | 2013 | 2014Q2 | 2014 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Not Veg | 2013-12-12 | N | 34.7667 | N | 4 | N | N | 1.1101 | 39.4971 | 787.6001
[7 empty] | 15451 | 7949 | 1054761 | 2013-12-13 05:27 | 2013-12-13 06:24 | 57 | 11kV | 1194 | 22 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2466 Flemington - 11kv Panel No.32 "Sub 8125 Birnie Par No.3" feeder tripped Relays: Earth fault, EFI, Fault check Signals: 11kv trip, Zone earth, No.3 group earth Field EFI's: Nil Remarks: UG fault. 11kv UG feeder fault from Zn2466 Flemington to Sub 8125 Birnie Par No.3 | December | 2013 | 2014Q2 | 2014 | ZN2466:PA32 | ZN2466:PA6 | ZN02466/000006 | CUMBERLAND | UG | Not Veg | 2013-12-13 | N | 54.2727 | N | 5 | N | N | 1.1101 | 39.4971 | 872.54
[7 empty] | 16127 | 16223 | 1054783 | 2013-12-13 08:15 | 2013-12-13 08:43 | 28 | 11kV | 40784.8 | 1820 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9035 Caringbah - Pnl 4 - C phase timed OC and lockout flag. Magpie cause falshover on pole near 66 Captian Cook Drive. Pnl 2 & 4 auto reclose made non auto for works. ME: 1054783. ME GIS: 1054815, 7, 9. Withdrawn: 1054788. | December | 2013 | 2014Q2 | 2014 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | OH | Not Veg | 2013-12-13 | N | 22.4092 | N | 5 | N | N | 1.1101 | 39.4971 | 29804.3289
[7 empty] | 15785 | 11953 | 1054789 | 2013-12-13 08:15 | 2013-12-13 08:44 | 29 | 11kV | 19140 | 660 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | ZN 9035 Caringbah - Pnl 2 - C phase IOC and Timed OC. Magpie caused flashover at pole near 66 Captian Cook Dr. Pnls 2 and 4 reclose made non auto for works. ME: 1054789. Withdrawn: 1054798, 820, 829. Exclude OMS 1054783 | December | 2013 | 2014Q2 | 2014 | ZN9035:PA2 | ZN9035:PA2 | ZN09035/000002 | SUTHERLAND | OH | Not Veg | 2013-12-13 | N | 29 | N | 5 | N | N | 1.1101 | 39.4971 | 13986.9475
[7 empty] | 16161 | 16599 | 1055139 | 2013-12-13 17:19 | 2013-12-13 18:39 | 80 | 11kV | 18838 | 422 | HV | Overload | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138608 Newline intellirupter tripped on overcurrent whist backfeeding Brandy Hill Zone No cause found - not storm conditions | December | 2013 | 2014Q2 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2013-12-13 | N | 44.6398 | N | 5 | N | N | 1.1101 | 39.4971 | 13766.2548
[7 empty] | 16186 | 16932 | 1055155 | 2013-12-13 17:20 | 2013-12-13 18:45 | 85 | 11kV | 255 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Unplanned - LID 138607 interrupt to repair stranded conductor near pole LI-31172 | December | 2013 | 2014Q2 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2013-12-13 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 16331 | 18288 | 1055207 | 2013-12-14 01:36 | 2013-12-14 03:25 | 109 | 11kV | 250898 | 2448 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S2310 Punchbowl Panel 3 "S4906 Pentland Payten" feeder tripped on: Relays: B phase IOC, EFI Signals: 11kv trip, ZE, 2 TX GE Field EFI's operated down to & Including S35679 Remarks: UG fault. 11kv UG cable fault fdr from S35679 Boulevarde Alice to S2340 Fairmount Punchbowl to S3309 Railway Alice | December | 2013 | 2014Q2 | 2014 | ZN2310:PA3 | ZN2310:PA4 | ZN02310/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-12-14 | N | 102.491 | N | 8 | N | N | 1.1101 | 39.4971 | 183348.8582
[7 empty] | 14921 | 2074 | 1055209 | 2013-12-14 06:24 | 2013-12-14 08:50 | 146 | 11kV | 146 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 138615 A Phase 63A DOLF - Fuse Fatique | December | 2013 | 2014Q2 | 2014 |  |  |  | PORT STEPHENS | OH | Not Veg | 2013-12-14 | N | 146 | N | 8 | N | N | 1.1101 | 39.4971 | 106.6925
[7 empty] | 14976 | 2600 | 1055213 | 2013-12-14 07:34 | 2013-12-14 09:45 | 131 | 11kV | 393 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S 9618 Cawarra Namco - Tx Tee from RMI - B phase (90A). Suspect transformer defective. Currently fed via the LV bus section. ME: 1055860. Withdrawn: 1055213. | December | 2013 | 2014Q2 | 2014 | ZN9550:PA27 | ZN9550:PA27 | ZN09550/000027 | SUTHERLAND | UG | Not Veg | 2013-12-14 | N | 131 | N | 8 | N | N | 1.1101 | 39.4971 | 287.1928
[7 empty] | 15808 | 12210 | 1055601 | 2013-12-14 08:59 | 2013-12-14 09:58 | 59 | 11kV | 35872 | 608 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S2400 Berowra ex panel 11 Field Recloser 1239 Brooklyn Tripped on OC Pole BR83811 Opposite 93 Brooklyn Rd - Inadequate clearence Bird See OMS 1055601 1055248 1055233 | December | 2013 | 2014Q2 | 2014 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2013-12-14 | N | 59 | N | 8 | N | N | 1.1101 | 39.4971 | 26214.1996
[7 empty] | 14804 | 983 | 1055245 | 2013-12-14 09:30 | 2013-12-14 10:55 | 85 | 11kV | 85 | 1 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | Unplanned - LID 138617 Magpie found on transformer Phase B and C - 10 Amp. Substation DOLF | December | 2013 | 2014Q2 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-12-14 | N | 85 | N | 8 | N | N | 1.1101 | 39.4971 | 62.1155
[7 empty] | 15378 | 7179 | 1055283 | 2013-12-14 13:00 | 2013-12-14 13:50 | 50 | 11kV | 150 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa1 @PT14591 GEORGE DOWN NANUNDI No.1 HDO failed, 31.5 Amp AEM Ultra Batch #1052 HDO Fuse Failed at crimp, not operated due to failure (31.5Amp AEM Ultra Batch #1052 See 1056351 exclude 1055283 | December | 2013 | 2014Q2 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2013-12-14 | N | 50 | N | 8 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 15070 | 3423 | 1055327 | 2013-12-14 16:49 | 2013-12-14 17:34 | 45 | 11kV | 26460 | 588 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9035 Caringbah - Pnl 7 - IOC, Timed EF, EFI. Underground fault. Front line feeder failure. | December | 2013 | 2014Q2 | 2014 | ZN9035:PA7 | ZN9035:PA7 | ZN09035/000007 | SUTHERLAND | UG | Not Veg | 2013-12-14 | N | 45 | N | 8 | N | N | 1.1101 | 39.4971 | 19336.1876
[7 empty] | 16191 | 16967 | 1055336 | 2013-12-14 17:57 | 2013-12-14 19:25 | 88 | 11kV | 1144 | 13 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | E Zn 12600 Lisarow Zone section of Pa2 @PT11789 The Ridgeway Fagans roadside and centre HDO's operated Cause: 11kv roadside transformer bushing appears failed See 1056388 GIS 1055339 exclude 1055336,7,43,8 | December | 2013 | 2014Q2 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | UG | Not Veg | 2013-12-14 | N | 88 | N | 8 | N | N | 1.1101 | 39.4971 | 836.0015
[7 empty] | 15940 | 13606 | 1055383 | 2013-12-15 01:49 | 2013-12-15 03:23 | 94 | 11kV | 71944 | 855 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12600 Lisarow Pa13 "Brush rd" fdr tripped on relays: A & C phase Overcurrent, EFI Signals: 11kv trip Cause: HV UGOH found damaged between section of 11kv from USL44899 to S14312 to S14776 tee PT13837 See 1056391,4,5 Exclude 1055383 | December | 2013 | 2014Q2 | 2014 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | Unknown | Unknown | 2013-12-15 | N | 84.145 | N | 2 | N | N | 1.1101 | 39.4971 | 52574.5532
[7 empty] | 16481 | 20260 | 1055384 | 2013-12-15 02:12 | 2013-12-15 04:12 | 120 | 11kV | 111585 | 1065 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At Zn15001 Brookvale Zone, Pnl 6 "S16892 Winbourne Rd 38" feeder tripped on A & C phase IOC, time, fault check, efi. Field efi's operated down to and including S16933. Possum on UGOH below S16933. | December | 2013 | 2014Q2 | 2014 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | OH | Not Veg | 2013-12-15 | N | 104.7746 | N | 2 | N | N | 1.1101 | 39.4971 | 81543.0268
[7 empty] | 15967 | 14080 | 1055529 | 2013-12-16 07:08 | 2013-12-16 07:39 | 31 | 11kV | 14043 | 453 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 4L - Earth leakage, EFI. DOp found small section of tree branch hadfallen across UGOH in Evelyn St, Sylvania near Port Hacking Road. ME: 1055529. Withdrawn: 1055533, 4. | December | 2013 | 2014Q2 | 2014 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | OH | Veg | 2013-12-16 | N | 31 | N | 6 | N | N | 1.1101 | 39.4971 | 10262.2102
[7 empty] | 15361 | 6930 | 1055595 | 2013-12-16 09:15 | 2013-12-16 10:30 | 75 | 11kV | 21671 | 453 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 4L - Earth Fault and EFI. UGOH in Evelyn St near Port Hacking Road failed in service. Suspect related to earlier outage with tree branch on UGOH. ME: 1056076. Rest Step: 1056079. Withdrawn: 1055595, 605, 618. | December | 2013 | 2014Q2 | 2014 | ZN9550:PA4 | ZN9550:PA4 | ZN09550/000004 | SUTHERLAND | Unknown | Unknown | 2013-12-16 | N | 47.8389 | N | 6 | N | N | 1.1101 | 39.4971 | 15836.5276
[7 empty] | 15652 | 10486 | 1055516 | 2013-12-16 02:21 | 2013-12-16 14:15 | 714 | 11kV | 6387 | 13 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 138627 138640 MVA - pole AN90523 on ground T&R at 48067 - no operation of 42027 Section of 11kV mains later isolated & repaired OMS 1057382, 384, 386 | December | 2013 | 2014Q2 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2013-12-16 | N | 491.3077 | N | 6 | N | N | 1.1101 | 39.4971 | 4667.4312
[7 empty] | 16105 | 16040 | 1055957 | 2013-12-16 20:07 | 2013-12-16 21:02 | 55 | 11kV | 7315 | 133 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of Panel 11 'Georgina St' 11kv feeder beyond AB 8 Abnormal: Sw/B closed at S.36110 Birch Marion, with Sw/B open at S.8602 Marion Birch No.3 Remarks: Bond at AB 8 | December | 2013 | 2014Q2 | 2014 | ZN1850:PA14 | ZN1850:PA45 | ZN01850/000045 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2013-12-16 | N | 55 | N | 6 | N | N | 1.1101 | 39.4971 | 5345.5862
[7 empty] | 15884 | 12974 | 1055978 | 2013-12-16 22:15 | 2013-12-16 23:35 | 80 | 11kV | 123024 | 1614 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1850 Bass Hill Panel 13 "Edgar Marion" tripped on: Relays: earth fault and EFI Signal: 11kv trip, Zn Earth, No 3 Grp Earth Remarks: UG fault. Front line feeder fault from Sub 1850 Bass Hill Panel #13 to Sub 4312 Sw A. Note Sub 4312 is a HAZ and will need to be extended for testing. Suspect parallel with S48207 Dist 2 at the time | December | 2013 | 2014Q2 | 2014 | ZN1850:PA13 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-12-16 | N | 76.223 | N | 6 | N | N | 1.1101 | 39.4971 | 89902.3106
[7 empty] | 14817 | 1097 | 1055989 | 2013-12-16 23:17 | 2013-12-17 05:15 | 358 | 11kV | 70934 | 803 | HV | Vandalism | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | Unplanned - LID 138647 OHM down between IU-30132 & IU-30135 suspected copper theft | December | 2013 | 2014Q2 | 2014 | 216:10724 | 216:10724 | ZN00216/010724 | LAKE MACQUARIE | OH | Not Veg | 2013-12-16 | N | 88.3362 | N | 6 | N | N | 1.1101 | 39.4971 | 51836.475
[7 empty] | 15114 | 3858 | 1056422 | 2013-12-17 16:23 | 2013-12-17 19:13 | 170 | 11kV | 254200 | 1550 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S847 Hornsby Pa 2 Opened on earth fault Zone Earth, No1 Tx Group Earth, 11kV trip Cause: UG cable fault between S49344 Normanhurst Pennant Hills to S5001 Huddard Pennant to S5292 Hammond Milson See Separate interruption on Pa7 ex S847 1057016 1057018 1057019 1057021 | December | 2013 | 2014Q2 | 2014 | ZN847:PA2 | ZN847:PA2 | ZN00847/000002 | HORNSBY | UG | Not Veg | 2013-12-17 | N | 164 | N | 3 | N | N | 1.1101 | 39.4971 | 185761.8624
[7 empty] | 14960 | 2404 | 1056489 | 2013-12-17 21:37 | 2013-12-17 22:15 | 38.3667 | 11kV | 2762.4 | 72 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 138663 C Phase 40A DOLF replaced | December | 2013 | 2014Q2 | 2014 | 217:33611 | 217:33611 | ZN00217/033611 | LAKE MACQUARIE | OH | Not Veg | 2013-12-17 | N | 38.3667 | N | 3 | N | N | 1.1101 | 39.4971 | 2018.6804
[7 empty] | 14703 | 74 | 1056471 | 2013-12-17 18:48 | 2013-12-17 23:45 | 297 | 11kV | 297 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 138662 A & B phase DOLF : 10 Amp Excluded OMS 1056471 | December | 2013 | 2014Q2 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2013-12-17 | N | 297 | N | 3 | N | N | 1.1101 | 39.4971 | 217.0388
[7 empty] | 15287 | 6298 | 1056919 | 2013-12-18 22:56 | 2013-12-19 01:54 | 178 | 11kV | 14596 | 82 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Zn15005 Belrose Panel 10 'S16807 Forest Way Dawes' section of feeder from CP 24722 Forest Crozier tripped on relays at recloser: SEL. CP 24722 Forest Crozier SEL had just been made auto on afternoon shift. This recloser has tripped on SEL number of times now and require T/PE to check SEL relays and CT's on this recloser. When tried back from CP 24271 Oxford Dreadnought the relcoser tripped instantaneously due to low gas SF6 lock out. | December | 2013 | 2014Q2 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-12-18 | N | 178 | N | 1 | N | N | 1.1101 | 39.4971 | 10666.3263
[7 empty] | 16204 | 17096 | 1056926 | 2013-12-19 07:10 | 2013-12-19 10:40 | 210 | 11kV | 210 | 1 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | Unplanned - LID 138687 11Kv dropper broken connection Replaced 11Kv dropper to dolf at sub 43168 | December | 2013 | 2014Q2 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | Unknown | Not Veg | 2013-12-19 | N | 210 | N | 5 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 15244 | 5570 | 1057113 | 2013-12-19 11:30 | 2013-12-19 13:50 | 140 | 11kV | 216891 | 1677 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.342 paddington Pnl.15 tripped on O/C C phase Abnormal: 11kV feeder O/O/S for decomissioning of S292 between Sw B @ S4194 - Sw A @ S292 - Sw A @ S50187 (Sw B @ S5853 Closed) UG feeder fault between S5277 (tee Tx 3) to S2246 (HVC water baord) Mulitple LV //s in place at time which later failed and have been included as seecondary events to this outage - also S292 included in outage as there was so many //'s in and the model is not reflective of how the network was at the time. | December | 2013 | 2014Q2 | 2014 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2013-12-19 | N | 129.3327 | N | 5 | N | N | 1.1101 | 39.4971 | 158497.5456
[7 empty] | 16287 | 17874 | 1056967 | 2013-12-19 12:00 | 2013-12-19 15:20 | 200 | 11kV | 600 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Hot >35C | N | Unplanned - LID 138692 Fuse: 10 Amp Substation DOLF Distribution transformer Old transformer failed SAO required. Outage start time estimated, time not supplied to the control room and no OMS number | December | 2013 | 2014Q2 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2013-12-19 | N | 200 | N | 5 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 15371 | 7051 | 1057317 | 2013-12-19 18:24 | 2013-12-19 20:01 | 97 | 11kV | 120425 | 1242 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S1610 Homebush Bay Zone Pnl 11 'S4127 RAS Showring North, Etc' feeder tripped on EF, EFI. 11kV UG cable fau;t from S46780 Australia Parkview No2 to S7662 Olympic Tennis No2 to S36085 Australia Parkview No1. | December | 2013 | 2014Q2 | 2014 | ZN1610:PA11 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2013-12-19 | N | 96.9605 | N | 5 | N | N | 1.1101 | 39.4971 | 88003.0381
[7 empty] | 16043 | 15317 | 1057344 | 2013-12-19 21:48 | 2013-12-19 23:57 | 129 | 11kV | 1032 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Dee Why West Zone, section of Pnl 12 L South Creek feeder beyond 24720 Cromer Fitness, 11kV OQFRN 71A Fuse blown. Cause not ascertained, mains to patrol OH section in daylight. | December | 2013 | 2014Q2 | 2014 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | OH | Veg | 2013-12-19 | N | 129 | N | 5 | N | N | 1.1101 | 39.4971 | 754.1552
[7 empty] | 15176 | 4397 | 1057357 | 2013-12-20 04:08 | 2013-12-20 15:35 | 687 | 11kV | 61153 | 540 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" fdr @RE48437 Peats Ridge Cooks tripped and locked out on overcurrent Cause: Truck hit pole REGO WVV-058) 11kv conductors on ground near USL43781 See 1058286,7,8 2nd 1057644,61 Exclude 1057357,8,447 | December | 2013 | 2014Q2 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2013-12-20 | N | 113.2463 | N | 6 | N | N | 1.1101 | 39.4971 | 44688.8087
[7 empty] | 16103 | 16014 | 1057619 | 2013-12-20 15:10 | 2013-12-20 16:10 | 60 | 11kV | 57839.0333 | 964 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | Ex Zn35500 Top Ryde section of Pa27 "Berripa Close" No Protection operated Roadside phase HV bond burnt at UGOH between S4341 and PT1267 in Twin Rd Restored via alternate switching Hospital was affected by the outage See 1058581 LV// 1058785 GIS 1057619 Exclude 1057621,23,49 | December | 2013 | 2014Q2 | 2014 | ZN35500:PA27 | ZN35500:PA27 | ZN35500/000027 | RYDE | OH | Not Veg | 2013-12-20 | N | 59.999 | N | 6 | N | N | 1.1101 | 39.4971 | 42267.0596
[7 empty] | 15644 | 10276 | 1057609 | 2013-12-20 14:50 | 2013-12-20 16:25 | 95 | 11kV | 54366 | 697 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | ZN 10995 Riverwood - Pnl 8 - Trip/reclose/trip, A phase IOC and Timed OC, reclose timing and lockout, Field EFI. 11kV UGOH adjacent to S 10997 failed in service. ME: 1058855. Withdrawn: 1057360, 609. | December | 2013 | 2014Q2 | 2014 | ZN10995:PA8 | ZN10995:PA8 | ZN10995/000008 | GEORGES RIVER | Unknown | Unknown | 2013-12-20 | N | 78 | N | 6 | N | N | 1.1101 | 39.4971 | 39729.0693
[7 empty] | 15429 | 7792 | 1057734 | 2013-12-20 21:29 | 2013-12-20 21:56 | 27 | 11kV | 19764 | 732 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn5868 Gore Hill 11kV Pa5 "Clarendon DIckson etc" fdr tripped on earth fault with fault check Signals: EFI Tx2 Group Earth and 11kv trip Cause: UG cable fault from Zn5868:Pa5 to S8464/SwB to S2936/SwD to S2936/SwB to Zn80:Pa41 See 1057734 GIS 1057735 | December | 2013 | 2014Q2 | 2014 | ZN5868:PA5 | ZN5868:PA5 | ZN05868/000005 | WILLOUGHBY | UG | Not Veg | 2013-12-20 | N | 27 | N | 6 | N | N | 1.1101 | 39.4971 | 14442.9483
[7 empty] | 15932 | 13441 | 1057739 | 2013-12-20 22:17 | 2013-12-21 00:15 | 118 | 11kV | 236 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138704 A phase DOLF : 10 Amp Excluded OMS 1057739 | December | 2013 | 2014Q2 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2013-12-20 | N | 118 | N | 6 | N | N | 1.1101 | 39.4971 | 172.4618
[7 empty] | 14705 | 77 | 1057731 | 2013-12-20 21:20 | 2013-12-21 01:00 | 220 | 11kV | 2420 | 11 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Lightning | N | At PT1752 Quarry Elouera Reserve, roadside phase 31 amp HDO blown. Lightning cause of interruption. | December | 2013 | 2014Q2 | 2014 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2013-12-20 | N | 220 | N | 6 | N | N | 1.1101 | 39.4971 | 1768.4646
[7 empty] | 16332 | 18292 | 1057747 | 2013-12-21 00:21 | 2013-12-21 01:44 | 83 | 11kV | 3154 | 38 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn14143 Somersby Pa21 "Ginurra Chivers 0.1" fdr tripped on earth fault and overcurrent Signals: Tx2 Group Earth and EFI EFI's: Pa21 - S14956 inclusive Cause: Possum vicinity AB45422 | December | 2013 | 2014Q2 | 2014 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2013-12-21 | N | 83 | N | 5 | N | N | 1.1101 | 39.4971 | 2304.8502
[7 empty] | 16150 | 16492 | 1057749 | 2013-12-21 03:31 | 2013-12-21 05:23 | 112 | 11kV | 150528 | 1344 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Zn2400 Berowra 11kv Pz22 "Crawford Glenview etc" fdr tripped on overcurrent Signals: 11kv trip EFI's: S4777 S47461 S8984 Cause: Animals/Birds. Possum at PT2233 Spriggs Jessica | December | 2013 | 2014Q2 | 2014 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2013-12-21 | N | 112 | N | 5 | N | N | 1.1101 | 39.4971 | 110001.4226
[7 empty] | 15608 | 9713 | 1057768 | 2013-12-21 07:29 | 2013-12-21 08:50 | 81 | 11kV | 243 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 138707 A phase DOLF : 20 Amp 248v 0 load irrigation pump Excluded oms 1057768 | December | 2013 | 2014Q2 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2013-12-21 | N | 81 | N | 5 | N | N | 1.1101 | 39.4971 | 177.5772
[7 empty] | 15723 | 11325 | 1057783 | 2013-12-21 11:20 | 2013-12-21 12:35 | 75 | 11kV | 375 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 138711 section isolated to repair burnt off tapping at pole 9L-20263 | December | 2013 | 2014Q2 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2013-12-21 | N | 75 | N | 5 | N | N | 1.1101 | 39.4971 | 274.0389
[7 empty] | 15219 | 4940 | 1057800 | 2013-12-21 09:50 | 2013-12-21 13:35 | 225 | 11kV | 225 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138714 Single phase DOLF : 10 Amp 242 V Excluded OMS 1057800 | December | 2013 | 2014Q2 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2013-12-21 | N | 225 | N | 5 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 16039 | 15297 | 1057978 | 2013-12-22 08:52 | 2013-12-22 09:46 | 54 | 11kV | 44732 | 882 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.7481 Darling Harbour - Panel 20 tripped on Overcurrent & Earth fault right side 11kV UG cable fault between S3822 Glebe Point Rd and S2561 Wigram Walsh see 1058483 1058484 1058485 | December | 2013 | 2014Q2 | 2014 | ZN7481:PA20 | ZN7481:PA20 | ZN07481/000020 | SYDNEY | UG | Not Veg | 2013-12-22 | N | 50.7166 | N | 7 | N | N | 1.1101 | 39.4971 | 32688.8262
[7 empty] | 15617 | 9856 | 1057949 | 2013-12-22 04:22 | 2013-12-22 11:35 | 433.15 | 11kV | 23465.55 | 77 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Unselected | N | At PT2082 Adams Princes footpath 50 K HDO blown. Cause due to tree branch contact. Note: PT2082 dist.2 interupted for emergency repairs following HDO replacement, reference OMS number 1058276. | December | 2013 | 2014Q2 | 2014 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | OH | Veg | 2013-12-22 | N | 304.7474 | N | 7 | N | N | 1.1101 | 39.4971 | 17147.9318
[7 empty] | 15813 | 12260 | 1058086 | 2013-12-22 19:09 | 2013-12-22 20:53 | 104 | 11kV | 117410 | 1153 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2466 Flemmington Panel 5 tripped on IOC, EFI Abnormal: Sw A @ S8718 CLOSED - Sw A @ S8580 OPEN UG cable fault from panel 5 to S2928 Swete St | December | 2013 | 2014Q2 | 2014 | ZN2466:PA5 | ZN2466:PA5 | ZN02466/000005 | CUMBERLAND | UG | Not Veg | 2013-12-22 | N | 101.83 | N | 7 | N | N | 1.1101 | 39.4971 | 85799.765
[7 empty] | 14896 | 1903 | 1058087 | 2013-12-22 19:09 | 2013-12-22 21:35 | 146 | 11kV | 127036 | 1006 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2466 Flemmington Panel 20 tripped on OC & EF, EFI 11kV UF cable fault from S7001 to S3460 to S1867 see 1058808 1058809 | December | 2013 | 2014Q2 | 2014 | ZN2466:PA20 | ZN2466:PA20 | ZN02466/000020 | CUMBERLAND | UG | Not Veg | 2013-12-22 | N | 126.2783 | N | 7 | N | N | 1.1101 | 39.4971 | 92834.1619
[7 empty] | 16295 | 17944 | 1058107 | 2013-12-22 20:57 | 2013-12-22 21:42 | 45 | 11kV | 73035 | 1623 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Zn2635 Epping New Pa31 "Essex Pembroke" reipped on Earth Fault overcurrent Timed overcurrent, earth fault EFI and Fault Check EFI's all down to S5283 operated 11kv trip Possum at PT1108 See 1058107 exclude 1058110 | December | 2013 | 2014Q2 | 2014 | ZN2635:PA31 | ZN2635:PA31 | ZN02635/000031 | PARRAMATTA | OH | Not Veg | 2013-12-22 | N | 45 | N | 7 | N | N | 1.1101 | 39.4971 | 53371.8238
[7 empty] | 16181 | 16876 | 1058122 | 2013-12-22 23:47 | 2013-12-23 01:45 | 118.3 | 11kV | 10173.8 | 86 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S7262 Ganmain Road, distributor 1, 400A fuse blown B phase. LV parallel failure. In LV // for defective out of S4635. | December | 2013 | 2014Q2 | 2014 | ZN3154:PA18 | ZN3154:PA18 | ZN03154/000018 | KU-RING-GAI | UG | Not Veg | 2013-12-22 | N | 118.3 | N | 7 | N | N | 1.1101 | 39.4971 | 7434.713
[7 empty] | 15754 | 11673 | 1058129 | 2013-12-23 00:36 | 2013-12-23 02:28 | 112 | 11kV | 110415 | 1242 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12580 Erina Pa1 "Green Point" fdr tripped and locked out Relays: 150TN, 51N, EFI Signals: 11kv trip EFI's: S18318 S18217 S18864 S18865 S11628 Cause: not ascertained. DOp patrolled feeder but could not find a cause. See 1058562,3,4 Exclude 1058129 | December | 2013 | 2014Q2 | 2014 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Veg | 2013-12-23 | N | 88.901 | N | 14 | N | N | 1.1101 | 39.4971 | 80688.0253
[7 empty] | 15047 | 3162 | 1058323 | 2013-12-23 02:55 | 2013-12-23 03:00 | 5 | 11kV | 6675 | 1335 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 138721 Possum across UGOH at pole IU-61778, blown Cph tapping pole IU-63021, Please inspect UGOH pole IU-61778 also refer to 1058322, 1058328 and 1058329 | December | 2013 | 2014Q2 | 2014 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | OH | Not Veg | 2013-12-23 | N | 5 | N | 14 | N | N | 1.1101 | 39.4971 | 4877.8931
[7 empty] | 15065 | 3338 | 1058328 | 2013-12-23 03:06 | 2013-12-23 06:40 | 214 | 11kV | 3488 | 58 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 138721 Possum across UGOH at pole IU-61778, blown Cph tapping pole IU-63021, Please inspect UGOH pole IU-61778 | December | 2013 | 2014Q2 | 2014 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | OH | Not Veg | 2013-12-23 | N | 60.1379 | N | 14 | N | N | 1.1101 | 39.4971 | 2548.9275
[7 empty] | 16157 | 16591 | 1058112 | 2013-12-22 22:05 | 2013-12-23 07:22 | 556.5833 | 11kV | 395304.05 | 728 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor U/G | Unplanned | Unselected | N | Zn.2466 Flemington Panel 5 - section of 11kV feeder interupted for load relief. S2928 to S1922 (4 DCs interrupted) Abnormal: Sw A @ S8718 CLOSED - Sw B @ S7407 CLOSED - Sw A @ S8125 OPEN - Sw A @ S2928 OPEN Load shedding - Sw B open @ S1922 Martin Raw for load relief to Panel 29. Abnormal switching due to defective cables see 1058845 GIS: 1058116 | December | 2013 | 2014Q2 | 2014 | ZN2466:PA5 | ZN2466:PA5 | ZN02466/000005 | CUMBERLAND | UG | Not Veg | 2013-12-22 | N | 543.0001 | N | 7 | N | N | 1.1101 | 39.4971 | 288876.5402
[7 empty] | 14833 | 1268 | 1058178 | 2013-12-23 08:14 | 2013-12-23 09:00 | 46 | 11kV | 3634 | 79 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 138723 Crossarm straps broken | December | 2013 | 2014Q2 | 2014 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2013-12-23 | N | 46 | N | 14 | N | N | 1.1101 | 39.4971 | 2655.62
[7 empty] | 16233 | 17412 | 1058290 | 2013-12-23 09:45 | 2013-12-23 11:21 | 96 | 11kV | 64801 | 928 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn35370 Galston Pa4 tripped on 51 A overcurrent Fault Indicator operated near AB387 operated. ABNORMAL: LB62158 closed. RE349 Berowra waters Open. Cause: not ascertained Loud explosion in mansfeild rd near #24 DOp unable to positively identify problem See 1059639,41,2,5 Exclude 1058290,4,9,333 | December | 2013 | 2014Q2 | 2014 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2013-12-23 | N | 69.8287 | N | 14 | N | N | 1.1101 | 39.4971 | 47354.6595
[7 empty] | 15333 | 6645 | 1058309 | 2013-12-23 10:02 | 2013-12-23 11:50 | 107.65 | 11kV | 10657.35 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138727 1 Fault operation Phases A & B Over Voltage PHASE trip U & V. Reclose off total bushfire ban FEEDER DROPPED OUT | December | 2013 | 2014Q2 | 2014 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2013-12-23 | N | 107.65 | N | 14 | N | N | 1.1101 | 39.4971 | 7788.077
[7 empty] | 16465 | 20120 | 1058289 | 2013-12-23 09:46 | 2013-12-23 12:45 | 179 | 11kV | 179 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138731 C Phase DOLF : 10 Amp Excluded OMS 1058289 | December | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2013-12-23 | N | 179 | N | 14 | N | N | 1.1101 | 39.4971 | 130.8079
[7 empty] | 15325 | 6598 | 1058488 | 2013-12-23 09:50 | 2013-12-23 14:23 | 273 | 11kV | 1339 | 5 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Hot >35C | N | Ex Zn12630 Peats Ridge section of Pa5 Between AB40526 and CP42860 interrupted for safety reasons. Overhead Linesman discovered a condmened pole that required urgent replacement. Customers notified verbally prior to interuption. See 1058779,80 Exclude 1058488,95 | December | 2013 | 2014Q2 | 2014 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2013-12-23 | N | 267.8 | N | 14 | N | N | 1.1101 | 39.4971 | 978.5017
[7 empty] | 15935 | 13474 | 1058398 | 2013-12-23 11:26 | 2013-12-23 15:00 | 214 | 11kV | 856 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | PT1353 Talbot Bellevue - DOP interrupted for safety to allow Tcon to repair A phase LV tail bond to dist #2 See 1058505 exclude 1058398 | December | 2013 | 2014Q2 | 2014 | ZN262:PA34 | ZN262:PA34 | ZN00262/000034 | INNER WEST | OH | Not Veg | 2013-12-23 | N | 214 | N | 14 | N | N | 1.1101 | 39.4971 | 625.5396
[7 empty] | 14813 | 1063 | 1058622 | 2013-12-23 18:39 | 2013-12-23 19:03 | 24 | 11kV | 1532 | 65 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Hot >35C | N | LID 138733 Feeder isolated to repair buring tapping (causing grassfire) at pole AL-70095. | December | 2013 | 2014Q2 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2013-12-23 | N | 23.5692 | N | 14 | N | N | 1.1101 | 39.4971 | 1119.5404
[7 empty] | 14845 | 1319 | 1058618 | 2013-12-23 18:14 | 2013-12-23 19:25 | 71 | 11kV | 710 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138734 C phase DOLF : 20 Amp Excluded OMS 1058618 | December | 2013 | 2014Q2 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2013-12-23 | N | 71 | N | 14 | N | N | 1.1101 | 39.4971 | 518.8471
[7 empty] | 15593 | 9473 | 1059567 | 2013-12-23 18:46 | 2013-12-23 20:19 | 93 | 11kV | 119586 | 1324 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman, 11kV Fdr Panel 10 tripped on B phase earth fault, timed fault check. Field efi down at S.5511. Not efi's defective at S.35371 and S.2404. UG cable fault between S.35371 and S.2404 to CP.342 | December | 2013 | 2014Q2 | 2014 | ZN180:PA10 | ZN180:PA10 | ZN00180/000010 | MOSMAN | UG | Not Veg | 2013-12-23 | N | 90.3218 | N | 14 | N | N | 1.1101 | 39.4971 | 87389.9216
[7 empty] | 16289 | 17883 | 1058642 | 2013-12-23 20:24 | 2013-12-23 20:33 | 9 | 11kV | 738 | 82 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Zn 15005 Belrose pnl 10 "forest way dawes" section of feeder from REC 24722 Forest Crozier tripped on SEL. Rec 24722 Forest Crozier just been made Auto on the afternoon shift of 18/12/13. Recloser has tripped on SEL a number of times now and requires T/PE to check SEL relays and CT's on recloser. SEL to be left N/A until further investigation. | December | 2013 | 2014Q2 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2013-12-23 | N | 9 | N | 14 | N | N | 1.1101 | 39.4971 | 539.3086
[7 empty] | 16479 | 20258 | 1058676 | 2013-12-24 01:56 | 2013-12-24 04:39 | 163 | 11kV | 115726 | 901 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.3154 St Ives, 11Kv fDR pANEL 24 TRIPPED ON p/c, EARTH FA ult, B phase timed OC, lockout and timing, 11kV trip. Field efi operated at S.4300. UG cable fault between S.35027 and S.8273 | December | 2013 | 2014Q2 | 2014 | ZN3154:PA24 | ZN3154:PA24 | ZN03154/000024 | KU-RING-GAI | UG | Not Veg | 2013-12-24 | N | 128.4417 | N | 8 | N | N | 1.1101 | 39.4971 | 84569.1475
[7 empty] | 14788 | 853 | 1058783 | 2013-12-24 04:37 | 2013-12-24 04:50 | 13 | 11kV | 14599 | 1123 | HV | Fire (non-electrical) | Adverse Weather/Environment | Pole | Unplanned | Unselected | N | LID 138741 No protection operation Feeder isolated to extinguish fire & repair 33kV mains. see report 138740 or OMS 1058781 | December | 2013 | 2014Q2 | 2014 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | OH | Not Veg | 2013-12-24 | N | 13 | N | 8 | N | N | 1.1101 | 39.4971 | 10668.5186
[7 empty] | 15525 | 8763 | 1058705 | 2013-12-24 06:10 | 2013-12-24 07:40 | 90 | 11kV | 6075 | 824 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Rain Light | N | Zn14144 Wamberal Pa4 tripped and reclosed on: Relays: EFI Alarms: Tx2 Group Earth, 11kv trip Cause: Flashover/Arcing @PT12632 Hastings Aspen 31.5Amp footpath and roadside HDO operated due to large piece of strinbark laying across transformer See 1059563,4 Exclude 1058705,8,9,22 | December | 2013 | 2014Q2 | 2014 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2013-12-24 | N | 7.3726 | N | 8 | N | N | 1.1101 | 39.4971 | 4439.4308
[7 empty] | 16320 | 18222 | 1058675 | 2013-12-24 06:40 | 2013-12-24 07:55 | 75 | 11kV | 150 | 2 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 138742 3 phase No protection operations. Fdr isolated to repair UGOH at pole NB-70026. Excluded OMS 1058675 | December | 2013 | 2014Q2 | 2014 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | Unknown | Unknown | 2013-12-24 | N | 75 | N | 8 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 15942 | 13617 | 1058159 | 2013-12-23 07:34 | 2013-12-24 08:00 | 1466.1 | 11kV | 60152 | 824 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 138726 Reclose off for Fire ban. Targets - 3714: G1/B; 7832 No1 & No2 Prot B&C O/C & M/T. Bird on 33kV at pole HW-40213. Please inspect | December | 2013 | 2014Q2 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2013-12-23 | N | 73 | N | 14 | N | N | 1.1101 | 39.4971 | 43957.3074
[7 empty] | 16441 | 19885 | 1058736 | 2013-12-24 07:56 | 2013-12-24 08:05 | 9 | 11kV | 7469 | 2191 | HV | Overload | Utility Process Issue | Fuse | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of pa1L RE41873 Wollana Woodlawn tripped on overload. Hot water Load. See 1059606,8 Exclude 1058736, 1059597,8 | December | 2013 | 2014Q2 | 2014 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2013-12-24 | N | 3.4089 | N | 8 | N | N | 1.1101 | 39.4971 | 5458.1249
[7 empty] | 15158 | 4211 | 1058735 | 2013-12-24 07:52 | 2013-12-24 08:07 | 15 | 11kV | 18000 | 1200 | HV | Overload | Utility Process Issue | Fuse | Unplanned | No Weather Impact | N | Ex Zn12620 Noraville section of Pa7 IR40185 Fravent Main tripped on overload Cause: Overload. Hot Water Load See 1059596 exclude 1058735 | December | 2013 | 2014Q2 | 2014 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2013-12-24 | N | 15 | N | 8 | N | N | 1.1101 | 39.4971 | 13153.8691
[7 empty] | 15869 | 12865 | 1058754 | 2013-12-24 08:22 | 2013-12-24 10:40 | 138 | 11kV | 414 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138745 A phase DOLF : 10 Amp Excluded OMS 1058754 | December | 2013 | 2014Q2 | 2014 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | UG | Not Veg | 2013-12-24 | N | 138 | N | 8 | N | N | 1.1101 | 39.4971 | 302.539
[7 empty] | 16236 | 17432 | 1059017 | 2013-12-24 23:55 | 2013-12-25 01:42 | 107 | 11kV | 93721 | 1081 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Rookie error Zn129 Hunters Hill Pa9 fdr has tripped Signals: 11kv trip TX1 Group Earth, Zone Earth Relays: Cphase inst and timed overcurrent, reclose, LO EFI's: Nil Cause: Bat flew into mains at UGOH at S2591 See 1059721,2,3 exclude 1059017,9,21,684,5,7 | December | 2013 | 2014Q2 | 2014 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | OH | Not Veg | 2013-12-24 | N | 86.6984 | N | 8 | N | N | 1.1101 | 39.4971 | 68488.5425
[7 empty] | 15621 | 9950 | 1059029 | 2013-12-25 04:10 | 2013-12-25 05:38 | 88 | 11kV | 188936 | 2147 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah Nth, Panel 19 Fdr CB tripped on A,B and C phase IOC and timed OC. 11kV trip and #1 Tx group eartyh. Field efi down at S.48811. Possum at LB.49832 | December | 2013 | 2014Q2 | 2014 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2013-12-25 | N | 88 | N | 6 | N | N | 1.1101 | 39.4971 | 138068.8561
[7 empty] | 16248 | 17519 | 1059042 | 2013-12-25 06:30 | 2013-12-25 07:15 | 45 | 11kV | 45 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138749 A phase DOLF : 10 Amp Volts = 243 Excluded OMS 1059042 | December | 2013 | 2014Q2 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | UG | Not Veg | 2013-12-25 | N | 45 | N | 6 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 15743 | 11585 | 1059087 | 2013-12-25 10:34 | 2013-12-25 10:53 | 19 | 11kV | 33858 | 1782 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 138750 1 fault operation A & C phase Overcurrent; Earth fault MAGPIE ON UGOH AT POLE AK-93070.RECLOSE FUNCTION ON SW 19066 MTCHELL LINE SUB DID NOT OPERATE PLEASE INVESTIGATE. | December | 2013 | 2014Q2 | 2014 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Not Veg | 2013-12-25 | N | 19 | N | 6 | N | N | 1.1101 | 39.4971 | 24742.4278
[7 empty] | 15389 | 7319 | 1059258 | 2013-12-25 21:39 | 2013-12-26 01:00 | 201 | 11kV | 161045 | 1594 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S690 Campsie Panel 30 tripped on B phase IOC and Timed Overcurrent, EFI and Fault Check Signals: 11kV Trip, Tx4 Group Earth Cause: Front Line feeder fault from Panel 30 Campsie Zn to S2141 Allen Cant See OMS 1059258 1060997/996/994/993/992 1059259/9261/9262/9270 | December | 2013 | 2014Q2 | 2014 | ZN690:PA30 | ZN690:PA30 | ZN00690/000030 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-12-25 | N | 101.032 | N | 6 | N | N | 1.1101 | 39.4971 | 117686.936
[7 empty] | 15212 | 4752 | 1059224 | 2013-12-25 19:30 | 2013-12-26 02:52 | 442 | 11kV | 117992 | 1602 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Zn12570 Avoca Pa22 tripped, reclosed, tripped on: Relays: B&C overcurrent and Earth Fault, 52T B (IOC, reclose, lockout Signals: EFI EFI's: S62297 Cause: 11kv CCT Mains on the ground adjacent to link 45430. Repaired. See 1059618,9,20 Exclude 1059224 | December | 2013 | 2014Q2 | 2014 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2013-12-25 | N | 73.6529 | N | 6 | N | N | 1.1101 | 39.4971 | 86225.0734
[7 empty] | 16396 | 19151 | 1059242 | 2013-12-25 20:45 | 2013-12-26 16:25 | 1180 | 11kV | 371866 | 1234 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S9900 Menai Panel 1 tripped reclosed tripped and locked out on OvercurrentS Signals: 11kV Trip, Zone earth and Group Earth Cause: UGOH Fault - UGOH near sports field entry failed. Located in section between SW/B at S9428 to SW/A ats S9020 See OMS 1061311 1061316 1059242 1059424 1059265 | December | 2013 | 2014Q2 | 2014 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | Unknown | Unknown | 2013-12-25 | N | 301.3501 | N | 6 | N | N | 1.1101 | 39.4971 | 271748.7046
[7 empty] | 15375 | 7125 | 1059450 | 2013-12-26 16:59 | 2013-12-26 19:30 | 151 | 11kV | 151 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 138756 C Phase DOLF : 10 Amp Blown LA replaced Excluded OMS 1059450 | December | 2013 | 2014Q2 | 2014 |  |  |  |  | OH | Not Veg | 2013-12-26 | N | 151 | N | 2 | N | N | 1.1101 | 39.4971 | 110.3463
[7 empty] | 15579 | 9219 | 1059458 | 2013-12-26 17:57 | 2013-12-26 20:39 | 162 | 11kV | 6864 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12630 Peats Ridge section of Pa3 RE45035 Mangrove Mountain tripped and locked out on overcurrent trip Tree branch on Mains at 62 Wisemans Ferry Rd See 1059630,3 exclude 1059458,9 | December | 2013 | 2014Q2 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2013-12-26 | N | 104 | N | 2 | N | N | 1.1101 | 39.4971 | 5016.0087
[7 empty] | 14910 | 1991 | 1059501 | 2013-12-27 01:18 | 2013-12-27 02:38 | 80 | 11kV | 54880 | 686 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn1193 Lindfeild Pa27 fdr tripped reclosed and locked out Relays: Trip LED (DOp unsure phase or type), reclose timer Signals: 11kv trip Flying fox came into contact with 11kv near LB2097 See 1059501 Exclude 1059502 | December | 2013 | 2014Q2 | 2014 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | OH | Not Veg | 2013-12-27 | N | 80 | N | 3 | N | N | 1.1101 | 39.4971 | 40104.6853
[7 empty] | 14917 | 2057 | 1059750 | 2013-12-27 17:54 | 2013-12-27 19:14 | 80.4333 | 11kV | 4232.6167 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138763 C phase DOLF : 63 Amp Excluded OMS 1059745, 1059750 & 1059759 | December | 2013 | 2014Q2 | 2014 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | UG | Not Veg | 2013-12-27 | N | 60.466 | N | 3 | N | N | 1.1101 | 39.4971 | 3093.0714
[7 empty] | 15438 | 7857 | 1059758 | 2013-12-27 18:50 | 2013-12-27 20:30 | 100 | 11kV | 200 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 138764 C phase DOLF : 10 Amp Fatigue Excluded OMS 1059758 | December | 2013 | 2014Q2 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2013-12-27 | N | 100 | N | 3 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 14744 | 398 | 1059822 | 2013-12-28 13:09 | 2013-12-28 15:00 | 111 | 11kV | 333 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 138767 B phase DOLF : 10 Amp Fatigue Excluded OMS 1059822 | December | 2013 | 2014Q2 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2013-12-28 | N | 111 | N | 1 | N | N | 1.1101 | 39.4971 | 243.3466
[7 empty] | 14771 | 593 | 1059887 | 2013-12-29 01:06 | 2013-12-29 02:18 | 72 | 11kV | 19224 | 267 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 20112 tripped and locked out on OC. Tree brnach removed from OH mains near PT.15458. | December | 2013 | 2014Q2 | 2014 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2013-12-29 | N | 72 | N | 7 | N | N | 1.1101 | 39.4971 | 14048.3322
[7 empty] | 15220 | 4948 | 1059893 | 2013-12-29 03:04 | 2013-12-29 04:42 | 98 | 11kV | 38739 | 414 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1285 Greenacre Park Pa29 fdr tripped on Relays: Earth Leakage, EFI, Fault Check Signals: 11kv trip, Zone Earth, Tx2 Group Earth EFI's S6887 S3653 S1483 Cause: 11kv UG cable fualt from S3653 Chapel Rickard to S6893 Chapel the Mall to S1483 Rickard Chapel See 1060963,5,6 Exclude 1059893 | December | 2013 | 2014Q2 | 2014 | ZN1285:PA29 | ZN37100:PA17 | ZN37100/000017 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2013-12-29 | N | 93.5725 | N | 7 | N | N | 1.1101 | 39.4971 | 28309.3186
[7 empty] | 14876 | 1742 | 1059895 | 2013-12-29 05:56 | 2013-12-29 08:43 | 167 | 11kV | 181863 | 1355 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S10991 Blakehurst Panel 1 tripped and locked out on Relays: C phase IOC timed and locked out Abnormal Switching: AB31328 Open with AB31021 Closed Tree branch on mains near Carwar St 1061270 1059895 | December | 2013 | 2014Q2 | 2014 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Veg | 2013-12-29 | N | 134.2162 | N | 7 | N | N | 1.1101 | 39.4971 | 132900.1163
[7 empty] | 14958 | 2361 | 1059961 | 2013-12-29 08:17 | 2013-12-29 11:50 | 213 | 11kV | 213 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 138769 Replace broken Live Line lead Excluded OMS 1059961 | December | 2013 | 2014Q2 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2013-12-29 | N | 213 | N | 7 | N | N | 1.1101 | 39.4971 | 155.6541
[7 empty] | 15539 | 8872 | 1059977 | 2013-12-29 08:43 | 2013-12-29 13:09 | 266 | 11kV | 54460 | 740 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser CP46113 Fiddens Wharf Coronga Tripped reclosed tripped and locked out on Overcurrent and Earth Fault Tree branch brought down 1 span of 11kV OH in Blaxland Rd Killara - Section of 11kV feeder from S35846 Manning Beaumont to S6931 tee PT1522. See OMS 1060845 1060846 1059977 1060039 | December | 2013 | 2014Q2 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2013-12-29 | N | 73.5946 | N | 7 | N | N | 1.1101 | 39.4971 | 39797.7617
[7 empty] | 15775 | 11859 | 1060072 | 2013-12-29 10:55 | 2013-12-29 13:35 | 160 | 11kV | 800 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 138770 A phase DOLF : 10 Amp Blown L/A cut away Excluded OMS 1060072 | December | 2013 | 2014Q2 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2013-12-29 | N | 160 | N | 7 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 14825 | 1182 | 1060186 | 2013-12-29 18:21 | 2013-12-29 20:10 | 109 | 11kV | 109 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 138773 Single phase DOLF : 10 Amp Fatigue Excluded OMS 1060186 | December | 2013 | 2014Q2 | 2014 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2013-12-29 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 16384 | 18917 | 1060206 | 2013-12-30 04:43 | 2013-12-30 06:00 | 77 | 11kV | 97251 | 1263 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3672 Maroubra Pa6 "The Rhodes Flint" fdr tripped on earht fault, fault check EFI Frontline Underground feeder fault form ZN3672:Pa2 to S6971 Rhodes Flint | December | 2013 | 2014Q2 | 2014 | ZN3672:PA6 | ZN3672:PA6 | ZN03672/000006 | BAYSIDE | UG | Not Veg | 2013-12-30 | N | 77 | N | 5 | N | N | 1.1101 | 39.4971 | 71068.1624
[7 empty] | 16303 | 18048 | 1060213 | 2013-12-30 07:05 | 2013-12-30 08:15 | 70 | 11kV | 140 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 138777 A Phase DOLF : 10 Amp Excluded OMS 1060213 | December | 2013 | 2014Q2 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | UG | Not Veg | 2013-12-30 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 15160 | 4223 | 1060216 | 2013-12-30 07:23 | 2013-12-30 08:52 | 89 | 11kV | 266.0833 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14144 Wamberal section of Pa5 @PT14316 Mittara Serpentine Middle Phase HV fuse blown 16Amp BB Cause not ascertained. Patrolled nothing found See 1060857 GIS 1060216 | December | 2013 | 2014Q2 | 2014 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2013-12-30 | N | 88.6944 | N | 5 | N | N | 1.1101 | 39.4971 | 194.4459
[7 empty] | 15978 | 14236 | 1060379 | 2013-12-30 13:47 | 2013-12-30 14:33 | 46 | 11kV | 34040 | 740 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser CP46113 Fiddens Wharf Coronga tripped reclosed tripped and locked out on IOC trip Cause: Outside 48 Beaumont Rd Killara tree branch with burn marks Tree branch hit 11kV Mains See OMS 1060379 1060387 | December | 2013 | 2014Q2 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2013-12-30 | N | 46 | N | 5 | N | N | 1.1101 | 39.4971 | 24875.428
[7 empty] | 15543 | 8892 | 1060479 | 2013-12-30 21:17 | 2013-12-31 02:08 | 291 | 11kV | 139386 | 1271 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn269 Waverley 11kv OCB Pa14 "Woodstock" tripped on Relays: B Phase Overcurrent, EFI EFI's: S1872 S14754 S3677 Signals: 11kv trip, Zone Earth, #3 Group Earth 11kv fdr failure between S3677 to S1215. 391 fdr & Zn269:Pa14 fdr tripped at same time See 1061295 2nd 1061296,7,8 3rd 1061299 4th 1060481 5th 1060479 Exclude 1060477,84,5,7,92 | December | 2013 | 2014Q2 | 2014 | ZN269:PA14 | ZN36800:PA56 | ZN36800/000056 | WAVERLEY | UG | Not Veg | 2013-12-30 | N | 109.6664 | N | 5 | N | N | 1.1101 | 39.4971 | 101859.1776
[7 empty] | 15787 | 11981 | 1060494 | 2013-12-31 00:33 | 2013-12-31 02:26 | 113 | 11kV | 22163 | 223 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 138782 3 fault operations Earth fault Feeder patrol required No access to 11kV links 9169 Excluded OMS 1060494 | December | 2013 | 2014Q2 | 2014 | 264:81240 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2013-12-31 | N | 99.3857 | N | 3 | N | N | 1.1101 | 39.4971 | 16196.0667
[7 empty] | 15587 | 9395 | 1060501 | 2013-12-31 03:18 | 2013-12-31 04:10 | 52 | 11kV | 3068 | 59 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Ex Zn12620 Noraville section of 11kv fdr Pa7 @PT12186 Reynolds Clark Centre and footpath 31.5Amp HDO operated Cause: Animals/Birds Flashover due to possum @PT12186 no damage to PT See 1060861 exclude 1060501,2 | December | 2013 | 2014Q2 | 2014 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | OH | Not Veg | 2013-12-31 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 2242.0039
[7 empty] | 15422 | 7695 | 1060507 | 2013-12-31 06:50 | 2013-12-31 08:01 | 71 | 11kV | 210728 | 2968 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn269 Waverely 11kv Pa9 tripped on Relays: Aph overcurrent Signals: EFI EFI's Nil ABNORMAL: Frontline fdr fault Zn269:Pa16. Closed S354/SwB Open S339 UG fault from Pa9 to S4051/SwA See 1061378 LV// 1060511 exclude 1060507,8,12 | December | 2013 | 2014Q2 | 2014 | ZN269:PA9 | ZN36100:PA6 | ZN36100/000006 | WAVERLEY | UG | Not Veg | 2013-12-31 | N | 71 | N | 3 | N | N | 1.1101 | 39.4971 | 153993.807
[7 empty] | 16404 | 19201 | 1060734 | 2014-01-01 07:01 | 2014-01-01 08:29 | 88 | 11kV | 26032 | 296 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14143 Somersby Pa10 fdr tripped Relays - Earth Fault, EFI Signals: 11kv trip, Tx1 Group Earth EFI's: S46875 11kv UG Fault between S46875 and AB44186 Note: Recloser was auto and the spring indicated charged, however there was no attempt at a a reclose as indicated by DNMS or the relays See 1060892,3 Exclude 1060734 | January | 2014 | 2014Q3 | 2014 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | UG | Not Veg | 2014-01-01 | N | 87.9459 | N | 3 | N | N | 1.1101 | 39.4971 | 19023.4178
[7 empty] | 14966 | 2464 | 1060782 | 2014-01-01 13:31 | 2014-01-01 14:30 | 59 | 11kV | 4877.8667 | 83 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1715 Capper Howard Roadside Phase HVDO fuse failed Cause: Fuse Fatigue See OMS 1060778 1060968 1060782 | January | 2014 | 2014Q3 | 2014 | ZN1193:PA16 | ZN1193:PA16 | ZN01193/000016 | KU-RING-GAI | OH | Not Veg | 2014-01-01 | N | 58.7695 | N | 3 | N | N | 1.1101 | 39.4971 | 3564.6011
[7 empty] | 15342 | 6745 | 1060793 | 2014-01-01 16:22 | 2014-01-01 17:40 | 78 | 11kV | 131412 | 2141 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.15008 harbord - Pnl.9 tripped on : A phase IOC, Lockout, reclose, time delay, fault check. UG cable fault - front line feeder see 1062113 1062114 | January | 2014 | 2014Q3 | 2014 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | UG | Not Veg | 2014-01-01 | N | 61.3788 | N | 3 | N | N | 1.1101 | 39.4971 | 96032.0136
[7 empty] | 14822 | 1132 | 1060833 | 2014-01-02 07:23 | 2014-01-02 08:35 | 72 | 11kV | 144 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148790 Single phase DOLF : 3 Amp Excluded OMS 1060833 | January | 2014 | 2014Q3 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | UG | Not Veg | 2014-01-02 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 105.231
[7 empty] | 14992 | 2756 | 1060842 | 2014-01-02 08:06 | 2014-01-02 10:05 | 119 | 11kV | 238 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148792 A phase DOLF : 10 Amp Excluded OMS 1060842 | January | 2014 | 2014Q3 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2014-01-02 | N | 119 | N | 5 | N | N | 1.1101 | 39.4971 | 173.9234
[7 empty] | 15200 | 4644 | 1060904 | 2014-01-02 11:16 | 2014-01-02 13:47 | 151 | 11kV | 12805 | 85 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge section of Pa3 @LB49261 opened for safety reasons. 11kv mains have come off the pin insulators on the corner o waratah Rd & Wisemans Ferry Rd. Section of fdr from RE45071 to LB49207 to LB49261 isolated & earthed to carry out repairs. See 1061197,8 exclude 1060904 | January | 2014 | 2014Q3 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-01-02 | N | 150.6471 | N | 5 | N | N | 1.1101 | 39.4971 | 9357.5163
[7 empty] | 15786 | 11969 | 1060945 | 2014-01-02 13:03 | 2014-01-02 14:03 | 60 | 11kV | 8520 | 142 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7900 Campbell st 11kv VCB pa3 fdr tripped on: Relays: P122 Relay trip, OC, EF, EF check, EFI EFI's: S35022 S5404 Signals: 11kv trip Cause: 11kv UG fault from S5404SWA to S4902SwB to S35852SwB | January | 2014 | 2014Q3 | 2014 | ZN7900:PA3 | ZN7900:PA3 | ZN07900/000003 | SYDNEY | UG | Not Veg | 2014-01-02 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 6226.1647
[7 empty] | 16436 | 19815 | 1060998 | 2014-01-02 15:17 | 2014-01-02 17:50 | 153 | 11kV | 11836 | 89 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Interrupted by DOp on 2nd event Zn14143 Somersby 11kv fdr Pa17 "Somersby Falls" tripped and reclosed Relays: IOC and Overcurrent B & C phase Cause: Tree branch fell onto HV mains between AB40511 to LK44302 etc. Damaged construction bringing Overhead mains to within 2 metres from ground. See first T&R 1061208 and 2nd 1061210,1 Exclude 1061007,8,10,27,34 | January | 2014 | 2014Q3 | 2014 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2014-01-02 | N | 132.9888 | N | 5 | N | N | 1.1101 | 39.4971 | 8649.3997
[7 empty] | 15345 | 6777 | 1061102 | 2014-01-03 03:57 | 2014-01-03 04:44 | 47 | 11kV | 43569 | 927 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn12610 Long Jetty Pa20 "Matcham st" fdr tripped, reclosed, tripped and locke dout: Relays: IOC ACphases, reclose relay and lockout relay Signals: 11kv trip EFI's: Nil Cause: Dead Possum found at base of Pole BV3968 on corner of Sherry st and Rotherham st Bateau Bay See 1061102,5 | January | 2014 | 2014Q3 | 2014 | ZN12610:PA20 | ZN12610:PA20 | ZN12610/000020 | CENTRAL COAST | OH | Not Veg | 2014-01-03 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 31838.9401
[7 empty] | 15251 | 5676 | 1061120 | 2014-01-03 07:12 | 2014-01-03 10:14 | 182 | 11kV | 1820 | 10 | HV | Vegetation Blow/Fall In | Vegetation | Insulator | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge seciton of Pa4 "Kulnura" fdr PT13382 Wise Ferry Hallards 0.6 11kv 20A HDO fuses operated (footpath & centre phase) Cause: Tree branch on HV Bushings See 1062554 exclude 1061120 | January | 2014 | 2014Q3 | 2014 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2014-01-03 | N | 182 | N | 3 | N | N | 1.1101 | 39.4971 | 1330.0023
[7 empty] | 14946 | 2233 | 1061260 | 2014-01-03 11:39 | 2014-01-03 13:00 | 81 | 11kV | 81 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148800 A phase DOLF : 10 Amp Excluded OMS 1061260 | January | 2014 | 2014Q3 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | UG | Not Veg | 2014-01-03 | N | 81 | N | 3 | N | N | 1.1101 | 39.4971 | 59.1924
[7 empty] | 15691 | 10935 | 1061434 | 2014-01-04 00:10 | 2014-01-04 01:26 | 76 | 11kV | 5928 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Recloser 1014 Suakin Drive tripped and locked out on overcurrent Cause not ascertained, mains to patrol | January | 2014 | 2014Q3 | 2014 | ZN180:PA17 | ZN180:PA17 | ZN00180/000017 | MOSMAN | OH | Veg | 2014-01-04 | N | 76 | N | 2 | N | N | 1.1101 | 39.4971 | 4332.0076
[7 empty] | 16089 | 15912 | 1061445 | 2014-01-04 03:10 | 2014-01-04 14:15 | 665 | 11kV | 175418 | 1411 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ZN36200 Empir Bay Pa11 fdr tripped, reclosed, tripped and lockedout on: Relays: B&C phases IOC, Reclose Time, Lockout and EFI Signals: 11kv trip EFI's: Nil Cause: Large tree has brought down 2 spans of 11kv in Yugari rd daleys point. Section og 11kv fdr from LK4075 to AB43079 to LB43302 tee to PT11624 See 1062561,2,3,4 Exclude 1061445,6,7,8,52,3,4,67 | January | 2014 | 2014Q3 | 2014 | ZN36200:PA11 | ZN36200:PA11 | ZN36200/000011 | CENTRAL COAST | OH | Veg | 2014-01-04 | N | 124.3218 | N | 2 | N | N | 1.1101 | 39.4971 | 128190.3004
[7 empty] | 14868 | 1678 | 1061579 | 2014-01-05 05:18 | 2014-01-05 10:37 | 319 | 11kV | 53243 | 831 | HV | Animal Bird | Animal | Bond | Unplanned | Unselected | N | LID 148809 2 fault operations B phase Overcurrent Magpie. Tapping off at 11kV Links 19653. Excluded oms1061579/80. | January | 2014 | 2014Q3 | 2014 | 256:80632 | 256:80632 | ZN00256/080632 | NEWCASTLE | OH | Not Veg | 2014-01-05 | N | 64.071 | N | 4 | N | N | 1.1101 | 39.4971 | 38908.414
[7 empty] | 15804 | 12151 | 1061602 | 2014-01-05 10:22 | 2014-01-05 12:33 | 130.8167 | 11kV | 60653.0333 | 1081 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn384 Camperdown - Pnl.43 tripped on Earth Fault - C phase OC - sealing contactor, EFI - Pnl.10 tripped on Earth Fault, A phase OC, EFI Front line cable fault on both panels (panel 10 to N/O point - no customers interrupted) see 1061750 1061752 | January | 2014 | 2014Q3 | 2014 | ZN384:PA43 | ZN384:PA70 | ZN00384/000070 | SYDNEY | UG | Not Veg | 2014-01-05 | N | 56.1083 | N | 4 | N | N | 1.1101 | 39.4971 | 44323.4478
[7 empty] | 14869 | 1685 | 1061632 | 2014-01-05 14:54 | 2014-01-05 15:39 | 45 | 11kV | 5445 | 121 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 148812 2 fault operations A phase Overcurrent tree branch on mains at pole HV-10115 | January | 2014 | 2014Q3 | 2014 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2014-01-05 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 3979.0454
[7 empty] | 15778 | 11886 | 1061672 | 2014-01-05 19:44 | 2014-01-05 20:53 | 69.1167 | 11kV | 3179.3667 | 46 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Wind | N | At PT49602 Kulgoa Bristol Roadside HDO fuse blown Cause: Trees on Tx Tank See OMS 1061678 1061672 | January | 2014 | 2014Q3 | 2014 | ZN3154:PA19 | ZN3154:PA19 | ZN03154/000019 | KU-RING-GAI | OH | Veg | 2014-01-05 | N | 69.1167 | N | 4 | N | N | 1.1101 | 39.4971 | 2323.3874
[7 empty] | 15102 | 3719 | 1061707 | 2014-01-06 04:04 | 2014-01-06 05:24 | 80 | 11kV | 99920 | 1249 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S129 Hunters Hill Panel 8 tripped on Relays: A phase overcurrent Signals : 11kV trip Cause not ascertained for outage mains to patrol in daylight | January | 2014 | 2014Q3 | 2014 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Veg | 2014-01-06 | N | 80 | N | 4 | N | N | 1.1101 | 39.4971 | 73018.5889
[7 empty] | 15577 | 9194 | 1061764 | 2014-01-06 09:31 | 2014-01-06 11:10 | 99 | 11kV | 99 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148819 B phase DOLF : 10 Amp Excluded OMS 1061764 | January | 2014 | 2014Q3 | 2014 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | UG | Not Veg | 2014-01-06 | N | 99 | N | 4 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 15968 | 14103 | 1061831 | 2014-01-06 11:05 | 2014-01-06 11:40 | 35 | 11kV | 910 | 26 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 148818 During SI 37563 11kV Links 40510 broke. Outage area extended to replace broken links. See also LID planned outage report #148817. Excluded OMS No. 1061831 | January | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-01-06 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 665.0012
[7 empty] | 15085 | 3536 | 1061982 | 2014-01-06 17:06 | 2014-01-06 19:20 | 134 | 11kV | 18814 | 225 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 148820 A phase Overcurrent Excluded OMS 1061982 | January | 2014 | 2014Q3 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-01-06 | N | 83.6178 | N | 4 | N | N | 1.1101 | 39.4971 | 13748.7163
[7 empty] | 16269 | 17638 | 1062476 | 2014-01-07 14:15 | 2014-01-07 16:00 | 105 | 11kV | 105 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 148829 1 fault operation 3 phase Overcurrent Mcgraw Eddison Recloser found opened. Closed on ok. Dop V Hickey found trees above private mains near private sub, which may have falen through conductors. | January | 2014 | 2014Q3 | 2014 |  |  |  | LAKE MACQUARIE | OH | Veg | 2014-01-07 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 16050 | 15411 | 1062376 | 2014-01-07 18:23 | 2014-01-07 19:15 | 52 | 11kV | 29322 | 630 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2473 North Sydney Panel 26 tripped on 26L B phase O/L, EFI and FC Alarms: Tx4 GE, ZE, 11kV Trip Cable Fault between S3683 to S35758 to S1683 See OMS 1062956 1062958 1062376 | January | 2014 | 2014Q3 | 2014 | ZN2473:PA26 | ZN35400:PA77 | ZN35400/000077 | NORTH SYDNEY | UG | Not Veg | 2014-01-07 | N | 46.5429 | N | 2 | N | N | 1.1101 | 39.4971 | 21427.6527
[7 empty] | 15206 | 4684 | 1062646 | 2014-01-08 11:45 | 2014-01-08 14:10 | 145 | 11kV | 25520 | 176 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 148843 Stranded conductor between poles HS 72458 & HS 72436 Mulbring St x Maitland St, Stanford Merthyr. Excluded OMS 1062646 & 1062709 | January | 2014 | 2014Q3 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-01-08 | N | 145 | N | 2 | N | N | 1.1101 | 39.4971 | 18649.2633
[7 empty] | 15117 | 3884 | 1062824 | 2014-01-08 22:59 | 2014-01-08 23:36 | 37 | 11kV | 79439 | 2147 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Unselected | N | At S.36300 Balgowlah North, Panel 19 Fdr CB tripped on AB and C phase IOC, efi, fault check. #1 Tx group earth. Filed efi's operated at S.16827, S.16064, S.49927, S.16928, S.48811, UG/OH at 16 Myrtle St. Possum on footpath side of LB.49832 and lightning arrestor | January | 2014 | 2014Q3 | 2014 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2014-01-08 | N | 37 | N | 2 | N | N | 1.1101 | 39.4971 | 58051.6781
[7 empty] | 15334 | 6692 | 1062838 | 2014-01-09 05:06 | 2014-01-09 06:05 | 59 | 11kV | 29355 | 657 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 148846 2 fault operations Earth fault UGOH blown at pole IV-93550 Excluded oms 1062838 | January | 2014 | 2014Q3 | 2014 | 222:33597 | 222:33597 | ZN00222/033597 | LAKE MACQUARIE | Unknown | Unknown | 2014-01-09 | N | 44.6804 | N | 3 | N | N | 1.1101 | 39.4971 | 21451.7682
[7 empty] | 14999 | 2865 | 1062950 | 2014-01-09 10:03 | 2014-01-09 12:00 | 117 | 11kV | 234 | 2 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | LID 148860 Fuse Size: 10 AMP REPLACED 10A DOLF. BLOWN DUE TO POSSUM ON 11KV UGOH. FAULT CLEARED. SUPPLY RESTORED. Also refer to 1062950 | January | 2014 | 2014Q3 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-01-09 | N | 117 | N | 3 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 15510 | 8579 | 1063131 | 2014-01-09 15:22 | 2014-01-09 17:20 | 118 | 11kV | 118 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 148862 Fuse Size: 16Amp Fuse Fatigue, TX Volts 247/247/247 Excluded OMS 1063131 | January | 2014 | 2014Q3 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-01-09 | N | 118 | N | 3 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 14770 | 589 | 1063208 | 2014-01-10 01:25 | 2014-01-10 03:25 | 120 | 11kV | 106560 | 888 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 148864 tapping open at pole IU-80037 ABS 6092 CLOSED & ABS 2394 OPENED. | January | 2014 | 2014Q3 | 2014 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2014-01-10 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 77870.905
[7 empty] | 15275 | 6129 | 1063220 | 2014-01-10 04:24 | 2014-01-10 05:25 | 61 | 11kV | 31005 | 945 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn12690 Berkeley Vale Pa6 tripped and reclosed: Relays: BC phase IOC, EFI, Recloser Timer, Lockout Signals: Tx12 Group Earth, Tx13 Group Earth, Under Voltage Tx12, Under Voltage Tx13 Cause: Open Bond Centre Phase at Load Breka Switch LB42262 See 1063292,4 Exclude 1063220,2,3,5 | January | 2014 | 2014Q3 | 2014 | ZN12690:PA6 | ZN12690:PA6 | ZN12690/000006 | CENTRAL COAST | OH | Not Veg | 2014-01-10 | N | 32.8095 | N | 7 | N | N | 1.1101 | 39.4971 | 22657.5395
[7 empty] | 16429 | 19574 | 1063218 | 2014-01-10 04:10 | 2014-01-10 05:40 | 90 | 11kV | 5670 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148865 A phase DOLF : 31 Amp Excluded OMS 1063218 & 1063224 | January | 2014 | 2014Q3 | 2014 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | UG | Not Veg | 2014-01-10 | N | 90 | N | 7 | N | N | 1.1101 | 39.4971 | 4143.4688
[7 empty] | 16415 | 19366 | 1063404 | 2014-01-10 13:55 | 2014-01-10 14:25 | 30 | 11kV | 660 | 22 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa9 "Wyoming South" fdr from AB41709 to LK43155 tee PT11671 & PT12024 interrupted for safety Interrupted by DOp to allow mains to remove limb of tree touching 11kv mains See 1064371 exclude 1063404 | January | 2014 | 2014Q3 | 2014 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2014-01-10 | N | 30 | N | 7 | N | N | 1.1101 | 39.4971 | 482.3085
[7 empty] | 16237 | 17443 | 1063381 | 2014-01-10 11:36 | 2014-01-10 16:51 | 315 | 11kV | 54583 | 1899 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 148880 2 fault operations B & C phases Truck hit mains near sub 90749 prot sw 80787 51BC Excluded OMS# 1063381 etc. | January | 2014 | 2014Q3 | 2014 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2014-01-10 | N | 28.743 | N | 7 | N | N | 1.1101 | 39.4971 | 39887.6465
[7 empty] | 15243 | 5558 | 1063324 | 2014-01-10 14:00 | 2014-01-10 17:00 | 180 | 11kV | 180 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 148881 3 phase DOLF : 10 Amp Reported by Bronco TX Replaced, Volts 247/247/247 | January | 2014 | 2014Q3 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2014-01-10 | N | 180 | N | 7 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 16402 | 19163 | 1063554 | 2014-01-10 19:09 | 2014-01-10 20:30 | 81 | 11kV | 162 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148883 Single phase DOLF : 10 Amp Excluded OMS 1063554 | January | 2014 | 2014Q3 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2014-01-10 | N | 81 | N | 7 | N | N | 1.1101 | 39.4971 | 118.3848
[7 empty] | 16300 | 18016 | 1063590 | 2014-01-11 00:09 | 2014-01-11 02:26 | 137 | 11kV | 26578 | 194 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" tripped and locked out on Relays: Overcurrent Trip & Lockout Cause: FlyingFox adjacent PT14580. Pole #PF69 | January | 2014 | 2014Q3 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2014-01-11 | N | 137 | N | 3 | N | N | 1.1101 | 39.4971 | 19422.4185
[7 empty] | 15796 | 12091 | 1063598 | 2014-01-11 01:50 | 2014-01-11 02:30 | 40 | 11kV | 29520 | 738 | HV | Animal Flying Fox | Animal | DC PT | Unplanned | Unselected | N | 11KV Rec.46118 Dalton Blaxland exiting Panel #36 labelled "S.4923" from Zn.4545 Meadowbank tripped & locked: Relays: O/C, IOC & Lockout Remarks: Animals/Birds. Flying Fox O/S 529 Blaxland Rd Eastwood. Adj PT2191 Russell Karnak | January | 2014 | 2014Q3 | 2014 | ZN4545:PA36 | ZN4545:PA36 | ZN04545/000036 | RYDE | OH | Not Veg | 2014-01-11 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 21572.3453
[7 empty] | 15794 | 12068 | 1063668 | 2014-01-11 15:48 | 2014-01-11 17:10 | 82.15 | 11kV | 38692.65 | 471 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | LID 148887 C phase nil protection (c phase fuse may have blown in RMU). Fdr interupted from sw 36721 Lycett Cres sub due to Haz sw gear on fire. dq | January | 2014 | 2014Q3 | 2014 | 238:34143 | 238:34143 | ZN00238/034143 | MAITLAND | Unknown | Not Veg | 2014-01-11 | N | 82.15 | N | 3 | N | N | 1.1101 | 39.4971 | 28275.4474
[7 empty] | 15730 | 11388 | 1063775 | 2014-01-12 11:59 | 2014-01-12 13:14 | 75 | 11kV | 138906 | 1892 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zone 72 Five Dock Panel 14 'Sub 8715 MWS & Martin St No 2' etc fdr Relays: Earth fault, EFI Signals: 11kv trip, Zone and Tx 4 Group earths Field EFI's: Nil Remarks: UG fault. 11kv UG feeder fault from Zn 72 Five Dock Panel 14 to Sub 8715 MWS & Martin St No 2 to Sub 40 Ramsay Rd | January | 2014 | 2014Q3 | 2014 | ZN72:PA14 | ZN35555:PA2 | ZN35555/000002 | INNER WEST | UG | Not Veg | 2014-01-12 | N | 73.4175 | N | 2 | N | N | 1.1101 | 39.4971 | 101508.4078
[7 empty] | 14888 | 1816 | 1063812 | 2014-01-12 19:24 | 2014-01-12 21:30 | 126 | 11kV | 882 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 148889 Isolated for safety B phase bond burned off at pole FP-50311 isolation at LF 40679 for safety. Excluded OMS 1063812. | January | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-01-12 | N | 126 | N | 2 | N | N | 1.1101 | 39.4971 | 644.5396
[7 empty] | 15394 | 7384 | 1063831 | 2014-01-13 01:23 | 2014-01-13 02:54 | 91 | 11kV | 67977 | 747 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S9550 Gwawley Bay, Panel 36 'LB47770 etc' 11kv feeder tripped on; A & B phase IOC Remarks: Animals/Birds. Bat located at section of OH between S.50345 (Sw/B) and S.9669 (Sw/B) | January | 2014 | 2014Q3 | 2014 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2014-01-13 | N | 91 | N | 7 | N | N | 1.1101 | 39.4971 | 49675.5866
[7 empty] | 16154 | 16499 | 1063832 | 2014-01-13 04:39 | 2014-01-13 05:53 | 74 | 11kV | 230880 | 3120 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S35500 Top Ryde Panel 28 tripped and locked out on PA28RL EFI, Fault check, under frequency and A and C phase IOC Cause: Possum at Base of UGOH to S7493 | January | 2014 | 2014Q3 | 2014 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2014-01-13 | N | 74 | N | 7 | N | N | 1.1101 | 39.4971 | 168720.2942
[7 empty] | 16477 | 20248 | 1063894 | 2014-01-13 08:56 | 2014-01-13 10:45 | 109 | 11kV | 109 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148898 B phase DOLF : 10 Amp Excluded OMS 1063894 | January | 2014 | 2014Q3 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | UG | Not Veg | 2014-01-13 | N | 109 | N | 7 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 15054 | 3278 | 1063955 | 2014-01-13 11:25 | 2014-01-13 14:55 | 210 | 11kV | 630 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 148901 Section isolated to repair low 11kV OHM at IU-20032 Replacing OMS 1064345 | January | 2014 | 2014Q3 | 2014 | 216:10724 | 216:10724 | ZN00216/010724 | LAKE MACQUARIE | OH | Not Veg | 2014-01-13 | N | 210 | N | 7 | N | N | 1.1101 | 39.4971 | 460.3854
[7 empty] | 15260 | 5823 | 1064341 | 2014-01-13 16:37 | 2014-01-13 16:41 | 4 | 11kV | 4672 | 1168 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.3155 Double Bay Pnl.34 tripped on timed O/C, Earth fault & fault check All field EFIs operated Abnormal: Frontline feeder Pnl.17 defective to S35410, S480 & S5782. Sw B @ S8303 CLOSED - Sw B @ S35410 OPEN Failed on energising - defective feeder from pnl 17 failed on proving / phasing after repirs from previous fault - tripping healthy pnl 34 | January | 2014 | 2014Q3 | 2014 | ZN3155:PA34 | ZN3155:PA34 | ZN03155/000034 | WOOLLAHRA | UG | Not Veg | 2014-01-13 | N | 4 | N | 7 | N | N | 1.1101 | 39.4971 | 3414.1598
[7 empty] | 16395 | 19149 | 1064226 | 2014-01-13 15:46 | 2014-01-13 16:57 | 71 | 11kV | 45221 | 972 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At ZN8000 Macquarie Park Panel 1 Tripped on Earth Fault At Zn35500 Top Ryde Pa23 Tripped on Timed earth fault with EFI. Cause: During switching DAR329238 across ZN8000 Macquarie Park Pa1 and Zn35500 Top Ryd Pa23 11kV UG fault located between S1842 and S7552 See OMS 1067585 1067586 1067587 1064226 1064232 1064234 1064238 1064240 1064241 | January | 2014 | 2014Q3 | 2014 | ZN8000:PA1 | ZN8000:PA2 | ZN08000/000002 | RYDE | UG | Not Veg | 2014-01-13 | N | 46.5237 | N | 7 | N | N | 1.1101 | 39.4971 | 33046.173
[7 empty] | 16298 | 17984 | 1064319 | 2014-01-13 20:44 | 2014-01-14 00:27 | 223 | 11kV | 45046 | 202 | HV | Animal Possum | Animal | DC Transformer | Unplanned | Unselected | N | S15193 Stuart st 53 HV fuse blown. KEBXO 80 Amps Aphase Cause: Possum found across Tx bushings which caused HV fuse to blow DOp also found LV USL 26988 closed in Carey St. Cross Zone Link See 1064465 exclude 1064319 | January | 2014 | 2014Q3 | 2014 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Not Veg | 2014-01-13 | N | 223 | N | 7 | N | N | 1.1101 | 39.4971 | 32918.2882
[7 empty] | 15622 | 9981 | 1064330 | 2014-01-14 05:28 | 2014-01-14 06:40 | 72 | 11kV | 24616 | 365 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.10999 Kogarah Pnl.2 - tripped on : Earth fault, EFI Field EFis - S10116 UG Cable fault see 1064809 1064810 | January | 2014 | 2014Q3 | 2014 | ZN10999:PA2 | ZN10999:PA2 | ZN10999/000002 | GEORGES RIVER | UG | Not Veg | 2014-01-14 | N | 67.4411 | N | 4 | N | N | 1.1101 | 39.4971 | 17988.6468
[7 empty] | 14814 | 1066 | 1064569 | 2014-01-14 12:42 | 2014-01-14 13:41 | 59 | 11kV | 16638 | 282 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 2466 Flemington Panel No.7 "Carnarvon Day" feeder Opened on Earth fault Zone Earth, No.4 Group Earth, 11 KV trip Remarks: 11kv UG cable fault from S2466 Flemington to S8376 Carnarvon Day | January | 2014 | 2014Q3 | 2014 | ZN2466:PA7 | ZN2466:PA7 | ZN02466/000007 | PARRAMATTA | UG | Not Veg | 2014-01-14 | N | 59 | N | 4 | N | N | 1.1101 | 39.4971 | 12158.5597
[7 empty] | 15841 | 12586 | 1064632 | 2014-01-14 14:01 | 2014-01-14 15:20 | 78.9 | 11kV | 6706.5 | 85 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148916 A Phase DOLF : 20 Amp | January | 2014 | 2014Q3 | 2014 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | UG | Not Veg | 2014-01-14 | N | 78.9 | N | 4 | N | N | 1.1101 | 39.4971 | 4900.9124
[7 empty] | 15132 | 4003 | 1064650 | 2014-01-14 14:53 | 2014-01-14 15:45 | 52 | 11kV | 78468 | 1509 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12580 Erina Pa10 tripped on A phase Instantaneous Overcurrent and Timed Overload DOp removed section of tree branch from overhead in Sun Valley Rd ex S18183 See 1064655 GIS 1064654,5,81,5 Exclude 1064650,1064719 CC1: 22-"Refer to SOp" | January | 2014 | 2014Q3 | 2014 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2014-01-14 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 57342.1
[7 empty] | 15939 | 13598 | 1064990 | 2014-01-15 12:09 | 2014-01-15 13:12 | 63 | 11kV | 38292 | 660 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S3154 St Ives 11kV Panel 12 tripped on Relayds: SEF, Lockout Signals: 11kV Trip Field EFI NIL Cause: Bond burnt off AB267 See OMS 1068692 1068691 1064990 | January | 2014 | 2014Q3 | 2014 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Not Veg | 2014-01-15 | N | 58.0182 | N | 3 | N | N | 1.1101 | 39.4971 | 27982.6642
[7 empty] | 16162 | 16600 | 1065635 | 2014-01-15 16:49 | 2014-01-15 16:54 | 5 | 11kV | 1970 | 394 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 148924 fdr 82578 was rearranged on SI 37661A AND sw 50797 was closed. SW 50787 TRIPPED ON OVERLOAD 80 A SW. also refer to further outage - LID 148926 and OMS 1065174 and 1065164 | January | 2014 | 2014Q3 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-01-15 | N | 5 | N | 3 | N | N | 1.1101 | 39.4971 | 1439.6179
[7 empty] | 16249 | 17520 | 1065164 | 2014-01-15 17:05 | 2014-01-15 17:52 | 47 | 11kV | 18518 | 394 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 148926 FDR REARRANGED TO REDUCE LOAD THROUGH SW 50797 - SEE REPORT 148925 - OMS 1065635 for previous event | January | 2014 | 2014Q3 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-01-15 | N | 47 | N | 3 | N | N | 1.1101 | 39.4971 | 13532.4082
[7 empty] | 16118 | 16146 | 1065243 | 2014-01-16 02:14 | 2014-01-16 03:14 | 60 | 11kV | 140640 | 2344 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S10999 Kogarah: 11kv feeder Panel NO 36 "Buchanan Hampton" tripped Relays: IOC (50T AB) E/F, EFI, Fault Check Field EFI's: S10669, S10601, S10661, S10073, S10585, S47631, S10106 Remarks: Flashover/arcing. Dop removed Possum off UGOH on S10662 SWA side, no damage | January | 2014 | 2014Q3 | 2014 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | OH | Not Veg | 2014-01-16 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 102775.5638
[7 empty] | 16098 | 15985 | 1065246 | 2014-01-16 03:37 | 2014-01-16 04:30 | 53 | 11kV | 4293 | 81 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12610 Long Jetty section of Pa11 "Lucinda Ave" PT13060 Watson Peach Footpath HDO operated 31.5Amp DOp replaced HDO @PT13060, all supply restored. Fuse Fatigue See 1065356 exclude 1065246,8 | January | 2014 | 2014Q3 | 2014 | ZN12610:PA11 | ZN12610:PA23 | ZN12610/000023 | CENTRAL COAST | OH | Not Veg | 2014-01-16 | N | 53 | N | 8 | N | N | 1.1101 | 39.4971 | 3137.1978
[7 empty] | 14895 | 1894 | 1065249 | 2014-01-16 04:31 | 2014-01-16 06:25 | 114 | 11kV | 276285 | 2480 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S15006 Dee Why West 11kV PA16 tripped on Earth Fault with fault check Cause: 11kV feeder fault from Pa16 to S16715 and S17041 See OMS 1070820 1065249 | January | 2014 | 2014Q3 | 2014 | ZN15006:PA16 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | UG | Not Veg | 2014-01-16 | N | 111.4052 | N | 8 | N | N | 1.1101 | 39.4971 | 201900.929
[7 empty] | 15679 | 10779 | 1065251 | 2014-01-16 06:16 | 2014-01-16 07:14 | 58 | 11kV | 28362 | 489 | HV | Animal Bird | Animal | UGOH | Unplanned | No Weather Impact | N | At Sub 1850 Bass Hill Panel No.14 "AB 279" feeder Opened on Earth Fault with EFI Zone Earth, No.3 Group Earth, 11KV Trip EFI's operated @ Subs 6660, 8602, 6857, 2170, 36110, 2520, 35455, 61706, 5083, 3517, 35149 Remarks: Animals/Birds. Dead Cockatoo found @ base of HV UGOH near AB 8 2F2 | January | 2014 | 2014Q3 | 2014 | ZN1850:PA14 | ZN1850:PA45 | ZN01850/000045 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-01-16 | N | 58 | N | 8 | N | N | 1.1101 | 39.4971 | 20726.1131
[7 empty] | 15879 | 12927 | 1065324 | 2014-01-16 09:10 | 2014-01-16 10:35 | 85 | 11kV | 141552 | 2081 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14892 Charmhaven 11kv fdr Pa16 "Charmhaven San Remo" tripped, reclosed & locked out on:O/C relay 50T A&C (IOC trip)Fault check reclosing and timing lockout EFI relays Alarms: Tx2 GE EFI's nil UG fault from Zn14892 Pa16 to AB44395 te to PT11494 See 1066524,6,7 Exclude 1065324 | January | 2014 | 2014Q3 | 2014 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | UG | Not Veg | 2014-01-16 | N | 68.0211 | N | 8 | N | N | 1.1101 | 39.4971 | 103442.0265
[7 empty] | 14758 | 538 | 1065379 | 2014-01-16 10:40 | 2014-01-16 11:40 | 60 | 11kV | 540 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 148941 Fuse: 40 Amp also refer to 1065379 and 1065384 | January | 2014 | 2014Q3 | 2014 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Veg | 2014-01-16 | N | 60 | N | 8 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 16460 | 20065 | 1065555 | 2014-01-16 14:48 | 2014-01-16 16:20 | 92 | 11kV | 20924 | 241 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Sub 1285 Greenacre Park Panel No.8 "Sub 1202 etc" Opened on Earth fault, Fault check & EFI. EFIs operated @ Subs 1202, 4476 Remarks: UG fault. 11kv UG cable fault from S4476 Noble Cardigan to S4477 Tennyson Hume | January | 2014 | 2014Q3 | 2014 | ZN1285:PA8 | ZN37100:PA36 | ZN37100/000036 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-01-16 | N | 86.8216 | N | 8 | N | N | 1.1101 | 39.4971 | 15290.642
[7 empty] | 15266 | 5926 | 1065598 | 2014-01-16 15:32 | 2014-01-16 16:42 | 70 | 11kV | 22750 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Hot >35C | N | D.Op removed tree branch from 11kV OH mains near PT.15577 and link 23793. | January | 2014 | 2014Q3 | 2014 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2014-01-16 | N | 70 | N | 8 | N | N | 1.1101 | 39.4971 | 16625.029
[7 empty] | 15137 | 4040 | 1065738 | 2014-01-17 04:01 | 2014-01-17 05:11 | 70 | 11kV | 65380 | 934 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Cause not ascertained. | January | 2014 | 2014Q3 | 2014 | ZN36300:PA8 | ZN15008:PA3 | ZN15008/000003 | NORTHERN BEACHES | OH | Veg | 2014-01-17 | N | 70 | N | 2 | N | N | 1.1101 | 39.4971 | 47777.7756
[7 empty] | 15672 | 10715 | 1066091 | 2014-01-17 21:00 | 2014-01-17 22:08 | 68 | 11kV | 40154 | 605 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | 11kV panel 39 labelled S3506 abd S1816 from Chatswood Zn80 tripped on Relays: Translay, fault check, EFI Cause: Underground cable fault in feeder from S47852SW/B to S7712 Artarmon Edward SW E See OMS 1067499 1067501 1066091 | January | 2014 | 2014Q3 | 2014 | ZN80:PA39 | ZN80:PA39 | ZN00080/000039 | WILLOUGHBY | UG | Not Veg | 2014-01-17 | N | 66.3702 | N | 2 | N | N | 1.1101 | 39.4971 | 29343.3589
[7 empty] | 15750 | 11641 | 1066129 | 2014-01-18 07:36 | 2014-01-18 08:49 | 73 | 11kV | 59586 | 902 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | At S80 Chatswood Panel 25 Tripped reclosed tripped and locked out on IOC - B and C phase, EF, EFI, LO, Timer and Fault Check Cause: Crane Hit OH In Gordon Cres Lane Cove See OMS 1068676 1066129 1068678 | January | 2014 | 2014Q3 | 2014 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | OH | Not Veg | 2014-01-18 | N | 66.0599 | N | 5 | N | N | 1.1101 | 39.4971 | 43543.6913
[7 empty] | 16131 | 16286 | 1066192 | 2014-01-18 12:00 | 2014-01-18 13:55 | 115 | 11kV | 805 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148957 B phase DOLF : 10 Amp | January | 2014 | 2014Q3 | 2014 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | UG | Not Veg | 2014-01-18 | N | 115 | N | 5 | N | N | 1.1101 | 39.4971 | 588.2703
[7 empty] | 15059 | 3304 | 1066193 | 2014-01-18 13:19 | 2014-01-18 17:55 | 276 | 11kV | 516 | 7 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 148958 B Phase 11 kV dropper bunrt off at sub 70096 Excluded OMS 1066193 | January | 2014 | 2014Q3 | 2014 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2014-01-18 | N | 73.7143 | N | 5 | N | N | 1.1101 | 39.4971 | 377.0776
[7 empty] | 16394 | 19090 | 1066269 | 2014-01-18 21:20 | 2014-01-18 22:18 | 58 | 11kV | 3364 | 58 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S.15011 Beacon Hill, 11kV Panel 4 Fdr CB tripped on C phase IOC and earth fault with frame leakage and fault check. Efi, 11kV trp and zone earth. No field efi's down. Tree on mains in vicinity of zone sub | January | 2014 | 2014Q3 | 2014 | ZN15011:PA4 | ZN15011:PA6 | ZN15011/000006 | NORTHERN BEACHES | OH | Veg | 2014-01-18 | N | 58 | N | 5 | N | N | 1.1101 | 39.4971 | 2458.312
[7 empty] | 15583 | 9275 | 1066274 | 2014-01-18 22:56 | 2014-01-19 01:50 | 174 | 11kV | 348 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 148959 Live Line Loop came off pole 4M-90082. feed to 3 subs Excluded OMS 1066274 | January | 2014 | 2014Q3 | 2014 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2014-01-18 | N | 174 | N | 5 | N | N | 1.1101 | 39.4971 | 254.3081
[7 empty] | 15215 | 4877 | 1066277 | 2014-01-19 01:36 | 2014-01-19 02:47 | 71 | 11kV | 133929 | 2105 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman, Panel 41 Fdr CB tripped on earth fault, fault check, 11kV trip, #4 group earth, efi. Field efi's down at S.8299, S.4071, S.3587, S.2242, S.6762. Cable fault bretween S.6762 to S.1382 to S.4069 | January | 2014 | 2014Q3 | 2014 | ZN180:PA41 | ZN180:PA41 | ZN00180/000041 | WILLOUGHBY | UG | Not Veg | 2014-01-19 | N | 63.6242 | N | 6 | N | N | 1.1101 | 39.4971 | 97871.363
[7 empty] | 16214 | 17200 | 1066278 | 2014-01-19 02:07 | 2014-01-19 07:00 | 293 | 11kV | 1758 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148961 C phase DOLF : 10 Amp Excluded OMS 1066278 | January | 2014 | 2014Q3 | 2014 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | UG | Not Veg | 2014-01-19 | N | 293 | N | 6 | N | N | 1.1101 | 39.4971 | 1284.6945
[7 empty] | 16010 | 14723 | 1066268 | 2014-01-19 05:01 | 2014-01-19 07:00 | 119 | 11kV | 74137 | 623 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Section of 11kv Panel 11 "Ewos Waratah, etc" feeder at Zn9118 Cronulla. Interrupted mains between AB 35418 and Recloser 35005 Bundeena Liverpool Remarks: HR bond at AB35752 and recloser 35005 is defective (open). Bonded through centre phase, downrod removed to make inoperable. | January | 2014 | 2014Q3 | 2014 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2014-01-19 | N | 119 | N | 6 | N | N | 1.1101 | 39.4971 | 54177.1329
[7 empty] | 16079 | 15750 | 1066297 | 2014-01-19 07:25 | 2014-01-19 08:45 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 148963 Single phase DOLF : 10 Amp Excluded OMS 1066297 | January | 2014 | 2014Q3 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-01-19 | N | 80 | N | 6 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 15878 | 12908 | 1066353 | 2014-01-19 15:58 | 2014-01-19 16:54 | 56 | 11kV | 12384 | 225 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 148966 1 fault operation A & B phase Overcurrent No operation of Reclose by DNMS please investigate. Timed overcurrent please patrol Excluded OMS 1066353 | January | 2014 | 2014Q3 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-01-19 | N | 55.04 | N | 6 | N | N | 1.1101 | 39.4971 | 9049.8619
[7 empty] | 15456 | 7984 | 1066395 | 2014-01-19 22:38 | 2014-01-19 23:43 | 65 | 11kV | 41665 | 641 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | @Zone 9037 Miranda Panel 7 "Princess Garnet" fdr tripped on: Relays - A & C phase IOC and EFI Signals - zone earth, Tx 1 group earth and 11kv trip Field EFI's - S9938, S9235, S9130, S9125 Remarks: animals/birds. Dop found possum on the UGOH beyond S9125 Bates Box | January | 2014 | 2014Q3 | 2014 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2014-01-19 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 30447.5531
[7 empty] | 15358 | 6905 | 1071239 | 2014-01-20 06:41 | 2014-01-20 07:05 | 24 | 11kV | 2184 | 91 | HV | Staff Operation | Utility Process Issue | Circuit Breaker | Unplanned | No Weather Impact | N | At S2635 Epping 11kV feeder panel 51 tripped on SEL Abnormal Switching: Routine Switching at time of interruption SW/B Closed at S5465, SW/A Open at S3740 SW/B Closed at S35124, SW/A Open at S35125 Cause: Incorrect protection set up for switching by Field staff | January | 2014 | 2014Q3 | 2014 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | Unknown | Not Veg | 2014-01-20 | N | 24 | N | 6 | N | N | 1.1101 | 39.4971 | 1596.0028
[7 empty] | 14935 | 2148 | 1066729 | 2014-01-20 11:56 | 2014-01-20 13:20 | 84 | 11kV | 252 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 148975 C phase DOLF : 10 Amp excluded OMS 1066729 | January | 2014 | 2014Q3 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | UG | Not Veg | 2014-01-20 | N | 84 | N | 6 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 16008 | 14713 | 1066481 | 2014-01-20 09:05 | 2014-01-20 17:25 | 500 | 11kV | 500 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 148976 Single phase DOLF : 5 Amp DOLF Burned up. Fuse replaced, Sub retrofitted. Excluded OMS 1066481 & 1066549 | January | 2014 | 2014Q3 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2014-01-20 | N | 500 | N | 6 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 16315 | 18145 | 1066924 | 2014-01-20 16:14 | 2014-01-20 17:27 | 73 | 11kV | 135488 | 1856 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | @Zn35900 Potts Hill 11kv VCB panel 4 "S-4379 Dasea Rook" feeder tripped on - Relays - O/C earth fault, 50 TB, EFI, EFC. Field EFI's - nil Signals: 11kv trip Remarks: Tree/branch on OH mains. Tree branch on 11kv O/H o/s 269 Cooper St | January | 2014 | 2014Q3 | 2014 | ZN35900:PA4 | ZN35900:PA4 | ZN35900/000004 | CANTERBURY-BANKSTOWN | OH | Veg | 2014-01-20 | N | 73 | N | 6 | N | N | 1.1101 | 39.4971 | 99010.6342
[7 empty] | 15258 | 5781 | 1066979 | 2014-01-20 17:47 | 2014-01-20 18:34 | 47 | 11kV | 104558 | 2344 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | ZN 10999 Kogarah - Pnl 36 - Earth Fault, Earth Fault Check, EFI, Field EFIs. UGOH surge arrestor blown at UGOH on corner of Garfield and Hampton intersection of mains between S 10601, S 10661 and USL 30584. ME: 1067853. Rest Step: 1067855. Withdrawn: 1066979, 85, 93, 1067060. | January | 2014 | 2014Q3 | 2014 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | OH | Not Veg | 2014-01-20 | N | 44.6067 | N | 6 | N | N | 1.1101 | 39.4971 | 76407.9025
[7 empty] | 15495 | 8417 | 1067111 | 2014-01-20 23:21 | 2014-01-21 00:02 | 41 | 11kV | 36449 | 889 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn3154 St Ives Pa17 tripped on Relays: Cphase timed overcurrent, EFI, Timing relay, Lockout relay ABNORMAL: S5389:B, Open and defective S8273:A to S35027:B Tree branch on HV Mains Adjacent LB2591 See 1067348 Exclude 1067111,41,3 | January | 2014 | 2014Q3 | 2014 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2014-01-20 | N | 41 | N | 6 | N | N | 1.1101 | 39.4971 | 26635.8541
[7 empty] | 15809 | 12211 | 1067167 | 2014-01-21 01:53 | 2014-01-21 05:06 | 193 | 11kV | 243527 | 1439 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Recloser CP3228 Berowra Pump ex Pa21 from Zn2400 Berowra Tripped and locked out Abnormal switching: LB473 Closed Ab2295 Open LB62158 Closed CP349 Open Cause: Patrolled and restored see OMS 1071375 1071376 1067167 1067168 | January | 2014 | 2014Q3 | 2014 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Veg | 2014-01-21 | N | 169.2335 | N | 4 | N | N | 1.1101 | 39.4971 | 177962.3488
[7 empty] | 15936 | 13484 | 1067578 | 2014-01-21 13:10 | 2014-01-21 14:00 | 50 | 11kV | 2200 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 AB40934 Interrupted by DOp. Bamboo touching HV conductors near AB44137 See 1068047 exclude 1067578 | January | 2014 | 2014Q3 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2014-01-21 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 1607.6951
[7 empty] | 15066 | 3381 | 1067660 | 2014-01-21 16:45 | 2014-01-21 19:15 | 150 | 11kV | 1350 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn 12630 Peats Ridge section of Pa4 @USL 44962 Opened by DOp for emergency repairs to 11kv CCT cable Tree branch on OH Mains | January | 2014 | 2014Q3 | 2014 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2014-01-21 | N | 150 | N | 4 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 16446 | 19909 | 1067727 | 2014-01-21 19:51 | 2014-01-21 23:24 | 213 | 11kV | 57675 | 321 | HV | Animal Other | Animal | Pole | Unplanned | Unselected | N | LID 148995 Appears cow has rubbed on stay wire. Stay wire has broken and burned down a phase between LLC and 70724 Wendouree. Excluded OMS 1067727 | January | 2014 | 2014Q3 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-01-21 | N | 179.6729 | N | 4 | N | N | 1.1101 | 39.4971 | 42147.1889
[7 empty] | 15833 | 12470 | 1067861 | 2014-01-22 08:59 | 2014-01-22 09:39 | 40 | 11kV | 15680 | 392 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN 9252 Jannali - Section of Pnl 2 - AB 35850 Roadside bond open circuit. @ AB 35850 roadside loadside bond burnt off. ME: 1068327. Withdrawn: 1067862, 3. | January | 2014 | 2014Q3 | 2014 | ZN9252:PA2 | ZN9252:PA27 | ZN09252/000027 | SUTHERLAND | OH | Not Veg | 2014-01-22 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 11458.4815
[7 empty] | 16359 | 18656 | 1067933 | 2014-01-22 10:16 | 2014-01-22 16:40 | 384 | 11kV | 50603 | 201 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 149001 3 fault operations Sensitive Earth Fault, Earth Fault HV wires down near pole 8N-20033. HV in contact with LV. | January | 2014 | 2014Q3 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-01-22 | N | 251.7562 | N | 3 | N | N | 1.1101 | 39.4971 | 36979.1799
[7 empty] | 15921 | 13329 | 1068227 | 2014-01-22 18:13 | 2014-01-22 20:00 | 106.9667 | 11kV | 1604.5 | 15 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149009 B phase DOLF Tail below LF 74232 burned off. | January | 2014 | 2014Q3 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2014-01-22 | N | 106.9667 | N | 3 | N | N | 1.1101 | 39.4971 | 1172.5213
[7 empty] | 15453 | 7966 | 1068292 | 2014-01-23 07:21 | 2014-01-23 09:50 | 149 | 11kV | 1192 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | 11KV HDO 10amp fuse centre phase blown @ PT13181 Manns Station Remarks: Fuse failure | January | 2014 | 2014Q3 | 2014 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Not Veg | 2014-01-23 | N | 149 | N | 3 | N | N | 1.1101 | 39.4971 | 871.0784
[7 empty] | 15310 | 6525 | 1068465 | 2014-01-23 11:09 | 2014-01-23 15:02 | 233.2 | 11kV | 138317.4 | 1331 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | ZN.3425 Castle Cove Zone - Section of Pa.15 - Relay Earth Fault. Abnormal - S.49051 SW/B Chiltern Frenchs Closed - S.4069 SW/B Tenilba Eastern Valley Open. Cause:- 11kV mains dug up at 50 Mowbray Rd. by external contractor between S.2055 Warners Ave & S.46452 Mowbray Alpha. ME - 1070483 Excluded - 1068467, 1068495, 1068504 & 1068465 | January | 2014 | 2014Q3 | 2014 | ZN3425:PA15 | ZN3425:PA15 | ZN03425/000015 | WILLOUGHBY | UG | Not Veg | 2014-01-23 | N | 103.9199 | N | 3 | N | N | 1.1101 | 39.4971 | 101078.2762
[7 empty] | 14967 | 2467 | 1068650 | 2014-01-23 14:14 | 2014-01-23 16:33 | 139 | 11kV | 106855 | 853 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S5868 Gore Hill Panel 6 tripped on B phase overcurrent, Fault Check and EFI. Cause: Suspect UG fault between S5632 to S3454 See OMS 1071154 1071158 1068650 | January | 2014 | 2014Q3 | 2014 | ZN5868:PA6 | ZN5868:PA6 | ZN05868/000006 | WILLOUGHBY | UG | Not Veg | 2014-01-23 | N | 125.2696 | N | 3 | N | N | 1.1101 | 39.4971 | 78086.4823
[7 empty] | 15549 | 8925 | 1068997 | 2014-01-24 12:10 | 2014-01-24 16:50 | 280 | 11kV | 280 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149032 A phase DOLF : 16 Amp Replace blown arrestors Excluded OMS 1068997 | January | 2014 | 2014Q3 | 2014 | 803:74007 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Not Veg | 2014-01-24 | N | 280 | N | 3 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 14812 | 1056 | 1069155 | 2014-01-24 20:46 | 2014-01-24 21:23 | 36.7667 | 11kV | 23383.6 | 636 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | ZN 9037 Miranda - Pnl 7 - A phase IOC, EFI, Field EFIs. Suspect UGOH fault between S 9125 and AB 35626. ME: 1069155. Withdrawn: 1069159. | January | 2014 | 2014Q3 | 2014 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | Unknown | Unknown | 2014-01-24 | N | 36.7667 | N | 3 | N | N | 1.1101 | 39.4971 | 17088.0452
[7 empty] | 14831 | 1260 | 1069202 | 2014-01-25 00:24 | 2014-01-25 01:45 | 81 | 11kV | 324 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | N | LID 149039 B phase DOLF : 10 Amp Excluded OMS 1069202 & 1069203 | January | 2014 | 2014Q3 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | UG | Not Veg | 2014-01-25 | N | 81 | N | 6 | N | N | 1.1101 | 39.4971 | 236.7696
[7 empty] | 15449 | 7928 | 1069248 | 2014-01-25 09:08 | 2014-01-25 09:50 | 42 | 11kV | 25872 | 616 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 10997 Sans Souci - Pnl 11 - Trip/reclose/trip, IOC, timing, lockout, EFI. Magpie on 11kV bare conductor on cross arm at top of HDOs at PT 10327. Design fault where 2 phases cross. ME: 1069695. Withdrawn: 1069248, 53. | January | 2014 | 2014Q3 | 2014 | ZN10997:PA11 | ZN10997:PA11 | ZN10997/000011 | GEORGES RIVER | OH | Not Veg | 2014-01-25 | N | 42 | N | 6 | N | N | 1.1101 | 39.4971 | 18906.4945
[7 empty] | 15555 | 8974 | 1069264 | 2014-01-25 10:28 | 2014-01-25 10:40 | 12 | 11kV | 936 | 78 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Section of Panel #13 @ S12640 Umina recloser 47746 Patonga Meroo was opened for safety to try & remove seagull tangled in 11kv feeder Remarks: Animals/Birds. Second attempt to remove Bird from HV feeder in water 20 metres of water offshore line in Patonga Creek. Unsuccessful left to the gods. | January | 2014 | 2014Q3 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2014-01-25 | N | 12 | N | 6 | N | N | 1.1101 | 39.4971 | 684.0012
[7 empty] | 15896 | 13143 | 1069153 | 2014-01-24 22:45 | 2014-01-25 11:50 | 785 | 11kV | 1570 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Previous Storm | N | LID 149044 & 149045 3 phase DOLF : 10 Amp TRANSFORMER REPLACED DUE TO LIGHTENING STRIKE. 3 PHASE CUSTOMER LEFT OFF DUE TO FAULT IN PRIVATE MAINS WITHIN CONDUIT. TX REPLACED DUE TO LIGHTENING STRIKE. 3 PHASE CUSTOMER LEFT OFF DUE TO FAULT IN PRIVATE MAINS. Excluded OMS 1069153. | January | 2014 | 2014Q3 | 2014 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | UG | Not Veg | 2014-01-24 | N | 785 | N | 3 | N | N | 1.1101 | 39.4971 | 1147.3097
[7 empty] | 14832 | 1264 | 1069246 | 2014-01-25 11:30 | 2014-01-25 13:00 | 90 | 11kV | 90 | 1 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 149046 Single phase DOLF : 10 Amp cockatoo on tx | January | 2014 | 2014Q3 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-01-25 | N | 90 | N | 6 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 15474 | 8183 | 1069368 | 2014-01-25 16:34 | 2014-01-25 17:40 | 66.1833 | 11kV | 1456.0333 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149050 A & B phase DOLF : 15 Amp | January | 2014 | 2014Q3 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2014-01-25 | N | 66.1833 | N | 6 | N | N | 1.1101 | 39.4971 | 1064.0262
[7 empty] | 15937 | 13549 | 1069326 | 2014-01-25 14:32 | 2014-01-25 23:10 | 518 | 11kV | 513128.4833 | 2372 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | ZN 10995 Riverwood - Pnl 2 - Trip/reclose/trip, A & C phase IOC, EFI. 33kV Fdr 768 fell into 11kV feeder near AB 31285 causing HDOs and arrestor failure at PT 10275, PT 10850 and PT 62474 on centre phase in each case. Centre phase arrestor has been cut away at PT 10850. Tcon to repair. - refer to 1069765 for subtrans record ME: 1069980. Rest Steps: 1069981 3, 4, 5, 6. Withdrawn: Various. | January | 2014 | 2014Q3 | 2014 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2014-01-25 | N | 216.3274 | N | 6 | N | N | 1.1101 | 39.4971 | 374979.1609
[7 empty] | 14697 | 22 | 1069446 | 2014-01-26 07:54 | 2014-01-26 11:20 | 206 | 11kV | 824 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149052 Single phase HV DROPPER LEAD BURNT OFF TOP OFF DOLF. Excluded OMS 1069437 | January | 2014 | 2014Q3 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-01-26 | N | 206 | N | 2 | N | N | 1.1101 | 39.4971 | 602.1549
[7 empty] | 15891 | 13079 | 1069473 | 2014-01-26 13:18 | 2014-01-26 17:20 | 242 | 11kV | 3872 | 16 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At S7071 Jabez Denby B Phase 11kv fuse #2 RMI 75 Alel OEFMA OFF Panel 20 Smith Victoria feeder @ Marrickville Remarks: Tx Failure. B phase 11kv fuse blew on reenergisation #2 Tx emitted loud growl, Dop reports Tx will require changing; and RMI requires overhaul oil very black. | January | 2014 | 2014Q3 | 2014 | ZN262:PA20 | ZN262:PA20 | ZN00262/000020 | INNER WEST | UG | Not Veg | 2014-01-26 | N | 242 | N | 2 | N | N | 1.1101 | 39.4971 | 2829.5434
[7 empty] | 15039 | 3111 | 1069593 | 2014-01-27 17:51 | 2014-01-27 19:35 | 103.8833 | 11kV | 5090.2833 | 49 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149053 C phase DOLF : 31 Amp Fuse Fatigue | January | 2014 | 2014Q3 | 2014 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2014-01-27 | N | 103.8833 | N | 1 | N | N | 1.1101 | 39.4971 | 3719.8289
[7 empty] | 14696 | 20 | 1069630 | 2014-01-28 00:41 | 2014-01-28 02:45 | 124 | 11kV | 36704 | 296 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex ZN 9118 Cronulla - Pnl 11 - AB 35753. Footpath side bond burnt off. ME: 1069688. WIthdrawn: 1069630, 1. | January | 2014 | 2014Q3 | 2014 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2014-01-28 | N | 124 | N | 7 | N | N | 1.1101 | 39.4971 | 26822.2006
[7 empty] | 15503 | 8479 | 1069635 | 2014-01-28 04:04 | 2014-01-28 06:00 | 116 | 11kV | 8700 | 75 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 149059 C phase DOLF : 40 Amp Possum Excluded OMS 1069635 | January | 2014 | 2014Q3 | 2014 | 206:34441 | 206:34441 | ZN00206/034441 | LAKE MACQUARIE | OH | Not Veg | 2014-01-28 | N | 116 | N | 7 | N | N | 1.1101 | 39.4971 | 6357.7034
[7 empty] | 15820 | 12336 | 1069965 | 2014-01-28 14:27 | 2014-01-28 19:25 | 298 | 11kV | 596 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn13000 Lake Munmorah section of Pa5 @PT14435 Pacific Wentworth 1.0 Centre Phase HDO assembly failure See 1070277 exclude 1069965 | January | 2014 | 2014Q3 | 2014 | ZN13000:PA5 | ZN13000:PA5 | ZN13000/000005 | CENTRAL COAST | OH | Not Veg | 2014-01-28 | N | 298 | N | 7 | N | N | 1.1101 | 39.4971 | 435.5392
[7 empty] | 16371 | 18751 | 1070049 | 2014-01-28 17:00 | 2014-01-28 19:25 | 145 | 11kV | 16965 | 117 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | Unselected | N | PT 10201 Alston Laycock - Footpath phase HDO operated (50K). Incorrectly loaded HV fuses. The other 2 phases have heat damage and will require replacement by T/Con. ME: 1070160. Withdrawn: 1070049. | January | 2014 | 2014Q3 | 2014 | ZN10999:PA10 | ZN10999:PA10 | ZN10999/000010 | BAYSIDE | OH | Not Veg | 2014-01-28 | N | 145 | N | 7 | N | N | 1.1101 | 39.4971 | 12397.5216
[7 empty] | 16274 | 17705 | 1070110 | 2014-01-28 20:32 | 2014-01-28 21:07 | 35 | 11kV | 73850 | 2110 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12750 Avoca 11kv fdr Pa37 "Avoca Beach" fdr tripped Relays: B phase overcurrent. A and B phase IOC Field EFI's Nil Tre branch removed by DOp adjacent AB43305. DOp reports PT12505 Walder Fitzgibbon C phase HDO assembly to be inspected in daylight. See 1070110 exclude 1070111,2 | January | 2014 | 2014Q3 | 2014 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2014-01-28 | N | 35 | N | 7 | N | N | 1.1101 | 39.4971 | 53967.4018
[7 empty] | 15380 | 7199 | 1070091 | 2014-01-28 20:48 | 2014-01-28 21:52 | 64 | 11kV | 16896 | 264 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | @ELB61085 opened 20:48 on advice from Linesmen interrupted for safety @Zn12630 Peats Ridge Pa3 "mangrove mountain" opened 21:53 on advice from DOp interrupted for safety Suspected broken crossarm pin caused overhead mains to clash. Bushfire brunt mains in section of 11kv fdr from LK44115 to B44253 to ELB61085 tee PT14038 See 1070306,19,20,1,2,3,5 Exclude 1070116,36 | January | 2014 | 2014Q3 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-01-28 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 12347.0985
[7 empty] | 16470 | 20163 | 1070136 | 2014-01-28 21:53 | 2014-01-28 23:04 | 71 | 11kV | 22905 | 422 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | @ELB61085 opened 20:48 on advice from Linesmen interrupted for safety @Zn12630 Peats Ridge Pa3 "mangrove mountain" opened 21:53 on advice from DOp interrupted for safety Suspected broken crossarm pin caused overhead mains to clash. Bushfire brunt mains in section of 11kv fdr from LK44115 to B44253 to ELB61085 tee PT14038 See 1070306,19,20,1,2,3,5 Exclude 1070116,36 | January | 2014 | 2014Q3 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-01-28 | N | 54.2773 | N | 7 | N | N | 1.1101 | 39.4971 | 16738.2984
[7 empty] | 16322 | 18230 | 1070143 | 2014-01-29 06:20 | 2014-01-29 08:40 | 140 | 11kV | 140 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | N | LID 149078 B phase DOLF : 20 Amp Excluded OMS 1070143 | January | 2014 | 2014Q3 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | UG | Not Veg | 2014-01-29 | N | 140 | N | 6 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 15440 | 7876 | 1070166 | 2014-01-29 07:57 | 2014-01-29 09:04 | 67 | 11kV | 66665 | 995 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | ZN 9245 Engadine - Pnl 15 - Trip/reclose/trip, A & C phase IOC, sealing contactor, Lockout, EFI, Field EFI. S 9069 Railway Old Princes Sw/B 11kV endbox failed. ME: 1070964. Withdrawn: 1070166, 1070180. | January | 2014 | 2014Q3 | 2014 | ZN9245:PA15 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | Unknown | Not Veg | 2014-01-29 | N | 67 | N | 6 | N | N | 1.1101 | 39.4971 | 48716.8157
[7 empty] | 15304 | 6474 | 1070238 | 2014-01-29 09:17 | 2014-01-29 10:02 | 45 | 11kV | 42345 | 941 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14892 Charmhaven section of Pa13 RE61133 Minnamurra Tosca tripped on overcurrent SEF Cause not ascertained. Patrolled fdr no cause found See 1070716 exclude 1070238 | January | 2014 | 2014Q3 | 2014 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Veg | 2014-01-29 | N | 45 | N | 6 | N | N | 1.1101 | 39.4971 | 30944.477
[7 empty] | 15335 | 6693 | 1070145 | 2014-01-29 06:45 | 2014-01-29 10:30 | 225 | 11kV | 1575 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149083 C phase DOLF : 20 Amp Excluded OMS 1070145 | January | 2014 | 2014Q3 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-01-29 | N | 225 | N | 6 | N | N | 1.1101 | 39.4971 | 1150.9635
[7 empty] | 14774 | 666 | 1070314 | 2014-01-29 10:37 | 2014-01-29 14:40 | 243 | 11kV | 972 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 149093 C phase DOLF : 16 Amp DOLF Carrier Burnt-up. Excluded OMS# 1070314. | January | 2014 | 2014Q3 | 2014 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2014-01-29 | N | 243 | N | 6 | N | N | 1.1101 | 39.4971 | 710.3089
[7 empty] | 15738 | 11475 | 1070608 | 2014-01-29 18:14 | 2014-01-29 20:25 | 131.3167 | 11kV | 12081.1333 | 92 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Hot >35C | N | LID 149095 3 phase isolation Xarm pole 5M-50067 failed | January | 2014 | 2014Q3 | 2014 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Not Veg | 2014-01-29 | N | 131.3167 | N | 6 | N | N | 1.1101 | 39.4971 | 8828.5359
[7 empty] | 15224 | 5042 | 1071399 | 2014-01-30 15:54 | 2014-01-30 16:41 | 47 | 11kV | 37297 | 941 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14892 Charmhaven section of pa13 @IR61133 "Minnamurra Tosca" tripped on SEF overcurrent Cause not ascertained T/PE to investivate spurious tripping Also tripped at 29/1/14 09:17 See 1071399,400 exclude 1070952 | January | 2014 | 2014Q3 | 2014 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Veg | 2014-01-30 | N | 39.6355 | N | 3 | N | N | 1.1101 | 39.4971 | 27255.5475
[7 empty] | 15770 | 11808 | 1071041 | 2014-01-30 18:08 | 2014-01-30 20:21 | 133 | 11kV | 167320.8167 | 1720 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S195 Pymble Panel 9 Tripped on A phase timed O/C Cause: Dop removed tree branch from mains adj AB3023. Abnormal Switching: LB62189 Open SW at S48186 Closed 1071416/418/419/420 See OMS 1071041 1071043 | January | 2014 | 2014Q3 | 2014 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | OH | Veg | 2014-01-30 | N | 97.2795 | N | 3 | N | N | 1.1101 | 39.4971 | 122273.1177
[7 empty] | 16210 | 17128 | 1071097 | 2014-01-30 23:12 | 2014-01-31 00:25 | 73 | 11kV | 37940 | 830 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9118 Cronulla - Pnl 3 - Trip/reclose/trip, Earth fault, timing, lockout and EFI. Suspect front line feeder fault. ME: 1071149. Rest Step: 1071150. Withdrawn: 1071097. | January | 2014 | 2014Q3 | 2014 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | UG | Not Veg | 2014-01-30 | N | 45.7108 | N | 3 | N | N | 1.1101 | 39.4971 | 27725.433
[7 empty] | 14766 | 571 | 1071144 | 2014-01-31 08:19 | 2014-01-31 09:25 | 66.0667 | 11kV | 1849.8667 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149113 A phase DOLF : 40 Amp CC1: 06-"Urgent - O.H Mains - No others" | January | 2014 | 2014Q3 | 2014 | 513:48057 | 513:83497 | ZN00513/083497 | SINGLETON | UG | Not Veg | 2014-01-31 | N | 66.0667 | N | 4 | N | N | 1.1101 | 39.4971 | 1351.828
[7 empty] | 16288 | 17879 | 1071429 | 2014-01-31 15:19 | 2014-01-31 15:27 | 8 | 11kV | 7536 | 942 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Zn14892 Charmhaven section of Pa13 IR61133 Minnamurra Tosca opened on overcurrent & sensitive earht fault SCADA telecontrol defective. 3rd time in 3 days. no cause found See 1072002 exclude 1071429 | January | 2014 | 2014Q3 | 2014 | ZN14892:PA13 | ZN14892:PA13 | ZN14892/000013 | CENTRAL COAST | OH | Not Veg | 2014-01-31 | N | 8 | N | 4 | N | N | 1.1101 | 39.4971 | 5507.0865
[7 empty] | 16072 | 15647 | 1071377 | 2014-01-31 14:08 | 2014-01-31 15:41 | 93 | 11kV | 196695 | 2115 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn15001 Brookvale Pa18 left side "Pine Pittwater" fdr tripped on Relay: #50 TBC Relay, timing relay, lockout, 11kv trip outside 37 Alfred St Narraweena Large Branch on feeder | January | 2014 | 2014Q3 | 2014 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Veg | 2014-01-31 | N | 93 | N | 4 | N | N | 1.1101 | 39.4971 | 143738.9045
[7 empty] | 15055 | 3283 | 1072088 | 2014-01-31 08:00 | 2014-01-31 19:15 | 675 | 11kV | 675 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 149132 Single phase DOLF : 10 Amp TX 62413 UPGRADED ON SI 37260,TX FAULTY & HAD TO BE CHANGED AGAIN. | January | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2014-01-31 | N | 675 | N | 4 | N | N | 1.1101 | 39.4971 | 493.2701
[7 empty] | 16235 | 17429 | 1071565 | 2014-02-01 08:37 | 2014-02-01 10:30 | 113 | 11kV | 113 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149136 Single phase DOLF : 10 Amp | February | 2014 | 2014Q3 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2014-02-01 | N | 113 | N | 5 | N | N | 1.1101 | 39.4971 | 82.5771
[7 empty] | 15736 | 11437 | 1071586 | 2014-02-01 09:56 | 2014-02-01 12:05 | 129 | 11kV | 129 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149138 A phase DOLF : 10 Amp Excluded OMS 1071586 | February | 2014 | 2014Q3 | 2014 | 242:81533 | 232:11460 | ZN00232/011460 | PORT STEPHENS | OH | Veg | 2014-02-01 | N | 129 | N | 5 | N | N | 1.1101 | 39.4971 | 94.2694
[7 empty] | 16463 | 20105 | 1071603 | 2014-02-01 11:40 | 2014-02-01 13:00 | 80 | 11kV | 80 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149140 C phase DOLF : 31 Amp Fuse carrier burnt in half. Tx Volts 235/235/234 No Load. Customer on gen. | February | 2014 | 2014Q3 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2014-02-01 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 14853 | 1420 | 1071680 | 2014-02-01 20:59 | 2014-02-01 22:16 | 77 | 11kV | 308 | 4 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149146 sub isolated to replace faulty LL Clamp Excluded OMS 1071680 | February | 2014 | 2014Q3 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-02-01 | N | 77 | N | 5 | N | N | 1.1101 | 39.4971 | 225.0773
[7 empty] | 15210 | 4727 | 1071685 | 2014-02-01 21:44 | 2014-02-01 23:45 | 121 | 11kV | 57337 | 507 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 10990 Arncliffe - Pnl 12 - Trip/reclose/trip, C phase IOC and Timed OC, Reclose timing, lockout, EFI. Suspect UG fault in section of 11kV feeder from S 10058 to S 10036 to AB 31051. ME: 1072626. Rest Steps: 1072630, 2, 6. Withdrawn: 1071685. | February | 2014 | 2014Q3 | 2014 | ZN10990:PA12 | ZN10998:PA9 | ZN10998/000009 | BAYSIDE | UG | Not Veg | 2014-02-01 | N | 113.0907 | N | 5 | N | N | 1.1101 | 39.4971 | 41900.1884
[7 empty] | 15364 | 6966 | 1071694 | 2014-02-02 05:38 | 2014-02-02 11:34 | 355.3 | 11kV | 8717.35 | 55 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149148 B phase DOLF : 63 Amp fuse fatigue Excluded OMS 1071711 & 1071723 | February | 2014 | 2014Q3 | 2014 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2014-02-02 | N | 158.4973 | N | 2 | N | N | 1.1101 | 39.4971 | 6370.3823
[7 empty] | 16067 | 15604 | 1071746 | 2014-02-02 11:42 | 2014-02-02 13:03 | 81 | 11kV | 18225 | 225 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale section of fdr pa3 RE41630 Keren Bundilla tripped, reclosed, tripped & locked out on Overcurrent Patrolled by DOp. All Clear. Cause not ascertained See 1071746 GIS 1071752 Exclude 1071747 | February | 2014 | 2014Q3 | 2014 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Veg | 2014-02-02 | N | 81 | N | 2 | N | N | 1.1101 | 39.4971 | 13318.2925
[7 empty] | 15351 | 6814 | 1071864 | 2014-02-03 08:52 | 2014-02-03 10:55 | 123 | 11kV | 2582.0833 | 21 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S.6362 Missenden Carillon - 11kV/415V No2 transformer defective - No fuses blown Transformer failure causing low volts - dist #2 supplied from this side of LV bus See 1072396 GIS: 1071864 | February | 2014 | 2014Q3 | 2014 | ZN2568:PA6 | ZN2568:PA27 | ZN02568/000027 | SYDNEY | UG | Not Veg | 2014-02-03 | N | 122.9563 | N | 5 | N | N | 1.1101 | 39.4971 | 1886.9103
[7 empty] | 16232 | 17396 | 1072006 | 2014-02-03 11:43 | 2014-02-03 12:51 | 68 | 11kV | 93135 | 1594 | HV | Excavation Ausgrid Staff | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At S80 Chatswood Zn Panel 37 tripped on OC and Earth Fault With EFI and Fault Check Cause: Pole crew boring to stand new pole hit feeder. See OMS 1073744 1073746 1072006 | February | 2014 | 2014Q3 | 2014 | ZN80:PA37 | ZN80:PA37 | ZN00080/000037 | LANE COVE | UG | Not Veg | 2014-02-03 | N | 58.4285 | N | 5 | N | N | 1.1101 | 39.4971 | 68060.311
[7 empty] | 15890 | 13066 | 1072189 | 2014-02-03 15:42 | 2014-02-03 17:40 | 118 | 11kV | 118 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149156 B phase DOLF : 16 Amp Fuse Fatigue Excluded OMS 1072189 | February | 2014 | 2014Q3 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-02-03 | N | 118 | N | 5 | N | N | 1.1101 | 39.4971 | 86.2309
[7 empty] | 15779 | 11903 | 1072259 | 2014-02-03 19:35 | 2014-02-03 20:32 | 57 | 11kV | 1254 | 22 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex 11kv Panel No.38 "Sub 5076, AB 893" feeder from ZN 2310 Punchbowl @ Sub 1182 Cooeeyana Pde - 11kv ABB 80 Amp Road & centre phase Drop out fuses operated @ Zn 2310 Punchbowl - EFI on Panel No.38 Remarks: Animals/Birds. Bird contacted 11kv Mains under HVDO fuses | February | 2014 | 2014Q3 | 2014 | ZN2310:PA38 | ZN35800:PA15 | ZN35800/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-02-03 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 916.3862
[7 empty] | 15115 | 3871 | 1072276 | 2014-02-03 21:12 | 2014-02-03 22:30 | 78 | 11kV | 78 | 1 | HV | Animal Other | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 149158 A phase DOLF : 31 Amp Dead Rats found Excluded OMS 1072276 | February | 2014 | 2014Q3 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2014-02-03 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 15566 | 9085 | 1072301 | 2014-02-04 07:48 | 2014-02-04 11:06 | 198 | 11kV | 990 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149170 C phase DOLF : 10 Amp Excluded OMS 1072301 | February | 2014 | 2014Q3 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | UG | Not Veg | 2014-02-04 | N | 198 | N | 9 | N | N | 1.1101 | 39.4971 | 723.4628
[7 empty] | 15599 | 9557 | 1072566 | 2014-02-04 12:31 | 2014-02-04 13:49 | 78 | 11kV | 4824 | 62 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | 11KV Panel #45 labelled "S.8189 Derbyshire William" @ ZN.116 Leichardt tripped on: Relays: Spag relay 140C - L3 No.4 trip & EFI Signals: 11kv trip, Zone earth & No.3 Group earth 33kV Tx.3 Group Earth, 33kV Zone Earth, 11KV trip Field EFI's S.8189 Remarks: UG fault. 11kv UG fault from Sub 8189 Derbyshire William to Sub 35867 Derbyshire William No.2 | February | 2014 | 2014Q3 | 2014 | ZN116:PA45 | ZN116:PA1 | ZN00116/000001 | INNER WEST | UG | Not Veg | 2014-02-04 | N | 77.8065 | N | 9 | N | N | 1.1101 | 39.4971 | 3525.2369
[7 empty] | 16378 | 18822 | 1072652 | 2014-02-04 14:37 | 2014-02-04 15:10 | 33 | 11kV | 7798 | 598 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12690 Berkeley Vale Pa3 fdr tripped and reclosed Bph time overcurrent & Earth Fault Relay - EFI, Lockout Recloser RE Keren Bundilla Tripped DOp removed branch adjacent to AB44498 See 1072967,8 GIS 1072668 Exclude 1072652,89,91,2,4 | February | 2014 | 2014Q3 | 2014 | ZN12690:PA3 | ZN12690:PA3 | ZN12690/000003 | CENTRAL COAST | OH | Veg | 2014-02-04 | N | 13.0401 | N | 9 | N | N | 1.1101 | 39.4971 | 5698.5484
[7 empty] | 15865 | 12821 | 1072737 | 2014-02-04 15:47 | 2014-02-04 16:59 | 72 | 11kV | 5616 | 78 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | ExZn12690 Berkely Vale section of Pa24L "Glenning Vale" fdr Recloser 45117 Glenning Valley tripped and reclosed and tripped and locked out Tree branch removed by DOp adjacent to LB44745 CC1: 22-"Refer to SOp" | February | 2014 | 2014Q3 | 2014 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2014-02-04 | N | 72 | N | 9 | N | N | 1.1101 | 39.4971 | 4104.0072
[7 empty] | 16279 | 17788 | 1072785 | 2014-02-04 15:14 | 2014-02-04 17:25 | 131 | 11kV | 1179 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 149181 Single phase DOLF Fuse saver 63369 was found to have one phase open. It had been moved to a new location today, where Links 40661 used to be . SI 40302. New system number has not been fitted to fuse saver. Excluded OMS 1072785 & 1072803 | February | 2014 | 2014Q3 | 2014 | 523:33501 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-02-04 | N | 131 | N | 9 | N | N | 1.1101 | 39.4971 | 861.5784
[7 empty] | 16044 | 15321 | 1072815 | 2014-02-04 17:16 | 2014-02-04 17:42 | 26 | 11kV | 38324 | 1474 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12658 West Gosford section of Pa1 "Dog Trap Rd" fdr RE44936 Bentley rd tripped & reclosed & tripped & Locked out Dop removed tree branch Adjacent AB44473 in Allan st See 1072807 exclude 1072808,15,7,8,9,24,7,8 | February | 2014 | 2014Q3 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-02-04 | N | 26 | N | 9 | N | N | 1.1101 | 39.4971 | 28006.0488
[7 empty] | 14936 | 2150 | 1072837 | 2014-02-04 17:51 | 2014-02-04 19:11 | 80 | 11kV | 26000 | 325 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 22381 tripped , reclosed and locked out - tree branch on 11kV OH adjacent to PT.15577 | February | 2014 | 2014Q3 | 2014 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2014-02-04 | N | 80 | N | 9 | N | N | 1.1101 | 39.4971 | 19000.0331
[7 empty] | 16302 | 18042 | 1072685 | 2014-02-04 14:53 | 2014-02-04 19:55 | 302 | 11kV | 132340 | 1635 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Zn12620 Noraville Pa11 Norah Head fdr tripped on sensitive Earth Fault 11kv trip OH down. Section of 11kv repaired by mains See 1073081,4 Exclude 1072685 | February | 2014 | 2014Q3 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2014-02-04 | N | 80.9419 | N | 9 | N | N | 1.1101 | 39.4971 | 96710.1686
[7 empty] | 16047 | 15383 | 1072896 | 2014-02-04 22:59 | 2014-02-05 00:15 | 76 | 11kV | 3724 | 49 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 149186 A phase DOLF : 32 Amp Excluded OMS 1072896, 1072897 & 1072900 | February | 2014 | 2014Q3 | 2014 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Veg | 2014-02-04 | N | 76 | N | 9 | N | N | 1.1101 | 39.4971 | 2721.3894
[7 empty] | 15301 | 6436 | 1072911 | 2014-02-05 07:18 | 2014-02-05 13:44 | 386 | 11kV | 29722 | 77 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | N | LID 149198 Broken pole at 11kV Links 40738, reported by public early Wednesday morning. Sw 42014 opened for safety & emergency repairs. Trip & reclose on this device approx 2141 tuesday night. See outage report 149183/OMS 1073235 | February | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-02-05 | N | 386 | N | 4 | N | N | 1.1101 | 39.4971 | 21719.9609
[7 empty] | 16095 | 15974 | 1073331 | 2014-02-05 17:19 | 2014-02-05 18:10 | 51 | 11kV | 8925 | 204 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.188 Zetland Pnl 15 tripped on: EF, Fault Check, EFI 11kV UG cable fault from S338 Sw B to S8305 to S1143 (tee Tx 2) see 1073414 1073415 | February | 2014 | 2014Q3 | 2014 | ZN188:PA15 | ZN188:PA33 | ZN00188/000033 | SYDNEY | UG | Not Veg | 2014-02-05 | N | 43.75 | N | 4 | N | N | 1.1101 | 39.4971 | 6522.1268
[7 empty] | 15643 | 10274 | 1073357 | 2014-02-05 19:24 | 2014-02-05 21:10 | 106 | 11kV | 106 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149220 Single phase HV Lead fell out of DOLF carrier. Excluded OMS 1073354 | February | 2014 | 2014Q3 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2014-02-05 | N | 106 | N | 4 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 15051 | 3247 | 1073379 | 2014-02-05 22:08 | 2014-02-05 23:30 | 82 | 11kV | 492 | 6 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | PT14777 Dickson Hue Hue 3.8 Blown HDO footpath side 16Amps Possum caused outage. See 1073566 exclude 1073397 | February | 2014 | 2014Q3 | 2014 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-02-05 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 359.5391
[7 empty] | 15391 | 7364 | 1073902 | 2014-02-06 10:50 | 2014-02-06 10:55 | 5 | 11kV | 1615 | 323 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | Section of 11kV feeder Double Bay Zn Pnl.33 from S1856 Mitchell Point was interrupted relays: intertrip receive Protection Malfunction: CB @ S1856 tripped when DOp made I/T auto on Tx #2. No cause found. I/T sends at remote centres not operated. | February | 2014 | 2014Q3 | 2014 | ZN3155:PA33 | ZN3155:PA33 | ZN03155/000033 | WOOLLAHRA | UG | Not Veg | 2014-02-06 | N | 5 | N | 3 | N | N | 1.1101 | 39.4971 | 1180.1944
[7 empty] | 15432 | 7824 | 1073833 | 2014-02-06 18:09 | 2014-02-06 19:15 | 66 | 11kV | 3894 | 59 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT48926 Robson Northwind center phase 63A HDO had operated Fuse Carrier was carbonised. Subs to investigate See 1074089 GIS 1074094 exclude 1073833 | February | 2014 | 2014Q3 | 2014 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Not Veg | 2014-02-06 | N | 66 | N | 3 | N | N | 1.1101 | 39.4971 | 2845.6203
[7 empty] | 15261 | 5839 | 1073846 | 2014-02-06 19:11 | 2014-02-06 20:46 | 95 | 11kV | 71548 | 794 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 1648 Enfield - Pnl 8 - Earth Fault, EFI, Field EFIs. Underground cable fault between S 5631 and S 5217. ME: 1074571. Rest Step: 1074572. ME GIS: 1073854. Withdrawn: 1073846. | February | 2014 | 2014Q3 | 2014 | ZN1648:PA8 | ZN4853:PA15 | ZN04853/000015 | BURWOOD | UG | Not Veg | 2014-02-06 | N | 90.1108 | N | 3 | N | N | 1.1101 | 39.4971 | 52285.1681
[7 empty] | 16297 | 17970 | 1073868 | 2014-02-07 02:32 | 2014-02-07 03:24 | 52 | 11kV | 111436 | 2143 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Unselected | N | At S36300 Balgowlah North P19 "Hayes Condamine" 11kv fdr tripped on; E/F, EFI Alarms; Tx1 Group Earth EFI's operated S16827 S16064 S49927 S16928 outside 16 myrtle st S48811 Possum has shorted HV connections at LB49832 Linesman to inspect in daylight See 1073868 exclude 1073869 | February | 2014 | 2014Q3 | 2014 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2014-02-07 | N | 52 | N | 3 | N | N | 1.1101 | 39.4971 | 81434.142
[7 empty] | 15986 | 14431 | 1074088 | 2014-02-07 13:57 | 2014-02-07 18:20 | 263 | 11kV | 68380 | 260 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Interrupted to effect emergency repairs to PT.532. Abnormally switched due to defective equipment for duration of summer - helicopter required for repairs | February | 2014 | 2014Q3 | 2014 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2014-02-07 | N | 263 | N | 3 | N | N | 1.1101 | 39.4971 | 49970.0871
[7 empty] | 16020 | 14876 | 1074216 | 2014-02-07 20:55 | 2014-02-07 23:00 | 125 | 11kV | 31250 | 250 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | At S.4041 a defective Tx . HV fuses not checked, unable to earth Tx | February | 2014 | 2014Q3 | 2014 | ZN180:PA18 | ZN35400:PA53 | ZN35400/000053 | NORTH SYDNEY | UG | Not Veg | 2014-02-07 | N | 125 | N | 3 | N | N | 1.1101 | 39.4971 | 22836.5783
[7 empty] | 16217 | 17231 | 1074239 | 2014-02-08 04:03 | 2014-02-08 05:45 | 102 | 11kV | 59902 | 1427 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149264 1 fault operation Sensitive Earth Fault Detailed Fdr patrol required between Sw 50319 & ELB 18241. J Smith reports tracking evident on pole OS-20619 & Bph insulator very close to pole at pole OS-20021 ATTENTION REQUIRED Excluded OMS 1074239 | February | 2014 | 2014Q3 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2014-02-08 | N | 41.9776 | N | 3 | N | N | 1.1101 | 39.4971 | 43774.6148
[7 empty] | 16179 | 16849 | 1074242 | 2014-02-08 05:55 | 2014-02-08 13:10 | 435 | 11kV | 31336 | 172 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 149265 2 fault operations Earth fault Mains down to sub 51419. Excluded OMS 1074242, 1074244 & 1074248. | February | 2014 | 2014Q3 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-02-08 | N | 182.186 | N | 3 | N | N | 1.1101 | 39.4971 | 22899.4245
[7 empty] | 14938 | 2164 | 1074285 | 2014-02-08 11:43 | 2014-02-08 14:45 | 182 | 11kV | 546 | 3 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 149269 Single phase DOLF : 10 Amp Dead burnt bird found at the base of the pole. Excluded OMS 1074285 and 1074286. | February | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-02-08 | N | 182 | N | 3 | N | N | 1.1101 | 39.4971 | 399.0007
[7 empty] | 15425 | 7719 | 1074471 | 2014-02-10 00:28 | 2014-02-10 00:59 | 31 | 11kV | 66433 | 2143 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah Nth, Panel 19 Fdr CB tripped on OC, earth fault, trip LED, UF, fault current, Tx 'B' Protection EF C-B. 11kV trip signal. Field efi's down at S.16827, S.16064, S.49927, S.16928, UG/OH, 48811. Possum at LB.49832 | February | 2014 | 2014Q3 | 2014 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2014-02-10 | N | 31 | N | 9 | N | N | 1.1101 | 39.4971 | 48547.277
[7 empty] | 15043 | 3131 | 1074476 | 2014-02-10 04:13 | 2014-02-10 05:02 | 49 | 11kV | 63798 | 1302 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | ZN 9252 Jannali - Pnl 4 - Trip, reclose, trip, A phase Timed OC, Lockout, timing, EFI, All field EFIs. Possum fried at UGOH near S 9553 Prince Edward Thames. ME: 1074476. Withdrawn: 1074479, 80. | February | 2014 | 2014Q3 | 2014 | ZN9252:PA4 | ZN9252:PA30 | ZN09252/000030 | SUTHERLAND | OH | Not Veg | 2014-02-10 | N | 49 | N | 9 | N | N | 1.1101 | 39.4971 | 46621.6967
[7 empty] | 14700 | 34 | 1074475 | 2014-02-10 03:56 | 2014-02-10 05:07 | 71 | 11kV | 84419 | 1189 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 3 Tripped on Relays: EF, EFI, Fault Check Signals: 11kV Trip, Zone Earth Tx1 Group Earth Possum UGOH to S5227 Isler Prince Edward | February | 2014 | 2014Q3 | 2014 | ZN129:PA3 | ZN129:PA35 | ZN00129/000035 | HUNTERS HILL | OH | Not Veg | 2014-02-10 | N | 71 | N | 9 | N | N | 1.1101 | 39.4971 | 61690.9153
[7 empty] | 15171 | 4318 | 1074483 | 2014-02-10 04:15 | 2014-02-10 05:58 | 103 | 11kV | 10486 | 898 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @ Zn1287 Revesby Panel 23 "S35560 River Montgomery Etc" fdr tripped & Reclosed on Relays - Earth fault with fault check Lock - out and timing Signals - 11KV trip, ZE, TX3 GE and EFI Field EFI's - Sub 35560, 4580, 5435, 5646, 1234 and 35484 Remarks: Cause not ascertained. Footpath side 31.5A HDO Fuse operated @ PT1244 Parmal Av | February | 2014 | 2014Q3 | 2014 | ZN1287:PA23 | ZN1287:PA23 | ZN01287/000023 | CANTERBURY-BANKSTOWN | OH | Veg | 2014-02-10 | N | 11.6771 | N | 9 | N | N | 1.1101 | 39.4971 | 7662.8595
[7 empty] | 15915 | 13284 | 1074499 | 2014-02-10 06:56 | 2014-02-10 07:45 | 49 | 11kV | 21302 | 560 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Ex Zn12620 Noraville section of Pa11 "Norah Head" fdr @Recloser 45053 Norah Head tripped, reclosed and locked out on IOC and timed overcurrent Pole Defective/ Failure Broken HV Crossarm on Pole No. TO 3919 Adjacent PT49314 See 1075334,5 Exclude 1074499 | February | 2014 | 2014Q3 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2014-02-10 | N | 38.0393 | N | 9 | N | N | 1.1101 | 39.4971 | 15566.8733
[7 empty] | 14994 | 2818 | 1074859 | 2014-02-10 14:22 | 2014-02-10 16:00 | 98 | 11kV | 196 | 2 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 149286 B phase DOLF : 16 Amp SUSPECT "SYMPATHY "OPERATION. See LID 149287/OMS 1075097 Excluded OMS 1074859 | February | 2014 | 2014Q3 | 2014 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2014-02-10 | N | 98 | N | 9 | N | N | 1.1101 | 39.4971 | 143.231
[7 empty] | 16139 | 16398 | 1074879 | 2014-02-10 14:20 | 2014-02-10 16:38 | 138 | 11kV | 138 | 1 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 149287 B phase DOLF : 10 AMp MYNA BIRD ACROSS ARRESTOR. Excluded OMS REPORT NO 1074879. | February | 2014 | 2014Q3 | 2014 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Not Veg | 2014-02-10 | N | 138 | N | 9 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 16222 | 17300 | 1074958 | 2014-02-10 18:02 | 2014-02-10 19:15 | 73 | 11kV | 511 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149288 B phase DOLF : 10 Amp NO CAUSE FOUND.STAFF ALSO FOUND BLOWN B PHASE 10A DOLF AT SUB 51507 RESTORED OK. Excluded OMS REPORT NO 1074958 & 1074962. | February | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-02-10 | N | 73 | N | 9 | N | N | 1.1101 | 39.4971 | 373.4237
[7 empty] | 16301 | 18034 | 1075006 | 2014-02-10 23:43 | 2014-02-11 01:30 | 107 | 11kV | 141245 | 1589 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12570 Avoca Pa39 "North Avoca" fdr tripped, reclosed, tripped & locked out Relays: B & C phase IOC, EFI, Lockout Signals: 11kv trip 11kV UG Fault from S18036 to S48327 to S61891 See 1075662,3,4 | February | 2014 | 2014Q3 | 2014 | ZN12570:PA39 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | UG | Not Veg | 2014-02-10 | N | 88.8892 | N | 9 | N | N | 1.1101 | 39.4971 | 103217.68
[7 empty] | 15846 | 12661 | 1075013 | 2014-02-11 00:36 | 2014-02-11 01:54 | 78 | 11kV | 88594 | 1234 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9900 Menai - Pnl 1 - Trip/reclose/trip, RHS Earth Fault, EFI, Timing, Lockout, Field EFIs. Underground cable fault from S 9983 to S 9889 to S 9891. ME: 1075554. Rest Step: 1075555. Withdrawn: 1075013. | February | 2014 | 2014Q3 | 2014 | ZN9900:PA1 | ZN9900:PA1 | ZN09900/000001 | SUTHERLAND | UG | Not Veg | 2014-02-11 | N | 71.7942 | N | 4 | N | N | 1.1101 | 39.4971 | 64741.8821
[7 empty] | 16059 | 15466 | 1075409 | 2014-02-11 15:22 | 2014-02-11 16:38 | 76 | 11kV | 100658 | 1448 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn4545 Meadowbank 11kv OCB Pa17 "S35438" fdr tripped and locked out on: Relays: EFI, Earth Fault, Fault Check, Timming, Lockout EFI's S35438 S3274 S8805 Signals: 11kv trip ABNORMAL: S3636:B closed, S35397:A opened Cause: Contractor hit 11kv UG cable between S8805:B & S6287:A See 1075883,4 Exclude 1075409,17,31,4,9,40,2 | February | 2014 | 2014Q3 | 2014 | ZN4545:PA17 | ZN129:PA36 | ZN00129/000036 | RYDE | UG | Not Veg | 2014-02-11 | N | 69.5152 | N | 4 | N | N | 1.1101 | 39.4971 | 73557.8975
[7 empty] | 15614 | 9792 | 1075467 | 2014-02-11 21:05 | 2014-02-11 21:30 | 25 | 11kV | 1800 | 72 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Ex Zn12580 Erina Pa1 "Greeen Point" section of Panel 1 @S12904 White Cedar Dalgetty Tx LV winding HR Interrupted for safety reasons for the inspection and testing/checking of transofrmer by DOp No Blown HV or LV fuses. When no load TX Volts OK as soon was connected volts dropped to 180 volts on one phase See 1075505 Exclude 1075467,501,2 | February | 2014 | 2014Q3 | 2014 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | UG | Not Veg | 2014-02-11 | N | 25 | N | 4 | N | N | 1.1101 | 39.4971 | 1315.3869
[7 empty] | 14784 | 769 | 1075490 | 2014-02-11 19:39 | 2014-02-11 23:20 | 221 | 11kV | 221 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149307 Broken dropper above DOLF Excluded OMS 1075490 | February | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-02-11 | N | 221 | N | 4 | N | N | 1.1101 | 39.4971 | 161.5003
[7 empty] | 16051 | 15421 | 1075541 | 2014-02-12 04:19 | 2014-02-12 05:07 | 48 | 11kV | 6000 | 125 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3425 Castle Cove 11kv Pa11 "S6328 Mcintosh Pacific" fdr tripped on Relays: C Phase Overcurrent & Earth Fault, EFI & Fault Check Siganls: 11kv trip, Tx2, Group Earth EFI's S6328 S3869 S1334 | February | 2014 | 2014Q3 | 2014 | ZN3425:PA11 | ZN3425:PA11 | ZN03425/000011 | WILLOUGHBY | UG | Not Veg | 2014-02-12 | N | 48 | N | 5 | N | N | 1.1101 | 39.4971 | 4384.623
[7 empty] | 15790 | 12008 | 1075740 | 2014-02-12 12:22 | 2014-02-12 13:45 | 83 | 11kV | 27810 | 344 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At Zn10999 Kogarah Section of HV 11kv feeder Pnl 38L Roadside bond burnt off at AB30095 affecting volts at Sub 10134 Solander Oconnell and Sub 10555 Grand Solander Remarks: Bond. At ABS 30995 Roadside bond burnt off. Live line repair required | February | 2014 | 2014Q3 | 2014 | ZN10999:PA38 | ZN10997:PA7 | ZN10997/000007 | BAYSIDE | OH | Not Veg | 2014-02-12 | N | 80.843 | N | 5 | N | N | 1.1101 | 39.4971 | 20322.7277
[7 empty] | 15414 | 7575 | 1075872 | 2014-02-12 15:59 | 2014-02-12 17:40 | 101 | 11kV | 9696 | 96 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At PT1811 Catherine St, Roadside phase HDO fell out due to a loose fuse holder and damged/cracked insulator Ex ZN1285 Greenacre Park, Panel 24L 'Banksia Stacey' feeder Remarks: vehicle hit pole. PT 1811 Catherine St ISOLATED LV // usl's: 9248, 9234 | February | 2014 | 2014Q3 | 2014 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-02-12 | N | 101 | N | 5 | N | N | 1.1101 | 39.4971 | 7085.5508
[7 empty] | 16318 | 18156 | 1075870 | 2014-02-12 15:56 | 2014-02-12 19:15 | 199 | 11kV | 4292 | 38 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Unselected | N | At S2728 Epping Bouys High School B phase HVDO fuse blown Cause: Tree branch fell onto LV cross arm which broke and mains tangled At S5604 Crimea Epping No 2 400A fuse blown on B phase of distrbutor 1. Above 2 centres in LV parallel Above 2 distributors were in parallel at the time of interruption See OMS 1076036 1076037 | February | 2014 | 2014Q3 | 2014 | ZN2635:PA52 | ZN2635:PA52 | ZN02635/000052 | RYDE | OH | Veg | 2014-02-12 | N | 112.9474 | N | 5 | N | N | 1.1101 | 39.4971 | 3136.467
[7 empty] | 16100 | 15994 | 1075931 | 2014-02-12 19:55 | 2014-02-12 20:45 | 50 | 11kV | 2999.2 | 60 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12610 Long Jetty section Pa10 "Wamberal" @PT11265 The Entrance Whalan middle HDO Blown. HV B Phase 31.5 Amp fuse replaced. See 1076274 gis 1075931 exclude 1075932,42 | February | 2014 | 2014Q3 | 2014 | ZN12610:PA10 | ZN12610:PA10 | ZN12610/000010 | CENTRAL COAST | OH | Not Veg | 2014-02-12 | N | 49.9867 | N | 5 | N | N | 1.1101 | 39.4971 | 2191.7269
[7 empty] | 16489 | 20334 | 1076413 | 2014-02-13 17:05 | 2014-02-13 18:40 | 95 | 11kV | 475 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" @Autolink 44775 "Linga Longa tripped cause not ascertained See 1076712 Exclude 1076413 | February | 2014 | 2014Q3 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2014-02-13 | N | 95 | N | 2 | N | N | 1.1101 | 39.4971 | 347.116
[7 empty] | 16484 | 20279 | 1076625 | 2014-02-13 16:30 | 2014-02-13 19:50 | 200 | 11kV | 3800 | 19 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 149339 EMERGENCY SWITCHING N0123.EYE BOLTS RUSTED THROUGH AT POLE JR-42405 MILLERS FOREST. | February | 2014 | 2014Q3 | 2014 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2014-02-13 | N | 200 | N | 2 | N | N | 1.1101 | 39.4971 | 2776.9279
[7 empty] | 14988 | 2677 | 1076485 | 2014-02-14 01:14 | 2014-02-14 02:17 | 63 | 11kV | 86392 | 1524 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn2602 Clovelly - Pnl 17 feeder tripped on 17L - C phase O/C, Fc, EFI Field EFis @ S7492 S4407 UG Cable fault from S7492 Sw B to S2732 Sw A see 1076688 1076690 gis 1076486 | February | 2014 | 2014Q3 | 2014 | ZN2602:PA17 | ZN2602:PA30 | ZN02602/000030 | RANDWICK | UG | Not Veg | 2014-02-14 | N | 56.6877 | N | 8 | N | N | 1.1101 | 39.4971 | 63132.7255
[7 empty] | 16455 | 20012 | 1076489 | 2014-02-14 03:01 | 2014-02-14 03:57 | 56 | 11kV | 13625 | 270 | HV | Fire (non-electrical) | Adverse Weather/Environment | UGOH | Unplanned | Unselected | N | LID 149340 2 fault operations Earth fault Pole fire at UGOH AK-61347 Excluded OMS 1076489 & 1076490 | February | 2014 | 2014Q3 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2014-02-14 | N | 50.463 | N | 8 | N | N | 1.1101 | 39.4971 | 9956.7481
[7 empty] | 15866 | 12832 | 1076481 | 2014-02-14 02:20 | 2014-02-14 05:00 | 160 | 11kV | 3135 | 39 | HV | Fire (non-electrical) | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 149341 Section interrupted to isolate sub 71887 NOTE: LV Link 43279 to PT.70803 does not phase, and links installed towards PT.71343 need number. Excluded OMS 1076481, 1076483 & 1076494 | February | 2014 | 2014Q3 | 2014 | 810:74062 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2014-02-14 | N | 80.3846 | N | 8 | N | N | 1.1101 | 39.4971 | 2290.9655
[7 empty] | 15757 | 11680 | 1076549 | 2014-02-14 08:08 | 2014-02-14 11:09 | 181 | 11kV | 202884 | 1172 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Mosman Pnl 43 tripped on: A & B phase timed O/C, E/F, EFI Field EFIs: S5188 S5088 - S46998 & S35976 Faulty EFIs giving false indication to restore feeder Underground cable fault from S46998 (Sw B) to S7950 (sw B) to S35976 (Sw A) see seperate outage on Pnl.41 @ 9:57 #1077654 see 1077653 1077657 1077654 GIS: 1076549 | February | 2014 | 2014Q3 | 2014 | ZN180:PA43 | ZN180:PA43 | ZN00180/000043 | WILLOUGHBY | UG | Not Veg | 2014-02-14 | N | 173.1092 | N | 8 | N | N | 1.1101 | 39.4971 | 148261.6431
[7 empty] | 15494 | 8408 | 1076652 | 2014-02-14 09:44 | 2014-02-14 11:32 | 108 | 11kV | 9828 | 91 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 149355 ISOLATED FOR SAFETY XARM FIRE AT POLE 8N-20027 | February | 2014 | 2014Q3 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-02-14 | N | 108 | N | 8 | N | N | 1.1101 | 39.4971 | 7182.0125
[7 empty] | 16278 | 17784 | 1076959 | 2014-02-14 19:24 | 2014-02-14 20:55 | 91 | 11kV | 1365 | 15 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Ex Zn12620 Noraville section of pa11 "Norah Head" @RE45053 Norah Head tripped and reclosed on IOC and Earth Fault - see 1078305 @PT14213 Soldiers Victoria 11kv Centre Phase Dropout fuse operated @PT14213 Soldiers Victoria 11kv Surge arrestors failed. See 1078305,7 Exclude 1076959,61 | February | 2014 | 2014Q3 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2014-02-14 | N | 91 | N | 8 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 15118 | 3888 | 1076982 | 2014-02-14 22:40 | 2014-02-15 00:15 | 95 | 11kV | 190 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149364 A Phase DOLF : 20 Amp Replaced 20A LF 43895 & 10A DOLF sub 49200. No cause found Excluded OMS 1076982 | February | 2014 | 2014Q3 | 2014 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2014-02-14 | N | 95 | N | 8 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 16037 | 15182 | 1076970 | 2014-02-14 20:30 | 2014-02-15 00:30 | 240 | 11kV | 12960 | 54 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 149362 3 phase No protection operations. Section isolated to replace pole JT-40050 on SI N0125. Excluded OMS 1076969, 1076970, 1076971 | February | 2014 | 2014Q3 | 2014 | 258:80787 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Not Veg | 2014-02-14 | N | 240 | N | 8 | N | N | 1.1101 | 39.4971 | 9470.7857
[7 empty] | 16167 | 16667 | 1078086 | 2014-02-15 03:46 | 2014-02-15 05:16 | 90 | 11kV | 31199 | 524 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At S35500 Top Ryde Panel 32 tripped on IOC with EFI No3 Tx Group Earth 11kV Trip Cause: UG fault between section of 11kV from S8911 Delhi Julius See OMS 1078086 1078087 1078088 1076991 | February | 2014 | 2014Q3 | 2014 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | UG | Not Veg | 2014-02-15 | N | 59.5401 | N | 2 | N | N | 1.1101 | 39.4971 | 22799.309
[7 empty] | 15252 | 5683 | 1077120 | 2014-02-15 10:19 | 2014-02-15 10:45 | 26.1833 | 11kV | 1649.55 | 63 | HV | Vandalism | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 149368 Earths stollen from pole. FP 10001. Recloser 42031 Bourkes Crossing Reg RAGCB. Pole smoking. Fire Brigade called. Isolated from ABS 61332 for safe operation of bypass ABS 42031Z. | February | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-02-15 | N | 26.1833 | N | 2 | N | N | 1.1101 | 39.4971 | 1205.4425
[7 empty] | 14940 | 2175 | 1077290 | 2014-02-16 08:31 | 2014-02-16 09:28 | 57 | 11kV | 50331 | 883 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | LID 149372 3 fault operations tree branch removed from OHM at pole VP-30151 | February | 2014 | 2014Q3 | 2014 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Veg | 2014-02-16 | N | 57 | N | 6 | N | N | 1.1101 | 39.4971 | 36780.4103
[7 empty] | 14862 | 1538 | 1077379 | 2014-02-16 13:44 | 2014-02-16 15:55 | 131 | 11kV | 3930 | 30 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of pa5 @LK41285 11kv bond failed. See 1078332 exclude 1077379 | February | 2014 | 2014Q3 | 2014 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | OH | Not Veg | 2014-02-16 | N | 131 | N | 6 | N | N | 1.1101 | 39.4971 | 2871.9281
[7 empty] | 16323 | 18233 | 1077427 | 2014-02-16 15:47 | 2014-02-16 18:20 | 152.5167 | 11kV | 5033.05 | 33 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 149381 Single phase DOLF : 16 Amp REPLACED BOTH FUSES | February | 2014 | 2014Q3 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-02-16 | N | 152.5167 | N | 6 | N | N | 1.1101 | 39.4971 | 3678.0045
[7 empty] | 16353 | 18613 | 1077473 | 2014-02-16 17:31 | 2014-02-16 18:30 | 59 | 11kV | 151663 | 2651 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn15006 Dee Why West - Pnl 9 tripped on OC & EF B phase Suspect UG cable fault between S16924 and S16677 see 1077693 1077694 GIS: 1077489 1077480 | February | 2014 | 2014Q3 | 2014 | ZN15006:PA9 | ZN15006:PA9 | ZN15006/000009 | NORTHERN BEACHES | UG | Not Veg | 2014-02-16 | N | 57.2097 | N | 6 | N | N | 1.1101 | 39.4971 | 110830.8471
[7 empty] | 16197 | 17057 | 1077575 | 2014-02-16 22:14 | 2014-02-16 23:32 | 78 | 11kV | 156 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Rain Heavy | N | LID 149383 A phase DOLF : 10 Amp Excluded OMS 1077575 & 1077576 | February | 2014 | 2014Q3 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | UG | Not Veg | 2014-02-16 | N | 78 | N | 6 | N | N | 1.1101 | 39.4971 | 114.0002
[7 empty] | 15483 | 8257 | 1077582 | 2014-02-16 22:41 | 2014-02-17 00:33 | 112 | 11kV | 48076 | 506 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 690 Campsie - Pnl 15 - C phase OC and Timed, EFI, Fault check. Section of 11kV feeder from ZN 690 Pnl 15 to S 6236 to S 3711 to S 2528 to S 2061. ME: 1078063. Rest Step: 1078064, 5. Withdrawn: 1077582. | February | 2014 | 2014Q3 | 2014 | ZN690:PA15 | ZN690:PA15 | ZN00690/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-02-16 | N | 95.0119 | N | 6 | N | N | 1.1101 | 39.4971 | 35132.5228
[7 empty] | 16339 | 18404 | 1077598 | 2014-02-17 00:50 | 2014-02-17 03:01 | 131 | 11kV | 174358 | 1334 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Heavy | N | LID 149384 4 fault operations A & B phase Overcurrent Faulty section isolated, suspect UGOH pole KS-60009 daylight investigation required. . excluded OMS 1077598 | February | 2014 | 2014Q3 | 2014 | 229:34989 | 233:82815 | ZN00233/082815 | PORT STEPHENS | Unknown | Unknown | 2014-02-17 | N | 130.7031 | N | 4 | N | N | 1.1101 | 39.4971 | 127415.6837
[7 empty] | 16045 | 15322 | 1077724 | 2014-02-17 09:26 | 2014-02-17 10:16 | 50 | 11kV | 69100 | 1382 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12640 Peats Ridge section of pa1 "Dog Trap Rd" 11kv fdr @RE44936 "bentley Rd" tripped on overcurrent trip ABNORMAL: For D&R 330576 Re44936 Sensitive Earth & Reclosing Non Auto, AB44606 closed with RE4937 open Tree Branch on mains near 29 Mangrove Rd Narara See 1078415 exclude 1077724,30,53 | February | 2014 | 2014Q3 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-02-17 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 50496.2419
[7 empty] | 15792 | 12020 | 1077828 | 2014-02-17 10:53 | 2014-02-17 12:15 | 82 | 11kV | 5166 | 63 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 149392 A & B Phase DOLF : 40 Amp Faulty txf replaced under A/P. Excluded OMS 1077828 & 1077829 | February | 2014 | 2014Q3 | 2014 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | UG | Not Veg | 2014-02-17 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 3775.1604
[7 empty] | 14891 | 1869 | 1077959 | 2014-02-17 13:25 | 2014-02-17 14:54 | 89 | 11kV | 445 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 149393 No Protection operation. Isolated to repair burnt through xarm at pole AL-60307 MAN access rd. Reported by public. | February | 2014 | 2014Q3 | 2014 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2014-02-17 | N | 89 | N | 4 | N | N | 1.1101 | 39.4971 | 325.1929
[7 empty] | 15353 | 6839 | 1078446 | 2014-02-18 13:50 | 2014-02-18 14:31 | 41 | 11kV | 29560 | 790 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN 9118 Cronulla - Pnl 2 - Trip/reclose/trip, B phase earth leakage, Sealing contactor, lockout, timing, EFI. Underground cable damaged by contractor outside 12 Caringbah Road. ME: 1078835. Rest Step: 1078836. Withdrawn: 1078446, 8. | February | 2014 | 2014Q3 | 2014 | ZN9118:PA2 | ZN9118:PA2 | ZN09118/000002 | SUTHERLAND | UG | Not Veg | 2014-02-18 | N | 37.4177 | N | 1 | N | N | 1.1101 | 39.4971 | 21601.5761
[7 empty] | 15772 | 11836 | 1078606 | 2014-02-19 07:25 | 2014-02-19 09:15 | 110 | 11kV | 81290 | 739 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Zn12610 Long Jetty 11kv Pa25 "long jetty Aux No.2" fdr tripped, reclosed, tripped & Locked out Relays: Earth Fault, Earth Fault Check, Reclose Timing relay, Lockout, EFI Signals: 11kv trip, Zone Earth, Tx3 Group Earth EFI's Nil Cause: Broken HV crossarm at pole no. TE1342 outside 118 Tuggerah Pde Long Jetty. HV contact with LV neutral See 1079493,4 1081782 Exclude 1078606,22 | February | 2014 | 2014Q3 | 2014 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2014-02-19 | N | 110 | N | 12 | N | N | 1.1101 | 39.4971 | 59404.3344
[7 empty] | 14950 | 2267 | 1078610 | 2014-02-19 07:51 | 2014-02-19 10:28 | 157 | 11kV | 253007 | 2198 | HV | Animal Bird | Animal | Air Break Switch | Unplanned | Unselected | N | Zn3425 Castle Cove Pa30 fdr tripped on Relays: Aphase INST and Timed, EFI EFI's S3252 Signals: 11kv trip ABNORMAL: S951 Archibold rd SwB closed SwA opened, PT328 in LV// with pa30 or Pa12 at time of interruption See 1079760,3,4,5,6,7 GIS 1078628,9894 Exclude 1078610,1,3 | February | 2014 | 2014Q3 | 2014 | ZN3425:PA30 | ZN3425:PA30 | ZN03425/000030 | KU-RING-GAI | OH | Not Veg | 2014-02-19 | N | 115.1078 | N | 12 | N | N | 1.1101 | 39.4971 | 184890.0532
[7 empty] | 16256 | 17538 | 1078721 | 2014-02-19 10:21 | 2014-02-19 11:29 | 68 | 11kV | 48374 | 713 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | At Zn8000 Macquarie Park Pa11 Tripped on Relays: Earth Fault Cause: external contractor hit 11kV Cable Lane Cove Rd between S8604 to S5446 to S447 See OMS 1079561 1079563 1078744 1078721 | February | 2014 | 2014Q3 | 2014 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2014-02-19 | N | 67.8457 | N | 12 | N | N | 1.1101 | 39.4971 | 35350.2924
[7 empty] | 16238 | 17465 | 1078891 | 2014-02-19 14:42 | 2014-02-19 15:47 | 65 | 11kV | 59681 | 1344 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149417 1 fault operation A & C phase Overcurrent system abnormal due to SI 40581 fdr 80923 feeds to abs 40397. Relcose was OFF due to this switching. targets AC 51 see report # 149418/OMS 1079271 | February | 2014 | 2014Q3 | 2014 | 502:48010 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Veg | 2014-02-19 | N | 44.4055 | N | 12 | N | N | 1.1101 | 39.4971 | 43613.1145
[7 empty] | 16412 | 19312 | 1078999 | 2014-02-19 16:37 | 2014-02-19 17:11 | 34 | 11kV | 27642 | 813 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 149416 1 fault operation B & C phase Overcurrent Branch fell on OHM at pole JR-90367. | February | 2014 | 2014Q3 | 2014 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2014-02-19 | N | 34 | N | 12 | N | N | 1.1101 | 39.4971 | 20199.9583
[7 empty] | 16046 | 15336 | 1078939 | 2014-02-19 15:18 | 2014-02-19 17:22 | 124 | 11kV | 10540 | 85 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 149419 C phase DOLF : 40 Amp suspect lightning Excluded oms 1078939/1078949 | February | 2014 | 2014Q3 | 2014 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | UG | Not Veg | 2014-02-19 | N | 124 | N | 12 | N | N | 1.1101 | 39.4971 | 7702.3211
[7 empty] | 15493 | 8387 | 1078906 | 2014-02-19 14:54 | 2014-02-19 17:25 | 151 | 11kV | 112711 | 781 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Zn12640 Umina Pa16 "Umina" trippped, reclosed and tripped on: Relays: IOC, A&C timed overcurrent Signals: EFI EFI's S18125 S48474 Trip occured during a lightning storm and coincided with outage on Pa15 at Umina Zone. DOp patrolled fdr and found no damage. See 1079522,3 Exclude 1078906 | February | 2014 | 2014Q3 | 2014 | ZN12640:PA16 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Veg | 2014-02-19 | N | 144.3163 | N | 12 | N | N | 1.1101 | 39.4971 | 82365.8744
[7 empty] | 16407 | 19232 | 1078905 | 2014-02-19 14:54 | 2014-02-19 17:30 | 156 | 11kV | 143940 | 1027 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Zn12640 Umina Pa15 "Bourke Rd" tripped on Relays: IOC, Aphase timed overcurrent, SEF Signals: EFI EFI's S18395 S18740 @PT13859 Ocean Beach Pozieries, Lightning arrestor damaged during lightning storm. Cutout for repairs required. See 1079528,9 Exclude 1078905,11,90,9022 | February | 2014 | 2014Q3 | 2014 | ZN12640:PA15 | ZN12640:PA5 | ZN12640/000005 | CENTRAL COAST | OH | Not Veg | 2014-02-19 | N | 140.1558 | N | 12 | N | N | 1.1101 | 39.4971 | 105187.1065
[7 empty] | 15534 | 8843 | 1079053 | 2014-02-19 21:50 | 2014-02-19 22:27 | 37 | 11kV | 13024 | 352 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | At S8328 Malvina Buffalo No.2 SW/B Opened Section of PT158 Cressy RD HV cross arm broken wiith 11kV Mains Hanging above LV mains. DOp placed PT158 in LV parallel. DOp tried opening AB501 Only 2 Phases will open. Dop tried opening AB2265 (No Top Rod) PT47322 Buffalo Provoidence Placed in parallel Dop attempted to open LB47403 - Did not open, spring assisted\ The next LB is LB47404 which is also spring assisted. AOp made the call with SOp to open SW/B at S8328 | February | 2014 | 2014Q3 | 2014 | ZN35500:PA28 | ZN35500:PA36 | ZN35500/000036 | RYDE | OH | Not Veg | 2014-02-19 | N | 37 | N | 12 | N | N | 1.1101 | 39.4971 | 9517.5551
[7 empty] | 15374 | 7119 | 1079149 | 2014-02-20 02:40 | 2014-02-20 04:00 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 149430 Single phase DOLF : 10 Amp Sub not retrofitted Volts at switchboard = 240V. Excluded OMS 1079149 | February | 2014 | 2014Q3 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | UG | Not Veg | 2014-02-20 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 15715 | 11101 | 1079114 | 2014-02-19 20:26 | 2014-02-20 10:45 | 859 | 11kV | 1718 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Rain Wind Storm | N | @19/2/14 20:26 PT18603 reported phase down @20/2/14 09:43 DOp attempted to restore PT18603, lightning arrestors appeared in tact, but were damaged from lightning storm the previous night RE45093 tripped and reclosed on: Relays: IOC, Overcurrent Signals: Nil 1079720 2nd 1079722 exclude 1078909,9114,9,46 | February | 2014 | 2014Q3 | 2014 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2014-02-19 | N | 859 | N | 12 | N | N | 1.1101 | 39.4971 | 1255.4637
[7 empty] | 15984 | 14318 | 1079222 | 2014-02-20 08:57 | 2014-02-20 11:09 | 132 | 11kV | 20512 | 244 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.2568 St Peters Pnl.6 tripped on Earth Fault, EFI Field EFIs: S47633, S6362 UG Cable fault from S6362 Sw D to S6103 Sw A to S3272 Sw B see 1079698 1079699 (LV // failure) GIS: 1079229 1079241 1079243 | February | 2014 | 2014Q3 | 2014 | ZN2568:PA19 | ZN2568:PA19 | ZN02568/000019 | INNER WEST | UG | Not Veg | 2014-02-20 | N | 84.0656 | N | 5 | N | N | 1.1101 | 39.4971 | 14989.5646
[7 empty] | 15728 | 11364 | 1079150 | 2014-02-20 03:34 | 2014-02-20 11:40 | 486 | 11kV | 38491.4 | 167 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 149429 2 fault operations B & C phase Overcurrent Faulty UGOH pole JS-27021 requires repairs Target =51BC. | February | 2014 | 2014Q3 | 2014 | 265:81648 | 265:81648 | ZN00265/081648 | PORT STEPHENS | Unknown | Unknown | 2014-02-20 | N | 230.4874 | N | 5 | N | N | 1.1101 | 39.4971 | 28128.3798
[7 empty] | 14942 | 2189 | 1079390 | 2014-02-20 11:36 | 2014-02-20 14:00 | 144 | 11kV | 576 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex ZN12570 Avoca section of Pa22 @PT18027 Island View Kin res Roadside 20amp HDO operated Batch #2283 Fatigue Cause not ascertained. Replaced by DOp See 1079742 exclude 1079390,429,54 | February | 2014 | 2014Q3 | 2014 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Not Veg | 2014-02-20 | N | 144 | N | 5 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 16434 | 19709 | 1079115 | 2014-02-19 14:51 | 2014-02-20 14:50 | 1439 | 11kV | 112242 | 78 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | N | Ex Zn12640 Umina section of Pa13 "patonga" RE47746 Patonga Meroo tripped, reclosed, tripped on Relays: Overcurrent, Earth Fault Signals: Nil EFI's: Lightning Arrestor at PT11051 See 1080243,5 Exclude 1078909,9621 | February | 2014 | 2014Q3 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2014-02-19 | N | 1439 | N | 12 | N | N | 1.1101 | 39.4971 | 82023.143
[7 empty] | 15975 | 14228 | 1079571 | 2014-02-20 15:36 | 2014-02-20 15:41 | 5 | 11kV | 2368 | 1184 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn4545 Meadowbank section of Pa13 "Ryedale Sixth" RE46117 Balaclava Vimera tripped and reclosed on 2 occasions on overcurrent A & B phase Tree branch in Vimiera rd. DOp Cauchi switched 11kv and removed tree branch See 1079788 2nd 107989 exclude 1079571 | February | 2014 | 2014Q3 | 2014 |  |  |  | PARRAMATTA | OH | Veg | 2014-02-20 | N | 2 | N | 5 | N | N | 1.1101 | 39.4971 | 1730.4646
[7 empty] | 15905 | 13213 | 1079119 | 2014-02-19 20:19 | 2014-02-20 16:25 | 1206 | 11kV | 197996 | 166 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" REcloser 45012 Bar Point tripped, reclosed, tripped and locked out Tree/branch borught down overhead. Mains down have been located See 1079734,7 Exclude 1079119 | February | 2014 | 2014Q3 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2014-02-19 | N | 1192.747 | N | 12 | N | N | 1.1101 | 39.4971 | 144689.6369
[7 empty] | 15904 | 13202 | 1079657 | 2014-02-21 05:22 | 2014-02-21 06:15 | 53 | 11kV | 3180 | 60 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 149441 A & B phase DOLF : 31 Amp Possum. Volts = 246, 246, 246. Amps = 120, 110, 120. Excluded OMS = 1079657 | February | 2014 | 2014Q3 | 2014 | 205:12205 | 205:12205 | ZN00205/012205 | LAKE MACQUARIE | OH | Not Veg | 2014-02-21 | N | 53 | N | 4 | N | N | 1.1101 | 39.4971 | 2323.8502
[7 empty] | 15511 | 8599 | 1079950 | 2014-02-21 16:38 | 2014-02-21 17:45 | 67 | 11kV | 3885.5167 | 58 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Fuse fatigue of the centre phase HDO at PT.15211 | February | 2014 | 2014Q3 | 2014 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2014-02-21 | N | 66.9917 | N | 4 | N | N | 1.1101 | 39.4971 | 2839.421
[7 empty] | 16304 | 18060 | 1079959 | 2014-02-21 17:06 | 2014-02-21 18:55 | 109 | 11kV | 5341 | 49 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 149449 3 Phase Interruption Interrupt to repair broken 11kV crossarm at sub 51623 | February | 2014 | 2014Q3 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-02-21 | N | 109 | N | 4 | N | N | 1.1101 | 39.4971 | 3903.0453
[7 empty] | 14780 | 748 | 1079954 | 2014-02-21 18:30 | 2014-02-21 19:45 | 75 | 11kV | 75 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149450 Broken LLC. Interrupt to repair. | February | 2014 | 2014Q3 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-02-21 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 14863 | 1547 | 1080111 | 2014-02-23 02:05 | 2014-02-23 03:32 | 87 | 11kV | 186441 | 2143 | HV | Animal Possum | Animal | Air Break Switch | Unplanned | Unselected | N | At S.36300 Balgowlah North, Panel 19 Fdr CB tripped on Timed earth fault, efi, fault check. 11kV trip signal. Field efi's dwon at S.48811, S.16928, S.49927, S.16064 and S.16827. Possum on Load Break Switch 49832 | February | 2014 | 2014Q3 | 2014 | ZN36300:PA19 | ZN36300:PA19 | ZN36300/000019 | NORTHERN BEACHES | OH | Not Veg | 2014-02-23 | N | 87 | N | 4 | N | N | 1.1101 | 39.4971 | 136245.5837
[7 empty] | 16129 | 16251 | 1080115 | 2014-02-23 07:17 | 2014-02-23 11:45 | 268 | 11kV | 6432 | 24 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 149462 2 Fault Operations Phases A & B 11kV mains down at pole EM-30158 (Hawk across Tappings) | February | 2014 | 2014Q3 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-02-23 | N | 268 | N | 4 | N | N | 1.1101 | 39.4971 | 4700.3159
[7 empty] | 15267 | 5927 | 1080151 | 2014-02-23 14:05 | 2014-02-23 15:01 | 56 | 11kV | 18256 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Recloser 22381 opened on IOC and OC tree branch on OH mains O/S #35 Walter St. Branch removed by D.Op | February | 2014 | 2014Q3 | 2014 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2014-02-23 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 13340.9463
[7 empty] | 15854 | 12741 | 1080160 | 2014-02-23 15:15 | 2014-02-23 16:10 | 55 | 11kV | 165 | 3 | HV | Animal Bird | Animal | DC PT | Unplanned | Unselected | N | LID 149464 B Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1080160 CASS 933766 Dead myna bird below transformer | February | 2014 | 2014Q3 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-02-23 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 120.5771
[7 empty] | 15624 | 9983 | 1080374 | 2014-02-24 11:03 | 2014-02-24 11:53 | 50 | 11kV | 118432 | 2413 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn901 Surry Hills - Pnl 11 tripped onL Timed E/F, EFI Field EFIs: S6382 S35657 S34 S2216 UG Cable fault from S2216 to S7466 see 1080733 1080734 | February | 2014 | 2014Q3 | 2014 | ZN901:PA11 | ZN901:PA27 | ZN00901/000027 | SYDNEY | UG | Not Veg | 2014-02-24 | N | 49.0808 | N | 4 | N | N | 1.1101 | 39.4971 | 86546.6124
[7 empty] | 14986 | 2675 | 1080729 | 2014-02-24 11:27 | 2014-02-24 12:05 | 38 | 11kV | 2812 | 74 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3288 City South - 45/46C feeder tripped on: Left side 45C Bz Trip Possible pilot cable fault S6075 restored via LV bus section links to 46B Tx see 1080729 1080731 | February | 2014 | 2014Q3 | 2014 | ZN3288:PA45 46ABC | ZN3288:PA45 46ABC | ZN03288/45 46ABC | SYDNEY | UG | Not Veg | 2014-02-24 | N | 38 | N | 4 | N | N | 1.1101 | 39.4971 | 2054.9267
[7 empty] | 15398 | 7427 | 1080687 | 2014-02-24 19:32 | 2014-02-24 20:52 | 80 | 11kV | 73774 | 969 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149472 2 Fault Operations A Phase Overcurrent Scada events did not show switch reclosed Excluded OMS 1080687 | February | 2014 | 2014Q3 | 2014 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Veg | 2014-02-24 | N | 76.1342 | N | 4 | N | N | 1.1101 | 39.4971 | 53911.8632
[7 empty] | 14781 | 760 | 1080692 | 2014-02-24 19:55 | 2014-02-24 23:50 | 235 | 11kV | 21620 | 92 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149473 B Phase - DOLF: 20amp Burnt up Bph DOLF carrier & burnt up Bph LVF assembly. 240V 66A, 113A, 94A Excluded OMS 1080692 | February | 2014 | 2014Q3 | 2014 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2014-02-24 | N | 235 | N | 4 | N | N | 1.1101 | 39.4971 | 15799.2583
[7 empty] | 16452 | 19964 | 1080708 | 2014-02-25 01:42 | 2014-02-25 12:35 | 653.4 | 11kV | 26789.4 | 41 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 149474 4 Fault Operations A Phase Earth Fault | February | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-02-25 | N | 653.4 | N | 2 | N | N | 1.1101 | 39.4971 | 19576.9034
[7 empty] | 16136 | 16347 | 1080914 | 2014-02-25 11:18 | 2014-02-25 15:04 | 226 | 11kV | 89474 | 611 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 149490 2 fault operations Feeder 89061 Locked out on E/F Fault in UG cable between UGOH and Pole AH 11777 and SW 59714 Ibis | February | 2014 | 2014Q3 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | UG | Not Veg | 2014-02-25 | N | 146.4386 | N | 2 | N | N | 1.1101 | 39.4971 | 65384.9602
[7 empty] | 16175 | 16755 | 1081290 | 2014-02-26 07:00 | 2014-02-26 10:35 | 215 | 11kV | 430 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149497 No Protection Op HV lead fell out oftop of DOLF. Reported by Meter Reader | February | 2014 | 2014Q3 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-02-26 | N | 215 | N | 5 | N | N | 1.1101 | 39.4971 | 314.2313
[7 empty] | 15765 | 11746 | 1081160 | 2014-02-26 06:19 | 2014-02-26 11:22 | 303 | 11kV | 44791 | 173 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 149493 1 Fault Operation Earth Fault Swans brought down OH mains Excluded OMS 1081160 & 1081161 | February | 2014 | 2014Q3 | 2014 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2014-02-26 | N | 258.9075 | N | 5 | N | N | 1.1101 | 39.4971 | 32731.9417
[7 empty] | 15234 | 5337 | 1081458 | 2014-02-26 13:30 | 2014-02-26 14:45 | 75.4667 | 11kV | 128293.3333 | 1700 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.15004 Newport, 11kV Fdr CB tripped on O.C. and earth fault, efi, fault check and frame leakage. No Ffield efi's operated, UG cable fault on first UG/OH from Panel 1 ex Newport Zone CC1: 22-"Refer to SOp" | February | 2014 | 2014Q3 | 2014 | ZN15004:PA1 | ZN15004:PA1 | ZN15004/000001 | NORTHERN BEACHES | UG | Not Veg | 2014-02-26 | N | 75.4667 | N | 5 | N | N | 1.1101 | 39.4971 | 93752.984
[7 empty] | 15076 | 3447 | 1081495 | 2014-02-26 14:10 | 2014-02-26 15:48 | 98 | 11kV | 12740 | 130 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | AB239 Roadside Bond blown off ex Pa32 Wicks Macquarie Hospital see OMS 1082354 1081495 1081505 | February | 2014 | 2014Q3 | 2014 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2014-02-26 | N | 98 | N | 5 | N | N | 1.1101 | 39.4971 | 9310.0162
[7 empty] | 16027 | 14930 | 1081600 | 2014-02-26 17:40 | 2014-02-26 23:20 | 340 | 11kV | 17227 | 154 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 149504 4 Fault Operations A & C Phase Overcurrent Broken Cross arm at pole AJ-20576 Excluded OMS 1081600 & 1081638 | February | 2014 | 2014Q3 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2014-02-26 | N | 111.8636 | N | 5 | N | N | 1.1101 | 39.4971 | 12588.9835
[7 empty] | 15014 | 2930 | 1081658 | 2014-02-27 02:55 | 2014-02-27 04:30 | 95 | 11kV | 380 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 149505 Single Phase - Fuse size: 10 Amp Substation DOLF Excluded 1081658 | February | 2014 | 2014Q3 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-02-27 | N | 95 | N | 9 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 16259 | 17542 | 1081659 | 2014-02-27 03:23 | 2014-02-27 04:48 | 85 | 11kV | 197470 | 2852 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S35500 Top Ryde Panel 24 Tripped on Relays 24R IOC A and B phase Cause not ascertaine dfor outage See OM S1082357 1082358 1081659 | February | 2014 | 2014Q3 | 2014 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Veg | 2014-02-27 | N | 69.2391 | N | 9 | N | N | 1.1101 | 39.4971 | 144305.2516
[7 empty] | 14930 | 2133 | 1081866 | 2014-02-27 12:00 | 2014-02-27 12:58 | 58 | 11kV | 21808 | 376 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Tree branch on 11kV OH mains O/S 2-6 Yindela St | February | 2014 | 2014Q3 | 2014 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Veg | 2014-02-27 | N | 58 | N | 9 | N | N | 1.1101 | 39.4971 | 15936.6432
[7 empty] | 15299 | 6417 | 1081975 | 2014-02-27 16:24 | 2014-02-27 16:35 | 11.0333 | 11kV | 33.1 | 3 | HV | Arcing | Equipment Failure | Pole | Unplanned | Unselected | N | LID 149519 Pole top fire at P: KT-70858. De energised Fdr for fire fighters to extinguish fire. | February | 2014 | 2014Q3 | 2014 | 228:7486 | 228:85407 | ZN00228/085407 | NEWCASTLE | OH | Not Veg | 2014-02-27 | N | 11.0333 | N | 9 | N | N | 1.1101 | 39.4971 | 24.1885
[7 empty] | 15586 | 9391 | 1081836 | 2014-02-27 11:27 | 2014-02-27 17:03 | 336.35 | 11kV | 23250.1 | 116 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT.15196 the roadside HDO fuse failed due to fatigue CC1: 22-"Refer to SOp" | February | 2014 | 2014Q3 | 2014 | ZN15002:PA6 | ZN15002:PA6 | ZN15002/000006 | NORTHERN BEACHES | OH | Not Veg | 2014-02-27 | N | 200.4319 | N | 9 | N | N | 1.1101 | 39.4971 | 16990.4873
[7 empty] | 15817 | 12289 | 1081813 | 2014-02-27 11:02 | 2014-02-27 17:22 | 380 | 11kV | 212918 | 1266 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 33 tripped reclosed tripped and locked out on Relays - O/C, Earth Fault 2nd AttemptAC fault Cause: Tree branch in Elouera Rd Near Westleigh Drive - Brought down Mains in section of feeder between AB2830 and AB2671 tee PT2217 Eloura Stringy Bark. See OMS 1083201 3203 3204 3206 3207 1081813 818 819 822 823 824 826 | February | 2014 | 2014Q3 | 2014 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2014-02-27 | N | 168.1817 | N | 9 | N | N | 1.1101 | 39.4971 | 155594.1944
[7 empty] | 15492 | 8321 | 1082053 | 2014-02-27 19:49 | 2014-02-27 22:35 | 166 | 11kV | 166 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 149521 C Phase DOLF - Fuse size: 10 Amp Excluded OMS 1082053 | February | 2014 | 2014Q3 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-02-27 | N | 166 | N | 9 | N | N | 1.1101 | 39.4971 | 121.3079
[7 empty] | 14798 | 931 | 1082060 | 2014-02-27 23:24 | 2014-02-28 01:20 | 116 | 11kV | 9396 | 81 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Recloser 24722 tripped on SEL due to a protection malfunction CC1: 22-"Refer to SOp" | February | 2014 | 2014Q3 | 2014 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-02-27 | N | 116 | N | 9 | N | N | 1.1101 | 39.4971 | 6866.3197
[7 empty] | 16387 | 18967 | 1082035 | 2014-02-27 18:20 | 2014-02-28 10:50 | 990 | 11kV | 146010 | 1039 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9245 Engadine - Pnl 14 - Trip/reclose/trip, EF, EFI, Lockout, Field EFIs. Tree branch brought down wires in Jerrara St. HV into LV Emso called to check 10 Jerrara St earth bonds open cct. ME: 1082859. Rest Steps: 1082860, 1. Withdrawn: 1082035, 49, 50. | February | 2014 | 2014Q3 | 2014 | ZN9245:PA14 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Veg | 2014-02-27 | N | 140.5294 | N | 9 | N | N | 1.1101 | 39.4971 | 106699.8014
[7 empty] | 16266 | 17624 | 1082083 | 2014-02-28 07:59 | 2014-02-28 12:00 | 241 | 11kV | 1848 | 39 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 149524 2 fault operations LV ABC in contact with HV Tx bushing. Excluded OMS 1082083 | February | 2014 | 2014Q3 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-02-28 | N | 47.3846 | N | 5 | N | N | 1.1101 | 39.4971 | 1350.4639
[7 empty] | 15598 | 9547 | 1082135 | 2014-02-28 08:55 | 2014-02-28 18:25 | 570 | 11kV | 11537 | 108 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Rain Heavy | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" RE44602 Ourimbah Creek Road opened * locked out on overcurrent Cause: Heavy Rain. Auto link 42941 defective not grading. Warning tagged by DOp. See 1082862,4,5 Exclude 1082290,135 | February | 2014 | 2014Q3 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2014-02-28 | N | 106.8241 | N | 5 | N | N | 1.1101 | 39.4971 | 8430.8993
[7 empty] | 15030 | 3058 | 1082409 | 2014-02-28 17:15 | 2014-02-28 19:15 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Rain Light | N | LID 149529 Single phase DOLF : 10 Amp Operator reported no obvious cause | February | 2014 | 2014Q3 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2014-02-28 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 16159 | 16593 | 1082461 | 2014-02-28 23:23 | 2014-03-01 00:36 | 73 | 11kV | 204756 | 2852 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Rain Light | N | At S35500 Top Ryde Panel 24R Labelled Arnold Frederick tripped on IOC A and B phase Abnormal Switching: SWB Closed at S7493, AB501 Open Cause: Dead Bat found O/S Beach St Tennison See OMS 1082823 1082824 1082461 | February | 2014 | 2014Q3 | 2014 | ZN35500:PA24 | ZN35500:PA24 | ZN35500/000024 | RYDE | OH | Not Veg | 2014-02-28 | N | 71.7938 | N | 5 | N | N | 1.1101 | 39.4971 | 149629.6455
[7 empty] | 15578 | 9199 | 1082435 | 2014-02-28 18:34 | 2014-03-01 01:50 | 436 | 11kV | 10740 | 47 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 149530 3 fault operations 3 phase Sensitive Earth Fault, Earth Fault, Overcurrent HV main down at pole 8K-40108,Live line connector lead at pole 8k-40090 had burnt off and was shorting. This line line conenctor supplies subs 70966 and beyond. Excluded OMS 1082435, 1082453 & 1082454 | February | 2014 | 2014Q3 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2014-02-28 | N | 228.5106 | N | 5 | N | N | 1.1101 | 39.4971 | 7848.4752
[7 empty] | 15349 | 6802 | 1082468 | 2014-03-01 03:39 | 2014-03-01 04:30 | 51 | 11kV | 3111 | 61 | HV | Animal Possum | Animal | DC PT | Unplanned | Rain Light | N | PT12152 Hilltop The Brow Right hand side and middle HDO's 31.5K HV fuses blown due to Possum See 1082917 exclude 1082468,9,70 | March | 2014 | 2014Q3 | 2014 | ZN14144:PA1 | ZN14144:PA1 | ZN14144/000001 | CENTRAL COAST | OH | Not Veg | 2014-03-01 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 2273.427
[7 empty] | 15161 | 4232 | 1082516 | 2014-03-01 09:44 | 2014-03-01 13:20 | 216 | 11kV | 48312 | 681 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 149531 1 fault operation Sensitive Earth Fault Broken X arm pole AI-90374 Excluded OMS 1082516, 1082525 & 1082549 | March | 2014 | 2014Q3 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2014-03-01 | N | 70.9427 | N | 4 | N | N | 1.1101 | 39.4971 | 35304.9846
[7 empty] | 16252 | 17527 | 1082583 | 2014-03-01 13:26 | 2014-03-01 15:20 | 114 | 11kV | 114 | 1 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Rain Light | N | LID 149533 Single phase DOLF : 5 Amp | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2014-03-01 | N | 114 | N | 4 | N | N | 1.1101 | 39.4971 | 83.3078
[7 empty] | 15259 | 5786 | 1082612 | 2014-03-01 15:51 | 2014-03-01 16:51 | 60 | 11kV | 54540 | 909 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S965 Pennant Hiss 11kV feeder panel no 26 tripped reclosed tripped and locked out on Relays: Times Earth Fault, Lockout, Timing and EFI Cause: UG fault in section of 11kV feeder from Pa26 to S6153 Victoria Wilson SW/A See OMS 1082914 1082612 | March | 2014 | 2014Q3 | 2014 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | UG | Not Veg | 2014-03-01 | N | 60 | N | 4 | N | N | 1.1101 | 39.4971 | 39856.2233
[7 empty] | 15670 | 10697 | 1082673 | 2014-03-02 07:28 | 2014-03-02 07:37 | 9 | 11kV | 1539 | 171 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | LID 149534 C phase Interruption to bypass Glendon Rd Reg 47921 due to faulty Cph Reg stuck on top tap and not indicating correctly. | March | 2014 | 2014Q3 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-03-02 | N | 9 | N | 3 | N | N | 1.1101 | 39.4971 | 1124.6558
[7 empty] | 15814 | 12266 | 1082716 | 2014-03-02 10:25 | 2014-03-02 12:15 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 149537 B phase DOLF : 31 Amp Tx. Volts : 246V Excluded OMS 1082716 | March | 2014 | 2014Q3 | 2014 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Veg | 2014-03-02 | N | 110 | N | 3 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 16445 | 19907 | 1082742 | 2014-03-02 12:50 | 2014-03-02 17:00 | 250 | 11kV | 500 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149538 C phase DOLF : 10 Amp LA blown on C phase. Replaced. Excluded OMS No. 1082742 | March | 2014 | 2014Q3 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-03-02 | N | 250 | N | 3 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 15647 | 10386 | 1082813 | 2014-03-03 07:14 | 2014-03-03 07:55 | 41 | 11kV | 802.9 | 20 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12732 Lake Munmorah section of Pa8 @PT12732 David Norah centre phase HDO fuse blown.Centre phase LA blown unable to cut away. Resotred via LV// See 1082813 GIS 1082816 | March | 2014 | 2014Q3 | 2014 | ZN13000:PA8 | ZN13000:PA8 | ZN13000/000008 | CENTRAL COAST | OH | Not Veg | 2014-03-03 | N | 40.145 | N | 3 | N | N | 1.1101 | 39.4971 | 586.7356
[7 empty] | 16324 | 18234 | 1083018 | 2014-03-03 11:07 | 2014-03-03 12:29 | 82 | 11kV | 173090 | 2233 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 10999 Kogarah - Pnl 11 - A & B phase IOC, EFI, Field EFIs. 11kV fault from S 10005 to AB 31199 to S 10194. ME: 1083744. Rest Step: 1083745. ME GIS: 1083082, 98. | March | 2014 | 2014Q3 | 2014 | ZN10999:PA11 | ZN10999:PA11 | ZN10999/000011 | BAYSIDE | UG | Not Veg | 2014-03-03 | N | 77.5146 | N | 3 | N | N | 1.1101 | 39.4971 | 126489.0667
[7 empty] | 15554 | 8962 | 1083300 | 2014-03-03 20:06 | 2014-03-04 00:35 | 269 | 11kV | 60525 | 225 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | PT 10935 Ashton Princes - Centre Phase HDO fuse. 11kV Dropout fuse assembly failed. ME: 1083355. Withdrawn: 1083300. | March | 2014 | 2014Q3 | 2014 | ZN10999:PA19 | ZN10999:PA19 | ZN10999/000019 | BAYSIDE | OH | Not Veg | 2014-03-03 | N | 269 | N | 3 | N | N | 1.1101 | 39.4971 | 44229.8848
[7 empty] | 15752 | 11663 | 1083322 | 2014-03-04 07:31 | 2014-03-04 10:30 | 179 | 11kV | 358 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex ZN12630 Peats Ridge section of 11kV VCB Pa2 "Gunderman" fdr @PT11214 Morgan Pacific 1.5 20Amp C phase HVDO operated Possible fuse fatigue See 1083839 excludes 1083322 | March | 2014 | 2014Q3 | 2014 | ZN12630:PA2 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2014-03-04 | N | 179 | N | 1 | N | N | 1.1101 | 39.4971 | 261.6158
[7 empty] | 15907 | 13217 | 1083727 | 2014-03-05 01:49 | 2014-03-05 02:29 | 40 | 11kV | 21560 | 539 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149553 1 fault operation Earth fault | March | 2014 | 2014Q3 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-03-05 | N | 40 | N | 14 | N | N | 1.1101 | 39.4971 | 15755.4121
[7 empty] | 15731 | 11390 | 1083728 | 2014-03-05 03:17 | 2014-03-05 05:03 | 106 | 11kV | 149436 | 1902 | HV | Animal Possum | Animal | Circuit Breaker | Unplanned | Unselected | N | ZN 9118 Cronulla - Pnl 11 - B & C phase IOC. Possum located at Corner of Eric and Baker Sts, Bundeena. ME: 1083843. Rest Step: 1083845. Withdrawn: 1083728, 30. | March | 2014 | 2014Q3 | 2014 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2014-03-05 | N | 78.5678 | N | 14 | N | N | 1.1101 | 39.4971 | 109203.4212
[7 empty] | 15262 | 5851 | 1083729 | 2014-03-05 03:25 | 2014-03-05 05:36 | 131 | 11kV | 136109 | 1039 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | ZN 9245 Engadine - Pnl 13 - Trip/reclose/trip, 3 phase Overload, Lockout. Cause not ascertained. Mains to patrol in daylight hours. ME: 1083729. Withdrawn: 1083733. | March | 2014 | 2014Q3 | 2014 | ZN9245:PA14 | ZN9245:PA1 | ZN09245/000001 | SUTHERLAND | OH | Veg | 2014-03-05 | N | 131 | N | 14 | N | N | 1.1101 | 39.4971 | 99464.4427
[7 empty] | 15625 | 10048 | 1084145 | 2014-03-05 16:18 | 2014-03-05 17:52 | 94 | 11kV | 97572 | 1038 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | ZN 9550 Gwawley Bay - Pnl 43 - Trip/reclose/trip, All phases OC, EFI, Field EFI. Lightning at AB 35327 has blown 11kV insulators on the Pnl 43 side. ME: 1084145. Withdrawn: 1084239, 40, 53, 60. | March | 2014 | 2014Q3 | 2014 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2014-03-05 | N | 94 | N | 14 | N | N | 1.1101 | 39.4971 | 71302.7397
[7 empty] | 15141 | 4062 | 1084149 | 2014-03-05 16:30 | 2014-03-05 18:29 | 119 | 11kV | 153867 | 1293 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | N | ZN 9550 Gwawley Bay - Pnl 3 - IOC, Field EFIs. Lightning strike hit pole outside 2 Mowbray st, Sylvania. Lineworker has inspected and no damage. | March | 2014 | 2014Q3 | 2014 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | OH | Not Veg | 2014-03-05 | N | 119 | N | 14 | N | N | 1.1101 | 39.4971 | 112441.4653
[7 empty] | 14739 | 355 | 1084292 | 2014-03-05 20:06 | 2014-03-05 20:36 | 30 | 11kV | 54060 | 1802 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149573 2 Fault Operations Phases A & B Overcurrent | March | 2014 | 2014Q3 | 2014 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2014-03-05 | N | 30 | N | 14 | N | N | 1.1101 | 39.4971 | 39505.4535
[7 empty] | 15737 | 11473 | 1084155 | 2014-03-05 16:32 | 2014-03-05 21:08 | 276 | 11kV | 531638 | 2275 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN 10999 Kogarah - Pnl 29 - All phases Overcurrent, Earth fault check relay, EFI, Tx 3 Earth fault check relay. Lightning in area. Patrolled by DOP. No cause found. Lineworker to patrol . ME: 1084700. Rest Steps: 1084701, 3, 4. Withdrawn: 1084155. | March | 2014 | 2014Q3 | 2014 | ZN10999:PA29 | ZN10999:PA29 | ZN10999/000029 | BAYSIDE | OH | Veg | 2014-03-05 | N | 233.687 | N | 14 | N | N | 1.1101 | 39.4971 | 388505.3697
[7 empty] | 16018 | 14874 | 1084148 | 2014-03-05 16:25 | 2014-03-05 21:53 | 328 | 11kV | 366128 | 1382 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Lightning | N | ZN 10991 Blakehurst - Pnl 12 - c phase timed overcurrent, EFI, Field EFIs. Lightning in area. LB 30535 is welded closed. Mains to patrol feeder in daylight hours. ME: 1084718. Rest Steps: 1084719, 20, 21. ME GIS: 1084249, 65, 81, 88. Withdrawn: 1084227, 82, 1084148. | March | 2014 | 2014Q3 | 2014 | ZN10991:PA12 | ZN10991:PA12 | ZN10991/000012 | GEORGES RIVER | UG | Not Veg | 2014-03-05 | N | 264.9262 | N | 14 | N | N | 1.1101 | 39.4971 | 267555.5435
[7 empty] | 14969 | 2523 | 1084299 | 2014-03-05 20:18 | 2014-03-05 22:30 | 132 | 11kV | 264 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149576 Phase A - Fuse size: 5 Amp Line DOLF Excluded job 1084299 | March | 2014 | 2014Q3 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-03-05 | N | 132 | N | 14 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 15120 | 3895 | 1084309 | 2014-03-05 21:28 | 2014-03-05 22:43 | 75.45 | 11kV | 2640.75 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Electrical Storm | N | LID 149575 A Phase - Fuse size: 16 Amp Substation DOLF | March | 2014 | 2014Q3 | 2014 | 238:34141 | 264:81240 | ZN00264/081240 | PORT STEPHENS | UG | Not Veg | 2014-03-05 | N | 75.45 | N | 14 | N | N | 1.1101 | 39.4971 | 1929.7822
[7 empty] | 15282 | 6243 | 1084064 | 2014-03-05 22:56 | 2014-03-05 23:58 | 62 | 11kV | 138886 | 2426 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7481 Darling Harbour - Pnl.1 tripped on : A + B phase O/C, EFI Field EFIs: S5786 S8382 S26 S48298 S1882 S2974 UG Cable fault between S2974 Lyndhurst Broughton Sw B and S369 Norton St Sw A. Cable fault in S369 see 1084364 1084365 | March | 2014 | 2014Q3 | 2014 | ZN7481:PA1 | ZN7481:PA1R | ZN07481/000001 | SYDNEY | UG | Not Veg | 2014-03-05 | N | 57.249 | N | 14 | N | N | 1.1101 | 39.4971 | 101493.7924
[7 empty] | 16064 | 15522 | 1084252 | 2014-03-05 21:00 | 2014-03-06 00:35 | 215 | 11kV | 49020 | 228 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 149574 Section Isolated to repair tappings at ABS 3605 & ABS 5550 Excluded OMS 1084259 | March | 2014 | 2014Q3 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2014-03-05 | N | 215 | N | 14 | N | N | 1.1101 | 39.4971 | 35822.3702
[7 empty] | 14844 | 1318 | 1084298 | 2014-03-05 20:16 | 2014-03-06 01:00 | 284 | 11kV | 568 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149577 Phases A & B - Fuse size: 5 Amp Line DOLF Excluded 1084298 | March | 2014 | 2014Q3 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2014-03-05 | N | 284 | N | 14 | N | N | 1.1101 | 39.4971 | 415.0776
[7 empty] | 16485 | 20283 | 1084326 | 2014-03-06 00:10 | 2014-03-06 01:05 | 55 | 11kV | 1870 | 34 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | Ex Zn12620 Noraville section of 11kv VCB Pa1L fdr @PT12562 Karangal Nth Buff - 11kv Lightning Arrestor found arcing DOp interupted PT125662 @0100 via 11kv dropout fuses. PT restored via LV// LV// links closed #15601,17101,30534 See 1084468 exclude 1084326,7 | March | 2014 | 2014Q3 | 2014 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Not Veg | 2014-03-06 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 16019 | 14875 | 1084171 | 2014-03-05 16:41 | 2014-03-06 01:15 | 514 | 11kV | 135645 | 873 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN 10996 Rockdale - Trip/reclose/trip, B phase Earth fault, timing, lockout, Field EFI. Section of 11kV feeder from LB 31116 to S 10402 tee PT 10050 is isolated. Sw/tag left at LV 31116. Not LB 31116 is defective as well. ME: 1084960. Rest Steps: 1084962, 3, 4, 5, 7. ME GIS: 1084174, 213. Withdrawn: 1084171. | March | 2014 | 2014Q3 | 2014 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Veg | 2014-03-05 | N | 155.378 | N | 14 | N | N | 1.1101 | 39.4971 | 99125.3651
[7 empty] | 15173 | 4336 | 1084337 | 2014-03-06 06:25 | 2014-03-06 09:35 | 190 | 11kV | 950 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 149580 C Phase DOLF : 10 Amp Excluded OMS 1084337 | March | 2014 | 2014Q3 | 2014 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | UG | Not Veg | 2014-03-06 | N | 190 | N | 4 | N | N | 1.1101 | 39.4971 | 694.232
[7 empty] | 15726 | 11352 | 1084860 | 2014-03-06 06:55 | 2014-03-06 14:15 | 440 | 11kV | 33144 | 578 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149588 1 Fault Operations Sensitive Earth Fault Excluded jobs 1084340 & 1084350 | March | 2014 | 2014Q3 | 2014 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2014-03-06 | N | 57.3426 | N | 4 | N | N | 1.1101 | 39.4971 | 24220.6576
[7 empty] | 14959 | 2388 | 1084698 | 2014-03-06 14:53 | 2014-03-06 16:15 | 82 | 11kV | 82 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Previous Storm | N | LID 149591 C Phase - DOLF: 10 Amp | March | 2014 | 2014Q3 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | UG | Not Veg | 2014-03-06 | N | 82 | N | 4 | N | N | 1.1101 | 39.4971 | 59.9232
[7 empty] | 14805 | 985 | 1084810 | 2014-03-07 02:40 | 2014-03-07 03:10 | 30 | 11kV | 18990 | 633 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149594 4 fault operations No fault found Excluded OMS 1084810 | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-03-07 | N | 30 | N | 6 | N | N | 1.1101 | 39.4971 | 13877.3319
[7 empty] | 14908 | 1976 | 1084820 | 2014-03-07 06:59 | 2014-03-07 07:50 | 50.65 | 11kV | 2076.65 | 41 | HV | Animal Flying Fox | Animal | DC PT | Unplanned | Unselected | N | Ex Zn14144 Wamberal section of Pa8 "Beaufort SPS C5" @PT12392 Willoughby Beaufort centre and roadside 31.5 Amp HDO Operated Bat caused flashover, removed by DOp, no damage See 1084825 exclude 1084820 CC1: 22-"Refer to SOp" | March | 2014 | 2014Q3 | 2014 | ZN14144:PA8 | ZN14144:PA8 | ZN14144/000008 | CENTRAL COAST | OH | Not Veg | 2014-03-07 | N | 50.65 | N | 6 | N | N | 1.1101 | 39.4971 | 1517.5546
[7 empty] | 14749 | 463 | 1085617 | 2014-03-07 02:40 | 2014-03-07 08:55 | 375 | 11kV | 244367 | 784 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149594 4 fault operations No fault found Note 2nd trip and lock out same night - refer to 1085613 | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-03-07 | N | 311.6926 | N | 6 | N | N | 1.1101 | 39.4971 | 178576.196
[7 empty] | 14947 | 2236 | 1085050 | 2014-03-07 12:28 | 2014-03-07 14:32 | 124 | 11kV | 1116 | 9 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149612 A phase DOLF : 10 Amp fuse holder found broken Excluded oms 1085050 | March | 2014 | 2014Q3 | 2014 | 227:13018 | 227:13018 | ZN00227/013018 | LAKE MACQUARIE | OH | Not Veg | 2014-03-07 | N | 124 | N | 6 | N | N | 1.1101 | 39.4971 | 815.5399
[7 empty] | 15829 | 12441 | 1085225 | 2014-03-07 18:44 | 2014-03-07 19:50 | 66 | 11kV | 264 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149614 C phase DOLF : 10 Amp excluded OMS 1085225 | March | 2014 | 2014Q3 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2014-03-07 | N | 66 | N | 6 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 16365 | 18703 | 1085187 | 2014-03-07 16:14 | 2014-03-08 01:25 | 551 | 11kV | 12203 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149613 1 fault operation Overcurrent Faulty tx at sub 70301 changed under AP. Excluded OMS 1085187 & 1085192. | March | 2014 | 2014Q3 | 2014 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2014-03-07 | N | 225.9815 | N | 6 | N | N | 1.1101 | 39.4971 | 8917.5925
[7 empty] | 15285 | 6280 | 1085243 | 2014-03-08 02:06 | 2014-03-08 03:03 | 57 | 11kV | 39330 | 690 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S.36300 Balgowlah North, Panel 7 Fdr CB tripped on C phase IOC. A flying fox found at base of pole at cnr. Woodlands and Griffiths Sts | March | 2014 | 2014Q3 | 2014 | ZN36300:PA7 | ZN36300:PA7 | ZN36300/000007 | NORTHERN BEACHES | OH | Not Veg | 2014-03-08 | N | 57 | N | 4 | N | N | 1.1101 | 39.4971 | 28741.204
[7 empty] | 15308 | 6497 | 1085253 | 2014-03-08 07:39 | 2014-03-08 09:06 | 87 | 11kV | 111700 | 1373 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 149620 4 fault operations Suspected cable fault between UGOH pole HR-22201 & Sw 56574 Hunter supa centre No 2 sub. Excluded OMS 1085253 | March | 2014 | 2014Q3 | 2014 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | UG | Not Veg | 2014-03-08 | N | 81.3547 | N | 4 | N | N | 1.1101 | 39.4971 | 81627.0654
[7 empty] | 16138 | 16383 | 1085268 | 2014-03-08 08:38 | 2014-03-08 10:50 | 132 | 11kV | 132 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149621 DOLF : 10 Amp Excluded OMS 1085268 | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2014-03-08 | N | 132 | N | 4 | N | N | 1.1101 | 39.4971 | 96.4617
[7 empty] | 14779 | 746 | 1085274 | 2014-03-08 08:45 | 2014-03-08 11:40 | 175 | 11kV | 350 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149622 DOLF : 10 Amp Excluded OMS 1085274 | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | UG | Not Veg | 2014-03-08 | N | 175 | N | 4 | N | N | 1.1101 | 39.4971 | 255.7697
[7 empty] | 14965 | 2459 | 1085379 | 2014-03-09 03:58 | 2014-03-09 05:15 | 77 | 11kV | 77 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149623 A phase DOLF : 10 Amp Excluded OMS 1085379 | March | 2014 | 2014Q3 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | UG | Not Veg | 2014-03-09 | N | 77 | N | 2 | N | N | 1.1101 | 39.4971 | 56.2693
[7 empty] | 15497 | 8423 | 1085386 | 2014-03-09 07:06 | 2014-03-09 08:15 | 69 | 11kV | 71139 | 1031 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12640 Umina section of Pa13 "Patonga" 11kv bond centre phase a pole donstream of LB45147 was open. Aux supply fail RE47749 & RE47746 See 1086591 exclude 1085385,6,7,8,9,90,1,2,3,5,7 | March | 2014 | 2014Q3 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2014-03-09 | N | 69 | N | 2 | N | N | 1.1101 | 39.4971 | 51986.283
[7 empty] | 15885 | 13000 | 1085511 | 2014-03-10 08:47 | 2014-03-10 09:55 | 68 | 11kV | 136 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149630 B phase DOLF : 10 Amp Excluded OMS 1085511 | March | 2014 | 2014Q3 | 2014 | 213:33773 | 213:33773 | ZN00213/033773 | NEWCASTLE | UG | Not Veg | 2014-03-10 | N | 68 | N | 2 | N | N | 1.1101 | 39.4971 | 99.3848
[7 empty] | 16062 | 15505 | 1085755 | 2014-03-10 12:58 | 2014-03-10 18:20 | 322 | 11kV | 35941 | 315 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 149640 1 fault operation A & B phases Overcurrent Planned outages for SI 40996, 40893 & 40847 in place at time of fault. Damaged single phase 11kV OHM between poles GW-40236 & GW-40235. Cph tapping burnt off ABS 18855. Excluded OMS No. 1085755 + 1085759 + 1085866 | March | 2014 | 2014Q3 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2014-03-10 | N | 114.0984 | N | 2 | N | N | 1.1101 | 39.4971 | 26264.6227
[7 empty] | 16144 | 16428 | 1086679 | 2014-03-12 13:05 | 2014-03-12 16:45 | 220 | 11kV | 220 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 149665 Single Phase No protection operation, faulty live line lead detached from top of DOLF. Excluded OMS 1086679 | March | 2014 | 2014Q3 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-03-12 | N | 220 | N | 3 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 15649 | 10408 | 1086839 | 2014-03-12 20:01 | 2014-03-12 21:15 | 74 | 11kV | 296 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 149668 A Phase LV fuse loose in carrier, fuse removed and re-inserted, volts then ok. Suspect fuse had vibrated loose. Excluded OMS 1086839 | March | 2014 | 2014Q3 | 2014 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-03-12 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 216.3081
[7 empty] | 16042 | 15315 | 1086922 | 2014-03-13 08:30 | 2014-03-13 09:42 | 72 | 11kV | 1008 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 149678 B Phase - Fuse Size: 31 Amp Substation DOLF Excluded OMS 1086935 | March | 2014 | 2014Q3 | 2014 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | UG | Not Veg | 2014-03-13 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 736.6167
[7 empty] | 16242 | 17489 | 1087131 | 2014-03-13 14:37 | 2014-03-13 16:11 | 94 | 11kV | 141564 | 1506 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | ZN12580 Erina Pa10 "Eina High Ernest" fdr tripped on Aph IOC, Timed Overcurrent, Sensitive Earth Leakage, EFI EFI down @ S14189 only. No signals/alarms @ Zone or on SCADA DOp Patrolled feeder nothing found See 1087131 GIS 1087134 Exclude 1087136 | March | 2014 | 2014Q3 | 2014 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2014-03-13 | N | 94 | N | 3 | N | N | 1.1101 | 39.4971 | 103450.7958
[7 empty] | 16364 | 18702 | 1087206 | 2014-03-13 18:13 | 2014-03-13 18:29 | 16 | 11kV | 6064 | 379 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Zn12610 Long Jetty Pa2 "Shely Beach" fdr tripped on A,C phase IOC, Earth Fault, Fault check @PT13650 Bateau Bay Lakin HV fuse blown Fuse Fatigue/ Failure ABNORMAL USL40266 open USL43644 open D&R333622 See 1088660 exclude 1087206 | March | 2014 | 2014Q3 | 2014 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Not Veg | 2014-03-13 | N | 16 | N | 3 | N | N | 1.1101 | 39.4971 | 4431.3923
[7 empty] | 15576 | 9167 | 1087233 | 2014-03-14 00:07 | 2014-03-14 01:17 | 70 | 11kV | 3175 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12600 Lisarow Zn 11kv trip Pa5 "Pacific Parsons" tripped on the following: C phase IOC, Timed Overcurrent, EFI EFI's: Nil ABNORMAL: S14059/D closed, USL 41285 open and defective Cause not ascertained Note Auto Reclose did not appear to operate TPE to investigate See 1088686,8 exclude 1087233 | March | 2014 | 2014Q3 | 2014 | ZN12600:PA5 | ZN12600:PA5 | ZN12600/000005 | CENTRAL COAST | OH | Veg | 2014-03-14 | N | 69.0217 | N | 15 | N | N | 1.1101 | 39.4971 | 2320.1964
[7 empty] | 16125 | 16212 | 1087286 | 2014-03-14 02:40 | 2014-03-14 05:15 | 155 | 11kV | 4185 | 27 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | Interr. feeder beyond Sw 74812 to replace faulty transformeR ALSO See OMS 1087285 | March | 2014 | 2014Q3 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-03-14 | N | 155 | N | 15 | N | N | 1.1101 | 39.4971 | 3058.2746
[7 empty] | 15352 | 6826 | 1087275 | 2014-03-14 08:25 | 2014-03-14 08:40 | 15 | 11kV | 1920 | 128 | HV | 3rd Party Action | 3rd Party Impact | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149688 A, B & C Phases Sensitive Earth Fault Essential energy made parrallel ring into ausgrid system on fdr that was not setup. request was insufficent or not correct for job refer SI N0135 Excluded OMS 1087275 | March | 2014 | 2014Q3 | 2014 | 508:82578 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2014-03-14 | N | 15 | N | 15 | N | N | 1.1101 | 39.4971 | 1403.0794
[7 empty] | 15713 | 11080 | 1087358 | 2014-03-14 15:25 | 2014-03-14 17:20 | 115 | 11kV | 31814 | 978 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 149731 Part supply to multiple customers until isolated No Protection Tapping Burnt off at pole HR-20626, near green st depot. Excluded OMS 1087358 & 1087404 | March | 2014 | 2014Q3 | 2014 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2014-03-14 | N | 32.5297 | N | 15 | N | N | 1.1101 | 39.4971 | 23248.7328
[7 empty] | 15069 | 3415 | 1087409 | 2014-03-14 16:42 | 2014-03-14 17:28 | 46 | 11kV | 11035 | 270 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149724 2 fault operation Earth fault Excluded OMS 1087409 | March | 2014 | 2014Q3 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Veg | 2014-03-14 | N | 40.8704 | N | 15 | N | N | 1.1101 | 39.4971 | 8064.0525
[7 empty] | 15903 | 13192 | 1087411 | 2014-03-14 16:49 | 2014-03-14 17:43 | 54 | 11kV | 97362 | 1803 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149719 2 Fault Operations Overcurrent, Earth Fault A & B Phases, OC + EF | March | 2014 | 2014Q3 | 2014 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2014-03-14 | N | 54 | N | 15 | N | N | 1.1101 | 39.4971 | 71149.2779
[7 empty] | 16348 | 18534 | 1087401 | 2014-03-14 16:25 | 2014-03-14 17:50 | 85 | 11kV | 765 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149715 Single Phase - Fuse Size: 20 Amp Line DOLF Blown Spur Fuse Excluded OMS 1087405 | March | 2014 | 2014Q3 | 2014 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-03-14 | N | 85 | N | 15 | N | N | 1.1101 | 39.4971 | 559.0394
[7 empty] | 14882 | 1762 | 1087447 | 2014-03-14 18:13 | 2014-03-14 19:40 | 87.1 | 11kV | 4616.3 | 53 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | LID 149722 A, B & C Phases - Fuse Size: 20 Amp Line DOLF | March | 2014 | 2014Q3 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2014-03-14 | N | 87.1 | N | 15 | N | N | 1.1101 | 39.4971 | 3373.4559
[7 empty] | 15390 | 7353 | 1087471 | 2014-03-14 19:35 | 2014-03-14 21:30 | 115 | 11kV | 115 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 149735 B phase DOLF : 10 Amp Excluded OMS 1087471 | March | 2014 | 2014Q3 | 2014 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2014-03-14 | N | 115 | N | 15 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 14982 | 2661 | 1087450 | 2014-03-14 18:17 | 2014-03-14 21:40 | 203 | 11kV | 203 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Electrical Storm | N | LID 149736 A Phase - Fuse Size: 10 Amp Substation DOLF Excluded OMS job 1087450 | March | 2014 | 2014Q3 | 2014 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | UG | Not Veg | 2014-03-14 | N | 203 | N | 15 | N | N | 1.1101 | 39.4971 | 148.3464
[7 empty] | 15086 | 3539 | 1089998 | 2014-03-14 18:01 | 2014-03-14 21:50 | 229 | 11kV | 3206 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 149732 3 phase DOLF : 20 Amp | March | 2014 | 2014Q3 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-03-14 | N | 229 | N | 15 | N | N | 1.1101 | 39.4971 | 2342.8502
[7 empty] | 15513 | 8603 | 1087445 | 2014-03-14 18:01 | 2014-03-14 22:15 | 254 | 11kV | 508 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149733 Single phase DOLF : 2 Amp Outage time was due to unplanned outage 149732 Blown spur fuses 40759 Excluded OMS 1087480 & 1087445 | March | 2014 | 2014Q3 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2014-03-14 | N | 254 | N | 15 | N | N | 1.1101 | 39.4971 | 371.2314
[7 empty] | 16314 | 18143 | 1085820 | 2014-03-14 16:57 | 2014-03-14 23:15 | 378 | 11kV | 1512 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | LID 149740 A, B & C Phases - Fuse size: 10 Amp Line DOLF Excluded OMS 1085820 | March | 2014 | 2014Q3 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-03-14 | N | 378 | N | 15 | N | N | 1.1101 | 39.4971 | 1104.925
[7 empty] | 15226 | 5189 | 1087526 | 2014-03-15 07:24 | 2014-03-15 09:05 | 101.35 | 11kV | 2027 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 149751 B Phase - Fuse Size: 10 Amp Line DOLF CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | March | 2014 | 2014Q3 | 2014 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2014-03-15 | N | 101.35 | N | 6 | N | N | 1.1101 | 39.4971 | 1481.2718
[7 empty] | 15661 | 10581 | 1087420 | 2014-03-14 17:12 | 2014-03-15 13:15 | 1203 | 11kV | 9623 | 11 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 149723 4 fault operations Single phase Earth fault Excluded OMS 1087418, 1087420 | March | 2014 | 2014Q3 | 2014 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2014-03-14 | N | 874.8182 | N | 15 | N | N | 1.1101 | 39.4971 | 7032.2046
[7 empty] | 15500 | 8466 | 1087516 | 2014-03-15 00:40 | 2014-03-15 14:05 | 805 | 11kV | 2415 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149756 DORF Mick Martin isolated sub at LVF due to customers MSB being damaged. John Frazer retuurned to reinstall LV fuses later same day. Excluded OMS 1087516 & 1087585. | March | 2014 | 2014Q3 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-03-15 | N | 805 | Y | 6 | N | Y | 1.1101 | 39.4971 | 1764.8108
[7 empty] | 15020 | 2983 | 1088524 | 2014-03-15 17:17 | 2014-03-15 17:58 | 41 | 11kV | 55555 | 1355 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | At S4545 Meadowbank Panel 35 Tripped on A and C phase O/C Alarmas; No3 Tx Group Earth, Cause: Suspect lighting | March | 2014 | 2014Q3 | 2014 | ZN4545:PA35 | ZN4545:PA35 | ZN04545/000035 | RYDE | OH | Not Veg | 2014-03-15 | N | 41 | N | 6 | N | N | 1.1101 | 39.4971 | 40597.9554
[7 empty] | 15298 | 6414 | 1087621 | 2014-03-15 17:21 | 2014-03-15 18:42 | 81 | 11kV | 210372 | 3109 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | N | At S35500 Top Ryde Pa28R Opened on Triped and EFI indicatior Cause: 11kV UGOH to SW/A at S49473 damaged by lightning See OMS 1088746 1088757 1088762 1087621 1087624 | March | 2014 | 2014Q3 | 2014 | ZN35500:PA28 | ZN35500:PA28 | ZN35500/000028 | RYDE | OH | Not Veg | 2014-03-15 | N | 67.6655 | N | 6 | N | N | 1.1101 | 39.4971 | 153733.6527
[7 empty] | 15585 | 9340 | 1087614 | 2014-03-15 17:11 | 2014-03-15 18:45 | 94 | 11kV | 197121 | 2107 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | ZN 10995 Riverwood - Pnl 7 - Trip/reclose/trip, A & C phase IOC and Timed OC, reclose timer, Lockout, EFI, Field EFIs. Report of lightning strike opposite 39A Mountview Av, Narwee. DOp reports that AB 30061 is at this address which is the normally ope point between Pnl 1 and Pnl 7. ME: 1089007. Rest Step: 1089008. Withdrawn: 1087614, 32. | March | 2014 | 2014Q3 | 2014 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2014-03-15 | N | 93.5553 | N | 6 | N | N | 1.1101 | 39.4971 | 144050.2127
[7 empty] | 15831 | 12461 | 1087619 | 2014-03-15 17:12 | 2014-03-15 19:08 | 116 | 11kV | 236060 | 2035 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | ZN 10995 Riverwood - Pnl 1 - Trip/reclose/trip, A & C phase IOC and Timed OC, timer, lockout, EFI, Field EFIs. Report of lightning strike opposite 39A Mountview Av, Narwee. DOp reports that AB 30061 is at this address which is the normally open point between Pnl 1 and Pnl 7. | March | 2014 | 2014Q3 | 2014 | ZN10995:PA1 | ZN10995:PA1 | ZN10995/000001 | GEORGES RIVER | OH | Not Veg | 2014-03-15 | N | 116 | N | 6 | N | N | 1.1101 | 39.4971 | 172505.6854
[7 empty] | 16108 | 16050 | 1087403 | 2014-03-14 16:23 | 2014-03-15 19:54 | 1651 | 11kV | 24527 | 23 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 149714 3 fault operations Overcurrent Trees hit mains near sub 46317. Broken X arm. WIre off pin beyond links 6708. Excluded OMS 1087403 + 1087513 + 1087444 | March | 2014 | 2014Q3 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-03-14 | N | 1066.3913 | N | 15 | N | N | 1.1101 | 39.4971 | 17923.6082
[7 empty] | 15953 | 13743 | 1087661 | 2014-03-15 18:26 | 2014-03-15 21:28 | 182 | 11kV | 546 | 3 | HV | Animal Bird | Animal | DC PT | Unplanned | Electrical Storm | N | LID 149764 Single Phase - Fuse Size: 10 Amp Substation DOLF Dead bird at base of pole Excluded OMS jobs 1087736 & 1087661 | March | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-03-15 | N | 182 | N | 6 | N | N | 1.1101 | 39.4971 | 399.0007
[7 empty] | 15774 | 11856 | 1087826 | 2014-03-16 12:33 | 2014-03-16 14:04 | 91 | 11kV | 10465 | 115 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | Y | At S.15013 Terrey Hills, Panel 6 Fdr CB tripped, reclosed, tripped and locked out on C phase IOC, OC, timing and lockout relays, 11kV trip signal. Tree branch on mains near link 24464 | March | 2014 | 2014Q3 | 2014 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 91 | N | 14 | N | Y | 1.1101 | 39.4971 | 7647.5133
[7 empty] | 15635 | 10141 | 1087827 | 2014-03-16 12:33 | 2014-03-16 14:50 | 137 | 11kV | 316333 | 2309 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | At S.15008 Harbord, Panel 1 Fdr CB ytipped, reclosed and tripped - locked out on A and C phase IOC, 11kV trip signal. Storm activity at the time. | March | 2014 | 2014Q3 | 2014 | ZN15008:PA1 | ZN15008:PA6 | ZN15008/000006 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 137 | N | 14 | N | Y | 1.1101 | 39.4971 | 231166.8262
[7 empty] | 15156 | 4187 | 1087909 | 2014-03-16 13:45 | 2014-03-16 15:35 | 110 | 11kV | 173511 | 1830 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | Y | Zn12600 Lisarow Pa9 "Wyoming South" fdr tripped and locked out on Relays: A phase IOC, timmed, EFI EFI's: S14991 S148921 S18461 S14686 Signals: 11kv trip @PT13860 Taylors Charmberlain 16K fotpath phase HVDO operated. Hit by lightning. Footpath phase lightning arrestor damaged See 1088822,4,5,6 Exclude 1087909,96 | March | 2014 | 2014Q3 | 2014 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2014-03-16 | N | 94.8148 | N | 14 | N | N | 1.1101 | 39.4971 | 126796.7211
[7 empty] | 15496 | 8419 | 1087823 | 2014-03-16 12:31 | 2014-03-16 15:40 | 189 | 11kV | 113211 | 599 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Lightning | Y | At S.3154 St. Ives, Panel 13 Fdr CB tripped on OC, IOC, efi, timing and lockout relays. 11kV trip zone earth, #1 group earth. Lightning storm at the time. | March | 2014 | 2014Q3 | 2014 | ZN3154:PA13 | ZN3154:PA13 | ZN03154/000013 | KU-RING-GAI | UG | Not Veg | 2014-03-16 | N | 189 | N | 14 | N | N | 1.1101 | 39.4971 | 82731.2596
[7 empty] | 16107 | 16045 | 1087822 | 2014-03-16 12:31 | 2014-03-16 15:49 | 198 | 11kV | 130284 | 658 | HV | Lightning Strike | Adverse Weather/Environment | DC Not Transformer | Unplanned | Lightning | Y | At S.3154 ST Ives, Panel 12 Fdr CB tripped on A phase OC, lockout and timing relays, efi. 11kV trip, zone earth, #1 group earth. Lightning storm at the time. | March | 2014 | 2014Q3 | 2014 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | UG | Not Veg | 2014-03-16 | N | 198 | N | 14 | N | N | 1.1101 | 39.4971 | 95207.7045
[7 empty] | 15096 | 3654 | 1088026 | 2014-03-16 15:02 | 2014-03-16 17:00 | 118 | 11kV | 6490 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Wind | Y | LID 149788 A phase DOLF : 31 Amp Excluded OMS 1088026 | March | 2014 | 2014Q3 | 2014 | 256:80650 | 256:80650 | ZN00256/080650 | NEWCASTLE | UG | Not Veg | 2014-03-16 | N | 118 | N | 14 | N | N | 1.1101 | 39.4971 | 4742.7006
[7 empty] | 16487 | 20317 | 1087836 | 2014-03-16 12:40 | 2014-03-16 17:20 | 280 | 11kV | 273000 | 975 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | Y | Recloser 20397 tripped and locked out on IOC, timed OC and timing and lockout relays. Tree branch removed from 11kV mains by D.Op near PT.15500 | March | 2014 | 2014Q3 | 2014 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 280 | N | 14 | N | Y | 1.1101 | 39.4971 | 199500.3479
[7 empty] | 16335 | 18349 | 1088079 | 2014-03-16 15:27 | 2014-03-16 17:45 | 138.1333 | 11kV | 60916.8 | 441 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Bare | Unplanned | Electrical Storm | Y | Ex Zn12620 Noraville section of Pa1L @RE47817 Buff Point Eloura found tripped off no protection indications were able to be retrieved by DOp. Was in fail on DNMS with no indication. T/PE & T/Tele to investigate | March | 2014 | 2014Q3 | 2014 | ZN12620:PA1 | ZN12620:PA1 | ZN12620/000001 | CENTRAL COAST | OH | Veg | 2014-03-16 | N | 138.1333 | N | 14 | N | N | 1.1101 | 39.4971 | 44516.2007
[7 empty] | 15562 | 9014 | 1087819 | 2014-03-16 12:25 | 2014-03-16 18:30 | 365 | 11kV | 183576 | 1314 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | At S2400 Berowra Panel 22 tripped on Earth fault, EFI, Fault Check, TX1 Earth Fault Check Signals: 11kV Trip Cause: Low voltage mains into the 11kV mains on Pacific Highway See OMS 1088790 1088793 1088795 1088796 1088792 1087913/8205/7819/7882/7894/7893 | March | 2014 | 2014Q3 | 2014 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2014-03-16 | N | 139.7078 | N | 14 | N | N | 1.1101 | 39.4971 | 134151.9262
[7 empty] | 15011 | 2909 | 1087923 | 2014-03-16 13:54 | 2014-03-16 18:31 | 277 | 11kV | 44648 | 178 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 149794 2 fault operations 3 phase Overcurrent | March | 2014 | 2014Q3 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-03-16 | N | 250.8315 | N | 14 | N | N | 1.1101 | 39.4971 | 32627.4415
[7 empty] | 14955 | 2329 | 1088007 | 2014-03-16 15:00 | 2014-03-16 18:45 | 225 | 11kV | 18675 | 83 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 149795 A phase LLC burnt off Excluded OMS 1088007,1088023 | March | 2014 | 2014Q3 | 2014 | 502:48001 | 502:48001 | ZN00502/048001 | MAITLAND | OH | Not Veg | 2014-03-16 | N | 225 | N | 14 | N | N | 1.1101 | 39.4971 | 13647.1392
[7 empty] | 16071 | 15644 | 1087974 | 2014-03-16 14:29 | 2014-03-16 18:50 | 261 | 11kV | 1762 | 12 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 149782 Phase B - Fuse Size: 10 Amp Line DOLF Excluded job OMS 1087974 & 1089316 | March | 2014 | 2014Q3 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2014-03-16 | N | 146.8333 | N | 14 | N | N | 1.1101 | 39.4971 | 1287.6176
[7 empty] | 16113 | 16098 | 1087927 | 2014-03-16 13:58 | 2014-03-16 18:52 | 294 | 11kV | 71462 | 277 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 149799 1 fault operation Sensitive Earth Fault Excluded OMS 1087927,1088092 | March | 2014 | 2014Q3 | 2014 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2014-03-16 | Y | 257.9856 | N | 14 | N | Y | 1.1101 | 39.4971 | 52222.3218
[7 empty] | 15019 | 2979 | 1087978 | 2014-03-16 14:32 | 2014-03-16 19:05 | 273 | 11kV | 3276 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 149796 B Phase - Fuse size: 200 Amp Tree onto mains Excluded OMS 1087978 Note customers were also a part of wider area outage - refer to 1089928 during the same time | March | 2014 | 2014Q3 | 2014 | 803:74010 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-03-16 | Y | 273 | N | 14 | N | Y | 1.1101 | 39.4971 | 2394.0042
[7 empty] | 16049 | 15403 | 1088228 | 2014-03-16 14:49 | 2014-03-16 19:56 | 307 | 11kV | 3684 | 12 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Wind | Y | LID 149802 A, B & C Phases - Fuse size: 200 Amp REPLACED 3 lv SUB FUSES remove debris from distribution wires - BLOW UP JUMPING CASTLE BLOWN ONTO DW in Sparke St Excluded OMS 1088228, 1088006, 1088002, 1089386 and 1088217 | March | 2014 | 2014Q3 | 2014 | 528:83011 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2014-03-16 | N | 307 | N | 14 | N | N | 1.1101 | 39.4971 | 2692.1585
[7 empty] | 16111 | 16067 | 1087895 | 2014-03-16 13:35 | 2014-03-16 20:00 | 385 | 11kV | 29045 | 100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex Zn12630 Peats Ridge section Pa1 "grants rd" fdr @RE44995 Kulnura tripped and locked out on overcurrent, IOC Tree brought down footpath and centre phase 11kv fdr between LB49853 and AB40548. Linesman called out to repair. See 1088763,4 Exclude 1087895 | March | 2014 | 2014Q3 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2014-03-16 | N | 290.45 | N | 14 | N | N | 1.1101 | 39.4971 | 21225.2293
[7 empty] | 14875 | 1723 | 1087959 | 2014-03-16 14:16 | 2014-03-16 20:50 | 394 | 11kV | 11766 | 35 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | Y | LID 149804 2 fault operations Earth fault Exclude OMS 1087959 | March | 2014 | 2014Q3 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-03-16 | N | 336.1714 | N | 14 | N | N | 1.1101 | 39.4971 | 8598.2458
[7 empty] | 15082 | 3520 | 1088479 | 2014-03-16 14:04 | 2014-03-16 21:17 | 433 | 11kV | 37745 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | Y | At recloser 20828 tripped, reclosed, tripped and locked out on OC. Tree branch on mains in Kinka Rd, Terrey Hills | March | 2014 | 2014Q3 | 2014 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 352.757 | N | 14 | N | Y | 1.1101 | 39.4971 | 27582.9327
[7 empty] | 14691 | 2 | 1088355 | 2014-03-16 20:39 | 2014-03-16 21:18 | 39 | 11kV | 51675 | 1325 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | Y | Ex ZN 10992 Blakehurst - Section of Pnl 1. AB 31134 Centre phase bond burnt off. ME: 1088499. ME GIS: 1088371, 2, 3, 6, 7. Withdrawn: 1088355, 69, 70. | March | 2014 | 2014Q3 | 2014 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2014-03-16 | N | 39 | N | 14 | N | N | 1.1101 | 39.4971 | 37762.5658
[7 empty] | 14746 | 425 | 1087971 | 2014-03-16 13:53 | 2014-03-16 21:30 | 457 | 11kV | 48776 | 154 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 149806 2 Fault operations Earth fault; Overcurrent 2 spans HV down at pole AI-80239 | March | 2014 | 2014Q3 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Not Veg | 2014-03-16 | Y | 316.7273 | N | 14 | N | Y | 1.1101 | 39.4971 | 35644.0622
[7 empty] | 16026 | 14923 | 1087844 | 2014-03-16 12:37 | 2014-03-16 22:20 | 583 | 11kV | 141250 | 326 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Recloser 22381 tripped, reclosed, tripped and locked out on IOC and OC trip. Tree branch on mains between AB,26227 and LB.46995 and tee to PT.15052 See 1088452,3,5 GIS 1088384 Exclude 1087844 | March | 2014 | 2014Q3 | 2014 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 433.2822 | N | 14 | N | Y | 1.1101 | 39.4971 | 103221.3338
[7 empty] | 15472 | 8162 | 1089279 | 2014-03-16 22:38 | 2014-03-16 22:42 | 4 | 11kV | 76 | 19 | HV | Staff Operation | Utility Process Issue | Recloser / Sectionaliser | Unplanned | Electrical Storm | Y | LID 149810 Wrong recloser information was given to AOP | March | 2014 | 2014Q3 | 2014 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2014-03-16 | Y | 4 | N | 14 | N | Y | 1.1101 | 39.4971 | 55.5386
[7 empty] | 14907 | 1968 | 1088028 | 2014-03-16 15:01 | 2014-03-16 23:53 | 532 | 11kV | 357253 | 682 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 149783 3 fault operations B & C phase Overcurrent Excluded OMS 1088028 | March | 2014 | 2014Q3 | 2014 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2014-03-16 | Y | 523.8314 | N | 14 | N | Y | 1.1101 | 39.4971 | 261069.9552
[7 empty] | 15992 | 14504 | 1088047 | 2014-03-16 15:06 | 2014-03-17 01:15 | 609 | 11kV | 567971 | 1705 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | LID 149786 2 fault operations A & B phase Instantaneous overcurrent CB 81535 Tomaree ZS Targets: 50TAB 11kV wires down. Tree in OHM. Excluded OMS 1088047 + 1088408 | March | 2014 | 2014Q3 | 2014 | 242:81535 | 242:81535 | ZN00242/081535 | PORT STEPHENS | OH | Veg | 2014-03-16 | Y | 333.1208 | N | 14 | N | Y | 1.1101 | 39.4971 | 415056.4545
[7 empty] | 15344 | 6749 | 1088052 | 2014-03-16 15:04 | 2014-03-17 01:18 | 614 | 11kV | 676938 | 1113 | HV | Vegetation Blow/Fall In | Vegetation | Pole | Unplanned | Wind | Y | LID 149785 2 fault operations A & B phase Overcurrent also refer to 1088052 - All phases were off. Removed service from under tree limb. Repaired and re-tensioned - 324 & 326 WANDA AVE SALAMANDER BAY 1088169 - replaced service 2 Phase - 92 SOLDIERS POINT RD SOLDIERS POINT, | March | 2014 | 2014Q3 | 2014 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Veg | 2014-03-16 | Y | 608.2102 | N | 14 | N | Y | 1.1101 | 39.4971 | 494686.3241
[7 empty] | 15032 | 3072 | 1088177 | 2014-03-16 14:02 | 2014-03-17 01:50 | 708 | 11kV | 140843.3333 | 199 | HV | Vegetation Blow/Fall In | Vegetation | DC Not Transformer | Unplanned | Lightning | Y | Calls and report devices not matched from CR report. Whole sub flagged as part of teh "roll up" | March | 2014 | 2014Q3 | 2014 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 707.7554 | N | 14 | N | Y | 1.1101 | 39.4971 | 102924.1538
[7 empty] | 15684 | 10819 | 1088193 | 2014-03-16 23:55 | 2014-03-17 02:00 | 125 | 11kV | 856 | 16 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | Y | LID 149811 3 phase Burnt tappings line side of 40787, on restoration found low mains near 61331 cass 940851 | March | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-03-16 | N | 53.5 | N | 14 | N | N | 1.1101 | 39.4971 | 625.5396
[7 empty] | 15700 | 10996 | 1088317 | 2014-03-16 19:19 | 2014-03-17 02:10 | 411.2 | 11kV | 4934.4 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 149809 Pole Mounted RAGCB Tree over mains / lightning storm | March | 2014 | 2014Q3 | 2014 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2014-03-16 | Y | 411.2 | N | 14 | N | Y | 1.1101 | 39.4971 | 3605.914
[7 empty] | 15965 | 14012 | 1088037 | 2014-03-16 15:04 | 2014-03-17 04:20 | 796 | 11kV | 475156 | 1556 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 149784 2 fault operation A & C phase Overcurrent sw 50354 was closed . Sw 18241 was open. OHM down at pole os-20357. Excluded oms 1088037 | March | 2014 | 2014Q3 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2014-03-16 | Y | 305.3702 | N | 14 | N | Y | 1.1101 | 39.4971 | 347229.9901
[7 empty] | 16226 | 17323 | 1088398 | 2014-03-16 23:14 | 2014-03-17 08:00 | 526 | 11kV | 3156 | 6 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 149798 11kV Fdr isolated to repair wire off insulator at pole OR-60670 & wire on crossarm at pole OR-60671. | March | 2014 | 2014Q3 | 2014 | 242:81533 | 242:81533 | ZN00242/081533 | PORT STEPHENS | OH | Not Veg | 2014-03-16 | Y | 526 | N | 14 | N | Y | 1.1101 | 39.4971 | 2306.3117
[7 empty] | 15508 | 8563 | 1087856 | 2014-03-16 12:45 | 2014-03-17 08:45 | 1200 | 11kV | 53580 | 123 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | Ex Zn15013 Terry Hills section of Pa4 "Aumuna Mona" fdr @RE21350 Booralie Kalgoa tripped and locked out on: SEF Tree brought down 11kv mains in Kinka Rd Terrey Hills. 3 bays of LV mains down in Tooronga Rd Terrey Hills feed from PT15361 Kulgoa Cr 240 as well See 1089423,4,5 Exclude 1087839,56,922,8287,352 | March | 2014 | 2014Q3 | 2014 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 435.6098 | N | 14 | N | Y | 1.1101 | 39.4971 | 39154.6837
[7 empty] | 15198 | 4584 | 1088433 | 2014-03-17 06:45 | 2014-03-17 09:10 | 145 | 11kV | 870 | 6 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Unselected | N | REPLACED 100amp FUSE ON SUB 70336 CC1: 06-"Urgent - O.H Mains - No others" Excluded OMS job 1088433 | March | 2014 | 2014Q3 | 2014 | 803:74016 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2014-03-17 | N | 145 | N | 6 | N | N | 1.1101 | 39.4971 | 635.7703
[7 empty] | 14760 | 543 | 1088013 | 2014-03-16 14:52 | 2014-03-17 12:20 | 1288 | 11kV | 553261 | 848 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 149781 1 fault operation Earth fault Excluded OMS 1088013, 1088411, 1088416 | March | 2014 | 2014Q3 | 2014 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2014-03-16 | Y | 652.4304 | N | 14 | N | Y | 1.1101 | 39.4971 | 404306.8204
[7 empty] | 16430 | 19586 | 1088439 | 2014-03-17 07:15 | 2014-03-17 13:55 | 400 | 11kV | 800 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 149820 B & C Phases - Fuse Size: 10 Amp Line DOLF Excluded OMS 1088439 and 1089381 | March | 2014 | 2014Q3 | 2014 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2014-03-17 | N | 400 | N | 6 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 15540 | 8873 | 1087834 | 2014-03-16 12:33 | 2014-03-17 15:14 | 1601 | 11kV | 126013 | 93 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | Ex Zn15013 Terrey Hills section of Pa10 @RE20852 MCarrs Dk Rd tripped, reclosed, tripped and locked out on: IOC & OC trip @CP49122 tripped on B&C phase OC Large tree branch on mains in West Head Rd Cottage Point adjacent to RE20852 MCarrs Ck Rd. Second fault beyond CP49122 See 1089416,7 Exclude 1087834,8409 | March | 2014 | 2014Q3 | 2014 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2014-03-16 | Y | 1354.9785 | N | 14 | N | Y | 1.1101 | 39.4971 | 92086.5836
[7 empty] | 16170 | 16709 | 1088231 | 2014-03-16 15:04 | 2014-03-17 15:37 | 1473 | 11kV | 1830591 | 1703 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 149787 2 fault operations Earth fault CB 81539 targets: 51N Excluded OMS 1088231 | March | 2014 | 2014Q3 | 2014 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2014-03-16 | Y | 1074.9213 | N | 14 | N | Y | 1.1101 | 39.4971 | 1337741.9095
[7 empty] | 16467 | 20143 | 1088938 | 2014-03-17 14:15 | 2014-03-17 16:30 | 135 | 11kV | 82352 | 904 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At Zn965 Pennnant Hills Pa 35 Tripped reclosed tripped and locked out on Relays Earth Fault, EFI, Reclose Timing and Lockout Signals: 11kV trip, Zone Earth, No1 Group Earth Cause: UG cable damaged by contractor (Hornsby Council) between S4962 - S5138 - S4961 tee PT1296 See OMS 1089574 1089577 1088917 1088938 1088939 1089000 | March | 2014 | 2014Q3 | 2014 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | UG | Not Veg | 2014-03-17 | N | 91.0973 | N | 6 | N | N | 1.1101 | 39.4971 | 60180.4126
[7 empty] | 15135 | 4036 | 1088076 | 2014-03-17 12:00 | 2014-03-17 17:10 | 310 | 11kV | 17360 | 56 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 149825 Sub isolated for repairs at OR-50094 | March | 2014 | 2014Q3 | 2014 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Not Veg | 2014-03-17 | N | 310 | N | 6 | N | N | 1.1101 | 39.4971 | 12686.176
[7 empty] | 15435 | 7848 | 1088211 | 2014-03-16 16:56 | 2014-03-17 17:10 | 1454 | 11kV | 1454 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | Y | Ex Zn12640 Umina section of Pa3 "Patonga" fdr @PT12385 Patonga Bay 1.7 HVDO's operated Suspect defective transformer. Subs to meet DOp on site AM noon 17/3/14. Customers affected. PT12385 replaced and OK DAROS order 334768 customers interrupted from CP42017 12:00-17:00 17/3/14 See 1088216 Exclude 1088211,847 | March | 2014 | 2014Q3 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | UG | Not Veg | 2014-03-16 | Y | 1454 | N | 14 | N | Y | 1.1101 | 39.4971 | 1062.5403
[7 empty] | 16369 | 18737 | 1088209 | 2014-03-16 15:03 | 2014-03-17 18:50 | 1667 | 11kV | 906931 | 963 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | LID 149789 2 fault operations B & C phase Overcurrent Excluded OMS 1088209 | March | 2014 | 2014Q3 | 2014 | 242:81538 | 242:81538 | ZN00242/081538 | PORT STEPHENS | OH | Veg | 2014-03-16 | Y | 941.7767 | N | 14 | N | Y | 1.1101 | 39.4971 | 662758.4249
[7 empty] | 16291 | 17907 | 1089116 | 2014-03-17 22:20 | 2014-03-17 23:18 | 58 | 11kV | 2088 | 36 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn14143 Somersby Pa21 "Somersby" fdr tripped on ABC Phase overcurrent, EFI EFI's: All field EFI's operated Possum on connection between CCT and Bare HV overhead beyond PT14454 | March | 2014 | 2014Q3 | 2014 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2014-03-17 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 1525.8488
[7 empty] | 15991 | 14503 | 1089119 | 2014-03-18 01:44 | 2014-03-18 03:30 | 106 | 11kV | 45061 | 431 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149830 4 fault operations 3 phase Earth fault; Overcurrent Excluded OMS 1089119 | March | 2014 | 2014Q3 | 2014 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Veg | 2014-03-18 | N | 104.5499 | N | 4 | N | N | 1.1101 | 39.4971 | 32929.2497
[7 empty] | 16346 | 18514 | 1089121 | 2014-03-18 03:19 | 2014-03-18 04:35 | 76 | 11kV | 8512 | 112 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 149831 A Phase - Fuse Size: 40 Amp Substation DOLF Excluded OMS 1089121 & 1089122 | March | 2014 | 2014Q3 | 2014 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2014-03-18 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 6220.3185
[7 empty] | 16143 | 16427 | 1089227 | 2014-03-18 08:01 | 2014-03-18 10:05 | 124 | 11kV | 92566 | 1099 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | AT S.15001 Brookvale, 11kV Panel 6 Fdr CB tripped on earth fault (Basler relay), efi, 11kV trip signal. Field efi's down at S.16892 and S.16948 (Note:- No operation at S.15189) UG cable fault between S.16948, S.16027 and tee to S.15939 | March | 2014 | 2014Q3 | 2014 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | UG | Not Veg | 2014-03-18 | N | 84.2275 | N | 4 | N | N | 1.1101 | 39.4971 | 67644.5026
[7 empty] | 15313 | 6547 | 1089245 | 2014-03-18 09:46 | 2014-03-18 11:00 | 74 | 11kV | 97007 | 1463 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | At Sub2835 Burwood 11kv fdr Pnl #10 'S 3515 Russell Wentworth" tripped on: SPAJ 140 T L1 L2 L3 No2 EFI fault check Field EFI's: S3355, S46519, S8480, S4658, S5109, S46978 Cp 2581 S3484 Remarks: contractor error caused failure. Road crossing cnr South and Ada Sth Strathfield. Contractors damaged 11kv cable. 2 workers taken to hospital for observation and checks. | March | 2014 | 2014Q3 | 2014 | ZN2835:PA10 | ZN2835:PA10 | ZN02835/000010 | STRATHFIELD | OH | Not Veg | 2014-03-18 | N | 66.3069 | N | 4 | N | N | 1.1101 | 39.4971 | 70889.8544
[7 empty] | 15605 | 9690 | 1089979 | 2014-03-12 16:08 | 2014-03-18 12:05 | 8397 | 11kV | 8397 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | Panel 67A @ S8700 City North Opened by Aop Interrupting supply to S48700 Hickson Barrangaroo temp & S62929 Hickson Barrangaroo temp No 2 (See interruption report for Darling Harbour @ S63294 Shelley Barrangaroo) Isolated only Sw/tag @ S62929 Hickson Barrangaroo Temp No2 Remarks: fire in basement area of Barrrangaroo construction site has weakened foundation of crane. (See interruption report for darling harbour @ S63294 Shelley Barrangaroo temp 2) | March | 2014 | 2014Q3 | 2014 |  |  |  |  | Unknown | Not Veg | 2014-03-12 | N | 8397 | N | 3 | N | N | 1.1101 | 39.4971 | 6136.2799
[7 empty] | 16092 | 15940 | 1088419 | 2014-03-17 03:34 | 2014-03-18 12:40 | 1986 | 11kV | 33506 | 341 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 1648 Enfield - Pnl 21 - Translay, EFI, Field EFIs. Underground fault. Testers to test. Extended outage due to nature of the fault and also due the fact that the customer affected by the extended outage was a Sydney Water pumping station. ME: 1090042. Rest Steps: 1090043, 4. Withdrawn: 1088419, 23. | March | 2014 | 2014Q3 | 2014 | ZN1648:PA21 | ZN4853:PA12 | ZN04853/000012 | STRATHFIELD | UG | Not Veg | 2014-03-17 | N | 98.2581 | N | 6 | N | N | 1.1101 | 39.4971 | 24485.1965
[7 empty] | 15296 | 6379 | 1089690 | 2014-03-19 04:11 | 2014-03-19 05:45 | 94 | 11kV | 10152 | 108 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | Unselected | N | PT 10305 Oates Anderson - PT Roadside HDO operated. Possum dead at base of PT. Bucket truck required to operate HV fuses due to LV Cross arm being in the way not allowing a ladder to be erected. ME: 1090027. Withdrawn: 1089690. | March | 2014 | 2014Q3 | 2014 | ZN10994:PA8 | ZN10994:PA8 | ZN10994/000008 | GEORGES RIVER | OH | Not Veg | 2014-03-19 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 7418.7822
[7 empty] | 14894 | 1888 | 1089706 | 2014-03-19 08:08 | 2014-03-19 09:12 | 64 | 11kV | 88512 | 1383 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S1673 Turramurra Panel 18 tripped on A and C phase IOC Cause not ascertained for outage | March | 2014 | 2014Q3 | 2014 | ZN1673:PA18 | ZN1673:PA18 | ZN01673/000018 | KU-RING-GAI | OH | Veg | 2014-03-19 | N | 64 | N | 4 | N | N | 1.1101 | 39.4971 | 64681.9589
[7 empty] | 15154 | 4175 | 1089760 | 2014-03-19 09:09 | 2014-03-19 11:05 | 116 | 11kV | 232 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa9 "Wyoming South" @PT12400 Taylors Barduk 0.3 HDO 16Amp ABB left road side Fust fatigue See 1090545 exclude 1089760 | March | 2014 | 2014Q3 | 2014 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Not Veg | 2014-03-19 | N | 116 | N | 4 | N | N | 1.1101 | 39.4971 | 169.5388
[7 empty] | 15966 | 14048 | 1090165 | 2014-03-19 23:05 | 2014-03-20 00:01 | 56 | 11kV | 896 | 16 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | S.17014 interrupted for safety; 11kV pole replacement in Oxford Falls Rd near Dereadnought St, Oxford Falls Excluded OMS job 1090165 | March | 2014 | 2014Q3 | 2014 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-03-19 | N | 56 | N | 4 | N | N | 1.1101 | 39.4971 | 654.7704
[7 empty] | 16110 | 16061 | 1090909 | 2014-03-20 05:16 | 2014-03-20 06:55 | 99 | 11kV | 1188 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149862 A & B Phases - Fuse size: 20 Amp Line DOLF Excluded OMS 1090171 | March | 2014 | 2014Q3 | 2014 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Veg | 2014-03-20 | N | 99 | N | 4 | N | N | 1.1101 | 39.4971 | 868.1554
[7 empty] | 16381 | 18887 | 1090169 | 2014-03-20 00:59 | 2014-03-20 08:35 | 456 | 11kV | 5015.6 | 11 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale section of Pa24L @PT18760 Bursh Anderson 0.9 centre phase HV fuse blown 16Amp BB Batch #0802 Lightning strike earlier in morning See 1090170 GIS 1090169 CC1: 22-"Refer to SOp" FRC1: 322-"No Supply at Point of Attachment - Other Services affected - District Operator required" | March | 2014 | 2014Q3 | 2014 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2014-03-20 | N | 455.9636 | N | 4 | N | N | 1.1101 | 39.4971 | 3665.2525
[7 empty] | 15482 | 8255 | 1090345 | 2014-03-20 10:33 | 2014-03-20 11:47 | 74 | 11kV | 71683 | 1007 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | ex Zn12570 Avoca section of Pa21L "LB49826" @RE41397 tripped on earth fault Outside #85 Karalta rd Erina Contractor hit cable See 1092048,9 exclude 1090345,53,65,70 | March | 2014 | 2014Q3 | 2014 | ZN12570:PA21 | ZN12580:PA2 | ZN12580/000002 | CENTRAL COAST | UG | Not Veg | 2014-03-20 | N | 71.1847 | N | 4 | N | N | 1.1101 | 39.4971 | 52383.8221
[7 empty] | 15972 | 14175 | 1090382 | 2014-03-20 11:13 | 2014-03-20 11:47 | 34 | 11kV | 48552 | 1428 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149873 Patrol done no fault found supply restored. Part of Fdr 11457 beyoun Sw 50319 transfered to Fdr 33413. ( Sw 50354 closed, Sw 18241 open) | March | 2014 | 2014Q3 | 2014 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2014-03-20 | N | 34 | N | 4 | N | N | 1.1101 | 39.4971 | 35480.3696
[7 empty] | 15263 | 5882 | 1090669 | 2014-03-21 04:38 | 2014-03-21 06:11 | 93 | 11kV | 171287 | 2142 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.15008 Harbord, Panel 9 Fdr CB tripped on A phase OC, lockout and timing relays. | March | 2014 | 2014Q3 | 2014 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Veg | 2014-03-21 | N | 79.9659 | N | 5 | N | N | 1.1101 | 39.4971 | 125171.4875
[7 empty] | 14773 | 663 | 1090928 | 2014-03-21 15:58 | 2014-03-21 17:10 | 72 | 11kV | 4608 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12640 Umina section of Pa13 @PT18648 Patonga Bay 11kv Aphase 63Amp HDO blown Cause not ascertained. See 1092136 GIS 1090929 Exclude 1090928,36 | March | 2014 | 2014Q3 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Veg | 2014-03-21 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 3367.3905
[7 empty] | 16421 | 19445 | 1090972 | 2014-03-21 17:41 | 2014-03-21 19:15 | 94 | 11kV | 81001 | 1129 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1285 Greenacre Park, 11kv Pnl 20R tripped reclosed and tripped on; Relays: Earth fault, EFI, Timing , Lockout. Signals: 11kv trip, Group Earth tx 3 Field EFI's: Sub 4409 Remarks: 11kV underground fault from SW/B @ Sub 4409 Islington Cres tee to PT1203 Noble Chis to SW/A @ Sub 3965 Chiswick Water | March | 2014 | 2014Q3 | 2014 | ZN1285:PA20 | ZN1285:PA20 | ZN01285/000020 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-03-21 | N | 71.7458 | N | 5 | N | N | 1.1101 | 39.4971 | 59193.1417
[7 empty] | 15863 | 12815 | 1090976 | 2014-03-21 18:30 | 2014-03-21 20:30 | 120 | 11kV | 120 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 149899 Single Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1090976 | March | 2014 | 2014Q3 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-03-21 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 15815 | 12269 | 1090988 | 2014-03-21 20:21 | 2014-03-21 21:25 | 64 | 11kV | 448 | 7 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Ex Zn14144 Wamberal section of Pa2 PT12130 McGarrity Oak 0.5 11kv B phase 16amp HDO blown Possum at PT. DOp made safe and restored supply See 1092140 exclude 1090988,94 | March | 2014 | 2014Q3 | 2014 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Not Veg | 2014-03-21 | N | 64 | N | 5 | N | N | 1.1101 | 39.4971 | 327.3852
[7 empty] | 16084 | 15806 | 1091011 | 2014-03-22 06:11 | 2014-03-22 08:10 | 119 | 11kV | 6657.5833 | 56 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Zn12620 Noraville section of Pa11 "Norah Head" @PT11066 Oleander Evans C phase 50K HDO operated Fuse Fatigue. See 1091005 GIS 1091013 exclude 1091011 CC1: 22-"Refer to SOp" CC2: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" FRC2: 329-"High Voltage Fuse - Requires replacement" | March | 2014 | 2014Q3 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2014-03-22 | N | 118.8854 | N | 5 | N | N | 1.1101 | 39.4971 | 4865.1655
[7 empty] | 14815 | 1080 | 1091110 | 2014-03-22 18:13 | 2014-03-22 21:36 | 203.5 | 11kV | 4273.5 | 21 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | LID 149907 Single Phase - Fuse size: 5 Amp Line DOLF Evidence of fuse fatigue as per operator | March | 2014 | 2014Q3 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-03-22 | N | 203.5 | N | 5 | N | N | 1.1101 | 39.4971 | 3122.9478
[7 empty] | 16325 | 18246 | 1091144 | 2014-03-22 21:30 | 2014-03-22 22:32 | 62 | 11kV | 36766 | 593 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Rain Light | N | At S4545 Meadowbank Panel 29 Tripped on A and C phase O/C, EFI and Fault Check Cause: Possum shorted surge arrestors adjacent to LB61231 See OMS 1091144 1091153 | March | 2014 | 2014Q3 | 2014 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2014-03-22 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 26867.5084
[7 empty] | 16385 | 18924 | 1091145 | 2014-03-22 21:33 | 2014-03-22 22:38 | 65 | 11kV | 135005 | 2077 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At S2400 Berowra Pa22 feeder tripped Relays: A and C phase Overcurrent Abnormal Switching: AV2785 Open AB116 Closed, AB2164 Closed AB134 Open Cause: Possum Came into contact with 11kV mains at corner pole on Chestnut and Foxglove Rd See OMS 109134347 1091150 1091145 1091308 | March | 2014 | 2014Q3 | 2014 | ZN2400:PA22 | ZN2400:PA22 | ZN02400/000022 | HORNSBY | OH | Not Veg | 2014-03-22 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 98657.672
[7 empty] | 14745 | 404 | 1091161 | 2014-03-22 23:23 | 2014-03-23 01:47 | 144 | 11kV | 134400 | 1134 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | At S.3154 St Ives, Panel 5 FDr CB tripped on A&C phase IOC, 11kV trip. Lightning storm at the time | March | 2014 | 2014Q3 | 2014 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Veg | 2014-03-22 | N | 118.5185 | N | 5 | N | N | 1.1101 | 39.4971 | 98215.5559
[7 empty] | 14989 | 2717 | 1091164 | 2014-03-23 01:12 | 2014-03-23 02:14 | 62 | 11kV | 73780 | 1190 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | Lightning | N | S.195 Pymble Zone Panel 30 CB. B Phase Overcurrent, EFI, Fault Check Possum came into contact with 11kV at recloser 46113. No visible damage to equipment. | March | 2014 | 2014Q3 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2014-03-23 | N | 62 | N | 7 | N | N | 1.1101 | 39.4971 | 53916.2479
[7 empty] | 15923 | 13366 | 1091264 | 2014-03-23 16:13 | 2014-03-23 17:00 | 47 | 11kV | 14490 | 449 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149911 1 fault operation Sensitive Earth Fault faulty LAs at sub 27796 Excluded oms # 1091264 | March | 2014 | 2014Q3 | 2014 | 220:8688 | 220:8688 | ZN00220/008688 | LAKE MACQUARIE | OH | Not Veg | 2014-03-23 | N | 32.2717 | N | 7 | N | N | 1.1101 | 39.4971 | 10588.8646
[7 empty] | 15844 | 12617 | 1091253 | 2014-03-23 16:15 | 2014-03-23 17:15 | 60 | 11kV | 180 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149912 A Phase - Fuse size: 5 Amp Substation DOLF | March | 2014 | 2014Q3 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-03-23 | N | 60 | N | 7 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 15083 | 3531 | 1091266 | 2014-03-23 16:37 | 2014-03-23 17:40 | 63 | 11kV | 71442 | 1134 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | N | AT S.3154 St Ives, Panel 5 Fdr CB tripped on C phase timed OC, efi. 11kV trip signal. Lightning strucl steel pole at UG/OH adjacent LB.1021 | March | 2014 | 2014Q3 | 2014 | ZN3154:PA5 | ZN3154:PA5 | ZN03154/000005 | KU-RING-GAI | OH | Not Veg | 2014-03-23 | N | 63 | N | 7 | N | N | 1.1101 | 39.4971 | 52207.7064
[7 empty] | 16112 | 16079 | 1091286 | 2014-03-23 19:03 | 2014-03-23 21:20 | 137 | 11kV | 2329 | 17 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | LID 149921 B & C Phases - Fuse size: 63 Amp Line DOLF Excluded OMS 1091286 | March | 2014 | 2014Q3 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2014-03-23 | N | 137 | N | 7 | N | N | 1.1101 | 39.4971 | 1701.9645
[7 empty] | 15341 | 6743 | 1091305 | 2014-03-23 21:45 | 2014-03-24 00:40 | 175 | 11kV | 175 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 149925 3 Phase - Fuse size: 10 Amp Line DOLF blown lightning arrestor cut away at sub 7629. A Pople will report to depot new arrestor required Excluded OMS 1091305 | March | 2014 | 2014Q3 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-03-23 | N | 175 | N | 7 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 16028 | 14940 | 1091310 | 2014-03-23 22:13 | 2014-03-24 02:23 | 250 | 11kV | 500 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149926 A & B Phases - Fuse size: 10 Amp Substation DOLF Excluded OMS 1091310 | March | 2014 | 2014Q3 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2014-03-23 | N | 250 | N | 7 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 15561 | 8996 | 1091370 | 2014-03-24 08:31 | 2014-03-24 09:49 | 78 | 11kV | 162156 | 2142 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At S15008 Harbord Panel 9 L Tripped on IOC and SEL Lockout Cause: Bond Burnt Off USL 23364 B phase See OMS 1094381 1094382 1091362 1091366 1091368 | March | 2014 | 2014Q3 | 2014 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2014-03-24 | N | 75.7031 | N | 11 | N | N | 1.1101 | 39.4971 | 118498.822
[7 empty] | 15074 | 3427 | 1091342 | 2014-03-24 07:49 | 2014-03-24 10:00 | 131 | 11kV | 131 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149933 Single Phase - Fuse size: 5 Amp Substation DOLF Excluded OMS 1091342 | March | 2014 | 2014Q3 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2014-03-24 | N | 131 | N | 11 | N | N | 1.1101 | 39.4971 | 95.7309
[7 empty] | 15368 | 7013 | 1091416 | 2014-03-24 09:24 | 2014-03-24 10:00 | 36 | 11kV | 108 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149934 A Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1091416 | March | 2014 | 2014Q3 | 2014 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Not Veg | 2014-03-24 | N | 36 | N | 11 | N | N | 1.1101 | 39.4971 | 78.9232
[7 empty] | 15763 | 11727 | 1091424 | 2014-03-24 09:28 | 2014-03-24 13:00 | 212 | 11kV | 212 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 149937 Single Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1091424 | March | 2014 | 2014Q3 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-03-24 | N | 212 | N | 11 | N | N | 1.1101 | 39.4971 | 154.9233
[7 empty] | 15145 | 4121 | 1091611 | 2014-03-24 13:37 | 2014-03-24 14:42 | 65 | 11kV | 80470 | 1238 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | ZN.1193 Lindfield Panel 26 CB A & B phase IOC Cause lightning, patrolled and reported to be ok. | March | 2014 | 2014Q3 | 2014 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Not Veg | 2014-03-24 | N | 65 | N | 11 | N | N | 1.1101 | 39.4971 | 58805.1025
[7 empty] | 14903 | 1958 | 1091705 | 2014-03-24 15:14 | 2014-03-24 16:30 | 76 | 11kV | 683.7833 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Section of ZN.35500 Top Ryde Panel 32 A & B phase 63A HDO blown at CP.1835 Tree branch on OH mains. See OMS 1092099 1091705 1091735/709 | March | 2014 | 2014Q3 | 2014 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2014-03-24 | N | 75.9759 | N | 11 | N | N | 1.1101 | 39.4971 | 499.6887
[7 empty] | 16016 | 14853 | 1091785 | 2014-03-24 16:52 | 2014-03-24 18:53 | 121 | 11kV | 70642 | 590 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | ZN 9252 Jannali - Pnl 7 - Trip/reclose/trip, A phase IOC and Timed OC, Earth Fault, timing, lockout. Lightning at time of failure on section of 11kV feeder from ZN 9252 Pnl 7 to IR 63274. Note: Field EFI at UGOH Soldier Rd near Washington Dr suspect defective failed to operate. Sub to investigate. Note: CLC defect alarm at Jannali. DOp unable to clear. Telecontrol required to investigate. ME: 1091998. Withdrawn: 1091785. | March | 2014 | 2014Q3 | 2014 | ZN9252:PA7 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | OH | Not Veg | 2014-03-24 | N | 119.7322 | N | 11 | N | N | 1.1101 | 39.4971 | 51623.09
[7 empty] | 16192 | 16970 | 1091539 | 2014-03-24 12:26 | 2014-03-24 19:00 | 394 | 11kV | 8228 | 42 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 149942 1 fault operation broken conductor at pole CV-53679 near sub 54050. Excluded oms 1091539, 52, 64 & 1091727 | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-03-24 | N | 195.9048 | N | 11 | N | N | 1.1101 | 39.4971 | 6012.7797
[7 empty] | 14756 | 531 | 1091816 | 2014-03-24 17:56 | 2014-03-24 19:35 | 99 | 11kV | 198 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149943 A Phase - Fuse size: 10 Amp Line DOLF Excluded OMS 1091816 | March | 2014 | 2014Q3 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-03-24 | N | 99 | N | 11 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 15824 | 12379 | 1091385 | 2014-03-24 08:56 | 2014-03-24 20:50 | 714 | 11kV | 714 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 149944 interrupt to repair HV tapping at LF 6940. Excluded OMS 1091385 | March | 2014 | 2014Q3 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-03-24 | N | 714 | N | 11 | N | N | 1.1101 | 39.4971 | 521.7701
[7 empty] | 16088 | 15890 | 1091855 | 2014-03-24 20:28 | 2014-03-25 02:08 | 340 | 11kV | 680 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149943 3 Phase - Fuse size: 20 Amp Line DOLF Excluded OMS 1091855 | March | 2014 | 2014Q3 | 2014 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2014-03-24 | N | 340 | N | 11 | N | N | 1.1101 | 39.4971 | 496.9239
[7 empty] | 15949 | 13687 | 1091877 | 2014-03-25 05:39 | 2014-03-25 07:50 | 131 | 11kV | 53812 | 512 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | iR 63275 Washington Lincoln - SCAN FAIL (no relays to report) (intelliRupter put in DMA). At S 9889 DOp found end box damage on the Sw/A side. Sub is now in LV//. ME: 1092573. Rest Step: 1092575. Withdrawn: 1091877. | March | 2014 | 2014Q3 | 2014 | ZN9252:PA11 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | UG | Not Veg | 2014-03-25 | N | 105.1016 | N | 3 | N | N | 1.1101 | 39.4971 | 39324.2224
[7 empty] | 14727 | 282 | 1092389 | 2014-03-25 09:00 | 2014-03-25 14:20 | 320 | 11kV | 320 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149957 B phase DOLF : 31 Amp No OMS number cutomer called depot bypassing system. Cause damaged arrester. | March | 2014 | 2014Q3 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-03-25 | N | 320 | N | 3 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 15838 | 12517 | 1092004 | 2014-03-25 10:35 | 2014-03-25 14:20 | 225 | 11kV | 12600 | 56 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149958 1 fault operation Earth fault When DOP closed B phase DOLF at sub 51447 the surge arestor failed and Sw 42028 operated.operation Excluded OMS # 1092004. | March | 2014 | 2014Q3 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-03-25 | N | 225 | N | 3 | N | N | 1.1101 | 39.4971 | 9207.7084
[7 empty] | 15938 | 13563 | 1092738 | 2014-03-26 19:36 | 2014-03-26 21:05 | 89 | 11kV | 157068 | 1770 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN.129 Hunters Hill Panel 19 feeder trip and locked out Relays: SEF AB.3243 Bond burnt off ME-1093162, RS-1093165, SE-1093176, RS GIS-1093157, 1092749, 1092747 Withdrawn: 1092738, 1092739, 1092743, 1092744, 1092745, 1092746, 1092750, 1092753 | March | 2014 | 2014Q3 | 2014 | ZN129:PA19 | ZN129:PA64 | ZN00129/000064 | RYDE | OH | Not Veg | 2014-03-26 | N | 88.739 | N | 2 | N | N | 1.1101 | 39.4971 | 114780.6617
[7 empty] | 15979 | 14237 | 1092774 | 2014-03-26 23:07 | 2014-03-27 00:10 | 63.5833 | 11kV | 46924.5 | 738 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Section of ZN.195 Pymble 11kV Panel 30 from REC.46113 to the remainder of the feeder. Tripped, re-closed, tripped and locked-out on OC. ME-109774 Related 1092776, 1092777 | March | 2014 | 2014Q3 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2014-03-26 | N | 63.5833 | N | 2 | N | N | 1.1101 | 39.4971 | 34291.0406
[7 empty] | 16041 | 15307 | 1092789 | 2014-03-27 02:42 | 2014-03-27 05:45 | 183 | 11kV | 36593 | 458 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9035 Caringbah - Pnl 1 - Earth Leakage, EFI, Field EFI. Underground fault between S 9925, S 9031 and S 9487. DOp was unable to gain access to S 9925 and S 9031 at 03:00am. ME: 1093644. Rest Steps: 1093645, 7, 8. Withdrawn: 1092789. | March | 2014 | 2014Q3 | 2014 | ZN9035:PA1 | ZN9035:PA1 | ZN09035/000001 | SUTHERLAND | UG | Not Veg | 2014-03-27 | N | 79.8974 | N | 8 | N | N | 1.1101 | 39.4971 | 26741.0851
[7 empty] | 14772 | 609 | 1092784 | 2014-03-27 03:48 | 2014-03-27 06:14 | 146 | 11kV | 36497 | 592 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 149976 1 fault operation 3 phase Earth fault; Overcurrent Fault detection occured at Sw 61643; Targets 51AB Car hit pole adj to ABS 8030 despatched to on call lw Excluded OMS 1092784 & 1092790 | March | 2014 | 2014Q3 | 2014 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Not Veg | 2014-03-27 | N | 61.6503 | N | 8 | N | N | 1.1101 | 39.4971 | 26670.9311
[7 empty] | 14893 | 1881 | 1092786 | 2014-03-27 02:22 | 2014-03-27 07:30 | 308 | 11kV | 141102 | 1804 | HV | Fire (non-electrical) | Adverse Weather/Environment | DC Not Transformer | Unplanned | Rain Light | N | LID 149981 2 fault operations A & C phase Earth fault; Overcurrent 11kV Hazemeyer Sw'Gear fault at Thompson Street sub 71181. Excluded OMS No. 1092786+1092788 | March | 2014 | 2014Q3 | 2014 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | Unknown | Not Veg | 2014-03-27 | N | 78.2162 | N | 8 | N | N | 1.1101 | 39.4971 | 103113.1798
[7 empty] | 14879 | 1755 | 1092794 | 2014-03-27 05:51 | 2014-03-27 08:50 | 179 | 11kV | 60359 | 1021 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Light | N | LID 149980 2 fault operations 3 phase Instantaneous Overcurrent 11kV Hazemeyer Switchgear fault at Dodd St sub 73026. Excluded OMS No. 1092794+1092800 | March | 2014 | 2014Q3 | 2014 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | UG | Not Veg | 2014-03-27 | N | 59.1175 | N | 8 | N | N | 1.1101 | 39.4971 | 44108.5769
[7 empty] | 15654 | 10503 | 1092876 | 2014-03-27 08:48 | 2014-03-27 10:40 | 112 | 11kV | 161853 | 1820 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | @S1287 Revesby Panel 15 'S47211 Eastern Tomp Etc" feeder tripped, reclosed, tripped and locked out on Relays - A & C phase IOC, C phase OC, lockout, timing Signals - 11kv trip Remarks: Air break switch. AB524 Insulators failed & will not open on 2 phases. | March | 2014 | 2014Q3 | 2014 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-03-27 | N | 88.9302 | N | 8 | N | N | 1.1101 | 39.4971 | 118277.3985
[7 empty] | 15686 | 10856 | 1093310 | 2014-03-27 19:21 | 2014-03-27 20:15 | 54 | 11kV | 1782 | 33 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Unselected | N | @PT13421 Serpentine Terrigal 0.4 31.5Amp Midle Phase HDO operated Tree branch on PT. @Zn14144 Wamberal Pa5 EFI operated @PT48338 suspect in LV// at time of outage. Due to customer calls having the same Low volts. See 1093511 lv// 1093312 exclude 1093308,10 | March | 2014 | 2014Q3 | 2014 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Veg | 2014-03-27 | N | 54 | N | 8 | N | N | 1.1101 | 39.4971 | 1302.233
[7 empty] | 15307 | 6493 | 1093315 | 2014-03-27 23:10 | 2014-03-28 01:00 | 110 | 11kV | 3300 | 30 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 149986 Section isolated for repairs at pole GU-61705 CC1: 22-"Refer to SOp" | March | 2014 | 2014Q3 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-03-27 | N | 110 | N | 8 | N | N | 1.1101 | 39.4971 | 2411.5427
[7 empty] | 14928 | 2130 | 1093335 | 2014-03-27 23:42 | 2014-03-28 02:00 | 138 | 11kV | 1380 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 149987 B phase DOLF carrier burnt up | March | 2014 | 2014Q3 | 2014 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2014-03-27 | N | 138 | N | 8 | N | N | 1.1101 | 39.4971 | 1008.4633
[7 empty] | 15416 | 7592 | 1093341 | 2014-03-28 02:56 | 2014-03-28 07:30 | 274 | 11kV | 9864 | 36 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 149988 A phase DOLF : 16 Amp B. Lindsay first attended, deenergise and interconnected. Blown HV arrestor Aph Excluded OMS 1093341 | March | 2014 | 2014Q3 | 2014 | 225:33679 | 270:83594 | ZN00270/083594 | LAKE MACQUARIE | OH | Not Veg | 2014-03-28 | N | 274 | N | 6 | N | N | 1.1101 | 39.4971 | 7208.3203
[7 empty] | 14916 | 2040 | 1093368 | 2014-03-28 08:01 | 2014-03-28 10:00 | 119 | 11kV | 119 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Rain Light | N | LID 149992 Single phase DOLF : 10 Amp Excluded OMS 1093368 | March | 2014 | 2014Q3 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-03-28 | N | 119 | N | 6 | N | N | 1.1101 | 39.4971 | 86.9617
[7 empty] | 15682 | 10788 | 1094107 | 2014-03-28 15:45 | 2014-03-28 16:10 | 25 | 11kV | 50 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 149995 C Phase - Fuse size: 31 Amp Line DOLF Excluded OMS 1093635 | March | 2014 | 2014Q3 | 2014 |  |  |  | UPPER HUNTER | OH | Veg | 2014-03-28 | N | 25 | N | 6 | N | N | 1.1101 | 39.4971 | 36.5385
[7 empty] | 16398 | 19154 | 1093692 | 2014-03-28 16:25 | 2014-03-28 17:32 | 67 | 11kV | 86677 | 1333 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn14891 Wyong Pa16 "Wadalba" fdr tripped on Relays: Earth Fault, Reclose & Lock out, fault check, EFI Tx2 Earth Fault Check Signals: Zone Tx2 Group Earth & Lock Out UG cable fault between S14939SwA Glider Dantree & S14938SwB Van Stapen Glider See 1094216,8 exclude 1093692 | March | 2014 | 2014Q3 | 2014 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | UG | Not Veg | 2014-03-28 | N | 65.024 | N | 6 | N | N | 1.1101 | 39.4971 | 63340.9951
[7 empty] | 16293 | 17937 | 1093732 | 2014-03-28 18:52 | 2014-03-28 19:30 | 38 | 11kV | 380 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140011 A & C phase DOLF : 10 Amp Excluded OMS 1093732, 1093754 | March | 2014 | 2014Q3 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-03-28 | N | 38 | N | 6 | N | N | 1.1101 | 39.4971 | 277.6928
[7 empty] | 15213 | 4799 | 1093745 | 2014-03-28 20:17 | 2014-03-28 21:37 | 80 | 11kV | 62160 | 777 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12570 Avoca Pa34 "Terrigal" fdr tripped Relays: A&B overcurrent and ABC IOC and lock out relay Cause: Flashover/Arcing Details: Palm tree branch in Easter Pde touching 11kv mains Lineworkers cut branches DOp checked volts at end of feeder See 1093745 Exclude 1093643,746,9,50,1 | March | 2014 | 2014Q3 | 2014 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2014-03-28 | N | 80 | N | 6 | N | N | 1.1101 | 39.4971 | 45424.6946
[7 empty] | 15990 | 14494 | 1093769 | 2014-03-29 03:54 | 2014-03-29 04:34 | 40 | 11kV | 18800 | 470 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140014 1 Fault Operations A Phase Overcurrent | March | 2014 | 2014Q3 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-03-29 | N | 40 | N | 6 | N | N | 1.1101 | 39.4971 | 13738.4855
[7 empty] | 14765 | 569 | 1093768 | 2014-03-29 03:27 | 2014-03-29 09:50 | 383 | 11kV | 20274 | 151 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 140023 3 phase Tree on Mains Excluded OMS 1093768 | March | 2014 | 2014Q3 | 2014 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2014-03-29 | N | 134.2649 | N | 6 | N | N | 1.1101 | 39.4971 | 14815.6412
[7 empty] | 14849 | 1377 | 1093825 | 2014-03-29 16:10 | 2014-03-29 17:10 | 60 | 11kV | 60 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 1490016 A & B Phases DORF Excluded OMS 1093825 | March | 2014 | 2014Q3 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-03-29 | N | 60 | N | 6 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 16056 | 15463 | 1093886 | 2014-03-29 19:35 | 2014-03-29 19:40 | 5 | 11kV | 30 | 6 | HV | Animal Bird | Animal | DC Not Transformer | Unplanned | Unselected | N | LID 140015 3 phase Bird on OHM at sub 51783 feeder de energised to remove | March | 2014 | 2014Q3 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-03-29 | N | 5 | N | 6 | N | N | 1.1101 | 39.4971 | 21.9231
[7 empty] | 15490 | 8314 | 1093894 | 2014-03-29 20:58 | 2014-03-29 22:44 | 106 | 11kV | 49736 | 485 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" Re45202 Pacific Ashbrookke 2.0 tripped, reclosed, tripped and locked out on OC & IOC Tree come down near USL42049 DOp remoed branches and supply restored See 1094235,7 exclude 1093894 | March | 2014 | 2014Q3 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2014-03-29 | N | 102.5485 | N | 6 | N | N | 1.1101 | 39.4971 | 36345.6018
[7 empty] | 16392 | 19056 | 1093891 | 2014-03-29 21:25 | 2014-03-30 04:55 | 450 | 11kV | 27930 | 87 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Section ZN.15002 Panel 2 from ABS.23610 to extent of feeder. Car Hit Pole. Interrupted for safety to replace HV pole at 11 Wilga St. ME-1094082, RS-1094085. Withdrawn-1093891 & 1093897. | March | 2014 | 2014Q3 | 2014 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Not Veg | 2014-03-29 | N | 321.0345 | N | 6 | N | N | 1.1101 | 39.4971 | 20410.4202
[7 empty] | 14719 | 223 | 1093910 | 2014-03-30 01:53 | 2014-03-30 05:50 | 237 | 11kV | 221650 | 1827 | HV | Equipment Failed in Service | Equipment Failure | Busbar | Unplanned | Electrical Storm | N | LID 140026 3 phase Overcurrent; Earth fault; Busbar Protection Feeder Fault on 34840 lost zone 2 bus bar | March | 2014 | 2014Q3 | 2014 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | Unknown | Not Veg | 2014-03-30 | N | 121.3191 | N | 5 | N | N | 1.1101 | 39.4971 | 161975.2824
[7 empty] | 15883 | 12958 | 1093945 | 2014-03-30 10:01 | 2014-03-30 11:45 | 104 | 11kV | 190895 | 2344 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10999 Kogarah - Pnl 36 - Earth Fault, Fault check, EFI, Field EFIs. Blown UGOH at top of pole below S 10662. ME: 1094184. Rest Steps: 1094186, 7. Withdrawn: Stacks. | March | 2014 | 2014Q3 | 2014 | ZN10999:PA36 | ZN10991:PA2 | ZN10991/000002 | GEORGES RIVER | Unknown | Unknown | 2014-03-30 | N | 81.4398 | N | 5 | N | N | 1.1101 | 39.4971 | 139500.4356
[7 empty] | 16286 | 17865 | 1093960 | 2014-03-30 10:44 | 2014-03-30 13:34 | 170 | 11kV | 4930 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 140017 A phase DOLF : 10 Amp Excluded OMS 1093960 | March | 2014 | 2014Q3 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-03-30 | N | 170 | N | 5 | N | N | 1.1101 | 39.4971 | 3602.6986
[7 empty] | 15072 | 3425 | 1094014 | 2014-03-30 18:50 | 2014-03-30 20:50 | 120.15 | 11kV | 841.05 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140002 B phase DOLF : 10 Amp | March | 2014 | 2014Q3 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-03-30 | N | 120.15 | N | 5 | N | N | 1.1101 | 39.4971 | 614.6145
[7 empty] | 15812 | 12257 | 1094040 | 2014-03-30 21:39 | 2014-03-30 23:20 | 101 | 11kV | 2323 | 23 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | Ex Zn14144 Wamberal section of Pa2 PT13872 Oak Koorin 0.5 footpath side HDO 31.5 Surge arrestor appears to have operated needs to be replaced. LV Network restored LV// link 36221 See 1095151 exclude 1094040,1,2,8 | March | 2014 | 2014Q3 | 2014 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Not Veg | 2014-03-30 | N | 101 | N | 5 | N | N | 1.1101 | 39.4971 | 1697.5799
[7 empty] | 15467 | 8119 | 1094055 | 2014-03-31 04:20 | 2014-03-31 05:49 | 89 | 11kV | 75964 | 1252 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN.15005 Belrose Panel 6, tripped & reclosed. Relays: B phase OC, locked out & timing relay and fault check. RE.24831 Locwood Peacock, tripped & locked out. Relay: B phase OC. Animal found near LBS.24802. ME-1094171, RS-1094175. Withdrawn-1094055. | March | 2014 | 2014Q3 | 2014 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2014-03-31 | N | 60.6741 | N | 3 | N | N | 1.1101 | 39.4971 | 55512.2506
[7 empty] | 15163 | 4236 | 1094114 | 2014-03-31 08:40 | 2014-03-31 13:20 | 280 | 11kV | 840 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140028 SECTION ISOLATED TO REPAIR LOW 11 KV MAINS | March | 2014 | 2014Q3 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-03-31 | N | 280 | N | 3 | N | N | 1.1101 | 39.4971 | 613.8472
[7 empty] | 15740 | 11504 | 1094484 | 2014-03-31 18:22 | 2014-03-31 19:55 | 93 | 11kV | 186 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | Ex Zn14143 Somersby section of Pa17 "Somersby Fall" fdr relays: EFI Signals: Tx2 Group Earth EFI's: No access to S18569 S18639 @PT18357 Pacific Cheero 2.1 Roadside 16K amp HDO & HV arrestor blown. See 1095147 exclude 1094484 | March | 2014 | 2014Q3 | 2014 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2014-03-31 | N | 93 | N | 3 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 14998 | 2860 | 1094717 | 2014-04-01 13:43 | 2014-04-01 15:20 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140048 B phase DOLF : 5 Amp TX Volts 244 Excluded OMS 1094717 | April | 2014 | 2014Q4 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-04-01 | N | 97 | N | 1 | N | N | 1.1101 | 39.4971 | 70.8847
[7 empty] | 15704 | 11027 | 1094955 | 2014-04-02 09:00 | 2014-04-02 16:30 | 449.5667 | 11kV | 7857.3167 | 24 | HV | Arcing | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140068 No protection operated, K Davidson attended after customer call to depoit advising of arcing on overhead mains. Outage extended to Re 46638 to repair lk 74760 Kevin found a tapping burnt off load side of 11kV link 74760 and opened the link. Excluded OMS job 1095207 | April | 2014 | 2014Q4 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-04-02 | N | 327.3882 | N | 2 | N | N | 1.1101 | 39.4971 | 5741.8953
[7 empty] | 14923 | 2081 | 1095212 | 2014-04-02 15:00 | 2014-04-02 16:55 | 115 | 11kV | 7245 | 63 | HV | 3rd Party Vehicle | 3rd Party Impact | DC PT | Unplanned | Unselected | N | LID 140073 A & B Phases - Fuse size: 315 Amp Distribution LV Fuse Car hit SP IU-22598 Excluded OMS 1095212 | April | 2014 | 2014Q4 | 2014 | 216:10726 | 216:10726 | ZN00216/010726 | LAKE MACQUARIE | OH | Not Veg | 2014-04-02 | N | 115 | N | 2 | N | N | 1.1101 | 39.4971 | 5294.4323
[7 empty] | 15517 | 8661 | 1095452 | 2014-04-03 09:54 | 2014-04-03 12:19 | 145 | 11kV | 145 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 140092 B Phase - Fuse size: 5 Amp DORF Excluded OMS 1095452 | April | 2014 | 2014Q4 | 2014 |  |  |  |  | OH | Not Veg | 2014-04-03 | N | 145 | N | 3 | N | N | 1.1101 | 39.4971 | 105.9617
[7 empty] | 15999 | 14615 | 1095543 | 2014-04-03 11:09 | 2014-04-03 13:08 | 119 | 11kV | 56910 | 554 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140070 1 fault operation Sensitive Earth Fault; Overcurrent fdr abnormal Sw 50354 closed & Sw 18241 open. Fdr patrolled no cause found. Excluded oms # 1095543 | April | 2014 | 2014Q4 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2014-04-03 | N | 102.7256 | N | 3 | N | N | 1.1101 | 39.4971 | 41588.1494
[7 empty] | 15214 | 4801 | 1095721 | 2014-04-03 17:08 | 2014-04-03 19:35 | 147 | 11kV | 19318 | 776 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn12570 Avoca 11kv Pa41 "Avoca Aux No.12" fdr tripped and reclosed Relays: A&B phase IOC Signals: 11kv trip EFI's Nil HV bond burnt off at LB44425 (footpath side/zone side) PT13984 Duffys Kings 0.5 interrupted at 1820 Unsafe to open LV44425 Repairs complete. Network Normal. See 1095866,7,8 GIS 1095748 Exclude 1095721,1,4,32,9 | April | 2014 | 2014Q4 | 2014 | ZN12570:PA41 | ZN12570:PA41 | ZN12570/000041 | CENTRAL COAST | OH | Not Veg | 2014-04-03 | N | 24.8943 | N | 3 | N | N | 1.1101 | 39.4971 | 14117.0246
[7 empty] | 15157 | 4198 | 1095764 | 2014-04-04 04:36 | 2014-04-04 05:40 | 64 | 11kV | 576 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140099 3 phase DOLF : 16 Amp Excluded OMS 1095764 | April | 2014 | 2014Q4 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-04-04 | N | 64 | N | 7 | N | N | 1.1101 | 39.4971 | 420.9238
[7 empty] | 15836 | 12488 | 1096691 | 2014-04-04 08:00 | 2014-04-04 10:00 | 120 | 11kV | 360 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 140106 Single phase DOLF : 16 Amp Outage reported to Muswellbrook depot directly. Operator reports that feeder was patrolled. | April | 2014 | 2014Q4 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-04-04 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 15201 | 4652 | 1096087 | 2014-04-04 17:53 | 2014-04-04 19:10 | 77 | 11kV | 231 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Ex Zn12620 Noraville section of Pa2 "Budgewoi" fdr @PT13477 Calga Pastoral Cooks, 11kV HDO 16K Blown Cause not ascertained. Lightning in area at time See 1097698 exclude 1096087 | April | 2014 | 2014Q4 | 2014 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2014-04-04 | N | 77 | N | 7 | N | N | 1.1101 | 39.4971 | 168.808
[7 empty] | 14704 | 76 | 1097704 | 2014-04-04 18:55 | 2014-04-04 19:42 | 47 | 11kV | 1674 | 37 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Heavy | N | Ex Zn12620 Noraville section of 11kv Pa2 "Budegwoi" fdr Urgent repair on HV crossarm on Pole BU3873 Repairs complete. See 1097704,5 | April | 2014 | 2014Q4 | 2014 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2014-04-04 | N | 45.2432 | N | 7 | N | N | 1.1101 | 39.4971 | 1223.3098
[7 empty] | 14823 | 1134 | 1096142 | 2014-04-04 21:35 | 2014-04-04 22:30 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140114 Single phase DOLF : 10 Amp Excluded OMS 1096142 | April | 2014 | 2014Q4 | 2014 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Veg | 2014-04-04 | N | 55 | N | 7 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 15826 | 12404 | 1096126 | 2014-04-04 20:40 | 2014-04-05 02:00 | 320 | 11kV | 78122 | 1646 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 140115 1 fault operation A & B phase Overcurrent; Earth fault Sw 33409 A & B O/C, E/F, Timed B & C O/C. B phase tapping blown off & in contact with C phase conductor between link 8424 & UGOH. Excluded OMS 1096126 | April | 2014 | 2014Q4 | 2014 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Not Veg | 2014-04-04 | N | 47.4617 | N | 7 | N | N | 1.1101 | 39.4971 | 57089.2534
[7 empty] | 15396 | 7395 | 1096160 | 2014-04-05 03:03 | 2014-04-05 06:14 | 191 | 11kV | 43547 | 1012 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn14144 Wamberal Pa2 "Glen Eagles Fairway" tripped on Relays: B & C Phase Overcureent, Earth Fault, EFI, Lockout Signals: 11kv trip, Tx2 Group Earth EFI's S14885 S11086 S12742 S18448 Cause: Large branch on LV OH mains adjacent PT14544 cause fdr trip See 1097715,7 Exclude 1096160 | April | 2014 | 2014Q4 | 2014 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2014-04-05 | N | 43.0306 | N | 2 | N | N | 1.1101 | 39.4971 | 31822.8632
[7 empty] | 15528 | 8779 | 1096262 | 2014-04-05 20:45 | 2014-04-05 21:45 | 60 | 11kV | 360 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | LID 140127 isolated for safety. burnt lv tx bushing lug Excluded OMS 1096262 | April | 2014 | 2014Q4 | 2014 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | UG | Not Veg | 2014-04-05 | N | 60 | N | 2 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 15153 | 4174 | 1096321 | 2014-04-06 01:32 | 2014-04-06 02:20 | 48 | 11kV | 2832 | 59 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa9 @PT11650 Malison Maranoa the roadside 11kv HDO tripped Fuse fatigue. 31.5 Amps Fuse (batch 0443) See 1097750 exclude 1096321,2 | April | 2014 | 2014Q4 | 2014 | ZN12600:PA9 | ZN12600:PA11 | ZN12600/000011 | CENTRAL COAST | OH | Not Veg | 2014-04-06 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 2069.5421
[7 empty] | 15388 | 7299 | 1096365 | 2014-04-06 12:50 | 2014-04-06 18:10 | 320 | 11kV | 7530 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of Pa1 @RE44853 Ourimbah Bumble tripped on SEF 1 phase section of 11kv fdr down between LB44051 & tee off PT12759 Ourimbah Ck Bumble 3.6 See 1097763,4 Exclude 1096365 | April | 2014 | 2014Q4 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2014-04-06 | N | 171.1364 | N | 4 | N | N | 1.1101 | 39.4971 | 5502.7019
[7 empty] | 16013 | 14770 | 1096432 | 2014-04-06 19:48 | 2014-04-06 20:39 | 51 | 11kV | 41973 | 823 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn14144 Wamberal Pa4 "Wamberal Aux#1" tripped & reclosed & locked out on: Aphase overcurrent EFI Tree branch removed from overhead outside #3 Mittara st Terrigal. Mains to check in daylight for stranding See 1096432 exclude 1096434,5,7 | April | 2014 | 2014Q4 | 2014 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2014-04-06 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 30672.6304
[7 empty] | 15452 | 7962 | 1096411 | 2014-04-06 18:10 | 2014-04-06 20:42 | 152 | 11kV | 127908 | 1080 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex ZN 10994 Mortdale - Pnl 4L - 11kV Bond 11kV Bond failed in service between AB 31047 and S 48983 tee PT 61869. ME: 1096990. Rest Step: 1096991. ME GIS: 1096423. Withdrawn: 1096411, 3, 9. | April | 2014 | 2014Q4 | 2014 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2014-04-06 | N | 118.4333 | N | 4 | N | N | 1.1101 | 39.4971 | 93471.3938
[7 empty] | 15383 | 7241 | 1096525 | 2014-04-07 08:54 | 2014-04-07 09:42 | 48 | 11kV | 66000 | 1375 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ZN.1673 Turramurra panel 11 11kV CB Feeder tripped, re-closed, tripped and Locked-out. Relays: (Basler BE1) A & B phase timed OC, Re-close, Lock-out. Signals: Tx 2 group earth. Tree branch on OH mains outside 55 The Comenarra near Ravenhill Rd. Suspected LV// at USL.4498 indicated on the LV// database at the time of known outage. ME-1096525, SE-1097036 Withdrawn-1096532, 1096551, 1096577. | April | 2014 | 2014Q4 | 2014 | ZN1673:PA11 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2014-04-07 | N | 48 | N | 3 | N | N | 1.1101 | 39.4971 | 48230.8533
[7 empty] | 16409 | 19273 | 1096816 | 2014-04-07 15:50 | 2014-04-07 16:45 | 55 | 11kV | 3190 | 58 | HV | Equipment Failed in Service | Equipment Failure | Joint | Unplanned | Unselected | N | LID 140143 LVF 38832 opened to make repairs at SP IU-10112 Excluded OMS 1096816 | April | 2014 | 2014Q4 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | Unknown | Not Veg | 2014-04-07 | N | 55 | N | 3 | N | N | 1.1101 | 39.4971 | 2331.1579
[7 empty] | 15026 | 3035 | 1096755 | 2014-04-07 14:50 | 2014-04-07 17:00 | 130 | 11kV | 130 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140142 B Phase - Fuse size: 10 Amp Substation DOLF Blown Bph L/A replaced. LLC dropper repaired. Excluded OMS 1096755 | April | 2014 | 2014Q4 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-04-07 | N | 130 | N | 3 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 15318 | 6569 | 1096916 | 2014-04-08 06:34 | 2014-04-08 08:55 | 141 | 11kV | 141 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140149 A phase DOLF : 10 Amp Excluded OMS 1097436 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-04-08 | N | 141 | N | 3 | N | N | 1.1101 | 39.4971 | 103.0386
[7 empty] | 16134 | 16343 | 1096116 | 2014-04-04 20:09 | 2014-04-08 14:10 | 5401 | 11kV | 470654.5667 | 2956 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140113 3 fault operations A phase Overcurrent; Earth fault Fdr abnormal taking part load from Fdr 34840 (56284/16289/2297) Repaired 11kV main on ground pole JT-91727 On restoration found faulty UGOH pole JT-87102. | April | 2014 | 2014Q4 | 2014 | 240:34840 | 240:34840 | ZN00240/034840 | NEWCASTLE | OH | Not Veg | 2014-04-04 | N | 159.2201 | N | 7 | N | N | 1.1101 | 39.4971 | 343940.4754
[7 empty] | 14821 | 1128 | 1097226 | 2014-04-08 14:13 | 2014-04-08 15:15 | 62 | 11kV | 62 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140163 C phase DOLF : 16 Amp Excluded OMS 1097226 | April | 2014 | 2014Q4 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2014-04-08 | N | 62 | N | 3 | N | N | 1.1101 | 39.4971 | 45.3078
[7 empty] | 15756 | 11679 | 1097350 | 2014-04-08 20:31 | 2014-04-08 21:59 | 88 | 11kV | 61424 | 698 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | ZN 10995 Riverwood - Pnl 8 - Trip/reclose, A phase IOC and Timed OC, Lockout, timing. Pole snapped in Trafalgar St near Hughs Rd, Peakhurst. Wires down. ME: 1097480. Rest Step: 1097482. ME GIS: 1097361. Withdrawn: 1097350, 3, 7, 8, 1097362. | April | 2014 | 2014Q4 | 2014 | ZN10995:PA8 | ZN10995:PA8 | ZN10995/000008 | GEORGES RIVER | OH | Not Veg | 2014-04-08 | N | 88 | N | 3 | N | N | 1.1101 | 39.4971 | 44886.8475
[7 empty] | 15946 | 13673 | 1097376 | 2014-04-09 01:07 | 2014-04-09 01:55 | 48 | 11kV | 70752 | 1474 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12650 West GOsford section of Pa1 @RE44936 Bently Rd, tripped & locked out on overcurrent trip Tree branch on Oh mains. Near PT13230 See 1097869 exclude 1097376,7 | April | 2014 | 2014Q4 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-04-09 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 51703.4748
[7 empty] | 16209 | 17127 | 1097419 | 2014-04-09 08:19 | 2014-04-09 14:45 | 386 | 11kV | 386 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | @Sub 5318 Eldridge Sim #2 HV fuse C phase OEFMA 75A Remarks: Fuse fatigue | April | 2014 | 2014Q4 | 2014 | ZN2196:PA18 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-04-09 | N | 386 | N | 4 | N | N | 1.1101 | 39.4971 | 282.0774
[7 empty] | 15303 | 6463 | 1097687 | 2014-04-09 15:00 | 2014-04-09 15:58 | 58 | 11kV | 87232 | 1504 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12580 Erina Pa10 "Erina High Erina" fdr tripped on Cphase overcurrent EFI & 11kv protection trip Large branch removed by DOp outside 34 Sunvalley Rd Green Point See 1097687 Exclude 1097701,32 | April | 2014 | 2014Q4 | 2014 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | OH | Veg | 2014-04-09 | N | 58 | N | 4 | N | N | 1.1101 | 39.4971 | 63746.5727
[7 empty] | 16466 | 20129 | 1097798 | 2014-04-09 18:49 | 2014-04-09 19:45 | 56 | 11kV | 78508 | 1410 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN195 Pymble Pa30 Tripped on Earth Fault, C phase O/C EFI and Fault Check. Cause: reports of explosion at PT1707 Corronga Fiddens See OMS 1098141 1097798 1098142 1097803/805/800/801/804 | April | 2014 | 2014Q4 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2014-04-09 | N | 55.6794 | N | 4 | N | N | 1.1101 | 39.4971 | 57371.3308
[7 empty] | 16310 | 18110 | 1097903 | 2014-04-10 09:44 | 2014-04-10 12:40 | 176.5 | 11kV | 6177.5 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 140181 section isolated to repair mains at pole FM-90038 | April | 2014 | 2014Q4 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | UG | Not Veg | 2014-04-10 | N | 176.5 | N | 3 | N | N | 1.1101 | 39.4971 | 4514.3348
[7 empty] | 16058 | 15465 | 1098287 | 2014-04-10 14:05 | 2014-04-10 14:15 | 10 | 11kV | 180 | 18 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 140192 11kV Fdr interrupted to remove tree branch near pole 8V-20031. | April | 2014 | 2014Q4 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-04-10 | N | 10 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 16094 | 15972 | 1098242 | 2014-04-10 20:56 | 2014-04-11 00:50 | 234.3667 | 11kV | 1949.75 | 9 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Section of ZN.35500 Top Ryde Panel 32 from CP.1835 to extent of feeder (2 DC's, PT.2141 & S.7611). Section of 11kV HV feeder from HDO's CP.1835. Phase centre and footpath HDO's 63K. Second recent occurrence, 24/3/2014 OMS-1092099 & 1091705. ME-1098539. ME GIS Error-1098242. Withdrawn-1098243, 1098244. | April | 2014 | 2014Q4 | 2014 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2014-04-10 | N | 216.6389 | N | 3 | N | N | 1.1101 | 39.4971 | 1424.8198
[7 empty] | 15550 | 8934 | 1098251 | 2014-04-11 04:31 | 2014-04-11 07:10 | 159 | 11kV | 40971 | 695 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Rain Light | N | @ S34722 Sefton Panel #29 tripped and reclose on 11kv trip and #2 GE IOC EFI EF check recloser timing Field EFIs, S4410, S8974, S4235 Remarks: UGOH fault open circuit. 11kv fdr from S1100 Esme Hector to AB 1510 tee PT1018 Esme Pram | April | 2014 | 2014Q4 | 2014 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2014-04-11 | N | 58.9511 | N | 2 | N | N | 1.1101 | 39.4971 | 29940.3984
[7 empty] | 14808 | 1015 | 1098325 | 2014-04-11 08:36 | 2014-04-11 09:10 | 34 | 11kV | 9109 | 311 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn711 Blackwattle Bay - Pnl.16 tripped on earth fault Field EFIs: S4785 S1203 (No EFI @ S7405) UG Cable fault between S1203 and S702 | April | 2014 | 2014Q4 | 2014 | ZN711:PA16 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2014-04-11 | N | 29.2894 | N | 2 | N | N | 1.1101 | 39.4971 | 6656.5885
[7 empty] | 15273 | 6072 | 1098677 | 2014-04-12 08:03 | 2014-04-12 10:40 | 157 | 11kV | 314 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140212 A phase - Fuse size: 16 Amp Substation DOLF Replaced fatigued HV fuse on Dist sub 9732. 16amp A phase. Power restored at 10:40 am and checked all ok. Excluded OMS 1098677 | April | 2014 | 2014Q4 | 2014 | 256:80632 | 256:80632 | ZN00256/080632 | LAKE MACQUARIE | OH | Not Veg | 2014-04-12 | N | 157 | N | 3 | N | N | 1.1101 | 39.4971 | 229.4619
[7 empty] | 16078 | 15743 | 1098646 | 2014-04-12 07:30 | 2014-04-12 12:17 | 287 | 11kV | 287 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | LID 140213 Isolated for safety. Fault on customers ugoh and UG cable. Customer to notify when supply needed. LV fuses left withdrawn and warning tagged. SUB 27750, ISOLATED AND DT LVF AT SUB. SHORT CCT SERVICE MAINS INSIDE CONDUIT ON LOAD SIDE OF SLV SUB FUSES AND LINE SIDE OF SERVICE FUSES. BOTH SETS OF FUSES MOUNTED ON SUB POLE. Replaced AG mains and replaced sub fuses. Meggered customer's consumers mains and all phases down to earth. Referred to contractor. Excluded OMS 1098646 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | Unknown | Not Veg | 2014-04-12 | N | 287 | N | 3 | N | N | 1.1101 | 39.4971 | 209.7311
[7 empty] | 15516 | 8621 | 1098760 | 2014-04-12 14:18 | 2014-04-12 15:17 | 59 | 11kV | 20816 | 408 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn14143 Somersby Pa5 "Wisemans sulo" fdr tripped on overcurrent & Earth Fault & EFI Field EFI: S18048. UG front line fdr fault See 1099073,6 Exclude 1098760 | April | 2014 | 2014Q4 | 2014 | ZN14143:PA5 | ZN14143:PA16 | ZN14143/000016 | CENTRAL COAST | UG | Not Veg | 2014-04-12 | N | 51.0196 | N | 3 | N | N | 1.1101 | 39.4971 | 15211.7188
[7 empty] | 16492 | 20355 | 1098868 | 2014-04-13 11:10 | 2014-04-13 14:15 | 185 | 11kV | 7400 | 40 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 140218 Sub isolated to replace faulty LV Crossarm Excluded OMS 1098869, 1098868 | April | 2014 | 2014Q4 | 2014 | 225:33676 | 270:83591 | ZN00270/083591 | LAKE MACQUARIE | OH | Not Veg | 2014-04-13 | N | 185 | N | 2 | N | N | 1.1101 | 39.4971 | 5407.7017
[7 empty] | 15024 | 3014 | 1098900 | 2014-04-13 14:01 | 2014-04-13 14:49 | 48 | 11kV | 37056 | 772 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12570 Avoca section of Pa29 @RE44982 "Bensville" tripped and locked out on Relays: Overcurrent trip, Lockout Singals: 11kv trip EFI's: Nil Large branch found on 11kv OH near PT14608 Empire Bay Wandi | April | 2014 | 2014Q4 | 2014 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2014-04-13 | N | 48 | N | 2 | N | N | 1.1101 | 39.4971 | 27079.4318
[7 empty] | 15633 | 10128 | 1098955 | 2014-04-14 04:37 | 2014-04-14 10:07 | 329.7167 | 11kV | 28355.6333 | 86 | HV | Arcing | Equipment Failure | UGOH | Unplanned | Unselected | N | Ex Zn12570 Avoca section of Pa21L "Mayfair Kings" fdr 11kv UGOH to S14297 Kale Belar arcing S14297 Kale Belar interrupted due to fluctuating volts caused by arcing HV UGOH 11kv fdr from S14858 Sw/A Sheffield Sainsbury to S18042 Sw/B Swindon Canterbury to AB42870 tee S14297 isolated & earthed LV// for S14297 link box 21783 See 1098948 exclude 1098955,65,8,74,6 CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | April | 2014 | 2014Q4 | 2014 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | OH | Not Veg | 2014-04-14 | N | 329.7167 | N | 3 | N | N | 1.1101 | 39.4971 | 20721.4605
[7 empty] | 16370 | 18747 | 1099428 | 2014-04-14 12:51 | 2014-04-14 12:57 | 6 | 11kV | 24 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section panel 6L 11kV feeder from RE-26228 Valley Rd to extent of feeder opened (3 DC's). Interruptted for safety reasons to remove tree branch resting against stand off insulators at pole FF-1571. ME-1099428. | April | 2014 | 2014Q4 | 2014 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2014-04-14 | N | 6 | N | 3 | N | N | 1.1101 | 39.4971 | 17.5385
[7 empty] | 15393 | 7381 | 1099390 | 2014-04-14 19:59 | 2014-04-14 21:27 | 88 | 11kV | 79531 | 1021 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | ZN.965 Pennant Hills Panel 4311kV feeder tripped. Relays:- Trip signal and EFI on Relay. Signals:- 11kV CB 43 Trip, CB 43 OC & EF Relay Trip, Tx2 Protection Under Volts. Field EFI's:- Nil. Cause not ascertained. Reported that OC & EF defective on Panel 43 at Pennant Hills, LED display would not work. ME-1099439, RS-1099440. Withdrawn-1099390, 1099397, 1099398. | April | 2014 | 2014Q4 | 2014 | ZN965:PA43 | ZN965:PA43 | ZN00965/000043 | HORNSBY | UG | Not Veg | 2014-04-14 | N | 77.8952 | N | 3 | N | N | 1.1101 | 39.4971 | 58118.909
[7 empty] | 15773 | 11850 | 1099481 | 2014-04-15 08:56 | 2014-04-15 10:29 | 93 | 11kV | 95477 | 1129 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ZN2310 Punchbowl - 11kv Panel No.17 "Sub 1055 Penshurst Rd" feeder tripped Relays: Earth fault, EFI Signals: 11kv trip, Zone earth, No.3 Group Earth Field EFI's: Sub 1055 Remarks: UG fault. 11kv UG fault from Sub 1055 Penshurst Ave to Sub 1612 Shorter Ave to Sub 3544 Moondari Ave | April | 2014 | 2014Q4 | 2014 | ZN2310:PA17 | ZN2310:PA25 | ZN02310/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-04-15 | N | 84.5678 | N | 4 | N | N | 1.1101 | 39.4971 | 69771.7755
[7 empty] | 14807 | 1002 | 1099620 | 2014-04-15 12:07 | 2014-04-15 13:30 | 83 | 11kV | 7138 | 86 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT.17120 Cheyne Timaru. Broken Roadside HV Fuse assembly/carrier. Restored by LV//'s at USL.37148, 36003, 36468. Switching tag at PT.17120 Cheyne Timaru. ME-1099620. Withdrawn-1099703. | April | 2014 | 2014Q4 | 2014 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-04-15 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 5216.2399
[7 empty] | 14937 | 2157 | 1099721 | 2014-04-15 14:41 | 2014-04-15 15:39 | 58 | 11kV | 2726 | 47 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 140243 B Phase Wire off a pin insulator | April | 2014 | 2014Q4 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2014-04-15 | N | 58 | N | 4 | N | N | 1.1101 | 39.4971 | 1992.0804
[7 empty] | 15504 | 8495 | 1100520 | 2014-04-15 21:43 | 2014-04-15 22:20 | 37 | 11kV | 4995 | 135 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Section of ZN.15013 Terry Hills 11kV panel 6 Feeder from 11kV USL.20945 to the extent of the feeder (11 DC's). At USL.20945 roadside link found open. Roadside link high resistance loose connection found open. ME-1100520. Withdrawn-1099843. | April | 2014 | 2014Q4 | 2014 | ZN15013:PA6 | ZN15013:PA6 | ZN15013/000006 | NORTHERN BEACHES | OH | Not Veg | 2014-04-15 | N | 37 | N | 4 | N | N | 1.1101 | 39.4971 | 3650.1987
[7 empty] | 15134 | 4016 | 1099861 | 2014-04-16 04:02 | 2014-04-16 05:48 | 106 | 11kV | 31416 | 311 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Zn188 Zetland Pnl.14 tripped on: A phase timmed O/C, EFI, Fault Check relay Field EFIs: S2937 S4250 S35786 End Box failure - S2977 Mentmore Epsom No.1 RMI Sw B endbox failed see 1099885 1099886 | April | 2014 | 2014Q4 | 2014 | ZN188:PA14 | ZN8100:PA28 | ZN08100/000028 | SYDNEY | Unknown | Not Veg | 2014-04-16 | N | 101.0161 | N | 4 | N | N | 1.1101 | 39.4971 | 22957.8862
[7 empty] | 15875 | 12892 | 1099857 | 2014-04-16 00:58 | 2014-04-16 08:05 | 427 | 11kV | 14091 | 33 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140249 6 Fault operations Pole Mounted RAGCB, Overcurrent, Earth Fault No Cause Found, Not Storm Conditions HV Reported Down, 11kV main on ground at pole 6K-60099 Note: There is a switching sheet, but on inspection, this made no difference to the restorations, all customer from 11874 off for 7 hrs and 7 minutes | April | 2014 | 2014Q4 | 2014 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2014-04-16 | N | 427 | N | 4 | N | N | 1.1101 | 39.4971 | 10297.2872
[7 empty] | 14906 | 1965 | 1100245 | 2014-04-16 17:05 | 2014-04-16 19:05 | 120.4167 | 11kV | 8790.4167 | 73 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S5868 Gore Hill 11kV CB Pa24 feeder tripped on overcurrent, EFI and Fault Check Cause; 11kV feeder fault from ZN5868 Gore Hill to S36102 Herbert Ella | April | 2014 | 2014Q4 | 2014 | ZN5868:PA24 | ZN5868:PA24 | ZN05868/000024 | WILLOUGHBY | UG | Not Veg | 2014-04-16 | N | 120.4167 | N | 4 | N | N | 1.1101 | 39.4971 | 6423.7772
[7 empty] | 15109 | 3849 | 1100236 | 2014-04-16 16:43 | 2014-04-16 19:15 | 152 | 11kV | 152 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140258 No OMS Job at time off doing this report. Problem reported to MBK Depot by Merriwa Contractor. Insulation perished on LV cable. LV cable touching tx bracket. Customers getting shocks of buildings. | April | 2014 | 2014Q4 | 2014 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-04-16 | N | 152 | N | 4 | N | N | 1.1101 | 39.4971 | 111.0771
[7 empty] | 15851 | 12696 | 1100426 | 2014-04-17 10:58 | 2014-04-17 11:50 | 52 | 11kV | 2132 | 41 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 140274 B phase DOLF : 31 Amp Excluded OMS 1100426 | April | 2014 | 2014Q4 | 2014 | 504:48028 | 522:83131 | ZN00522/083131 | CESSNOCK | UG | Not Veg | 2014-04-17 | N | 52 | N | 2 | N | N | 1.1101 | 39.4971 | 1558.0027
[7 empty] | 15401 | 7466 | 1100383 | 2014-04-17 09:43 | 2014-04-17 11:55 | 132 | 11kV | 2244 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140275 B phase DOLF : 20 Amp Excluded OMS 1100383 | April | 2014 | 2014Q4 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2014-04-17 | N | 132 | N | 2 | N | N | 1.1101 | 39.4971 | 1639.849
[7 empty] | 14870 | 1687 | 1100628 | 2014-04-18 02:30 | 2014-04-18 08:45 | 375 | 11kV | 159970 | 1070 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 140279 2 fault operations C phase Earth fault; Overcurrent faulty pin insulator at pole KU-13103, high into low Excluded OMS 1100628 | April | 2014 | 2014Q4 | 2014 | 228:7487 | 228:85410 | ZN00228/085410 | NEWCASTLE | OH | Not Veg | 2014-04-18 | N | 149.5047 | N | 1 | N | N | 1.1101 | 39.4971 | 116901.3577
[7 empty] | 15189 | 4471 | 1100800 | 2014-04-19 15:18 | 2014-04-19 19:30 | 252 | 11kV | 252 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140283 A phase DOLF : 10 Amp Blown arrestor on Aph - cut away - replacement required. Excluded OMS 1100800 | April | 2014 | 2014Q4 | 2014 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2014-04-19 | N | 252 | N | 1 | N | N | 1.1101 | 39.4971 | 184.1542
[7 empty] | 16218 | 17243 | 1100880 | 2014-04-20 11:33 | 2014-04-20 12:46 | 73 | 11kV | 94170 | 1290 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn847 Hornsby Pa21 Jersey Bridge has tripped Relays: C phase IOC and Timed LO and Timer Signals: 11kV Trip Cause: Tree on Mains near 41 Manor Rd See OMS 1100885 1100880 1100882 | April | 2014 | 2014Q4 | 2014 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2014-04-20 | N | 73 | N | 2 | N | N | 1.1101 | 39.4971 | 68816.6585
[7 empty] | 15225 | 5060 | 1100935 | 2014-04-21 07:00 | 2014-04-21 09:30 | 150 | 11kV | 1650 | 11 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | Ez Zn12630 Peats Ridge section of Pa4 "Kulnura" fdr @PT13662 Ross Peats Ridge 0.8 16Amp footpath HDO operated Flashovedr by possum @ PT13662. DOp completed from ground suspect pole unsafe to climb, refer mains See 1101471 exclude 1100935,7,42 | April | 2014 | 2014Q4 | 2014 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-04-21 | N | 150 | N | 2 | N | N | 1.1101 | 39.4971 | 1205.7713
[7 empty] | 15900 | 13174 | 1100966 | 2014-04-21 11:32 | 2014-04-21 13:01 | 89 | 11kV | 49306 | 554 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140288 1 fault operation Sensitive Earth Fault On going SEF fault, unable to find. Network switched abnormal to reduce customer interruptions. LBS 14605 now OPEN to narrow down fault area beyond intellirupter 50319.. | April | 2014 | 2014Q4 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Veg | 2014-04-21 | N | 89 | N | 2 | N | N | 1.1101 | 39.4971 | 36031.3705
[7 empty] | 16069 | 15639 | 1100926 | 2014-04-20 22:25 | 2014-04-21 15:15 | 1010 | 11kV | 280867 | 1900 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 140286 2 fault operations B & C Phase Overcurrent suspect ug cable between abs 42529 & sw 24257 Excluded OMS 1100926, 1100927, 1100928, 1100929, 1100931 | April | 2014 | 2014Q4 | 2014 | 217:33610 | 217:33610 | ZN00217/033610 | LAKE MACQUARIE | UG | Not Veg | 2014-04-20 | N | 147.8247 | N | 2 | N | N | 1.1101 | 39.4971 | 205249.3194
[7 empty] | 16438 | 19835 | 1101017 | 2014-04-22 00:50 | 2014-04-22 01:05 | 15 | 11kV | 5367 | 516 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Zn12650 West Gosford section of pa6L @RE44824 Wyoming was opened for safety Centre phase link @ USL40336 has burnt away and was arcing badly see 1101494,6 exclude 1101017,8,20,1 | April | 2014 | 2014Q4 | 2014 | ZN12650:PA6 | ZN12650:PA6 | ZN12650/000006 | CENTRAL COAST | OH | Not Veg | 2014-04-22 | N | 10.4012 | N | 4 | N | N | 1.1101 | 39.4971 | 3922.0453
[7 empty] | 14785 | 793 | 1101462 | 2014-04-22 16:00 | 2014-04-22 17:45 | 105 | 11kV | 315 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140293 Fix stranded conductor at sub pole FS-14302, Dapkos Winery sub 52624 | April | 2014 | 2014Q4 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-04-22 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 230.1927
[7 empty] | 15331 | 6636 | 1101391 | 2014-04-22 20:14 | 2014-04-22 21:10 | 55.55 | 11kV | 222.2 | 4 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 140294 Single phase DOLF : 16 Amp Possum. Volts = 242. Amps = 35. | April | 2014 | 2014Q4 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2014-04-22 | N | 55.55 | N | 4 | N | N | 1.1101 | 39.4971 | 162.3772
[7 empty] | 15144 | 4097 | 1101405 | 2014-04-22 23:47 | 2014-04-23 00:15 | 28 | 11kV | 112 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140295 A Phase DOLF : 10 Amp Aph DOLF had fallen open, not blown Excluded OMS 1101405 | April | 2014 | 2014Q4 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2014-04-22 | N | 28 | N | 4 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 15328 | 6614 | 1101406 | 2014-04-23 00:10 | 2014-04-23 01:39 | 89 | 11kV | 43076 | 484 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 140297 rusted & broken x-arm brace straps pole OS-30508 Section isolated for repair Excluded OMS 1101395 & 1101406 | April | 2014 | 2014Q4 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2014-04-23 | N | 89 | N | 3 | N | N | 1.1101 | 39.4971 | 31478.6703
[7 empty] | 15088 | 3564 | 1101582 | 2014-04-23 12:21 | 2014-04-23 13:55 | 94 | 11kV | 470 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140303 B phase DOLF : 40 Amp Fuse fatigued. Volts = 244. Excluded OMS # 1101582 | April | 2014 | 2014Q4 | 2014 | 214:8665 | 214:8665 | ZN00214/008665 | LAKE MACQUARIE | OH | Not Veg | 2014-04-23 | N | 94 | N | 3 | N | N | 1.1101 | 39.4971 | 343.4621
[7 empty] | 15237 | 5485 | 1101736 | 2014-04-23 23:47 | 2014-04-24 01:18 | 91 | 11kV | 177450 | 1950 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12650 West Gosford 11kv Pa20 "Central Moore" fdr tripped on Aphase IOC SIgnals: 11kv gtrip and EFI EFI's: S18737 S18121 S12794 S18498 S11142 Report of explosion around 126 Albany Gosford mains to patrol. Cause not ascertained See 1101736 Exclude 1101737 | April | 2014 | 2014Q4 | 2014 | ZN12650:PA20 | ZN12650:PA20 | ZN12650/000020 | CENTRAL COAST | OH | Veg | 2014-04-23 | N | 91 | N | 3 | N | N | 1.1101 | 39.4971 | 129675.2261
[7 empty] | 15095 | 3635 | 1101738 | 2014-04-24 01:51 | 2014-04-24 08:20 | 389 | 11kV | 142136 | 1854 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 140306 2 fault operations C phase Earth Fault; Overcurrent Possum on L/A on ELB 61913 Excluded OMS 1101738, 1101744 & 1101745 | April | 2014 | 2014Q4 | 2014 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Not Veg | 2014-04-24 | N | 76.6645 | N | 3 | N | N | 1.1101 | 39.4971 | 103868.7965
[7 empty] | 15591 | 9438 | 1101788 | 2014-04-24 08:21 | 2014-04-24 11:27 | 186 | 11kV | 57587 | 372 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140309 3 Fault Operations B Phase Earth Fault, Sensitive Earth Fault SCADA indicated SEF and Earth Fault operated. The District Operaters checked the control panel in the field where they found three reclose operations had occurred but the local display panel indicated only the Earth Fault had operated not the SEF. NO CAUSE FOUND FEEDER RESTORED IN SECTIONS. | April | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-04-24 | N | 154.8038 | N | 3 | N | N | 1.1101 | 39.4971 | 42082.8811
[7 empty] | 15130 | 3986 | 1101991 | 2014-04-24 14:43 | 2014-04-24 16:10 | 87 | 11kV | 95361 | 1173 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | At Zn965 Pennant Hills Panel 46 tripped on EF NO field EFI's operated Cause: Endbox No2 at S5370 failed explosively. See OMS 1102854 1102856 1102864 1102011 1101999 1101991 1101992 | April | 2014 | 2014Q4 | 2014 | ZN965:PA42 | ZN965:PA42 | ZN00965/000042 | HORNSBY | UG | Not Veg | 2014-04-24 | N | 81.2967 | N | 3 | N | N | 1.1101 | 39.4971 | 69687.0061
[7 empty] | 14970 | 2541 | 1102076 | 2014-04-25 06:02 | 2014-04-25 08:12 | 130 | 11kV | 234910 | 1807 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140358 2 Fault operations, overcurrent during electrical storm, no cause found | April | 2014 | 2014Q4 | 2014 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 130 | N | 53 | Y | Y | 1.1101 | 39.4971 | 171665.2993
[7 empty] | 14741 | 384 | 1102091 | 2014-04-25 06:52 | 2014-04-25 09:30 | 158 | 11kV | 150039 | 2428 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140389 1 fault operation Sw 80793 51N | April | 2014 | 2014Q4 | 2014 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Veg | 2014-04-25 | N | 61.7953 | N | 53 | Y | Y | 1.1101 | 39.4971 | 109644.0758
[7 empty] | 14865 | 1573 | 1102171 | 2014-04-25 08:56 | 2014-04-25 09:40 | 44 | 11kV | 81576 | 1854 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140359 2 Fault operations, overcurrent, electrical storm | April | 2014 | 2014Q4 | 2014 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 44 | N | 53 | Y | Y | 1.1101 | 39.4971 | 59613.3347
[7 empty] | 14690 | 1 | 1102077 | 2014-04-25 06:06 | 2014-04-25 10:00 | 234 | 11kV | 14534 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140367 2 fault operation A & C phase Overcurrent DOLFS Down on PT 73042 and PT 72064. Excluded OMS 1102077 | April | 2014 | 2014Q4 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 154.617 | N | 53 | Y | Y | 1.1101 | 39.4971 | 25914.2482
[7 empty] | 15392 | 7377 | 1102180 | 2014-04-25 09:36 | 2014-04-25 10:05 | 29 | 11kV | 19713 | 2115 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140390 Broken crossarm and blown lightning arrestors on subs 10600 & 61756 | April | 2014 | 2014Q4 | 2014 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 9.3206 | N | 53 | Y | Y | 1.1101 | 39.4971 | 14405.679
[7 empty] | 16499 | 20406 | 1102201 | 2014-04-25 08:30 | 2014-04-25 10:15 | 105 | 11kV | 155505 | 1481 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | Ex Zn14892 Charmhaven section of Pa19 "Lakeheaven Wyong Leagues" No relay or fuse operation ABNORMAL: USL44402 is closed. USL41128 is open Cause: 11kV UGOH bon burnt on S14816/SwA side. Hanging close to LV Mains. See 1103669 exclude 1102194,201 | April | 2014 | 2014Q4 | 2014 | ZN14892:PA19 | ZN14892:PA19 | ZN14892/000019 | CENTRAL COAST | OH | Not Veg | 2014-04-25 | N | 105 | N | 53 | Y | Y | 1.1101 | 39.4971 | 113638.4674
[7 empty] | 15346 | 6784 | 1102078 | 2014-04-25 06:05 | 2014-04-25 10:57 | 292 | 11kV | 33736 | 116 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Electrical Storm | N | LID 140498 appears as though premise is vacant, and sub could be spare 25/04/14 21:26 t50787: CHRIS POWER TO INVESTIGATE WHETHER SUB IS NEEDED. WILL REFER ON MONDAY | April | 2014 | 2014Q4 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2014-04-25 | N | 290.8276 | N | 53 | Y | Y | 1.1101 | 39.4971 | 24653.2738
[7 empty] | 16087 | 15889 | 1102166 | 2014-04-25 07:30 | 2014-04-25 11:00 | 210 | 11kV | 4620 | 22 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140402 Fuse: 20 Amp - line dolf operated electrical storm 953093 quoted, assuming this could be a cass job number | April | 2014 | 2014Q4 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-04-25 | N | 210 | N | 53 | Y | Y | 1.1101 | 39.4971 | 3376.1597
[7 empty] | 15628 | 10084 | 1102110 | 2014-04-25 07:25 | 2014-04-25 11:00 | 215 | 11kV | 215 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140403 C phase DOLF : 10 Amp Excluded OMS 1102110 | April | 2014 | 2014Q4 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 215 | N | 53 | Y | Y | 1.1101 | 39.4971 | 157.1157
[7 empty] | 15874 | 12887 | 1102149 | 2014-04-25 08:21 | 2014-04-25 11:01 | 160 | 11kV | 227208 | 1839 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Electrical Storm | N | Zn14892 Charmhaven P{a6 tripped, reclosed, tripped and locked out on: Timed A & B phase overcurrent, EFI FC, Reclose timer, Lock out PT14053 damaged by lightning, Pole BU1025 also has broken insulator. Tx failure See 1103208,12,4,5 Exclude 1102149,263,4 | April | 2014 | 2014Q4 | 2014 | ZN14892:PA6 | ZN14892:PA6 | ZN14892/000006 | CENTRAL COAST | OH | Not Veg | 2014-04-25 | N | 123.5498 | N | 53 | Y | Y | 1.1101 | 39.4971 | 166036.9049
[7 empty] | 16432 | 19633 | 1102231 | 2014-04-25 08:31 | 2014-04-25 11:30 | 179 | 11kV | 13116 | 122 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | Ex Zn14892 Charmhaven section of Pa14 @RE40149 Blue Haven tripped and reclosed on overcurent @PT12174 Emu Yurgua 11kv footpath phase 16K HDO blown EFI's:S18599 S18600 S14932 S14765 S14749 S14796 S18100 S18106 Heavy lightning storm in area See 1103211,2 Exclude 1102231 | April | 2014 | 2014Q4 | 2014 | ZN14892:PA14 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2014-04-25 | N | 107.5082 | N | 53 | Y | Y | 1.1101 | 39.4971 | 9584.7859
[7 empty] | 15860 | 12768 | 1102252 | 2014-04-25 10:10 | 2014-04-25 11:44 | 94 | 11kV | 5452 | 58 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140392 Fuse size: 20Amp Substation DOLF, electrical storm, lightning arrestor cut away Note: incorrect start time entered into LID, job began amended in OMS to reflect first call received from customer refer to 1102252 CC1: 22-"Refer to SOp" | April | 2014 | 2014Q4 | 2014 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 94 | N | 53 | Y | Y | 1.1101 | 39.4971 | 3984.1608
[7 empty] | 14850 | 1378 | 1102154 | 2014-04-25 08:41 | 2014-04-25 11:50 | 189 | 11kV | 5103 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140406 B phase DOLF : 20 Amp Excluded OMS 1102154, 1103122 & 1103203 | April | 2014 | 2014Q4 | 2014 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2014-04-25 | N | 189 | N | 53 | Y | Y | 1.1101 | 39.4971 | 3729.1219
[7 empty] | 15944 | 13642 | 1102075 | 2014-04-25 06:02 | 2014-04-25 11:56 | 354 | 11kV | 131246 | 830 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 140454 2 fault operations A phase Overcurrent A Phase OC 2600A. Note CB 74120 at muswellbrook also tripped during restoration. Pole split AK-61401 UGOH Faulty AK-61403 Excluded OMS 1102075,1102082,1102335 | April | 2014 | 2014Q4 | 2014 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | Unknown | Unknown | 2014-04-25 | N | 158.1277 | N | 53 | Y | Y | 1.1101 | 39.4971 | 95910.7057
[7 empty] | 14914 | 2010 | 1102295 | 2014-04-25 08:47 | 2014-04-25 12:40 | 233.2 | 11kV | 3031.6 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140405 3 phase DOLF : 20 Amp CC1: 22-"Refer to SOp" | April | 2014 | 2014Q4 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-04-25 | N | 233.2 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2215.4039
[7 empty] | 16036 | 15141 | 1102253 | 2014-04-25 10:12 | 2014-04-25 12:45 | 153 | 11kV | 1377 | 9 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140397 Fuse size: 20 AMP, substation DOLF Note: incorrect start time entered into LID, this OMS job amended to reflect first call received by customer as per 1102253 | April | 2014 | 2014Q4 | 2014 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 153 | N | 53 | Y | Y | 1.1101 | 39.4971 | 1006.271
[7 empty] | 15989 | 14493 | 1103488 | 2014-04-25 12:20 | 2014-04-25 12:56 | 36 | 11kV | 43488 | 1208 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Trip after restoration of faulty UGOH on Panel 812:19071 - refer to LID 140454 - OMS 1103478 | April | 2014 | 2014Q4 | 2014 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 36 | N | 53 | Y | Y | 1.1101 | 39.4971 | 31779.7477
[7 empty] | 15062 | 3332 | 1102185 | 2014-04-25 09:10 | 2014-04-25 13:10 | 240 | 11kV | 1440 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140399 A phase DOLF : 10 Amp replace blown dolf | April | 2014 | 2014Q4 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 240 | N | 53 | Y | Y | 1.1101 | 39.4971 | 1052.3095
[7 empty] | 15314 | 6548 | 1102243 | 2014-04-25 10:03 | 2014-04-25 13:15 | 192 | 11kV | 3648 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140422 C phase DOLF : 10 Amp Note: incorrect began time entered into LID, have amended this OMS job to reflect the first customer call received refer to 1102243 and 1102302 | April | 2014 | 2014Q4 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 192 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2665.8508
[7 empty] | 16258 | 17541 | 1102125 | 2014-04-25 07:46 | 2014-04-25 13:20 | 334 | 11kV | 49098 | 147 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 140396 Out to repair 33kV OHM | April | 2014 | 2014Q4 | 2014 | 232:11457 | 232:11457 | ZN00232/011457 | PORT STEPHENS | OH | Not Veg | 2014-04-25 | N | 334 | N | 53 | Y | Y | 1.1101 | 39.4971 | 35879.3703
[7 empty] | 14913 | 2009 | 1102086 | 2014-04-25 06:50 | 2014-04-25 13:33 | 403 | 11kV | 8866 | 22 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140410 Fuse: 16 Amp, line DOLF operated during electrical storm, also refer to 1102086 | April | 2014 | 2014Q4 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2014-04-25 | N | 403 | N | 53 | Y | Y | 1.1101 | 39.4971 | 6479.0113
[7 empty] | 15581 | 9248 | 1102224 | 2014-04-25 09:47 | 2014-04-25 14:05 | 258 | 11kV | 3870 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | Ex Zn14891 Wyong section of Pa21 PT11333 Bruce Dakara 1.6 Footpath HDO 16Amp 11kV Fuse operated during storm. See 1104571 exclude 1102224 | April | 2014 | 2014Q4 | 2014 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2014-04-25 | N | 258 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2828.0819
[7 empty] | 15573 | 9144 | 1104114 | 2014-04-25 08:41 | 2014-04-25 14:08 | 327 | 11kV | 654 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140429 B phase DOLF : 10 Amp | April | 2014 | 2014Q4 | 2014 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2014-04-25 | N | 327 | N | 53 | Y | Y | 1.1101 | 39.4971 | 477.9239
[7 empty] | 15651 | 10461 | 1102137 | 2014-04-25 08:14 | 2014-04-25 14:10 | 356 | 11kV | 2848 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140427 3 phase DOLF : 20 Amp Excluded OMS 1102137 | April | 2014 | 2014Q4 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-04-25 | N | 356 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2081.2344
[7 empty] | 16416 | 19412 | 1102352 | 2014-04-25 12:43 | 2014-04-25 14:15 | 92 | 11kV | 4140 | 45 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | Ex Zn14892 Charmhaven section of Pa14 PT12929 Drysdon Court Yuruba footpath HDO 11kV fuse 31.5 Amp operated Lightning Arrestor at PT failed during lightning storm See 1104585 excludee 1102352,73 | April | 2014 | 2014Q4 | 2014 | ZN14892:PA14 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2014-04-25 | N | 92 | N | 53 | Y | Y | 1.1101 | 39.4971 | 3025.3899
[7 empty] | 15092 | 3593 | 1102359 | 2014-04-25 09:00 | 2014-04-25 14:15 | 315 | 11kV | 1260 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140421 Fuse size: 16 Amp, substation DOLF operated during electrical storm also refer to 1102893 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-04-25 | N | 315 | N | 53 | Y | Y | 1.1101 | 39.4971 | 920.7708
[7 empty] | 15338 | 6723 | 1102216 | 2014-04-25 09:42 | 2014-04-25 14:24 | 282 | 11kV | 846 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140424 C phase DOLF : 10 Amp sub isolated to replace la Excluded OMS 1102216 | April | 2014 | 2014Q4 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-04-25 | N | 282 | N | 53 | Y | Y | 1.1101 | 39.4971 | 618.2318
[7 empty] | 15015 | 2936 | 1102164 | 2014-04-25 08:53 | 2014-04-25 14:25 | 331.55 | 11kV | 3647.05 | 11 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140432 Fuse Size: 10 Amp. line DOLF operated Electrical storm | April | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2014-04-25 | N | 331.55 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2665.1566
[7 empty] | 14811 | 1053 | 1102188 | 2014-04-25 09:15 | 2014-04-25 14:25 | 310 | 11kV | 930 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140417 C phase DOLF : 10 Amp | April | 2014 | 2014Q4 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-04-25 | N | 310 | N | 53 | Y | Y | 1.1101 | 39.4971 | 679.6166
[7 empty] | 16497 | 20399 | 1102376 | 2014-04-25 08:41 | 2014-04-25 14:50 | 369 | 11kV | 738 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140428 A phase DOLF : 10 Amp Excluded OMS 1102376 | April | 2014 | 2014Q4 | 2014 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2014-04-25 | N | 369 | N | 53 | Y | Y | 1.1101 | 39.4971 | 539.3086
[7 empty] | 15460 | 8045 | 1102136 | 2014-04-25 08:14 | 2014-04-25 15:25 | 431 | 11kV | 4741 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140425 3 phase DOLF : 20 Amp excluded OMS 1102136 Note: incorrect began time entered into LID, have amended this oms job to reflect the first customer call received refer to 1102136 and 1102407 | April | 2014 | 2014Q4 | 2014 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2014-04-25 | N | 431 | N | 53 | Y | Y | 1.1101 | 39.4971 | 3464.583
[7 empty] | 16091 | 15914 | 1102405 | 2014-04-25 14:37 | 2014-04-25 15:25 | 48 | 11kV | 144 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140418 Fuse size: 10 Amp substation DOLF operated, electrical storm Note: incorrect start time entered into LID, this OMS job amended as per first call in received from customer refer to 1102405, note also this customer was affected by previous outage 1102855 | April | 2014 | 2014Q4 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-04-25 | N | 48 | N | 53 | Y | Y | 1.1101 | 39.4971 | 105.231
[7 empty] | 15399 | 7428 | 1102366 | 2014-04-25 12:57 | 2014-04-25 16:00 | 183 | 11kV | 366 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140438 A phase DOLF Excluded OMS 1102366 | April | 2014 | 2014Q4 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 183 | N | 53 | Y | Y | 1.1101 | 39.4971 | 267.462
[7 empty] | 15526 | 8772 | 1102238 | 2014-04-25 12:53 | 2014-04-25 16:00 | 187 | 11kV | 374 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140415 Single phase DOLF : 10 Amp Note incorrect job began time entered into lid, have amended OMS record to reflect time first customer called as per OMS 1102238 | April | 2014 | 2014Q4 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-04-25 | N | 187 | N | 53 | Y | Y | 1.1101 | 39.4971 | 273.3082
[7 empty] | 16057 | 15464 | 1103132 | 2014-04-25 11:09 | 2014-04-25 16:15 | 306 | 11kV | 18972 | 62 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 140387 wire on xarm no further information supplied, no calls received | April | 2014 | 2014Q4 | 2014 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 306 | N | 53 | Y | Y | 1.1101 | 39.4971 | 13864.178
[7 empty] | 16177 | 16813 | 1103393 | 2014-04-25 16:26 | 2014-04-25 16:32 | 6 | 11kV | 492 | 82 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140434 sw tripped when dropout tried back at sub 50930 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-04-25 | N | 6 | N | 53 | Y | Y | 1.1101 | 39.4971 | 359.5391
[7 empty] | 14949 | 2259 | 1102431 | 2014-04-25 14:40 | 2014-04-25 16:45 | 125 | 11kV | 4000 | 32 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 140420 11kV section isolated to repair 33kV OHM on same pole also refer to OMS 1102431 | April | 2014 | 2014Q4 | 2014 | 214:8671 | 224:80326 | ZN00224/080326 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 125 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2923.082
[7 empty] | 16205 | 17111 | 1102267 | 2014-04-25 10:23 | 2014-04-25 17:00 | 397 | 11kV | 794 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | Excluded OMS 1102267 and 1102309 | April | 2014 | 2014Q4 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-04-25 | N | 397 | N | 53 | Y | Y | 1.1101 | 39.4971 | 580.2318
[7 empty] | 16188 | 16940 | 1102130 | 2014-04-25 08:04 | 2014-04-25 17:15 | 551 | 11kV | 1102 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | Blown TX 70652 Excluded job OMS 1102130 | April | 2014 | 2014Q4 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-04-25 | N | 551 | N | 53 | Y | Y | 1.1101 | 39.4971 | 805.3091
[7 empty] | 15211 | 4732 | 1102402 | 2014-04-25 14:32 | 2014-04-25 17:25 | 173 | 11kV | 3806 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 140431 A phase DOLF : 16 Amp Excluded OMS 1102402 & 1102421 | April | 2014 | 2014Q4 | 2014 | 801:74120 | 801:74120 | ZN00801/074120 | MUSWELLBROOK | UG | Not Veg | 2014-04-25 | N | 173 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2781.3125
[7 empty] | 15600 | 9564 | 1102189 | 2014-04-25 09:16 | 2014-04-25 17:40 | 504 | 11kV | 504 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140430 Single phase DOLF : 10 Amp sub isolated to replace both la's Excluded OMS 1102189 | April | 2014 | 2014Q4 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-04-25 | N | 504 | N | 53 | Y | Y | 1.1101 | 39.4971 | 368.3083
[7 empty] | 14912 | 2005 | 1102151 | 2014-04-25 08:37 | 2014-04-25 18:45 | 607.9167 | 11kV | 7295 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140433 A phase DOLF : 10 Amp | April | 2014 | 2014Q4 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 607.9167 | N | 53 | Y | Y | 1.1101 | 39.4971 | 5330.9708
[7 empty] | 15805 | 12154 | 1102396 | 2014-04-25 09:00 | 2014-04-25 19:15 | 615 | 11kV | 615 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 140437 single phase fuse: 3 Amp, substation dolf operated during electrical storm also refer to OMS 1102396 | April | 2014 | 2014Q4 | 2014 | 528:83014 | 528:83014 | ZN00528/083014 | MAITLAND | OH | Not Veg | 2014-04-25 | N | 615 | N | 53 | Y | Y | 1.1101 | 39.4971 | 449.4239
[7 empty] | 15862 | 12800 | 1102459 | 2014-04-25 09:00 | 2014-04-25 19:40 | 640 | 11kV | 1280 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140440 Sub Isolated to replace LA | April | 2014 | 2014Q4 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-04-25 | N | 640 | N | 53 | Y | Y | 1.1101 | 39.4971 | 935.3862
[7 empty] | 14973 | 2571 | 1102463 | 2014-04-25 19:56 | 2014-04-25 21:05 | 69 | 11kV | 207 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | as per related record 1102463 HV fuse replaced. No further information available, no LID report | April | 2014 | 2014Q4 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Veg | 2014-04-25 | N | 69 | N | 53 | Y | Y | 1.1101 | 39.4971 | 151.2695
[7 empty] | 15515 | 8612 | 1102442 | 2014-04-25 17:43 | 2014-04-25 21:15 | 212 | 11kV | 848 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140442 Single phase DOLF : 10 Amp | April | 2014 | 2014Q4 | 2014 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-04-25 | N | 212 | N | 53 | Y | Y | 1.1101 | 39.4971 | 619.6934
[7 empty] | 15781 | 11914 | 1102327 | 2014-04-25 12:07 | 2014-04-25 21:20 | 553 | 11kV | 553 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140443 A Phase DOLF : 2 Amp Note: incorrect start time entered into LID, have amended this OMS record to reflect the first customer call received | April | 2014 | 2014Q4 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-04-25 | N | 553 | N | 53 | Y | Y | 1.1101 | 39.4971 | 404.1161
[7 empty] | 15595 | 9502 | 1102392 | 2014-04-25 18:15 | 2014-04-25 22:45 | 270 | 11kV | 1350 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140445 Fuse: 10 Amp. substation dolf operated during lighting storm also refer to OMS 1102305 defective surge arrestors cut away and Tx restored Excluded OMS 1102392 | April | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2014-04-25 | N | 270 | N | 53 | Y | Y | 1.1101 | 39.4971 | 986.5402
[7 empty] | 15348 | 6793 | 1102468 | 2014-04-25 20:48 | 2014-04-26 00:01 | 193 | 11kV | 44004 | 228 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 140446 A phase tapping off at ABS 5550 Excluded oms 1102468 | April | 2014 | 2014Q4 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2014-04-25 | N | 193 | N | 53 | Y | Y | 1.1101 | 39.4971 | 32156.8253
[7 empty] | 16458 | 20031 | 1102138 | 2014-04-25 08:14 | 2014-04-26 10:00 | 1546 | 11kV | 6184 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 140448 A phase DOLF : 10 Amp Excluded OMS 1102138 cust have been contacted by erc advised will attend am sat | April | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-04-25 | N | 1546 | N | 53 | Y | Y | 1.1101 | 39.4971 | 4519.0848
[7 empty] | 15572 | 9142 | 1102559 | 2014-04-26 12:08 | 2014-04-26 13:02 | 54 | 11kV | 19780 | 1601 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | ZN.15011 Beacon Hill Panel 2 11kV OCB Tripped and relosed on:- Relays:- C phase Instantaneous OC, Lockout, Reclose, Timing, EFI. Field EFI:- S.16011. Signals:- 11kV Trip. Cause:- 11kV USL.24924 found open on footpath phase suspected HR connection. ME-1102817, RS-1102820. Withdrawn-1102559, 1102562, 1102563, 1102577, 1102565. | April | 2014 | 2014Q4 | 2014 | ZN15011:PA2 | ZN15011:PA2 | ZN15011/000002 | NORTHERN BEACHES | OH | Not Veg | 2014-04-26 | N | 12.3548 | N | 3 | N | N | 1.1101 | 39.4971 | 14454.6406
[7 empty] | 16219 | 17251 | 1102514 | 2014-04-26 09:46 | 2014-04-26 13:20 | 214.05 | 11kV | 991.05 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | LID 140453 C Phase - fuse size: 80 Amp Switch fuse - Oil filled Replaced LV fuse strip SUB 35714. LIGHNING STRIKE HAS CAUSE FLASHOVER DAMAGE IN LV END OF KIOSK. DISTRICT OPERATORS ON SITE HAVE MADE SAFE AND HAVE ORGANISED REPAIRS WITH SUBS ERC. CC1: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" | April | 2014 | 2014Q4 | 2014 | 224:80331 | 224:80331 | ZN00224/080331 | LAKE MACQUARIE | OH | Not Veg | 2014-04-26 | N | 123.8812 | N | 3 | N | N | 1.1101 | 39.4971 | 724.2301
[7 empty] | 16145 | 16435 | 1102538 | 2014-04-26 11:25 | 2014-04-26 13:20 | 115 | 11kV | 1150 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 140458 3 Phase - fuse size: 20 Amp Line DOLF | April | 2014 | 2014Q4 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-04-26 | N | 115 | N | 3 | N | N | 1.1101 | 39.4971 | 840.3861
[7 empty] | 15428 | 7771 | 1102416 | 2014-04-25 15:29 | 2014-04-26 15:45 | 1456 | 11kV | 3962 | 7 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 140435 Sub isolated to replace L/A's | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-04-25 | N | 566 | N | 53 | Y | Y | 1.1101 | 39.4971 | 2895.3127
[7 empty] | 14768 | 587 | 1102074 | 2014-04-25 05:58 | 2014-04-26 15:55 | 2037 | 11kV | 115482 | 643 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 140494 2 fault operations 3 phase Earth fault; Overcurrent UGOH at pole HS-43366 damaged by lightning. Excluded OMS 1102074 | April | 2014 | 2014Q4 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | Unknown | Unknown | 2014-04-25 | N | 179.5988 | N | 53 | Y | Y | 1.1101 | 39.4971 | 84390.8395
[7 empty] | 16065 | 15529 | 1102652 | 2014-04-27 09:55 | 2014-04-27 10:39 | 44 | 11kV | 92576 | 2104 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex ZN 10995 Riverwood - AB 30590 - Footpath Bond failed in service. Footpath side bond failed in service at AB 30590. On attempt to open AB 30590, the footpath flicker blade appears welded in. Left switch closed and opened Pnl 7 at ZN 10995. ABS requires repair. ME: 1102656. Withdrawn: 1102652, 3, 1102662, 4, 5, 1102672. CC1: 22-"Refer to SOp" | April | 2014 | 2014Q4 | 2014 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2014-04-27 | N | 44 | N | 3 | N | N | 1.1101 | 39.4971 | 67651.8103
[7 empty] | 15464 | 8063 | 1102671 | 2014-04-27 10:21 | 2014-04-27 11:35 | 74 | 11kV | 74 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 140464 A Phase - fuse size: 10 Amp Substation DOLF Suspect previous storm. Burnt DOLF carriers replaced. LIGHTNING STRIKE FLASHED OVER A PHASE DOLF CARRIER AT SUB 49605. REPLACED DOLF CARRIER AND 10A FUSE ELEMENT. SUPPLY RESTORED Withdrawn: OMS 1102671 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-04-27 | N | 74 | N | 3 | N | N | 1.1101 | 39.4971 | 54.077
[7 empty] | 15230 | 5262 | 1102740 | 2014-04-27 17:37 | 2014-04-27 18:50 | 73 | 11kV | 292 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140467 A Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1102740 | April | 2014 | 2014Q4 | 2014 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2014-04-27 | N | 73 | N | 3 | N | N | 1.1101 | 39.4971 | 213.385
[7 empty] | 15637 | 10169 | 1102828 | 2014-04-28 08:04 | 2014-04-28 10:00 | 116 | 11kV | 232 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140470 HV fuse replaced Single Phase, Substation DOLF Excluded OMS 1102828 | April | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-04-28 | N | 116 | N | 9 | N | N | 1.1101 | 39.4971 | 169.5388
[7 empty] | 15317 | 6563 | 1104606 | 2014-04-28 11:35 | 2014-04-28 12:35 | 60 | 11kV | 1620 | 27 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa2 Btw AB41934 to USL41935 interrupted for emergency repairs Large tree on wires on busy road | April | 2014 | 2014Q4 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2014-04-28 | N | 60 | N | 9 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 15569 | 9108 | 1102906 | 2014-04-28 09:16 | 2014-04-28 13:10 | 234 | 11kV | 468 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 140474 A phase DOLF : 21 Amp Probably from 25/04/2014 247V Excluded OMS No 1102906 | April | 2014 | 2014Q4 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-04-28 | N | 234 | N | 9 | N | N | 1.1101 | 39.4971 | 342.0006
[7 empty] | 16308 | 18097 | 1103354 | 2014-04-28 17:15 | 2014-04-28 18:00 | 45 | 11kV | 450 | 10 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 140478 A Phase - Fuse size: 20 Amp Line DOLF Blown arrestor at sub 53438 Excluded OMS 1103279 | April | 2014 | 2014Q4 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2014-04-28 | N | 45 | N | 9 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 15343 | 6747 | 1103149 | 2014-04-28 13:05 | 2014-04-28 18:25 | 320 | 11kV | 320 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 140479 A Phase - Fuse size: 10 Amp DORF - Blown Arrestor | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2014-04-28 | N | 320 | N | 9 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 14819 | 1107 | 1103310 | 2014-04-28 16:55 | 2014-04-28 18:55 | 120 | 11kV | 360 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 140480 A phase - Fuse size: 3 Amp DORF Excluded OMS 1103310 | April | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | UG | Not Veg | 2014-04-28 | N | 120 | N | 9 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 15101 | 3700 | 1103315 | 2014-04-28 17:05 | 2014-04-28 20:20 | 195 | 11kV | 195 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140481 A Phase - Fuse size: 10 Amp Substation DOLF 10AMP HV DOLF DOWN - RHS HV ARRESTOR DEFECTIVE Excluded OMS 1103315 | April | 2014 | 2014Q4 | 2014 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Not Veg | 2014-04-28 | N | 195 | N | 9 | N | N | 1.1101 | 39.4971 | 142.5002
[7 empty] | 15657 | 10531 | 1103155 | 2014-04-28 13:09 | 2014-04-28 23:10 | 601 | 11kV | 95545 | 1489 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140475 2 Fault Operations Earth Fault HV Reported Down Earth Wire down from 96Z High into Low Sub 5954 Excluded OMS 1103210 | April | 2014 | 2014Q4 | 2014 | 216:10727 | 216:10722 | ZN00216/010722 | LAKE MACQUARIE | OH | Not Veg | 2014-04-28 | N | 64.1672 | N | 9 | N | N | 1.1101 | 39.4971 | 69821.4679
[7 empty] | 15706 | 11037 | 1103355 | 2014-04-28 23:29 | 2014-04-29 01:03 | 94 | 11kV | 24681 | 264 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12620 Noraville section of Pa11 RE45050 Magenta Tripped and Locked out on Overcurrent and IOC Cause not ascertained See 1104607,8 Exclude 1103355 | April | 2014 | 2014Q4 | 2014 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Veg | 2014-04-28 | N | 93.4886 | N | 9 | N | N | 1.1101 | 39.4971 | 18036.1468
[7 empty] | 14972 | 2556 | 1103360 | 2014-04-29 06:31 | 2014-04-29 08:15 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140483 A Phase - fuse size: 10 Amp Substation DOLF Excluded OMS 1103360 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-04-29 | N | 104 | N | 4 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 16212 | 17146 | 1102082 | 2014-04-25 06:26 | 2014-04-29 10:30 | 6004 | 11kV | 25040.35 | 60 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Electrical Storm | N | LID 140457 3 fault operations Sensitive Earth Fault; Earth fault Defective sub 72905 | April | 2014 | 2014Q4 | 2014 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2014-04-25 | N | 417.3392 | N | 53 | Y | Y | 1.1101 | 39.4971 | 18298.7492
[7 empty] | 15870 | 12866 | 1103419 | 2014-04-29 09:13 | 2014-04-29 11:10 | 117 | 11kV | 234 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140491 A Phase - Fuse size: 10 Amp Substation DOLF Replaced blown HV fuse element on Dist. Sub 23174. Excluded OMS 1103419 | April | 2014 | 2014Q4 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2014-04-29 | N | 117 | N | 4 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 16073 | 15661 | 1103571 | 2014-04-29 12:18 | 2014-04-29 14:00 | 102 | 11kV | 102 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 140495 A Phase HV dropper hanging. No protection operation. Excluded OMS 1103571 | April | 2014 | 2014Q4 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-04-29 | N | 102 | N | 4 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 15357 | 6899 | 1103664 | 2014-04-29 13:34 | 2014-04-29 15:55 | 141 | 11kV | 141 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140499 Single Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1103664 | April | 2014 | 2014Q4 | 2014 | 512:48048 | 526:34633 | ZN00526/034633 | CESSNOCK | OH | Not Veg | 2014-04-29 | N | 141 | N | 4 | N | N | 1.1101 | 39.4971 | 103.0386
[7 empty] | 15977 | 14235 | 1103816 | 2014-04-30 01:30 | 2014-04-30 04:40 | 190 | 11kV | 3800 | 20 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140502 B Phase - fuse size: 16 Amp Substation DOLF Excluded OMS 1103816 and 1103817 | April | 2014 | 2014Q4 | 2014 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-04-30 | N | 190 | N | 1 | N | N | 1.1101 | 39.4971 | 2776.9279
[7 empty] | 15128 | 3976 | 1104237 | 2014-05-01 01:54 | 2014-05-01 04:05 | 131 | 11kV | 130683 | 1074 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn14892 Charmhaven Pa21 tripped on Earth Fault, EFI, Fault Check, Earth Fault Check Tx2B EFI operated at S14501 Suspected UG fault betwn S14501 S14576 S14461 S14557 See 1104813,5,6,7 Exclude 1104237 | May | 2014 | 2014Q4 | 2014 | ZN14892:PA21 | ZN14892:PA21 | ZN14892/000021 | CENTRAL COAST | UG | Not Veg | 2014-05-01 | N | 121.6788 | N | 2 | N | N | 1.1101 | 39.4971 | 95499.2819
[7 empty] | 15002 | 2883 | 1104270 | 2014-05-01 08:45 | 2014-05-01 09:52 | 67 | 11kV | 79663 | 1189 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S195 Pymble Panel 30 Tripped on Relays: Earth Fault and EFI Signals: Tx1 Group Earth and Zone Earth and 11kV trip See OMS 1104270 1105456 1105455 1104315 | May | 2014 | 2014Q4 | 2014 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | UG | Not Veg | 2014-05-01 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 58215.3707
[7 empty] | 14962 | 2427 | 1104880 | 2014-05-02 12:45 | 2014-05-02 16:08 | 203 | 11kV | 609 | 3 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 140537 isolation to repair xarm | May | 2014 | 2014Q4 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-05-02 | N | 203 | N | 3 | N | N | 1.1101 | 39.4971 | 445.0392
[7 empty] | 14748 | 450 | 1104997 | 2014-05-02 18:30 | 2014-05-02 20:00 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140538 3 phase DOLF : 10 Amp Excluded OMS 1104997 | May | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-05-02 | N | 90 | N | 3 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 15565 | 9084 | 1105015 | 2014-05-02 21:38 | 2014-05-02 23:47 | 129 | 11kV | 262240 | 2088 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ Zn2310 Punchbowl 11kv Panel 33 "Denman Tucker, Denman Cant' fdr tripped on: Relays - MICOM relay - earth fault, EFI fault Field EFI's: 4125, 3289, 5467, 6107, 5571, 36638, 1244, 4693, 4010 Signals: 11kv trip. Zn + Group earth Remarks: UG fault. 11kv feeder fault between S-4010 Bennaroon Knox (Sw/B) and S-4014 Barremma Road (SW-A) | May | 2014 | 2014Q4 | 2014 | ZN2310:PA33 | ZN2310:PA15 | ZN02310/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-05-02 | N | 125.5939 | N | 3 | N | N | 1.1101 | 39.4971 | 191637.2572
[7 empty] | 14735 | 339 | 1105078 | 2014-05-03 10:30 | 2014-05-03 13:21 | 171.4 | 11kV | 2231.4667 | 15 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 140540 BROKEN LIVE LINE LEAD. | May | 2014 | 2014Q4 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-05-03 | N | 148.7644 | N | 6 | N | N | 1.1101 | 39.4971 | 1630.69
[7 empty] | 16130 | 16268 | 1105069 | 2014-05-03 09:49 | 2014-05-03 13:35 | 226 | 11kV | 18906 | 318 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Zn12630 Peats Ridge Pa4 "Kulnura" tripped and locked out Relays: A phase timed overcurrent, EFI, and SEL trip Signals: 11kv trip 11kV mains brought down by tree outside 1618 Wisemans Ferry Rd See 1105964,5 Exclude 1105069,72,85 | May | 2014 | 2014Q4 | 2014 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2014-05-03 | N | 59.4528 | N | 6 | N | N | 1.1101 | 39.4971 | 13815.9472
[7 empty] | 16224 | 17321 | 1105091 | 2014-05-03 12:03 | 2014-05-03 17:00 | 297 | 11kV | 32666 | 440 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn14891 Wyong Section of Pa12 @CP48838 Yarramalong Maitland 1.2 tripped on: Relays: A & C phase overcurrent trip and lock out Cause: Wires Down See 1106000,2,3,4 Exclude 1105091,105 | May | 2014 | 2014Q4 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2014-05-03 | N | 74.2409 | N | 6 | N | N | 1.1101 | 39.4971 | 23871.3493
[7 empty] | 15819 | 12296 | 1105101 | 2014-05-03 12:45 | 2014-05-03 17:12 | 267 | 11kV | 1602 | 6 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 140541 3 phase DOLF : 20 Amp wire down between poles DN-20223 & DN-10226 | May | 2014 | 2014Q4 | 2014 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2014-05-03 | N | 267 | N | 6 | N | N | 1.1101 | 39.4971 | 1170.6943
[7 empty] | 15810 | 12228 | 1105161 | 2014-05-03 17:46 | 2014-05-03 22:20 | 274 | 11kV | 112733 | 1969 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 140543 2 fault operations 3 phase Overcurrent targets required from Tomaree CB 81539 no access due to asbestos. Fault detection at ELB 61643 ABC OC tree on 11kV OHM Sandy Point Rd x Pantowora Corlette Excluded OMS 1105161, 1105163, 1105164, 1105167, 1105168, 1105171 | May | 2014 | 2014Q4 | 2014 | 242:81539 | 242:81539 | ZN00242/081539 | PORT STEPHENS | OH | Veg | 2014-05-03 | N | 57.2539 | N | 6 | N | N | 1.1101 | 39.4971 | 82381.9513
[7 empty] | 15294 | 6355 | 1105210 | 2014-05-03 23:58 | 2014-05-04 01:35 | 97 | 11kV | 21534 | 222 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 140545 2 fault operations A & C phase Overcurrent Tree branch removed 10m before sub 26967. DOp's report burn mark on OHM please inspect in day light. | May | 2014 | 2014Q4 | 2014 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2014-05-03 | N | 97 | N | 6 | N | N | 1.1101 | 39.4971 | 15736.4121
[7 empty] | 15760 | 11689 | 1105262 | 2014-05-04 10:29 | 2014-05-04 12:09 | 100 | 11kV | 8600 | 86 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 140551 ABS 5183 Arcing Excluded OMS 1105262 | May | 2014 | 2014Q4 | 2014 | 235:2857 | 235:2857 | ZN00235/002857 | MAITLAND | OH | Not Veg | 2014-05-04 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 6284.6263
[7 empty] | 15426 | 7762 | 1105307 | 2014-05-04 15:36 | 2014-05-04 16:37 | 61 | 11kV | 88572 | 1452 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | 11kv Panel #24 labelled "S47649" from Zn35900 Potts Hill tripped on: Relays: Basler Relay 50TN (earth fault), 51BC (B phase O/C); EFI Signals: Field EFI's S47649 Remarks: Vehicle hit pole. Joseph st corner Weeroona St opposite Carnarvon Golf Club. 11KV mains twised together/broken cross arm. (Potts Hill Pnl24 is a recently developed feeder cut from Sefton. Hence the many OMS jobs to correctly identify each DC) | May | 2014 | 2014Q4 | 2014 | ZN3472:PA7 | ZN35900:PA24 | ZN35900/000024 | CUMBERLAND | OH | Not Veg | 2014-05-04 | N | 61 | N | 5 | N | N | 1.1101 | 39.4971 | 64725.8052
[7 empty] | 15274 | 6100 | 1105279 | 2014-05-04 12:20 | 2014-05-04 19:40 | 440 | 11kV | 94391 | 1294 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind | N | LID 140552 2 fault operations B phase Earth fault; Overcurrent 11kV UGOH TO SUB 24946 50TN OC & EF PROT 2 B PHASE | May | 2014 | 2014Q4 | 2014 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | Unknown | Unknown | 2014-05-04 | N | 72.9451 | N | 5 | N | N | 1.1101 | 39.4971 | 68978.1587
[7 empty] | 15306 | 6491 | 1105335 | 2014-05-04 17:18 | 2014-05-04 19:50 | 152 | 11kV | 760 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 140553 interrupt to repair live line lead Excluded OMS 1105335 & 1105342 | May | 2014 | 2014Q4 | 2014 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2014-05-04 | N | 152 | N | 5 | N | N | 1.1101 | 39.4971 | 555.3856
[7 empty] | 16476 | 20217 | 1105356 | 2014-05-04 18:25 | 2014-05-04 22:30 | 245 | 11kV | 490 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140554 DOLF : 10 Amp Replaced faulty lightning arrestors Excluded OMS 1105356 | May | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-05-04 | N | 245 | N | 5 | N | N | 1.1101 | 39.4971 | 358.0775
[7 empty] | 14851 | 1382 | 1105443 | 2014-05-05 08:53 | 2014-05-05 10:25 | 92 | 11kV | 6440 | 70 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT50265 Oceano Segura 11kv HDO 63Amp roadside fuse operated fuse failure See 1106023 exclude 1105443 | May | 2014 | 2014Q4 | 2014 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Not Veg | 2014-05-05 | N | 92 | N | 2 | N | N | 1.1101 | 39.4971 | 4706.1621
[7 empty] | 15997 | 14560 | 1105722 | 2014-05-05 15:32 | 2014-05-05 16:20 | 48 | 11kV | 33648 | 701 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9900 Menai - Pnl 6 - A & B phase timed OC, EFI, Field EFIs. Cockatoo flew into 11kV outside 39 David Rd, Barden Ridge. ME: 1105722. Withdrawn: 1105726, 29, 33, 40. | May | 2014 | 2014Q4 | 2014 | ZN9900:PA6 | ZN9900:PA6 | ZN09900/000006 | SUTHERLAND | OH | Not Veg | 2014-05-05 | N | 48 | N | 2 | N | N | 1.1101 | 39.4971 | 24588.966
[7 empty] | 16239 | 17470 | 1106341 | 2014-05-06 14:47 | 2014-05-06 14:58 | 11 | 11kV | 1287 | 117 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 140582 2 fault operations Earth fault Short interrruption did not find an OMS customer gernerated job yet. See SI 477. At step 13 reconnect Switching no 477 closed Sw 28223, staff saw a flash and heard the explosion and Sw 82576 opened on timed earth fault at Brandy Hill sub. Staff identifed the fault at UGOH pole IQ-93581 and isolated both sides at ABS 27588 and Sw 28223. | May | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82576 | ZN00508/082576 | PORT STEPHENS | Unknown | Unknown | 2014-05-06 | N | 11 | N | 5 | N | N | 1.1101 | 39.4971 | 940.5016
[7 empty] | 15254 | 5727 | 1106018 | 2014-05-06 12:54 | 2014-05-06 17:00 | 246 | 11kV | 1230 | 5 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140586 A phase DOLF : 10 Amp | May | 2014 | 2014Q4 | 2014 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-05-06 | N | 246 | N | 5 | N | N | 1.1101 | 39.4971 | 898.8477
[7 empty] | 15580 | 9246 | 1106194 | 2014-05-06 16:45 | 2014-05-06 17:20 | 35 | 11kV | 490 | 14 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 140587 Conductor found off pin at pole 90-60001 | May | 2014 | 2014Q4 | 2014 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2014-05-06 | N | 35 | N | 5 | N | N | 1.1101 | 39.4971 | 358.0775
[7 empty] | 16285 | 17858 | 1106065 | 2014-05-06 13:14 | 2014-05-06 19:50 | 396 | 11kV | 15543 | 122 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington - Pnl 15 tripped on: EFI, C Phase O/C. E/F Field EFIs: S5277 UG Cable fault - outside 44 Oxford St. Pitt lid blew off with an explosion, Wollarah Council has barricaded the area off. Lid is in Pieces down the hole. Between S5277 (Tee Tx3) to S2246 (Tee HVC #2) see 1106729 1106734 | May | 2014 | 2014Q4 | 2014 | ZN342:PA15 | ZN342:PA15 | ZN00342/000015 | WOOLLAHRA | UG | Not Veg | 2014-05-06 | N | 127.4016 | N | 5 | N | N | 1.1101 | 39.4971 | 11358.366
[7 empty] | 16048 | 15402 | 1106253 | 2014-05-06 22:55 | 2014-05-07 00:04 | 69 | 11kV | 3933 | 57 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140589 A phase DOLF : 40 Amp Excluded OMS 1106253 & 1106254 | May | 2014 | 2014Q4 | 2014 | 225:33679 | 270:83586 | ZN00270/083586 | LAKE MACQUARIE | OH | Veg | 2014-05-06 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 2874.1204
[7 empty] | 16126 | 16217 | 1106255 | 2014-05-07 01:41 | 2014-05-07 03:54 | 133 | 11kV | 257696 | 2078 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.180 Mosman Panel 41 11kV feeder tripped on:- Relays:- EF, EFI, FC. Signals:- 11kV trip, No.2 GE. EFI's:- S.8299, S.4071, S.3587, S.2242, S.6762. Cause:- 11kV UG Cable Fault located between S.6762 SW/B and S.4069 SW/B and S.1382 SW/B. ME-1106273. Withdrawn-1106255. | May | 2014 | 2014Q4 | 2014 | ZN180:PA41 | ZN180:PA41 | ZN00180/000041 | WILLOUGHBY | UG | Not Veg | 2014-05-07 | N | 124.0115 | N | 3 | N | N | 1.1101 | 39.4971 | 188316.6361
[7 empty] | 14926 | 2118 | 1106258 | 2014-05-07 05:11 | 2014-05-07 06:15 | 64 | 11kV | 74512 | 1262 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S3672 Maroubra Pnl.6 tripped on: A & B OC, EFi, EF, FC Field EFIs: S6971 S35462 S2308 UG Cable fault between S2308 (Sw B) and S2490 (Sw A) see 1106744 1106746 | May | 2014 | 2014Q4 | 2014 | ZN3672:PA6 | ZN3672:PA6 | ZN03672/000006 | BAYSIDE | UG | Not Veg | 2014-05-07 | N | 59.0428 | N | 3 | N | N | 1.1101 | 39.4971 | 54451.1719
[7 empty] | 15193 | 4527 | 1106294 | 2014-05-07 08:28 | 2014-05-07 09:14 | 46 | 11kV | 1426 | 31 | HV | Animal Bird | Animal | Lightning Arrestor | Unplanned | Unselected | N | LID 140594 A phase DOLF : 20 Amp Bird on L/A excluded OMS 1106294 | May | 2014 | 2014Q4 | 2014 | 801:74122 | 801:74122 | ZN00801/074122 | MUSWELLBROOK | OH | Not Veg | 2014-05-07 | N | 46 | N | 3 | N | N | 1.1101 | 39.4971 | 1042.0787
[7 empty] | 16187 | 16935 | 1106694 | 2014-05-08 01:52 | 2014-05-08 05:12 | 200 | 11kV | 2146 | 355 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | Unselected | N | At Recloser 428 Bayfield Rd Panel 4 tripped and reclosed Cause: Phantom Operator AB2421 Found Open With Lock bolt cutted away See OMS 1106727 110730 1106694 | May | 2014 | 2014Q4 | 2014 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2014-05-08 | N | 6.0451 | N | 5 | N | N | 1.1101 | 39.4971 | 1568.2335
[7 empty] | 16246 | 17508 | 1106804 | 2014-05-08 09:06 | 2014-05-08 09:15 | 9 | 11kV | 8262 | 918 | HV | Staff Operation | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | At S187 Panel 21 Tripped By TPE for DISC335277 and ITR sent to S214 S3416 Abnromal Switching: Yes SW/A Closed at S5945 Pa21 Opened For Trip Check ITR link at S187 Left in at S187 Crows Nest Pa21 was inadvertantly left closed which sent a trip positive to S214 abd S3416 See OMS 1106804 1108763 | May | 2014 | 2014Q4 | 2014 | ZN187:PA21 | ZN187:PA21 | ZN00187/000021 | NORTH SYDNEY | UG | Not Veg | 2014-05-08 | N | 9 | N | 5 | N | N | 1.1101 | 39.4971 | 6037.6259
[7 empty] | 16358 | 18649 | 1106854 | 2014-05-08 09:40 | 2014-05-08 10:09 | 29 | 11kV | 39846 | 1374 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | LID 140617 & 140618 DO error network abnormally switched. relates to report 140617 | May | 2014 | 2014Q4 | 2014 | 264:81238 | 264:81238 | ZN00264/081238 | PORT STEPHENS | Unknown | Not Veg | 2014-05-08 | N | 29 | N | 5 | N | N | 1.1101 | 39.4971 | 29118.2815
[7 empty] | 14874 | 1722 | 1107143 | 2014-05-08 16:28 | 2014-05-08 18:05 | 97 | 11kV | 194 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140627 B phase DOLF : 16 Amp Excluded OMS 1107143 | May | 2014 | 2014Q4 | 2014 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Veg | 2014-05-08 | N | 97 | N | 5 | N | N | 1.1101 | 39.4971 | 141.7695
[7 empty] | 15300 | 6435 | 1107157 | 2014-05-08 17:02 | 2014-05-08 19:26 | 144 | 11kV | 3207 | 39 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140628 2 fault operations A & C phase Overcurrent Fault detected by EB 63470. Possible fault might be irrigation sprinkler. Excluded OMS 1107157 & 1107159 | May | 2014 | 2014Q4 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-05-08 | N | 82.2308 | N | 5 | N | N | 1.1101 | 39.4971 | 2343.581
[7 empty] | 15405 | 7493 | 1107297 | 2014-05-09 09:55 | 2014-05-09 11:25 | 90 | 11kV | 7380 | 82 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 140637 Switching 42221 Replace broken x arm at sub 27706 Sebedya Excluded OMS 1107297 | May | 2014 | 2014Q4 | 2014 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2014-05-09 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 5393.0863
[7 empty] | 14981 | 2637 | 1107537 | 2014-05-09 23:21 | 2014-05-10 01:06 | 105 | 11kV | 210 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140646 Single Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1107537 | May | 2014 | 2014Q4 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-05-09 | N | 105 | N | 2 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 16085 | 15853 | 1107553 | 2014-05-10 07:56 | 2014-05-10 12:40 | 283.8333 | 11kV | 3689.8333 | 13 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140648 Crew found a burnt bird on the ground, it appears the bird caused the fault. No protection operated. Section isolated for safety and to allow repairs. 11kV mains had fallen on the ground between poles FR-84755 and FR-82104. Note Fdr did not trip on SEF, the operator reports the 11kV cable on the ground was backfed thought he TX and the other end of the broken cable was a few feet off the ground. | May | 2014 | 2014Q4 | 2014 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2014-05-10 | N | 283.8333 | N | 3 | N | N | 1.1101 | 39.4971 | 2696.4214
[7 empty] | 15330 | 6633 | 1107591 | 2014-05-10 11:33 | 2014-05-10 17:00 | 327 | 11kV | 55404 | 524 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | CP61392 Dartford Sefton Tripped Reclosed Tripped and locked out Cause: Large Tree fell ont mains outside 26 Brookes St see OMS 1111223 1111225 1111224 | May | 2014 | 2014Q4 | 2014 | ZN847:PA1 | ZN847:PA1 | ZN00847/000001 | HORNSBY | OH | Veg | 2014-05-10 | N | 105.7328 | N | 3 | N | N | 1.1101 | 39.4971 | 40487.6091
[7 empty] | 15677 | 10771 | 1107649 | 2014-05-10 19:32 | 2014-05-10 20:00 | 28 | 11kV | 1036 | 37 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 140651 B Phase - fuse size: 20 Amp Substation DOLF DOp found B ph DOLF carrier burnt up. Replaced and left OK. Excluded OMS 1107649 | May | 2014 | 2014Q4 | 2014 | 217:33612 | 221:11893 | ZN00221/011893 | LAKE MACQUARIE | OH | Not Veg | 2014-05-10 | N | 28 | N | 3 | N | N | 1.1101 | 39.4971 | 757.0782
[7 empty] | 14733 | 328 | 1107737 | 2014-05-11 16:00 | 2014-05-11 17:22 | 82 | 11kV | 246 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 140657 A Phase - fuse size: 10 Amp Substation DOLF Excluded OMS 1107737 | May | 2014 | 2014Q4 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-05-11 | N | 82 | N | 1 | N | N | 1.1101 | 39.4971 | 179.7695
[7 empty] | 16165 | 16631 | 1107790 | 2014-05-12 01:36 | 2014-05-12 02:27 | 51 | 11kV | 47226 | 926 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman, Panel 24 Fdr CB tripped on B phase timed OC, fault check, efi with signals:- 11kV trip, zone earth, #3 Tx group earth. Field efi's operated at S.1340, S.7807, CP.575, S.2743; Note:- efi did NOT operate at S.49773 defective | May | 2014 | 2014Q4 | 2014 | ZN180:PA24 | ZN180:PA24 | ZN00180/000024 | WILLOUGHBY | UG | Not Veg | 2014-05-12 | N | 51 | N | 2 | N | N | 1.1101 | 39.4971 | 34511.3679
[7 empty] | 16294 | 17938 | 1107839 | 2014-05-12 08:05 | 2014-05-12 09:30 | 85 | 11kV | 1530 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140666 C phase DOLF : 10 Amp Excluded OMS 1107839 | May | 2014 | 2014Q4 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-05-12 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 1118.0789
[7 empty] | 16326 | 18258 | 1108264 | 2014-05-13 08:26 | 2014-05-13 10:02 | 96 | 11kV | 113110 | 1203 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2568 St Peters - Pnl.6 tripped on: SPAJ relay Earth Fault, EFI, F/C Field EFis: S47663 and S6362 Abnormal: Sw B Closed @ S3272 - Sw A open @ S1939 UG Cable fault from S6362 (Sw D) to S6103 (Sw A) to S3272 (Sw B) see 1108755 1108756 1108757 | May | 2014 | 2014Q4 | 2014 | ZN2568:PA32 | ZN2568:PA32 | ZN02568/000032 | SYDNEY | UG | Not Veg | 2014-05-13 | N | 94.0233 | N | 3 | N | N | 1.1101 | 39.4971 | 82657.4518
[7 empty] | 15842 | 12611 | 1108226 | 2014-05-13 07:01 | 2014-05-13 15:25 | 504 | 11kV | 34351 | 370 | HV | Vegetation Blow/Fall In | Vegetation | Pole | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" RE61340 Goerge Bloodtree #2 tripped, reclosed, tripped and reclosed on; Relays: A&B overcurrent, lockout Signals: nil Vehicle hit pole, overhead to replace pole and replace low voltage. See 1109159,62,3,4 Exclude 1108226,38,9 | May | 2014 | 2014Q4 | 2014 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2014-05-13 | N | 92.8405 | N | 3 | N | N | 1.1101 | 39.4971 | 25102.6976
[7 empty] | 14796 | 912 | 1108552 | 2014-05-13 16:24 | 2014-05-13 23:35 | 431 | 11kV | 28998 | 72 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Unselected | N | At S6691 Pennant Trebor 400A fuse bloen on B phase of distributor 2 At PT1362 Weemala Trebor 400A fuse blown on A B and C phase of disribributor 1 and 2 Cause: Tree feel onto PT1362 Damaging Crossarm See OMS 1108599 1108564 1108554/557/553/549/552/564/ | May | 2014 | 2014Q4 | 2014 | ZN965:PA22 | ZN965:PA22 | ZN00965/000022 | HORNSBY | OH | Veg | 2014-05-13 | N | 402.75 | N | 3 | N | N | 1.1101 | 39.4971 | 21190.8831
[7 empty] | 16267 | 17626 | 1108614 | 2014-05-14 04:09 | 2014-05-14 05:46 | 97 | 11kV | 129301 | 1333 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | ZN 9700 Kirrawee - Pnl 24 - Trip/reclose/trip, A phase timed OC, B phase leakage, timing, lockout, EFI, Frame leakage, Field EFIs. Feeder patrolled by DOp and no cause found. ME: 1108614. Withdrawn: 1108615. | May | 2014 | 2014Q4 | 2014 | ZN9700:PA24 | ZN9700:PA24 | ZN09700/000024 | SUTHERLAND | OH | Veg | 2014-05-14 | N | 97 | N | 2 | N | N | 1.1101 | 39.4971 | 94489.3571
[7 empty] | 16280 | 17806 | 1109021 | 2014-05-14 22:51 | 2014-05-15 00:47 | 116 | 11kV | 99064 | 854 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 140694 1 fault operation B & C phase Earth Fault, Overcurrent Cable termination at Sw 41159 failed. Targets B-C-N. Relay currents A=87A, B= 6933A, C=5816A, E= 4521A | May | 2014 | 2014Q4 | 2014 | 523:33505 | 523:33505 | ZN00523/033505 | SINGLETON | UG | Not Veg | 2014-05-14 | N | 116 | N | 2 | N | N | 1.1101 | 39.4971 | 72393.0493
[7 empty] | 15288 | 6307 | 1109284 | 2014-05-15 13:16 | 2014-05-15 15:08 | 112 | 11kV | 11200 | 100 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140707 OMS REPORT NO 1109284.NO TARGETS SW 42062 FOUND OPEN .CLOSED OK PLEASE INVESTIGATE SW 42062 & SEE UNPLANNED OUTAGE REPORT 140705 (OMS job 1109500) | May | 2014 | 2014Q4 | 2014 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-05-15 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 8184.6297
[7 empty] | 16494 | 20370 | 1109294 | 2014-05-15 13:39 | 2014-05-15 16:15 | 156 | 11kV | 312 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140708 A Phase - fuse size: 16 Amp Substation DOLF A ph DOLF recently replaced 25/5/14 Excluded OMS 1109294 | May | 2014 | 2014Q4 | 2014 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-05-15 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 228.0004
[7 empty] | 15680 | 10782 | 1109095 | 2014-05-15 08:54 | 2014-05-15 19:00 | 606 | 11kV | 106712 | 1264 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 140709 2 fault operations C phase Earth fault; Overcurrent Raised tip truck pulled down OHM near pole IU-10129 | May | 2014 | 2014Q4 | 2014 | 213:33777 | 216:10728 | ZN00216/010728 | LAKE MACQUARIE | OH | Not Veg | 2014-05-15 | N | 84.4241 | N | 3 | N | N | 1.1101 | 39.4971 | 77981.9821
[7 empty] | 14943 | 2198 | 1109835 | 2014-05-16 18:13 | 2014-05-16 19:50 | 97 | 11kV | 97 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140720 A phase DOLF : 10 Amp excluded OMS 1109835 | May | 2014 | 2014Q4 | 2014 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2014-05-16 | N | 97 | N | 2 | N | N | 1.1101 | 39.4971 | 70.8847
[7 empty] | 16360 | 18657 | 1109854 | 2014-05-16 23:39 | 2014-05-17 04:49 | 310 | 11kV | 7440 | 24 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 140721 Car hit pole HQ-61513. Wire off pin, broken x-arm & tapping broken at sub 42757. Isolate to repair. Excluded OMS 1109855, 1109854 | May | 2014 | 2014Q4 | 2014 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2014-05-16 | N | 310 | N | 2 | N | N | 1.1101 | 39.4971 | 5436.9326
[7 empty] | 16180 | 16855 | 1110585 | 2014-05-17 11:50 | 2014-05-17 12:18 | 28 | 11kV | 28 | 1 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Ex Zn14143 Somersby Zn 11kv Pa5 "Kariong" fdr S18048 de-energised for safety to allow DOp access into sub. Fluctuating supply and loud noise coming from S18048. closing mechanice on tee off of 11kv No2 RMCB S18048. Circlip found dislodged, switch closed through untill replacmenet of RMCB to be programmed. IF tee off trip will not be able to close properly. will trip in event of fault. See 1110585,6 Exclude 1109883 | May | 2014 | 2014Q4 | 2014 | ZN14143:PA5 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | Unknown | Not Veg | 2014-05-17 | N | 28 | N | 2 | N | N | 1.1101 | 39.4971 | 20.4616
[7 empty] | 15339 | 6730 | 1109948 | 2014-05-17 14:47 | 2014-05-17 17:00 | 133 | 11kV | 55728 | 633 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 140724 2 fault operations A phase Overcurrent Sw 8088 Carrington sub A phase OC. Sw 90574 Wheat Silo sub A & B phase Dir O/C Faulty UGOH Pole JU-31040. Excluded OMS 1109948 | May | 2014 | 2014Q4 | 2014 | 203:8088 | 204:82703 | ZN00204/082703 | NEWCASTLE | Unknown | Unknown | 2014-05-17 | N | 88.0379 | N | 2 | N | N | 1.1101 | 39.4971 | 40724.3787
[7 empty] | 15626 | 10062 | 1110018 | 2014-05-18 10:56 | 2014-05-18 11:50 | 54.4333 | 11kV | 2014.0333 | 37 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 140730 Off duty linesman noticed Xarm swinging in the breeze at pole GP-43083 Stanhope Rd. Excluded OMS 1110018 | May | 2014 | 2014Q4 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-05-18 | N | 54.4333 | N | 1 | N | N | 1.1101 | 39.4971 | 1471.7962
[7 empty] | 16176 | 16778 | 1110707 | 2014-05-19 07:53 | 2014-05-19 08:43 | 50 | 11kV | 52178 | 1201 | HV | Overload | Utility Process Issue | Feeder/Distributor U/G | Unplanned | Unselected | N | Ex Zn12620 Noraville section of pa7 "Fravent fdr" @RE40185 tripped on overcurrent due to hot water load still on after loss of supply due to 33kv 743 fdr trip See 1110707,8 | May | 2014 | 2014Q4 | 2014 | ZN12620:PA7 | ZN12620:PA7 | ZN12620/000007 | CENTRAL COAST | UG | Not Veg | 2014-05-19 | N | 43.4455 | N | 4 | N | N | 1.1101 | 39.4971 | 38130.1434
[7 empty] | 15116 | 3877 | 1110488 | 2014-05-19 17:36 | 2014-05-19 18:48 | 71.7 | 11kV | 2007.6 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140734 A phase DOLF : 20 Amp field operator Steve Bartush | May | 2014 | 2014Q4 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2014-05-19 | N | 71.7 | N | 4 | N | N | 1.1101 | 39.4971 | 1467.0949
[7 empty] | 15297 | 6406 | 1110504 | 2014-05-19 18:51 | 2014-05-19 19:30 | 39 | 11kV | 48399 | 1241 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12580 Erina Pa1 "green point" fdr tripped, reclosed, tripped and locked out on: Relays: A+B phase timed overcurrent, Earth Fault, SEF, EFI, REC timer, lockout EFI's: S18318 S18217 S18864 Signals: 11kv trip Tree branch found on 11kv overhead near PT18632 Kemare Avoca See 1110504 exclude 1110510,8,9 | May | 2014 | 2014Q4 | 2014 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Veg | 2014-05-19 | N | 39 | N | 4 | N | N | 1.1101 | 39.4971 | 35368.5617
[7 empty] | 16462 | 20077 | 1110508 | 2014-05-19 18:58 | 2014-05-19 22:55 | 237.05 | 11kV | 6637.4 | 28 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140735 B phase DOLF : 20 Amp 2nd time tonight | May | 2014 | 2014Q4 | 2014 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2014-05-19 | N | 237.05 | N | 4 | N | N | 1.1101 | 39.4971 | 4850.4161
[7 empty] | 15784 | 11944 | 1110535 | 2014-05-20 02:36 | 2014-05-20 04:17 | 101 | 11kV | 98718 | 1851 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S195 Pymble Panel 9 tripped reclosed tripped and locked out on B phase Times OC, Lockout, Timing Relay, Fault Check and EFI Signals: 11kV trip Note: Faulty EFI - S5428 Did not operated Cause: 11kV UG cable cable fault from S5428 Edwards Rosedale to S47190 Minns ro S2542 See OMS 1111153/55/56 1110535 | May | 2014 | 2014Q4 | 2014 | ZN195:PA9 | ZN195:PA9 | ZN00195/000009 | KU-RING-GAI | UG | Not Veg | 2014-05-20 | N | 53.3323 | N | 3 | N | N | 1.1101 | 39.4971 | 72140.2027
[7 empty] | 15369 | 7023 | 1110632 | 2014-05-20 10:00 | 2014-05-20 10:04 | 4 | 11kV | 7016 | 1754 | HV | Staff Operation | Utility Process Issue | O/H Link | Unplanned | No Weather Impact | N | Recloser 62774 tripped on SEL. During the switching of D&R 337234; the sensitive earth fault relay was NOT made non auto at CP.62774. Opening of underslung links 22823 resulted in an out of balance resulting in SEL operation | May | 2014 | 2014Q4 | 2014 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2014-05-20 | N | 4 | N | 3 | N | N | 1.1101 | 39.4971 | 5127.0859
[7 empty] | 15486 | 8278 | 1110838 | 2014-05-20 16:30 | 2014-05-20 18:05 | 95 | 11kV | 1330 | 14 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 140748 No OMS number someone notified depot directly. No protection operated, section isolated for safety and to perform repairs ASAP. 11kV cross arm failed at pole DN-20308. | May | 2014 | 2014Q4 | 2014 | 523:33501 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2014-05-20 | N | 95 | N | 3 | N | N | 1.1101 | 39.4971 | 971.9248
[7 empty] | 14754 | 523 | 1111017 | 2014-05-21 07:14 | 2014-05-21 08:42 | 88 | 11kV | 45909 | 640 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.711 Blackwattle Bay 5kV Pnl.14 tripped on 14R: EFI, EF 14L: EFI Front line feeder fault panel 14 to S808 to S7538 to S1628 see 1111594 | May | 2014 | 2014Q4 | 2014 | ZN711:PA14 | ZN7481:PA12 | ZN07481/000012 | SYDNEY | UG | Not Veg | 2014-05-21 | N | 71.7328 | N | 4 | N | N | 1.1101 | 39.4971 | 33548.9431
[7 empty] | 16488 | 20328 | 1111401 | 2014-05-21 20:50 | 2014-05-21 21:40 | 50 | 11kV | 30050 | 601 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 140763 interruption due to blown out CT at Maize St Cap Bank 42344 | May | 2014 | 2014Q4 | 2014 | 503:48078 | 532:83293 | ZN00532/083293 | MAITLAND | OH | Not Veg | 2014-05-21 | N | 50 | N | 4 | N | N | 1.1101 | 39.4971 | 21959.6537
[7 empty] | 14951 | 2276 | 1111392 | 2014-05-21 19:47 | 2014-05-22 00:38 | 291.4333 | 11kV | 5537.2333 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140764 Wire on ground at sub 72798 Excluded OMS 1111396. | May | 2014 | 2014Q4 | 2014 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2014-05-21 | N | 291.4333 | N | 4 | N | N | 1.1101 | 39.4971 | 4046.4468
[7 empty] | 15418 | 7679 | 1111414 | 2014-05-22 05:18 | 2014-05-22 10:30 | 312 | 11kV | 12821 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of pa3 "Mangrove Mountain" RE45035 Mangrove Mountain 11kv fdr Tree on Lillicrapp Rd brought down mains See 1112802,3 Exclude 1111414 | May | 2014 | 2014Q4 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2014-05-22 | N | 194.2576 | N | 2 | N | N | 1.1101 | 39.4971 | 9369.2086
[7 empty] | 15822 | 12361 | 1111343 | 2014-05-21 16:33 | 2014-05-22 13:30 | 1257 | 11kV | 1257 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 140773 A phase DOLF : 5 Amp Burnt tapping at 11Kv links 40583 plus A phase dolf blown at sub 51542 | May | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-05-21 | N | 1257 | N | 4 | N | N | 1.1101 | 39.4971 | 918.5785
[7 empty] | 16033 | 15114 | 1111509 | 2014-05-22 09:09 | 2014-05-22 13:40 | 271 | 11kV | 45591 | 1237 | HV | Staff Operation | Utility Process Issue | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Zn12660 Woy Woy Pa14 tripped Signals: 11kv trip Relays: C phase overcurrent and Earth fault Whilst taking out D&R 336991 @ S14457 Woy Woy Nichols. DOp applied Earth (Tx was isolated) switch on Tx and brought out fdr. Incorrectly connected RMI. Staff error. See 1112811,2,3 Exclude 1111509,57,69 | May | 2014 | 2014Q4 | 2014 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | Unknown | Not Veg | 2014-05-22 | N | 36.8561 | N | 2 | N | N | 1.1101 | 39.4971 | 33316.5581
[7 empty] | 15698 | 10993 | 1111841 | 2014-05-23 03:01 | 2014-05-23 04:00 | 59 | 11kV | 1121 | 19 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | Ex Zn12570 Avoca secgtion of Pa26 @S1426 Peppers Kurrawyba No.2 tx tripped on Buchholz. Suspect transformer failure due to Buchholz trip See 1112821 exclude 1111841 | May | 2014 | 2014Q4 | 2014 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | UG | Not Veg | 2014-05-23 | N | 59 | N | 3 | N | N | 1.1101 | 39.4971 | 819.1937
[7 empty] | 15079 | 3479 | 1111952 | 2014-05-23 08:00 | 2014-05-23 11:10 | 190 | 11kV | 190 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 140780 A phase DOLF : 10 Amp excluded OMS 1111952 | May | 2014 | 2014Q4 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-05-23 | N | 190 | N | 3 | N | N | 1.1101 | 39.4971 | 138.8464
[7 empty] | 15502 | 8475 | 1111840 | 2014-05-23 02:50 | 2014-05-24 15:50 | 2220 | 11kV | 24710 | 164 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1290 Leightonfield the 11kv panel 13 "S.7858" CB tripped on: Earth Leakage, EFI Signals: Tx3 Group Earth, Zone Earth, 11kv trip Field EFIs down at S.7858 Remarks: UG fault. Section of 11kv UG feeder from S.7858 SwB to S.5236 SwA to S35281 SwA tee S.5671 | May | 2014 | 2014Q4 | 2014 | ZN1290:PA13 | ZN1290:PA13 | ZN01290/000013 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-05-23 | N | 150.6707 | N | 3 | N | N | 1.1101 | 39.4971 | 18057.3392
[7 empty] | 16225 | 17322 | 1112285 | 2014-05-24 22:32 | 2014-05-24 23:32 | 60 | 11kV | 93155 | 1611 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | ZN.15009 Manly Zone Panel 5 tripped on:- B & C phase OC EFI Earth Fault Fault Check Zone E Field EFI:- S.17029 Cause:- Bat found on OH near S.15965. Fault current caused second fault at UGOH near S.16427, footpath bond burnt off. ME-1112443, RS-1112444. Withdrawn-1112290, 1112285, 1112286, 1112288, 1112287. | May | 2014 | 2014Q4 | 2014 | ZN15009:PA5 | ZN15009:PA5 | ZN15009/000005 | NORTHERN BEACHES | OH | Not Veg | 2014-05-24 | N | 57.8243 | N | 2 | N | N | 1.1101 | 39.4971 | 68074.9264
[7 empty] | 15835 | 12484 | 1112276 | 2014-05-24 19:58 | 2014-05-25 01:00 | 302 | 11kV | 49528 | 164 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 140798 C phase Overcurrent B phase tapping off at pole hw-40005 affecting subs 5462 & 21550. Isolate to repair. Excluded OMS 1112270, 1112272, 1112275, 1112277, 1112281 & 1112282 | May | 2014 | 2014Q4 | 2014 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Not Veg | 2014-05-24 | N | 302 | N | 2 | N | N | 1.1101 | 39.4971 | 36193.6016
[7 empty] | 15847 | 12668 | 1112292 | 2014-05-25 00:28 | 2014-05-25 04:15 | 227 | 11kV | 454 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140799 A phase DOLF : 10 Amp Excluded OMS 1112292 | May | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-05-25 | N | 227 | N | 2 | N | N | 1.1101 | 39.4971 | 331.7698
[7 empty] | 15724 | 11327 | 1112398 | 2014-05-25 17:50 | 2014-05-25 20:10 | 140 | 11kV | 2520 | 18 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140801 A Phase DOLF : 10 Amp excluded OMS 1112398 & 1112399 | May | 2014 | 2014Q4 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-05-25 | N | 140 | N | 2 | N | N | 1.1101 | 39.4971 | 1841.5417
[7 empty] | 16264 | 17609 | 1112860 | 2014-05-26 20:25 | 2014-05-26 21:54 | 89 | 11kV | 106533 | 1197 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn15012 Killarney Pa4 "Forrestville West" tripped, reclosed, tripped & locked out: Relays: C phase Overcurrent and instant, EFI, Lockout, Timing, Fault CHeck. Tx2 Fault Check Signals: 11kv trip, Zone Earth EFI's Nil UGOH fault short circuit between USL22875, S16537 & S16795 See 1112860 exclude 1112862 | May | 2014 | 2014Q4 | 2014 | ZN15012:PA4 | ZN15012:PA4 | ZN15012/000004 | NORTHERN BEACHES | Unknown | Unknown | 2014-05-26 | N | 89 | N | 2 | N | N | 1.1101 | 39.4971 | 77851.1742
[7 empty] | 14843 | 1315 | 1112867 | 2014-05-26 21:08 | 2014-05-26 23:55 | 167 | 11kV | 501 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140811 A phase DOLF : 16 Amp excluded OMS 1112867 | May | 2014 | 2014Q4 | 2014 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-05-26 | N | 167 | N | 2 | N | N | 1.1101 | 39.4971 | 366.116
[7 empty] | 15347 | 6785 | 1112880 | 2014-05-27 07:40 | 2014-05-27 08:48 | 68 | 11kV | 5772 | 114 | HV | Animal Bird | Animal | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140812 2 fault operations A & C phase Earth fault; Overcurrent Dead bird found next to Hollydeen RAGCB 75262 pole. Targets: Sw 74180 Denman sub - Aph OC (Locked out) Sw 75262 Hollydeen RAGCB - Cph EF (Reclosed) Excluded OMS No. 1112880 | May | 2014 | 2014Q4 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2014-05-27 | N | 50.6316 | N | 2 | N | N | 1.1101 | 39.4971 | 4218.0074
[7 empty] | 15468 | 8121 | 1113174 | 2014-05-27 18:00 | 2014-05-27 20:49 | 169 | 11kV | 16731 | 99 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14144 Wamberal section of Pa10L @RE44607 Matcham North was opened Tree fallen on mains near PT 14895. Interrutped to remove trees Excluded OMS 1113174 | May | 2014 | 2014Q4 | 2014 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2014-05-27 | N | 169 | N | 2 | N | N | 1.1101 | 39.4971 | 12226.5213
[7 empty] | 16423 | 19484 | 1113667 | 2014-05-28 20:22 | 2014-05-29 12:10 | 948 | 11kV | 18418 | 45 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 140849 2 fault operations stay wire on 11kV at DP-30883. Excluded OMS 1113667 & 1113674 | May | 2014 | 2014Q4 | 2014 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Not Veg | 2014-05-28 | N | 409.2889 | N | 1 | N | N | 1.1101 | 39.4971 | 13459.3312
[7 empty] | 15800 | 12131 | 1113985 | 2014-05-29 15:02 | 2014-05-29 16:57 | 115 | 11kV | 99090 | 989 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10990 Arncliffe - Pnl 7 - Trip/reclose/trip, A phase Timed OC, IOC, lockout, timing, EFI. 11kV UGOH in section of feeder from ZN 10990 to LB 62006 to S 48227 went short circuit. Surge arrestor failed. ME: 1115589. Rest Step: 1115590. Withdrawn: 1113985, 93, 98. | May | 2014 | 2014Q4 | 2014 | ZN10990:PA7 | ZN10998:PA18 | ZN10998/000018 | BAYSIDE | Unknown | Unknown | 2014-05-29 | N | 100.1921 | N | 2 | N | N | 1.1101 | 39.4971 | 72412.0493
[7 empty] | 14716 | 167 | 1114060 | 2014-05-29 16:47 | 2014-05-29 20:57 | 250 | 11kV | 18128 | 73 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 140868 B phase HV TAPPING AT POLE GR-62010 BISHOPS BRIDGE. Excluded OMS 1114097 & 1114060 | May | 2014 | 2014Q4 | 2014 | 511:29877 | 511:29877 | ZN00511/029877 | CESSNOCK | OH | Not Veg | 2014-05-29 | N | 248.3288 | N | 2 | N | N | 1.1101 | 39.4971 | 13247.4077
[7 empty] | 15501 | 8471 | 1114125 | 2014-05-30 05:40 | 2014-05-30 08:10 | 150 | 11kV | 300 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | LID 140869 B phase DOLF : 16 Amp B ph L/A tracking in light rain. Excluded OMS 1114125. | May | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-05-30 | N | 150 | N | 2 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 15983 | 14316 | 1114305 | 2014-05-30 13:20 | 2014-05-30 17:20 | 240 | 11kV | 480 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140885 C phase DOLF : 10 Amp SUB 23174 - 10A C PHASE DOLF DOWN - DEFECTIVE C PHASE ARRESTOR CUT AWAY MADE SAFE - REFER TO DEPOT FOR ASSERTOR REPLACMENT - AP 69552 - 10A DOLF REPLACED - RESTORED AT 17:20 Note copied from OMS , appears no LID job ebtered on day due to computer shut down. | May | 2014 | 2014Q4 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2014-05-30 | N | 240 | N | 2 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 14809 | 1025 | 1114534 | 2014-05-31 18:44 | 2014-05-31 20:15 | 91 | 11kV | 3822 | 42 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pnl.16 tripped on Earth Fault and EFI. Field EFIs: S49323 50353 8139 50569 5211 5022 6127 5199 5455 UG cable fault between S5455 and S7576 (N/O) | May | 2014 | 2014Q4 | 2014 | ZN1788:PA16 | ZN35700:PA13 | ZN35700/000013 | RANDWICK | UG | Not Veg | 2014-05-31 | N | 91 | N | 1 | N | N | 1.1101 | 39.4971 | 2793.0049
[7 empty] | 16032 | 15109 | 1114630 | 2014-06-01 17:44 | 2014-06-01 22:45 | 301 | 11kV | 89614 | 1474 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap rd" fdr CP44936 Bentley rd tripped and locked out on overcurrent and SEF trip. Corner Sylvan Valley Close and alan st Niagara Park HV into LV See 1115237,9 Exclude 1114630,44 | June | 2014 | 2014Q4 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2014-06-01 | N | 60.7965 | N | 1 | N | N | 1.1101 | 39.4971 | 65487.268
[7 empty] | 15919 | 13323 | 1114979 | 2014-06-02 15:11 | 2014-06-02 18:15 | 184 | 11kV | 920 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140894 A & B Phases - Fuse size: 16 Amp Line DOLF Excluded OMS 1114979 | June | 2014 | 2014Q4 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-06-02 | N | 184 | N | 3 | N | N | 1.1101 | 39.4971 | 672.3089
[7 empty] | 16366 | 18711 | 1115067 | 2014-06-02 18:16 | 2014-06-03 00:15 | 359 | 11kV | 30621 | 837 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140895 sw 59193 opened to isolate sub 39359 repair burnt LV fuse 39361 excluded oms 1115059, 1115061 & 1115067 | June | 2014 | 2014Q4 | 2014 | 205:12206 | 205:12206 | ZN00205/012206 | NEWCASTLE | OH | Not Veg | 2014-06-02 | N | 36.5842 | N | 3 | N | N | 1.1101 | 39.4971 | 22376.9236
[7 empty] | 15408 | 7507 | 1115098 | 2014-06-02 22:17 | 2014-06-03 04:15 | 358 | 11kV | 27956 | 152 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Ex Zn12600 section of Pa2 "Chamberlan Taylor" fdr RE41020 tripped on overcurrent & Earth Fault ABNORMAL: CP44605 closed LB41933 Open & Defective Cause: Car hit Pole ridgeway near PT13773 High into LV See 1115252,3 Exclude 1115098 | June | 2014 | 2014Q4 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2014-06-02 | N | 183.9211 | N | 3 | N | N | 1.1101 | 39.4971 | 20429.4202
[7 empty] | 16097 | 15982 | 1117278 | 2014-06-03 14:18 | 2014-06-03 16:57 | 159 | 11kV | 535 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 140905 broken stay on 66/11kV pole BN-90356. CB 60112 - EF prot 1 - Aph-E 190A 21.6km prot 2 CB 66137 - A-C o/c & EF - fdr lockout ## | June | 2014 | 2014Q4 | 2014 |  |  |  | SINGLETON | OH | Not Veg | 2014-06-03 | N | 5.297 | N | 2 | N | N | 1.1101 | 39.4971 | 390.9622
[7 empty] | 16123 | 16176 | 1115482 | 2014-06-03 18:11 | 2014-06-03 22:25 | 254 | 11kV | 762 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 140907 Isolate to replace burnt out LVF carrier Sub isolated for clearance | June | 2014 | 2014Q4 | 2014 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-06-03 | N | 254 | N | 2 | N | N | 1.1101 | 39.4971 | 556.8471
[7 empty] | 15423 | 7704 | 1115851 | 2014-06-04 18:24 | 2014-06-04 19:49 | 85 | 11kV | 46665 | 724 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S4545 Meadowbank Panel 21 tripped. No Protection Relays Operated Cause; SEL RElay Indication malfunction Section of OH feeder on Pa21 now supplied from Pa17 to allow SEL to be auto See OMS 1117203 1117204 1115851 | June | 2014 | 2014Q4 | 2014 | ZN4545:PA21 | ZN4545:PA21 | ZN04545/000021 | RYDE | OH | Veg | 2014-06-04 | N | 64.4544 | N | 2 | N | N | 1.1101 | 39.4971 | 34101.4056
[7 empty] | 15648 | 10387 | 1115889 | 2014-06-05 06:23 | 2014-06-05 08:40 | 137 | 11kV | 274 | 2 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 140921 Single Phase - Fuse size: 10 Amp Substation DOLF Dead possum found at sub Excluded OMS 1115889 | June | 2014 | 2014Q4 | 2014 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-06-05 | N | 137 | N | 5 | N | N | 1.1101 | 39.4971 | 200.2311
[7 empty] | 15597 | 9538 | 1115876 | 2014-06-05 00:52 | 2014-06-05 10:09 | 557.3833 | 11kV | 20041.65 | 56 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 140930 A phase - Fuse size: 31 Amp Substation DOLF blown dolf at Halewood Cl sub could not be replaced due to old carrier. sub restored via LV//. Cause not ascertained CC1: 22-"Refer to SOp" | June | 2014 | 2014Q4 | 2014 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2014-06-05 | N | 357.8866 | N | 5 | N | N | 1.1101 | 39.4971 | 14645.8467
[7 empty] | 15823 | 12377 | 1115869 | 2014-06-04 22:44 | 2014-06-05 10:58 | 734 | 11kV | 7230 | 88 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn14144 Wamberal section of Pa10 RE44582 Erina tripped and locked out on overcurrent Not Accessible to Patrol at night Lineworker patrolled and removed branch from 11kv Overhead on clyde rd See 1117303,5 Exclude 1115869 | June | 2014 | 2014Q4 | 2014 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2014-06-04 | N | 82.1591 | N | 2 | N | N | 1.1101 | 39.4971 | 5283.4708
[7 empty] | 15194 | 4530 | 1115883 | 2014-06-05 05:41 | 2014-06-05 12:10 | 389 | 11kV | 778 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 140920 B phase DOLF : 10 Amp replaced faulty B phase Lightning Arrestor Excluded OMS 1115883 | June | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-06-05 | N | 389 | N | 5 | N | N | 1.1101 | 39.4971 | 568.5395
[7 empty] | 15592 | 9469 | 1116155 | 2014-06-05 13:32 | 2014-06-05 16:21 | 169 | 11kV | 298064 | 1904 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | Zn3672 Maroubra Pnl.44 tripped on Earth Fault & EFI Field EFIs: S8454 993 3255 2860 1587 UG cable danaged by contractor between S1587, S8225 and S5935 see 1116512 & 1116513 | June | 2014 | 2014Q4 | 2014 | ZN3672:PA44 | ZN3672:PA44 | ZN03672/000044 | RANDWICK | UG | Not Veg | 2014-06-05 | N | 156.5462 | N | 5 | N | N | 1.1101 | 39.4971 | 217816.3798
[7 empty] | 15721 | 11170 | 1116273 | 2014-06-05 17:13 | 2014-06-05 20:13 | 180 | 11kV | 5940 | 33 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of pa2 "Holgate" From LB44275 to LK41374, tee to PT18790 PT14866 PT13986 PT14479 was interrupted for emergency rpairs after car hit pole See 1117316 exclude 1116266,73,9 | June | 2014 | 2014Q4 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2014-06-05 | N | 180 | N | 5 | N | N | 1.1101 | 39.4971 | 4340.7768
[7 empty] | 15253 | 5723 | 1116331 | 2014-06-06 08:26 | 2014-06-06 09:05 | 38.7667 | 11kV | 271.3667 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Rain Light | N | LID 140936 B phase : 10 Amp Excluded OMS 1116331 CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | June | 2014 | 2014Q4 | 2014 | 243:80074 | 243:80074 | ZN00243/080074 | LAKE MACQUARIE | OH | Not Veg | 2014-06-06 | N | 38.7667 | N | 5 | N | N | 1.1101 | 39.4971 | 198.3068
[7 empty] | 15917 | 13317 | 1116627 | 2014-06-06 15:58 | 2014-06-06 16:55 | 57 | 11kV | 570 | 10 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | LID 140950 Isolation to repair OHM laying on crossarm at abs 74460 normally open point Excluded OMS 1116632 & 1116627 | June | 2014 | 2014Q4 | 2014 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-06-06 | N | 57 | N | 5 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 16401 | 19162 | 1117419 | 2014-06-06 15:58 | 2014-06-06 17:00 | 62 | 11kV | 310 | 5 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | LID 140951 B & C phase Broken tapping at abs 74460 laying on crossarm | June | 2014 | 2014Q4 | 2014 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2014-06-06 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 226.5389
[7 empty] | 15337 | 6710 | 1116670 | 2014-06-06 17:54 | 2014-06-06 18:33 | 39 | 11kV | 30342 | 778 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | Rain Heavy | N | Zn12570 Avoca section of 11kv fdr "Terrigal" Feeder tripped, reclosed, tripped and locked out Relays: IOC trip B and C phase (1.2.1 target 50 TBC) lockout The overhead construction at PT11089 Easter Lake Shore requires modification clearance between unlike phases of the main and droppper are insufficient allowing possible flashover untill rectified. See 1116670 Exclude 1116673,4 | June | 2014 | 2014Q4 | 2014 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Not Veg | 2014-06-06 | N | 39 | N | 5 | N | N | 1.1101 | 39.4971 | 22173.0387
[7 empty] | 15064 | 3337 | 1116664 | 2014-06-06 19:43 | 2014-06-06 20:55 | 72 | 11kV | 360 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 140952 A & B phase DOLF : 20 Amp | June | 2014 | 2014Q4 | 2014 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-06-06 | N | 72 | N | 5 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 15122 | 3899 | 1116814 | 2014-06-07 16:50 | 2014-06-07 19:25 | 155 | 11kV | 192534 | 1467 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 140954 2 fault operations C phase Overcurrent Targets 121 50T C O/C Excluded OMS 1116814 & 1116821 | June | 2014 | 2014Q4 | 2014 | 511:29880 | 511:29880 | ZN00511/029880 | MAITLAND | Unknown | Unknown | 2014-06-07 | N | 131.2434 | N | 1 | N | N | 1.1101 | 39.4971 | 140698.1684
[7 empty] | 16228 | 17359 | 1116930 | 2014-06-09 17:20 | 2014-06-09 18:20 | 60 | 11kV | 60 | 1 | HV | Vandalism | 3rd Party Impact | DC PT | Unplanned | Unselected | N | LID 140959 stolen earths. No prot operation. Isolated for safety as the earth was cut off at the TX tank. There are two other known subs with missing earths. Joe Lewis over ruled and said they can be fixed in normal hours tues, 10th june. | June | 2014 | 2014Q4 | 2014 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-06-09 | N | 60 | N | 3 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 15898 | 13160 | 1117137 | 2014-06-09 23:31 | 2014-06-10 00:56 | 85 | 11kV | 225911 | 2900 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.342 Paddington Pnl.26 tripepd on: B phase OC, EF, EFI Field EFIs: S3568 UG cable fault between S3568 (Sw B) to S48371 (Sw A) see 1117168 1117170 1117172 1117171 | June | 2014 | 2014Q4 | 2014 | ZN342:PA26 | ZN342:PA26 | ZN00342/000026 | SYDNEY | UG | Not Veg | 2014-06-09 | N | 77.9003 | N | 3 | N | N | 1.1101 | 39.4971 | 165089.0956
[7 empty] | 15419 | 7682 | 1117091 | 2014-06-09 17:51 | 2014-06-10 03:15 | 564 | 11kV | 66601 | 872 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 140961 1 fault operation A phase Overcurrent ugoh between Lk3628 and SS.29639 Allendale Aged Care damaged. Generators to be installed to restore all supply until repairs are made. | June | 2014 | 2014Q4 | 2014 | 524:33578 | 524:33578 | ZN00524/033578 | CESSNOCK | Unknown | Unknown | 2014-06-09 | N | 76.3773 | N | 3 | N | N | 1.1101 | 39.4971 | 48670.0464
[7 empty] | 16063 | 15507 | 1117708 | 2014-06-11 10:16 | 2014-06-11 10:55 | 39 | 11kV | 585 | 15 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 140982 B phase DOLF : 16 Amp Fuse fatigue. Volts = 251, 250, 252. Amps = 25,30,8. Excluded OMS 1117708 | June | 2014 | 2014Q4 | 2014 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2014-06-11 | N | 39 | N | 3 | N | N | 1.1101 | 39.4971 | 427.5007
[7 empty] | 16198 | 17061 | 1117731 | 2014-06-11 10:49 | 2014-06-11 11:30 | 41 | 11kV | 7338.8 | 179 | HV | Staff Other | Utility Process Issue | DC Not Transformer | Unplanned | Unselected | N | S 10358 Warialda Queen Vic - HV fuse (incorrect operation, not blown). RMI at S 10358 was incorrectly labelled not as per System Diagram, resulting in an outage when switching for planned work. DOp has restored supply and correctly labelled RMI with N/O now on Sw/B. ME: 1117735. ME GIS: 1117731. CC1: 22-"Refer to SOp" | June | 2014 | 2014Q4 | 2014 | ZN10999:PA29 | ZN10999:PA29 | ZN10999/000029 | BAYSIDE | UG | Not Veg | 2014-06-11 | N | 40.9989 | N | 3 | N | N | 1.1101 | 39.4971 | 5362.9786
[7 empty] | 15856 | 12750 | 1118067 | 2014-06-12 01:25 | 2014-06-12 05:00 | 215 | 11kV | 71813 | 797 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9900 Menai - Pnl 12 - Trip/reclose/trip, B phase Timed leakage, Timing, reclose, lockout, Earth Fault, Field EFIs. 11kV feeder fault between S 9049 and S 9168 tee S 9944. ME: 1118337. Rest Steps: 1118338, 9. Withdrawn: 1118067. | June | 2014 | 2014Q4 | 2014 | ZN9900:PA12 | ZN9900:PA12 | ZN09900/000012 | SUTHERLAND | UG | Not Veg | 2014-06-12 | N | 90.1041 | N | 2 | N | N | 1.1101 | 39.4971 | 52478.8223
[7 empty] | 15590 | 9415 | 1118063 | 2014-06-11 23:56 | 2014-06-12 07:25 | 449 | 11kV | 53843 | 542 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 140991 2 fault operations MVA at pole FT-23118. Broken xarms 11kV & 433V mains very low. Sw 48031 A & C Overcurrent and multitrip alarm. Also note alarms for 11kv cap banks 29632 and 29634 operated and had to be reset when Sw 48031 operated.. EMSO Brian Lindsay checked all services at sub 62724 in case energised HV conductors had touched LV conductors, no sign of damage was found . Excluded OMS 1118063 & 1118068 | June | 2014 | 2014Q4 | 2014 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-06-11 | N | 99.3413 | N | 3 | N | N | 1.1101 | 39.4971 | 39346.8763
[7 empty] | 15852 | 12712 | 1118484 | 2014-06-12 22:09 | 2014-06-12 23:02 | 53 | 11kV | 79818 | 1506 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 10 - Trip/reclose/trip, IOC, lockout timing, sealing contactor. Possum on HV UGOH in Kiora Rd near President Ave. ME: 1119531. ME GIS: 1118488, 9. Withdrawn: 1118484, 5, 6, 1118490. | June | 2014 | 2014Q4 | 2014 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | OH | Not Veg | 2014-06-12 | N | 53 | N | 2 | N | N | 1.1101 | 39.4971 | 58328.6402
[7 empty] | 16263 | 17588 | 1118549 | 2014-06-13 09:26 | 2014-06-13 11:15 | 109 | 11kV | 109 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141012 C phase DOLF : 15 Amp Blown Lv tapping and Blown DOLF both on C phase. Excluded OMS 1118549 | June | 2014 | 2014Q4 | 2014 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-06-13 | N | 109 | N | 1 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 14738 | 349 | 1118960 | 2014-06-14 10:55 | 2014-06-14 11:58 | 63 | 11kV | 6666 | 882 | HV | Staff Operation | Utility Process Issue | DC PT | Unplanned | Unselected | N | LID 141023 1 fault operation Trip & lock out during restoration of sub 7010. Flash over at DOLF's see LID 141022/ OMS 1119224 | June | 2014 | 2014Q4 | 2014 | 243:80081 | 243:80081 | ZN00243/080081 | LAKE MACQUARIE | OH | Not Veg | 2014-06-14 | N | 7.5578 | N | 2 | N | N | 1.1101 | 39.4971 | 4871.3162
[7 empty] | 16202 | 17084 | 1118978 | 2014-06-14 11:57 | 2014-06-14 13:15 | 78 | 11kV | 18696 | 387 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S167 Auburn Zn P20 the sation park etc fdr tripped on e/f, e/f check and efi Remarks: UG fault. S167 auburn Zn P20 to S2951 Station par tee S1338 addreley station to S35622 auburn aux no2 | June | 2014 | 2014Q4 | 2014 | ZN167:PA20 | ZN167:PA20 | ZN00167/000020 | PARRAMATTA | UG | Not Veg | 2014-06-14 | N | 48.3101 | N | 2 | N | N | 1.1101 | 39.4971 | 13662.4854
[7 empty] | 15985 | 14429 | 1119061 | 2014-06-15 23:40 | 2014-06-16 02:30 | 170 | 11kV | 9180 | 54 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141024 faulty dolf at sub sub left interconnected on LV Excluded OMS 1119061 & 1119065 | June | 2014 | 2014Q4 | 2014 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2014-06-15 | N | 170 | N | 1 | N | N | 1.1101 | 39.4971 | 6708.4732
[7 empty] | 15107 | 3817 | 1119215 | 2014-06-16 07:20 | 2014-06-16 11:12 | 232 | 11kV | 11600 | 50 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | LID 141037 interrupt to repair tapping at pole 5I-40110 Excluded OMS 1119215 | June | 2014 | 2014Q4 | 2014 | 810:74062 | 810:74062 | ZN00810/074062 | UPPER HUNTER | OH | Not Veg | 2014-06-16 | N | 232 | N | 2 | N | N | 1.1101 | 39.4971 | 8476.9379
[7 empty] | 15049 | 3216 | 1119726 | 2014-06-16 14:35 | 2014-06-16 15:27 | 52 | 11kV | 416 | 8 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 141038 Single Phase Pole EO-50168 broken crossarm | June | 2014 | 2014Q4 | 2014 | 513:48059 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-06-16 | N | 52 | N | 2 | N | N | 1.1101 | 39.4971 | 304.0005
[7 empty] | 16418 | 19415 | 1120079 | 2014-06-17 17:15 | 2014-06-17 18:49 | 93.8333 | 11kV | 197331.5 | 2103 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | PT 10518 Yurga Central - Dist 11 - A phase (400A). Tree branch on mains adjacent to PT. ME: 1120077. Withdrawn: 1120079. CC1: 22-"Refer to SOp" | June | 2014 | 2014Q4 | 2014 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Veg | 2014-06-17 | N | 93.8333 | N | 1 | N | N | 1.1101 | 39.4971 | 144204.0399
[7 empty] | 14810 | 1049 | 1120260 | 2014-06-18 01:59 | 2014-06-18 06:34 | 275 | 11kV | 5225 | 19 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141056 4 fault operations main down at pole 5H-40042 | June | 2014 | 2014Q4 | 2014 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2014-06-18 | N | 275 | N | 3 | N | N | 1.1101 | 39.4971 | 3818.2759
[7 empty] | 14897 | 1907 | 1120267 | 2014-06-18 07:00 | 2014-06-18 08:57 | 117 | 11kV | 1521 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141058 Single phase DOLF : 20 Amp excluded OMS 1120267 | June | 2014 | 2014Q4 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-06-18 | N | 117 | N | 3 | N | N | 1.1101 | 39.4971 | 1111.5019
[7 empty] | 15716 | 11118 | 1120547 | 2014-06-18 13:30 | 2014-06-18 17:30 | 240 | 11kV | 3120 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141067 Single phase DOLF : 20 Amp L/F blown earlier today also. Line patrolled - no obvious cause. | June | 2014 | 2014Q4 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-06-18 | N | 240 | N | 3 | N | N | 1.1101 | 39.4971 | 2280.004
[7 empty] | 15329 | 6615 | 1121076 | 2014-06-19 18:26 | 2014-06-19 18:34 | 8 | 11kV | 12684 | 1604 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Zn12580 Erina Pa12 & Pa16 tripped Pa12 - B&C phase IOC EFI Pa16 Band C Phase overload EFi ABNORMAL: AB44966 closed for DAROS 339986 P12 & P16 on SE&R Centre phase dropper hit footpath phase blade when DOp opened LB45145 See 1121372,4 Exclude 1121076,7,8 | June | 2014 | 2014Q4 | 2014 | ZN12580:PA16 | ZN12580:PA16 | ZN12580/000016 | CENTRAL COAST | OH | Not Veg | 2014-06-19 | N | 7.9077 | N | 3 | N | N | 1.1101 | 39.4971 | 9269.0931
[7 empty] | 15668 | 10668 | 1121351 | 2014-06-19 17:05 | 2014-06-19 20:15 | 190 | 11kV | 570 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa5 LK43586 interrupted for safety reasons to remove tree. Larege tree branch fell onto CCT conductors. | June | 2014 | 2014Q4 | 2014 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2014-06-19 | N | 190 | N | 3 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 14918 | 2060 | 1121119 | 2014-06-19 23:52 | 2014-06-20 09:49 | 597 | 11kV | 29649 | 56 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At ZN2400 Berowra ex Panel 11. Rec1238 Milsons Passage Has tripped Cause Not ascertained for outage See OMS 1125355 1125356 1121117 | June | 2014 | 2014Q4 | 2014 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2014-06-19 | N | 529.4464 | N | 3 | N | N | 1.1101 | 39.4971 | 21666.6147
[7 empty] | 15009 | 2904 | 1121149 | 2014-06-20 08:30 | 2014-06-20 10:10 | 100 | 11kV | 100 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141091 B phase DOLF : 10 Amp burnt DOLF Excluded OMS 1121177 & 1121149 | June | 2014 | 2014Q4 | 2014 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-06-20 | N | 100 | N | 1 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 15379 | 7184 | 1121573 | 2014-06-22 04:57 | 2014-06-22 07:00 | 123 | 11kV | 1106.6 | 9 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | At CP1835 Caravan Plassey 2 X HDOS Operated POssum on UGOH to S7611 Moran CCt Plassey See OMS 1125396 1121573 1121574 | June | 2014 | 2014Q4 | 2014 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2014-06-22 | N | 122.9556 | N | 1 | N | N | 1.1101 | 39.4971 | 808.6706
[7 empty] | 15536 | 8851 | 1121880 | 2014-06-23 12:28 | 2014-06-23 13:33 | 65 | 11kV | 1170 | 18 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S 10376 Turrella NCR - 2 HDOs. Possible transformer failure. ME: 1122144. Withdrawn: 1121880. | June | 2014 | 2014Q4 | 2014 | ZN10990:PA8 | ZN10998:PA10 | ZN10998/000010 | BAYSIDE | UG | Not Veg | 2014-06-23 | N | 65 | N | 2 | N | N | 1.1101 | 39.4971 | 855.0015
[7 empty] | 16352 | 18573 | 1121627 | 2014-06-23 10:25 | 2014-06-23 14:25 | 240 | 11kV | 960 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12600 Lisarow Ex Pa2 from LB45185 to AB44313 PT12703 Koorin Ridgeway Tree branch brought down CCT. Interrutped by DOp for mains to restring | June | 2014 | 2014Q4 | 2014 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2014-06-23 | N | 240 | N | 2 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 15001 | 2878 | 1122215 | 2014-06-24 10:10 | 2014-06-24 13:08 | 178 | 11kV | 38393 | 315 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 141118 2 fault operations A & B phase Overcurrent A & B o/c 704A Excluded oms 1122215 | June | 2014 | 2014Q4 | 2014 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2014-06-24 | N | 121.8825 | N | 19 | N | N | 1.1101 | 39.4971 | 28056.472
[7 empty] | 15588 | 9399 | 1122349 | 2014-06-24 12:28 | 2014-06-24 13:14 | 46 | 11kV | 14766 | 321 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141125 1 Fault Operations Overcurrent Branch on OHM at P:DQ-70101 | June | 2014 | 2014Q4 | 2014 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2014-06-24 | N | 46 | N | 19 | N | N | 1.1101 | 39.4971 | 10790.5573
[7 empty] | 14915 | 2022 | 1122245 | 2014-06-24 12:17 | 2014-06-24 13:40 | 83 | 11kV | 332 | 4 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Wind | N | LID 141130 LLC failed | June | 2014 | 2014Q4 | 2014 | 512:48046 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2014-06-24 | N | 83 | N | 19 | N | N | 1.1101 | 39.4971 | 242.6158
[7 empty] | 16040 | 15298 | 1122344 | 2014-06-24 12:25 | 2014-06-24 13:48 | 83 | 11kV | 138527 | 1669 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141129 2 Fault Operations A & B Phases Overcurrent Tree fell through 11kV in avery Lane Cliftleigh | June | 2014 | 2014Q4 | 2014 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2014-06-24 | N | 83 | N | 19 | N | N | 1.1101 | 39.4971 | 101231.4457
[7 empty] | 14841 | 1307 | 1122214 | 2014-06-24 10:08 | 2014-06-24 14:20 | 252 | 11kV | 103194 | 1327 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind | N | LID 141117 2 fault operations Earth fault Wire off pin at sub 896. High into low. Excluded oms 122214. | June | 2014 | 2014Q4 | 2014 | 235:2123 | 235:2123 | ZN00235/002123 | NEWCASTLE | OH | Not Veg | 2014-06-24 | N | 77.7649 | N | 19 | N | N | 1.1101 | 39.4971 | 75411.1315
[7 empty] | 16309 | 18109 | 1122429 | 2014-06-24 13:21 | 2014-06-24 14:30 | 69 | 11kV | 4671 | 183 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 141132 & 141133 2 Fault Operations B & C Phases Pole Mounted RAGCB, Overcurrent Mains blowing against tree at pole FP-50470 Excluded OMS 1123824 | June | 2014 | 2014Q4 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-06-24 | N | 25.5246 | N | 19 | N | N | 1.1101 | 39.4971 | 3413.429
[7 empty] | 14708 | 107 | 1122326 | 2014-06-24 12:08 | 2014-06-24 15:15 | 187 | 11kV | 73390 | 985 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | LID 141155 fdr opened to make repairs at pole JU-10911 Excluded OMS 1122662 | June | 2014 | 2014Q4 | 2014 | 210:8681 | 210:83473 | ZN00210/083473 | NEWCASTLE | OH | Not Veg | 2014-06-24 | N | 74.5076 | N | 19 | N | N | 1.1101 | 39.4971 | 53631.2474
[7 empty] | 14762 | 555 | 1122482 | 2014-06-24 14:25 | 2014-06-24 15:38 | 73 | 11kV | 22310 | 314 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | At S2400 Berowra Panel 23 Tripped on A and C phase O/C Cause: Bond Burnt off adjacent to S4402 See OMS 1123003 1123008 1222482 | June | 2014 | 2014Q4 | 2014 | ZN2400:PA23 | ZN2400:PA23 | ZN02400/000023 | HORNSBY | OH | Not Veg | 2014-06-24 | N | 71.051 | N | 19 | N | N | 1.1101 | 39.4971 | 16303.49
[7 empty] | 16140 | 16408 | 1122587 | 2014-06-24 15:45 | 2014-06-24 16:20 | 34.7167 | 11kV | 208.3 | 6 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141134 C Phase Tree in mains at pole FP-50470. Proble cause of reports 141132 & 141133. Mains damaged/stranding and require urgent repair. | June | 2014 | 2014Q4 | 2014 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-06-24 | N | 34.7167 | N | 19 | N | N | 1.1101 | 39.4971 | 152.2195
[7 empty] | 15205 | 4677 | 1122470 | 2014-06-24 14:09 | 2014-06-24 16:33 | 143.55 | 11kV | 10621.0333 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | No blue outage form provided, All details based on customer comments See OMS 1122504 1122470 | June | 2014 | 2014Q4 | 2014 | ZN129:PA8 | ZN129:PA38 | ZN00129/000038 | HUNTERS HILL | OH | Veg | 2014-06-24 | N | 108.3779 | N | 19 | N | N | 1.1101 | 39.4971 | 7761.5379
[7 empty] | 14984 | 2672 | 1122670 | 2014-06-24 17:00 | 2014-06-24 18:07 | 67 | 11kV | 75015 | 1221 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | ZN 9118 Cronulla - Pnl 11 - A & B phase IOC and OC. Weather related outage. AB 35838 open and defective. ME: 1122869. Rest Step: 1122870. Withdrawn: 1122670. | June | 2014 | 2014Q4 | 2014 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2014-06-24 | N | 61.4373 | N | 19 | N | N | 1.1101 | 39.4971 | 54818.7494
[7 empty] | 16005 | 14654 | 1122406 | 2014-06-24 13:20 | 2014-06-24 18:10 | 290 | 11kV | 10213 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn148491 Wyong Pa12 "Yarramalong" RE45015 Bursh Creek tripped and locked out on SEL & Lockout Tree has brought down 11kv OH Mains tee off to PT14656 Brush Creek Koopman See 1123372,4,5 Exclude 1122406 | June | 2014 | 2014Q4 | 2014 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2014-06-24 | N | 182.375 | N | 19 | N | N | 1.1101 | 39.4971 | 7463.3592
[7 empty] | 15926 | 13398 | 1122227 | 2014-06-24 10:16 | 2014-06-24 18:20 | 484 | 11kV | 21259 | 250 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Wind | N | Ex Zn12630 Peats Ridge Pa3 "Mangrove Mtn" fdr RE45035 Mangrove Mtn, tripped & reclosed Relays: OC, IOC RE46992 Goolara Holy Cross tripped & locked out Relays: OC, IOC, L/O Car hit pole beyong Re45035 btwn LK40779 to AB44642. PT14627 to remain isolated until repairs are complete. Possible grading issue btwn RE45035 & RE46992. reported to T/PE See 1123226,9,30 Exclude 1122227,39,41,391 | June | 2014 | 2014Q4 | 2014 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-06-24 | N | 85.036 | N | 19 | N | N | 1.1101 | 39.4971 | 15535.4502
[7 empty] | 16451 | 19939 | 1122568 | 2014-06-24 16:20 | 2014-06-24 18:20 | 120 | 11kV | 360 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 141142 isolated for repairs to clashed 11kV OHM Excluded oms 1122586 | June | 2014 | 2014Q4 | 2014 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2014-06-24 | N | 120 | N | 19 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 14878 | 1752 | 1122401 | 2014-06-24 13:11 | 2014-06-24 20:20 | 429 | 11kV | 186368 | 552 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 141149 Mains down near sub 50768 Excluded OMS 1122401 | June | 2014 | 2014Q4 | 2014 | 510:48164 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-06-24 | N | 337.6232 | N | 19 | N | N | 1.1101 | 39.4971 | 136192.2375
[7 empty] | 15747 | 11616 | 1122428 | 2014-06-24 17:00 | 2014-06-24 22:00 | 300 | 11kV | 1456 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 141144 HV Dropper Replace Transformer | June | 2014 | 2014Q4 | 2014 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Not Veg | 2014-06-24 | N | 41.6 | N | 19 | N | N | 1.1101 | 39.4971 | 1064.0019
[7 empty] | 16431 | 19611 | 1122781 | 2014-06-24 20:30 | 2014-06-24 23:30 | 180 | 11kV | 39090 | 395 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141151 2 Fault Operations Overcurrent, Earth Fault Tree removed from OHM at pole MW-90023 Excluded OMS 1122781; 1123631 | June | 2014 | 2014Q4 | 2014 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2014-06-24 | N | 98.962 | N | 19 | N | N | 1.1101 | 39.4971 | 28565.819
[7 empty] | 15547 | 8908 | 1122799 | 2014-06-24 22:03 | 2014-06-25 01:20 | 197 | 11kV | 142295 | 769 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141153 3 fault operations Tree onmains resulting in mains down Possible high into low Excluded jobs OMS 1122799 & 1122808 | June | 2014 | 2014Q4 | 2014 | 229:34983 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2014-06-24 | N | 185.039 | N | 19 | N | N | 1.1101 | 39.4971 | 103984.989
[7 empty] | 15183 | 4423 | 1122804 | 2014-06-25 01:10 | 2014-06-25 03:00 | 110 | 11kV | 2090 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 141157 1 fault operation Reclose still off from previous emergency switching see OMS 1124042 | June | 2014 | 2014Q4 | 2014 | 229:34983 | 233:82819 | ZN00233/082819 | PORT STEPHENS | OH | Veg | 2014-06-25 | N | 110 | N | 10 | N | N | 1.1101 | 39.4971 | 1527.3104
[7 empty] | 15708 | 11044 | 1122835 | 2014-06-25 07:12 | 2014-06-25 08:16 | 64 | 11kV | 106573 | 1758 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 141159 1 Fault Operations Sensitive Earth Fault Burnt out contact at ABS 40326 Excluded OMS 1122835; 1122844; 1123776; 1123777; 1123778 | June | 2014 | 2014Q4 | 2014 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Not Veg | 2014-06-25 | N | 60.6217 | N | 10 | N | N | 1.1101 | 39.4971 | 77880.405
[7 empty] | 15799 | 12120 | 1122879 | 2014-06-25 08:41 | 2014-06-25 11:10 | 149 | 11kV | 149 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Wind | N | LID 141167 C phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1122879 | June | 2014 | 2014Q4 | 2014 | 265:81649 | 265:81649 | ZN00265/081649 | PORT STEPHENS | OH | Not Veg | 2014-06-25 | N | 149 | N | 10 | N | N | 1.1101 | 39.4971 | 108.8848
[7 empty] | 15177 | 4403 | 1122917 | 2014-06-25 10:15 | 2014-06-25 12:35 | 139.9 | 11kV | 78048.6333 | 1222 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | ZN 9118 Cronulla - Pnl 11 - A & C phase IOC. DOp has patrolled feeder and found nothing. Tree requires pruning at PT 9385. ME: 1123440. Rest Step: 1123575. ME GIS: 1122989. Withdrawn: 1122917, 1123004, 6, 1123091. | June | 2014 | 2014Q4 | 2014 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Veg | 2014-06-25 | N | 63.8696 | N | 10 | N | N | 1.1101 | 39.4971 | 57035.6392
[7 empty] | 15006 | 2896 | 1122849 | 2014-06-25 07:54 | 2014-06-25 12:35 | 281 | 11kV | 3091 | 11 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Wind | N | LID 141162 11kV C phase dropper to DOLF broken away Excluded OMS 1122849 | June | 2014 | 2014Q4 | 2014 | 238:34150 | 238:34150 | ZN00238/034150 | NEWCASTLE | OH | Not Veg | 2014-06-25 | N | 281 | N | 10 | N | N | 1.1101 | 39.4971 | 2258.8116
[7 empty] | 16223 | 17313 | 1127766 | 2014-06-25 12:55 | 2014-06-25 13:05 | 10 | 11kV | 1210 | 121 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 paddington Pnl.15 tripped on Overcurrent and Earth Fault UG cable failed on restoration - D/R #3398551 DOp proved feeder from S5277 OTC Gordon St - failed on energisation Excluded OMS 1123531 | June | 2014 | 2014Q4 | 2014 | ZN342:PA15 | ZN342:PA15 | ZN00342/000015 | WOOLLAHRA | UG | Not Veg | 2014-06-25 | N | 10 | N | 10 | N | N | 1.1101 | 39.4971 | 884.2323
[7 empty] | 15071 | 3424 | 1122720 | 2014-06-24 18:47 | 2014-06-25 14:10 | 1163 | 11kV | 12179 | 43 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 141152 3 phase DOLF : 16 Amp Mains down near sub 2801 Excluded OMS 1122720 | June | 2014 | 2014Q4 | 2014 | 264:81240 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-06-24 | N | 283.2326 | N | 19 | N | N | 1.1101 | 39.4971 | 8900.054
[7 empty] | 16373 | 18764 | 1123545 | 2014-06-25 10:57 | 2014-06-25 15:20 | 263 | 11kV | 198579 | 2103 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | ZN 10995 Riverwood - Pnl 7 - Trip/reclose/trip, B phase EF, C phase OC, EFI, Lockout. 11kV feeder from AB 31272 to LB 30650 tee PT 10509 isolated and earthed. Wires down. PT 10509 had an extended outage as the LV// would not hold. Remained isolated until HV repairs were finished. ME: 1123542. Rest Steps: 1123544, 5. Withdrawn: 1123048. | June | 2014 | 2014Q4 | 2014 | ZN10995:PA7 | ZN10995:PA7 | ZN10995/000007 | GEORGES RIVER | OH | Not Veg | 2014-06-25 | N | 94.4265 | N | 10 | N | N | 1.1101 | 39.4971 | 145115.6761
[7 empty] | 15545 | 8900 | 1123241 | 2014-06-25 13:31 | 2014-06-25 20:41 | 430 | 11kV | 161714 | 966 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At Zn965 Pennant Hills Panel 26 Tripped, reclosed Tripped and Lockedout out on Relays: A phase IOC and Timed O/C, B phase Timed Mains Down in Wareemba Ave - Tree Mains Down in Larool Ave Caused By - Overload See OMS 1125453 1125454 1123350 1123241 | June | 2014 | 2014Q4 | 2014 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2014-06-25 | N | 167.4058 | N | 10 | N | N | 1.1101 | 39.4971 | 118175.8214
[7 empty] | 16299 | 18011 | 1123173 | 2014-06-25 12:37 | 2014-06-25 21:10 | 513 | 11kV | 22572 | 44 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" @RE44853 Ourimbah Bumble tripped and locked out on: Overcurrent & Lockout 2 bays of 11kV overhead mains down adjacent to AB44060 See 1123173 exclude 1123411 | June | 2014 | 2014Q4 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2014-06-25 | N | 513 | N | 10 | N | N | 1.1101 | 39.4971 | 16494.9518
[7 empty] | 15058 | 3302 | 1123471 | 2014-06-25 20:40 | 2014-06-25 22:10 | 90 | 11kV | 2035 | 23 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 141173 Car hit pole Excluded OMS 1123471 & 1123478 | June | 2014 | 2014Q4 | 2014 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-06-25 | N | 88.4783 | N | 10 | N | N | 1.1101 | 39.4971 | 1487.118
[7 empty] | 14740 | 360 | 1123490 | 2014-06-26 05:13 | 2014-06-26 07:10 | 117 | 11kV | 169981 | 2151 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn.7481 Darling harbour Pnl. 17 tripped on : Panel 17R FNG 1A (Earth Fault), EFI UG Cable fault - Frontline feeder | June | 2014 | 2014Q4 | 2014 | ZN7481:PA17 | ZN384:PA76 | ZN00384/000076 | SYDNEY | UG | Not Veg | 2014-06-26 | N | 79.0242 | N | 5 | N | N | 1.1101 | 39.4971 | 124217.1012
[7 empty] | 15931 | 13426 | 1123729 | 2014-06-26 12:20 | 2014-06-26 14:00 | 100 | 11kV | 700 | 7 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 141184 C phase DOLF : 20 Amp Pelican came into contact with mains. Excluded OMS # 1123729. | June | 2014 | 2014Q4 | 2014 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-06-26 | N | 100 | N | 5 | N | N | 1.1101 | 39.4971 | 511.5394
[7 empty] | 16023 | 14908 | 1123705 | 2014-06-26 11:43 | 2014-06-26 16:10 | 267.2 | 11kV | 534.4 | 2 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind | N | LID 141183 interrupt to repair wire off pin at 11kV links 27612 | June | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-06-26 | N | 267.2 | N | 5 | N | N | 1.1101 | 39.4971 | 390.5238
[7 empty] | 15849 | 12675 | 1123946 | 2014-06-26 21:24 | 2014-06-26 22:26 | 62 | 11kV | 88474 | 1427 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Zn12690 Berkeley Vale Pa19 "Corella Enterprise Etc" tripped on: Relays: IOC A & B Phase Signals: 11kv trip ABNORMAL: LB40034 closed RE41630 defective and open Flying Fox found opposite 43 Bundilla Rd Berkeley Vale See 1125535 GIS 1123961 Exclude 1123946,8,51,6,9 | June | 2014 | 2014Q4 | 2014 | ZN12690:PA19 | ZN12690:PA19 | ZN12690/000019 | CENTRAL COAST | OH | Not Veg | 2014-06-26 | N | 62 | N | 5 | N | N | 1.1101 | 39.4971 | 64654.1897
[7 empty] | 15192 | 4514 | 1123969 | 2014-06-27 01:49 | 2014-06-27 03:50 | 121 | 11kV | 91358 | 1150 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn12610 Long Jetty Pa9 "Denning st" tripped on A&C phase overcurrent, EFI Signals: 11kv trip Zone Earth Group Earth Tx1 Section of 11kv fdr from S18382/SwB to LB41034 to LB42805 tee PT11115, bond at UGOH defective. See 1125543,4,5 Exclude 1123969 | June | 2014 | 2014Q4 | 2014 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | OH | Not Veg | 2014-06-27 | N | 79.4417 | N | 5 | N | N | 1.1101 | 39.4971 | 66761.7318
[7 empty] | 15998 | 14582 | 1123967 | 2014-06-26 23:58 | 2014-06-27 03:55 | 237 | 11kV | 22804 | 186 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141186 3 fault operations Conductor broken at pole AI-80065. Repaired under AP. Excluded OMS 1123967 | June | 2014 | 2014Q4 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2014-06-26 | N | 122.6022 | N | 5 | N | N | 1.1101 | 39.4971 | 16664.4906
[7 empty] | 15956 | 13780 | 1124012 | 2014-06-27 08:32 | 2014-06-27 10:15 | 103 | 11kV | 12124 | 802 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | The 11kV Recloser 20285 tripped and reclosed on OC and IOC trip. At PT.15350 Larmer Pl the footpath and centre phase 40 k HDO fuses blew after bird flew into OH | June | 2014 | 2014Q4 | 2014 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2014-06-27 | N | 15.1172 | N | 5 | N | N | 1.1101 | 39.4971 | 8859.8616
[7 empty] | 15007 | 2897 | 1124300 | 2014-06-27 16:40 | 2014-06-27 17:45 | 65 | 11kV | 1235 | 19 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind | N | LID 141196 11kV main detached from pin insulator at pole DK-80030.. SINO N0322 | June | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-06-27 | N | 65 | N | 5 | N | N | 1.1101 | 39.4971 | 902.5016
[7 empty] | 14977 | 2625 | 1124327 | 2014-06-27 17:55 | 2014-06-27 18:55 | 60 | 11kV | 1080 | 18 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Wind | N | LID 141197 OH MAIN became detached from insulator. SINO N0323 | June | 2014 | 2014Q4 | 2014 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-06-27 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 789.2321
[7 empty] | 16449 | 19928 | 1124457 | 2014-06-27 15:10 | 2014-06-27 21:00 | 350 | 11kV | 157673 | 682 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141201 1 fault operation Overcurrent Tree branch brought 11kV main Boyd St at pole NR-60296. Excluded OMS 1124457, | June | 2014 | 2014Q4 | 2014 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2014-06-27 | N | 231.1921 | N | 5 | N | N | 1.1101 | 39.4971 | 115222.7778
[7 empty] | 16343 | 18446 | 1124368 | 2014-06-28 04:42 | 2014-06-28 08:34 | 232 | 11kV | 14384 | 62 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn4545 Meadowbank Pa29 - Zone Earth and No2 Tx Group Earth At S1017 Threlfall Rd Roadside HDO found operated Cause: Possum at base of pole adjacent to S1017 Linesman called out to inspect 11kV UGOH and repair LV crossarm See OMS 1124367 1124375 1124368 | June | 2014 | 2014Q4 | 2014 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2014-06-28 | N | 232 | N | 9 | N | N | 1.1101 | 39.4971 | 10511.4029
[7 empty] | 15612 | 9781 | 1124392 | 2014-06-28 09:36 | 2014-06-28 10:35 | 59 | 11kV | 5882 | 1996 | HV | Animal Bird | Animal | Fuse | Unplanned | Unselected | N | Zn12640 Umina Pa13 "Patonga" fdr tripped and reclosed on Aph IOC & Timed OC, EFI @PT18022 Lace Cowper B phase HDO 31.5Amp fuse blew due Birds flew into HV fuse assembly See 1125551,2 Exclude 1124392,4,5,7,9,406 | June | 2014 | 2014Q4 | 2014 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2014-06-28 | N | 2.9469 | N | 9 | N | N | 1.1101 | 39.4971 | 4298.3921
[7 empty] | 15909 | 13245 | 1125222 | 2014-06-28 11:05 | 2014-06-28 13:40 | 155 | 11kV | 13020 | 84 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 141199 Car into pole GS-23326, crossarm broken | June | 2014 | 2014Q4 | 2014 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2014-06-28 | N | 155 | N | 9 | N | N | 1.1101 | 39.4971 | 9514.632
[7 empty] | 16074 | 15702 | 1124432 | 2014-06-28 14:56 | 2014-06-28 15:35 | 39 | 11kV | 25581 | 869 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Wind | N | Ex Zn12570 Avoca section of Pa37L "Avoca Beach" fdr RE45180 Avoca Beach tripped and reclosed on OC & IOC Cause not ascertained 2nd Event RE45180 triped and locked out on IOC OC SEF trip PT11447 Fairscene Three points 0.5 defective lightning arrestor. Suspect defective since 1st event See 1125798,9 2nd 1125800 Exclude 1124432,3,456,64 | June | 2014 | 2014Q4 | 2014 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2014-06-28 | N | 29.4373 | N | 9 | N | N | 1.1101 | 39.4971 | 18693.8403
[7 empty] | 15855 | 12745 | 1124500 | 2014-06-28 16:15 | 2014-06-28 18:11 | 116 | 11kV | 175244 | 1670 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | At S4545 Meadowbank Panel 29 tripped on A and C phase O/C Signals: 11kV Trip EFI's Nil. Cause: Tree branch into 11kV in Banksia St Near North Rd See OMS 1125856 1125858 1124500 1125038 | June | 2014 | 2014Q4 | 2014 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Veg | 2014-06-28 | N | 104.9365 | N | 9 | N | N | 1.1101 | 39.4971 | 128063.1464
[7 empty] | 15776 | 11866 | 1124660 | 2014-06-28 18:10 | 2014-06-28 18:25 | 15 | 11kV | 2486 | 186 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 141203 ABS 46773 reported/found to be glowing & arcing, not closed properly. Opened Fdr CB to safely operate ABS | June | 2014 | 2014Q4 | 2014 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2014-06-28 | N | 13.3656 | N | 9 | N | N | 1.1101 | 39.4971 | 1816.6955
[7 empty] | 15367 | 6980 | 1124472 | 2014-06-28 15:50 | 2014-06-28 22:20 | 390 | 11kV | 20562 | 107 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12690 Berkely Vale section of Pa16 "the catamaran sailcraft" fdr CP45026 fountaindale tripped and locke dout on IOC OC Tree branch brought down OH 182 peach orchard rd See 1125889,90 Exclude 1124472,3 | June | 2014 | 2014Q4 | 2014 | ZN12690:PA16 | ZN12690:PA16 | ZN12690/000016 | CENTRAL COAST | OH | Veg | 2014-06-28 | N | 192.1682 | N | 9 | N | N | 1.1101 | 39.4971 | 15026.1031
[7 empty] | 14968 | 2514 | 1124566 | 2014-06-28 17:00 | 2014-06-28 23:48 | 408 | 11kV | 42432 | 104 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | pt11336 Wananda Cooinda Dist 1 & Dist 2 ABC phase fuses blown due to tree brought down OH See 1125849 exclude 1124566,76 | June | 2014 | 2014Q4 | 2014 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2014-06-28 | N | 408 | N | 9 | N | N | 1.1101 | 39.4971 | 31008.0541
[7 empty] | 15444 | 7892 | 1124624 | 2014-06-28 17:41 | 2014-06-29 06:30 | 769 | 11kV | 14461 | 27 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn14891 Wyong section of Pa5 "Dooralong" fdr From Isolator 43160 to rest of fdr interrupted by DOp for repairs to CCT OH @PT13339 Dooralong Yamba 0.8 Tree branch brought down OH See 1125919 2nd 1125920 Exclude 1124624 | June | 2014 | 2014Q4 | 2014 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2014-06-28 | N | 535.5926 | N | 9 | N | N | 1.1101 | 39.4971 | 10567.6723
[7 empty] | 15052 | 3274 | 1124749 | 2014-06-29 03:16 | 2014-06-29 08:20 | 304 | 11kV | 87196 | 1075 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | LID 141206 2 fault operations A & B phases Overcurrent Tree brought down mains pole HU-60120. | June | 2014 | 2014Q4 | 2014 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2014-06-29 | N | 81.1126 | N | 5 | N | N | 1.1101 | 39.4971 | 63720.265
[7 empty] | 15008 | 2898 | 1124757 | 2014-06-29 06:46 | 2014-06-29 08:55 | 128.7833 | 11kV | 1931.75 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 141207 A phase DOLF : 16 Amp No cause found | June | 2014 | 2014Q4 | 2014 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2014-06-29 | N | 128.7833 | N | 5 | N | N | 1.1101 | 39.4971 | 1411.6659
[7 empty] | 16117 | 16143 | 1124841 | 2014-06-29 09:41 | 2014-06-29 10:41 | 60 | 11kV | 75960 | 1266 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | At Zn965 Pennant Hills Panel 33 tripped, reclosed tripped and locked out on B and C pgase O/C, Reclose Timing and Lockout Cause Not ascertained - Dop Patrolled and Nothing Found. | June | 2014 | 2014Q4 | 2014 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Veg | 2014-06-29 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 55509.3276
[7 empty] | 15674 | 10748 | 1124923 | 2014-06-29 11:54 | 2014-06-29 13:30 | 96 | 11kV | 21024 | 219 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | Ex Zn12620 Noraville section of Pa10 Isolator 40199 bond open circuit. See 1125965 exclude 1124923 | June | 2014 | 2014Q4 | 2014 | ZN12620:PA10 | ZN12620:PA10 | ZN12620/000010 | CENTRAL COAST | OH | Not Veg | 2014-06-29 | N | 96 | N | 5 | N | N | 1.1101 | 39.4971 | 15363.7191
[7 empty] | 15146 | 4133 | 1124792 | 2014-06-29 08:16 | 2014-06-29 15:50 | 454 | 11kV | 10072 | 108 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12650 West Gosford section of Pa1 "Dog trap rd" fdr RE44602 Ourimbah Creek rd tripped on SEF 2 bays 11kV OH Down near PT12419 Bumble Creek Ourimbah 0.4 See 1125934,6,8,9 Exclude 1124792 | June | 2014 | 2014Q4 | 2014 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2014-06-29 | N | 93.2593 | N | 5 | N | N | 1.1101 | 39.4971 | 7360.3205
[7 empty] | 15150 | 4165 | 1125574 | 2014-06-30 18:30 | 2014-06-30 20:55 | 145 | 11kV | 1595 | 11 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | LID 141226 Replace 2 broken crossarms at sub 3906 Langbein N No Protection Operated | June | 2014 | 2014Q4 | 2014 | 264:81244 | 264:81244 | ZN00264/081244 | PORT STEPHENS | OH | Not Veg | 2014-06-30 | N | 145 | N | 1 | N | N | 1.1101 | 39.4971 | 1165.579
[7 empty] | 14372 | 17701 | 1125612 | 2014-07-01 06:41 | 2014-07-01 07:38 | 57 | 11kV | 50844 | 892 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of P13 "Hanlan St" RE62730 Manns Narara Creek tripped reclosed and tripped then locked out on overcurrent Tree branch on mains in Manns Rd near 11kv USL 42497 on pole GO 30338 DOp removed tree branch | July | 2014 | 2015Q1 | 2015 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2014-07-01 | N | 57 | N | 3 | N | N | 1.1101 | 39.4971 | 37155.2956
[7 empty] | 13660 | 12189 | 1125734 | 2014-07-01 17:25 | 2014-07-01 20:45 | 200 | 11kV | 200 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 141239 TRANSFORMER REPORTED FAULTY & CHANGED. Excluded OMS 1125734 | July | 2014 | 2015Q1 | 2015 |  |  |  |  | OH | Not Veg | 2014-07-01 | N | 200 | N | 3 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 13917 | 14284 | 1126042 | 2014-07-01 08:30 | 2014-07-01 21:20 | 770 | 11kV | 1540 | 2 | HV | Staff Operation | Utility Process Issue | DC PT | Unplanned | Unselected | N | LID 141241 DOLFs left open on planned switching Excluded OMS 1126042 | July | 2014 | 2015Q1 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2014-07-01 | N | 770 | N | 3 | N | N | 1.1101 | 39.4971 | 1125.3866
[7 empty] | 13445 | 10541 | 1126245 | 2014-07-02 11:01 | 2014-07-02 12:40 | 99 | 11kV | 129078 | 2122 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 10 - B phase timed OC, Earth Fault, EFI, Field EFIs. (Note: SEL and Recloser were Non-Auto for D&R 339468) UGOH went short circuit outside 88 Attunga Rd, Yowie Bay. ME: 1128557. Rest Steps: 1128558, 9. Withdrawn: 1126245, 9, 1127019. | July | 2014 | 2015Q1 | 2015 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | Unknown | Unknown | 2014-07-02 | N | 60.8285 | N | 1 | N | N | 1.1101 | 39.4971 | 94326.3952
[7 empty] | 12338 | 812 | 1126571 | 2014-07-03 00:44 | 2014-07-03 01:58 | 74 | 11kV | 34854 | 471 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | At Zn1673 Turramurra panel 19 tripped on Relays: C phase IOC and EFI. Signals: Tx3 Group Earth. Cause: Possum found at PT1809 Billyard Young on C phase HDO | July | 2014 | 2015Q1 | 2015 | ZN1673:PA19 | ZN1673:PA19 | ZN01673/000019 | KU-RING-GAI | OH | Not Veg | 2014-07-03 | N | 74 | N | 6 | N | N | 1.1101 | 39.4971 | 25470.2752
[7 empty] | 14043 | 15384 | 1126572 | 2014-07-03 00:46 | 2014-07-03 02:01 | 75 | 11kV | 5475 | 73 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141261 A phase DOLF suspect fuse fatigue Excluded oms 1126572 | July | 2014 | 2015Q1 | 2015 | 258:80779 | 258:80779 | ZN00258/080779 | NEWCASTLE | OH | Not Veg | 2014-07-03 | N | 75 | N | 6 | N | N | 1.1101 | 39.4971 | 4000.9685
[7 empty] | 14088 | 15698 | 1126604 | 2014-07-03 08:09 | 2014-07-03 08:45 | 36 | 11kV | 792 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141263 A phase DOLF : 40 Amp A phase DOLf found blown. Operator reports that when opening ABS 27953 as per Switching Instruction 42659 the flicker blades were slow to open and did not open at the same time. It appears the fuse blew at the time the air break switch was opened. Also possible fuse fatigue. Excluded OMS 1126604 | July | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-07-03 | N | 36 | N | 6 | N | N | 1.1101 | 39.4971 | 578.7702
[7 empty] | 13671 | 12287 | 1126659 | 2014-07-03 09:14 | 2014-07-03 10:07 | 53 | 11kV | 37674 | 1008 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Cable fault between S.35571 and S.4930: At S.180 Mosman, Panel 24 Fdr CB tripped on A phase OC and earth fault. 11kV trip, efi and fault check. Field efi's down at S.1340, S.47402 and S.1620. No efi operation at S.35571 (defective)) | July | 2014 | 2015Q1 | 2015 | ZN180:PA24 | ZN180:PA24 | ZN00180/000024 | WILLOUGHBY | UG | Not Veg | 2014-07-03 | N | 37.375 | N | 6 | N | N | 1.1101 | 39.4971 | 27531.048
[7 empty] | 13180 | 8238 | 1126577 | 2014-07-03 06:35 | 2014-07-03 13:30 | 415 | 11kV | 110125 | 529 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge 11kc OCB Pa2 "Gunderman" fdr RE45189 Cooks PEats Ridge 0.5 tripped and reclosed tripped and locked out on overucrrent 11kv overhead down near PT11214 Morgan Pacific 1.5 See 1128074,5,6 Exclude 1126577 | July | 2014 | 2015Q1 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2014-07-03 | N | 208.1758 | N | 6 | N | N | 1.1101 | 39.4971 | 80476.1019
[7 empty] | 12487 | 2142 | 1126820 | 2014-07-03 12:54 | 2014-07-03 16:58 | 244 | 11kV | 320406 | 1848 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 141279 1 fault operation Earth fault FAULTY ARRESTOR AT UGOH TO SW 15810. Excluded OMS REPORT NO 1126842 & 1126824. | July | 2014 | 2015Q1 | 2015 | 232:11454 | 232:11454 | ZN00232/011454 | PORT STEPHENS | Unknown | Unknown | 2014-07-03 | N | 173.3799 | N | 6 | N | N | 1.1101 | 39.4971 | 234143.2544
[7 empty] | 12313 | 577 | 1127058 | 2014-07-04 00:44 | 2014-07-04 01:58 | 74 | 11kV | 139652 | 1975 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | ZN 10994 Mortdale - Pnl 12L - Trip/reclose/trip, B and C phase IOC, Lockout, EFI, Instantaeous Earth Fault, Field EFIs. Possum on UGOH between S 10901, AB 31018 and S 10683. ME: 1128354. Rest Step: 1128356. Withdrawn: 1127058. | July | 2014 | 2015Q1 | 2015 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2014-07-04 | N | 70.7099 | N | 3 | N | N | 1.1101 | 39.4971 | 102053.5626
[7 empty] | 13146 | 7963 | 1127060 | 2014-07-04 01:53 | 2014-07-04 04:40 | 167 | 11kV | 57448 | 344 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | At ZN 10994 Mortdale - Section of 11kV - AB 31296 Centre Phase Open Circuit. Centre phase bond burnt off at AB 31296 after earlier outage. ME: 1128365. Withdrawn: 1127060, 2. | July | 2014 | 2015Q1 | 2015 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2014-07-04 | N | 167 | N | 3 | N | N | 1.1101 | 39.4971 | 41981.304
[7 empty] | 12783 | 4872 | 1127326 | 2014-07-04 13:05 | 2014-07-04 16:55 | 230 | 11kV | 78460 | 1394 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10997 Sans Souci - Pnl 12 - Trip/reclose/trip, A phase IOC, Fault Check, EFI, Lockout. 11kV UGOH above AB 30118 Centre phase blown. S 10348 supply restored via LV//. Defective UGOH cut away from OH. ME: 1128547. Rest Steps: 1128548, 9. Withdrawn: 1127326, 29, 56. | July | 2014 | 2015Q1 | 2015 | ZN10997:PA12 | ZN10997:PA12 | ZN10997/000012 | BAYSIDE | Unknown | Unknown | 2014-07-04 | N | 56.2841 | N | 3 | N | N | 1.1101 | 39.4971 | 57336.2538
[7 empty] | 14649 | 20126 | 1127504 | 2014-07-05 07:05 | 2014-07-05 08:46 | 101.3 | 11kV | 1013 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141302 Single phase DOLF : 10 Amp | July | 2014 | 2015Q1 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-07-05 | N | 101.3 | N | 1 | N | N | 1.1101 | 39.4971 | 740.2705
[7 empty] | 13181 | 8248 | 1127729 | 2014-07-06 19:08 | 2014-07-06 21:30 | 142 | 11kV | 32904 | 507 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | Unselected | N | Ex Panel 31 Zn2473 North Sydney At S2316 North Sydney Anzac Club TX2 found Tripped - Cause Not Ascertained At S3856 Moodie Falcon 400A fuse blown on A phase of distributor 3 - LV Parallel Failure At S373 Middle St 400A fuse blown on A phase of distributor 2 and 4 - LV parallel Failure At S4375 Bay View East Cres 400A fuse blown on A phase of distributor 3 - LV parallel Failure See OMS 1128080 1128082 1128086 1128087 1128088 1127737 1127738 1127729 | July | 2014 | 2015Q1 | 2015 | ZN2473:PA31 | ZN187:PA19 | ZN00187/000019 | NORTH SYDNEY | UG | Not Veg | 2014-07-06 | N | 64.8994 | N | 1 | N | N | 1.1101 | 39.4971 | 24045.2727
[7 empty] | 14134 | 16078 | 1127759 | 2014-07-07 07:35 | 2014-07-07 11:34 | 238.7667 | 11kV | 2387.6667 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141314 Burnt off Tapping at pole BN-70003 CC1: 06-"Urgent - O.H Mains - No others" | July | 2014 | 2015Q1 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2014-07-07 | N | 238.7667 | N | 4 | N | N | 1.1101 | 39.4971 | 1744.8364
[7 empty] | 12328 | 695 | 1128304 | 2014-07-07 09:40 | 2014-07-07 14:50 | 310 | 11kV | 1240 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141316 Deteriorated mains at pole IQ-42202 | July | 2014 | 2015Q1 | 2015 | 510:48164 | 508:82579 | ZN00508/082579 | MAITLAND | OH | Not Veg | 2014-07-07 | N | 310 | N | 4 | N | N | 1.1101 | 39.4971 | 906.1554
[7 empty] | 12701 | 4164 | 1127897 | 2014-07-07 16:45 | 2014-07-07 17:30 | 45 | 11kV | 720 | 16 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 141317 section isolated to repair x-arm at P. JR-54422 Cross Rd Nelson Plain | July | 2014 | 2015Q1 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Not Veg | 2014-07-07 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 14140 | 16116 | 1128141 | 2014-07-07 14:46 | 2014-07-07 18:40 | 234 | 11kV | 104864 | 970 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9301 Kurnell - Pnl 15 - SEL. High Voltage fell into Low Voltage on the corner of Silverbeach Rd and Captain Cook Drive. ME: 1128466. Rest Step: 1128467. Withdrawn: 1128141, 42, 50, 1128240. | July | 2014 | 2015Q1 | 2015 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2014-07-07 | N | 108.1072 | N | 4 | N | N | 1.1101 | 39.4971 | 76631.5182
[7 empty] | 12337 | 805 | 1128290 | 2014-07-08 07:22 | 2014-07-08 07:38 | 15.6667 | 11kV | 32859.3333 | 2790 | HV | Overload | Utility Process Issue | Feeder/Distributor U/G | Unplanned | Unselected | N | At S.15005 Belrose, 11kV Feeder CB's #5 "SW 1926" and #9 "SW 1932" tripped due to T/PE staff injecting into the incorrect circuit as a result of incorrect diagrams. Futher Information from Andrew Cleary | July | 2014 | 2015Q1 | 2015 | ZN15005:PA8 | ZN15005:PA8 | ZN15005/000008 | NORTHERN BEACHES | UG | Not Veg | 2014-07-08 | N | 11.7775 | N | 2 | N | N | 1.1101 | 39.4971 | 24012.6316
[7 empty] | 12375 | 1143 | 1128286 | 2014-07-08 06:51 | 2014-07-08 13:02 | 371.4 | 11kV | 154088.35 | 543 | HV | Vandalism | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Ex Panel 31 At ZN2473 North Sydney - S.2316 North Sydney Anzac Club SW/D Operated by Phantom Operator At S2316 North Sydney Anzac Club - Phantom Operator and cable theft See OMS 1128830 1128307 1128431 1128286 1128429 | July | 2014 | 2015Q1 | 2015 | ZN2473:PA31 | ZN35400:PA81 | ZN35400/000081 | NORTH SYDNEY | UG | Not Veg | 2014-07-08 | N | 283.7723 | N | 2 | N | N | 1.1101 | 39.4971 | 112603.2213
[7 empty] | 14086 | 15696 | 1128748 | 2014-07-09 07:26 | 2014-07-09 08:17 | 51 | 11kV | 72726 | 1426 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141332 3 phase Sensitive Earth Fault sw 50319 tripped on sef during SI 1025. When SEF was returned to auto sw 50319 tripped. Fdr has been switched abnormal due to previous spurious SEF faults please investigate. | July | 2014 | 2015Q1 | 2015 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Veg | 2014-07-09 | N | 51 | N | 4 | N | N | 1.1101 | 39.4971 | 53146.0157
[7 empty] | 13800 | 13281 | 1128800 | 2014-07-09 08:45 | 2014-07-09 09:13 | 28 | 11kV | 46984 | 1678 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 24 - Earth Fault, EFI, Field EFIs. While doing trip checks at Campsie Zone, both Pnls 24 and 34 tripped whilst in parallel. Presumably an underground fault between S 3969, S 4173 tee S 7436 on Pnl 34. ME: 1128800. | July | 2014 | 2015Q1 | 2015 | ZN690:PA24 | ZN690:PA35 | ZN00690/000035 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-07-09 | N | 28 | N | 4 | N | N | 1.1101 | 39.4971 | 34334.5214
[7 empty] | 12967 | 6546 | 1128803 | 2014-07-09 08:45 | 2014-07-09 11:47 | 181.65 | 11kV | 226396.65 | 2553 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 34 - Earth Fault, EFI, Field EFIs. While doing trip checks at Campsie Zone, both Pnls 24 and 34 tripped whilst in parallel. Presumably an underground fault between S 3969, S 4173 tee S 7436. ME: 129372. Rest Steps: 1129374, 6. ME GIS: 1128817. Withdrawn: 1128803. | July | 2014 | 2015Q1 | 2015 | ZN690:PA34 | ZN690:PA34 | ZN00690/000034 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-07-09 | N | 88.6787 | N | 4 | N | N | 1.1101 | 39.4971 | 165443.9942
[7 empty] | 13687 | 12415 | 1129191 | 2014-07-09 19:32 | 2014-07-10 02:10 | 398.1 | 11kV | 45383.4 | 114 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ExZn12630 Peats Ridge section of Pa2 "Gunderman" fdr Recloser 61097 Wise Ferry Lavender 10.2 tripped, reclosed and locked out on timed overcurrent tree on 11kV | July | 2014 | 2015Q1 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2014-07-09 | N | 398.1 | N | 4 | N | N | 1.1101 | 39.4971 | 33164.8501
[7 empty] | 12553 | 2830 | 1129459 | 2014-07-10 12:05 | 2014-07-10 13:20 | 75 | 11kV | 2400 | 32 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12600 Lisarow Pa3 @PT47662 Kathleen Pacific 11kv roadside 63 HDO operated. Fuse Fatigue See 1129849 GIS 1129459 Exclude 1129510 | July | 2014 | 2015Q1 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Not Veg | 2014-07-10 | N | 75 | N | 1 | N | N | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 14573 | 19265 | 1129706 | 2014-07-11 01:24 | 2014-07-11 02:45 | 81 | 11kV | 81966 | 1086 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn965 Pennant Hills - Panel 4 tripped on Earth Fault, Timing and lockout Signals: 11kV Trip, Zone Earth and Group Earth Cause: Cable fault between S6808 David Barcote to S7350 James Henty New Line and S7535 Oakhill Allara See OMS 1130491 1130493 1129706 | July | 2014 | 2015Q1 | 2015 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | UG | Not Veg | 2014-07-11 | N | 75.4751 | N | 3 | N | N | 1.1101 | 39.4971 | 59898.3352
[7 empty] | 14584 | 19411 | 1129917 | 2014-07-11 12:07 | 2014-07-11 12:45 | 38 | 11kV | 13623 | 371 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | At S2635 Epping Panel 51 Tripped on IOC and EFI. Cause:11kV feeder fault O/S Shipway Village between S62347 Dyman Epping to S3740 Shipway Village 11kV feeder hit by contractor O/S Vimera Village 217 Vimera Rd See OMS 1130536 1130538 1129917 1129930 | July | 2014 | 2015Q1 | 2015 | ZN2635:PA51 | ZN2635:PA51 | ZN02635/000051 | RYDE | UG | Not Veg | 2014-07-11 | N | 36.7197 | N | 3 | N | N | 1.1101 | 39.4971 | 9955.2866
[7 empty] | 12583 | 3122 | 1129744 | 2014-07-11 08:05 | 2014-07-11 13:10 | 305 | 11kV | 1830 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind | N | LID 141378 11kV dropper broken. Excluded OMS 1129744. | July | 2014 | 2015Q1 | 2015 | 510:48164 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2014-07-11 | N | 305 | N | 3 | N | N | 1.1101 | 39.4971 | 1337.31
[7 empty] | 13743 | 12859 | 1130139 | 2014-07-12 04:09 | 2014-07-12 05:10 | 61 | 11kV | 45626 | 929 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At ZN3425 Castle Cove 11kV feeder Panel 44 tripped on Relays: A phase overcurrent Signals: 11kV trip Field EFI's: NIL High Voltage Mains Down O/S 15 High Tor Castle Cove See OMS 1130560 1130564 1130563 1130139 | July | 2014 | 2015Q1 | 2015 | ZN3425:PA44 | ZN3425:PA44 | ZN03425/000044 | WILLOUGHBY | OH | Not Veg | 2014-07-12 | N | 49.113 | N | 2 | N | N | 1.1101 | 39.4971 | 33342.1351
[7 empty] | 13077 | 7453 | 1130136 | 2014-07-12 01:51 | 2014-07-12 05:40 | 229 | 11kV | 402084 | 2096 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | At S.15001 Brookvale, 11kV Fdr.,panel 18 CB tripped, reclosed and tripped on SEL, fault check, reclose and timing relays, efi, 11kV trip signal. Field efi's down at S.16312, S.17044. S.63779. S.16905, S.16837 and S.46891. OH Earth Wire of O/O/S "S06" came away from 33kV pole across 11kV OH conductor | July | 2014 | 2015Q1 | 2015 | ZN15001:PA18 | ZN15001:PA18 | ZN15001/000018 | NORTHERN BEACHES | OH | Not Veg | 2014-07-12 | N | 191.834 | N | 2 | N | N | 1.1101 | 39.4971 | 293831.1277
[7 empty] | 13461 | 10658 | 1130281 | 2014-07-13 00:31 | 2014-07-13 03:20 | 169 | 11kV | 1014 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141389 A & B phase DOLF : 20 Amp Excluded OMS 1130281 & 1130282 | July | 2014 | 2015Q1 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2014-07-13 | N | 169 | N | 5 | N | N | 1.1101 | 39.4971 | 741.0013
[7 empty] | 12501 | 2275 | 1130285 | 2014-07-13 02:58 | 2014-07-13 04:30 | 92 | 11kV | 2668 | 29 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 141390 B phase DOLF : 31 Amp DOp reports all DOLFs should be replaced. Excluded OMS 1130285 & 1130286 | July | 2014 | 2015Q1 | 2015 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | UG | Not Veg | 2014-07-13 | N | 92 | N | 5 | N | N | 1.1101 | 39.4971 | 1949.6957
[7 empty] | 13163 | 8071 | 1130291 | 2014-07-13 06:56 | 2014-07-13 08:51 | 115 | 11kV | 36201 | 531 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn340 Botnay Pnl.8 tripped on: Earth Fault, EFI Suspect UG cable fault between S8559, S3409 & S36156 tee S2120 see 1130574 1130575 1130576 | July | 2014 | 2015Q1 | 2015 | ZN340:PA8 | ZN340:PA8 | ZN00340/000008 | BAYSIDE | UG | Not Veg | 2014-07-13 | N | 68.1751 | N | 5 | N | N | 1.1101 | 39.4971 | 26454.6231
[7 empty] | 13561 | 11393 | 1130301 | 2014-07-13 07:49 | 2014-07-13 09:28 | 99 | 11kV | 166953 | 1780 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn12650 West Gosford Pa9 "Wyoming" fdr tripped and reclosed and locked out on B & C IOC, Timing and lockout relay ABNORMAL: IR63068 Hills Etna defective and open, LB63071 closed Cause not ascertained See 1131496,7 Exclude 1130301,4 | July | 2014 | 2015Q1 | 2015 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | OH | Veg | 2014-07-13 | N | 93.7938 | N | 5 | N | N | 1.1101 | 39.4971 | 122004.3281
[7 empty] | 12885 | 5888 | 1130284 | 2014-07-13 02:04 | 2014-07-13 12:09 | 605 | 11kV | 21191 | 85 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141388 2 fault operations Wires down pole FQ-23032. After restoration burnt off tapping found at pole FQ-23157 & islated section again. Excluded OMS 1130284, 113032 & 1130325 | July | 2014 | 2015Q1 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-07-13 | N | 249.3059 | N | 5 | N | N | 1.1101 | 39.4971 | 15485.7578
[7 empty] | 12665 | 3873 | 1130449 | 2014-07-14 02:20 | 2014-07-14 03:29 | 69 | 11kV | 75417 | 1093 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S847 Hornsby panel 18 tripped and locked out on C phase IOC L/O and Timing EFI and Fault Check Tx2 Group Earth and Zone Earth With 11kV Trip Cause: Possum on UGOH near LB63753 - mains to inspect See OMS 1130449 1130453 CC1: 22-"Refer to SOp" | July | 2014 | 2015Q1 | 2015 | ZN847:PA18 | ZN847:PA18 | ZN00847/000018 | HORNSBY | OH | Not Veg | 2014-07-14 | N | 69 | N | 5 | N | N | 1.1101 | 39.4971 | 55112.5192
[7 empty] | 12403 | 1455 | 1130455 | 2014-07-14 05:03 | 2014-07-14 05:50 | 47 | 11kV | 45872 | 976 | HV | Animal Possum | Animal | DC Not Transformer | Unplanned | Unselected | N | At S.3154 St Ives, the 11kV Panel 10 Fdr CB tripped on A phase IOC and timed OC, efi, Field efi's down at S.7763 and S.4911. Possum at PT.297 | July | 2014 | 2015Q1 | 2015 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | OH | Not Veg | 2014-07-14 | N | 47 | N | 5 | N | N | 1.1101 | 39.4971 | 33521.9046
[7 empty] | 12449 | 1782 | 1130835 | 2014-07-14 16:30 | 2014-07-14 17:00 | 30 | 11kV | 120 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 141403 Isolated for repairs Conductor off pin at pole BS-10022 | July | 2014 | 2015Q1 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-07-14 | N | 30 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 13855 | 13733 | 1130869 | 2014-07-14 18:36 | 2014-07-14 20:06 | 89.9333 | 11kV | 43700.3833 | 583 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN 10999 Kogarah - Pnl 24L - Section of Feeder from AB 30253. B phase bond burnt off at AB 30253. ME: 1131245. ME GIS: 1130881. Withdrawn: 1130869, 83. | July | 2014 | 2015Q1 | 2015 | ZN10999:PA24 | ZN10993:PA43 | ZN10993/000043 | GEORGES RIVER | OH | Not Veg | 2014-07-14 | N | 74.9578 | N | 5 | N | N | 1.1101 | 39.4971 | 31934.9512
[7 empty] | 14384 | 17785 | 1130900 | 2014-07-14 21:24 | 2014-07-14 23:10 | 106 | 11kV | 530 | 5 | HV | Animal Possum | Animal | Fuse | Unplanned | Rain Light | N | PT13362 Peats Ridge 0.8 footpath HDO 16K HV fuse blown due to Possum. See 1131610 exclude 1130900,3 | July | 2014 | 2015Q1 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2014-07-14 | N | 106 | N | 5 | N | N | 1.1101 | 39.4971 | 387.3084
[7 empty] | 13339 | 9651 | 1131108 | 2014-07-15 11:55 | 2014-07-15 12:55 | 60 | 11kV | 44060 | 831 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | 5kV Zn 384 Camperdown panel 33 tripped on Earth Fault and EFI Front line feeder fault from Panel 33 to S142 and S5758 see 1131349 GIS 1131138 1131125 | July | 2014 | 2015Q1 | 2015 | ZN384:PA33 | ZN2568:PA26 | ZN02568/000026 | INNER WEST | UG | Not Veg | 2014-07-15 | N | 53.0205 | N | 4 | N | N | 1.1101 | 39.4971 | 32197.7485
[7 empty] | 13098 | 7645 | 1131081 | 2014-07-15 11:25 | 2014-07-15 14:10 | 165 | 11kV | 6487 | 93 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141413 2 fault operations Earth fault Protection Flags Required.- EARTH FAULT Fuse blown at 74960. A-PHASE - PLEASE INVESTIGATE GRADING BETWEEN SW 74183 & L/FUSE 74960. Excluded OMS 1131081 & 1131128 | July | 2014 | 2015Q1 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2014-07-15 | N | 69.7527 | N | 4 | N | N | 1.1101 | 39.4971 | 4740.5083
[7 empty] | 13813 | 13359 | 1130981 | 2014-07-15 09:13 | 2014-07-15 16:05 | 412 | 11kV | 412 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 141414 A & B phase DOLF : 10 Amp TX 72795 faulty , changed. Excluded OMS 1130981 | July | 2014 | 2015Q1 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-07-15 | N | 412 | N | 4 | N | N | 1.1101 | 39.4971 | 301.0774
[7 empty] | 13913 | 14218 | 1131320 | 2014-07-15 21:43 | 2014-07-16 00:10 | 147 | 11kV | 143955 | 1695 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S4545 meadowbank Panel 29 Tripped on A and C phase Overcurrent Signals: 11kV trip Cause not ascertained for outage | July | 2014 | 2015Q1 | 2015 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Veg | 2014-07-15 | N | 84.9292 | N | 4 | N | N | 1.1101 | 39.4971 | 105198.068
[7 empty] | 14111 | 15885 | 1131684 | 2014-07-16 15:27 | 2014-07-16 19:40 | 253 | 11kV | 21009 | 260 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141423 2 fault operations B & C phase Overcurrent Burnt off tapping at pole BI-90235. Comms not available at Sw 63399 | July | 2014 | 2015Q1 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2014-07-16 | N | 80.8038 | N | 1 | N | N | 1.1101 | 39.4971 | 15352.7575
[7 empty] | 12791 | 4947 | 1132117 | 2014-07-17 15:06 | 2014-07-17 17:45 | 159 | 11kV | 186864 | 1876 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1285 Greenacre Park 11kv Panel 31 'Sub 5729, Sub 4862 etc' feeder C/B tripped, closed, and tripped on; Relays: 31 Right; B phase Overcurrent, EFI, Timing, Lockout. Signals: Zone Earth, Group Earth, 11kv trip. Field EFI's: Sub 4862, Sub 4867 Incorrect EFI indication at Sub 5917 Sylvanus Juno Remarks: UG fault. 11kv feeder Sw/B @ Sub 4867 Acacia Wilber to Sub 5917 Sylvanus Juno tee to PT 1433 Roberts Juno | July | 2014 | 2015Q1 | 2015 | ZN1285:PA31 | ZN1285:PA31 | ZN01285/000031 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-07-17 | N | 99.6077 | N | 1 | N | N | 1.1101 | 39.4971 | 136554.6996
[7 empty] | 13955 | 14603 | 1132250 | 2014-07-18 10:05 | 2014-07-18 12:58 | 173 | 11kV | 44980 | 260 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | LID 141443 No Protection. Pole Fire at ABS. Burnt out base of pole. Appears the fire was not caused by our equipment. 40m square of grass burnt. Excluded OMS # 1132347, 1132250, 1132251. | July | 2014 | 2015Q1 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2014-07-18 | N | 173 | N | 3 | N | N | 1.1101 | 39.4971 | 32870.0573
[7 empty] | 12477 | 1986 | 1132267 | 2014-07-18 13:45 | 2014-07-18 14:20 | 35 | 11kV | 175 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 141445 Replace defective cross arm at pole HR-51263. | July | 2014 | 2015Q1 | 2015 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2014-07-18 | N | 35 | N | 3 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 14358 | 17596 | 1132637 | 2014-07-18 20:43 | 2014-07-18 22:40 | 117 | 11kV | 212224 | 1864 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn3922 Drummoyne P11 the thornley victoria fdr tripped on earth fault, fault check, efi. EFI's at S7738, Remarks: UG fault. UG fault in section of 11kv feeder from Sub 7738 Renwick Roseby to Sub 3874 PMG Balmain to Sub 2872 Darling Birch | July | 2014 | 2015Q1 | 2015 | ZN3922:PA11 | ZN3922:PA11 | ZN03922/000011 | INNER WEST | UG | Not Veg | 2014-07-18 | N | 113.8541 | N | 3 | N | N | 1.1101 | 39.4971 | 155087.0397
[7 empty] | 12982 | 6680 | 1132766 | 2014-07-19 14:55 | 2014-07-19 15:36 | 40.7833 | 11kV | 35440.7167 | 869 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12570 Avoca section of Pa37L "Avoca Beach" @RE45180 tripped, reclosed and locked out on: Relays IOC, OC Signals: 11kv trip, Lockout EFI's: Nil Cause: Branch on 2 phases adjacent Pole AV1127 | July | 2014 | 2015Q1 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2014-07-19 | N | 40.7833 | N | 2 | N | N | 1.1101 | 39.4971 | 25899.0304
[7 empty] | 13053 | 7192 | 1132772 | 2014-07-19 16:01 | 2014-07-19 18:14 | 133.3833 | 11kV | 45797.3833 | 1111 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 10994 Mortdale - Pnl 10 - Trip/reclose/trip, A & B phase overcurrent, lockout. Tree branch came in contact with HV overhead. Branch was clear of mains. ME: 1134245. Rest Step: 1134247. Withdrawn: 1132772, 3, 4, 6, 7. | July | 2014 | 2015Q1 | 2015 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2014-07-19 | N | 41.2218 | N | 2 | N | N | 1.1101 | 39.4971 | 33467.3769
[7 empty] | 14284 | 17113 | 1134531 | 2014-07-20 00:17 | 2014-07-20 01:18 | 61 | 11kV | 1132 | 20 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn8700 City North 61/62E tripped on: 62E Leg O/C & Earth Fault (51N) Suspect UG cable fault on 62E leg See 1134531 1134532 1134535 | July | 2014 | 2015Q1 | 2015 | ZN8700:PA61 62DEF | ZN8700:PA61 62DEF | ZN08700/61 62DEF | SYDNEY | UG | Not Veg | 2014-07-20 | N | 56.6 | N | 2 | N | N | 1.1101 | 39.4971 | 827.2322
[7 empty] | 12942 | 6356 | 1132935 | 2014-07-20 18:21 | 2014-07-21 01:19 | 418 | 11kV | 52009 | 253 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141456 1 fault operation Sensitive Earth Fault wire down beyond abs 64833 Excluded oms 1132935, 1132951 & 1132964 | July | 2014 | 2015Q1 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-07-20 | N | 205.5692 | N | 2 | N | N | 1.1101 | 39.4971 | 38006.6432
[7 empty] | 13265 | 8876 | 1132966 | 2014-07-21 09:22 | 2014-07-21 10:27 | 65 | 11kV | 2405 | 37 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141460 interrupt to repair HV tapping at pole AF-80042 near sub 71664. | July | 2014 | 2015Q1 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2014-07-21 | N | 65 | N | 3 | N | N | 1.1101 | 39.4971 | 1757.5031
[7 empty] | 13795 | 13246 | 1132998 | 2014-07-21 08:19 | 2014-07-21 15:31 | 432.2167 | 11kV | 9940.9833 | 23 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141461 3 fault operations B phase Earth Fault wire down between pole GT-92209 & GT-92210 near sub 27310 | July | 2014 | 2015Q1 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-07-21 | N | 432.2167 | N | 3 | N | N | 1.1101 | 39.4971 | 7264.5774
[7 empty] | 14680 | 20364 | 1133436 | 2014-07-21 20:12 | 2014-07-21 23:40 | 208 | 11kV | 14560 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141467 1 fault operation 3 phase No fault found. | July | 2014 | 2015Q1 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Veg | 2014-07-21 | N | 208 | N | 3 | N | N | 1.1101 | 39.4971 | 10640.0186
[7 empty] | 14222 | 16689 | 1133462 | 2014-07-22 06:41 | 2014-07-22 07:22 | 41 | 11kV | 3198 | 78 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn14892 Charmhaven section of Pa3 PT12656 Overview Gilbert 11kv roadside HDO 31.5Amp fuse failed Suspect fuse failure. See 1134651 exclude 1133462,3 | July | 2014 | 2015Q1 | 2015 | ZN14892:PA3 | ZN14892:PA3 | ZN14892/000003 | CENTRAL COAST | OH | Not Veg | 2014-07-22 | N | 41 | N | 5 | N | N | 1.1101 | 39.4971 | 2337.0041
[7 empty] | 13255 | 8790 | 1133941 | 2014-07-22 11:30 | 2014-07-22 12:20 | 50 | 11kV | 100 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 141479 section isolated to repair xarm at pole GW-87006 | July | 2014 | 2015Q1 | 2015 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2014-07-22 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 73.0771
[7 empty] | 12863 | 5650 | 1133617 | 2014-07-22 10:55 | 2014-07-22 13:34 | 159 | 11kV | 15108 | 280 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 141481 SW 50356 OPENED BY S.O.AFTER REPORT OF LOW MAINS AT HINTON RD. (SEE LID No 141477/OMS 1133954) Vehicle hit pole JR-12413 near 694 Hinton Road Hinton | July | 2014 | 2015Q1 | 2015 | 238:34141 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2014-07-22 | N | 53.9571 | N | 5 | N | N | 1.1101 | 39.4971 | 11040.4808
[7 empty] | 14112 | 15892 | 1133904 | 2014-07-22 19:48 | 2014-07-22 22:40 | 172 | 11kV | 2064 | 12 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn14891 Wyong seciton of Pa20 PT11792 Sandra Hue Hue the footpath side 11kv HDO fuse operated. 20Amps Fuse Fatigue See 1134657 exclude 1133904,5 | July | 2014 | 2015Q1 | 2015 | ZN14891:PA20 | ZN14891:PA20 | ZN14891/000020 | CENTRAL COAST | OH | Not Veg | 2014-07-22 | N | 172 | N | 5 | N | N | 1.1101 | 39.4971 | 1508.3103
[7 empty] | 12528 | 2551 | 1133923 | 2014-07-22 22:30 | 2014-07-22 23:30 | 60 | 11kV | 540 | 9 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141483 Isolate to repair tapping | July | 2014 | 2015Q1 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2014-07-22 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 394.6161
[7 empty] | 12840 | 5431 | 1134371 | 2014-07-23 17:05 | 2014-07-23 18:40 | 95 | 11kV | 10165 | 107 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | Ex Zn14891 Wyong Zone section of Pa16 "Figtree Orchard" Feeder from USL40139 to LB45068 tee to PT13098 & 11813 11kv fdr in grave danger of falling to ground in tuggerawong rd. reported by lineworkers See 1134663 exclude 1134371,3 | July | 2014 | 2015Q1 | 2015 | ZN14891:PA16 | ZN14891:PA16 | ZN14891/000016 | CENTRAL COAST | OH | Not Veg | 2014-07-23 | N | 95 | N | 4 | N | N | 1.1101 | 39.4971 | 7428.2822
[7 empty] | 14328 | 17369 | 1134390 | 2014-07-23 18:07 | 2014-07-23 19:47 | 100 | 11kV | 57560 | 585 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 10993 Hurstville North - Pnl 6 - C phase IOC and timed OC, EFI, Field EFIs. Section of UG feeder failed between S 10821, S 10197 and S 10836. ME: 1134502. Rest Step: 1134504, 5. ME GIS: 1134393. Withdrawn: 1134390, 4. | July | 2014 | 2015Q1 | 2015 | ZN10993:PA6 | ZN10993:PA26 | ZN10993/000026 | GEORGES RIVER | UG | Not Veg | 2014-07-23 | N | 98.3932 | N | 4 | N | N | 1.1101 | 39.4971 | 42063.1503
[7 empty] | 13393 | 10106 | 1134387 | 2014-07-23 17:56 | 2014-07-23 20:16 | 140 | 11kV | 41440 | 296 | HV | Equipment Failed in Service | Equipment Failure | O/H Link | Unplanned | Unselected | N | Zn14891 Wyong Pa5 "Wyong" fdr tripped on SEL ABNORMAL: AB43928 open LB61946 closed (sht.4 B9) USL 44800 found not fully closed NB isolation point for work ealier today See 1134668,9 exclude 1134387 | July | 2014 | 2015Q1 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-07-23 | N | 140 | N | 4 | N | N | 1.1101 | 39.4971 | 30283.1297
[7 empty] | 12850 | 5554 | 1134419 | 2014-07-23 20:55 | 2014-07-23 22:36 | 101 | 11kV | 158245 | 1637 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn36300 Balgowlah North Pa8 tripped on: relays: B & C phase overcurrnet Signals: 11kv trip DOps investigated "OMS Hazards" could not find any problems See 1134717,8,9,20 LV// 1134731 Exclude 1134419,20,1,3,4,5 | July | 2014 | 2015Q1 | 2015 | ZN36300:PA8 | ZN36300:PA8 | ZN36300/000008 | NORTHERN BEACHES | OH | Veg | 2014-07-23 | N | 96.6677 | N | 4 | N | N | 1.1101 | 39.4971 | 115640.7786
[7 empty] | 14078 | 15653 | 1134939 | 2014-07-25 08:31 | 2014-07-25 15:05 | 394 | 11kV | 1575.1667 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141528 C phase DOLF Cph Burnt up DOLF Carrier replaced. Excluded OMS OMS# 1134939 CC1: 06-"Urgent - O.H Mains - No others" CC2: 22-"Refer to SOp" FRC1: 366-"Defective (Mechanical) High Voltage Drop-Out Fuse - Requires repair/replacement" FRC2: 366-"Defective (Mechanical) High Voltage Drop-Out Fuse - Requires repair/replacement" | July | 2014 | 2015Q1 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2014-07-25 | N | 393.7917 | N | 3 | N | N | 1.1101 | 39.4971 | 1151.0853
[7 empty] | 14518 | 18827 | 1135150 | 2014-07-25 15:09 | 2014-07-25 17:01 | 112 | 11kV | 82880 | 740 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Pnl 15L beyong AB2110 Remarks: 11kv bonds off on center phase load side of AB 2110 | July | 2014 | 2015Q1 | 2015 | ZN35800:PA15 | ZN35800:PA7 | ZN35800/000007 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-07-25 | N | 112 | N | 3 | N | N | 1.1101 | 39.4971 | 60566.2595
[7 empty] | 13421 | 10338 | 1135811 | 2014-07-26 01:07 | 2014-07-26 01:24 | 17 | 11kV | 262 | 116 | HV | Lightning Strike | Adverse Weather/Environment | DC PT | Unplanned | Electrical Storm | N | LID 141535 1 fault operation A & C phase Overcurrent Emerg switching feeding Fdr 74179. See report 141533/OMS 1135807 | July | 2014 | 2015Q1 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-07-26 | N | 2.2586 | N | 9 | N | N | 1.1101 | 39.4971 | 191.4619
[7 empty] | 12377 | 1155 | 1135240 | 2014-07-26 00:27 | 2014-07-26 04:08 | 221 | 11kV | 43897 | 204 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 141534 4 fault operations A & B phase Overcurrent Removed tree branch at Denman Rd RAGCB | July | 2014 | 2015Q1 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-07-26 | N | 215.1814 | N | 9 | N | N | 1.1101 | 39.4971 | 32078.6329
[7 empty] | 12432 | 1675 | 1135243 | 2014-07-26 04:50 | 2014-07-26 05:57 | 67 | 11kV | 77988 | 1164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | @Zn12570 Avoca Pa40 "Davistown" fdr tripped & locked out on Relays: C & B phase overcurrent, lockout Signals: 11kv trip DOp removed branch from 11kv overhead near AB44586 | July | 2014 | 2015Q1 | 2015 | ZN12570:PA40 | ZN12570:PA40 | ZN12570/000040 | CENTRAL COAST | OH | Veg | 2014-07-26 | N | 67 | N | 9 | N | N | 1.1101 | 39.4971 | 56991.3301
[7 empty] | 14145 | 16161 | 1135272 | 2014-07-26 07:37 | 2014-07-26 08:41 | 64 | 11kV | 49408 | 772 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Zn12570 Avoca section of Pa29 "'Scaysbrook Edmonson" fdr @ recloser 44982 tripped. Cause not ascertained. branches in huntley could have been cause See 1135271 Exclude 1135272,4 | July | 2014 | 2015Q1 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2014-07-26 | N | 64 | N | 9 | N | N | 1.1101 | 39.4971 | 36105.9091
[7 empty] | 14218 | 16645 | 1135255 | 2014-07-26 07:03 | 2014-07-26 08:43 | 100.1333 | 11kV | 81468 | 1405 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington - Pnl.17 tripped on: Earth Fault, EFI EFIs: S4194 50187 671 UG cable fault between S671, S36251 & S160 see 1135599 1135600 | July | 2014 | 2015Q1 | 2015 | ZN342:PA17 | ZN342:PA17 | ZN00342/000017 | WOOLLAHRA | UG | Not Veg | 2014-07-26 | N | 57.9843 | N | 9 | N | N | 1.1101 | 39.4971 | 59534.4115
[7 empty] | 12335 | 785 | 1135236 | 2014-07-25 22:42 | 2014-07-26 11:10 | 748 | 11kV | 40801 | 147 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | N | LID 141533 5 fault operations A & C phase Overcurrent Lightning struck pole 8L-90243 Excluded OMS 1135236, 1135251 & 1135342 | July | 2014 | 2015Q1 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-07-25 | N | 277.5578 | N | 3 | N | N | 1.1101 | 39.4971 | 29816.1674
[7 empty] | 14017 | 15116 | 1135244 | 2014-07-26 05:10 | 2014-07-26 14:50 | 580 | 11kV | 11020 | 19 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | N | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" fdr AB44471 interrupted. Lightning split 2 poles. Interrupted for safety See 1135267 Exclude 1135273 CC1: 22-"Refer to SOp" | July | 2014 | 2015Q1 | 2015 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2014-07-26 | N | 580 | N | 9 | N | N | 1.1101 | 39.4971 | 8053.091
[7 empty] | 12719 | 4314 | 1135295 | 2014-07-26 09:27 | 2014-07-26 15:40 | 373 | 11kV | 1119 | 3 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" @PT14982 Wise Ferry Larool road phase 20 Amp HDO fuse blown. Tree branch found resting on transformer tank See 1136210 exclude 135295 | July | 2014 | 2015Q1 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2014-07-26 | N | 373 | N | 9 | N | N | 1.1101 | 39.4971 | 817.7322
[7 empty] | 14323 | 17342 | 1135305 | 2014-07-26 09:51 | 2014-07-26 17:20 | 449 | 11kV | 13064 | 100 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa1 "Somersby" fdr Recloser 44995 Kulnura tripped & locked out Overhead down near PT11874 See 1136280,1 Exclude 1135305 | July | 2014 | 2015Q1 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-07-26 | N | 130.64 | N | 9 | N | N | 1.1101 | 39.4971 | 9546.7859
[7 empty] | 14550 | 19054 | 1135382 | 2014-07-26 13:34 | 2014-07-26 18:40 | 306 | 11kV | 1224 | 4 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 141537 C phase DOLF : 10 Amp C ph LA replaced. Excluded OMS# 1135382. | July | 2014 | 2015Q1 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-07-26 | N | 306 | N | 9 | N | N | 1.1101 | 39.4971 | 894.4631
[7 empty] | 12919 | 6105 | 1135459 | 2014-07-27 10:00 | 2014-07-27 12:00 | 120 | 11kV | 960 | 8 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 141539 Isolated to Repair damaged sub earth at sub 70926. Excluded OMS 1135459 | July | 2014 | 2015Q1 | 2015 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Not Veg | 2014-07-27 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 701.5397
[7 empty] | 13820 | 13402 | 1135482 | 2014-07-27 11:46 | 2014-07-27 17:00 | 314 | 11kV | 314 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141540 Single phase HV opened to make repair BURNT-UP LVF Assy. Excluded OMS 1135482 | July | 2014 | 2015Q1 | 2015 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | OH | Not Veg | 2014-07-27 | N | 314 | N | 5 | N | N | 1.1101 | 39.4971 | 229.4619
[7 empty] | 14340 | 17457 | 1135549 | 2014-07-27 18:25 | 2014-07-27 19:26 | 61 | 11kV | 43030 | 762 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ S874 Concord Zn Panel #3 labelled LLeewellyn St tripped on Earth fault EFI, 11kv trip, Field EFI's - All Remarks: UG fault. Section of 11kv feeder from S5826 Marquet Gauthorpe #1 SW B to Sub 8380 Marquet Gauthorpe #3 Sw A to Sub 7107 Marquet Gauthorpe #2 Sw A. | July | 2014 | 2015Q1 | 2015 | ZN874:PA3 | ZN874:PA3 | ZN00874/000003 | CANADA BAY | UG | Not Veg | 2014-07-27 | N | 56.4698 | N | 5 | N | N | 1.1101 | 39.4971 | 31445.0548
[7 empty] | 13612 | 11810 | 1135532 | 2014-07-27 16:26 | 2014-07-27 20:20 | 234 | 11kV | 114133 | 1521 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 141542 2 fault operations B phase Earth fault UGM fault at pole IU-31417 Excluded OMS 1135532, 1135535, 1135539, 1135543 & 1135564 | July | 2014 | 2015Q1 | 2015 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | UG | Not Veg | 2014-07-27 | N | 75.0381 | N | 5 | N | N | 1.1101 | 39.4971 | 83405.03
[7 empty] | 12775 | 4829 | 1135568 | 2014-07-27 20:01 | 2014-07-27 21:04 | 63 | 11kV | 74603 | 1526 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | @ Sub 1287 Revesby Zn Panel #3 labelled Mars Virginius tripped on sensitive Earth Lockout 11kv trip Abnormal: AB330 & ALB3276 defective Remarks: Bond. Road side bond at AB644 | July | 2014 | 2015Q1 | 2015 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-07-27 | N | 48.8879 | N | 5 | N | N | 1.1101 | 39.4971 | 54517.672
[7 empty] | 13900 | 14151 | 1135960 | 2014-07-28 17:26 | 2014-07-28 17:30 | 4 | 11kV | 440 | 110 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 141550 Related to outage report 141542/ OMS 1136160 Interruption to disconnect islanded generator. | July | 2014 | 2015Q1 | 2015 | 213:33771 | 213:33771 | ZN00213/033771 | NEWCASTLE | UG | Not Veg | 2014-07-28 | N | 4 | N | 4 | N | N | 1.1101 | 39.4971 | 321.539
[7 empty] | 14073 | 15592 | 1135973 | 2014-07-28 18:22 | 2014-07-28 18:57 | 35 | 11kV | 76762 | 3375 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Zn12570 Avoca Pa29 "North Avoca" fdr tripped and locked out Relays: SEL Signals: 11kv trip ABNORMAL: S61891:B closed with LK43385 Open 11kv centre phase flicker blade stuck closed @ Defective AB43387 after switching by DOp Recloser 44855 Lake Tram tripped on SE at same time See 1136305,6 Exclude 1135973,5,83 | July | 2014 | 2015Q1 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Not Veg | 2014-07-28 | N | 22.7443 | N | 4 | N | N | 1.1101 | 39.4971 | 56095.4055
[7 empty] | 13988 | 14825 | 1136017 | 2014-07-28 23:30 | 2014-07-29 00:22 | 52 | 11kV | 40664 | 782 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington - panel 35 tripped on : O/C and E/F Right Hand Side Front line feeder fault from panel 35 to S4371 (Sw A) to S1681 (Sw F) | July | 2014 | 2015Q1 | 2015 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2014-07-28 | N | 52 | N | 4 | N | N | 1.1101 | 39.4971 | 29716.0518
[7 empty] | 14291 | 17178 | 1136013 | 2014-07-28 22:31 | 2014-07-29 03:55 | 324 | 11kV | 131804 | 1667 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 141551 1 fault operation B phase Sensitive Earth Fault car hit pole JU-41701 bring down 11kV into LV Excluded OMS 1136013, 1136014, 1136018, 1136019 & 1136020 | July | 2014 | 2015Q1 | 2015 | 205:12205 | 205:12205 | ZN00205/012205 | LAKE MACQUARIE | OH | Not Veg | 2014-07-28 | N | 79.0666 | N | 4 | N | N | 1.1101 | 39.4971 | 96318.4756
[7 empty] | 12307 | 502 | 1136420 | 2014-07-29 21:21 | 2014-07-30 08:30 | 669 | 11kV | 88666 | 1854 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | LID 141570 Sw 80337 opened due fire at sub 55459 | July | 2014 | 2015Q1 | 2015 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | UG | Not Veg | 2014-07-29 | N | 47.8242 | N | 1 | N | N | 1.1101 | 39.4971 | 64794.4976
[7 empty] | 14022 | 15168 | 1136813 | 2014-07-30 20:49 | 2014-07-30 21:17 | 28 | 11kV | 59276 | 2117 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 141586 2 fault operations Overcurrent bat removed at pole JU-70352 | July | 2014 | 2015Q1 | 2015 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2014-07-30 | N | 28 | N | 1 | N | N | 1.1101 | 39.4971 | 43317.1525
[7 empty] | 12344 | 839 | 1137194 | 2014-07-31 16:50 | 2014-07-31 18:20 | 90 | 11kV | 1170 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Wind | N | LID 141600 Isolated for repairs Broken Xarm at sub 51133. | July | 2014 | 2015Q1 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-07-31 | N | 90 | N | 1 | N | N | 1.1101 | 39.4971 | 855.0015
[7 empty] | 14217 | 16636 | 1137265 | 2014-08-01 00:49 | 2014-08-01 01:56 | 67 | 11kV | 17688 | 264 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | Ex Zn12620 Noraville section of Pa11 @ Recloser 45050 Magenta tripped on IOC Cause: Possum at 11kv UGOH above S14581/SwB Evans Vietnam Hostel | August | 2014 | 2015Q1 | 2015 | ZN12620:PA11 | ZN12620:PA11 | ZN12620/000011 | CENTRAL COAST | OH | Not Veg | 2014-08-01 | N | 67 | N | 2 | N | N | 1.1101 | 39.4971 | 12925.8687
[7 empty] | 14285 | 17115 | 1137457 | 2014-08-01 12:05 | 2014-08-01 13:00 | 55 | 11kV | 3400 | 64 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | Ex Zn12660 Woy WOy section of Pa5 "Fassifern Picnic" Feeder btw LB41713 to LB62074 tee PT11014 & PT13414 interrupted for ermergency repairs to 11kV OH OH resting on cross arm See 1138502,3 Exclude 1137457,9,67,9 | August | 2014 | 2015Q1 | 2015 | ZN12660:PA5 | ZN12660:PA5 | ZN12660/000005 | CENTRAL COAST | OH | Not Veg | 2014-08-01 | N | 53.125 | N | 2 | N | N | 1.1101 | 39.4971 | 2484.6197
[7 empty] | 13273 | 8940 | 1137633 | 2014-08-02 02:21 | 2014-08-02 04:40 | 139 | 11kV | 46150 | 685 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 7 - C phase IOC, EFI. DOp patrolled and found nothing. LV// in place for PT 9593. ME: 1137633. Withdrawn: 1137635. | August | 2014 | 2015Q1 | 2015 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Veg | 2014-08-02 | N | 67.3723 | N | 2 | N | N | 1.1101 | 39.4971 | 33725.0588
[7 empty] | 13479 | 10765 | 1137749 | 2014-08-02 19:23 | 2014-08-02 21:44 | 141 | 11kV | 116539 | 844 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn35600 Kingsford ex pnl.4 - S2582 Anzac Wal 11kV CB "p" tripped on Earth Fault, EFI (feeder to S50034, S970) UG cable fault - fire in pitt outside 21 Bunnerong Rd/Stuart St. Pitt lid blown off, UG on-call notified. Smell of gas in pitt by DOp/Jointer, fire bridage notified. 11kV feeder from S2582 to S970 to S30034 isolated and earthed see 1137947 1137761 | August | 2014 | 2015Q1 | 2015 | ZN35600:PA4 | ZN35600:PA4 | ZN35600/000004 | RANDWICK | UG | Not Veg | 2014-08-02 | N | 138.0794 | N | 2 | N | N | 1.1101 | 39.4971 | 85163.2639
[7 empty] | 12508 | 2332 | 1137773 | 2014-08-03 00:13 | 2014-08-03 01:47 | 94 | 11kV | 14990 | 161 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 141624 4 fault operations A phase Earth fault Cable fault behind no.7 peppertree drive on McDonald road. | August | 2014 | 2015Q1 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | UG | Not Veg | 2014-08-03 | N | 93.1056 | N | 5 | N | N | 1.1101 | 39.4971 | 10954.2499
[7 empty] | 12894 | 5917 | 1137785 | 2014-08-03 07:11 | 2014-08-03 09:40 | 149 | 11kV | 191194 | 1744 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn15006 Dee Why Pa8 "Narraweena" fdr tripped relays: SEL & EFISignals: 11kv trip 11kv centre phase bond off LK20956. See 1138660,3,4 Exclude 1137785,6,7 | August | 2014 | 2015Q1 | 2015 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2014-08-03 | N | 109.6296 | N | 5 | N | N | 1.1101 | 39.4971 | 139718.9359
[7 empty] | 13463 | 10661 | 1137747 | 2014-08-03 10:29 | 2014-08-03 11:47 | 78 | 11kV | 5772 | 74 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex ZN12660 Woy Woysection of Pa8 "North Burge Rd" @ PT47206 Camellia Sonter 63.5A HDO blew. 10:29 DOp/Staff reported blew. Customer report Low Volts 19:20 2/8/14. Suspect HV Amp blown earlier than DOp/staff report time. See 1138528 exclude 1137747,829,37 | August | 2014 | 2015Q1 | 2015 | ZN12660:PA8 | ZN12660:PA8 | ZN12660/000008 | CENTRAL COAST | OH | Not Veg | 2014-08-03 | N | 78 | N | 5 | N | N | 1.1101 | 39.4971 | 4218.0074
[7 empty] | 13063 | 7340 | 1137845 | 2014-08-03 13:16 | 2014-08-03 15:32 | 136 | 11kV | 119634 | 1072 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | @ZN847 Hornsby - 11kv Panel No.22 "Sub 6373 Hunter Bridge West" feeder trippedd Relays: A and C phase timed O/C, EFI, Fault Check Signals: 11kv trip, Zone earth, No.2 Group earth, No.2 Tx prot U/V, No.1 Tx cooling supply fail Field EFI's: S6373, S5996, S8248, S5159, S35034 Remarks: Cause not ascertained. Dop patrolled extent of feede, unable to locate cause | August | 2014 | 2015Q1 | 2015 | ZN847:PA22 | ZN847:PA22 | ZN00847/000022 | HORNSBY | OH | Not Veg | 2014-08-03 | N | 111.5989 | N | 5 | N | N | 1.1101 | 39.4971 | 87424.9986
[7 empty] | 12811 | 5109 | 1137883 | 2014-08-03 18:20 | 2014-08-03 19:35 | 75 | 11kV | 10500 | 140 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT1477 Cobham Lancaster 50k footpath HDO operated Section of 11kv feeder Panel No25 "CP337 etc" Ex S4545 Meadowbank Remarks: Fuse failure. At PT1477 Cobham Lancaster 50k footpath HDO operated, no cause found. Susupect LV parallel at the time with S48977 Dist 1 | August | 2014 | 2015Q1 | 2015 | ZN4545:PA25 | ZN4545:PA25 | ZN04545/000025 | RYDE | OH | Not Veg | 2014-08-03 | N | 75 | N | 5 | N | N | 1.1101 | 39.4971 | 7673.0903
[7 empty] | 12957 | 6500 | 1138264 | 2014-08-04 16:40 | 2014-08-04 17:15 | 35 | 11kV | 105 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa5 @PT12117 Jilliby Durren T/Con reported C phase fuse carrier bolt has broken aqa from cross arm. Carrier and fuse were hanging very close to B phase requiring urgent repair. See 1138626 exclude 1138264 | August | 2014 | 2015Q1 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-08-04 | N | 35 | N | 4 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 14441 | 18237 | 1138286 | 2014-08-04 16:25 | 2014-08-04 17:43 | 78.45 | 11kV | 52404.6 | 668 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn36200 Empire Bay Pa8 fdr AB43265 burnt off bond footpath side See 1138286 exclude 1138297 | August | 2014 | 2015Q1 | 2015 | ZN36200:PA8 | ZN36200:PA8 | ZN36200/000008 | CENTRAL COAST | OH | Not Veg | 2014-08-04 | N | 78.45 | N | 4 | N | N | 1.1101 | 39.4971 | 38295.736
[7 empty] | 14189 | 16419 | 1138319 | 2014-08-04 17:15 | 2014-08-04 19:00 | 105 | 11kV | 105 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 141631 A phase DOLF : 20 Amp sub isolated to replace la Excluded oms 1138319 | August | 2014 | 2015Q1 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | MUSWELLBROOK | OH | Not Veg | 2014-08-04 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 14019 | 15162 | 1138349 | 2014-08-04 20:16 | 2014-08-05 00:01 | 225 | 11kV | 1350 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141632 A phase DOLF : 16 Amp excluded job OMS 1138349 | August | 2014 | 2015Q1 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-08-04 | N | 225 | N | 4 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 14347 | 17523 | 1138423 | 2014-08-05 08:53 | 2014-08-05 10:50 | 117 | 11kV | 117 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141640 Single phase DOLF : 10 Amp Fuse broke due to fatigue. TX Volts: 247V Excluded OMS No. 1138423 | August | 2014 | 2015Q1 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-08-05 | N | 117 | N | 7 | N | N | 1.1101 | 39.4971 | 85.5001
[7 empty] | 12562 | 2943 | 1138466 | 2014-08-05 10:00 | 2014-08-05 11:27 | 87 | 11kV | 174 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141641 C phase DOLF : 63 Amp Excluded OMS 1138466 | August | 2014 | 2015Q1 | 2015 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2014-08-05 | N | 87 | N | 7 | N | N | 1.1101 | 39.4971 | 127.1541
[7 empty] | 14484 | 18561 | 1138370 | 2014-08-05 06:58 | 2014-08-05 13:30 | 392 | 11kV | 1960 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT2054 Peebles Mathie Property HV dropout fuse failed : Fatigue HV Fuse details: ABB 16Amp (BN22343) - Footpath Phase See OMS 1139103 1138371 1138370 | August | 2014 | 2015Q1 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2014-08-05 | N | 392 | N | 7 | N | N | 1.1101 | 39.4971 | 1432.3102
[7 empty] | 13573 | 11491 | 1138644 | 2014-08-05 13:40 | 2014-08-05 16:11 | 151 | 11kV | 114358 | 818 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12570 Avoca section pa29 "Bensville" fdr @REcloser 44982 Bensville tripped & Locked out Relays: SEF trip, L/O Section of 11kv fdr below RE44982 patrolled no cause found 11kv B phase bond burnt off at AB42501 See 1138886 Exclude 1138644,55,9,70,84 | August | 2014 | 2015Q1 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Not Veg | 2014-08-05 | N | 139.802 | N | 7 | N | N | 1.1101 | 39.4971 | 83569.4534
[7 empty] | 12708 | 4208 | 1138728 | 2014-08-05 16:20 | 2014-08-05 17:45 | 85 | 11kV | 1105 | 13 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 141645 3 phase SECTION ISOLATED TO REPAIR X-ARM AT POLE 6O-40027 | August | 2014 | 2015Q1 | 2015 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2014-08-05 | N | 85 | N | 7 | N | N | 1.1101 | 39.4971 | 807.5014
[7 empty] | 14503 | 18722 | 1138826 | 2014-08-05 22:46 | 2014-08-06 09:52 | 666 | 11kV | 102236 | 1072 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @S3922 Drummoyne Panel 17 "S35126 Jersey Barnstaple" feeder tripped on Relays - Timed EF, Fault Check, EFI Signals - 11kv trip, ZE, TX2 GE Field operated @ S35126, S1563, S47482 Remarks: UG fault. Underground feeder fault in the submarine cable from S.47482 Nelson Darling to S.8366 Cockatoo Island No.2 | August | 2014 | 2015Q1 | 2015 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2014-08-05 | N | 95.3694 | N | 7 | N | N | 1.1101 | 39.4971 | 74711.0533
[7 empty] | 12758 | 4654 | 1138719 | 2014-08-05 15:49 | 2014-08-06 12:27 | 1238 | 11kV | 1238 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | Sub isolated after again blowing HV fuses Excluded OMS 1138719 | August | 2014 | 2015Q1 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Not Veg | 2014-08-05 | N | 1238 | N | 7 | N | N | 1.1101 | 39.4971 | 904.6939
[7 empty] | 13926 | 14427 | 1139741 | 2014-08-08 10:34 | 2014-08-08 11:26 | 52 | 11kV | 61672 | 1186 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex ZN 10990 Arncliffe - Pnl 11 - ABS 31271. Roadside phase bond burnt off at AB 31271. Now the switch is not working at all. ME: 1140280. Withdrawn: 1139741. | August | 2014 | 2015Q1 | 2015 | ZN10990:PA11 | ZN10998:PA17 | ZN10998/000017 | BAYSIDE | OH | Not Veg | 2014-08-08 | N | 52 | N | 2 | N | N | 1.1101 | 39.4971 | 45068.0786
[7 empty] | 13011 | 6883 | 1139964 | 2014-08-08 22:15 | 2014-08-09 01:46 | 211 | 11kV | 295821 | 2482 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141682 5 fault operations 3 phase Overcurrent; Earth fault wires on ground at pole HR-92040 Excluded oms 1139964 | August | 2014 | 2015Q1 | 2015 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2014-08-08 | N | 119.1865 | N | 2 | N | N | 1.1101 | 39.4971 | 216177.2616
[7 empty] | 14336 | 17449 | 1139977 | 2014-08-09 06:15 | 2014-08-09 08:15 | 120 | 11kV | 67125 | 981 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | At S35900 Potts Hill Panel #20 "Muir Dasea" fdr tripped on: - Relays 50TN-efc. 51N -ef Reclose Lockout. EFIs down @35899-4314-4955-8991-4474-4475 Remarks: Vehicle hit pole. HV UG pole hit by vehicle in Powell St Lagoona. On switching AB 505 closed on 2 phases only & top down rod broke. Subs to check S7129 Clarmont Brunker #2 as EFI did not operate | August | 2014 | 2015Q1 | 2015 | ZN35900:PA20 | ZN35900:PA20 | ZN35900/000020 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-08-09 | N | 68.4251 | N | 4 | N | N | 1.1101 | 39.4971 | 49052.9701
[7 empty] | 13502 | 10954 | 1140359 | 2014-08-09 13:23 | 2014-08-09 13:46 | 23 | 11kV | 805 | 35 | HV | Staff Other | Utility Process Issue | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | Zn3288 City South - 41/42 K CB tripped on: 41/42K Buchholz trip During work @ S6873 market City No2, vibration has caused feeder to trip see 1140359 1140361 | August | 2014 | 2015Q1 | 2015 | ZN3288:PA41 42KLM | ZN3288:PA41 42KLM | ZN03288/41 42KLM | SYDNEY | UG | Not Veg | 2014-08-09 | N | 23 | N | 4 | N | N | 1.1101 | 39.4971 | 588.2703
[7 empty] | 13309 | 9202 | 1140004 | 2014-08-09 10:50 | 2014-08-09 14:20 | 210 | 11kV | 14070 | 129 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141683/02 11kv main on ground between sub 1028 & sub 54002. Excluded OMS 1140452, 1140004 & 1140066 | August | 2014 | 2015Q1 | 2015 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2014-08-09 | N | 109.0698 | N | 4 | N | N | 1.1101 | 39.4971 | 10281.941
[7 empty] | 12605 | 3251 | 1140052 | 2014-08-09 21:25 | 2014-08-09 22:20 | 55 | 11kV | 75020 | 1364 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | On Panel 12 - C phase bond off on AB 101 CP50006 marion Wilkins. No protection operations. Remarks: Bond. High Voltage bond burnt off on zone side of AB101 C phase road side. | August | 2014 | 2015Q1 | 2015 | ZN1850:PA12 | ZN35800:PA1 | ZN35800/000001 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-08-09 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 54822.4033
[7 empty] | 12459 | 1833 | 1140125 | 2014-08-10 05:01 | 2014-08-10 07:00 | 119 | 11kV | 2618 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141690 A & B phase DOLF : 16 Amp Excluded OMS 1140125 | August | 2014 | 2015Q1 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-08-10 | N | 119 | N | 2 | N | N | 1.1101 | 39.4971 | 1913.1572
[7 empty] | 13070 | 7396 | 1140225 | 2014-08-10 22:04 | 2014-08-11 00:45 | 161 | 11kV | 966 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 14696 B phase DOLF : 16 Amp readings 250v & 17, 24, 0 amps Excluded oms # 1140225 & 1140227 | August | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-08-10 | N | 161 | N | 2 | N | N | 1.1101 | 39.4971 | 705.9243
[7 empty] | 12615 | 3329 | 1140722 | 2014-08-11 22:25 | 2014-08-12 11:15 | 770 | 11kV | 2310 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141719 LLC Hanging at pole 7L-80287, Tee off to sub 70516 Jaben Pasteral Sub. No Protection Operation Excluded OMS 1140722 | August | 2014 | 2015Q1 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-08-11 | N | 770 | N | 1 | N | N | 1.1101 | 39.4971 | 1688.0799
[7 empty] | 13674 | 12337 | 1141172 | 2014-08-12 21:46 | 2014-08-12 22:20 | 34 | 11kV | 22848 | 672 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn12570 Avoca section of panel 22 "Davies Wilma" recloser 46529 labelled "Davidston Mundora tripped and locked out on overcurrent Tree Branch on mains outside 93 Broadwater rd See 1141172 Exclude 1141173,84 | August | 2014 | 2015Q1 | 2015 | ZN12570:PA22 | ZN12570:PA22 | ZN12570/000022 | CENTRAL COAST | OH | Veg | 2014-08-12 | N | 34 | N | 2 | N | N | 1.1101 | 39.4971 | 16696.6445
[7 empty] | 12768 | 4711 | 1141186 | 2014-08-12 22:17 | 2014-08-13 01:15 | 178 | 11kV | 111759 | 1412 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S.180 Mosman, Panel 19 Fdr CB tripped on C phase IOC and timed OC, efi, fault check and #1 Tx group earth, 11kv trip. UG fault on the section of UG feeder from S.2001 Sw 'B' to S.2780 Sw 'A' to S.1627 Sw 'B' | August | 2014 | 2015Q1 | 2015 | ZN180:PA19 | ZN180:PA19 | ZN00180/000019 | NORTH SYDNEY | UG | Not Veg | 2014-08-12 | N | 79.1494 | N | 2 | N | N | 1.1101 | 39.4971 | 81670.1809
[7 empty] | 13496 | 10923 | 1141246 | 2014-08-13 08:30 | 2014-08-13 08:40 | 10 | 11kV | 1000 | 100 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | Unselected | N | Planned LID 141724 SINO SRR 1512 The customers were not notified of planned outage. The job was then cancelled and customers reinstated | August | 2014 | 2015Q1 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2014-08-13 | N | 10 | N | 5 | N | N | 1.1101 | 39.4971 | 730.7705
[7 empty] | 14684 | 20407 | 1141311 | 2014-08-13 09:57 | 2014-08-13 11:40 | 103 | 11kV | 66226 | 706 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S2196 Milperra, feeder panel No.21 Marigold Malleys fdr tripped on A phase timed overcurrent and earth leakage. EFI's down at S4319, S35794 and S5434 Remarks: UG fault. Suspected underground feeder fault from S5434 Greenway Pde to S2254 Queen Car No.1 to S5433 Queen Beaconsfield. | August | 2014 | 2015Q1 | 2015 | ZN2196:PA21 | ZN2196:PA21 | ZN02196/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-08-13 | N | 93.8045 | N | 5 | N | N | 1.1101 | 39.4971 | 48396.0075
[7 empty] | 14206 | 16543 | 1141546 | 2014-08-13 14:58 | 2014-08-13 17:13 | 135.2167 | 11kV | 135.2167 | 1 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | wire down cut away and made safe - cut branch CC1: 06-"Urgent - O.H Mains - No others" CC2: 23-"Mains Required" FRC1: 334-"Overhead Service Line Down - Cut away and made safe" FRC2: 334-"Overhead Service Line Down - Cut away and made safe" FRC3: 300-"Specify details by voice" | August | 2014 | 2015Q1 | 2015 | ZN9301:PA13 | ZN9118:PA22 | ZN09118/000022 | SUTHERLAND | OH | Veg | 2014-08-13 | N | 135.2167 | N | 5 | N | N | 1.1101 | 39.4971 | 98.8124
[7 empty] | 14301 | 17227 | 1141646 | 2014-08-13 19:00 | 2014-08-13 20:05 | 64.8333 | 11kV | 2269.1667 | 35 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | LID 141736 incorrect of auto link - fell open. left bypassed Excluded oms 1141650 | August | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-08-13 | N | 64.8333 | N | 5 | N | N | 1.1101 | 39.4971 | 1658.2401
[7 empty] | 12373 | 1106 | 1141623 | 2014-08-13 19:27 | 2014-08-14 03:50 | 503 | 11kV | 26659 | 53 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | At PT1008 Gros Game Supply interrupted Tree brought down OH in Grosvenor Rd Lindfield. See OMS 1141652 1141623 1141625 CC1: 22-"Refer to SOp" | August | 2014 | 2015Q1 | 2015 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | KU-RING-GAI | OH | Veg | 2014-08-13 | N | 503 | N | 5 | N | N | 1.1101 | 39.4971 | 19481.6109
[7 empty] | 12482 | 2069 | 1141703 | 2014-08-14 08:17 | 2014-08-14 08:26 | 9 | 11kV | 2079 | 231 | HV | Staff Operation | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 141738 Operator error See planned SI 1539 (Meant to be live line work however customers were interrupted) Excluded OMS 1141703 | August | 2014 | 2015Q1 | 2015 | 801:74123 | 801:74123 | ZN00801/074123 | MUSWELLBROOK | OH | Not Veg | 2014-08-14 | N | 9 | N | 1 | N | N | 1.1101 | 39.4971 | 1519.2719
[7 empty] | 13705 | 12579 | 1142078 | 2014-08-15 04:40 | 2014-08-15 07:38 | 178 | 11kV | 9203 | 1592 | HV | Animal Bird | Animal | Bond | Unplanned | Unselected | N | zn12570 Avoca Pa39 "North Avoca" fdr tripped and reclosed Relays - EF, EFI Signals: 11kv trip EFI's S14134 S18035 S18036 Roadside HV bond burnt off UGOH near LB45056 @ Pole AV538 See 1143302,3 Exclude 1142078 | August | 2014 | 2015Q1 | 2015 | ZN12570:PA39 | ZN12570:PA39 | ZN12570/000039 | CENTRAL COAST | OH | Not Veg | 2014-08-15 | N | 5.7808 | N | 2 | N | N | 1.1101 | 39.4971 | 6725.281
[7 empty] | 12859 | 5640 | 1142396 | 2014-08-15 16:30 | 2014-08-15 18:20 | 110 | 11kV | 770 | 7 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 141767 Interruption was required to repair faulty 11kV cross arm. No protection operations occurred. | August | 2014 | 2015Q1 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-08-15 | N | 110 | N | 2 | N | N | 1.1101 | 39.4971 | 562.6933
[7 empty] | 14689 | 20440 | 1142611 | 2014-08-17 00:27 | 2014-08-17 02:12 | 105 | 11kV | 25109 | 242 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | CP421 Crosslands Rd Tripped and locked out on O/C CP420 Reynolds Crosslands Opened and Reclosed on O/C Cause Not ascertained - Mains to patrol. Protection did not grade. See OMS 1143893 1143894 1142611 1142612 | August | 2014 | 2015Q1 | 2015 | ZN847:PA45 | ZN847:PA45 | ZN00847/000045 | HORNSBY | OH | Veg | 2014-08-17 | N | 103.7562 | N | 4 | N | N | 1.1101 | 39.4971 | 18348.9166
[7 empty] | 13879 | 13926 | 1142602 | 2014-08-16 23:12 | 2014-08-17 02:30 | 198 | 11kV | 294858 | 2961 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | At ZN1850 Bass Hill: 11KV feeder Panel No 13 "Edgar Marion" Tripped Relays: Timed E/F, EFI Signals: 11kv trip, Zone earth, No3 Grp Earth+ Field EFIs: S4312, S4434 Remarks: UG fault. 11kv feeder failure between S4434 Curtin Sim Sw/B to S8894 Taylor Norman Sw/A. In attempt of restoring and Opening 11kv AB821 failed on opening, parts of damaged insulator fell onto vehicle Toyota Hilux Rego: BS54GP, Dop left note to contact Ausgrids. See separate DMA 17/8 | August | 2014 | 2015Q1 | 2015 | ZN1850:PA13 | ZN1850:PA41 | ZN01850/000041 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-08-16 | N | 99.5805 | N | 1 | N | N | 1.1101 | 39.4971 | 215473.5296
[7 empty] | 14638 | 20063 | 1142617 | 2014-08-17 03:53 | 2014-08-17 08:20 | 267 | 11kV | 6942 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 141776 A phase DOLF : 16 Amp excluded OMS 1142617, 1142624, 1142626, 1142628 | August | 2014 | 2015Q1 | 2015 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2014-08-17 | N | 267 | N | 4 | N | N | 1.1101 | 39.4971 | 5073.0088
[7 empty] | 12461 | 1836 | 1142679 | 2014-08-17 11:03 | 2014-08-17 12:35 | 92 | 11kV | 92 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 141777 Single phase DOLF : 10 Amp Excluded OMS 1142679 | August | 2014 | 2015Q1 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2014-08-17 | N | 92 | N | 4 | N | N | 1.1101 | 39.4971 | 67.2309
[7 empty] | 13802 | 13293 | 1142662 | 2014-08-17 14:45 | 2014-08-17 16:30 | 105 | 11kV | 3465 | 33 | HV | Unselected | Unknown (CASS) | Pole | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Panel 2 fdr from LB44275 to LK41374 tee to PT18790, PT14866 PT13986 PT14479. Interrupted by DOp to allow lineworker to repair 11kv Pole damaged by vehicle See 1143408 exclude 1142724; 1142662 | August | 2014 | 2015Q1 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2014-08-17 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 2532.1198
[7 empty] | 13851 | 13688 | 1142789 | 2014-08-18 05:03 | 2014-08-18 06:10 | 67 | 11kV | 87851 | 1397 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | @S269 Waverly Panel 2 "S2311 New Old" feeder tripped on Relays - EF, EFI Signals: 11kv trip, Tx4 GE, ZE Field EFIS operated @ S35813, S3256 (EFI not working @ S2311 NEW OLD) Remarks: 11kv UG cable faulty from S3256 Birriga Bund to S185 Birriga Rd to S7897 Bonus Murriverie | August | 2014 | 2015Q1 | 2015 | ZN269:PA2 | ZN36100:PA21 | ZN36100/000021 | WOOLLAHRA | UG | Not Veg | 2014-08-18 | N | 62.8855 | N | 10 | N | N | 1.1101 | 39.4971 | 64198.9196
[7 empty] | 13054 | 7206 | 1142916 | 2014-08-18 09:25 | 2014-08-18 10:30 | 65 | 11kV | 70265 | 1081 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At S1673 Turramurra Panel 6 tripped on Relays: IOC and A and B phase EFI with fault check Field EFI's Nil Signals: 11kV trip Dop patrolled feeder and no fault found. | August | 2014 | 2015Q1 | 2015 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2014-08-18 | N | 65 | N | 10 | N | N | 1.1101 | 39.4971 | 51347.5895
[7 empty] | 13446 | 10543 | 1142792 | 2014-08-18 06:18 | 2014-08-18 11:30 | 312 | 11kV | 1128 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | @ZN 2196 Milperra Panel 21 'Marigold Malleys' fdr tripped on: Relays: A & C O/C & EFI Signals: 11kv trip, Tx2 and Zn earths, Battery and oil separator defect Remarks: End box fault @ S4319 Marigold Malleys on the SW B side. | August | 2014 | 2015Q1 | 2015 | ZN2196:PA21 | ZN2196:PA21 | ZN02196/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-08-18 | N | 125.3333 | N | 10 | N | N | 1.1101 | 39.4971 | 824.3091
[7 empty] | 12659 | 3827 | 1143076 | 2014-08-18 10:54 | 2014-08-18 11:56 | 62 | 11kV | 54064 | 872 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | S384 Camperdown Panel 2 "Ross Parramatta" fdr tripped Relays - Earth Fault, EFI Signals: Tx5 group Earth, 5kV trip Remarks: UG fault. Front line feeder fault from Panel 2 to S5378 Ross Parramatta Sw/A | August | 2014 | 2015Q1 | 2015 | ZN384:PA2 | ZN384:PA2 | ZN00384/000002 | SYDNEY | UG | Not Veg | 2014-08-18 | N | 62 | N | 10 | N | N | 1.1101 | 39.4971 | 39508.3766
[7 empty] | 13967 | 14679 | 1142823 | 2014-08-18 08:18 | 2014-08-18 12:04 | 226 | 11kV | 111831.5 | 711 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn35900 Potts Hill Panel 12 'Muir Worth' fdr tripped on: Relays: Earth fault, EFI Signals: 11kv CB 12 protection trip, sub station protection trip lacked Field EFI's: S8675, S3274, S4110 Remarks: See seperate interruption on Pnl 16 Potts Hill for try back from Sub 4397 Brunker Coop. EFI @ Sub 4469 Larien Cres Faulty did not indicate. Section of OH out of service and under A/P Trans Lineworkers. From AB1709 1709 to Sub 4437 Cooper Marmion to Sub 7852 Auburn Morris to Sub 7213 Gunya Auburn. | August | 2014 | 2015Q1 | 2015 | ZN3472:PA15 | ZN35900:PA2 | ZN35900/000002 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-08-18 | N | 157.2876 | N | 10 | N | N | 1.1101 | 39.4971 | 81723.1617
[7 empty] | 13890 | 14008 | 1143001 | 2014-08-18 10:10 | 2014-08-18 12:40 | 149.7333 | 11kV | 58845.2 | 393 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Ex Zn10999 Kogarah Zone section of Pa22L "Argyle Wilson" Feeder below S10451 sw/B to S10067 to AB30019. 11kv UGOH open circuit B/cengtre phase between S10451 Swb/ to AB31262 | August | 2014 | 2015Q1 | 2015 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | Unknown | Unknown | 2014-08-18 | N | 149.7333 | N | 10 | N | N | 1.1101 | 39.4971 | 43002.3365
[7 empty] | 14665 | 20240 | 1143079 | 2014-08-18 14:12 | 2014-08-18 16:36 | 144 | 11kV | 224218 | 1818 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | Zn690 Campsie Pa18 "Canterbury Hospital" tripped on Relays: Earth Fault Signals: EFI, FC EFI's S1346 S1688 S8056 S5608 11kv fdr fault between S5608swB to S2947swA to S356swB to S274swA See 1144091,3,4,5 GIS 1143341 Exclude 1143079,339,44,68,75,9,428,33 | August | 2014 | 2015Q1 | 2015 | ZN690:PA18 | ZN690:PA18 | ZN00690/000018 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-08-18 | N | 123.3322 | N | 10 | N | N | 1.1101 | 39.4971 | 163851.9011
[7 empty] | 13517 | 11072 | 1143537 | 2014-08-18 19:05 | 2014-08-18 19:46 | 41.1 | 11kV | 28564.5 | 695 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Rain Heavy | N | At ZN4545 Meadowbank Panel 6 tripped Relays: A and C phase IOC, A phase timed O/C, EFI, Fault Check Relay Signals: 11kV Trip, No1 Group Earth and Zone Earth Cause:Birds across 11kV Surge arrestors at LB61232 | August | 2014 | 2015Q1 | 2015 | ZN4545:PA6 | ZN4545:PA6 | ZN04545/000006 | RYDE | OH | Not Veg | 2014-08-18 | N | 41.1 | N | 10 | N | N | 1.1101 | 39.4971 | 20874.0941
[7 empty] | 12525 | 2529 | 1143515 | 2014-08-18 18:10 | 2014-08-18 19:55 | 105 | 11kV | 210 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Rain Light | N | LID 141782 B phase DOLF : 10 Amp Excluded OMS 1143515 | August | 2014 | 2015Q1 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2014-08-18 | N | 105 | N | 10 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 13637 | 12013 | 1143616 | 2014-08-19 06:00 | 2014-08-19 07:03 | 63 | 11kV | 7911 | 597 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 141792 FEEDER TRIP & RECLOSE EARLIER SEE REPORT NO 141783. CUSTOMERS HAD LOW VOLTS AFTER T&R. TAPPING OFF AT POLE IV-90723. | August | 2014 | 2015Q1 | 2015 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Not Veg | 2014-08-19 | N | 13.2513 | N | 6 | N | N | 1.1101 | 39.4971 | 5781.1255
[7 empty] | 13558 | 11378 | 1143720 | 2014-08-19 08:59 | 2014-08-19 09:45 | 46 | 11kV | 46 | 1 | HV | Animal Bird | Animal | DC PT | Unplanned | Rain Light | N | LID 141785 Single phase DOLF : 10 Amp DEAD BIRD AT SUB Excluded OMS 1143720 | August | 2014 | 2015Q1 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-08-19 | N | 46 | N | 6 | N | N | 1.1101 | 39.4971 | 33.6154
[7 empty] | 12690 | 4050 | 1143354 | 2014-08-18 14:47 | 2014-08-19 12:12 | 1285.3833 | 11kV | 192329.1 | 1378 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn12610 Long Jetty Pa25 "Long Jetty Aux No.2" feeder opened, reclosed & opened on B & C phase overcurrent, reclose, lockout & timing relays, 11kv trip 11kv down S18655 to S47375 to AB40288 to S47376. Originally caused by fire at top of AB42807 pole. See 1143752,3,4; 1143468 Exclude 1143354,464 | August | 2014 | 2015Q1 | 2015 | ZN12610:PA25 | ZN12610:PA25 | ZN12610/000025 | CENTRAL COAST | OH | Not Veg | 2014-08-18 | N | 139.5712 | N | 10 | N | N | 1.1101 | 39.4971 | 140548.4335
[7 empty] | 13533 | 11134 | 1144007 | 2014-08-19 14:46 | 2014-08-19 16:10 | 84 | 11kV | 2268 | 27 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 141798 interrupt to remove fallen tree on OHM pole ET-25511 near sub 52447. Excluded OMS 1143965 | August | 2014 | 2015Q1 | 2015 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2014-08-19 | N | 84 | N | 6 | N | N | 1.1101 | 39.4971 | 1657.3875
[7 empty] | 12722 | 4380 | 1144047 | 2014-08-19 15:38 | 2014-08-19 21:40 | 362 | 11kV | 77634 | 906 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | LID 141800 Mains on the ground due to fallen tree. Adjacent to ABS 41012. 512/5 C5 Three phase earth fault. 2700 ampss per phase. Also reset tx undervotlage flag | August | 2014 | 2015Q1 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-08-19 | N | 85.6887 | N | 6 | N | N | 1.1101 | 39.4971 | 56732.6374
[7 empty] | 13518 | 11074 | 1144184 | 2014-08-19 21:30 | 2014-08-19 22:05 | 35 | 11kV | 3510 | 2116 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 141803 Trip & reclose 10 fault operations B& C phases Overcurrent 51 BC see report # 141804 possum at sub 21836 See OMS 1144310 | August | 2014 | 2015Q1 | 2015 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2014-08-19 | N | 1.6588 | N | 6 | N | N | 1.1101 | 39.4971 | 2565.0045
[7 empty] | 12533 | 2574 | 1143951 | 2014-08-19 15:30 | 2014-08-20 00:40 | 550 | 11kV | 63800 | 116 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn847 Hornsby section of Pa10 PT1699 King Gleneagles interrutped by DOp. Allow Lineworker to remove large tree of fallen LV mains adjacent PT1699 CC1: 22-"Refer to SOp" | August | 2014 | 2015Q1 | 2015 | ZN847:PA10 | ZN847:PA10 | ZN00847/000010 | HORNSBY | OH | Veg | 2014-08-19 | N | 550 | N | 6 | N | N | 1.1101 | 39.4971 | 46623.1582
[7 empty] | 12255 | 19 | 1144776 | 2014-08-20 12:02 | 2014-08-20 12:37 | 35 | 11kV | 560 | 16 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" DOp interrupted supply from USL 41935 to AB41934. Tree on 11kc CCT mains outside 324 Fagans rd. | August | 2014 | 2015Q1 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2014-08-20 | N | 35 | N | 3 | N | N | 1.1101 | 39.4971 | 409.2315
[7 empty] | 12329 | 702 | 1144760 | 2014-08-20 09:13 | 2014-08-20 13:35 | 262 | 11kV | 2314 | 137 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor CCT | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Panel 2 AOp opened Recloser 41020 Wattle Tree Rd North for safety reasons Near PT13306 damaged HV CCT had set fire to pole See 1144760,2 | August | 2014 | 2015Q1 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2014-08-20 | N | 16.8905 | N | 3 | N | N | 1.1101 | 39.4971 | 1691.0029
[7 empty] | 14616 | 19825 | 1144695 | 2014-08-20 23:01 | 2014-08-21 10:48 | 706.9833 | 11kV | 1648.1167 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | PT18153 Brush Ck Yarra 0.3 No3 HDO on roadside blown. HDO ABB 16 Amps. Fuse failure see 1146488 exclude 114695 | August | 2014 | 2015Q1 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2014-08-20 | N | 549.3722 | N | 3 | N | N | 1.1101 | 39.4971 | 1204.395
[7 empty] | 13076 | 7441 | 1144921 | 2014-08-21 12:39 | 2014-08-21 13:10 | 31 | 11kV | 186 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 141834 Replaced fuse Excluded OMS 1144945 | August | 2014 | 2015Q1 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2014-08-21 | N | 31 | N | 3 | N | N | 1.1101 | 39.4971 | 135.9233
[7 empty] | 13034 | 7050 | 1144861 | 2014-08-21 11:15 | 2014-08-21 17:02 | 347.4333 | 11kV | 43933.4333 | 889 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | ZN15014 Mona Vale Pa22 tripped on: Relays: Timed overcurrent, earht fault, IOC, EFI & Fault check relay Signals: 11kv trip, Zone Earth EFI's S16761 S16817 S16695 S16699 S6763 Truck hit pole at corner of Warriewood Rd & McPherson street, Warriewood See 1146529,30,1 Exclude 1144861 | August | 2014 | 2015Q1 | 2015 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Not Veg | 2014-08-21 | N | 49.4189 | N | 3 | N | N | 1.1101 | 39.4971 | 32105.2573
[7 empty] | 14270 | 17017 | 1145093 | 2014-08-21 18:06 | 2014-08-21 19:53 | 107 | 11kV | 145948 | 1364 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 10999 Kogarah - Pnl 7 - Trip, reclose, trip, Earth fault, timer, EFI, Fault check, Field EFIs. UG cable fault in feeder from S 62206 to S 10925. Sw/A closed at S 10067 and AB 31262 open. ME: 1146342. ME GIS: 1145102. Withdrawn: 1145093, 6, 7. | August | 2014 | 2015Q1 | 2015 | ZN10999:PA7 | ZN10999:PA7 | ZN10999/000007 | BAYSIDE | UG | Not Veg | 2014-08-21 | N | 107 | N | 3 | N | N | 1.1101 | 39.4971 | 106654.4937
[7 empty] | 12372 | 1104 | 1145406 | 2014-08-22 15:15 | 2014-08-22 23:05 | 470 | 11kV | 3290 | 7 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 141859 Transformer expired and replaced Excluded OMS 1145406 | August | 2014 | 2015Q1 | 2015 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2014-08-22 | N | 470 | N | 1 | N | N | 1.1101 | 39.4971 | 2404.235
[7 empty] | 13257 | 8805 | 1145505 | 2014-08-23 06:28 | 2014-08-23 08:35 | 127 | 11kV | 254 | 2 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 141861 Eagle with crow across mains. Excluded OMS 1145505. | August | 2014 | 2015Q1 | 2015 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2014-08-23 | N | 127 | N | 4 | N | N | 1.1101 | 39.4971 | 185.6157
[7 empty] | 14491 | 18614 | 1145520 | 2014-08-23 07:53 | 2014-08-23 08:50 | 57 | 11kV | 75279 | 1378 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 931 Darlinghurst - Pnl 9 - Earth Fault, EFI, Fault check, Field EFIs. 11kV feeder faultin section of feeder S 35008 to S 8249. ME: 1147004. REst Step: 1147006. Withdrawn: 1145520. | August | 2014 | 2015Q1 | 2015 | ZN931:PA9 | ZN931:PA9 | ZN00931/000009 | SYDNEY | UG | Not Veg | 2014-08-23 | N | 54.6292 | N | 4 | N | N | 1.1101 | 39.4971 | 55011.6728
[7 empty] | 13318 | 9423 | 1145614 | 2014-08-23 17:38 | 2014-08-23 18:53 | 75 | 11kV | 63750 | 850 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | @ZN1287 Revesby, section of 11kv Panel 15 'S.47211 Eastern Tomp etc' feeder At AB2985, centre phase bond burnt off (line side) Remarks: Bond, At AB 2985 centre phase bond burnt off (line side) | August | 2014 | 2015Q1 | 2015 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-08-23 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 46586.6197
[7 empty] | 12302 | 470 | 1145687 | 2014-08-24 10:08 | 2014-08-24 12:04 | 116 | 11kV | 7974.5333 | 69 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT 9357 Pacific Mainbar - HDO Roadside (31.5A). HDO operated due to fuse fatigue. ME: 1145687. ME GIS: 1145698. | August | 2014 | 2015Q1 | 2015 | ZN9118:PA3 | ZN9118:PA3 | ZN09118/000003 | SUTHERLAND | OH | Not Veg | 2014-08-24 | N | 115.5729 | N | 2 | N | N | 1.1101 | 39.4971 | 5827.5538
[7 empty] | 14644 | 20111 | 1145646 | 2014-08-23 23:47 | 2014-08-24 12:50 | 783 | 11kV | 228918 | 2330 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Zn12650 West Gosford Pa17 "Mann Beane" tripped on A & B phase IOC Signals: 11kv trip EFI's: Nil S14462 Henry Parry NRMA Dist 2 "Henry Parry Dr N OH" Vehicle Hit Pole between B40303 & S14462 Event No. 55302144 Holden Ute CA34AO See 1146717,20 Exclude 1145651,2,6 | August | 2014 | 2015Q1 | 2015 | ZN12650:PA17 | ZN12650:PA17 | ZN12650/000017 | CENTRAL COAST | OH | Not Veg | 2014-08-23 | N | 98.2481 | N | 4 | N | N | 1.1101 | 39.4971 | 167286.5225
[7 empty] | 13809 | 13334 | 1145740 | 2014-08-24 18:39 | 2014-08-25 14:20 | 1181 | 11kV | 10358 | 70 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa5 "Wyong" Relays: EFI Signals: Tx1 Group Earth RE45016 Dickson opened, reclosed, opened & locked out on overcurrent & IOC Fault on section of UG cable between USL44195 & LB42008 tee PT14305 See 1146761,3 Exclude 1145740,63 | August | 2014 | 2015Q1 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | UG | Not Veg | 2014-08-24 | N | 147.9714 | N | 2 | N | N | 1.1101 | 39.4971 | 7569.3209
[7 empty] | 12643 | 3682 | 1146172 | 2014-08-25 18:01 | 2014-08-25 18:42 | 40.4 | 11kV | 5979.2 | 148 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 901 Surry Hills - Pnl 2 - Earth Fault, C phase overcurrent. Cable fault from Pnl 2 to S 8413 to S 8958 to S 112. ME: 1146172. Withdrawn: 1146177. | August | 2014 | 2015Q1 | 2015 | ZN901:PA2 | ZN901:PA2 | ZN00901/000002 | SYDNEY | UG | Not Veg | 2014-08-25 | N | 40.4 | N | 2 | N | N | 1.1101 | 39.4971 | 4369.423
[7 empty] | 13438 | 10464 | 1146204 | 2014-08-25 20:57 | 2014-08-25 22:25 | 88 | 11kV | 88 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 141872 A phase DOLF : 10 Amp Excluded OMS 1146204 | August | 2014 | 2015Q1 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-08-25 | N | 88 | N | 2 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 14052 | 15435 | 1146621 | 2014-08-26 18:33 | 2014-08-26 19:39 | 65.7833 | 11kV | 86176.1667 | 1310 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S.15006 Dee Why West, Panel 13 Fdr CB tripped on C phase overcurrent and earth fault. 11kV trip, Zone earth, #1 and #2 Tx Cooling fail. Field efi down at S.47595. On reengerising feeder a small flash was observed at pole FF83418 | August | 2014 | 2015Q1 | 2015 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Veg | 2014-08-26 | N | 65.7833 | N | 1 | N | N | 1.1101 | 39.4971 | 62975.0008
[7 empty] | 14136 | 16092 | 1146662 | 2014-08-27 03:10 | 2014-08-27 04:08 | 58.2167 | 11kV | 30738.4 | 528 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S35500 Top Ryde Panel 32 tripped on Relays: 50T ABC, Fault Check and EFI Signals: 11kV Trip, Zone Earth and Tx3 Group Earth Cause: Possum at Base of UGOH below S8532 | August | 2014 | 2015Q1 | 2015 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Not Veg | 2014-08-27 | N | 58.2167 | N | 4 | N | N | 1.1101 | 39.4971 | 22462.7161
[7 empty] | 12937 | 6290 | 1146849 | 2014-08-27 11:13 | 2014-08-27 16:20 | 307.2667 | 11kV | 2217.2667 | 318 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | Zn12630 Peats Ridge Pa4 "Kulnura" interrupted by AOp for safety @1215 Moving Vehicle Accident hitting Pole CM383 1Km North of Peats Ridge rd Intersection. Pole down. Distributor Wire suspended from remaining poles. Damaged section of 11kf feeder from AB41053 to AB41972 tee PT18735 tee PT13027 See 1147234,5,7,8 GIS 1146846 Exclude 1146867,908,16 | August | 2014 | 2015Q1 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-08-27 | N | 6.9725 | N | 4 | N | N | 1.1101 | 39.4971 | 1620.3131
[7 empty] | 14617 | 19840 | 1147064 | 2014-08-27 20:01 | 2014-08-27 21:14 | 73 | 11kV | 4599 | 63 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Rain Light | N | LID 141897 fdr opened off for pole fire 8N-20368 | August | 2014 | 2015Q1 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-08-27 | N | 73 | N | 4 | N | N | 1.1101 | 39.4971 | 3360.8136
[7 empty] | 12711 | 4225 | 1147094 | 2014-08-27 22:37 | 2014-08-27 23:50 | 73 | 11kV | 9390 | 822 | HV | Vegetation Blow/Fall In | Vegetation | DC PT | Unplanned | Unselected | N | @Zn14144 Wamberal Pa4 tripped & reclosed on Relays: 50 TC, EFI Signals: 11kv trip, Tx2 Group Earth EFI: S18823 @PT13463 Hastings Anchorage 50Amp footpath side HDO fuse operated Branch on PT13463 See 1147258,9 Exclude 1147094,5,6 | August | 2014 | 2015Q1 | 2015 | ZN14144:PA4 | ZN14144:PA4 | ZN14144/000004 | CENTRAL COAST | OH | Veg | 2014-08-27 | N | 11.4234 | N | 4 | N | N | 1.1101 | 39.4971 | 6861.935
[7 empty] | 12930 | 6229 | 1147106 | 2014-08-28 02:11 | 2014-08-28 12:50 | 639 | 11kV | 24694 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge section of Panel 3 "Mangrove Mountain" REcloser 45035 Mangrove Mountain tripped and locked out on SEF 3 Bays of 11kv brought down by tree on tee off to PT13212 Lillicrapps Wise 0.2 section of 11kv OH from USL40940 to USL41124 isolated See 1147690 exclude 1147106 | August | 2014 | 2015Q1 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2014-08-28 | N | 374.1515 | N | 2 | N | N | 1.1101 | 39.4971 | 18045.6469
[7 empty] | 12466 | 1878 | 1147369 | 2014-08-28 13:27 | 2014-08-28 16:50 | 203.4667 | 11kV | 14039.2 | 69 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Light | N | LID 141911 Single phase Outage to repair stranding conductor to Lynch sub 50602. | August | 2014 | 2015Q1 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-08-28 | N | 203.4667 | N | 2 | N | N | 1.1101 | 39.4971 | 10259.4333
[7 empty] | 13172 | 8144 | 1147864 | 2014-08-29 17:49 | 2014-08-29 19:30 | 101 | 11kV | 46876 | 1036 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 43 - SEL. Broken cross arm on AB 35904 collapsed causing fire to start on pole. 11kV feeder isolated from LB 35102 to LB 35328 to S 49698 tee PT9109 and PT 9459. ME: 1148299. Rest Steps: 1148300, 1, 2, 3. Withdrawn: 1147864. | August | 2014 | 2015Q1 | 2015 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Not Veg | 2014-08-29 | N | 45.2471 | N | 1 | N | N | 1.1101 | 39.4971 | 34255.5982
[7 empty] | 13084 | 7501 | 1148061 | 2014-08-30 19:42 | 2014-08-30 22:10 | 148 | 11kV | 296 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 141922 Single phase DOLF : 10 Amp Excluded OMS 1148061 | August | 2014 | 2015Q1 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-08-30 | N | 148 | N | 1 | N | N | 1.1101 | 39.4971 | 216.3081
[7 empty] | 12962 | 6514 | 1148100 | 2014-08-31 11:15 | 2014-08-31 12:40 | 85 | 11kV | 255 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 141926 Isolated for safety due to low mains reported by customer. Customer agreed to interruption. | August | 2014 | 2015Q1 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2014-08-31 | N | 85 | N | 2 | N | N | 1.1101 | 39.4971 | 186.3465
[7 empty] | 13659 | 12173 | 1148157 | 2014-08-31 16:07 | 2014-08-31 19:40 | 213 | 11kV | 51933 | 808 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 141929 2 fault operation A phase Overcurrent; Earth fault Transformer exploded and was on fire (reports received from police and public) Damage Cable at UGOH at pole IU-20616. SI on desk 1. Cable not yet repaired. Excluded OMS 1148172 | August | 2014 | 2015Q1 | 2015 | 216:10724 | 216:10724 | ZN00216/010724 | LAKE MACQUARIE | OH | Not Veg | 2014-08-31 | N | 64.2735 | N | 2 | N | N | 1.1101 | 39.4971 | 37951.1046
[7 empty] | 13666 | 12245 | 1148405 | 2014-09-01 12:43 | 2014-09-01 13:55 | 72 | 11kV | 41997 | 779 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12570 Avoca Pa34 "Terrigal" fdr tripped on relays - A & C phase IOC, EFI, Lockout Signals: 11kv trip 11kv UGOH fault short circuit between 41756 to AB42799 tee PT18697 See 1148837,8,9 Exclude 1148401,5,7 | September | 2014 | 2015Q1 | 2015 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | Unknown | Unknown | 2014-09-01 | N | 53.9114 | N | 1 | N | N | 1.1101 | 39.4971 | 30690.1689
[7 empty] | 13704 | 12559 | 1148852 | 2014-09-02 13:29 | 2014-09-02 15:27 | 118 | 11kV | 174721 | 1552 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12570 Avoca Zone Pa29 "Bensville" fdr tripped, reclosed, tripped & Locked out Relays: A Phase IOC, EFI, Lockout Signals: 11kv trip EFI's: S18574 11kv UG cable fault from Zn12570 Avoca Pa29 to S12692 Scaysvrook Edmondson See 1149113,4 Exclude 1148852 | September | 2014 | 2015Q1 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | UG | Not Veg | 2014-09-02 | N | 112.578 | N | 1 | N | N | 1.1101 | 39.4971 | 127680.9534
[7 empty] | 13152 | 7997 | 1149032 | 2014-09-03 01:06 | 2014-09-03 02:20 | 74 | 11kV | 52318 | 707 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At S35370 Galston Panel 8 tripped on B and C phase IOC Cause: Tree branch removed by DOp | September | 2014 | 2015Q1 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2014-09-03 | N | 74 | N | 8 | N | N | 1.1101 | 39.4971 | 38232.4513
[7 empty] | 13977 | 14743 | 1149068 | 2014-09-03 05:35 | 2014-09-03 08:01 | 146 | 11kV | 42199 | 1622 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Ex Zn12610 Long Jetty section of Panel 13 ABNORMAL: AB40376 Closed, LB61960 opened. 1st Event fed from Pa6 1st Event AB40271 HV centre phase bond open circuit 2nd Event happened on restoration of 1st Event. Section of Pa6 "Rhoddin Drive" IR62166 tripped on Overcurrent, Sensitive Earth Fault, Lockout HV bond open circuit middle phase at AB40271 See 1149857,9 Exclude 1149068,72,7 | September | 2014 | 2015Q1 | 2015 | ZN12610:PA13 | ZN12610:PA13 | ZN12610/000013 | CENTRAL COAST | OH | Not Veg | 2014-09-03 | N | 26.0166 | N | 8 | N | N | 1.1101 | 39.4971 | 30837.7845
[7 empty] | 13467 | 10675 | 1149147 | 2014-09-03 09:22 | 2014-09-03 10:41 | 79 | 11kV | 111374 | 1524 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 141962 1 fault operation A & C phase Overcurrent bang reported near sub 48902. nothing found. Fdr was on one shot for live line work Excluded OMS 1149147 | September | 2014 | 2015Q1 | 2015 | 507:80925 | 507:80925 | ZN00507/080925 | CESSNOCK | OH | Veg | 2014-09-03 | N | 73.0801 | N | 8 | N | N | 1.1101 | 39.4971 | 81388.8342
[7 empty] | 13395 | 10129 | 1149297 | 2014-09-03 11:04 | 2014-09-03 11:26 | 22 | 11kV | 22484 | 1022 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Ex Zn12570 Avoca 11kv Pa21L "Mayfair Kings etc" fdr Recloser 41397 karalta Rd tripped, reclosed, tripped & Lockout Tree branch removed near 11kv UGOH at AB44656 See 1149298 Exclude 1149297 CC1: 22-"Refer to SOp" | September | 2014 | 2015Q1 | 2015 | ZN12570:PA21 | ZN12580:PA2 | ZN12580/000002 | CENTRAL COAST | OH | Veg | 2014-09-03 | N | 22 | N | 8 | N | N | 1.1101 | 39.4971 | 16430.644
[7 empty] | 13885 | 13959 | 1149386 | 2014-09-03 12:17 | 2014-09-03 19:00 | 403 | 11kV | 126952 | 964 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | N | Zn12660 Woy Woy Panel 6 "Davistown" feeder tripped reclosed, tripped Relays: Aphase IOC, E/F, L/O, EFI Signals: 11kv trip EFI's: S18272 S18272 Dist 3 isolated for safety PT11038 Dist 2 came into contact with HV. EMSO required Section of overhead has come down between LB41139 to S18272 Sw/B tee PT11038 See 1149993,4,5,6 Exclude 1149356,482,5 | September | 2014 | 2015Q1 | 2015 | ZN12660:PA6 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2014-09-03 | N | 131.6929 | N | 8 | N | N | 1.1101 | 39.4971 | 92772.7771
[7 empty] | 12866 | 5669 | 1149427 | 2014-09-03 13:20 | 2014-09-03 21:16 | 476 | 11kV | 188455 | 2021 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | Zn15002 Narrabeen Pa8 "Nareen Tatiara" fdr tripped on Relays: Earth Fault, Fault Check & EFI Signals: 11kv trip and Zone Earth EFI's: S47436 S1536 S16347 S16913 EFI at CP24276 did not operate ABNORMAL: S16784:SwA Closed, S16942:SwA Open. For Load Relief of Tx3 fault at Mona Vale Tree/Branch brought down Overhead in Irrawong st 5 bays of 11kv down See 1149568,50016,7,8 Exclude 1149424,38,505,35 | September | 2014 | 2015Q1 | 2015 | ZN15002:PA8 | ZN15002:PA8 | ZN15002/000008 | NORTHERN BEACHES | OH | Veg | 2014-09-03 | N | 93.2484 | N | 8 | N | N | 1.1101 | 39.4971 | 137717.3555
[7 empty] | 14682 | 20397 | 1149454 | 2014-09-03 13:46 | 2014-09-03 22:31 | 525 | 11kV | 247849 | 2710 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Wind | N | At S.15008 Harbord, Panel 7 Fdr CB tripped on OC and Earth Fault, timing and reclosing relays plus 11kV trip signal and zone earth. Customer's acrport blown onto 11kV OH mains in Headlands Rd | September | 2014 | 2015Q1 | 2015 | ZN15008:PA7 | ZN15008:PA7 | ZN15008/000007 | NORTHERN BEACHES | OH | Not Veg | 2014-09-03 | N | 91.4572 | N | 8 | N | N | 1.1101 | 39.4971 | 181120.7389
[7 empty] | 13167 | 8098 | 1149774 | 2014-09-04 01:33 | 2014-09-04 01:38 | 5 | 11kV | 655 | 131 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 141969 1 fault operation Overcurrent; Earth fault Sw 42060 on 1 shot for switching purposes to repair Lv main. See unplanned 141967/ OMS 1149773. Sw tripped when restoring sub 50153. | September | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2014-09-04 | N | 5 | N | 7 | N | N | 1.1101 | 39.4971 | 478.6547
[7 empty] | 12584 | 3123 | 1149597 | 2014-09-03 19:30 | 2014-09-04 02:15 | 405 | 11kV | 810 | 2 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Rain Light | N | LID 141967 Broken x arm brought LV mains down. Repaired under AP. Sw 42060 tripped when restoring. See unplanned 141969/OMS 1149774. Found arrestors faulty. Replaced under AP. Excluded OMS 1149597 | September | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2014-09-03 | N | 405 | N | 8 | N | N | 1.1101 | 39.4971 | 591.9241
[7 empty] | 13272 | 8929 | 1149685 | 2014-09-04 07:09 | 2014-09-04 11:50 | 281 | 11kV | 562 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At S.16127 th C phase 40 amp HV fuse operated - Cause Unknown | September | 2014 | 2015Q1 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-09-04 | N | 281 | N | 7 | N | N | 1.1101 | 39.4971 | 410.693
[7 empty] | 13005 | 6856 | 1149894 | 2014-09-04 12:18 | 2014-09-04 12:59 | 41 | 11kV | 164 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Tree branch on mains in Davidson Park caused Recloser 26228 to trip and lockout on OOC and IOC trip. | September | 2014 | 2015Q1 | 2015 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | OH | Veg | 2014-09-04 | N | 41 | N | 7 | N | N | 1.1101 | 39.4971 | 119.8464
[7 empty] | 13572 | 11471 | 1149833 | 2014-09-04 11:14 | 2014-09-04 13:10 | 115.9333 | 11kV | 8717.0667 | 104 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | S2368 Tucabia St - C Phase HV fuse blown Fuse fatigued see #1150816 for Dist #1 interuption for safety 1149833 1150816 | September | 2014 | 2015Q1 | 2015 | ZN35600:PA1 | ZN35600:PA1 | ZN35600/000001 | RANDWICK | OH | Not Veg | 2014-09-04 | N | 83.8179 | N | 7 | N | N | 1.1101 | 39.4971 | 6370.1752
[7 empty] | 14420 | 18050 | 1150009 | 2014-09-04 15:13 | 2014-09-04 22:05 | 412 | 11kV | 1564 | 5 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 141984 C Phase Connection to top of DOLF had fatigued and snapped off. The interruption had to be extended to ABS 74627 to remake the connection safely as no live line crew was available. Excluded OMS 1150009, 1150110, 1150361 | September | 2014 | 2015Q1 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-09-04 | N | 312.8 | N | 7 | N | N | 1.1101 | 39.4971 | 1142.9251
[7 empty] | 14686 | 20422 | 1150132 | 2014-09-04 21:32 | 2014-09-04 23:05 | 93 | 11kV | 4185 | 45 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 141985 B Phase No protection operation. B Phase of line DOLF 40617 was found glowing (high resistance), fuse was opened to allow live line crew to re make the connection. Excluded OMS 1150135 | September | 2014 | 2015Q1 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-09-04 | N | 93 | N | 7 | N | N | 1.1101 | 39.4971 | 3058.2746
[7 empty] | 14406 | 17978 | 1150139 | 2014-09-04 23:56 | 2014-09-05 01:42 | 106 | 11kV | 118838 | 1888 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | At S.15005 Belrose, 11kV Fdr CB tripped on 50TAC Basler Relay - LED OC, 11kV trip signal - No Field efi's operated. | September | 2014 | 2015Q1 | 2015 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Veg | 2014-09-04 | N | 62.9439 | N | 7 | N | N | 1.1101 | 39.4971 | 86843.3053
[7 empty] | 14635 | 20027 | 1150532 | 2014-09-06 09:01 | 2014-09-06 10:46 | 105.3 | 11kV | 1735.65 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 141997 A phase DOLF : 31 Amp excluded OMS 1150532 | September | 2014 | 2015Q1 | 2015 | 513:48058 | 513:83504 | ZN00513/083504 | SINGLETON | OH | Veg | 2014-09-06 | N | 75.463 | N | 4 | N | N | 1.1101 | 39.4971 | 1268.3618
[7 empty] | 12498 | 2230 | 1150574 | 2014-09-06 12:27 | 2014-09-06 13:45 | 78 | 11kV | 78 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 141999 Single phase DOLF : 10 Amp excluded OMS 1150574 | September | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2014-09-06 | N | 78 | N | 4 | N | N | 1.1101 | 39.4971 | 57.0001
[7 empty] | 13997 | 14902 | 1150647 | 2014-09-06 21:25 | 2014-09-06 22:38 | 73 | 11kV | 36507 | 527 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | 11kV Panel 4 at Brookvale Zone ZN.15001 Relays: C-Phase IOC Signals: 11kV trip Field EFI's: S.16106 @ S.16838 Cause: UG Cable fault from S.16838(SW/B) to S.16628(SW/B) to S.46920(SW/A) ME-1150845 RS-1150846, 1150847 Withdrawn-1150647 | September | 2014 | 2015Q1 | 2015 | ZN15001:PA4 | ZN15001:PA4 | ZN15001/000004 | NORTHERN BEACHES | UG | Not Veg | 2014-09-06 | N | 69.2732 | N | 4 | N | N | 1.1101 | 39.4971 | 26678.2388
[7 empty] | 12586 | 3132 | 1150654 | 2014-09-06 22:38 | 2014-09-06 23:43 | 65 | 11kV | 23790 | 366 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | At ZN35370 Galston Panel 2 Tripped, reclosed tripped and locked out on C phase IOC Cause: Mains removed tree adjacent to LB3093. | September | 2014 | 2015Q1 | 2015 | ZN35370:PA2 | ZN35370:PA2 | ZN35370/000002 | HORNSBY | OH | Veg | 2014-09-06 | N | 65 | N | 4 | N | N | 1.1101 | 39.4971 | 17385.0303
[7 empty] | 14338 | 17454 | 1150659 | 2014-09-07 01:30 | 2014-09-07 05:52 | 262 | 11kV | 478310 | 1888 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | ZN-15005 Belrose - 11kV Panel 2 Relays: Basler 50 TAC - No.1 Definite Timed O/C (left side) Signals: 11kV trip, Zone Earth, Tx.2 Cooling Supply Fail Alarm Field EFI's: S.16881, S.15425 & S.16801 Cause: Defective ABS-25622 (Killarney 2D6) towards S.16801 ME-1150925 RS-1150928, 1150929 Withdrawn-1150659 | September | 2014 | 2015Q1 | 2015 | ZN15005:PA2 | ZN15005:PA2 | ZN15005/000002 | NORTHERN BEACHES | OH | Not Veg | 2014-09-07 | N | 253.3422 | N | 1 | N | N | 1.1101 | 39.4971 | 349534.8402
[7 empty] | 14072 | 15591 | 1150905 | 2014-09-08 09:31 | 2014-09-08 13:10 | 219 | 11kV | 273964 | 3296 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12570 Avoca Pa33 "Macmasters Beach" fdr tripped reclosed and locked out Relays: IOC, Earth fault, Timing, Lockout, EFI Signals: 11kv trip EFI's S14155 S12595 ABNORMAL: Avoca Pa29 Open, AB40447 closed AB44523 closed AB43768 open AB40456 closed AB43709 AB43710 open 11kv UGOH Fault on UGOH to S12740 See 1151306,9 Exclude 1150905,10,21,2,52,8,9,78,98 | September | 2014 | 2015Q1 | 2015 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | Unknown | Unknown | 2014-09-08 | N | 83.1201 | N | 2 | N | N | 1.1101 | 39.4971 | 200204.8106
[7 empty] | 13942 | 14531 | 1151069 | 2014-09-08 14:05 | 2014-09-08 17:10 | 185 | 11kV | 62573 | 981 | HV | 3rd Party Action | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | LID 142009 2 fault operations C phase Overcurrent Hang glider into 11kV mains pole CH-80294 Flower St Catherine Hill Bay. Repaired 2 X 11kV mains stranding. Also replaced C phase 16A DOLF sub 8197 on energising. Excluded OMS 1151069; 1151076; 1151078 and 1151115 | September | 2014 | 2015Q1 | 2015 | 223:14395 | 223:14399 | ZN00223/014399 | LAKE MACQUARIE | OH | Not Veg | 2014-09-08 | N | 63.7849 | N | 2 | N | N | 1.1101 | 39.4971 | 45726.5028
[7 empty] | 12488 | 2163 | 1151720 | 2014-09-10 10:30 | 2014-09-10 11:10 | 40 | 11kV | 80 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142033 C Phase - Fuse size: 10 Amp Substation DOLF Excluded OMS 1151720 | September | 2014 | 2015Q1 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-09-10 | N | 40 | N | 3 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 13456 | 10589 | 1151602 | 2014-09-10 04:40 | 2014-09-10 15:25 | 645 | 11kV | 1935 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 142040 A & B Phases Substation DOLF Tx 72528 Faulty after storm on previous night. Excludes OMS 1151602 | September | 2014 | 2015Q1 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-09-10 | N | 645 | N | 3 | N | N | 1.1101 | 39.4971 | 1414.0409
[7 empty] | 13176 | 8175 | 1151961 | 2014-09-10 22:01 | 2014-09-11 01:46 | 225 | 11kV | 402411 | 2720 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12570 Avoca Pa21 tripped and locked out on Earth Fault and lockout 11kv trip Defective EFI @S14890 Underground Cable Fault between S18012:B to S14907:B to S14916:B See 1152222,3,5,6,7,8 2nd 1152235,8 Exclude 1151961 | September | 2014 | 2015Q1 | 2015 | ZN12570:PA21 | ZN12570:PA21 | ZN12570/000021 | CENTRAL COAST | UG | Not Veg | 2014-09-10 | N | 147.9452 | N | 3 | N | N | 1.1101 | 39.4971 | 294070.0897
[7 empty] | 12760 | 4663 | 1152092 | 2014-09-11 10:05 | 2014-09-11 11:55 | 110 | 11kV | 55668 | 528 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn1287 Revesby 11kv Pnl 16 "Polo St" feeder tripped on Relays: B phase overcurrent and fault check Signals: Zone earth, Tx #3 group earth, 11kv trip and efi Field efi's: Sub 3961 Remarks: Cable fault between sub 3961 Polo St to Sub 4577 Sherwood Carr tee to PT 1226 Sherwood Bransgrove (suspect cable damaged). Also earthing grid damaged at Sub 3961 | September | 2014 | 2015Q1 | 2015 | ZN1287:PA16 | ZN1287:PA16 | ZN01287/000016 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-09-11 | N | 105.4318 | N | 1 | N | N | 1.1101 | 39.4971 | 40680.5325
[7 empty] | 13870 | 13866 | 1152343 | 2014-09-12 03:34 | 2014-09-12 13:00 | 566 | 11kV | 125825 | 1082 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S129 Hunters Hill Panel 9 Tripped, reclosed tripped and locked out on Relays: A and C phase overcurrent, timing relay, lockout relay, fault check and EFI Signals: 11kV trip, Zone Earth and Group Earth Cause: Suspect UG cable Fault betwee S 736 and LB399 Second Fault:Bond Burnt Off 11kV before S7636 \See OMS 1153245 1153248 1153250 1153251 1153249 1152343 1152348 | September | 2014 | 2015Q1 | 2015 | ZN129:PA9 | ZN129:PA41 | ZN00129/000041 | LANE COVE | UG | Not Veg | 2014-09-12 | N | 116.2893 | N | 3 | N | N | 1.1101 | 39.4971 | 91949.1988
[7 empty] | 13168 | 8114 | 1152606 | 2014-09-12 15:50 | 2014-09-12 17:30 | 100 | 11kV | 400 | 4 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Unselected | N | LID 142066 Single phase section isolated to repair x-arm at pole ET-72608 | September | 2014 | 2015Q1 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-09-12 | N | 100 | N | 3 | N | N | 1.1101 | 39.4971 | 292.3082
[7 empty] | 13838 | 13515 | 1152632 | 2014-09-12 16:48 | 2014-09-12 23:20 | 392 | 11kV | 392 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142067 Single phase SUB ISOLATED TO REPAIR BURNT OFF DROPPER LEAD Excluded OMS 1152632 | September | 2014 | 2015Q1 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-09-12 | N | 392 | N | 3 | N | N | 1.1101 | 39.4971 | 286.462
[7 empty] | 13975 | 14710 | 1152817 | 2014-09-14 07:19 | 2014-09-14 08:11 | 52 | 11kV | 3224 | 62 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ ZN2196 Milperra 11kv Panel 26 'Nancy Milperra McDonalds" feeder tripped Relays: Earth Fault Check, efi Signals: 11kv trip, ZE, No.2 GE Field EFI's: S63412 Remarks: UG fault. cause not ascertained | September | 2014 | 2015Q1 | 2015 | ZN2196:PA26 | ZN2196:PA26 | ZN02196/000026 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-09-14 | N | 52 | N | 1 | N | N | 1.1101 | 39.4971 | 2356.0041
[7 empty] | 14228 | 16729 | 1153312 | 2014-09-15 18:10 | 2014-09-15 19:30 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Unselected | N | LID 142084 A phase DOLF : 31 Amp Excluded OMS 1153312 | September | 2014 | 2015Q1 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | UG | Not Veg | 2014-09-15 | N | 80 | N | 1 | N | N | 1.1101 | 39.4971 | 58.4616
[7 empty] | 12441 | 1745 | 1153369 | 2014-09-16 08:39 | 2014-09-16 10:10 | 91 | 11kV | 1365 | 15 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12690 Berkeley Vale section of Pa24 11kv LB44746 opened by DOp Wilson for safety due to large tree branch on Overhead CCT cable. Branch on HV adjacent to USL41228 See 1153407 exclude 1153369 | September | 2014 | 2015Q1 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2014-09-16 | N | 91 | N | 6 | N | N | 1.1101 | 39.4971 | 997.5017
[7 empty] | 14357 | 17595 | 1153664 | 2014-09-16 15:46 | 2014-09-16 17:20 | 94 | 11kV | 48132 | 518 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S262 Marrickville: 11kv feeder Panel No40 "Ruby St" tripped Relays: E/F, EFI, fault check Field EFI's: S581, S6784, S35858 Remarks: UG fault. 11kv feeder fault from S35858 Warren Carrington (SWB) to S5626 Edwin Gannon (SwA) to S8489 Renwick Carrington HV (SWA) Note HAZ @ S5626 LV// required to extend for testers. | September | 2014 | 2015Q1 | 2015 | ZN262:PA40 | ZN262:PA40 | ZN00262/000040 | INNER WEST | UG | Not Veg | 2014-09-16 | N | 92.9189 | N | 6 | N | N | 1.1101 | 39.4971 | 35173.4459
[7 empty] | 13634 | 11998 | 1153684 | 2014-09-16 16:20 | 2014-09-16 17:25 | 65 | 11kV | 390 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridgve section of Pa5 PT11878 Bushells Peats 0.6 middle phase 31.5K HDO failed due to fuse fatigue See 1153865 Exclude 1153684 | September | 2014 | 2015Q1 | 2015 | ZN12630:PA5 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-09-16 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 285.0005
[7 empty] | 13324 | 9485 | 1153689 | 2014-09-16 18:00 | 2014-09-16 19:05 | 65 | 11kV | 325 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142099 A phase isolate to repair broken HV lead at sub. | September | 2014 | 2015Q1 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-09-16 | N | 65 | N | 6 | N | N | 1.1101 | 39.4971 | 237.5004
[7 empty] | 14243 | 16862 | 1153741 | 2014-09-16 18:45 | 2014-09-16 19:38 | 53.25 | 11kV | 3567.75 | 67 | HV | Vegetation Blow/Fall In | Vegetation | Unselected | Unplanned | Unselected | N | At PT1846 Kippara Kooyong 400A fuse blown on B and C phase of distirbutor 1. Cause: Tree branch on OH mains Based on customer calls, suspect distributor 1 and 2 were bridged at time of interruption See OMS 1153742 1153741 1153752 1153743 | September | 2014 | 2015Q1 | 2015 | ZN195:PA29 | ZN195:PA29 | ZN00195/000029 | KU-RING-GAI | OH | Veg | 2014-09-16 | N | 53.25 | N | 6 | N | N | 1.1101 | 39.4971 | 2607.2065
[7 empty] | 12778 | 4844 | 1153730 | 2014-09-16 20:31 | 2014-09-16 21:15 | 44 | 11kV | 3212 | 73 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn13000 Lake Munmorah section of Pa2 "Tall TImbers" feeder beyond LB44037 Interrupted for emergency repairs to 11kv OH Car into Pole VP913 See 1153749 exclude 1153730 | September | 2014 | 2015Q1 | 2015 | ZN13000:PA2 | ZN13000:PA2 | ZN13000/000002 | CENTRAL COAST | OH | Not Veg | 2014-09-16 | N | 44 | N | 6 | N | N | 1.1101 | 39.4971 | 2347.2349
[7 empty] | 14244 | 16873 | 1153774 | 2014-09-17 07:28 | 2014-09-17 11:51 | 263 | 11kV | 263 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 142112 Single Phase Sub isolated to repair burnt off dropper lead Excludes OMS 1153774 | September | 2014 | 2015Q1 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2014-09-17 | N | 263 | N | 1 | N | N | 1.1101 | 39.4971 | 192.1926
[7 empty] | 13697 | 12477 | 1154275 | 2014-09-18 11:50 | 2014-09-18 13:03 | 73 | 11kV | 83549.8833 | 1513 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | Zn180 Mosman Pa20 fdr tripped on relays: B Phase Earth Fault, EFI Signals: 11kv trip, Zone Earth, Tx3 Group Earth 11kv UG frontline fault feeder from Zn180 Mosman Pa20 to S4282 to S5193 to S2057 See 1154584 Exclude 1154275,303,10 | September | 2014 | 2015Q1 | 2015 | ZN180:PA20 | ZN180:PA20 | ZN00180/000020 | NORTH SYDNEY | UG | Not Veg | 2014-09-18 | N | 55.2213 | N | 2 | N | N | 1.1101 | 39.4971 | 61055.7904
[7 empty] | 12972 | 6583 | 1154430 | 2014-09-18 17:33 | 2014-09-18 18:35 | 62 | 11kV | 95294 | 1537 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12610 Long Jetty section of Pa6 from LB41061 to S47376SwA experienced fluxuating volts after switching ABNORMAL: S47376SwA closed CP41061 open Cause not ascertained. Suspect burned off bond See 1154569 exclude 1154430,42 | September | 2014 | 2015Q1 | 2015 | ZN12610:PA6 | ZN12610:PA6 | ZN12610/000006 | CENTRAL COAST | OH | Not Veg | 2014-09-18 | N | 62 | N | 2 | N | N | 1.1101 | 39.4971 | 69638.0445
[7 empty] | 13371 | 9861 | 1154645 | 2014-09-19 13:16 | 2014-09-19 14:05 | 49 | 11kV | 3234 | 66 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT2473 Derby Somerset 11kV HVDO centre phase fuse blown Cause: Fuse Fatigue See OMS 1154975 1154976 1154645 1145647 | September | 2014 | 2015Q1 | 2015 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | OH | Not Veg | 2014-09-19 | N | 49 | N | 3 | N | N | 1.1101 | 39.4971 | 2363.3118
[7 empty] | 12829 | 5306 | 1154746 | 2014-09-19 18:15 | 2014-09-19 21:30 | 195 | 11kV | 3510 | 18 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 142143 interrupt for emergency sub pole replacement. sub 53377. | September | 2014 | 2015Q1 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-09-19 | N | 195 | N | 3 | N | N | 1.1101 | 39.4971 | 2565.0045
[7 empty] | 14672 | 20298 | 1154765 | 2014-09-19 22:18 | 2014-09-19 23:45 | 87 | 11kV | 170337 | 1976 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN 10994 Mortdale - Pnl 12L - Sensitive Earth, lockout. Bond burnt off at AB 30799. ME: 1155062. Rest Step: 1155063. Withdrawn: 1154765, 6. | September | 2014 | 2015Q1 | 2015 | ZN10994:PA12 | ZN10994:PA12 | ZN10994/000012 | GEORGES RIVER | OH | Not Veg | 2014-09-19 | N | 86.2029 | N | 3 | N | N | 1.1101 | 39.4971 | 124477.2555
[7 empty] | 14658 | 20171 | 1154825 | 2014-09-20 14:22 | 2014-09-20 16:30 | 128 | 11kV | 152322 | 1820 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn9035 Caringbah - Pnl.4 tripped on: Right leg: A phase Inst O/C, lockout, timing relay & EFI Field EFIs: S9797, UGOH Near PT9504 UG cable fault between S9797 Cararra Dian & S9472 Sindone Cawarra tee PT9505 Sindone Pl see 1155085 1155086 - 1154833 1154832 1154828 | September | 2014 | 2015Q1 | 2015 | ZN9035:PA4 | ZN9035:PA4 | ZN09035/000004 | SUTHERLAND | UG | Not Veg | 2014-09-20 | N | 83.6934 | N | 1 | N | N | 1.1101 | 39.4971 | 111312.4249
[7 empty] | 12578 | 3073 | 1155330 | 2014-09-22 17:11 | 2014-09-22 18:05 | 54 | 11kV | 54 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | DC Not Transformer | Unplanned | Unselected | N | LID 142162 Sub 28854 was isolated to extend the area to make taps under access | September | 2014 | 2015Q1 | 2015 | 214:8671 | 214:8671 | ZN00214/008671 | LAKE MACQUARIE | UG | Not Veg | 2014-09-22 | N | 54 | N | 1 | N | N | 1.1101 | 39.4971 | 39.4616
[7 empty] | 13171 | 8137 | 1155535 | 2014-09-23 13:08 | 2014-09-23 15:10 | 122 | 11kV | 218361 | 2016 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2568 St Peters - Pnl.27 tripped on: B phase Overcurrent and earth fault + fault check Field EFIs: S1941 S1508 S35180 UG cable fault between S35180 Sw B and S1753 Sw B see 1155773 1155776 GIS errors: 1155540 1155570 Multiple other jobs possible address errors or LV //'s potentially in place: 1155549 1155544 1155553 1155789 1155788 1155789 1155801 1155802 1155803 | September | 2014 | 2015Q1 | 2015 | ZN2568:PA27 | ZN2568:PA27 | ZN02568/000027 | SYDNEY | UG | Not Veg | 2014-09-23 | N | 108.314 | N | 1 | N | N | 1.1101 | 39.4971 | 159571.7782
[7 empty] | 14567 | 19189 | 1155999 | 2014-09-24 15:00 | 2014-09-24 15:34 | 33.6667 | 11kV | 9999 | 297 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | S711 Blackwattle Bay Pnl.23 tripped on: C phase Inst OC, EF and EFI UG Cable fault from Pnl.23 to S3566 to S2983 | September | 2014 | 2015Q1 | 2015 | ZN711:PA23 | ZN7481:PA13 | ZN07481/000013 | SYDNEY | UG | Not Veg | 2014-09-24 | N | 33.6667 | N | 1 | N | N | 1.1101 | 39.4971 | 7306.9743
[7 empty] | 14014 | 15093 | 135 | 2014-09-25 | 2014-09-25 01:25 | 85 | 11kV | 9520 | 112 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS |  | Unplanned |  | N | Event not finalised - awaiting Extract update(s) | September | 2014 | 2015Q1 | 2015 |  |  |  |  | Unknown | Unknown | 2014-09-25 | N | 85 | N | 10 | N | N | 1.1101 | 39.4971 | 6956.9352
[7 empty] | 13745 | 12872 | 1156094 | 2014-09-25 08:48 | 2014-09-25 10:24 | 96 | 11kV | 12256 | 582 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142198 1 fault operation A & B phase Instantaneous Overcurrent feeder tripped on try back of DOLF 5810 Stewart Ave. then broken tapping found at pole JU-62202. Excluded oms 1156116 & 1156094 | September | 2014 | 2015Q1 | 2015 | 202:34232 | 202:34232 | ZN00202/034232 | NEWCASTLE | OH | Not Veg | 2014-09-25 | N | 21.0584 | N | 10 | N | N | 1.1101 | 39.4971 | 8956.3233
[7 empty] | 14445 | 18261 | 1156276 | 2014-09-25 13:55 | 2014-09-25 15:30 | 95 | 11kV | 570 | 6 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S5716 Conrail Park Mcpherson - 11kV / 415V No1 Tx failed RMI #1 and Tx #1 isolated restored via Tx #2 | September | 2014 | 2015Q1 | 2015 | ZN35700:PA1 | ZN340:PA32 | ZN00340/000032 | BAYSIDE | UG | Not Veg | 2014-09-25 | N | 95 | N | 10 | N | N | 1.1101 | 39.4971 | 416.5392
[7 empty] | 13490 | 10873 | 1156290 | 2014-09-25 14:26 | 2014-09-25 16:40 | 134 | 11kV | 536 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142211 Single phase DOLF : 10 Amp Blew both 10 A DOLF's Excluded OMS 1156290 | September | 2014 | 2015Q1 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-09-25 | N | 134 | N | 10 | N | N | 1.1101 | 39.4971 | 391.693
[7 empty] | 13646 | 12092 | 1156367 | 2014-09-25 17:04 | 2014-09-25 17:50 | 46 | 11kV | 25254 | 549 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn4545 Meadowbank section of Pa41 Reclsoer 46120 Lovell Russell tripped, reclosed and lockout out on timed overcurrent Tree branch on 11kv outside 20 Hunts Ave | September | 2014 | 2015Q1 | 2015 | ZN4545:PA41 | ZN4545:PA41 | ZN04545/000041 | RYDE | OH | Veg | 2014-09-25 | N | 46 | N | 10 | N | N | 1.1101 | 39.4971 | 18454.8783
[7 empty] | 13618 | 11872 | 1156296 | 2014-09-25 14:33 | 2014-09-25 18:45 | 252 | 11kV | 504 | 2 | HV | 3rd Party Vehicle | 3rd Party Impact | O/H Conductor Bare | Unplanned | Rain Light | N | LID 142210 A phase DOLF 10 Amp service mains pulled down by vehicle.Don Evans of 938 Mandalong Rd (car BJQ-94Q) stated he hit low service wire to NO695, he was uninjured but car sustained panel damage & ripped off roof racks.Dave Hedger advised & photos to be emailed.Damage to LV equip on sub pole.Suspect LV short circuit operated DOLF.NO695 insulation on 2 bays of 25mmXLPE aerial con mains were deteriorated on neutral due to exposure to elements. Refer to 1156296 for more info on corrective actions taken | September | 2014 | 2015Q1 | 2015 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2014-09-25 | N | 252 | N | 10 | N | N | 1.1101 | 39.4971 | 368.3083
[7 empty] | 14207 | 16553 | 1156358 | 2014-09-25 16:36 | 2014-09-25 19:50 | 194 | 11kV | 1706 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 142208/04 A & C phase : 10 Amp A and C phase line DOLFs blown. Note on load side of C Phase DOLF tapping had blown off and had to be remade. | September | 2014 | 2015Q1 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-09-25 | N | 131.2308 | N | 10 | N | N | 1.1101 | 39.4971 | 1246.6945
[7 empty] | 14351 | 17574 | 1156395 | 2014-09-25 19:34 | 2014-09-25 20:20 | 46 | 11kV | 56028 | 1218 | HV | Animal Possum | Animal | Recloser / Sectionaliser | Unplanned | Unselected | N | Zn195 Pymble 11kv Pa30 S49345 Suakin Council Works: fdr tripped Relays: A+B phase timed overcurrent & EFI Signals: 11kv trip, Zoen Earth, No.1 Group Earth EFI: S49345 S6830 S7562 S4938 S4939 S47451 S4940 Possum across 11kv bushing on recloser 46113 Fiddens Whard Coronga S5126 Primula Dorman Dist 1 "Dorman Cres" in LV// when Pa30 @ Pymble failed. Supple restored with restoration of feeder See 1157005 exclude 1156395,7 | September | 2014 | 2015Q1 | 2015 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Not Veg | 2014-09-25 | N | 46 | N | 10 | N | N | 1.1101 | 39.4971 | 40943.6099
[7 empty] | 14135 | 16081 | 1156389 | 2014-09-25 18:38 | 2014-09-25 20:35 | 117 | 11kV | 234 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142215 Single phase dist fuse : 10 Amp Excluded OMS 1156389 | September | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2014-09-25 | N | 117 | N | 10 | N | N | 1.1101 | 39.4971 | 171.0003
[7 empty] | 14322 | 17338 | 1156405 | 2014-09-25 21:02 | 2014-09-25 23:30 | 148 | 11kV | 296 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 142216 Single phase DOLF : 10 Amp 256V, 17A Excluded OMS 1156405 | September | 2014 | 2015Q1 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-09-25 | N | 148 | N | 10 | N | N | 1.1101 | 39.4971 | 216.3081
[7 empty] | 14085 | 15693 | 1156543 | 2014-09-26 11:40 | 2014-09-26 13:40 | 120 | 11kV | 360 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 142222 Single phase DOLF : 10 Amp Excluded OMS 1156543 | September | 2014 | 2015Q1 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2014-09-26 | N | 120 | N | 1 | N | N | 1.1101 | 39.4971 | 263.0774
[7 empty] | 14129 | 16063 | 1156792 | 2014-09-28 00:05 | 2014-09-28 02:40 | 155 | 11kV | 1240 | 8 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 142231 CAR HIT POLE KS-60220 Medowie Rd Excluded OMS 1156792, 1156793, 1156794 | September | 2014 | 2015Q1 | 2015 |  |  |  |  | OH | Not Veg | 2014-09-28 | N | 155 | N | 1 | N | N | 1.1101 | 39.4971 | 906.1554
[7 empty] | 14077 | 15649 | 1156884 | 2014-09-29 00:37 | 2014-09-29 02:25 | 108 | 11kV | 216 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142234 A phase DOLF : 10 Amp Excluded OMS 1156884 | September | 2014 | 2015Q1 | 2015 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2014-09-29 | N | 108 | N | 7 | N | N | 1.1101 | 39.4971 | 157.8464
[7 empty] | 13987 | 14807 | 1156985 | 2014-09-29 09:44 | 2014-09-29 13:20 | 216 | 11kV | 126402 | 971 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S116 Leichhardt Panel 49 Trafalgar Booth feeder tripped on: A phase IOC fault check EFI Field efi: S8923, S1088 Remarks: UG cable fault from S61430 to S5924. Faulty EFI indications. (Some DC's on Panel 49 have no customers listed in OMS) | September | 2014 | 2015Q1 | 2015 | ZN116:PA49 | ZN116:PA23 | ZN00116/000023 | INNER WEST | UG | Not Veg | 2014-09-29 | N | 130.1771 | N | 7 | N | N | 1.1101 | 39.4971 | 92370.8534
[7 empty] | 12354 | 948 | 1157150 | 2014-09-29 13:38 | 2014-09-29 14:35 | 57 | 11kV | 64020 | 1601 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 142238 2 fault operation C Phase Overcurrent; Earth fault Excluded OMS 1157150; 1157154 | September | 2014 | 2015Q1 | 2015 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | Unknown | Unknown | 2014-09-29 | N | 39.9875 | N | 7 | N | N | 1.1101 | 39.4971 | 46783.9277
[7 empty] | 13976 | 14724 | 1157240 | 2014-09-29 16:14 | 2014-09-29 17:38 | 84 | 11kV | 112550 | 1741 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12600 Lisarow Pa3 CB tripped on Relays: C phase OC Signals: 11kv trip Entire feeder patrolled. No cause found See 1157384,5,94 Exclude 1157240 | September | 2014 | 2015Q1 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2014-09-29 | N | 64.6468 | N | 7 | N | N | 1.1101 | 39.4971 | 82248.2203
[7 empty] | 13691 | 12435 | 1157215 | 2014-09-29 15:21 | 2014-09-29 17:45 | 144 | 11kV | 88518 | 1213 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At Zn15001 Brookvale, 11kv Panel 6L 'Winbourne Rd' feeder tripped. Relays: Earth fault, Fault check, efi Signals: 11kv trip Field efi's: S16892, S15189, S16948, S16027, S16636, S16816, S50675, S16933 Abnormal: Section of defective 11kv feeder isolated at AB24223 to N/O AB22547 to N/O Sw/B @ S15939 Headland Rd 226 Remarks: 11kv UGOH to S17046 Francis Lewis Sw/B has exploded (reference Dee Why West Sht 1 C7) L/W has broken 11kv bonds at pole FF 56214 | September | 2014 | 2015Q1 | 2015 | ZN15001:PA6 | ZN15001:PA6 | ZN15001/000006 | NORTHERN BEACHES | Unknown | Unknown | 2014-09-29 | N | 72.9744 | N | 7 | N | N | 1.1101 | 39.4971 | 64686.3436
[7 empty] | 13734 | 12799 | 1157151 | 2014-09-29 13:45 | 2014-09-29 19:05 | 320 | 11kV | 21440 | 67 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | At PT15799 Delaigh Av, 11kv footpath side drop out fuse and surge arrestor exploded. Ex Zn15001 Brookvale, 11kv panel 8 'Harbourd Rd' feeder Remarks: Fuse failure. At PT 15799 Delaigh Av, 11kv footpath side drop out fuse and surge arrestor exploded. 11kv dropper came into contact with LV. 11kv feeder isolateed at/from S.17093 Fairport Pitt to S46596 Playfair Pitt tee PT15799 Delaigh Rd. LV//: usl's 29229, 25916, 7439, sw/tag at S17093 Related jobs: #1157171, 1157161, 1157173, 1157151 | September | 2014 | 2015Q1 | 2015 | ZN15001:PA8 | ZN15001:PA8 | ZN15001/000008 | NORTHERN BEACHES | OH | Not Veg | 2014-09-29 | N | 320 | N | 7 | N | N | 1.1101 | 39.4971 | 15667.7196
[7 empty] | 14448 | 18284 | 1157312 | 2014-09-29 23:38 | 2014-09-30 01:16 | 98 | 11kV | 84831 | 1043 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | Unselected | N | Zn630 Mascot - Pnl.20 "Transformer #3" tripped on C phase overload and multitrip relays. While closing Pnl.22 on transfer bar it "shot through' and flagged on EFI. Possible fault on pnl 22 with protection malfunction (under investigation) see 1157331 1157332 1157333 1157334 1157335 1157336 | September | 2014 | 2015Q1 | 2015 | ZN630:PA24 | ZN630:PA24 | ZN00630/000024 | BAYSIDE | Unknown | Not Veg | 2014-09-29 | N | 81.3337 | N | 7 | N | N | 1.1101 | 39.4971 | 61991.9927
[7 empty] | 13121 | 7787 | 1157317 | 2014-09-30 03:25 | 2014-09-30 04:31 | 66 | 11kV | 25131 | 471 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 33 - B & C phase OC, Field EFIs. B phase HDO blown at PT 9451. Isolated PT and restored supply. ME: 1157839. Rest Step: 1157840. Withdrawn: 1157317, 8. | September | 2014 | 2015Q1 | 2015 | ZN9550:PA33 | ZN9550:PA33 | ZN09550/000033 | SUTHERLAND | OH | Not Veg | 2014-09-30 | N | 53.3567 | N | 8 | N | N | 1.1101 | 39.4971 | 18364.9936
[7 empty] | 12540 | 2696 | 1157319 | 2014-09-30 05:28 | 2014-09-30 06:19 | 51 | 11kV | 65739 | 1289 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 3 - A & B phase OC. Possum at 4 Mowbray Road, Sylvania. ME: 1157319. Withdrawn: 1157320, 1. | September | 2014 | 2015Q1 | 2015 | ZN9550:PA3 | ZN9550:PA3 | ZN09550/000003 | SUTHERLAND | OH | Not Veg | 2014-09-30 | N | 51 | N | 8 | N | N | 1.1101 | 39.4971 | 48040.1222
[7 empty] | 13059 | 7275 | 1157322 | 2014-09-30 05:44 | 2014-09-30 09:15 | 210.6333 | 11kV | 842.5333 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 142245 C phase DOLF : 10 Amp CC1: 22-"Refer to SOp" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | September | 2014 | 2015Q1 | 2015 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2014-09-30 | N | 210.6333 | N | 8 | N | N | 1.1101 | 39.4971 | 615.6985
[7 empty] | 13326 | 9494 | 1157337 | 2014-09-30 07:25 | 2014-09-30 12:35 | 310 | 11kV | 40086 | 300 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | CCT 11kV O/S 26 Sorlie Rd, Frenchs Forest was on ground. Section of feeder interrupted by A.Op and earthed to allow mains to carry out repairs. EMSO to check services due to suspected contact between HV and LV mains | September | 2014 | 2015Q1 | 2015 | ZN15005:PA4 | ZN15005:PA4 | ZN15005/000004 | NORTHERN BEACHES | OH | Not Veg | 2014-09-30 | N | 133.62 | N | 8 | N | N | 1.1101 | 39.4971 | 29293.6665
[7 empty] | 13939 | 14480 | 1157578 | 2014-09-30 12:56 | 2014-09-30 13:25 | 29 | 11kV | 18047 | 631 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S262 Marrickville Panel 20 Smith Victoria feeder tripped on : Earth Leakage EFI Fault Check Remarks: UG fault. UG fault in feeder from S262 Marrickville P20 to SW/A S6398 Smith Victoria Related jobs: #1157579, 1157578, 1158244 | September | 2014 | 2015Q1 | 2015 | ZN262:PA20 | ZN262:PA20 | ZN00262/000020 | INNER WEST | UG | Not Veg | 2014-09-30 | N | 28.6006 | N | 8 | N | N | 1.1101 | 39.4971 | 13188.2153
[7 empty] | 14091 | 15724 | 1157558 | 2014-09-30 12:27 | 2014-09-30 15:59 | 212 | 11kV | 58350 | 434 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | AT S3472 Sefton Panel 29 Joanne Court Fdr tripped on: A Phase overcurrent earthfault EFI fault check reclose time delay lockout 1st 3 EFI's only Down Remarks: UG fault. Related jobs: #1157558, 1157580, 1158295, 1157572, 1158297, 1158296 | September | 2014 | 2015Q1 | 2015 | ZN3472:PA29 | ZN3472:PA29 | ZN03472/000029 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-09-30 | N | 134.447 | N | 8 | N | N | 1.1101 | 39.4971 | 42640.459
[7 empty] | 12285 | 304 | 1157660 | 2014-09-30 15:40 | 2014-09-30 17:38 | 118 | 11kV | 46540 | 570 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | AT S1285 Greenacre Park Panel 22 Jacobs Heath tripped on: Earth leakage with EFI fault check Field EFIs to S6052 Remarks: UG fault. UG cable fault in feeders rom S6494 to S3468 Sw/D to Sw/A at S7015 Related jobs: #1157660, 1157662, 1158259, 1158283, 1158257 | September | 2014 | 2015Q1 | 2015 | ZN1285:PA22 | ZN1285:PA22 | ZN01285/000022 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-09-30 | N | 81.6491 | N | 8 | N | N | 1.1101 | 39.4971 | 34010.0593
[7 empty] | 13136 | 7869 | 1157747 | 2014-09-30 22:30 | 2014-10-01 01:06 | 156 | 11kV | 115149 | 812 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | At S35370 Galston Panel 10 tripped reclosed tripped and locked out on Relays: B and C phase with EFI Signals: Lockout, Timing Abnormal Switching: SW/A Closed At S8401 LB487 Open Cause not ascertained for outage See OMS 1157789 1157792 1157793 1157747 1152248 | September | 2014 | 2015Q1 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2014-09-30 | N | 141.8091 | N | 8 | N | N | 1.1101 | 39.4971 | 84147.4929
[7 empty] | 13338 | 9646 | 1157754 | 2014-10-01 03:22 | 2014-10-01 05:15 | 113 | 11kV | 88146 | 976 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | At S.3154 St Ives, 11kV panel 10 Fdr CB tripped on A phase IOC and timed OC with efi. Field efi's down at S.7763, S.4911 and S.4912. Possum on UG/OH to PT.1642 | October | 2014 | 2015Q2 | 2015 | ZN3154:PA10 | ZN3154:PA10 | ZN03154/000010 | KU-RING-GAI | OH | Not Veg | 2014-10-01 | N | 90.3135 | N | 9 | N | N | 1.1101 | 39.4971 | 64414.4969
[7 empty] | 14398 | 17918 | 1157756 | 2014-10-01 03:51 | 2014-10-01 05:15 | 84 | 11kV | 132159 | 1741 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Zn12600 Lisarow Pa3 tripped on Relays: C phase timed overcurrent Signals: 11kv trip Cause not ascertained See 1157869,70,1 Exclude 1157756 | October | 2014 | 2015Q2 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2014-10-01 | N | 75.9098 | N | 9 | N | N | 1.1101 | 39.4971 | 96577.8992
[7 empty] | 13123 | 7802 | 1157877 | 2014-10-01 09:48 | 2014-10-01 10:29 | 41.3 | 11kV | 48321 | 1170 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 142261 2 fault operations B & C phase Overcurrent tree on ohm at sub 9860 Excluded oms 1157879,1157881 | October | 2014 | 2015Q2 | 2015 | 238:34147 | 532:83301 | ZN00532/083301 | MAITLAND | OH | Veg | 2014-10-01 | N | 41.3 | N | 9 | N | N | 1.1101 | 39.4971 | 35311.5616
[7 empty] | 13205 | 8463 | 1157784 | 2014-10-01 07:15 | 2014-10-01 10:55 | 220 | 11kV | 111170 | 1036 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At Zn3425 Castle Cove Panel 44 Tripped Tree removed from O/S Linden St Removed By OH. See OMS 1159475 1159510 1159514 1159478 1159477 1157784 1157773 1157794 1157825 1157830 1157786 Note: Based on customer callssuspect S8354#3 and S326#2 were in parallel with Panel 44 at the time of interruption | October | 2014 | 2015Q2 | 2015 | ZN3425:PA44 | ZN3425:PA44 | ZN03425/000044 | WILLOUGHBY | OH | Veg | 2014-10-01 | N | 107.3069 | N | 9 | N | N | 1.1101 | 39.4971 | 81239.757
[7 empty] | 13153 | 7999 | 1157919 | 2014-10-01 10:46 | 2014-10-01 12:42 | 116 | 11kV | 232686 | 2112 | HV | Vegetation Blow/Fall In | Vegetation | UGOH | Unplanned | Unselected | N | Zn124570 Avoca Pa37 "Avoca Beach fdr tripped Relays: ABC phase IOC, EFI EFI's: S18438 S49066 S18135 S14561 S14562 S14563, EFI cnr Willow & Moores Note: remote viewable EFI oeprated but no remote indication on DNMS Tree branch on UGOH pole AV499 in Hillside rd Avoca. Mains to inspect and arrange vermin proofing See 1158662,3,4,5 GIS 1157931 Exclude 1157919 | October | 2014 | 2015Q2 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2014-10-01 | N | 110.1733 | N | 9 | N | N | 1.1101 | 39.4971 | 170040.0657
[7 empty] | 14142 | 16129 | 1157828 | 2014-10-01 08:28 | 2014-10-01 13:25 | 297 | 11kV | 891 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142277 B phase DOLF : 10 Amp VOLTS A=248 B= 247 C= 250. Excluded OMS REPORT NO 1157828. | October | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-10-01 | N | 297 | N | 9 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 13142 | 7948 | 1158137 | 2014-10-01 18:47 | 2014-10-01 19:28 | 41 | 11kV | 14594 | 426 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn7481 Darling Harbour - Pnl.14 tripped on: Pnl.14 Left - B phase O/C & Earth Fault, Tx No 12 earth fault check relay Field EFIs: S8986 & S7946 UG cable fault between S7946 (Sw B) and S7729 (Sw A) see 1158194 1158195 | October | 2014 | 2015Q2 | 2015 | ZN7481:PA14 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2014-10-01 | N | 34.2582 | N | 9 | N | N | 1.1101 | 39.4971 | 10664.8647
[7 empty] | 12621 | 3400 | 1158135 | 2014-10-01 18:41 | 2014-10-01 19:30 | 49 | 11kV | 43267 | 883 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn342 Paddington - Pnl.35 tripped on: Overcurrent & earth fault, C phase + Neutral, EFI, Tx#4 Earth fault check relay Front line UG feeder fault - Pnl.35 to S4371 (Sw A) to S1681 (Sw D) see 1158188 Others: 1158189 1158190 1158191 | October | 2014 | 2015Q2 | 2015 | ZN342:PA35 | ZN342:PA35 | ZN00342/000035 | SYDNEY | UG | Not Veg | 2014-10-01 | N | 49 | N | 9 | N | N | 1.1101 | 39.4971 | 31618.2474
[7 empty] | 12905 | 6022 | 1158155 | 2014-10-01 22:26 | 2014-10-02 00:53 | 147 | 11kV | 149166 | 1294 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At Zn2635 Epping Panel 57 tripped on C phase overcurrent Signals: EFI. Cause: Suspect fault on 11kV UG cable fault between S5537 and IS3082 tee PT1934. See OMS 1159465 1159468 1158158 1158155 1158156 Note: Based on customer comments and LV parallel database - Suspect S5537 was in parallel with S5355 at the time of interruption | October | 2014 | 2015Q2 | 2015 | ZN2635:PA57 | ZN2635:PA57 | ZN02635/000057 | PARRAMATTA | UG | Not Veg | 2014-10-01 | N | 115.2751 | N | 9 | N | N | 1.1101 | 39.4971 | 109006.1131
[7 empty] | 13823 | 13431 | 1158206 | 2014-10-02 10:00 | 2014-10-02 13:20 | 200 | 11kV | 600 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142291 A Phase HV Tapping broken at pole AH-42113 Excludes OMS 1158206 | October | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-10-02 | N | 200 | N | 3 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 14482 | 18557 | 1158523 | 2014-10-02 18:36 | 2014-10-02 20:15 | 99 | 11kV | 396 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142295 A & B Phases: Fuse size: 10 Amp Substation DOLF Excludes OMS 1158523 | October | 2014 | 2015Q2 | 2015 | 503:48017 | 532:83307 | ZN00532/083307 | MAITLAND | OH | Not Veg | 2014-10-02 | N | 99 | N | 3 | N | N | 1.1101 | 39.4971 | 289.3851
[7 empty] | 14530 | 18955 | 1158553 | 2014-10-02 23:09 | 2014-10-03 00:38 | 89 | 11kV | 183114 | 2257 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 690 Campsie - Pnl 25 - A phase IOC and timed OC, EFI, Fault Check. Front line underground feeder fault. ME: 1159312. Rest Steps: 1159313, 4, 5. Withdrawn: 1158553. | October | 2014 | 2015Q2 | 2015 | ZN690:PA25 | ZN690:PA25 | ZN00690/000025 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-10-02 | N | 81.1316 | N | 3 | N | N | 1.1101 | 39.4971 | 133814.3103
[7 empty] | 14449 | 18285 | 1158574 | 2014-10-03 08:06 | 2014-10-03 09:34 | 88 | 11kV | 7128 | 81 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn630 Mascot - Pnl.34 tripped on Earth leakage with EFI - UG Cable fault between S35380 Dunning Hayes no 3 to S3814 Hayes Roth At the same time: Tx #6 @ Mascot zone tripped on SR Aux relay only - Protection malfunction from Pnl.34 trip Abnormal: Bus Couplers non auto due to Tx #3 out of service see 1159454 1159455 1159456 1159457 GIS: 1158586 | October | 2014 | 2015Q2 | 2015 | ZN630:PA34 | ZN630:PA34 | ZN00630/000034 | SYDNEY | UG | Not Veg | 2014-10-03 | N | 88 | N | 1 | N | N | 1.1101 | 39.4971 | 5208.9322
[7 empty] | 14035 | 15324 | 1158929 | 2014-10-04 13:53 | 2014-10-04 18:35 | 282 | 11kV | 7896 | 28 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142312 interrupt to repair HV tapping at pole FU-54226 to sub 50501 Excluded oms 1158929 | October | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-10-04 | N | 282 | N | 2 | N | N | 1.1101 | 39.4971 | 5770.1639
[7 empty] | 14409 | 17981 | 1158946 | 2014-10-04 16:33 | 2014-10-04 18:40 | 127 | 11kV | 75138 | 770 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Sub 874 Concord Zn Panel #3 labelled Sub 5667 and Aux tripped on C phase OC, EFI, 11kv trip ZE and #4 GE Field EFIs Sub 35569 Remarks: UG fault. Section of 11kv feeder from Sub 2031 Llewellan St to Sub 35669 Gauthorpe Marquet tee to Sub 6141 Llewellan Cropley Underground fault. | October | 2014 | 2015Q2 | 2015 | ZN874:PA3 | ZN874:PA3 | ZN00874/000003 | CANADA BAY | UG | Not Veg | 2014-10-04 | N | 97.5818 | N | 2 | N | N | 1.1101 | 39.4971 | 54908.6342
[7 empty] | 12258 | 37 | 1159040 | 2014-10-05 15:58 | 2014-10-05 16:30 | 32.1667 | 11kV | 29689.8333 | 923 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | ZN 9550 Gwawley Bay - Pnl 42 - B & C phase OC, Earth Fault, EFI, Field EFIs. Lightning arrestor failed in service at UGOH to AB 39348 near 151 Corea St. | October | 2014 | 2015Q2 | 2015 | ZN9550:PA42 | ZN9550:PA42 | ZN09550/000042 | SUTHERLAND | OH | Not Veg | 2014-10-05 | N | 32.1667 | N | 1 | N | N | 1.1101 | 39.4971 | 21696.4545
[7 empty] | 13784 | 13179 | 1159089 | 2014-10-06 01:16 | 2014-10-06 01:44 | 28 | 11kV | 854 | 40 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn2602 Clovelly - Pnl.24 tripped on: EF timed, EF instantaneous, EFI UG Cable fault (11kV) between Zn2602 Clovelly (Pnl.24) and S1087 (Sw F) and S500 (Sw A) | October | 2014 | 2015Q2 | 2015 | ZN2602:PA24 | ZN2602:PA27 | ZN02602/000027 | RANDWICK | UG | Not Veg | 2014-10-06 | N | 21.35 | N | 5 | N | N | 1.1101 | 39.4971 | 624.078
[7 empty] | 12368 | 1060 | 1159136 | 2014-10-06 12:02 | 2014-10-06 13:48 | 106 | 11kV | 92417 | 907 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN 9700 Kirrawee - Pnl 19 - Earth Leakage, Field EFIs. Underground fault between S 9410 to S 9023. ME: 1159302. Rest Step: 1159304. ME GIS: 1159141. Withdrawn: 1159136. | October | 2014 | 2015Q2 | 2015 | ZN9700:PA19 | ZN9700:PA19 | ZN09700/000019 | SUTHERLAND | UG | Not Veg | 2014-10-06 | N | 101.8931 | N | 5 | N | N | 1.1101 | 39.4971 | 67535.6178
[7 empty] | 13934 | 14446 | 1159159 | 2014-10-06 14:51 | 2014-10-06 17:00 | 129 | 11kV | 9159 | 71 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | PT63491 Evans Irene Dist 1 & Dist 2 interrupted by DOp for safety. Car hit Pole with PT. Tx requires replacement. Tx has come off pole on ground with oil spilling out of it. See 1159254 exclude 1159159,60,1,3,5 | October | 2014 | 2015Q2 | 2015 | ZN12620:PA3 | ZN12620:PA3 | ZN12620/000003 | CENTRAL COAST | OH | Not Veg | 2014-10-06 | N | 129 | N | 5 | N | N | 1.1101 | 39.4971 | 6693.1271
[7 empty] | 13418 | 10303 | 1159168 | 2014-10-06 15:40 | 2014-10-06 17:42 | 122 | 11kV | 150928 | 1475 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12650 West Gosford section of Pa1 "Bentley rd" fdr Recloser 44936 Bentley Rd tripped on SEL Cause not ascertained tripped on SEL when trying back from LB41121 to LB41131 to S14947 Fdr from LB41121 to LB41131 to S14947 sw:A isolated. Load reads Aph 46Amp Bph 240Amp Cph 45Amp @ RE44936 See 1159266,8,70 Exclude 1159168 | October | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-10-06 | N | 102.3241 | N | 5 | N | N | 1.1101 | 39.4971 | 110293.7308
[7 empty] | 12541 | 2698 | 1159188 | 2014-10-06 19:18 | 2014-10-06 20:18 | 60 | 11kV | 83120 | 1416 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1164 Rose Bay (old) - Pnl.57 tripped on: IOC, Earth Fault, EFI UG cable fault from Pnl.57 to S35167 (Sw B) to S471 (Sw A) | October | 2014 | 2015Q2 | 2015 | ZN1164:PA57 | ZN36100:PA5 | ZN36100/000005 | WOOLLAHRA | UG | Not Veg | 2014-10-06 | N | 58.7006 | N | 5 | N | N | 1.1101 | 39.4971 | 60741.6444
[7 empty] | 14407 | 17979 | 1159889 | 2014-10-08 13:04 | 2014-10-08 14:14 | 70 | 11kV | 2814 | 41 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S847 Concord Panel 24 Pomeroy Underwood feeder tripped on: Relays: A phase and Earth leakage, EFI Signals: 11kv trip, Zone Earth, Group Earth EFI's: Nil Remarks: UG fault betwween S847 Concord Panel 24 and S35177 Pomeroy Underwood No.2 Sw/A and S3385 Rothwell Conway Sw/A Related jobs: #1159897, 1159889, 1161181, 1161180 | October | 2014 | 2015Q2 | 2015 | ZN874:PA24 | ZN874:PA24 | ZN00874/000024 | CANADA BAY | UG | Not Veg | 2014-10-08 | N | 68.6341 | N | 4 | N | N | 1.1101 | 39.4971 | 2056.3882
[7 empty] | 13698 | 12507 | 1160111 | 2014-10-08 14:55 | 2014-10-08 15:08 | 13 | 11kV | 130 | 10 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Bond | Unplanned | Unselected | N | LID 142334 See Planned SI 43686. Section of 11kV Fdr isolated to MAKE taps during rain to restore customers supply at subs 54417 & 50739 (planned outage). | October | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-10-08 | N | 13 | N | 4 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 13918 | 14289 | 1159945 | 2014-10-08 15:10 | 2014-10-08 16:40 | 90 | 11kV | 133928 | 1655 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | S.16194 Manly Hospital No.1 SW/B fdr CB tripped Ex ZN.15015 North Head Panel 5 Fdr EFI's:-S.16194, S.16136, S.16721 Cause:- 11kV UGOH below LBS.21129 failed ME:-1160298 RS:-1160301, 1160303, 1160302 Withdrawn:-1159945, 1159947, 1159956, 1159958, 1159959 | October | 2014 | 2015Q2 | 2015 | ZN15015:PA5 | ZN15015:PA5 | ZN15015/000005 | NORTHERN BEACHES | Unknown | Unknown | 2014-10-08 | N | 80.9233 | N | 4 | N | N | 1.1101 | 39.4971 | 97870.6322
[7 empty] | 13688 | 12422 | 1160014 | 2014-10-08 17:40 | 2014-10-09 01:25 | 465 | 11kV | 206241 | 1587 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Ex Zn12580 Erina section of Pa4 "Springfield" Recloseer 49612 Barinya Wells tripped and locked out on overload UG cable fault between USL41076 to USL 44033 tee to PT11155 to S12531 See 1160216,7,8,9,20 Exclude 1160014,44 | October | 2014 | 2015Q2 | 2015 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | UG | Not Veg | 2014-10-08 | N | 129.9565 | N | 4 | N | N | 1.1101 | 39.4971 | 150714.8397
[7 empty] | 14257 | 16950 | 1160105 | 2014-10-09 08:45 | 2014-10-09 20:40 | 715 | 11kV | 4780 | 69 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 142343 Wire off insulator burning x arm ready to fall at pole IV-10016. Isolated for safety Excluded OMS 1160059; 1160082; 1160105, 1160107 & 1160108 | October | 2014 | 2015Q2 | 2015 | 224:80332 | 270:83586 | ZN00270/083586 | LAKE MACQUARIE | OH | Not Veg | 2014-10-09 | N | 69.2754 | N | 2 | N | N | 1.1101 | 39.4971 | 3493.083
[7 empty] | 12854 | 5595 | 1160438 | 2014-10-09 18:48 | 2014-10-09 21:28 | 160 | 11kV | 24160 | 151 | HV | Overload | Utility Process Issue | U/G Cable | Unplanned | No Weather Impact | N | Ex Zn12580 Erina Zone section of Pa4L 11kv fdr from CP41076 to CP44033 tee to PT11155, S12531 interrupted due to MG overload Region tried to restore customers hot water after fdr failure and overloaded MG sets causing them to trip. Feeder was returned to service after repair of UG faulty section. See previouse outage 1160216 See 1160507 exclude 1160443 | October | 2014 | 2015Q2 | 2015 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | UG | Not Veg | 2014-10-09 | N | 160 | N | 2 | N | N | 1.1101 | 39.4971 | 17655.4154
[7 empty] | 13765 | 13028 | 1160872 | 2014-10-11 13:34 | 2014-10-11 15:15 | 101 | 11kV | 34714 | 470 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10990 Arncliffe - Pnl 5 - Trip/reclose/trip, C phase OC, Timing, Lockout, EFI, Field EFI. UGOH went short circuit in section of feeder from LB 31208 to S 10803 tee S 10835. ME: 1161176. Rest Steps: 1161177, 8. Withdrawn: 1160872, 3, 4. | October | 2014 | 2015Q2 | 2015 | ZN10990:PA5 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | Unknown | Unknown | 2014-10-11 | N | 73.8596 | N | 4 | N | N | 1.1101 | 39.4971 | 25367.9673
[7 empty] | 14008 | 15000 | 1160908 | 2014-10-11 17:01 | 2014-10-11 18:34 | 93.3167 | 11kV | 1493.0667 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn14143 Somersby section of Pa6 tripped reclosed tripped and locked out cause not ascertained. :( Note: There was a report of an explosion from pole from one customer off PT13182 | October | 2014 | 2015Q2 | 2015 | ZN14143:PA6 | ZN14143:PA5 | ZN14143/000005 | CENTRAL COAST | OH | Veg | 2014-10-11 | N | 93.3167 | N | 4 | N | N | 1.1101 | 39.4971 | 1091.0891
[7 empty] | 12421 | 1574 | 1160931 | 2014-10-11 23:33 | 2014-10-12 01:22 | 109 | 11kV | 15475 | 142 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ S2196 Milperra Panel 28 'S5922 Mavis Canterbury' feeder tripped on Relays - fault check, EFI, 51N Signals - 11kv trip, ZE, TX2 GE Field EFI's operated @ All DC's Remarks: UG fault. 11kv UG feeder fault from S4353 Gallipoli Eldridge to S49550 Eldridge Antwerp | October | 2014 | 2015Q2 | 2015 | ZN2196:PA28 | ZN2196:PA28 | ZN02196/000028 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-10-11 | N | 108.9789 | N | 4 | N | N | 1.1101 | 39.4971 | 11308.6736
[7 empty] | 13962 | 14659 | 1160920 | 2014-10-11 18:59 | 2014-10-12 15:28 | 1229 | 11kV | 212888 | 529 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" RE45189 Cooks Peats Ridge tripped, reclosed, tripped and locked out RE44945 Found to be defective left isolated mains patrolled found nothing See 1161194,9,200,1,2,3,4,5,7,8,10 Exclude 1160920,9 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2014-10-11 | N | 402.4348 | N | 4 | N | N | 1.1101 | 39.4971 | 155572.2713
[7 empty] | 14683 | 20402 | 1161023 | 2014-10-12 17:47 | 2014-10-12 20:55 | 188 | 11kV | 37987 | 284 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" RE41845 tripped on overcurrent Very Large branch removed from 11kV OH outside 38 Katandera Holgate. EMSO checked LV at effected properties. LV came into contact with high voltage from distributors at PT11346 See 1161227,8 Exclude 1161023,4,8,33,52 | October | 2014 | 2015Q2 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2014-10-12 | N | 133.757 | N | 2 | N | N | 1.1101 | 39.4971 | 27759.7792
[7 empty] | 14092 | 15735 | 1161075 | 2014-10-13 02:57 | 2014-10-13 04:16 | 79 | 11kV | 120081 | 1722 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12660 Woy Woy Pa10 "Ocean Beach Road, etc" fdr tripped on earth fault Signals: 11kv trip and EFI EFI's S12696 Cable Fault between S12617 to S12618 to LB49686. EFI did not operate at S12617. See 1161253,6,8 2nd 1161266 Exclude 1161075 | October | 2014 | 2015Q2 | 2015 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | UG | Not Veg | 2014-10-13 | N | 69.7334 | N | 17 | N | N | 1.1101 | 39.4971 | 87751.653
[7 empty] | 14653 | 20149 | 1160947 | 2014-10-12 07:33 | 2014-10-13 08:00 | 1467 | 11kV | 147271 | 1337 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn2835 Burwood 11kv Panel #31 labelled "S2265 & S5392 tee S3126" tripped on Relays: Earth fault, EFI, Fault check Signals: No.1 Group Earth, 11kv trip, Zone Earth Field EFI's: S2265, S4872, S5392, S2879, S3851, S4130 Remarks: 11kv feeder fault from: S4130 Weeroona Rd North (Sw/B) to S3746 Weeroona Centenary No.2 (Sw/A) tee S850 Rookwood Cemetary No.2 & S879 Rookwood Cemetary No.3 Related jobs: #1160947, 1160977, 1160978, 1161814, 1161813, 1161809 | October | 2014 | 2015Q2 | 2015 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2014-10-12 | N | 110.1503 | N | 2 | N | N | 1.1101 | 39.4971 | 107621.303
[7 empty] | 12262 | 67 | 1161078 | 2014-10-13 05:54 | 2014-10-13 11:48 | 354 | 11kV | 8402 | 28 | HV | Animal Bird | Animal | DC PT | Unplanned | Electrical Storm | N | LID 142380 B & C phase DOLF : 20 Amp Pelican found near Shearman G sub 26542. | October | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2014-10-13 | N | 300.0714 | N | 17 | N | N | 1.1101 | 39.4971 | 6139.9338
[7 empty] | 14131 | 16068 | 1161209 | 2014-10-13 10:28 | 2014-10-13 13:02 | 154 | 11kV | 6765 | 70 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Road" RE44994 Mangrove Creek tripped, reclosed, tripped, reclosed and tripped on Relays: Overcurrent DOp's patrolled feeder and no problem was found. See 1161766,,8,9,70 Exclude 1161209 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2014-10-13 | N | 96.6429 | N | 17 | N | N | 1.1101 | 39.4971 | 4943.6625
[7 empty] | 12614 | 3319 | 1161320 | 2014-10-13 13:57 | 2014-10-13 15:47 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142391 Single phase DOLF : 10 Amp Excluded OMS 1161320 | October | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-10-13 | N | 110 | N | 17 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 13462 | 10659 | 1161453 | 2014-10-13 18:22 | 2014-10-13 19:13 | 51 | 11kV | 87516 | 1716 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Electrical Storm | N | At S4545 Meadowbank Panel 29 tripped on A and C phase Overcurrent, Earth Fault and EFI Signals: 11kV Trip Cause: Lightning Strike at AB1595 (Common Pole With Top Ryde Pa22) See OMS 1161659 1161453 1161523 1161520 1161476 NOTE: BASED on customer calls and LV parallel tracking database PT1136#1 was in parallel with PA29 at teh time of interruption | October | 2014 | 2015Q2 | 2015 | ZN4545:PA29 | ZN4545:PA29 | ZN04545/000029 | RYDE | OH | Not Veg | 2014-10-13 | N | 51 | N | 17 | N | N | 1.1101 | 39.4971 | 63954.1115
[7 empty] | 12331 | 727 | 1161446 | 2014-10-13 18:19 | 2014-10-13 19:20 | 61 | 11kV | 2684 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | Ex Zn12650 West Gosford section of Pa1 "Dog Trap rd" RE44853 Ourimbah Bumble tripped & locked out on overcurrent, Lockout Branch removed by DOp from PT14120 | October | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-10-13 | N | 61 | N | 17 | N | N | 1.1101 | 39.4971 | 1961.388
[7 empty] | 13127 | 7814 | 1161454 | 2014-10-13 18:23 | 2014-10-13 20:24 | 121 | 11kV | 136246 | 1126 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | At S1673 Turramurra Panel 6 Tripped on Earth Fault, Fault Check with EFI. Cause: Falling Tree branch tripped 11kV Feeder and brough down streetlight conductor outside 19 Koombalah Ave See OMS 1161742 1161454 See OMS 1161742 1161454 1161516 1161514 1161514 NOTE: BAsed on Customer calls and LV parallel tracking database PT1543 was in Parallel with Panel 6 at time of interruption | October | 2014 | 2015Q2 | 2015 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Veg | 2014-10-13 | N | 121 | N | 17 | N | N | 1.1101 | 39.4971 | 99564.5582
[7 empty] | 13486 | 10854 | 1161549 | 2014-10-13 19:30 | 2014-10-13 20:35 | 65 | 11kV | 130 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142398 B & C phase DOLF : 10 Amp 3 X HV FUSES REPLACED | October | 2014 | 2015Q2 | 2015 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2014-10-13 | N | 65 | N | 17 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 14663 | 20232 | 1161445 | 2014-10-13 18:25 | 2014-10-13 21:45 | 200 | 11kV | 146192 | 1960 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Rain Wind Storm | N | @ZN1285 Greenacre Park Panel #27 labelled 'Stiller Place Etc" tripped and locked out. Relays: 'C' phase O/C, E/F, lock-out Signals: ZE, 11kv Trip Remarks: AB 15 has been hit by lightning. 11kv bonds have been broken away Related jobs: 1161510, 1161508, 1161498, 1161493, 1161487, 1161470, 1161469, 1161459, 1161456, 1161750, 1161751, 1161752, 1161745, 1161737, 1161734, 1161753, 1161445 | October | 2014 | 2015Q2 | 2015 | ZN1285:PA27 | ZN1285:PA27 | ZN01285/000027 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-10-13 | N | 74.5878 | N | 17 | N | N | 1.1101 | 39.4971 | 106832.8017
[7 empty] | 12505 | 2302 | 1161467 | 2014-10-13 18:24 | 2014-10-14 00:47 | 383 | 11kV | 512071 | 1337 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa9 "Wyoming South" RE47607 Toomeys rd tripped & locked out on o/c, lockout Large tree came down | October | 2014 | 2015Q2 | 2015 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2014-10-13 | N | 383 | N | 17 | N | N | 1.1101 | 39.4971 | 374206.3833
[7 empty] | 12434 | 1690 | 1161608 | 2014-10-13 22:35 | 2014-10-14 01:00 | 144.6333 | 11kV | 6508.5 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142400 A & C phase DOLF : 16 Amp CC1: 22-"Refer to SOp" | October | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-10-13 | N | 144.6333 | N | 17 | N | N | 1.1101 | 39.4971 | 4756.2198
[7 empty] | 14099 | 15794 | 1161448 | 2014-10-13 18:20 | 2014-10-14 01:18 | 418 | 11kV | 154346 | 1153 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | At S965 Pennant Hills Panel 11 Tripped Reclosed tripped and locked out on Relays: Overcurrent and Earth Fault IOC with Timed, Reclose Timer, Lockout, Earth Fault Signals: 11kV Trip Cause: 11kV wires down between LB46768 AB307 and IS2359 on LB46768 side of Gully See OMS 1171947 1171955 11741958 1161448/496/555 | October | 2014 | 2015Q2 | 2015 | ZN965:PA11 | ZN965:PA17 | ZN00965/000017 | HORNSBY | OH | Not Veg | 2014-10-13 | N | 133.8647 | N | 17 | N | N | 1.1101 | 39.4971 | 112791.5044
[7 empty] | 14316 | 17316 | 1161615 | 2014-10-13 23:17 | 2014-10-14 01:35 | 138 | 11kV | 162456 | 1215 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | At Zn847 Hornsby Panel 23 tripped reclosed tripped and locked out on B phase timed, C phase IOC, Fault Check, Lockout Timing and EFI. Signals: Zone Earth, TX2 Group Earth and 11kB Trip. Cause: 11kV cable fault from S6978 to S8630 to S4254 See OMS 1161772 1161778 1161775 1161622 1161615 | October | 2014 | 2015Q2 | 2015 | ZN847:PA23 | ZN847:PA23 | ZN00847/000023 | HORNSBY | UG | Not Veg | 2014-10-13 | N | 133.7086 | N | 17 | N | N | 1.1101 | 39.4971 | 118718.0532
[7 empty] | 13263 | 8840 | 1161441 | 2014-10-13 18:05 | 2014-10-14 01:45 | 460 | 11kV | 23210 | 100 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" RE44995 Kulnura tripped & locked out on overcurrent & IOC Section of 11kv OH between AB44109 to USL42325 tee to PT12245 & PT13322 See 1161825,7,8 Exclude 1161441,60 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-10-13 | N | 232.1 | N | 17 | N | N | 1.1101 | 39.4971 | 16961.1834
[7 empty] | 13212 | 8494 | 1161442 | 2014-10-13 18:07 | 2014-10-14 02:45 | 518 | 11kV | 22836 | 66 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" RE45035 Mangrove Mountain tripped & locked out on Earth Fault, Lockout 5 Bays of HV Mains down in Lillicraps rd See 1161836,7 Exclude 1161442,99,509 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Veg | 2014-10-13 | N | 346 | N | 17 | N | N | 1.1101 | 39.4971 | 16687.8753
[7 empty] | 13672 | 12291 | 1161478 | 2014-10-13 18:35 | 2014-10-14 11:35 | 1020 | 11kV | 69483 | 93 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Lightning | N | Section of ZN.15013 Terry Hills Panel 10 Feerder from RE.20852 to extent of feeder RE.20852 McCarrs Ck Rd Tripped, Reclosed & Locked Out on IOC and Earth Fault Sectionaliser CP.49122 opened Cause:- Ugoh @ S.46269 defective Line workers made repairs and supply restored Note:- Sectionaiser CP.49122 opened for safety to close USL.24299 De-energised @ 11.27 (PT.16809 interrupted 11.27 to 11.30) ME:-1163012, 1163038 RS:-1163026, 1163031 Withdrawn:-1161478, 1161580, 1161605 | October | 2014 | 2015Q2 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | Unknown | Unknown | 2014-10-13 | N | 747.129 | N | 17 | N | N | 1.1101 | 39.4971 | 50776.127
[7 empty] | 13600 | 11702 | 1161811 | 2014-10-14 10:28 | 2014-10-14 12:43 | 134.85 | 11kV | 3775.8 | 28 | HV | Staff Other | Utility Process Issue | Fuse | Unplanned | Unselected | Y | LID 142407 B phase DOLF : 20 Amp Dop reported LF over tightened. Excluded OMS No. 1161810, 1161818, CC1: 22-"Refer to SOp" | October | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2014-10-14 | N | 134.85 | N | 4 | N | N | 1.1101 | 39.4971 | 2759.2433
[7 empty] | 13189 | 8313 | 1161443 | 2014-10-13 18:05 | 2014-10-14 14:50 | 1245 | 11kV | 490352 | 529 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | N | Ex Zn12630 Peats Ridge Zone section of Pa2 "Gunderman" fdr RE44316 Wisemans Ferry tripped & locked out on o/c, lockout Tree brought down OH mains and Poles 2nd Event RE45189 Cooks Peats Ridge 0.5 tripped & locked out on o/c lockout Overhead repaired HV mains See 1163392 2nd 1163392,3,5,6,7,8,9,400,2,3,4 Exclude 1161443,52,95,570 Restoration times as per DNMS | October | 2014 | 2015Q2 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2014-10-13 | N | 926.9414 | N | 17 | N | N | 1.1101 | 39.4971 | 358334.7787
[7 empty] | 12558 | 2917 | 1162070 | 2014-10-14 16:10 | 2014-10-14 18:05 | 115.4167 | 11kV | 461.6667 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | Y | LID 142408 sub isolated to repair dropper lead | October | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-10-14 | N | 115.4167 | N | 4 | N | N | 1.1101 | 39.4971 | 337.3724
[7 empty] | 13134 | 7864 | 1162094 | 2014-10-14 16:47 | 2014-10-14 18:46 | 119 | 11kV | 99462 | 1486 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | Y | Zn384 Camperdown - P43 tripped on A phase IOC, EFI (5kV) EFI @ S4538 - Defective EFI @ S2753 no indication - No EFI @ S2783 Abnormal: Sw B Clsoed @ S2783 Mt Vernon St - Sw A Open @ S5662 Barr Parramatta (see D/R # 346158B) UG Cable fault from S35388 Ross Parramatta No2 to S2783 Mt Vernon St see 1163762 1163763 Other: 1162114 1162112 | October | 2014 | 2015Q2 | 2015 | ZN384:PA43 | ZN384:PA70 | ZN00384/000070 | SYDNEY | UG | Not Veg | 2014-10-14 | N | 66.9327 | N | 4 | N | N | 1.1101 | 39.4971 | 72683.896
[7 empty] | 14450 | 18289 | 1162151 | 2014-10-14 20:16 | 2014-10-14 23:30 | 194 | 11kV | 290658 | 1527 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Lightning | Y | ZN 10999 Kogarah - Pnl 32 - All phases IOC. Lightning hit pole as per hazard comments. 11kV cross arm has broken and 11kV mains fell into LV. S 10546 Dist 3 interrupted, II to inspect services. PT 10362 Dist 4 interrupted for safety. ME: 1163959. Rest Step: 1163960. Withdrawn: 1162151, 3, 6. | October | 2014 | 2015Q2 | 2015 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | OH | Not Veg | 2014-10-14 | N | 190.3458 | N | 4 | N | N | 1.1101 | 39.4971 | 212404.2934
[7 empty] | 12721 | 4352 | 1162348 | 2014-10-14 23:54 | 2014-10-15 01:30 | 96 | 11kV | 87471 | 1309 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | Y | ZN.15006 Dee Why 11kV Panel 13 "Long Reef" tripped on:- Relays:-OC 51N, Fault Check, EFI Signals:- 11kV trip Cause:- 11kV UG cable fault from SW/B @ S.15777 to SW/A @ S.16255 to SW/B @ S.16618 tee S.16120 ME:-1162686 RS:-1162698, 1162717, 1162716, 1162715 Withdrawn:-1162348 | October | 2014 | 2015Q2 | 2015 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | UG | Not Veg | 2014-10-14 | Y | 66.8228 | N | 4 | N | Y | 1.1101 | 39.4971 | 63921.2268
[7 empty] | 12960 | 6508 | 1162349 | 2014-10-14 23:55 | 2014-10-15 04:20 | 265 | 11kV | 207526 | 1213 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN.15002 Narrabeen 11kV Panel 2L Tripped , Reclosed, Tripped and locked out Relays:- B & C phase OC, Reclose, Timing, Lockout, Fault Check, A phase BU OC Signals:- 11kV Trip, Zone Earth Cause:- Large tree fell and brought down OH mains ME:-1162349 RS:-1162500 Withdrawn:-1162374, 1162388 | October | 2014 | 2015Q2 | 2015 | ZN15002:PA2 | ZN15002:PA2 | ZN15002/000002 | NORTHERN BEACHES | OH | Veg | 2014-10-14 | Y | 171.0849 | N | 4 | N | Y | 1.1101 | 39.4971 | 151653.8798
[7 empty] | 14080 | 15673 | 1162351 | 2014-10-14 23:59 | 2014-10-15 06:25 | 386 | 11kV | 589808 | 1528 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Wind Storm | Y | ZN.15008 Harbord Zone - Panel 9L - Section of 11kV feeder from LBS.62773 to extent of feeder Cause:- 11kV bond burnt off @ 38 Ozone Parade, Harbord - Pole no.29096. Beyond tee off to ABS.25221 & S.16049. Ex Panel 9L. ME:-1163740 Withdrawn:-1162351 | October | 2014 | 2015Q2 | 2015 | ZN15008:PA9 | ZN15008:PA9 | ZN15008/000009 | NORTHERN BEACHES | OH | Not Veg | 2014-10-14 | Y | 386 | N | 4 | N | Y | 1.1101 | 39.4971 | 431014.29
[7 empty] | 12661 | 3830 | 1162434 | 2014-10-15 04:33 | 2014-10-15 07:33 | 180 | 11kV | 323676 | 1880 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | AT Zn262 Marrickville Panel 16 "Victoria Sydenham" has tripped Signals: 11kv trip, No.4 Tx Group Earth Relays: Earth Fault, Fault Check, EFI EFI's: S7843, S6973, S5276, S1447, S1434, S5796 Remarks: weather related. 11kv undgerground feeder fault from S5796 Margaret Crystal (sw/B) to S1902 Petersham Lane (Sw/A) Related jobs: #1164890, 1164887, 1162434, 1162507 | October | 2014 | 2015Q2 | 2015 | ZN262:PA16 | ZN262:PA16 | ZN00262/000016 | INNER WEST | UG | Not Veg | 2014-10-15 | N | 172.1681 | N | 15 | N | N | 1.1101 | 39.4971 | 236532.874
[7 empty] | 12944 | 6382 | 1162381 | 2014-10-15 00:08 | 2014-10-15 07:55 | 467 | 11kV | 276333 | 597 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At Zn2466 Flemington Panel 12 "Mons St" feeder has tripped Relays: T-lay, Fault check, EFI, Signals: 11kv trip, No.4 Group Earth Panel #21 Fault check, EFI Panel #19 Fault check, EFI At Sub 3620 Tooheys Lidcombe Sw/A has tripped. Relas: T-lay, EFI Remarks: weather related, 11kv underground feeder fault from S698 Mons St (Sw/B) to S4137 Frances Grace (Sw/A). (Suspect S1653 Dist 2 & 3 were in parallel at the time) | October | 2014 | 2015Q2 | 2015 | ZN2466:PA12 | ZN2466:PA12 | ZN02466/000012 | CUMBERLAND | UG | Not Veg | 2014-10-15 | N | 462.8693 | N | 15 | N | N | 1.1101 | 39.4971 | 201936.006
[7 empty] | 14374 | 17703 | 1162452 | 2014-10-15 02:24 | 2014-10-15 08:00 | 336 | 11kV | 382052 | 1736 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Zn12570 Avoca Pa24 "Copacabana" tripped on Relays: SEF, Lockout Heavy Storm and wind at time of interruption. Tree on mains in 2 location See 1163551,3,4,6 Exclude 1162452,518 | October | 2014 | 2015Q2 | 2015 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2014-10-15 | N | 220.076 | N | 15 | N | N | 1.1101 | 39.4971 | 279192.333
[7 empty] | 14181 | 16353 | 1162513 | 2014-10-15 04:54 | 2014-10-15 08:50 | 236 | 11kV | 83845 | 434 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | Zn14891 Wyong Pa14 "WSC Hely" tripped on Relays: Earth Fault, OC, EFI Signals: 11kv trip EFI's S14799 S14630 S18820 UG Fault between S18820 to LB44992 to S12860 See 1163857,9,60,6,4 2nd 1163932 | October | 2014 | 2015Q2 | 2015 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | UG | Not Veg | 2014-10-15 | N | 193.1912 | N | 15 | N | N | 1.1101 | 39.4971 | 61271.453
[7 empty] | 13470 | 10691 | 1162522 | 2014-10-15 06:24 | 2014-10-15 09:12 | 168 | 11kV | 131522 | 882 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn1788 Matraville Pnl.1 - tripped on: Earth leakage C phase field EFIs @ S35265 & S35266 UG cable fault between S35267 Sw A and S35266 Sw B | October | 2014 | 2015Q2 | 2015 | ZN1788:PA1 | ZN1788:PA42 | ZN01788/000042 | RANDWICK | UG | Not Veg | 2014-10-15 | N | 149.1179 | N | 15 | N | N | 1.1101 | 39.4971 | 96112.3984
[7 empty] | 13516 | 11071 | 1162297 | 2014-10-14 22:58 | 2014-10-15 10:00 | 662 | 11kV | 38760 | 78 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | Y | At Zn35800 Bankstown Panel 4 "Fairford Gow" has tripped Signals: 11kv trip Relays: 50 TN - 51ABC - EFI EFI's: S7397- S8888 - S5188 - S36154 - S1734 - S4852 Remarks: weather related. See outgage on Panel 21. JKSS RMI @ S1091 Moxon Rd has failed and requires urgent repair/replacement | October | 2014 | 2015Q2 | 2015 | ZN35800:PA4 | ZN35800:PA4 | ZN35800/000004 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-10-14 | Y | 496.9231 | N | 4 | N | Y | 1.1101 | 39.4971 | 28324.6648
[7 empty] | 13193 | 8371 | 1162083 | 2014-10-14 20:26 | 2014-10-15 10:15 | 829 | 11kV | 336185 | 2573 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | Y | At Zn1285 Greenacre Park Panel 33 "Greenacre Rd" Etc 11kv feeder CB has tripped, Relays:A & C phase OC, EFI, Timer, Relays: 11kv trip EFI's: All right leg down to Sub 35179 Remarks: Transformer failure. It appears the No.2 tx RMCB @ Sub 7387 Roberts Mayvic has sustained damage to cable terms/ endboxes | October | 2014 | 2015Q2 | 2015 | ZN1285:PA33 | ZN1285:PA33 | ZN01285/000033 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-10-14 | Y | 130.6588 | N | 4 | N | Y | 1.1101 | 39.4971 | 245674.0822
[7 empty] | 12450 | 1788 | 1162642 | 2014-10-15 07:08 | 2014-10-15 10:20 | 191.75 | 11kV | 18216.25 | 95 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | 11kv Bond off top of HDO assembly at PT46144 Henry Boos See 11692642 Exclude 1163068 | October | 2014 | 2015Q2 | 2015 | ZN12610:PA18 | ZN12610:PA18 | ZN12610/000018 | CENTRAL COAST | OH | Not Veg | 2014-10-15 | N | 191.75 | N | 15 | N | N | 1.1101 | 39.4971 | 13311.8982
[7 empty] | 12895 | 5924 | 1162478 | 2014-10-15 03:30 | 2014-10-15 10:30 | 420 | 11kV | 69574 | 239 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Pa5 IR61082 Brieses Peats Ridge tripped on O/C Tree on 11kv O/H between PT11757 and PT13257. Mains have repaired See 1163545,6,7,8 Exclude 1162478 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2014-10-15 | N | 291.1046 | N | 15 | N | N | 1.1101 | 39.4971 | 50842.6271
[7 empty] | 12267 | 93 | 1162647 | 2014-10-15 07:04 | 2014-10-15 10:50 | 226 | 11kV | 684 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 142413/01 see OMS 1163853 | October | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-10-15 | N | 52.6154 | N | 15 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 12379 | 1190 | 1162662 | 2014-10-15 07:22 | 2014-10-15 11:35 | 253 | 11kV | 9361 | 37 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Rain Light | N | Ex Zn12620 Noraville section of Pa2 "Budgewoi" 11kv Bond off USL 41777 See 1163912 Exclude 1162662,917,3086 | October | 2014 | 2015Q2 | 2015 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Not Veg | 2014-10-15 | N | 253 | N | 15 | N | N | 1.1101 | 39.4971 | 6840.7427
[7 empty] | 12745 | 4587 | 1162769 | 2014-10-15 08:03 | 2014-10-15 11:53 | 230 | 11kV | 54740 | 238 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | Section of 11kV feeder ZN.15006 Dee Why West Panel 13 - Affected Subs S.16045, PT.15330 & S.15777 only due to abnormal switching Abnormal Switching:- Suspected UG cable fault, isolated between S.15777 SW/B to S.16255 SW/A to S.16618 SW/B tee S.16120 (See ME:-1162686) Cause:- Possum found at UGOH, footpath phase bond at 11kV USL.24947 Restored via alternate switching ME:-1163794 Withdrawn:-1162769 | October | 2014 | 2015Q2 | 2015 | ZN15006:PA13 | ZN15006:PA13 | ZN15006/000013 | NORTHERN BEACHES | OH | Not Veg | 2014-10-15 | N | 230 | N | 15 | N | N | 1.1101 | 39.4971 | 40002.3774
[7 empty] | 14645 | 20112 | 1162526 | 2014-10-15 01:50 | 2014-10-15 12:25 | 635.15 | 11kV | 9527.25 | 15 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 142416 A phase DOLF : 8 Amp OHM down between P: GR-74760 & GR-74761, Majors Ln, Keinbar Excluded OMS 1162528 & 1162435. CC1: 22-"Refer to SOp" | October | 2014 | 2015Q2 | 2015 | 526:34636 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Not Veg | 2014-10-15 | N | 635.15 | Y | 15 | N | Y | 1.1101 | 39.4971 | 6962.2333
[7 empty] | 13217 | 8517 | 1162361 | 2014-10-14 21:07 | 2014-10-15 12:40 | 933 | 11kV | 846375 | 1508 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 10991 Blakehurst - Pnl 1 - A phase timed OC, Earth Fault, Lockout, EFI, Field EFIs. 11kV in LV near S 10793. Repaired and given clearance. ME: 1163830. Rest Steps: 1163833, 4, 5, 6, 8. WIthdrawn: 1163103, 1162176, 361. | October | 2014 | 2015Q2 | 2015 | ZN10991:PA1 | ZN10991:PA1 | ZN10991/000001 | GEORGES RIVER | OH | Not Veg | 2014-10-14 | Y | 561.2566 | N | 4 | N | Y | 1.1101 | 39.4971 | 618505.8862
[7 empty] | 14297 | 17213 | 1162221 | 2014-10-14 21:58 | 2014-10-15 13:55 | 957 | 11kV | 167246 | 278 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Rain Wind Storm | Y | At Zn35800 Bankstown Panel 21 "Bankstown Aux" has tripped Signals: 11kv trip Relays: 50TN - 51ABC - EFI EFI's: S46109 - S3094 S3095 - S1108 Remarks: Weather related. See outage on Panel 4. JKSS RMI @ Sub 1091 Moxon Rd has failed and require urgent repair/replacement. Tide level at sub 1/2 way up Tx. | October | 2014 | 2015Q2 | 2015 | ZN35800:PA21 | ZN35800:PA21 | ZN35800/000021 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-10-14 | Y | 601.6043 | N | 4 | N | Y | 1.1101 | 39.4971 | 122218.4439
[7 empty] | 13716 | 12646 | 1162227 | 2014-10-14 22:29 | 2014-10-15 14:00 | 930.7833 | 11kV | 89355.2 | 96 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Tree on Mains, LV down, field staff carried out repairs to conductors and restored supply via LV Parallel No further information available, exact restoration time is unavailable | October | 2014 | 2015Q2 | 2015 | ZN9245:PA10 | ZN9245:PA13 | ZN09245/000013 | SUTHERLAND | OH | Veg | 2014-10-14 | Y | 930.7833 | N | 4 | N | Y | 1.1101 | 39.4971 | 65298.1446
[7 empty] | 13589 | 11623 | 1162246 | 2014-10-14 21:55 | 2014-10-15 14:55 | 1020 | 11kV | 494723 | 724 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | ZN 9301 Kurnell - Pnl 8 - Trip/reclose/trip, Earth Fault, SEL, lockout, timing, CAG13 EFI. 11kV mains down in Silver Beach Rd. Came into contact with 415v. II to give clearance before re-energising. ME: 1163785. Rest Steps: 1163786, 7. WIthdrawn: 1162225, 246, 424, 1163114, 257. | October | 2014 | 2015Q2 | 2015 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | OH | Not Veg | 2014-10-14 | Y | 683.3191 | N | 4 | N | Y | 1.1101 | 39.4971 | 361528.9765
[7 empty] | 12969 | 6558 | 1162958 | 2014-10-15 11:55 | 2014-10-15 15:00 | 185 | 11kV | 142500 | 1419 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN.180 Mosman 11kV Panel 10 feeder tripped on earth fault Signals:- EFI & 11kV trip Abnormal Switching:- Feeder isolated between S.233 SW/B to S.2058 SW/B tee S.5338 (S.2058 on Panel 10 @ ZN.180 Mosman) Cause:- 11kV UG cable fault located between S.8255 SW/B to S.2721 SW/A to S.2058 SW/A ME:-1163841 RS:-1163844, 1163845 Withdrawn:-1162958, 1163280 SE:-1163892, 1163893 | October | 2014 | 2015Q2 | 2015 | ZN180:PA10 | ZN180:PA10 | ZN00180/000010 | MOSMAN | UG | Not Veg | 2014-10-15 | N | 100.4228 | N | 15 | N | N | 1.1101 | 39.4971 | 104134.797
[7 empty] | 14044 | 15389 | 1162670 | 2014-10-15 09:27 | 2014-10-15 15:45 | 378 | 11kV | 4536 | 12 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Light | N | Ex Zn14891 Wyong section Pa5 "Wyong" 11kV section between CP45083 to LB45108 Interrupted for safety. Tree fell on CCT OH on durren rd | October | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2014-10-15 | N | 378 | N | 15 | N | N | 1.1101 | 39.4971 | 3314.775
[7 empty] | 13268 | 8909 | 1163216 | 2014-10-15 11:34 | 2014-10-15 19:35 | 481 | 11kV | 8297 | 41 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 142418 3 phase Overcurrent tree on mains section isolated to repair mains Excluded oms 1163216, 1163348 | October | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-10-15 | N | 202.3659 | N | 15 | N | N | 1.1101 | 39.4971 | 6063.2029
[7 empty] | 13793 | 13240 | 1162506 | 2014-10-15 03:24 | 2014-10-15 20:10 | 1006 | 11kV | 405418 | 403 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | Zn384 Camperdown - panel 41 tripped on: Earth Leakage with no EFI No field EFIs Section of feeder from Sw B @2783 and Sw B @ S35388 out of service defective from previous outage #1163762 (no other interconnecting points to restore feeer) Flooding - cable fault - restored after emergency repair | October | 2014 | 2015Q2 | 2015 | ZN384:PA41 | ZN7481:PA20 | ZN07481/000020 | SYDNEY | UG | Not Veg | 2014-10-15 | N | 1006 | Y | 15 | N | Y | 1.1101 | 39.4971 | 296267.5166
[7 empty] | 12684 | 4015 | 1162535 | 2014-10-15 05:09 | 2014-10-15 20:35 | 926 | 11kV | 543538 | 781 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | ZN 9118 Cronulla - Rec 35756 Bundeena - Trip/reclose/trip. UG fault between S 9096, LB 35838 tee PT 9679. Also, there was a blown lightning arrestor at PT 9235. These two possibly occurred at the same time and caused this extended outage time. ME: 1167743. Rest Steps: 1167747, 51. Withdrawn: 1162535, 1163172, 86, 89, 1163284. | October | 2014 | 2015Q2 | 2015 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | UG | Not Veg | 2014-10-15 | N | 695.9513 | Y | 15 | N | Y | 1.1101 | 39.4971 | 397201.5387
[7 empty] | 12426 | 1597 | 1163653 | 2014-10-15 19:46 | 2014-10-15 22:25 | 159 | 11kV | 318 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142419 A phase sub isolated for arcing live line clamps Excluded OMS 1163668 & 1163653 | October | 2014 | 2015Q2 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2014-10-15 | N | 159 | N | 15 | N | N | 1.1101 | 39.4971 | 232.385
[7 empty] | 14625 | 19930 | 1163225 | 2014-10-15 11:36 | 2014-10-15 23:32 | 715.7833 | 11kV | 148765.8833 | 823 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | ZN 9037 Miranda - Pnl 9 - Trip/reclose/trip, A phase overcurrent and IOC, EFI, timer and lockout, Field EFI. 11kV into 415 in Rocklea Cres. Feeder repaired 15/10/14. ME: 1163907. Rest Step: 1163908, 9. ME GIS: 1163248. Withdrawn: 1163225, 419, 485. | October | 2014 | 2015Q2 | 2015 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | OH | Not Veg | 2014-10-15 | N | 180.7605 | N | 15 | N | N | 1.1101 | 39.4971 | 108713.7197
[7 empty] | 12303 | 493 | 1163704 | 2014-10-16 05:29 | 2014-10-16 07:29 | 120 | 11kV | 480 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142421 DOLF : 10 Amp Excluded OMS 1163704 | October | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2014-10-16 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 12394 | 1380 | 1163717 | 2014-10-16 06:30 | 2014-10-16 07:55 | 85.2333 | 11kV | 2642.2333 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 142422 A phase DOLF : 16 Amp | October | 2014 | 2015Q2 | 2015 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2014-10-16 | N | 85.2333 | N | 5 | N | N | 1.1101 | 39.4971 | 1930.8662
[7 empty] | 13720 | 12671 | 1163705 | 2014-10-16 05:44 | 2014-10-16 08:55 | 191.2667 | 11kV | 120807.5833 | 1405 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 142420 2 fault operations C phase Overcurrent Excluded OMS 1163705, 1163718, 1163722, 1163732 | October | 2014 | 2015Q2 | 2015 | 214:8670 | 214:8670 | ZN00214/008670 | LAKE MACQUARIE | UG | Not Veg | 2014-10-16 | N | 85.984 | N | 5 | N | N | 1.1101 | 39.4971 | 88282.6187
[7 empty] | 14015 | 15096 | 1163756 | 2014-10-16 07:47 | 2014-10-16 09:14 | 87 | 11kV | 609 | 7 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | ZN 9301 Kurnell - Pnl 13 - Open circuit. Bond burnt off at IS 35962. ME: 1166173. Withdrawn: 1163756. | October | 2014 | 2015Q2 | 2015 | ZN9301:PA13 | ZN9534:PA18 | ZN09534/000018 | SUTHERLAND | OH | Not Veg | 2014-10-16 | N | 87 | N | 5 | N | N | 1.1101 | 39.4971 | 445.0392
[7 empty] | 14331 | 17383 | 1163878 | 2014-10-16 10:03 | 2014-10-16 11:49 | 106 | 11kV | 16803 | 387 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | At S1193 Lindfield Panel 11 Tripped reclosed tripped and locked out on A phase IOC, Reclose and Timing, EFI, 11kV Trip, No2 Gorup Earth Cause: UGOH pole cnr the Grove and Glanview St Caught Fire. See OMS 1164888 1163878 1163878 | October | 2014 | 2015Q2 | 2015 | ZN1193:PA11 | ZN1193:PA11 | ZN01193/000011 | KU-RING-GAI | Unknown | Unknown | 2014-10-16 | N | 43.4186 | N | 5 | N | N | 1.1101 | 39.4971 | 12279.1368
[7 empty] | 12485 | 2123 | 1164347 | 2014-10-17 11:08 | 2014-10-17 11:17 | 9 | 11kV | 15210 | 1690 | HV | Animal Goanna | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 142432 Dip Fdr requested by DOp to remove large Goanna. | October | 2014 | 2015Q2 | 2015 | 229:34995 | 229:34995 | ZN00229/034995 | PORT STEPHENS | OH | Not Veg | 2014-10-17 | N | 9 | N | 7 | N | N | 1.1101 | 39.4971 | 11115.0194
[7 empty] | 12468 | 1901 | 1164280 | 2014-10-17 09:37 | 2014-10-17 11:37 | 120 | 11kV | 48840 | 407 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Zn12630 Peats Ridge section of pa3 "Mangrove Mountain" Burnt off bond at 11kv USL 44115 see 1164894 exclude 1164280 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-10-17 | N | 120 | N | 7 | N | N | 1.1101 | 39.4971 | 35690.8315
[7 empty] | 13779 | 13161 | 1164411 | 2014-10-17 13:02 | 2014-10-17 13:40 | 38 | 11kV | 59240 | 1990 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ ZN.36300 Balgowlah North 11kV Panel 3 tripped on:- Relays:- Earth Fault Signals:- Tx.1 Group Earth, EFI Field EFI's:- S.17119 Cause:- 11kV UG Feeder Fault from S.17119 SW/B to S.16912 SW/A ME:-1164806 RS:-1164808 Withdrawn:-1164411 | October | 2014 | 2015Q2 | 2015 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | UG | Not Veg | 2014-10-17 | N | 29.7688 | N | 7 | N | N | 1.1101 | 39.4971 | 43290.8447
[7 empty] | 13448 | 10553 | 1164903 | 2014-10-17 12:00 | 2014-10-17 14:25 | 145 | 11kV | 1160 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mounatin" 11kv fdr from AB44889 to LB61085 to AB44253 was interrutped so emergency repairs could be carried out on LK44115 See 1164894 for previous event | October | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2014-10-17 | N | 145 | N | 7 | N | N | 1.1101 | 39.4971 | 847.6938
[7 empty] | 12342 | 823 | 1164474 | 2014-10-17 15:52 | 2014-10-17 18:25 | 153 | 11kV | 306 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC PT | Unplanned | Unselected | N | LID 142438 B & C phase LVF ISOLATED & CTW ISSUED TO REPAIR LV WIRING AT SUB 72605. Excluded OMS REPORT NO 1164474. | October | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-10-17 | N | 153 | N | 7 | N | N | 1.1101 | 39.4971 | 223.6158
[7 empty] | 13358 | 9774 | 1164509 | 2014-10-17 18:09 | 2014-10-17 19:15 | 66 | 11kV | 66 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142439 C phase DOLF : 10 Amp A/B/C VOLTS =241 OMS REPORT NO 1164509. | October | 2014 | 2015Q2 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-10-17 | N | 66 | N | 7 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 13725 | 12747 | 1164547 | 2014-10-17 23:40 | 2014-10-18 09:00 | 560 | 11kV | 1120 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 142440 No protection operations. Dropper to DOLF burnt off. Repaired under AP. A Regan perfmormed switching on 18/10/2014. Excluded OMS 1164547. | October | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-10-17 | N | 560 | N | 7 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 14377 | 17745 | 1164662 | 2014-10-18 21:53 | 2014-10-19 00:15 | 142 | 11kV | 111186 | 783 | HV | Animal Possum | Animal | O/H Conductor Bare | Unplanned | Unselected | N | ZN 9118 Cronulla - Pnl 11 - Recloser 35756 Trip/reclose/trip, Phase to earth. Possum on UGOH. ME: 1166269. Withdrawn: 1164662. | October | 2014 | 2015Q2 | 2015 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2014-10-18 | N | 142 | N | 1 | N | N | 1.1101 | 39.4971 | 81251.4494
[7 empty] | 13192 | 8370 | 1164696 | 2014-10-19 09:57 | 2014-10-19 10:52 | 55 | 11kV | 42842 | 812 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | At S1285 Greenacre Park P10 the "East terrace" etc fdr tripped on B phase OC, EFI, fault check Remarks: UG fault. S1285 Greenacre Park P10 to S4109 East Terrace to S8025 East Terrace South Terrace | October | 2014 | 2015Q2 | 2015 | ZN1285:PA10 | ZN1285:PA10 | ZN01285/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-10-19 | N | 52.7611 | N | 3 | N | N | 1.1101 | 39.4971 | 31307.67
[7 empty] | 12433 | 1680 | 1164740 | 2014-10-19 17:43 | 2014-10-19 20:45 | 182 | 11kV | 364 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa4 AT PT14595 Main Rd Gallard #1 20K HDO blown off. Fuse Fatigue See 1164914 exclude 1164740 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-10-19 | N | 182 | N | 3 | N | N | 1.1101 | 39.4971 | 266.0005
[7 empty] | 14193 | 16450 | 1164733 | 2014-10-19 16:57 | 2014-10-19 22:20 | 322.5 | 11kV | 1612.5 | 5 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Bare | Unplanned | Unselected | N | LID 142444 3 Phase DOLF : 16 Amp TREE FELLED ONTO MAINS BY TREE TRIMMER. OMS REPORT NO 1164735. | October | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-10-19 | N | 322.5 | N | 3 | N | N | 1.1101 | 39.4971 | 1178.3674
[7 empty] | 12465 | 1874 | 1164770 | 2014-10-20 05:33 | 2014-10-20 06:11 | 38 | 11kV | 73682 | 1939 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | ZN 10991 Blakehurst - Pnl 13 - Trip/reclose/trip, A & C phase OC, lockout, EFI, Field EFIs. Tree branch on mains in Terry St. ME: 1166328. Withdrawn: 1164770, 1. | October | 2014 | 2015Q2 | 2015 | ZN10991:PA13 | ZN10991:PA13 | ZN10991/000013 | GEORGES RIVER | OH | Veg | 2014-10-20 | N | 38 | N | 7 | N | N | 1.1101 | 39.4971 | 53844.6323
[7 empty] | 14116 | 15945 | 1165056 | 2014-10-20 11:48 | 2014-10-20 12:30 | 42 | 11kV | 15567 | 505 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 142450 2 fault operations B phase Overcurrent Tree branch across mains. Removed by DOp. Fault Code 51B Excluded OMS # 1165056 | October | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2014-10-20 | N | 30.8257 | N | 7 | N | N | 1.1101 | 39.4971 | 11375.9045
[7 empty] | 13777 | 13132 | 1164948 | 2014-10-20 10:11 | 2014-10-20 13:05 | 174.4667 | 11kV | 197321.8 | 1131 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Wind | N | ZN 10991 Blakehurst - Pnl 13 - Interrupted for safety reasons. HV pole found broken outside Blakehurst Zone. Panel interrupted for safety reasons. | October | 2014 | 2015Q2 | 2015 | ZN10991:PA13 | ZN10991:PA13 | ZN10991/000013 | GEORGES RIVER | OH | Not Veg | 2014-10-20 | N | 174.4667 | N | 7 | N | N | 1.1101 | 39.4971 | 144196.9514
[7 empty] | 12516 | 2412 | 1164835 | 2014-10-20 07:10 | 2014-10-20 15:10 | 480 | 11kV | 2400 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Wind | N | PT 9095 Heathcote South - HDO B phase. B phase HDO fuse equipment broken. ME: 1166267. Withdrawn: 1164793. | October | 2014 | 2015Q2 | 2015 | ZN9245:PA8 | ZN9245:PA3 | ZN09245/000003 | SUTHERLAND | OH | Not Veg | 2014-10-20 | N | 480 | N | 7 | N | N | 1.1101 | 39.4971 | 1753.8492
[7 empty] | 14563 | 19177 | 1165240 | 2014-10-20 16:21 | 2014-10-20 16:58 | 37 | 11kV | 31133 | 865 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Wind | N | ZN 10996 Rockdale - Pnl 10 - Interrupted for safety. Interrupted for safety reasons. Car hit pole at corner of Bestic and West Botany Road. HV OH into LV ABC. ME: 1166338. Rest Step: 1166339. Withdrawn: 1165240. | October | 2014 | 2015Q2 | 2015 | ZN10996:PA10 | ZN10998:PA2 | ZN10998/000002 | BAYSIDE | OH | Not Veg | 2014-10-20 | N | 35.9919 | N | 7 | N | N | 1.1101 | 39.4971 | 22751.0781
[7 empty] | 12735 | 4518 | 1165246 | 2014-10-20 16:27 | 2014-10-20 17:35 | 68 | 11kV | 748 | 11 | HV | Arcing | Equipment Failure | Fuse | Unplanned | Rain Light | N | Ex Zn12580 Erina section of Pa1 "THe Entrance" PT11929 11kv 31K HDO fuse blown due to Flashover/Arcing See 1165275 exclude 1165246,55,6,8,61 | October | 2014 | 2015Q2 | 2015 | ZN12580:PA1 | ZN12580:PA1 | ZN12580/000001 | CENTRAL COAST | OH | Not Veg | 2014-10-20 | N | 68 | N | 7 | N | N | 1.1101 | 39.4971 | 546.6163
[7 empty] | 12349 | 880 | 1165320 | 2014-10-20 19:06 | 2014-10-20 23:03 | 237 | 11kV | 20053 | 253 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 142452 2 fault operations C phase Earth fault | October | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2014-10-20 | N | 79.2609 | N | 7 | N | N | 1.1101 | 39.4971 | 14654.1409
[7 empty] | 12364 | 1030 | 1165366 | 2014-10-21 06:06 | 2014-10-21 09:40 | 214 | 11kV | 1712 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142462 A phase DOLF : 10 Amp linked to previous 66kV fault OMS 1165621 Excluded OMS 1165366 | October | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-10-21 | N | 214 | N | 5 | N | N | 1.1101 | 39.4971 | 1251.0791
[7 empty] | 13365 | 9829 | 1165387 | 2014-10-21 07:37 | 2014-10-21 11:30 | 233 | 11kV | 466 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142464 C phase DOLF : 10 Amp linked to previous 66kV fault OMS 1165621 Excluded oms 1165367 | October | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-10-21 | N | 233 | N | 5 | N | N | 1.1101 | 39.4971 | 340.5391
[7 empty] | 13679 | 12371 | 1165657 | 2014-10-21 16:36 | 2014-10-21 17:20 | 44 | 11kV | 44 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142469 Single phase DOLF Possibly caused by previous night's 66kV line fault Excluded OMS# 1165657. | October | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-10-21 | N | 44 | N | 5 | N | N | 1.1101 | 39.4971 | 32.1539
[7 empty] | 13046 | 7128 | 1165364 | 2014-10-21 05:32 | 2014-10-21 17:45 | 733 | 11kV | 73694 | 168 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.15010 Careel Bay 11kV Panel 9 part of the feeder @ CP.25760 SW/C to extent of the feeder (S.15682, S.15681, S.15680, S, 47300, S.16097) @ CP.25760 - C phase 80A HV fuse blown Field EFI's:- CP.23247, S.16484, S.16485, CP.25760, S.15682 SW/2686 @ ZN.15010 - EFI on Panel 9 signals Fault Check on Panel 9 & Tx.3 Cause:- 11kV UG cable fault between S.15682 SW/2686 to S.47300 SW/A Note:- S.47300 & S.16097 restored via MG's ME:-1166151 RS:-1166152 Withdrawn:-1165364, 1165512 | October | 2014 | 2015Q2 | 2015 | ZN15010:PA9 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | UG | Not Veg | 2014-10-21 | N | 438.6548 | N | 5 | N | N | 1.1101 | 39.4971 | 53853.4016
[7 empty] | 12629 | 3466 | 1165762 | 2014-10-21 20:31 | 2014-10-21 22:15 | 104 | 11kV | 520 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 142470 B & C phase DOLF : 20 Amp Excluded OMS 1165762 | October | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-10-21 | N | 104 | N | 5 | N | N | 1.1101 | 39.4971 | 380.0007
[7 empty] | 13301 | 9166 | 1165817 | 2014-10-22 08:42 | 2014-10-22 10:00 | 78 | 11kV | 8970 | 115 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.15010 Careel Bay 11kV Panel 9 part of the feeder @ CP.25760 SW/C to extent of the feeder (S.15682, S.15681, S.15680) Interruption cause:- Interrupted for safety reasons to allow for the disconnection of feeder to S.47300 and allow for testing of defective feeder (See cause) Cause:- 11kV UG cable fault between S.15682 SW/2686 to S.47300 SW/A Note:- S.47300 & S.16097 supplied via MG's so no interruption ME:-1166159 RS:-1166160 Withdrawn:-1165817 See also from 21/10/14:- ME:-1166151 RS:-1166152 | October | 2014 | 2015Q2 | 2015 | ZN15010:PA9 | ZN15010:PA28 | ZN15010/000028 | NORTHERN BEACHES | UG | Not Veg | 2014-10-22 | N | 78 | N | 3 | N | N | 1.1101 | 39.4971 | 6555.0114
[7 empty] | 12669 | 3897 | 1165905 | 2014-10-22 11:10 | 2014-10-22 11:45 | 35 | 11kV | 105 | 3 | HV | Customer Installation Fault | Customer Installation | OTHER - REFER COMMENTS | Unplanned | Unselected | N | At Sub 6459 Boorea nyrang No1, Ex 11kv Pnl 15 @ Zn 2466 Flemington tripped on; Relays: BBOC trip Signals: BBOC trip Remarks: Overload. Customers installation is unevenly balanced and tripped on over current | October | 2014 | 2015Q2 | 2015 | ZN2466:PA15 | ZN1068:PA19 | ZN01068/000019 | CUMBERLAND | Unknown | Unknown | 2014-10-22 | N | 35 | N | 3 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 12632 | 3516 | 1166053 | 2014-10-22 15:52 | 2014-10-22 16:55 | 63 | 11kV | 126 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142482 A phase DOLF : 20 Amp Excluded OMS 1166053 | October | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-10-22 | N | 63 | N | 3 | N | N | 1.1101 | 39.4971 | 92.0771
[7 empty] | 13966 | 14677 | 1166147 | 2014-10-23 07:21 | 2014-10-23 10:25 | 184 | 11kV | 1288 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 142491 B phase DOLF : 10 Amp Replaced 10A Bph LF 75306 & 10A Bph sub DOLF 71288. Excluded OMS No. 1166147 | October | 2014 | 2015Q2 | 2015 | 814:82285 | 814:82291 | ZN00814/082291 | UPPER HUNTER | OH | Veg | 2014-10-23 | N | 184 | N | 8 | N | N | 1.1101 | 39.4971 | 941.2324
[7 empty] | 13297 | 9095 | 1166300 | 2014-10-23 12:25 | 2014-10-23 13:30 | 65 | 11kV | 61620 | 948 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Unselected | N | Ex Zn36200 Empire Bay section of Pa11 left "Empire Bay Aux" High Resistance connection on footpath phase at LK44075 Report flickering lights. See 1167845 exclude 1166300,31 | October | 2014 | 2015Q2 | 2015 | ZN36200:PA11 | ZN36200:PA1 | ZN36200/000001 | CENTRAL COAST | OH | Not Veg | 2014-10-23 | N | 65 | N | 8 | N | N | 1.1101 | 39.4971 | 45030.0785
[7 empty] | 13663 | 12221 | 1166474 | 2014-10-23 17:10 | 2014-10-23 18:30 | 80 | 11kV | 64060 | 955 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142500 2 fault operations A & B phases Instantaneous Overcurrent Excluded OMS 1166474 | October | 2014 | 2015Q2 | 2015 | 814:82285 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-10-23 | N | 67.0785 | N | 8 | N | N | 1.1101 | 39.4971 | 46813.1585
[7 empty] | 12383 | 1208 | 1166494 | 2014-10-23 18:00 | 2014-10-23 19:20 | 80 | 11kV | 720 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142515 B phase DOLF : 20 Amp Excluded OMS 1166494 | October | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-10-23 | N | 80 | N | 8 | N | N | 1.1101 | 39.4971 | 526.1548
[7 empty] | 13865 | 13826 | 1166485 | 2014-10-23 17:49 | 2014-10-23 21:10 | 201 | 11kV | 201 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142520 B & C phase DOLF : 20 Amp Excluded OMS 1166485 | October | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-10-23 | N | 201 | N | 8 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 14248 | 16898 | 1166526 | 2014-10-23 20:53 | 2014-10-23 22:07 | 74 | 11kV | 148 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142519 A Phase DOLF : 10 Amp Excluded OMS 1166526 | October | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-10-23 | N | 74 | N | 8 | N | N | 1.1101 | 39.4971 | 108.154
[7 empty] | 12287 | 322 | 1166517 | 2014-10-23 19:59 | 2014-10-23 22:56 | 177 | 11kV | 1593 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142522 A phase DOLF : 15 Amp | October | 2014 | 2015Q2 | 2015 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2014-10-23 | N | 177 | N | 8 | N | N | 1.1101 | 39.4971 | 1164.1174
[7 empty] | 13747 | 12891 | 1166520 | 2014-10-23 20:10 | 2014-10-23 23:15 | 185 | 11kV | 370 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 142523 Single phase DOLF : 5 Amp Blown LA replaced by C Pengelly. Excluded oms 1166520 | October | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-10-23 | N | 185 | N | 8 | N | N | 1.1101 | 39.4971 | 270.3851
[7 empty] | 14529 | 18940 | 1166539 | 2014-10-24 08:30 | 2014-10-24 11:00 | 150 | 11kV | 300 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142525 burnt off tapping pole 9L-40070 Excluded OMS 1166539 | October | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-10-24 | N | 150 | N | 5 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 14225 | 16710 | 1166778 | 2014-10-24 12:51 | 2014-10-24 13:58 | 66.5667 | 11kV | 60575.6667 | 910 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | At S965 Pennant Hills Panel 26 Tripped Reclosed Tripped and Locked out on Relays: A and C phase IOC and A phase Timed and Lockout Signals: 11kV Trip EFI's NIL. Cause: Tree on OH near PT1137 Larool Cres See OMS1166778 1166785 | October | 2014 | 2015Q2 | 2015 | ZN965:PA26 | ZN965:PA26 | ZN00965/000026 | HORNSBY | OH | Veg | 2014-10-24 | N | 66.5667 | N | 5 | N | N | 1.1101 | 39.4971 | 44266.9105
[7 empty] | 12529 | 2554 | 1166536 | 2014-10-24 04:09 | 2014-10-24 14:50 | 641 | 11kV | 1923 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 142524 Single Phase DOLF Replaced L/A Excluded OMS 1166536 | October | 2014 | 2015Q2 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2014-10-24 | N | 641 | N | 5 | N | N | 1.1101 | 39.4971 | 1405.2717
[7 empty] | 12800 | 5029 | 1167567 | 2014-10-24 08:55 | 2014-10-24 14:50 | 355 | 11kV | 2840 | 8 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 142524/02 this recloser tripped in morning at 855 when sub 70233 was tried back (refer to OMS 1167566) | October | 2014 | 2015Q2 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2014-10-24 | N | 355 | N | 5 | N | N | 1.1101 | 39.4971 | 2075.3882
[7 empty] | 12685 | 4017 | 1166552 | 2014-10-24 07:25 | 2014-10-24 17:00 | 575 | 11kV | 575 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Unselected | N | Copy of 1166552 which was accidently closed Replaced transfomer 400kva lightning storm night before | October | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Not Veg | 2014-10-24 | N | 575 | N | 5 | N | N | 1.1101 | 39.4971 | 420.193
[7 empty] | 14418 | 18043 | 1166941 | 2014-10-25 01:49 | 2014-10-25 06:19 | 270 | 11kV | 62720 | 634 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142538 2 fault operations A phase Overcurrent Blown UGOH at pole JU-31043, Blown tapping at pole JU-35513 Prot Sw 8088 - Aph O/C, Sw 90574 - A+C Dir OC. Excluded OMS 1166941 / 42 / 43 | October | 2014 | 2015Q2 | 2015 | 203:8088 | 204:82703 | ZN00204/082703 | NEWCASTLE | OH | Not Veg | 2014-10-25 | N | 98.9274 | N | 10 | N | N | 1.1101 | 39.4971 | 45833.9261
[7 empty] | 12974 | 6594 | 1166999 | 2014-10-25 11:01 | 2014-10-25 11:31 | 30 | 11kV | 90 | 3 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | At Sub 6459 Boorea Nyrang No.1 LV Busbar Supply tripped on No.1 Busbar O/C Panel: BBOC 1 Relay 25/10/2014: Trip LED, Protection Trip LED, BBOC LED Remarks: Overload. Customer exceeding O/C Setting | October | 2014 | 2015Q2 | 2015 | ZN2466:PA15 | ZN1068:PA19 | ZN01068/000019 | CUMBERLAND | Unknown | Not Veg | 2014-10-25 | N | 30 | N | 10 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 12801 | 5039 | 1166990 | 2014-10-25 10:00 | 2014-10-25 11:40 | 100 | 11kV | 300 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142542 A phase DOLF : 16 Amp | October | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-10-25 | N | 100 | N | 10 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 14203 | 16511 | 1167033 | 2014-10-25 13:39 | 2014-10-25 14:26 | 46.55 | 11kV | 31979.85 | 687 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | LID 142544 2 fault operations 3 Phase Overcurrent Faulty pothead Pole AH-11643 Satur Rd x Gray St. Link 74256 on same pole. Excluded OMS 1167038 | October | 2014 | 2015Q2 | 2015 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | Unknown | Unknown | 2014-10-25 | N | 46.55 | N | 10 | N | N | 1.1101 | 39.4971 | 23369.9311
[7 empty] | 13037 | 7069 | 1167073 | 2014-10-25 16:13 | 2014-10-25 16:47 | 34 | 11kV | 3146 | 338 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142555 2 fault operations Instantaneous Earth Fault; Earth Fault; Overcurrent Excluded OMS 1167073 | October | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2014-10-25 | N | 9.3077 | N | 10 | N | N | 1.1101 | 39.4971 | 2299.004
[7 empty] | 14523 | 18881 | 1167010 | 2014-10-25 11:51 | 2014-10-25 17:48 | 357 | 11kV | 40099 | 192 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa2 "THe gunderman" fdr from RE45013 Gunderman tripped reclosed and locked out on overcurrent Tree branch brought down HV through LV mains outside 5615 Wisemans Ferry rd Gunderman. 2nd Event Dump and Restore at 1705 as it does not phase with Endeavour Energy Supply. DESO Contacted to have EMSO chech customer installation See 1168242,5,6,7 2nd 1168249,50,1 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2014-10-25 | N | 208.849 | N | 10 | N | N | 1.1101 | 39.4971 | 29303.1665
[7 empty] | 13949 | 14577 | 1167080 | 2014-10-25 16:59 | 2014-10-25 20:16 | 197 | 11kV | 197 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Unselected | Unplanned | Electrical Storm | N | LID 142558 Single phase DOLF : 10 Amp Excluded OMS 1167080 | October | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | Unknown | Veg | 2014-10-25 | N | 197 | N | 10 | N | N | 1.1101 | 39.4971 | 143.9618
[7 empty] | 12924 | 6152 | 1167119 | 2014-10-25 20:40 | 2014-10-25 22:39 | 119.2167 | 11kV | 583.3833 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142564 A phase DOLF : 10 Amp Excluded OMS # 1167119 Grouped with OMS # 1167127 | October | 2014 | 2015Q2 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2014-10-25 | N | 83.3405 | N | 10 | N | N | 1.1101 | 39.4971 | 426.3193
[7 empty] | 12298 | 434 | 1167131 | 2014-10-25 22:32 | 2014-10-26 00:55 | 143 | 11kV | 715 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142566 C Phase DOLF : 40 Amp Excluded OMS 1167131 | October | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-10-25 | N | 143 | N | 10 | N | N | 1.1101 | 39.4971 | 522.5009
[7 empty] | 14541 | 19019 | 1167121 | 2014-10-25 20:41 | 2014-10-26 01:10 | 269 | 11kV | 26631 | 99 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 142563 4 fault operations B phase Earth fault Wire on ground at pole HQ-83908 Excluded OMS 1167139 | October | 2014 | 2015Q2 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Not Veg | 2014-10-25 | N | 269 | N | 10 | N | N | 1.1101 | 39.4971 | 19461.1493
[7 empty] | 12707 | 4203 | 1167142 | 2014-10-26 06:35 | 2014-10-26 08:22 | 107 | 11kV | 186345 | 1744 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 142568 1 fault operation A & C phase Overcurrent Sensitive Earth Fault faulty reclose relay on fdr, reported 30.9.14 splitting timber removed from pole hr 51005 Excluded OMS 1167142 | October | 2014 | 2015Q2 | 2015 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2014-10-26 | N | 106.8492 | N | 9 | N | N | 1.1101 | 39.4971 | 136175.4298
[7 empty] | 12306 | 500 | 1167145 | 2014-10-26 06:55 | 2014-10-26 08:25 | 90 | 11kV | 180 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142567 Single phase DOLF : 10 Amp Excluded OMS 1167145 | October | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-10-26 | N | 90 | N | 9 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 12568 | 3010 | 1167158 | 2014-10-26 07:28 | 2014-10-26 08:45 | 77 | 11kV | 231 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 142569 A & C phase DOLF : 10 Amp Excluded OMS 1167158 | October | 2014 | 2015Q2 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2014-10-26 | N | 77 | N | 9 | N | N | 1.1101 | 39.4971 | 168.808
[7 empty] | 13430 | 10425 | 1167206 | 2014-10-26 11:07 | 2014-10-26 12:55 | 108 | 11kV | 169412 | 2003 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | Zn12640 Umina Pa13 fdr tripped on A&C phase overcurrent, earth fault, lockout, reclose, time delay UGOH Fault short circuit below PT11189. Between PT11189 tee to Ab45428, RE47749. See 1168269,71,2 Exclude 1167201,2,4,6,8,10,12,51 | October | 2014 | 2015Q2 | 2015 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | Unknown | Unknown | 2014-10-26 | N | 84.5791 | N | 9 | N | N | 1.1101 | 39.4971 | 123801.2928
[7 empty] | 13443 | 10518 | 1167226 | 2014-10-26 13:27 | 2014-10-26 16:00 | 152.8833 | 11kV | 5350.9167 | 35 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 142573 A phase Sectionaliser tree found on mains | October | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-10-26 | N | 152.8833 | N | 9 | N | N | 1.1101 | 39.4971 | 3910.2921
[7 empty] | 13225 | 8565 | 1167253 | 2014-10-26 16:10 | 2014-10-26 16:45 | 35 | 11kV | 140 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 142574 C phase DOLF : 10 Amp Excluded oms 1167253 | October | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-10-26 | N | 35 | N | 9 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 12475 | 1954 | 1167268 | 2014-10-26 17:07 | 2014-10-26 17:58 | 51 | 11kV | 51 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 142575 C Phase DOLF : 10 Amp oms device is wrong the sub is 51477 Excluded oms 1167268 | October | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-10-26 | N | 51 | N | 9 | N | N | 1.1101 | 39.4971 | 37.2693
[7 empty] | 14164 | 16249 | 1167263 | 2014-10-26 16:49 | 2014-10-26 20:33 | 224.4 | 11kV | 20869.2 | 93 | HV | Arcing | Equipment Failure | O/H Link | Unplanned | Unselected | N | Section of ZN.15013 Terrey Hills 11kV Panel 10 feeder from RE.20852 to the extent of the feeder (5DC's - PT.15952, PT.16481, S.16159, PT.16809, S.46269) Cause:- 11kV USL.24283 arcing requiring repair Interrupted for safety reasons. Note: customer reports that "FLAMES COMING FROM POLE TX IN FRONT OF 302 ME:-1167263 CC1: 22-"Refer to SOp" | October | 2014 | 2015Q2 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-10-26 | N | 224.4 | N | 9 | N | N | 1.1101 | 39.4971 | 15250.5958
[7 empty] | 13067 | 7365 | 1167319 | 2014-10-26 23:10 | 2014-10-27 00:14 | 64 | 11kV | 53568 | 837 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | @Zn 1287 Revesby Panel 6 "River Blamey" fdr tripped, reclosed and locked out: Relays: C phase IOC, timing and lock out relay Signals: 11kv trip Field EFI's: Nil Remarks: cause not ascertained. Dop Phan patrolled feeder. Feeder closed and restored volts checked at S4106 | October | 2014 | 2015Q2 | 2015 | ZN1287:PA6 | ZN1287:PA6 | ZN01287/000006 | CANTERBURY-BANKSTOWN | OH | Veg | 2014-10-26 | N | 64 | N | 9 | N | N | 1.1101 | 39.4971 | 39145.9144
[7 empty] | 14168 | 16269 | 1167324 | 2014-10-27 02:29 | 2014-10-27 04:10 | 101 | 11kV | 21815 | 321 | HV | Animal Possum | Animal | O/H Link | Unplanned | Unselected | N | Zn12630 Peats Ridge Pa4 "Kulnura" fdr triped and reclosed locked out on Relays: A & C Phase timed overcurrent lock out relay and EFI Signals: 11kv trip Cause: Possum found crispy at base of pole with USL43383 on it See 1168345,6,7 Exclude 1167324,5,6,7,8 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-10-27 | N | 67.9595 | N | 12 | N | N | 1.1101 | 39.4971 | 15941.7586
[7 empty] | 13647 | 12097 | 1167331 | 2014-10-27 04:54 | 2014-10-27 09:40 | 286 | 11kV | 391149.3333 | 2886 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @Zn116 Leichhardt Panel 48 'Booth Anna' tripped on: Relays: C phase IOC, EFI Signal: 11kv trip, Tx3 Group earth and Zone earth Field EFIs: S3832, 7536, S4748, S6446, S98, S2346, S48372, S35550, S8707, S8950 Remarks: UG fault between Sub 8950 Alexandra Sterling Sw/B and Sub 7696 Pyrmont Bridge Rd Bush Sw/F. Sub 7696 Pyrmont Bridge Rd Bush 11kv must be changed to 5kv to be restored. At S7696 No1 and No2 Tx's changed over to 5k, No3 Tx isolated Related jobs: #1167331, 1167338, 1167335 | October | 2014 | 2015Q2 | 2015 | ZN116:PA48 | ZN384:PA70 | ZN00384/000070 | SYDNEY | UG | Not Veg | 2014-10-27 | N | 135.5334 | N | 12 | N | N | 1.1101 | 39.4971 | 285840.3958
[7 empty] | 12743 | 4581 | 1167346 | 2014-10-27 07:42 | 2014-10-27 09:40 | 118 | 11kV | 1888 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142580 A & B phase DOLF : 20 Amp Excluded OMS 1167346 | October | 2014 | 2015Q2 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2014-10-27 | N | 118 | N | 12 | N | N | 1.1101 | 39.4971 | 1379.6947
[7 empty] | 14426 | 18120 | 1167545 | 2014-10-27 13:10 | 2014-10-27 13:55 | 45 | 11kV | 1170 | 26 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142585 ISOLATE SECTION TO REPAIR TAPPING AT SUB 70574. | October | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-10-27 | N | 45 | N | 12 | N | N | 1.1101 | 39.4971 | 855.0015
[7 empty] | 12934 | 6256 | 1167488 | 2014-10-27 10:42 | 2014-10-27 14:00 | 198.2833 | 11kV | 41242.9333 | 208 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Wind | N | Broken bond /tap on sub 70574 could have been damaged from earlier lightning storm no further information available, further investigation required CC1: 06-"Urgent - O.H Mains - No others" | October | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-10-27 | N | 198.2833 | N | 12 | N | N | 1.1101 | 39.4971 | 30139.1192
[7 empty] | 13738 | 12824 | 1167362 | 2014-10-27 08:27 | 2014-10-27 14:55 | 388 | 11kV | 388 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142584 Single phase Replace DOLF's & LV fuses Excluded OMS 1167362 | October | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-10-27 | N | 388 | N | 12 | N | N | 1.1101 | 39.4971 | 283.539
[7 empty] | 14310 | 17292 | 1167639 | 2014-10-27 14:32 | 2014-10-27 15:24 | 52 | 11kV | 14820 | 285 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Unselected | N | LID 142591 1 fault operation 3 phase Overcurrent; Earth fault FLAGS fdr 48001 o/c & e/f fdr 48010 was feed from 48001 via RMU sw 48057 planned switching. 33kV fdr KU13 fell into 11kV at pole HR-80555 near sub 43596 figtree ln WWPS. Tapping blown off at pole HR-80442. UGOH blown up at pole HR-50893. Arrestor damaged at UGOH pole HR-50604. relates to Reports 142592 & 142593 also Sw 48001 has vented oil. Please check. | October | 2014 | 2015Q2 | 2015 | 502:48001 | 502:48001 | ZN00502/048001 | MAITLAND | OH | Not Veg | 2014-10-27 | N | 52 | N | 12 | N | N | 1.1101 | 39.4971 | 10830.0189
[7 empty] | 13283 | 8999 | 1167688 | 2014-10-27 14:54 | 2014-10-27 15:51 | 57 | 11kV | 83370 | 1742 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Zn12600 Lisarow Pa3 tripped Relays: C phase overcurrent Signals: 11kv trip Strong Wind and high temerature when trip occured. DOp found no cause visible during patrol See 1168369,71,2 Exclude 1167688 | October | 2014 | 2015Q2 | 2015 | ZN12600:PA3 | ZN12600:PA3 | ZN12600/000003 | CENTRAL COAST | OH | Veg | 2014-10-27 | N | 47.8588 | N | 12 | N | N | 1.1101 | 39.4971 | 60924.337
[7 empty] | 12271 | 123 | 1167804 | 2014-10-27 15:54 | 2014-10-27 18:10 | 136 | 11kV | 9792 | 72 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142589 No protection operation, Conductor burnt off top of C phase DOLF. | October | 2014 | 2015Q2 | 2015 | 230:81440 | 230:81440 | ZN00230/081440 | PORT STEPHENS | OH | Not Veg | 2014-10-27 | N | 136 | N | 12 | N | N | 1.1101 | 39.4971 | 7155.7048
[7 empty] | 13048 | 7149 | 1167989 | 2014-10-27 21:08 | 2014-10-27 21:25 | 17 | 11kV | 3672 | 216 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | N | Section of 11kv feeder from S5412 Cottam Cant Sw/B to AB 324 tee PT421 Hoskins Ave to S7438 Exceller Hoskins Sw/A to AB 380 interrupted by Dop to allow removal of tree branch from 11kv mains. Ex panel 16 "Canterbury Fair" fdr Remarks: tree/branch on OH mains. Branch on 11kv mains near AB 2487. Note: AB 2487 would not open. Required to be extended back to S5412 and AB 324 | October | 2014 | 2015Q2 | 2015 | ZN35800:PA16 | ZN35800:PA16 | ZN35800/000016 | CANTERBURY-BANKSTOWN | OH | Veg | 2014-10-27 | N | 17 | N | 12 | N | N | 1.1101 | 39.4971 | 2683.3893
[7 empty] | 14269 | 17006 | 1167663 | 2014-10-27 14:40 | 2014-10-27 23:05 | 505 | 11kV | 33896 | 190 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | CP Quarry Old Northern Tripped and locked out on Relays: O/C Trip and Lockout Cause: Tree branch on mains O/S 2 Hemers Rd Dural See OMS 1168978 1168976 11167663 1167675 | October | 2014 | 2015Q2 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2014-10-27 | N | 178.4 | N | 12 | N | N | 1.1101 | 39.4971 | 24770.197
[7 empty] | 13164 | 8075 | 1168015 | 2014-10-28 05:56 | 2014-10-28 07:30 | 94 | 11kV | 21056 | 224 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn14144 Wamberal Section of Pa5 @LK41596 bond off see 1168536 exclude 1168015,7 | October | 2014 | 2015Q2 | 2015 | ZN14144:PA5 | ZN14144:PA5 | ZN14144/000005 | CENTRAL COAST | OH | Not Veg | 2014-10-28 | N | 94 | N | 4 | N | N | 1.1101 | 39.4971 | 15387.1038
[7 empty] | 12613 | 3307 | 1170902 | 2014-10-28 11:30 | 2014-10-28 11:50 | 20 | 11kV | 60 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142612 sub isolated to repair ll clamp Excluded oms 1168104 | October | 2014 | 2015Q2 | 2015 | 526:34637 | 526:34637 | ZN00526/034637 | CESSNOCK | OH | Not Veg | 2014-10-28 | N | 20 | N | 4 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 14343 | 17496 | 1167624 | 2014-10-27 14:16 | 2014-10-28 12:55 | 1359 | 11kV | 31863 | 101 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | LID 142594 1 fault operation Sensitive Earth Fault Full patrol due to TOBAN day | October | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-10-27 | N | 315.4752 | N | 12 | N | N | 1.1101 | 39.4971 | 23284.5406
[7 empty] | 12981 | 6662 | 1168255 | 2014-10-28 13:00 | 2014-10-28 13:45 | 45 | 11kV | 270 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | PT47388 SPrings Finns centre phase 11kv HDO was found open 63A. FUse Fatigue See 1168537 exclude 1168255 | October | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-10-28 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 14220 | 16669 | 1168405 | 2014-10-28 16:17 | 2014-10-28 17:21 | 64 | 11kV | 10239 | 200 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | Unselected | N | At S5868 Gore Hill Panel 18 Tripped on Earth Leakage and EFI. Abnormal Switching: Panel 16 at S35335 RNS was OOS and Open with SW/B at S47162 RNSH Closed Cause: 11KV feeder from S5888 Gore Hill to S47162 to S62445 SW/F Failed after being abnormally switched. See OMS 1168967 1168405 | October | 2014 | 2015Q2 | 2015 | ZN35335:PA16 | ZN35335:PA16 | ZN35335/000016 | WILLOUGHBY | UG | Not Veg | 2014-10-28 | N | 51.195 | N | 4 | N | N | 1.1101 | 39.4971 | 7482.3592
[7 empty] | 12445 | 1766 | 1168483 | 2014-10-29 00:59 | 2014-10-29 01:20 | 21 | 11kV | 84 | 4 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 142615 A phase DOLF : 10 Amp Possum excluded OMS 1168483 | October | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2014-10-29 | N | 21 | N | 5 | N | N | 1.1101 | 39.4971 | 61.3847
[7 empty] | 13816 | 13387 | 1168874 | 2014-10-29 16:05 | 2014-10-29 17:30 | 85 | 11kV | 1870 | 22 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 142633 Pole GT 14388 Damaged. 11kV 500mm above LV. Excluded OMS 1168874 | October | 2014 | 2015Q2 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Not Veg | 2014-10-29 | N | 85 | N | 5 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 13829 | 13486 | 1168751 | 2014-10-29 13:10 | 2014-10-29 17:51 | 281 | 11kV | 150770 | 1513 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn12580 Erina Pa10 fdr tripped Relays: Aphase IOC and Timed Overcurrent, EFI Signals: 11kv trip EFI's: S13682 S12866 S4189 11kV UG Fault from S14189 to S18183 to S14190 to Open UGOH See 1169025,7,9,30,1 Exclude 1168751,904 | October | 2014 | 2015Q2 | 2015 | ZN12580:PA10 | ZN12580:PA10 | ZN12580/000010 | CENTRAL COAST | UG | Not Veg | 2014-10-29 | N | 99.6497 | N | 5 | N | N | 1.1101 | 39.4971 | 110178.269
[7 empty] | 13695 | 12457 | 1168838 | 2014-10-29 15:00 | 2014-10-29 21:20 | 380 | 11kV | 152151 | 1187 | HV | Excavation Ausgrid Contractor | Utility Process Issue | U/G Cable | Unplanned | Unselected | N | LID 142634 2 fault operations A phase Earth fault HV Cable damaged by contractor (not ours) at 16 Walsh St Rutherford. Generator Installed at 56218 Walsh St sub. Excluded OMS 1168838; 1168847; 1168892 | October | 2014 | 2015Q2 | 2015 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | UG | Not Veg | 2014-10-29 | N | 128.1811 | N | 5 | N | N | 1.1101 | 39.4971 | 111187.4631
[7 empty] | 12418 | 1560 | 1168939 | 2014-10-29 23:41 | 2014-10-30 00:44 | 63 | 11kV | 81144 | 1288 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn3672 Maroubra Pnl.9 tripeed on: E/F, EFI, Fault Check Field EFIs: S2901 S2127 S8048 S35092 UG cable fault from S35092 (Sw B) to S8960 (Sw A) See 1168939 1168940 | October | 2014 | 2015Q2 | 2015 | ZN3672:PA9 | ZN3672:PA9 | ZN03672/000009 | RANDWICK | UG | Not Veg | 2014-10-29 | N | 63 | N | 5 | N | N | 1.1101 | 39.4971 | 59297.6419
[7 empty] | 14241 | 16846 | 1168941 | 2014-10-30 00:29 | 2014-10-30 01:45 | 76 | 11kV | 4864 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142635 B phase DOLF : 40 Amp Volts = 243. Amps = 107, 93, 47. Excluded OMS 1168941; 1168942 | October | 2014 | 2015Q2 | 2015 | 221:11897 | 221:11897 | ZN00221/011897 | LAKE MACQUARIE | OH | Veg | 2014-10-30 | N | 76 | N | 4 | N | N | 1.1101 | 39.4971 | 3554.4677
[7 empty] | 12593 | 3185 | 1168999 | 2014-10-30 08:52 | 2014-10-30 10:55 | 123 | 11kV | 984 | 8 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex Zn14891 Wyong section of Pa5 "Wyong" @PT13265 Jilliby 2.4 Centre phase 11kb bond above dropout fuse has come away See 1169402 exclude 1168999,9036 | October | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-10-30 | N | 123 | N | 4 | N | N | 1.1101 | 39.4971 | 719.0782
[7 empty] | 13497 | 10933 | 1169116 | 2014-10-30 12:17 | 2014-10-30 17:25 | 308 | 11kV | 22767 | 108 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | Zn12650 West Gosford section of Pa1 "Dog Trap Road" Recloser 44602 Ourimbah Creek rd tripped and lockedout on Relays: SEL, Lockout Small truck hit pole bringing mains down on the truck and shifting pole. 385 Ourimbah creek rd Ourimbah See 1169415,7,8,9 Exclude 1169116,21 | October | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2014-10-30 | N | 210.8056 | N | 4 | N | N | 1.1101 | 39.4971 | 16637.4521
[7 empty] | 14229 | 16746 | 1169304 | 2014-10-31 06:17 | 2014-10-31 08:00 | 103 | 11kV | 103 | 1 | HV | Vegetation Blow/Fall In | Vegetation | Fuse | Unplanned | Unselected | N | @ S.1352 MWS & DB Victoria Rd, section of ZN.965 Pennant Hills Zone Panel 42 feeder - Centre phase 80K HDO blown Cause:- Tree branch contact, twig on UGOH ME:-1169305 Withdrawn:-1169304 CC1: 22-"Refer to SOp" | October | 2014 | 2015Q2 | 2015 |  |  |  | HORNSBY | OH | Veg | 2014-10-31 | N | 103 | N | 3 | N | N | 1.1101 | 39.4971 | 75.2694
[7 empty] | 13286 | 9011 | 1169396 | 2014-10-31 10:20 | 2014-10-31 10:47 | 27 | 11kV | 2835 | 105 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | LID 142653 Interruption to disconnect generator and restore normal supply after 11kV cable repaired. | October | 2014 | 2015Q2 | 2015 | 502:48004 | 502:48004 | ZN00502/048004 | MAITLAND | UG | Not Veg | 2014-10-31 | N | 27 | N | 3 | N | N | 1.1101 | 39.4971 | 2071.7344
[7 empty] | 13151 | 7993 | 1170852 | 2014-10-30 14:10 | 2014-10-31 17:10 | 1620 | 11kV | 1620 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Unselected | N | LID 142657 Parkville piggeries. Broken X-arm on customer pole. Isolated while customer carries out repairs. | October | 2014 | 2015Q2 | 2015 |  |  |  |  | Unknown | Not Veg | 2014-10-30 | N | 1620 | N | 4 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 12462 | 1838 | 1169564 | 2014-10-31 16:47 | 2014-10-31 21:21 | 274 | 11kV | 38086 | 139 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | LID 142658 Tree on OHM at pole AS-30078 sub 59066 | October | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-10-31 | N | 274 | N | 3 | N | N | 1.1101 | 39.4971 | 27832.1255
[7 empty] | 12320 | 630 | 1169660 | 2014-11-01 10:17 | 2014-11-01 12:00 | 103 | 11kV | 103 | 1 | HV | Animal Frog | Animal | DC PT | Unplanned | Unselected | Y | LID 142663 B Phase DOLF : 10 Amp Excluded OMS 1169660 | November | 2014 | 2015Q2 | 2015 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Not Veg | 2014-11-01 | Y | 103 | N | 8 | N | Y | 1.1101 | 39.4971 | 75.2694
[7 empty] | 13982 | 14796 | 1169688 | 2014-11-01 11:57 | 2014-11-01 13:17 | 80 | 11kV | 91821 | 1293 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | Y | Zn2602 Clovelly - Pnl. 36 tripped on: A & C phase IOC, Fault Check, EFI Signals: Zone earth, no.4 group trip Field EFIs: S47365, S4053, S49242 S8811 S8476 S2678 UG cablle fault (11kV) from S2678 to S4592 to S47028 see 1170772 1170775 GIS: 1169697 1169695 | November | 2014 | 2015Q2 | 2015 | ZN2602:PA36 | ZN35600:PA11 | ZN35600/000011 | RANDWICK | UG | Not Veg | 2014-11-01 | N | 71.0139 | N | 8 | N | N | 1.1101 | 39.4971 | 67100.0785
[7 empty] | 14259 | 16964 | 1169709 | 2014-11-01 13:17 | 2014-11-01 14:36 | 79 | 11kV | 55932 | 708 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | @ ZN.35370 Galston Zone 11kV Panel 8 tripped, reclosed, tripped & locked out on:- Relays:- 50T A & C phase, A & C trip, EFI, Lockout Signals:- 11kV Trip, Zone Earth, Group Earth EFI's:- NIL Cause:- Tree/branch on OH mains Tree branch on 11kV OH mains in Johnson St, Opposite Hansen St ME:-1169709 Withdrawn:-1169712, 1169713 | November | 2014 | 2015Q2 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2014-11-01 | Y | 79 | N | 8 | N | Y | 1.1101 | 39.4971 | 40873.4559
[7 empty] | 12686 | 4021 | 1169667 | 2014-11-01 11:05 | 2014-11-01 15:00 | 235 | 11kV | 986 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | Y | Ex Zn12650 West Gosford section of Pa1 "Dog Trap Rd" fdr Falling tree branch twisted 11kV mains together beyond LK43922 See 1171348,50,1 Exclude 1169667,9 | November | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 9.1296 | N | 8 | N | Y | 1.1101 | 39.4971 | 720.5397
[7 empty] | 14329 | 17373 | 1169751 | 2014-11-01 14:28 | 2014-11-01 16:30 | 122 | 11kV | 135542 | 1111 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | ZN 10994 Mortdale - Pnl 10 - Trip/reclose/trip, A & B phase OC, Earth Fault, EFI, Lockout. Tree on mains during storm. | November | 2014 | 2015Q2 | 2015 | ZN10994:PA10 | ZN10994:PA10 | ZN10994/000010 | GEORGES RIVER | OH | Veg | 2014-11-01 | N | 122 | N | 8 | N | N | 1.1101 | 39.4971 | 99050.0958
[7 empty] | 14000 | 14937 | 1169770 | 2014-11-01 14:45 | 2014-11-01 17:36 | 171 | 11kV | 219906 | 1286 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | Y | ZN 10995 Riverwood - Pnl 13 - Trip/reclose/trip, A phase IOC, timing, lockout. Branch on mains at 28 Belmore Rd, Riverwood. Patrolled and restored. | November | 2014 | 2015Q2 | 2015 | ZN10995:PA13 | ZN10995:PA13 | ZN10995/000013 | GEORGES RIVER | OH | Veg | 2014-11-01 | N | 171 | N | 8 | N | N | 1.1101 | 39.4971 | 160700.8187
[7 empty] | 12978 | 6632 | 1169734 | 2014-11-01 14:03 | 2014-11-01 17:45 | 222 | 11kV | 99887 | 851 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | ZN.15014 Mona Vale Zone 11kV Panel 22 feeder tripped on:- Relays:- Earth Fault, Fault Check, EFI Signals:- 11kV Trip Field EFI's:- S.16761, S.16817, S.16695 Cause:- Tree branch removed for 11kV OH mains ME:-1170850 RS:-1170851, 1170855 Related:- ME:-1170848 (LV S.16248 Dist.2) ME:-1169738 (Customer reported wires down) Withdrawn:-1170362, 1169734 | November | 2014 | 2015Q2 | 2015 | ZN15014:PA22 | ZN15014:PA22 | ZN15014/000022 | NORTHERN BEACHES | OH | Veg | 2014-11-01 | N | 117.376 | N | 8 | N | N | 1.1101 | 39.4971 | 72994.4734
[7 empty] | 14600 | 19625 | 1170007 | 2014-11-01 16:25 | 2014-11-01 17:46 | 81 | 11kV | 115101 | 1421 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | Zn14891 Wyong Pa5 "The Wyong" fdr tripped on AB phase IOC, reclose lockout, reclsoe timer Tree/Branch on Oh Mains location 1: outside 3 Wakehurst Drive, Wyong location 2: near 1st UGOH from Zone both cleared by DOp See 1171451 GIS 1170021,36,47 Exclude 1170007,9,13,43,9,27,8 | November | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 81 | N | 8 | N | Y | 1.1101 | 39.4971 | 84112.4159
[7 empty] | 13260 | 8833 | 1169904 | 2014-11-01 15:48 | 2014-11-01 18:20 | 152 | 11kV | 5181 | 48 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | Y | LID 142670 1 fault operation A phase Overcurrent Cause was damaaged 11kV dropper lead at sub 53358, one had broken away and clashed. Reclsoer was non auto due to bush fire defects. Excluded OMS 1169904 | November | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2014-11-01 | Y | 107.9375 | N | 8 | N | Y | 1.1101 | 39.4971 | 3786.122
[7 empty] | 12655 | 3785 | 1171461 | 2014-11-01 16:17 | 2014-11-01 18:40 | 143 | 11kV | 14586 | 102 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | Y | LID 142687 1 fault operation Overcurrent Reclose non Auto (TFB) | November | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-11-01 | Y | 143 | N | 8 | N | Y | 1.1101 | 39.4971 | 10659.0186
[7 empty] | 12447 | 1779 | 1169908 | 2014-11-01 15:53 | 2014-11-01 18:58 | 185 | 11kV | 8140 | 44 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 142668 2 fault operation 3 phase Overcurrent Tree limb found across mains at pole CM-60515. Excluded OMS see 1169908 | November | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-11-01 | Y | 185 | N | 8 | N | Y | 1.1101 | 39.4971 | 5948.4719
[7 empty] | 12563 | 2952 | 1170065 | 2014-11-01 16:53 | 2014-11-01 19:33 | 160 | 11kV | 224713 | 1409 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 142672 2 fault operations A phase Overcurrent; Earth fault (not bushfire fdr) cursory patrol by dop nil found, please arrange detailed patrol. DQ | November | 2014 | 2015Q2 | 2015 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Veg | 2014-11-01 | Y | 159.484 | N | 8 | N | Y | 1.1101 | 39.4971 | 164213.6325
[7 empty] | 13316 | 9358 | 1170136 | 2014-11-01 16:58 | 2014-11-01 19:49 | 171 | 11kV | 21204 | 124 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 142683 1 fault operation Overcurrent Sw 75379 reclose non auto (TFB) Excluded OMS 1170136 | November | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-11-01 | N | 171 | N | 8 | N | N | 1.1101 | 39.4971 | 15495.2578
[7 empty] | 13360 | 9800 | 1169776 | 2014-11-01 14:30 | 2014-11-01 19:50 | 320 | 11kV | 201566 | 1308 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Previous Storm | Y | ZN 9252 Jannali - Pnl 4 - Trip/reclose/trip, C phase IOC, Timed OC, Lockout, EFI. Metal sheeting off a roof blew off in storm and wrapped around 11kV and LV mains. AB 35313 was defective and left open. ME: 1172063. Rest Steps: 1172065, 6. Withdrawn: 1169754, 59, 76, 90, 1169844. | November | 2014 | 2015Q2 | 2015 | ZN9252:PA4 | ZN9252:PA30 | ZN09252/000030 | SUTHERLAND | OH | Veg | 2014-11-01 | Y | 154.1024 | N | 8 | N | Y | 1.1101 | 39.4971 | 147298.4876
[7 empty] | 12677 | 3945 | 1169883 | 2014-11-01 15:43 | 2014-11-01 20:05 | 262 | 11kV | 301585 | 1858 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 142690 2 fault operations 3 phase Overcurrent; Earth fault Mains down NEH near Pinaroo Caravan Pk Excluded OMS 1169883 | November | 2014 | 2015Q2 | 2015 | 812:19066 | 812:19066 | ZN00812/019066 | MUSWELLBROOK | OH | Not Veg | 2014-11-01 | Y | 162.317 | N | 8 | N | Y | 1.1101 | 39.4971 | 220389.4227
[7 empty] | 14387 | 17816 | 1169735 | 2014-11-01 13:59 | 2014-11-01 20:10 | 371 | 11kV | 37427 | 260 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | Section of ZN.15013 Terrey Hills Zone 11kv feeder from RE.1126 to extent of the feeder (20DC's) RE.1126 Mona Vale Rd tripped on:- Relays:- OC trip, Lock out Cause:- Weather related, 11kV OH mains down in Addison Rd Terrey Hills Note:- RE.1126 made N/A for vegetation clearance ME:-1170949 RS:-1170951 Withdrawn:-1169735 | November | 2014 | 2015Q2 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-11-01 | N | 143.95 | N | 8 | N | N | 1.1101 | 39.4971 | 27350.5477
[7 empty] | 13224 | 8555 | 1169763 | 2014-11-01 14:31 | 2014-11-01 20:23 | 352 | 11kV | 339656 | 996 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | ZN 9245 Engadine - Pnl 15 - trip/reclose/trip, C phase timed OC, Earth leakage, lockout. Storm in the area. Mains to patrol. ME: 1171770. Rest Steps: 1171772, 3. Withdrawn: 1169763. | November | 2014 | 2015Q2 | 2015 | ZN9245:PA15 | ZN9245:PA10 | ZN09245/000010 | SUTHERLAND | OH | Veg | 2014-11-01 | Y | 341.0201 | N | 8 | N | Y | 1.1101 | 39.4971 | 248210.5866
[7 empty] | 13327 | 9529 | 1169928 | 2014-11-01 16:02 | 2014-11-01 21:15 | 313 | 11kV | 40112 | 284 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | LID 142669 1 fault operation 3 phase Overcurrent Tree across mains near sub 27636. | November | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-11-01 | Y | 141.2394 | N | 8 | N | Y | 1.1101 | 39.4971 | 29312.6665
[7 empty] | 14460 | 18383 | 1170102 | 2014-11-01 16:50 | 2014-11-01 21:20 | 270 | 11kV | 48348 | 395 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 142675 1 fault operation B & C phase Overcurrent; Earth fault tree brought 11kv ohm down adj pole MW90053 Tanilba bay rd x browns rd | November | 2014 | 2015Q2 | 2015 | 230:81438 | 230:81438 | ZN00230/081438 | PORT STEPHENS | OH | Veg | 2014-11-01 | Y | 122.4 | N | 8 | N | Y | 1.1101 | 39.4971 | 35331.2924
[7 empty] | 12275 | 180 | 1169942 | 2014-11-01 16:08 | 2014-11-01 21:27 | 319 | 11kV | 19140 | 60 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 142688 1 fault operation Overcurrent Reclose Non Auto (TFB) | November | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-11-01 | Y | 319 | N | 8 | N | Y | 1.1101 | 39.4971 | 13986.9475
[7 empty] | 12589 | 3157 | 1170109 | 2014-11-01 17:17 | 2014-11-01 21:40 | 263 | 11kV | 263 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | Y | LID 142677 DOLF : 10 Amp Excluded OMS 1170109 | November | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-11-01 | N | 263 | N | 8 | N | N | 1.1101 | 39.4971 | 192.1926
[7 empty] | 12431 | 1671 | 1170368 | 2014-11-01 15:35 | 2014-11-01 21:44 | 369 | 11kV | 19414 | 60 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | Y | LID 142685 2 fault operation Earth fault Wire off Pin Excluded OMS 1169870 | November | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-11-01 | Y | 323.5667 | N | 8 | N | Y | 1.1101 | 39.4971 | 14187.1786
[7 empty] | 12983 | 6694 | 1169767 | 2014-11-01 14:31 | 2014-11-01 22:10 | 459 | 11kV | 286215 | 1941 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | Y | ZN 9700 Kirrawee - Pnl 11 - Trip/reclose/trip, Earth fault, lockout, timing, fault check, EFI, Field EFIs. 11kV into LV. Section of Pnl 11 fell into distributor from S 9106. PT 9502 was in LV// with PT 9644. ME: 1171931. Rest Steps: 1171933, 5. Withdrawn: 1169767. | November | 2014 | 2015Q2 | 2015 | ZN9700:PA11 | ZN9700:PA18 | ZN09700/000018 | SUTHERLAND | OH | Not Veg | 2014-11-01 | Y | 147.4575 | N | 8 | N | Y | 1.1101 | 39.4971 | 209157.4801
[7 empty] | 12511 | 2359 | 1170082 | 2014-11-01 17:02 | 2014-11-01 22:30 | 328.4333 | 11kV | 5583.3667 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 142676 C phase DOLF : 63 Amp | November | 2014 | 2015Q2 | 2015 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2014-11-01 | Y | 328.4333 | N | 8 | N | Y | 1.1101 | 39.4971 | 4080.1597
[7 empty] | 12322 | 661 | 1170306 | 2014-11-01 19:00 | 2014-11-01 23:25 | 265 | 11kV | 530 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 142679 A phase DOLF : 10 Amp | November | 2014 | 2015Q2 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Veg | 2014-11-01 | N | 265 | N | 8 | N | N | 1.1101 | 39.4971 | 387.3084
[7 empty] | 14390 | 17855 | 1169793 | 2014-11-01 14:51 | 2014-11-01 23:30 | 519 | 11kV | 111243 | 232 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | Section of ZN.2400 Berwora Zone 11kV Panel 21 feeder from RE.3202 Pacific South Cowan to the extent of the feeder (6 DC's) RE.3202 Pacific South Cowan tripped Relays:- EF trip, Lockout Cause:- Wires down Two bays of OH mains down between ABS.1191 & ABS.1061, repaired. Lighning arrestor blown at PT.640 Fraser Pacific ME:-1171545 RS:-1171549, 1171554 Withdrawn:-1169793 | November | 2014 | 2015Q2 | 2015 | ZN2400:PA21 | ZN2400:PA21 | ZN02400/000021 | HORNSBY | OH | Not Veg | 2014-11-01 | Y | 479.4957 | N | 8 | N | Y | 1.1101 | 39.4971 | 81293.1033
[7 empty] | 12486 | 2131 | 1169925 | 2014-11-01 16:03 | 2014-11-02 00:10 | 487 | 11kV | 21428 | 44 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | Y | Ex Zn12580 Erina section of Pa12 PT12993 Narrawa Entrance Footpath side phase HDO fuse blown. Size 20k Fuse Fatigue See 1171445 Exclude 1169925 | November | 2014 | 2015Q2 | 2015 | ZN12580:PA12 | ZN12580:PA12 | ZN12580/000012 | CENTRAL COAST | OH | Not Veg | 2014-11-01 | Y | 487 | N | 8 | N | Y | 1.1101 | 39.4971 | 15658.9504
[7 empty] | 12688 | 4023 | 1169849 | 2014-11-01 15:26 | 2014-11-02 00:21 | 535 | 11kV | 28355 | 53 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 142682 1 fault operation Sw 74712 reclose non auto (TFB). Fdr patrolled, no cause found. Burnt off tapping found at pole 9L-40811 upstream of Sw 74712. Switch left open until tapping could be repaired live line | November | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-11-01 | Y | 535 | N | 8 | N | Y | 1.1101 | 39.4971 | 20720.9977
[7 empty] | 13469 | 10681 | 1170230 | 2014-11-01 18:15 | 2014-11-02 00:33 | 378 | 11kV | 78506 | 616 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Zn12600 Lisarow Pa1 tripped reclosed tripped and locked out on Relays:51N (timed OC) EFI SEF LO Signals: 11kv trip Wires down from S14833 to AB44058 etc repaired. See 1171873,5,6 Exclude 1170230 | November | 2014 | 2015Q2 | 2015 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Not Veg | 2014-11-01 | Y | 127.4448 | N | 8 | N | Y | 1.1101 | 39.4971 | 57369.8693
[7 empty] | 12809 | 5086 | 1169863 | 2014-11-01 15:34 | 2014-11-02 02:00 | 626 | 11kV | 34430 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | Y | LID 142684 trip & Reclose non auto (TFB) Excluded OMS 1169863 Note: These 55 customers were also affected by sustained event with multiple restorations affecting Feeder 509:48039 - (refer to OMS 1171130 for the overlapping record which went from 01/11/2014 18:36:00 to 02/11/2014 11:39:00) | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-11-01 | Y | 626 | N | 8 | N | Y | 1.1101 | 39.4971 | 25160.4285
[7 empty] | 13013 | 6898 | 1171845 | 2014-11-02 00:45 | 2014-11-02 02:03 | 78 | 11kV | 20358 | 261 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 142678/02 Blown B phase tapping load side of ABS 41013. There were not enough live line workers to do the job live line, so had to do repairs via an access permit, the points of isolation meant the outage area had to be extended to do the job safely. | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-02 | N | 78 | N | 12 | N | N | 1.1101 | 39.4971 | 14877.0259
[7 empty] | 13436 | 10458 | 1169992 | 2014-11-01 16:06 | 2014-11-02 02:12 | 606 | 11kV | 78174 | 129 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | Y | LID 142671 Overcurrent 2 spans of 11kV were found down near sub 53321, also at the same time on downstream device HC42046 LID 142674 Earth fault Tree on 11kv near sub 53115. Also suspected HV to LV contact at sub 53115 had to be checked for safety. | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-01 | Y | 606 | N | 8 | N | Y | 1.1101 | 39.4971 | 57127.2535
[7 empty] | 14569 | 19219 | 1170039 | 2014-11-01 18:41 | 2014-11-02 02:12 | 451 | 11kV | 5863 | 13 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 142678/01 ABC DOLF : 3 Amp at sub 51532 Pankhurst Associated with excluded OMS # 1170248. The 3 DOLFs were blown at this sub, but staff also suspect another fault on the 11kV line. | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-01 | Y | 451 | N | 8 | N | Y | 1.1101 | 39.4971 | 4284.5075
[7 empty] | 14366 | 17628 | 1170132 | 2014-11-01 17:23 | 2014-11-02 02:33 | 550 | 11kV | 51049 | 190 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | Y | Section of ZN.35370 Galston 11 kV Panel 10L from IR.50015 to the extent of the feeder (19DC's) IR.50015 tripped, reclosed, tripped and locked out on:- Relays:- OC trip Field EFI's:- S.35228 Cause:- Tree/branchon OH mains Tree branch on 11kV mains outside 11 Harris Rd, Dural ME:-1171487 RS:-1171488 Withdrawn:-1170355, 1170218, 1170164, 1170133, 1170132 | November | 2014 | 2015Q2 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2014-11-01 | Y | 268.6789 | N | 8 | N | Y | 1.1101 | 39.4971 | 37305.1035
[7 empty] | 12437 | 1694 | 1170342 | 2014-11-01 16:00 | 2014-11-02 03:05 | 665 | 11kV | 7315 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 142697 B & C phase DOLF : 20 Amp | November | 2014 | 2015Q2 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2014-11-01 | Y | 665 | N | 8 | N | Y | 1.1101 | 39.4971 | 5345.5862
[7 empty] | 14334 | 17436 | 1169840 | 2014-11-01 15:23 | 2014-11-02 03:40 | 737 | 11kV | 737 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | Y | LID 142700 Live Line Clamp off Excluded OMS 1169840 | November | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-11-01 | Y | 737 | N | 8 | N | Y | 1.1101 | 39.4971 | 538.5779
[7 empty] | 13640 | 12063 | 1170237 | 2014-11-01 18:14 | 2014-11-02 04:25 | 611 | 11kV | 240902 | 852 | HV | Vegetation Blow/Fall In | Vegetation | Cross arm | Unplanned | Electrical Storm | Y | Ex Zn12580 Erina section of Pa4L "Springfield" fdr IR49613 Marana Tulip tripped, reclosed, tripped and locked out on overcurrent Large tree has broken cross arms adjacent AB41402. Section of fdr from AB41763 to AB41401 to S49973 to S50361 to AB41619 See 1171609,12 Exclude 1170237,44,55,70,437 | November | 2014 | 2015Q2 | 2015 | ZN12580:PA4 | ZN12580:PA4 | ZN12580/000004 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 282.7488 | N | 8 | N | Y | 1.1101 | 39.4971 | 176044.0762
[7 empty] | 13394 | 10126 | 1170239 | 2014-11-01 18:14 | 2014-11-02 05:10 | 656 | 11kV | 490284 | 772 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12570 Avoca Zone section of Pa29 RE44982 Bensville tripped on Relays: OC Signals: Lockout EFI's: ? Tree Branch on contact other. Burnt stick found near AB44383 See 1171786,8,9,91,2 Exclude 1170239 | November | 2014 | 2015Q2 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 635.0829 | N | 8 | N | Y | 1.1101 | 39.4971 | 358285.0863
[7 empty] | 14059 | 15461 | 1170442 | 2014-11-02 05:18 | 2014-11-02 06:09 | 51 | 11kV | 73548 | 1462 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.15011 Beacon Hill Zone Panel 10 feeder tripped on:- Relays:- Earth Fault, Fault Check & EFI Signals:- 11kV Trip, Zone Earth Field EFI's:- Nil Cause:- 11kV UG cable fault between ZN.15011 Beacon Hill Zone Panel 10 to S.16857 French Hurdis No.2 SW/B to S.16679 Rodborough Rd 14A SW/A ME:-1170764 RS:-1170765 Withdrawn:-1170442 | November | 2014 | 2015Q2 | 2015 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | UG | Not Veg | 2014-11-02 | N | 50.3064 | N | 12 | N | N | 1.1101 | 39.4971 | 53746.7091
[7 empty] | 13159 | 8039 | 1170453 | 2014-11-02 06:27 | 2014-11-02 07:30 | 63 | 11kV | 12096 | 192 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 Zetland - Pnl.45 tripped on: EF timed, FC, EFI Signals: Zn Earth, Tx 4 Group, 11kV Trip Field EFIs: S4176 UG cable fault from S4176 to S6436 to S6431 | November | 2014 | 2015Q2 | 2015 | ZN188:PA45 | ZN188:PA45 | ZN00188/000045 | SYDNEY | UG | Not Veg | 2014-11-02 | N | 63 | N | 12 | N | N | 1.1101 | 39.4971 | 8839.4
[7 empty] | 12796 | 4990 | 1170277 | 2014-11-01 18:40 | 2014-11-02 08:15 | 815 | 11kV | 13040 | 16 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn14143 Somersby section of Pa17 "Somersby Falls" PT14340 Daqwson Reeves 31A footpath HDO blown Weather related. Sever storm See 1171639 exclude 1170277,305,93,467,85 | November | 2014 | 2015Q2 | 2015 | ZN14143:PA17 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 815 | N | 8 | N | Y | 1.1101 | 39.4971 | 9529.2474
[7 empty] | 13478 | 10754 | 1170205 | 2014-11-01 18:10 | 2014-11-02 09:40 | 930 | 11kV | 70791 | 227 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Wind Storm | Y | Ex Zn12650 West Gosford section of Pa1 1st Event RE45010 Palm Grove tripped and locked out on earth fault 11kv Overhead down from USL43168 to PT12433 to PT12434. 2nd Event RE47849 Reservoir Beckford tripped reclosed, tripped and locked out on: Relays: OC, EF Signals: Lockout EFI's: N/A 3 Bays of OH down at hidden valley from AB44939 to LB47947 to RE44604 tee PT12616 See 1171546,57 2nd 1171548,51,2,3,5 Exclude 1170205,35 | November | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 311.8546 | N | 8 | N | Y | 1.1101 | 39.4971 | 51731.9748
[7 empty] | 12443 | 1757 | 1170530 | 2014-11-01 23:00 | 2014-11-02 10:50 | 710 | 11kV | 1420 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | Y | LID 142707 B phase DOLF : 10 Amp Excluded OMS 1170530 | November | 2014 | 2015Q2 | 2015 | 812:19071 | 812:19071 | ZN00812/019071 | MUSWELLBROOK | OH | Veg | 2014-11-01 | Y | 710 | N | 8 | N | Y | 1.1101 | 39.4971 | 1037.6941
[7 empty] | 12355 | 980 | 1170579 | 2014-11-01 15:36 | 2014-11-02 12:10 | 1234 | 11kV | 61430 | 50 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | Y | Ex Zn14143 Somersby section of Pa17 PT13610 Bar Point 0.3 Water side 10A HDO blown PT13611 Bar Point 0.7 Water side 10A HDO blown Cause not ascertained. During Storm See 1171438 2nd 1171442 GIS 1170579 exclude 1169869 | November | 2014 | 2015Q2 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 1228.6 | N | 8 | N | Y | 1.1101 | 39.4971 | 44891.2321
[7 empty] | 14090 | 15713 | 1170290 | 2014-11-01 18:36 | 2014-11-02 12:20 | 1064 | 11kV | 729128 | 786 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Wind | Y | LID 142689 1 fault operation A & C phase Overcurrent 3 spans of 11kV on ground near sub 50576 Wollombi No 1. Note DO's suspect 11kV contacted mains, Despatch arraqnging EMSO to check LV at customers installations. PD Also replaced DOLF at Hankin sub 50607 Excluded OMS 1170290 | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-11-01 | Y | 927.6438 | N | 8 | N | Y | 1.1101 | 39.4971 | 532825.2368
[7 empty] | 13722 | 12731 | 1169873 | 2014-11-01 15:37 | 2014-11-02 13:50 | 1333 | 11kV | 126114 | 143 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 142691 2 fault operations 3 phase Overcurrent; Earth fault Multiple spans OHM down Denman Rd | November | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-11-01 | Y | 881.9161 | N | 8 | N | Y | 1.1101 | 39.4971 | 92160.3915
[7 empty] | 13806 | 13327 | 1170444 | 2014-11-02 07:31 | 2014-11-02 14:11 | 400 | 11kV | 1200 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 142709 broken hv lead to LF 40877 Excluded oms 1170473 | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-02 | N | 400 | N | 12 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 13609 | 11774 | 1170203 | 2014-11-01 18:09 | 2014-11-02 15:55 | 1306 | 11kV | 255721 | 779 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | Y | Zn12570 Avoca Zn Pa34 tripped and locked out Relays: 50T, 150Tn, EFI, IOC AB phase Signals: 11kv trip Section of 11kv fdr from LB41406 to AB43138 to LB41002 tee PT18531 tree brought down OH See 1171490,1,2,3,4,5 Exclude 1170202,3,450,7 | November | 2014 | 2015Q2 | 2015 | ZN12570:PA34 | ZN12570:PA34 | ZN12570/000034 | CENTRAL COAST | OH | Veg | 2014-11-01 | Y | 328.2683 | N | 8 | N | Y | 1.1101 | 39.4971 | 186873.3643
[7 empty] | 14383 | 17780 | 1169860 | 2014-11-01 15:31 | 2014-11-02 16:10 | 1479 | 11kV | 59543 | 153 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | Y | LID 142686 1 fault operation Earth fault OHMs down to sub 50055 | November | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-11-01 | Y | 389.1699 | N | 8 | N | Y | 1.1101 | 39.4971 | 43512.2682
[7 empty] | 12699 | 4158 | 1171406 | 2014-11-02 13:34 | 2014-11-02 16:43 | 189 | 11kV | 23814 | 126 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | Section of ZN 9900 Menai - Pnl 19 - AB 35278 Tree branch on mains. DOp interrupted from ABS for safety reasons. | November | 2014 | 2015Q2 | 2015 | ZN9900:PA19 | ZN9900:PA19 | ZN09900/000019 | SUTHERLAND | OH | Veg | 2014-11-02 | N | 189 | N | 12 | N | N | 1.1101 | 39.4971 | 17402.5688
[7 empty] | 14185 | 16381 | 1170643 | 2014-11-02 14:44 | 2014-11-02 17:00 | 136 | 11kV | 272 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 142714 C phase DOLF : 10 Amp | November | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-11-02 | N | 136 | N | 12 | N | N | 1.1101 | 39.4971 | 198.7696
[7 empty] | 12687 | 4022 | 1170592 | 2014-11-02 11:39 | 2014-11-02 17:56 | 377 | 11kV | 20735 | 55 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 142715 2 fault operations Earth fault Tree on OHM at pole MN-82901 Excluded OMS 1170592 | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-11-02 | N | 377 | N | 12 | N | N | 1.1101 | 39.4971 | 15152.5264
[7 empty] | 13287 | 9026 | 1170659 | 2014-11-02 15:28 | 2014-11-02 18:06 | 158 | 11kV | 13114 | 83 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | Ex Zn12690 Berkeley Vale section of Pa24L "Berkeley Rd" 11kv feeder section from LB44757 to RE45117 to LK42212 to LB40904 interrupted for safety to remove tree off mains. Note LB42219 will not open See 1172623 exclude 1170659 | November | 2014 | 2015Q2 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Veg | 2014-11-02 | N | 158 | N | 12 | N | N | 1.1101 | 39.4971 | 9583.3244
[7 empty] | 13914 | 14219 | 1170671 | 2014-11-02 16:39 | 2014-11-02 20:15 | 215.65 | 11kV | 40591.6 | 244 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | @ S.4698 Boronia Kissing Point - 11kV 40A centre phase blown @ PT.52 Yeramba Dawson LV Dist.1 - A, B, C phase blown (LV//) @ PT.2050 Wattle Kissing Point - 11kV 31.5A roadside & centre phase blown (LV//) @ S.4975 Kate Waratah LV Dist 1 - A, B, C phase blown (LV//) Cause:- Vehicle hit mains Truck brought down LV Oh mains on the corner of Boronia St & Yeramba St, Turramurra Note:- S.4698, S.4975, PT.2050, PT.52 in LV// ME:-1170674 ME:-1170685, 1170673, 1170677 (LV//) Withdrawn:-1170671 CC1: 22-"Refer to SOp" | November | 2014 | 2015Q2 | 2015 | ZN1673:PA6 | ZN1673:PA6 | ZN01673/000006 | KU-RING-GAI | OH | Not Veg | 2014-11-02 | N | 166.359 | N | 12 | N | N | 1.1101 | 39.4971 | 29663.144
[7 empty] | 14155 | 16199 | 1170670 | 2014-11-02 21:03 | 2014-11-02 22:35 | 92 | 11kV | 26404 | 287 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Previous Storm | N | Ex Zn14144 Wamberal section of Pa10 "Wmaberal Aux No.2" fdr from LK41244 to LK40857 OH CCT on crossarm in matcham interrupted by DOp for repairs Also Customer report Tree on Mains close to PT12080 See 1172631 exclude 1170670,722 | November | 2014 | 2015Q2 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2014-11-02 | N | 92 | N | 12 | N | N | 1.1101 | 39.4971 | 19295.2644
[7 empty] | 12602 | 3234 | 1170681 | 2014-11-02 19:21 | 2014-11-02 22:45 | 204 | 11kV | 762 | 120 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 142716 1 fault operation Overcurrent Sub tank failed. Reclose was off as crew was on site when Sw 42268 tripped. | November | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-11-02 | N | 6.35 | N | 12 | N | N | 1.1101 | 39.4971 | 556.8471
[7 empty] | 13310 | 9203 | 1170730 | 2014-11-02 22:20 | 2014-11-02 23:37 | 77 | 11kV | 158263 | 2203 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ Zn2310 Punchbowl 11kv Panel 34 'S3106 Sylvester King Georges" feeder tripped Relays: E/F, EFI Signals: ZE, Tx5 Ge, 11kv trip Field EFIs: S3106, S36008, S48550 Remarks: UG fault. 11kv feeder isolated at/from S3528 Quigg Cant to S2509 Leyland Marie to S274 Wilson Av | November | 2014 | 2015Q2 | 2015 | ZN2310:PA34 | ZN2310:PA14 | ZN02310/000014 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-11-02 | N | 71.8398 | N | 12 | N | N | 1.1101 | 39.4971 | 115653.9324
[7 empty] | 14391 | 17857 | 1170875 | 2014-11-03 09:32 | 2014-11-03 12:20 | 168 | 11kV | 1344 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Unselected | N | LID 142730 B phase DOLF : 16 Amp b ph dolf replaced 16amp. single ph subs not affected. only 2x 3ph subs effected Excluded oms 1170875. | November | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-11-03 | N | 168 | N | 5 | N | N | 1.1101 | 39.4971 | 982.1556
[7 empty] | 12782 | 4870 | 1170777 | 2014-11-03 07:57 | 2014-11-03 14:05 | 368 | 11kV | 57829 | 732 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn14143 Somersby Pa17 "Somersby Falls" fdr tripped, reclosed and locked out Relays: B phase IOC and timed overcurrent, earth fault, efi Signals: 11kv trip EFI's Nil Tree brought 11kv mains down adjacent PT13021 Wise Ferry Ulinga 0.4 See 1172737,8 GIS 1170783 Exclude 1170777,9,821,23 | November | 2014 | 2015Q2 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2014-11-03 | N | 79.0014 | N | 5 | N | N | 1.1101 | 39.4971 | 42259.7275
[7 empty] | 13856 | 13734 | 1171229 | 2014-11-03 18:45 | 2014-11-03 19:16 | 31 | 11kV | 4743 | 153 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142736 B phase DOLF : 31 Amp B phase DOLF burnt in half, replaced with new wedge. Readings as left 60A, 90A, 200A @ 239V. Note Report from FIRE & RESCUE NSW - EXPLOSION FROM POLE AND POLE ON FIRE - POLE NO# 755JU33 Wires also reported down Excluded OMS 1171231 | November | 2014 | 2015Q2 | 2015 | 203:8086 | 204:82691 | ZN00204/082691 | NEWCASTLE | OH | Not Veg | 2014-11-03 | N | 31 | N | 5 | N | N | 1.1101 | 39.4971 | 3466.0445
[7 empty] | 14669 | 20273 | 1172774 | 2014-11-03 17:34 | 2014-11-03 19:50 | 136 | 11kV | 2856 | 21 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn12630 Peats Ridge section of Pa4 "Kulnura" btw LB45003 to LB40887. Isolated by Dop for safety. Tree branch on OH Mains | November | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2014-11-03 | N | 136 | N | 5 | N | N | 1.1101 | 39.4971 | 2087.0806
[7 empty] | 12979 | 6634 | 1171253 | 2014-11-03 23:05 | 2014-11-04 02:00 | 175 | 11kV | 133047 | 1416 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Unselected | N | ZN 10990 Arncliffe - Pnl 2 - Trip/reclose/trip, 51BC, lockout, Field EFIs. HV UGOH on pole KO-19018 failed and went short circuit. S 10143 in LV// at the time. ME: 1172690. Rest STeps: 1171256, 1172692. Withdrawn: 1171253. | November | 2014 | 2015Q2 | 2015 | ZN10990:PA2 | ZN10998:PA5 | ZN10998/000005 | BAYSIDE | Unknown | Unknown | 2014-11-03 | N | 93.9597 | N | 5 | N | N | 1.1101 | 39.4971 | 97226.8234
[7 empty] | 12254 | 15 | 1171263 | 2014-11-04 04:45 | 2014-11-04 05:57 | 72 | 11kV | 37110 | 608 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | Zn188 Zetland - pnl 43 tripped on: E/F, EFI/ FC Field EFIs: S545 S35816 S3666 UG cable fault from S3666 (Sw P) tee Tx3 to S2021 Sw A see 1171321 1171317 | November | 2014 | 2015Q2 | 2015 | ZN188:PA43 | ZN188:PA43 | ZN00188/000043 | SYDNEY | UG | Not Veg | 2014-11-04 | N | 61.0362 | N | 4 | N | N | 1.1101 | 39.4971 | 27118.8934
[7 empty] | 13770 | 13078 | 1171467 | 2014-11-04 12:16 | 2014-11-04 14:35 | 139 | 11kV | 2085 | 15 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S7926 Bourke Rd 77 - B phase HV OEFMA 75 Amp fuse blown Suspect transformer failure - restored OK Note: Network left abnormally switched if re-occurence within 24 hours to enable access to HV switch and HV fuses due to RMI type. | November | 2014 | 2015Q2 | 2015 | ZN630:PA32 | ZN630:PA18 | ZN00630/000018 | SYDNEY | UG | Not Veg | 2014-11-04 | N | 139 | N | 4 | N | N | 1.1101 | 39.4971 | 1523.6565
[7 empty] | 13357 | 9767 | 1171485 | 2014-11-04 12:55 | 2014-11-04 15:35 | 160 | 11kV | 160 | 1 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 142749 A & C phase DOLF : 10 Amp Possum Excluded OMS 1171485 | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-11-04 | N | 160 | N | 4 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 14048 | 15406 | 1171324 | 2014-11-04 08:57 | 2014-11-04 16:25 | 448 | 11kV | 3171 | 37 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Section of 11kV feeder Pnl.30 @ Matraville Zn - 11kV bond burnt off on tee to PT1993 PMG Long Bay Section of feeder from CP2552 tee PT1993 (N//) tee PT1238 (N//) interrupted @ 1520 by DOp to allow for emergency repairs. see 1171735 1171736 | November | 2014 | 2015Q2 | 2015 | ZN1788:PA30 | ZN1788:PA44 | ZN01788/000044 | RANDWICK | OH | Not Veg | 2014-11-04 | N | 85.7027 | N | 4 | N | N | 1.1101 | 39.4971 | 2317.2733
[7 empty] | 13919 | 14291 | 1171712 | 2014-11-05 00:53 | 2014-11-05 02:16 | 83 | 11kV | 147544 | 1927 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | @ ZN.2473 North Sydney 11kV Panel 21 feeder tripped on:- Earth Fault, EFI, Fault Check Tx.3 EFI's:- S.8107, S.2296, S.2920, S.4433, S.3343 Cause:- 11kV UG cable fault located between S.3343 SW/B to S.6131 SW/A ME:-1171756 RS:-1171761 Withdrawn:-1171712 | November | 2014 | 2015Q2 | 2015 | ZN2473:PA21 | ZN35400:PA52 | ZN35400/000052 | NORTH SYDNEY | UG | Not Veg | 2014-11-05 | N | 76.5667 | N | 24 | Y | Y | 1.1101 | 39.4971 | 107820.8034
[7 empty] | 14342 | 17492 | 1171713 | 2014-11-05 04:04 | 2014-11-05 05:39 | 95 | 11kV | 68495 | 721 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Unselected | N | @ ZN.36300 Balgowlah North 11kV Panel 17 tripped on:- Relays:- B & C phase IOC Signals:- 11kV trip, EFI EFI's:- S.46665, S.48110, S.62663, S.46775, S.16797, S.17039, S.16320, S.15107, CP.20901 Cause:- Not ascertained Suspect OH adjacent to PT.15524 ME:-1171713 CC1: 22-"Refer to SOp" | November | 2014 | 2015Q2 | 2015 | ZN36300:PA17 | ZN36300:PA17 | ZN36300/000017 | NORTHERN BEACHES | OH | Not Veg | 2014-11-05 | N | 95 | N | 24 | Y | Y | 1.1101 | 39.4971 | 50054.1257
[7 empty] | 13322 | 9450 | 1171818 | 2014-11-05 09:24 | 2014-11-05 10:35 | 71 | 11kV | 71 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142758 B phase DOLF : 10 Amp Excluded OMS 1171818 | November | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2014-11-05 | N | 71 | N | 24 | Y | Y | 1.1101 | 39.4971 | 51.8847
[7 empty] | 13978 | 14746 | 1171833 | 2014-11-05 09:39 | 2014-11-05 11:10 | 91 | 11kV | 91 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | @ PT.16698 Kimbriki Tip No.2 - HDO 20 amp ABB C phase blown Cause:- Fuse fatigue Fuse fatigue HDO C phase D/Op replaced all three fuses with 20 amp ABB's ME:-1173596 Withdrawn:-1171833 | November | 2014 | 2015Q2 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-11-05 | N | 91 | N | 24 | Y | Y | 1.1101 | 39.4971 | 66.5001
[7 empty] | 14488 | 18601 | 1171999 | 2014-11-05 13:06 | 2014-11-05 14:37 | 91 | 11kV | 15857 | 175 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | LID 142760 1 fault operation Earth fault | November | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-11-05 | N | 90.6114 | N | 24 | Y | Y | 1.1101 | 39.4971 | 11587.8279
[7 empty] | 12779 | 4853 | 1172024 | 2014-11-05 13:33 | 2014-11-05 16:35 | 182 | 11kV | 289481 | 2249 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | ZN 9700 Kirrawee - Pnl 17 - SEL, lockout. Tree branch brought down OH adjacent to ABS 35213 on Gymea Bay Road. ME: 1172719. Rest Steps: 1172720, 1. Withdrawn: 1172024. | November | 2014 | 2015Q2 | 2015 | ZN9700:PA17 | ZN9700:PA17 | ZN09700/000017 | SUTHERLAND | OH | Veg | 2014-11-05 | N | 128.7154 | N | 24 | Y | Y | 1.1101 | 39.4971 | 211544.1766
[7 empty] | 13057 | 7240 | 1172240 | 2014-11-05 17:39 | 2014-11-05 18:40 | 61 | 11kV | 1037 | 17 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of Pa4 'Kulnura' PT13825 Peats Ridge Euloo 0.7 HDO 11kv 31.5 Amp ABB Fuse Blown Customer report Lightning hit pole See 1172873 exclude 1172240,55 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-11-05 | N | 61 | N | 24 | Y | Y | 1.1101 | 39.4971 | 757.809
[7 empty] | 12884 | 5864 | 1172257 | 2014-11-05 17:45 | 2014-11-05 18:42 | 57 | 11kV | 59322 | 1077 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142780 1 fault operation A & B phase Overcurrent: Esarth fault | November | 2014 | 2015Q2 | 2015 | 503:48077 | 532:83295 | ZN00532/083295 | MAITLAND | OH | Veg | 2014-11-05 | N | 55.0808 | N | 24 | Y | Y | 1.1101 | 39.4971 | 43350.7679
[7 empty] | 13753 | 12924 | 1172299 | 2014-11-05 18:17 | 2014-11-05 19:10 | 53 | 11kV | 1060 | 20 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Rain Heavy | N | Ex Zn12600 Lisarow section of Pa1 PT12631 Teralba Wallarah 11kv 20A roadside & Middle Phase fuse blown Tree branch contact OH See 1172900 exclude 1172299 | November | 2014 | 2015Q2 | 2015 | ZN12600:PA1 | ZN12600:PA1 | ZN12600/000001 | CENTRAL COAST | OH | Veg | 2014-11-05 | N | 53 | N | 24 | Y | Y | 1.1101 | 39.4971 | 774.6167
[7 empty] | 13530 | 11119 | 1172162 | 2014-11-05 16:36 | 2014-11-05 19:10 | 154.45 | 11kV | 3861.25 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142794 B Phase DOLF : 10 Amp | November | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-11-05 | N | 154.45 | N | 24 | Y | Y | 1.1101 | 39.4971 | 2821.6876
[7 empty] | 13709 | 12613 | 1172219 | 2014-11-05 16:54 | 2014-11-05 19:20 | 146 | 11kV | 1168 | 8 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge Zone section of Pa1 PT11535 Mangrove Dam 2.1 11kv 10Amp footpath side fuse blown. Lightning in area. Weather related See 1172869 exclude 1172177,219 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-11-05 | N | 146 | N | 24 | Y | Y | 1.1101 | 39.4971 | 853.5399
[7 empty] | 12744 | 4583 | 1172255 | 2014-11-05 17:54 | 2014-11-05 20:10 | 136 | 11kV | 1768 | 13 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge section of pa4 PT18735 Geo Down Nurses 0.25 11kv 16K footpath side fuse blown Lightning in Area See 1172879 GIS 1172288 exclude 1172255 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-11-05 | N | 136 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1292.0023
[7 empty] | 12312 | 548 | 1172155 | 2014-11-05 16:25 | 2014-11-05 20:45 | 260 | 11kV | 87150 | 1365 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 142770 Earth fault Sw 80785 - 51N (Inst E/F), 50TN (Timed E/F) 11kV mains down Tillie St Wallsend. Excluded OMS 1172155 | November | 2014 | 2015Q2 | 2015 | 258:80785 | 258:80785 | ZN00258/080785 | NEWCASTLE | OH | Not Veg | 2014-11-05 | N | 63.8462 | N | 24 | Y | Y | 1.1101 | 39.4971 | 63686.6495
[7 empty] | 12603 | 3235 | 1172402 | 2014-11-05 19:28 | 2014-11-05 21:00 | 92 | 11kV | 184 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142781 C phase DOLF : 10 Amp Excluded OMS 1172402 | November | 2014 | 2015Q2 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-11-05 | N | 92 | N | 24 | Y | Y | 1.1101 | 39.4971 | 134.4618
[7 empty] | 12294 | 373 | 1172283 | 2014-11-05 18:07 | 2014-11-05 21:50 | 223 | 11kV | 2007 | 9 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 142785 A phase DOLF : 30 Amp sub interconnected. Suspect faulty TX Excluded oms1172283. | November | 2014 | 2015Q2 | 2015 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Not Veg | 2014-11-05 | N | 223 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1466.6564
[7 empty] | 12520 | 2479 | 1172278 | 2014-11-05 17:58 | 2014-11-05 22:15 | 257 | 11kV | 67058 | 521 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 142779 faulty arrestor at sub 50011.arrestor mounted on line side of DOLF. WIRING MODIFIED. Excluded oms 1172278. | November | 2014 | 2015Q2 | 2015 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2014-11-05 | N | 128.7102 | N | 24 | Y | Y | 1.1101 | 39.4971 | 49004.0085
[7 empty] | 12507 | 2319 | 1172277 | 2014-11-05 18:03 | 2014-11-05 23:00 | 297.0333 | 11kV | 13663.5333 | 46 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142786 C phase DOLF : 20 Amp Excluded OMS 1172403 & 1172433 | November | 2014 | 2015Q2 | 2015 | 205:12213 | 205:12213 | ZN00205/012213 | NEWCASTLE | OH | Veg | 2014-11-05 | N | 297.0333 | N | 24 | Y | Y | 1.1101 | 39.4971 | 9984.9072
[7 empty] | 12736 | 4528 | 1172466 | 2014-11-05 22:54 | 2014-11-05 23:40 | 46 | 11kV | 2990 | 65 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | Unselected | N | Section of ZN.15012 Killarney Zone 11kV Panel 8 - F.21577 to PT.15429 Mavor Ave footpath and centre phase HDO's blown Cause:- Flying fox came into contact with 11kV mains, bucket required to be used to replace HDO's Restored by LV// ME:-1172465 1 Withdrawn:-1172468, 1172466 | November | 2014 | 2015Q2 | 2015 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | OH | Not Veg | 2014-11-05 | N | 46 | N | 24 | Y | Y | 1.1101 | 39.4971 | 2185.0038
[7 empty] | 14255 | 16937 | 1172172 | 2014-11-05 16:44 | 2014-11-06 00:20 | 456 | 11kV | 101542 | 1182 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | LID 142791 2 fault operations Earth fault faulty u/g cable at UGOH pole KT-70080. Excluded oms report no 1172329. | November | 2014 | 2015Q2 | 2015 | 228:7490 | 228:85413 | ZN00228/085413 | PORT STEPHENS | Unknown | Unknown | 2014-11-05 | N | 85.9069 | N | 24 | Y | Y | 1.1101 | 39.4971 | 74203.8986
[7 empty] | 13707 | 12594 | 1172474 | 2014-11-06 00:25 | 2014-11-06 01:45 | 80 | 11kV | 15920 | 199 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 142795 ISOLATE FOR CLEARANCE TO REPAIR 33KV FAULT Excluded OMS 1172474/5/6. | November | 2014 | 2015Q2 | 2015 | 220:8692 | 220:8692 | ZN00220/008692 | LAKE MACQUARIE | OH | Not Veg | 2014-11-06 | N | 80 | N | 11 | N | N | 1.1101 | 39.4971 | 11633.8664
[7 empty] | 12846 | 5523 | 1172249 | 2014-11-05 17:48 | 2014-11-06 03:10 | 561.8167 | 11kV | 26967.2 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 142800 3 Phase DOLF : 40 Amp Crews could not find any damage when patrolling during the evening. | November | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-11-05 | N | 561.8167 | N | 24 | Y | Y | 1.1101 | 39.4971 | 19706.8344
[7 empty] | 14671 | 20287 | 1172478 | 2014-11-06 01:47 | 2014-11-06 03:50 | 123 | 11kV | 246 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142807 A phase DOLF : 10 Amp Excluded OMS 1172478 | November | 2014 | 2015Q2 | 2015 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Veg | 2014-11-06 | N | 123 | N | 11 | N | N | 1.1101 | 39.4971 | 179.7695
[7 empty] | 12514 | 2390 | 1172497 | 2014-11-06 06:30 | 2014-11-06 08:25 | 115 | 11kV | 345 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Previous Storm | N | LID 142808 A & B phase DOLF : 16 Amp Branch on Fdr near sub 12059 removed by operator Excluded 1172497 | November | 2014 | 2015Q2 | 2015 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Veg | 2014-11-06 | N | 115 | N | 11 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 12635 | 3540 | 1172408 | 2014-11-05 19:00 | 2014-11-06 08:32 | 812 | 11kV | 2436 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 142809 C phase DOLF : 10 Amp Excluded OMS 1172494 | November | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-11-05 | N | 812 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1780.157
[7 empty] | 12697 | 4126 | 1172525 | 2014-11-06 07:50 | 2014-11-06 10:45 | 175 | 11kV | 175 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 142825 A phase dolf : 5 Amp Excluded OMS 1172525 BLOWN ARRESTOR - - REPLACING ARRESTOR | November | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-11-06 | N | 175 | N | 11 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 13740 | 12835 | 1172644 | 2014-11-06 11:30 | 2014-11-06 11:47 | 17 | 11kV | 34 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 142824 C phase DOLF : 16 Amp Excluded OMS 1172644 | November | 2014 | 2015Q2 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Not Veg | 2014-11-06 | N | 17 | N | 11 | N | N | 1.1101 | 39.4971 | 24.8462
[7 empty] | 13895 | 14096 | 1172276 | 2014-11-05 17:41 | 2014-11-06 12:00 | 1099 | 33kV Distribution | 5302 | 18 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 142789 1 fault operation A phase Earth fault Pole replaced. Note: 33kV mains also reported to be down and on the cross arm near sub 9715 A A TO E - MULTI B 51N - MULTI Excluded OMS OMS1172256. | November | 2014 | 2015Q2 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2014-11-05 | N | 294.5556 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3874.5452
[7 empty] | 14327 | 17363 | 1172254 | 2014-11-05 17:39 | 2014-11-06 12:00 | 1101 | 33kV Distribution | 4454 | 22 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Electrical Storm | N | LID 142787 1 fault operation 3 phase Earth fault Sw 80500 A ABC E - MULTI B 51 ABC 33kV Mains on cross arm near Sub 9715 | November | 2014 | 2015Q2 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2014-11-05 | N | 202.4545 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3254.8518
[7 empty] | 12556 | 2859 | 1172484 | 2014-11-06 10:00 | 2014-11-06 14:30 | 270 | 11kV | 1620 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Previous Storm | N | LID 142818 3 phase DOLF : 20 Amp HV reported down ewxcluded OMS 1172597 | November | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-11-06 | N | 270 | N | 11 | N | N | 1.1101 | 39.4971 | 1183.8482
[7 empty] | 12365 | 1033 | 1172165 | 2014-11-05 16:46 | 2014-11-06 14:35 | 1309 | 11kV | 27624 | 59 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 142799 4 fault operations Earth fault; Overcurrent Cable on ground at pole 6M-60006. Blown surge arestor at sub 71400. Excluded OMS 1172168 AND 1172199. | November | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-11-05 | N | 468.2034 | N | 24 | Y | Y | 1.1101 | 39.4971 | 20186.8044
[7 empty] | 12560 | 2933 | 1172132 | 2014-11-06 16:10 | 2014-11-06 19:01 | 171 | 11kV | 513 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142790 Single phase DOLF : 10 Amp Excluded OMS 1172132 | November | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-11-06 | N | 171 | N | 11 | N | N | 1.1101 | 39.4971 | 374.8853
[7 empty] | 12448 | 1780 | 1172364 | 2014-11-06 18:59 | 2014-11-06 22:20 | 201 | 11kV | 201 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142793 DOLF : 10 Amp Excluded OMS 1172364 | November | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-11-06 | N | 201 | N | 11 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 12532 | 2569 | 1172230 | 2014-11-06 17:36 | 2014-11-06 22:30 | 294 | 11kV | 882 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Electrical Storm | N | LID 142796 DOLF : 10 Amp Excluded OMS 1172230 | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-11-06 | N | 294 | N | 11 | N | N | 1.1101 | 39.4971 | 644.5396
[7 empty] | 13174 | 8151 | 1172961 | 2014-11-06 23:58 | 2014-11-07 04:55 | 297 | 11kV | 46084 | 668 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Zn14144 Wamberal Pa10 "Willoughby Central Coast" Fdr tripped, reclosed and tripped on: Relays: TImed overcurrent A & B Phases, reclsoer time and lock out and EFI Signals: Tx2 Group Earth EFI's: Nil Tree/branch brought down 11kv OH near LB45192 See 1173196,7,8,9 excluded 1172961 | November | 2014 | 2015Q2 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Veg | 2014-11-06 | N | 68.988 | N | 11 | N | N | 1.1101 | 39.4971 | 33676.828
[7 empty] | 14051 | 15428 | 1172967 | 2014-11-07 03:41 | 2014-11-07 05:10 | 89 | 11kV | 379251 | 4679 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Unselected | N | ZN.15006 Dee Why West 11kV Feeder Panel 12 tripped on:- Relays:- Timed OC, Fault Check, Earth Leakage, Fault Check Tx.1 & 3 Signals:- Zone Earth and 11kV trip Abnormal Switching:- S.17046 SW/B Closed, S.16027 SW/A Open - OOS @ ZN.15001 Brookvale Zone from CP.22558 to CP.24223 to S.16027 SW/A (See SAO #348771) Cause:- UG cable fault from S.15108 SW/B to S.16321 SW/A ME:-1173695 RS:-1173697 Withdrawn:-1172967 | November | 2014 | 2015Q2 | 2015 | ZN15006:PA12 | ZN15006:PA12 | ZN15006/000012 | NORTHERN BEACHES | UG | Not Veg | 2014-11-07 | N | 81.0539 | N | 5 | N | N | 1.1101 | 39.4971 | 277145.4448
[7 empty] | 14424 | 18106 | 1173166 | 2014-11-07 12:15 | 2014-11-07 14:30 | 135 | 11kV | 14040 | 104 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Unselected | N | LID 142837 3 phase car hit pole hr-92037 Excluded oms 1173166,1173167,1173168 | November | 2014 | 2015Q2 | 2015 | 503:48011 | 532:83309 | ZN00532/083309 | MAITLAND | OH | Not Veg | 2014-11-07 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 10260.0179
[7 empty] | 13814 | 13364 | 1173279 | 2014-11-07 08:36 | 2014-11-07 20:00 | 684 | 11kV | 684 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142841 BROKEN L/L LEAD AT SUB 53470. Excluded OMS REPORT NO 1173309. | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-07 | N | 684 | N | 5 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 14643 | 20106 | 1173116 | 2014-11-07 12:30 | 2014-11-07 20:00 | 450 | 11kV | 450 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 142840 B & C phase DOLF : 10 Amp FAULTY ARRESTORS AT SUB 25559. Excluded OMS REPORT NO 1173171. | November | 2014 | 2015Q2 | 2015 |  |  |  |  | OH | Not Veg | 2014-11-07 | N | 450 | N | 5 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 12539 | 2693 | 1173745 | 2014-11-07 22:00 | 2014-11-08 00:40 | 160 | 11kV | 800 | 5 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 142845 Pole BM 30002 blown insulators tracking caused grass fire fdr isolated for repairs | November | 2014 | 2015Q2 | 2015 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2014-11-07 | N | 160 | N | 5 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 13762 | 12995 | 1173333 | 2014-11-08 05:19 | 2014-11-08 07:20 | 121 | 11kV | 41624 | 344 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | Ex ZN 10999 Kogarah - Pnl 38 - AB 31088 Footpath HV bond went open circuit at AB 31088. ME: 1173710. Withdrawn: 1173333. | November | 2014 | 2015Q2 | 2015 | ZN10999:PA38 | ZN10997:PA7 | ZN10997/000007 | BAYSIDE | OH | Not Veg | 2014-11-08 | N | 121 | N | 4 | N | N | 1.1101 | 39.4971 | 30417.5915
[7 empty] | 12727 | 4437 | 1173340 | 2014-11-08 06:38 | 2014-11-08 07:55 | 77 | 11kV | 308 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142846 C phase DOLF : 10 Amp HV FUSE CARRIER BURNT IN HALF. Excluded OMS REPORT NO 1173340. | November | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-11-08 | N | 77 | N | 4 | N | N | 1.1101 | 39.4971 | 225.0773
[7 empty] | 14509 | 18785 | 1173376 | 2014-11-08 10:02 | 2014-11-08 11:45 | 103 | 11kV | 412 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142850 C phase DOLF : 10 Amp Excluded OMS 1173376 | November | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-11-08 | N | 103 | N | 4 | N | N | 1.1101 | 39.4971 | 301.0774
[7 empty] | 14216 | 16630 | 1173437 | 2014-11-08 17:00 | 2014-11-08 18:45 | 105 | 11kV | 2205 | 21 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 142851 1 fault operation A phase Aph Fusesaver @ LF 63353 tripped & locked out. Customer reported seeing bird hit OHM near sub 53276 @ approx. 1700hrs. Excluded OMS No. 1173437 | November | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | MUSWELLBROOK | OH | Not Veg | 2014-11-08 | N | 105 | N | 4 | N | N | 1.1101 | 39.4971 | 1611.349
[7 empty] | 14057 | 15453 | 1173476 | 2014-11-09 06:58 | 2014-11-09 09:15 | 137 | 11kV | 1096 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge Hensons Hoipos 0.5 A pHase HDO replaced ABB 16K Batch 1001 Fust Fatigue See 1173801 Exclude 1173476 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2014-11-09 | N | 137 | N | 3 | N | N | 1.1101 | 39.4971 | 800.9245
[7 empty] | 13766 | 13034 | 1173512 | 2014-11-09 11:20 | 2014-11-09 12:35 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142856 Single phse DOLF : 10 Amp Excluded OMS 1173512 | November | 2014 | 2015Q2 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2014-11-09 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 13382 | 9977 | 1173562 | 2014-11-09 18:27 | 2014-11-09 18:50 | 23 | 11kV | 23 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142857 C phase DOLF : 10 Amp TX Volts: 240V Excluded OMS No. 1173562 | November | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-11-09 | N | 23 | N | 3 | N | N | 1.1101 | 39.4971 | 16.8077
[7 empty] | 12600 | 3219 | 1173606 | 2014-11-10 07:53 | 2014-11-10 08:29 | 36.2333 | 11kV | 16957.2 | 468 | HV | Animal Bird | Animal | O/H Conductor Bare | Unplanned | Unselected | N | LID 142860 2 fault operations C phase Overcurrent dead galahs found at pole AK-60505. | November | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-11-10 | N | 36.2333 | N | 2 | N | N | 1.1101 | 39.4971 | 12391.8216
[7 empty] | 12565 | 2974 | 1173945 | 2014-11-10 18:16 | 2014-11-10 18:22 | 6 | 11kV | 8772 | 1462 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | @ ZN.15011 Beacon Hill Panel 10L feeder tripped on:- SEL Cause:- Protection Malfunction SEL Panel 10L tripped instantly when D/Op made auto ME:-1173945 | November | 2014 | 2015Q2 | 2015 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-11-10 | N | 6 | N | 2 | N | N | 1.1101 | 39.4971 | 6410.3189
[7 empty] | 12549 | 2815 | 1174098 | 2014-11-11 11:51 | 2014-11-11 14:53 | 182 | 11kV | 27846 | 153 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Unselected | N | LID 142886 2 fault operations C phase Overcurrent wire off pin | November | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-11-11 | N | 182 | N | 3 | N | N | 1.1101 | 39.4971 | 20349.0355
[7 empty] | 12590 | 3163 | 1174124 | 2014-11-11 12:57 | 2014-11-11 15:25 | 148 | 11kV | 444 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | HV Fuse replaced - also refer to OMS 1174124 No further information received | November | 2014 | 2015Q2 | 2015 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Not Veg | 2014-11-11 | N | 148 | N | 3 | N | N | 1.1101 | 39.4971 | 324.4621
[7 empty] | 12966 | 6543 | 1174132 | 2014-11-11 13:10 | 2014-11-11 16:30 | 200 | 11kV | 9705 | 56 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Section of ZN.2400 Berowra Zone from RE.1238 Milsons Passage to the extent of the feeder (4DC's) RE.1238 tripped on:- Relays:- Trip and reclose tripped off: V max 323 amp & U max 324 amp locked out aux supply fail Signals:- See WSOS log for recloser Cause:- Tree/branch on OH mains at Milsons Passage ME:-1174316 RS:-1174317 Withdrawn:-1174198, 1174142, 1174126,1174132 | November | 2014 | 2015Q2 | 2015 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2014-11-11 | N | 173.3036 | N | 3 | N | N | 1.1101 | 39.4971 | 7092.1278
[7 empty] | 12548 | 2813 | 1174302 | 2014-11-12 02:31 | 2014-11-12 07:05 | 273.55 | 11kV | 547.1 | 2 | HV | Animal Possum | Animal | DC PT | Unplanned | Unselected | N | LID 142888 Single phase DOLF : 3 Amp Dead Possum found at sub. Tx volts: 240V; Tx load: 40A Excluded OMS No. 1174304 | November | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2014-11-12 | N | 273.55 | N | 4 | N | N | 1.1101 | 39.4971 | 399.8045
[7 empty] | 14242 | 16858 | 1172789 | 2014-11-06 13:04 | 2014-11-12 13:49 | 8684.6 | 11kV | 8684.6 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 142829 transformer change Excluded OMS 1173232; 1173870 | November | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2014-11-06 | N | 8684.6 | N | 11 | N | N | 1.1101 | 39.4971 | 6346.4495
[7 empty] | 14353 | 17580 | 1174494 | 2014-11-12 12:18 | 2014-11-12 14:22 | 124 | 11kV | 372 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142898 A phase DOLF : 16 Amp Replaced Carrier Excluded OMS : 1174494 | November | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-11-12 | N | 124 | N | 4 | N | N | 1.1101 | 39.4971 | 271.8466
[7 empty] | 13901 | 14156 | 1174211 | 2014-11-12 09:08 | 2014-11-12 16:30 | 442 | 11kV | 70720 | 160 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | Unselected | N | S3160 Llewellyn Enmore - Customers experiencing low volts - no devices operated - Placed in LV // for subs to test Note: tap changer maintenance took place on 7/11/14 D/R #348056 Abnormal: Dist #2 OOS from 10/11/14 OMS #1174731 and in LV // suspected transformer tap changer defect Note: calls received from 11/11/14 15:22 advising Low Volts, device opened as above control room report at 12/11/14 09:08 CC1: 22-"Refer to SOp" | November | 2014 | 2015Q2 | 2015 | ZN2568:PA9 | ZN2568:PA9 | ZN02568/000009 | INNER WEST | UG | Not Veg | 2014-11-12 | N | 442 | N | 4 | N | N | 1.1101 | 39.4971 | 51680.0901
[7 empty] | 12545 | 2716 | 1174647 | 2014-11-12 21:02 | 2014-11-12 21:56 | 54 | 11kV | 34020 | 630 | HV | Animal Possum | Animal | UGOH | Unplanned | Unselected | N | ZN 9037 Miranda - Pnl 7 - C phase IOC, sealing contactor, EFI. Possum located underneath UGOH near PT 9639. Mains to inspect for damage. ME: 1174647. ME GIS: 1174648. Withdrawn: 1174655. | November | 2014 | 2015Q2 | 2015 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2014-11-12 | N | 54 | N | 4 | N | N | 1.1101 | 39.4971 | 24860.8126
[7 empty] | 13027 | 6997 | 1174761 | 2014-11-13 10:42 | 2014-11-13 12:10 | 88.1667 | 11kV | 79879 | 906 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | @ ZN.80 Chatswood Zone 11kV Feeder Panel 25 tripped on:- Relays: SEF Signals:- 11kV Trip EFI's:- NIL Cause:- Not ascertained Mains to patrol ME:-1174761 | November | 2014 | 2015Q2 | 2015 | ZN80:PA25 | ZN80:PA25 | ZN00080/000025 | LANE COVE | UG | Not Veg | 2014-11-13 | N | 88.1667 | N | 2 | N | N | 1.1101 | 39.4971 | 58373.2172
[7 empty] | 14556 | 19131 | 1174752 | 2014-11-13 10:22 | 2014-11-13 12:15 | 113 | 11kV | 79528 | 911 | HV | 3rd Party Action | 3rd Party Impact | U/G Cable | Unplanned | Unselected | N | @ ZN.965 Pennant Hills 11kV Feeder Panel 35 tripped on:- Relays:- IOC A and C phase Signals:- 11kV Trip EFI's:- S.4442, S.4558, S.7867, S.4962, Austral Av Cause:- UG cable damaged by contractor outside 21 Orchard Rd, Beecroft ME:-1174957 RS:-1174958, 1174959, 1174960 Withdrawn:-1174752 | November | 2014 | 2015Q2 | 2015 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | UG | Not Veg | 2014-11-13 | N | 87.2975 | N | 2 | N | N | 1.1101 | 39.4971 | 58116.7167
[7 empty] | 14283 | 17110 | 1175125 | 2014-11-14 11:57 | 2014-11-14 14:55 | 178 | 11kV | 356 | 2 | HV | Overload | Utility Process Issue | DC Transformer | Unplanned | Unselected | N | Ex 11kv Panel No.17 "sub 8103 Derby Suttor No.3" feeder from Zn 167 Auburn @ Sub 8103 Derby Suttor No.3 - 11kv RMCB tripped Remarks: Overload. Tx overload | November | 2014 | 2015Q2 | 2015 | ZN167:PA17 | ZN167:PA17 | ZN00167/000017 | PARRAMATTA | UG | Not Veg | 2014-11-14 | N | 178 | N | 6 | N | N | 1.1101 | 39.4971 | 260.1543
[7 empty] | 12997 | 6811 | 1175171 | 2014-11-14 13:48 | 2014-11-14 15:52 | 124 | 11kV | 103925 | 1010 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | @Zn35900 Potts Hill - 11kv Panel No.4L "Sub 4379 Dasea Rook" tripped, recosed & locked out. Relays: A+B+C phase timed O/C, IOC, Earth fault, EFI Signals: 11kv trip, No.1 Group earth Fields EFI's: Sub 4379, Sub 62691, S4412, S4415 Remarks: UGOH fault short circuit. Fault on 11kv UGOH to sub 1222 Palomar Pde Related jobs: #1175256, 1175233, 1175211, 1175171, 1176106, 1176105 | November | 2014 | 2015Q2 | 2015 | ZN35900:PA4 | ZN35900:PA4 | ZN35900/000004 | CANTERBURY-BANKSTOWN | Unknown | Unknown | 2014-11-14 | N | 102.896 | N | 6 | N | N | 1.1101 | 39.4971 | 75945.3247
[7 empty] | 12555 | 2858 | 1175255 | 2014-11-14 16:19 | 2014-11-14 17:25 | 65.8667 | 11kV | 5137.6 | 78 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Hot >35C | N | LID 142916 B Phase DOLF : 40 Amp 240 volts 98, 58, 76 amps | November | 2014 | 2015Q2 | 2015 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2014-11-14 | N | 65.8667 | N | 6 | N | N | 1.1101 | 39.4971 | 3754.4065
[7 empty] | 14065 | 15531 | 1175128 | 2014-11-14 13:47 | 2014-11-14 17:34 | 227 | 11kV | 8399 | 37 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | @PT11702 Goorama Taronga HDO Fuse carrier assembly fell apart. Heatwave See 1176035 exclude 11750128 | November | 2014 | 2015Q2 | 2015 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2014-11-14 | N | 227 | N | 6 | N | N | 1.1101 | 39.4971 | 6137.7415
[7 empty] | 13099 | 7646 | 1175232 | 2014-11-14 15:22 | 2014-11-14 20:25 | 303 | 11kV | 909 | 3 | HV | Overload | Utility Process Issue | Feeder/Distributor U/G | Unplanned | Hot >35C | N | Ex Panel No.41 "sub 1616 Manson Rd" from Zn 2835 Burwood @Sub 4100 Beresford Coventry - 11kv B phase 80 Amp OQFRN fuse operated Remarks: overload | November | 2014 | 2015Q2 | 2015 | ZN2835:PA31 | ZN2835:PA31 | ZN02835/000031 | STRATHFIELD | UG | Not Veg | 2014-11-14 | N | 303 | N | 6 | N | N | 1.1101 | 39.4971 | 664.2704
[7 empty] | 12570 | 3021 | 1175353 | 2014-11-14 21:46 | 2014-11-14 23:52 | 126 | 11kV | 33096 | 893 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Wind | N | Zn12690 Berkely Vale Pa24 "Burns Rd" tripped and locked out on: Relays: A+C Phase overcurrent right hand leg, EFI Signals: 11kv trip Damaged UGOH to S11984:B WSC Footes See 1176095,6,7,8 Exclude 1175353 | November | 2014 | 2015Q2 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | Unknown | Unknown | 2014-11-14 | N | 37.0616 | N | 6 | N | N | 1.1101 | 39.4971 | 24185.5806
[7 empty] | 12346 | 847 | 1175457 | 2014-11-15 13:10 | 2014-11-15 13:40 | 30 | 11kV | 90 | 3 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Unselected | N | LID 142921 Stay wire found laying on trans & LAs. Excluded OMS# 1175457. | November | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-11-15 | N | 30 | N | 2 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 13325 | 9487 | 1175439 | 2014-11-15 10:52 | 2014-11-15 14:52 | 240 | 11kV | 1200 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | PT18473 Yarramalong Stinson 0.7 16Amp B phase HDO blown Cause not ascertained See 1176123 exclude 1175439 | November | 2014 | 2015Q2 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2014-11-15 | N | 240 | N | 2 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 13332 | 9594 | 1175519 | 2014-11-16 03:40 | 2014-11-16 10:40 | 420 | 11kV | 35188 | 239 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Unselected | N | Ex Zn12630 Peats Ridge section of Pa5 IR61082 Brieses Peats Ridge 0.3 tripped and locked out on overcurrent 2 spans mains down between LK44100 to PT14029 See 1176129,30,1,2 Exclude 1175519 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Veg | 2014-11-16 | N | 147.2301 | N | 5 | N | N | 1.1101 | 39.4971 | 25714.3525
[7 empty] | 12380 | 1194 | 1175719 | 2014-11-16 15:31 | 2014-11-16 17:00 | 89 | 11kV | 48149 | 541 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind | N | Ex Zn14143 Somersby section of Pa17 "Somserbsy Falls" RE48437 Peats Ridge Cooks 1.35 tripped and locked out on overucrrent DOp patrolled, nothing found See 1175719 exclude 1175733 | November | 2014 | 2015Q2 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2014-11-16 | N | 89 | N | 5 | N | N | 1.1101 | 39.4971 | 35185.869
[7 empty] | 14500 | 18688 | 1175748 | 2014-11-16 13:15 | 2014-11-16 18:35 | 320 | 11kV | 30400 | 95 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Unselected | N | LID 142927 Single phase Burnt off tapping to sub 3814 & 50943. No Protection Op Excluded OMS # 1175623 & 1175748 | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-11-16 | N | 320 | N | 5 | N | N | 1.1101 | 39.4971 | 22215.4234
[7 empty] | 14253 | 16917 | 1175674 | 2014-11-16 14:28 | 2014-11-16 20:40 | 372 | 11kV | 13716 | 119 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Wind | N | LID 142924 1 fault operation 11kV tapping burnt off pole GW-60255 11kV OHM down by tree at pole GW-30310. FIRE STARTED | November | 2014 | 2015Q2 | 2015 | 227:13019 | 227:13019 | ZN00227/013019 | LAKE MACQUARIE | OH | Veg | 2014-11-16 | N | 115.2605 | N | 5 | N | N | 1.1101 | 39.4971 | 10023.2482
[7 empty] | 14182 | 16356 | 1175786 | 2014-11-16 20:45 | 2014-11-16 22:15 | 90 | 11kV | 47998 | 1154 | HV | Animal Possum | Animal | Insulator | Unplanned | Wind | N | LID 142930 3 phase Overcurrent Blown skirts UGOH JU-61607. Perpairs required monday Excluded 1175786, 1175789, 1175790 & 1175792 | November | 2014 | 2015Q2 | 2015 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2014-11-16 | N | 41.5927 | N | 5 | N | N | 1.1101 | 39.4971 | 35075.5227
[7 empty] | 14049 | 15408 | 1176024 | 2014-11-17 13:00 | 2014-11-17 14:30 | 90 | 11kV | 2340 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142938 A phase DOLF : 31 Amp FUSE FATIGUE.SUPPLY CHECKED AT CUSTOMER PREMISES. Excluded OMS REPORT NO 1176024 & 1176027. | November | 2014 | 2015Q2 | 2015 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Veg | 2014-11-17 | N | 90 | N | 1 | N | N | 1.1101 | 39.4971 | 1710.003
[7 empty] | 13754 | 12926 | 1176212 | 2014-11-18 04:12 | 2014-11-18 08:30 | 258 | 11kV | 15996 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | Ex Zn14892 Charmhaven section of Pa16 "charmhaven san remo" PT12592 Iluka Lamenda footpath HVDO operated 31.5k Possible fuse fatigue See 1176710 exclude 1176212,46 | November | 2014 | 2015Q2 | 2015 | ZN14892:PA16 | ZN14892:PA16 | ZN14892/000016 | CENTRAL COAST | OH | Not Veg | 2014-11-18 | N | 258 | N | 3 | N | N | 1.1101 | 39.4971 | 11689.405
[7 empty] | 12340 | 821 | 1176256 | 2014-11-18 08:49 | 2014-11-18 11:25 | 156 | 11kV | 312 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC PT | Unplanned | Unselected | N | LID 142952 B phase DOLF : 10 Amp Excluded OMS 1176256 | November | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-11-18 | N | 156 | N | 3 | N | N | 1.1101 | 39.4971 | 228.0004
[7 empty] | 14378 | 17751 | 1176222 | 2014-11-18 07:32 | 2014-11-18 11:48 | 256.1667 | 11kV | 1496.7167 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Unselected | N | LID 142946 C phase DOLF : 10 Amp Suspect fuse fatigue. TX volts: Aph - 238V, Bph - 240V, Cph - 242V Tx Load: Aph - 45A, Bph - 1A, Cph - 1A Excluded OMS No. 1176235 & 1176259 CC1: 22-"Refer to SOp" CC2: 22-"Refer to SOp" FRC1: 300-"Specify details by voice" FRC2: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" | November | 2014 | 2015Q2 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2014-11-18 | N | 249.4528 | N | 3 | N | N | 1.1101 | 39.4971 | 1093.7564
[7 empty] | 13932 | 14443 | 1176890 | 2014-11-19 15:22 | 2014-11-19 16:47 | 85 | 11kV | 76186 | 1417 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 142962 3 fault operations Earth fault EFI at sub 56340 did not work. faulty cable in section 24828/24256/56339 Excluded OMS 1176890 | November | 2014 | 2015Q2 | 2015 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | UG | Not Veg | 2014-11-19 | N | 53.7657 | N | 3 | N | N | 1.1101 | 39.4971 | 55674.4817
[7 empty] | 14100 | 15801 | 1176901 | 2014-11-19 15:33 | 2014-11-19 17:30 | 117 | 11kV | 3861 | 33 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Panel 2 IR44316 Wisemans Ferry tripped on SEF DOps patrolled but could not find a cause | November | 2014 | 2015Q2 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2014-11-19 | N | 117 | N | 3 | N | N | 1.1101 | 39.4971 | 2821.5049
[7 empty] | 13937 | 14478 | 1177115 | 2014-11-19 17:09 | 2014-11-19 17:30 | 21 | 11kV | 3047 | 2015 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 142963 1 fault operation EFI did not work at sub 56340. Fdr closed on to fault during restoration | November | 2014 | 2015Q2 | 2015 | 261:81882 | 261:81882 | ZN00261/081882 | LAKE MACQUARIE | UG | Not Veg | 2014-11-19 | N | 1.5122 | N | 3 | N | N | 1.1101 | 39.4971 | 2226.6577
[7 empty] | 13576 | 11511 | 1177016 | 2014-11-20 03:20 | 2014-11-20 05:21 | 121 | 11kV | 78434 | 837 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn1788 Matraville Panel 7 tripped on: C phase O/C, EFI Field EFIs: NIL Abnormal: Defective 11kV feeder from S35266 (Sw B) to S35267 (Sw A) - SS7853 (Sw A) CLOSED - 15/10/14 11kV feeder fault from Matraville Zn P7 to S667 (Sw A) to S47763 (Sw B) to S7853 (Sw B) | November | 2014 | 2015Q2 | 2015 | ZN1788:PA1 | ZN1788:PA42 | ZN01788/000042 | RANDWICK | UG | Not Veg | 2014-11-20 | N | 93.7085 | N | 4 | N | N | 1.1101 | 39.4971 | 57317.2538
[7 empty] | 13566 | 11440 | 1177142 | 2014-11-20 11:15 | 2014-11-20 11:25 | 10 | 11kV | 1370 | 137 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Electrical Storm | N | LID 142980 CB did not trip Note parts of ABS fell to ground small grass fire reported. Excluded OMS 1177102 and 1177142. | November | 2014 | 2015Q2 | 2015 | 238:34144 | 238:34144 | ZN00238/034144 | MAITLAND | OH | Not Veg | 2014-11-20 | N | 10 | N | 4 | N | N | 1.1101 | 39.4971 | 1001.1556
[7 empty] | 14170 | 16273 | 1177197 | 2014-11-20 13:24 | 2014-11-20 18:10 | 286 | 11kV | 572 | 2 | HV | Vandalism | 3rd Party Impact | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 142982 Sub Isolated to replace stolen earths | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-11-20 | N | 286 | N | 4 | N | N | 1.1101 | 39.4971 | 418.0007
[7 empty] | 12887 | 5899 | 1177348 | 2014-11-20 23:54 | 2014-11-21 08:50 | 536 | 11kV | 190268 | 1034 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | ZN 9037 Miranda - Pnl 2 - Trip/reclose/trip, B & C phase OC, timing, lockout, EFI, Field EFIs. 11kV OH into LV mains in Kangaroo Point Rd. Possibly caused by Flying contact fault. ME: 1181100. Rest Steps: 1181102, 3, 4. Withdrawn: 1177348, 50. | November | 2014 | 2015Q2 | 2015 | ZN9037:PA2 | ZN9037:PA2 | ZN09037/000002 | SUTHERLAND | OH | Not Veg | 2014-11-20 | N | 184.0116 | N | 4 | N | N | 1.1101 | 39.4971 | 139042.2424
[7 empty] | 12406 | 1468 | 1177356 | 2014-11-21 06:21 | 2014-11-21 13:50 | 449 | 11kV | 449 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | Hot >35C | N | LID 142987 LL Clamp burnt off - sub isolated for repairs | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2014-11-21 | N | 449 | N | 5 | N | N | 1.1101 | 39.4971 | 328.116
[7 empty] | 13345 | 9714 | 1177456 | 2014-11-21 13:03 | 2014-11-21 14:20 | 77 | 11kV | 4543 | 59 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | Ex Zn12690 Berkeley Vale section of Pa10 PT12865 James Watt Eclipse. HDO raod side phase failed HDO have been failing in high temperatures See 1178259 exclude 1177456,68 | November | 2014 | 2015Q2 | 2015 | ZN12690:PA10 | ZN12690:PA10 | ZN12690/000010 | CENTRAL COAST | OH | Not Veg | 2014-11-21 | N | 77 | N | 5 | N | N | 1.1101 | 39.4971 | 3319.8904
[7 empty] | 12912 | 6070 | 1178496 | 2014-11-21 22:37 | 2014-11-21 22:48 | 11 | 11kV | 8008 | 728 | HV | Animal Possum | Animal | UGOH | Unplanned | Hot >35C | N | ZN 10994 Mortdale - Pnl 11 - Trip/reclose/trip, B phase IOC, Earth Fault, Reclose, Lockout. Possum on UGOH in Mulgoa Rd. | November | 2014 | 2015Q2 | 2015 | ZN10994:PA11 | ZN10994:PA11 | ZN10994/000011 | GEORGES RIVER | OH | Not Veg | 2014-11-21 | N | 11 | N | 5 | N | N | 1.1101 | 39.4971 | 5852.0102
[7 empty] | 12656 | 3791 | 1177651 | 2014-11-21 22:47 | 2014-11-21 23:55 | 68 | 11kV | 1700 | 25 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Hot >35C | N | LID 142997 Broken live line lead BPH, Repaird Bph and Cph LL leads also refer to 1177651 and 1177652 | November | 2014 | 2015Q2 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2014-11-21 | N | 68 | N | 5 | N | N | 1.1101 | 39.4971 | 1242.3099
[7 empty] | 13033 | 7047 | 1177613 | 2014-11-21 21:00 | 2014-11-22 00:49 | 229.2167 | 11kV | 65097.5333 | 284 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | LID 142998 1 Fault Operations Pole Mounted RAGCB, Overcurrent No Cause Found, Not Storm Conditions Reclose was non auto for fire ban | November | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-11-21 | N | 229.2167 | N | 5 | N | N | 1.1101 | 39.4971 | 47571.3573
[7 empty] | 13404 | 10184 | 1177660 | 2014-11-22 00:56 | 2014-11-22 01:49 | 53.1833 | 11kV | 11859.8833 | 223 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Wind Strong | N | OMS 142999 2 Fault operations Pole Mounted RAGCB, Overcurrent, No Cause Found Not Storm Conditions Note: Related record 1177662 report from customer (at 59 Lisadell Rd Medowie) of explosion from pole | November | 2014 | 2015Q2 | 2015 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2014-11-22 | N | 53.1833 | N | 5 | N | N | 1.1101 | 39.4971 | 8666.8529
[7 empty] | 13227 | 8574 | 1177724 | 2014-11-22 11:15 | 2014-11-22 13:15 | 120 | 11kV | 9840 | 82 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | lid 143004 11Kv SECTION ISOLATED TO REPLACE FAULTY 33kV INSULATORS AT POLE OS-20001. NO PROTECTION OPERATION. | November | 2014 | 2015Q2 | 2015 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2014-11-22 | N | 120 | N | 5 | N | N | 1.1101 | 39.4971 | 7190.7818
[7 empty] | 12952 | 6470 | 1177751 | 2014-11-22 14:34 | 2014-11-22 15:00 | 26.4833 | 11kV | 1244.7167 | 47 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 143005 Section beyond ABS 25622 isolated to remove tree from mains at pole HT-41005. No Protection Operations | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-11-22 | N | 26.4833 | N | 5 | N | N | 1.1101 | 39.4971 | 909.6022
[7 empty] | 13733 | 12788 | 1177798 | 2014-11-22 21:38 | 2014-11-22 22:45 | 67 | 11kV | 4288 | 64 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143007 Fuse size: 40 Amp Substation DOLF Volts = 242, Loads = Aph 110A, Bph 120A, Cph 150 A No cause found, not storm conditions | November | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2014-11-22 | N | 67 | N | 5 | N | N | 1.1101 | 39.4971 | 3133.5439
[7 empty] | 12674 | 3930 | 1177802 | 2014-11-22 22:11 | 2014-11-23 01:04 | 173 | 11kV | 167714 | 1087 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 4 Tripped on A phase IOC Reclose TD Lockout with EFI Cause: UGOH Fault - 1st UGOH below LB486, UGOH Below LB1209 also suspect. See OMS 1179097 1179098 1179099 1177803 1177802 1177804 | November | 2014 | 2015Q2 | 2015 | ZN965:PA4 | ZN965:PA4 | ZN00965/000004 | HORNSBY | Unknown | Unknown | 2014-11-22 | N | 154.2907 | N | 5 | N | N | 1.1101 | 39.4971 | 122560.4445
[7 empty] | 12786 | 4898 | 1177807 | 2014-11-23 05:37 | 2014-11-23 07:30 | 113 | 11kV | 452 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143008 Fuse size: 16 Amp - Line DOLF also refer to 1177807, CASS 21194 Patrol Requested | November | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-11-23 | N | 113 | N | 36 | Y | Y | 1.1101 | 39.4971 | 330.3083
[7 empty] | 12795 | 4964 | 1177826 | 2014-11-23 07:21 | 2014-11-23 08:04 | 43 | 11kV | 3612 | 84 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 143009 1 Fault operations, Pole Mounted RAGCB Bird Strike at Pole FQ-43157 | November | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-11-23 | N | 43 | N | 36 | Y | Y | 1.1101 | 39.4971 | 2639.5431
[7 empty] | 13539 | 11176 | 1177810 | 2014-11-23 06:15 | 2014-11-23 08:15 | 120 | 11kV | 240 | 2 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143010 Fuse size: 10 Amp Bird hit dolfs Also refer to 1177810 | November | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2014-11-23 | N | 120 | N | 36 | Y | Y | 1.1101 | 39.4971 | 175.3849
[7 empty] | 12746 | 4589 | 1177818 | 2014-11-23 07:03 | 2014-11-23 08:17 | 74 | 11kV | 148 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | NO LID report refer to 1177818 and 1177819 DOLF Replaced | November | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-11-23 | N | 74 | N | 36 | Y | Y | 1.1101 | 39.4971 | 108.154
[7 empty] | 14475 | 18520 | 1177825 | 2014-11-23 07:21 | 2014-11-23 16:55 | 574 | 11kV | 31720 | 101 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 143011 2 fault operations C phase Wire down to sub 59027 at P. 8W-20014. Dead magpie at the scene. | November | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-11-23 | N | 314.0594 | N | 36 | Y | Y | 1.1101 | 39.4971 | 23180.0404
[7 empty] | 12847 | 5537 | 1177923 | 2014-11-23 16:10 | 2014-11-23 17:57 | 107 | 11kV | 149855 | 1547 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At ZN965 Pennant Hills 11kV panel 28 Tripped on Overcurrent and Earth Fault Abnormals Switching: LB1209 Open, S7350 SW/A Closed LB486, AB1405 and LB482 Opened - SW/A Closed at S7373 - SW/A Closed at S8401. Cause: Cable Fault between S7352 Shepherd Lemongrass to S5424 McCuster Darlington to S48292 Bernard Doulton NOTE: Panel 28 Did not alarm as 11kV DNMS Trip See OMS 1179359 1179362 1179364 1177923 1177928 | November | 2014 | 2015Q2 | 2015 | ZN965:PA28 | ZN965:PA28 | ZN00965/000028 | HORNSBY | UG | Not Veg | 2014-11-23 | N | 96.8681 | N | 36 | Y | Y | 1.1101 | 39.4971 | 109509.614
[7 empty] | 14478 | 18541 | 1177922 | 2014-11-23 16:07 | 2014-11-23 17:58 | 111 | 11kV | 3496 | 247 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Hot >35C | N | LID 143024 A phase Overcurrent SECTION ISOLATED FOR REPAIRS AT UGOH POLE AK-83200 FDR RESTORED VIA FDR 19071 | November | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | Unknown | Unknown | 2014-11-23 | N | 14.1538 | N | 36 | Y | Y | 1.1101 | 39.4971 | 2554.7737
[7 empty] | 14144 | 16150 | 1177844 | 2014-11-23 09:10 | 2014-11-23 18:50 | 580 | 11kV | 43843 | 273 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Hot >35C | N | Zn12600 Lisarow Pa12 fdr tripped, reclosed and locked out Relays-A&C phase IOC, C phase timed Overcurrent, EFI Signals: 11kv trip EFI's S18264 S18250 S18078 S18011 See 1178421,2 2nd 1178424 Exclude 1177844,66 | November | 2014 | 2015Q2 | 2015 | ZN12600:PA12 | ZN12600:PA12 | ZN12600/000012 | CENTRAL COAST | OH | Veg | 2014-11-23 | N | 160.5971 | N | 36 | Y | Y | 1.1101 | 39.4971 | 32039.1713
[7 empty] | 12692 | 4071 | 1177987 | 2014-11-23 18:24 | 2014-11-23 19:34 | 70 | 11kV | 38290 | 547 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 143022 Overcurrent, Lightning Stuck pole FT-63154 also refer to 1177997 | November | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-11-23 | N | 70 | N | 36 | Y | Y | 1.1101 | 39.4971 | 27981.2026
[7 empty] | 12321 | 631 | 1178119 | 2014-11-23 19:59 | 2014-11-23 20:14 | 15 | 11kV | 15585 | 1039 | HV | Equipment Failed in Service | Equipment Failure | Stay Wire | Unplanned | Electrical Storm | N | LID 143045 TRIPPED FDR TO MAKE STAYWIRE SAFE | November | 2014 | 2015Q2 | 2015 | 222:33600 | 222:33600 | ZN00222/033600 | LAKE MACQUARIE | OH | Not Veg | 2014-11-23 | N | 15 | N | 36 | Y | Y | 1.1101 | 39.4971 | 11389.0583
[7 empty] | 14554 | 19110 | 1178010 | 2014-11-23 19:11 | 2014-11-23 20:47 | 96 | 11kV | 168660 | 1781 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | At S695 Pennant Hills Panel 46 Feeder tripped on Earth Fault Abnormal Switching: SW/B Closed at S7291, SW/B Closed at S7350 and SW/A Open at S7134. SW/A Opened at S6452, SW/B Opened at S6808, SW/A Closed at S7373 Cause: 11kV Cable fault between S6904 Fallon Water Board to S6611 Fallon Kenneth. See OMS 1179387 11479389 1178010 1178020 1178037 | November | 2014 | 2015Q2 | 2015 | ZN965:PA46 | ZN965:PA46 | ZN00965/000046 | HORNSBY | UG | Not Veg | 2014-11-23 | N | 94.6996 | N | 36 | Y | Y | 1.1101 | 39.4971 | 123251.7534
[7 empty] | 13451 | 10568 | 1178095 | 2014-11-23 20:05 | 2014-11-23 21:10 | 65 | 11kV | 8385 | 129 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143042 1 Fault operations, Pole Mounted RAGCB Overcurrent | November | 2014 | 2015Q2 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Veg | 2014-11-23 | N | 65 | N | 36 | Y | Y | 1.1101 | 39.4971 | 6127.5107
[7 empty] | 12642 | 3633 | 1178011 | 2014-11-23 18:48 | 2014-11-23 21:11 | 143 | 11kV | 91091 | 637 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143040 A & C phase Overcurrent | November | 2014 | 2015Q2 | 2015 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Veg | 2014-11-23 | N | 143 | N | 36 | Y | Y | 1.1101 | 39.4971 | 66566.6161
[7 empty] | 12531 | 2562 | 1177995 | 2014-11-23 18:47 | 2014-11-23 21:24 | 157 | 11kV | 144011 | 1249 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143031 1 fault operation B phase Overcurrent Excluded OMS 1177995 | November | 2014 | 2015Q2 | 2015 | 238:34141 | 238:34136 | ZN00238/034136 | MAITLAND | OH | Veg | 2014-11-23 | N | 115.301 | N | 36 | Y | Y | 1.1101 | 39.4971 | 105238.9912
[7 empty] | 14382 | 17774 | 1178060 | 2014-11-23 19:29 | 2014-11-23 21:27 | 118 | 11kV | 248980 | 2110 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143039 Overcurrent RH Leg ABC Overcurrent | November | 2014 | 2015Q2 | 2015 | 202:34254 | 202:34254 | ZN00202/034254 | NEWCASTLE | OH | Veg | 2014-11-23 | N | 118 | N | 36 | Y | Y | 1.1101 | 39.4971 | 181947.2403
[7 empty] | 13522 | 11089 | 1177992 | 2014-11-23 18:38 | 2014-11-23 21:35 | 177 | 11kV | 72393 | 409 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143029 Pole Mounted RAGCB No further information supplied | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-11-23 | N | 177 | N | 36 | Y | Y | 1.1101 | 39.4971 | 52902.6692
[7 empty] | 12547 | 2752 | 1177960 | 2014-11-23 17:20 | 2014-11-23 21:48 | 268.4333 | 11kV | 4831.8 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 143030 FDR ISOLATED TO REPAIR BROKEN LF 40267 | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-23 | N | 268.4333 | N | 36 | Y | Y | 1.1101 | 39.4971 | 3530.9369
[7 empty] | 12660 | 3829 | 1178054 | 2014-11-23 19:13 | 2014-11-23 22:01 | 168 | 11kV | 218400 | 1300 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143041 Fuse Size: 10 Amp Overcurrent Substation DOLF No Cause Found although electrical storm at time of operation | November | 2014 | 2015Q2 | 2015 | 221:11899 | 221:11899 | ZN00221/011899 | LAKE MACQUARIE | OH | Veg | 2014-11-23 | N | 168 | N | 36 | Y | Y | 1.1101 | 39.4971 | 159600.2783
[7 empty] | 13444 | 10535 | 1177974 | 2014-11-23 18:03 | 2014-11-23 22:10 | 247 | 11kV | 25688 | 104 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143033 Fuse: 16Amp Substation DOLF also refer to 1177974 | November | 2014 | 2015Q2 | 2015 | 502:48001 | 502:48001 | ZN00502/048001 | MAITLAND | OH | Veg | 2014-11-23 | N | 247 | N | 36 | Y | Y | 1.1101 | 39.4971 | 18772.0327
[7 empty] | 13351 | 9748 | 1177986 | 2014-11-23 18:30 | 2014-11-23 22:17 | 227 | 11kV | 29056 | 128 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | CC1: 19-"Complete - Network related fault" FRC1: 328-"High Voltage Fuse - Replaced - Specify Detail By Voice" Note: appears that DOLF was replaced by the EMSO, there is no Control Room LID entered. No further information available also refer to customers that called in on OMS 1178135 and OMS 1177986, Customer at 17 GREEN ST was advising of LV and Cust says A.C not working properly - ref to claims | November | 2014 | 2015Q2 | 2015 | 502:48008 | 502:48008 | ZN00502/048008 | MAITLAND | OH | Veg | 2014-11-23 | N | 227 | N | 36 | Y | Y | 1.1101 | 39.4971 | 21233.2678
[7 empty] | 12878 | 5814 | 1177967 | 2014-11-23 20:35 | 2014-11-23 22:25 | 110 | 11kV | 220 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 143025 B phase SUB ISOLATED VIA ABS 9183 TO REPAIR SWING LL LEAD AT SUB 54775 | November | 2014 | 2015Q2 | 2015 | 524:33570 | 524:33570 | ZN00524/033570 | CESSNOCK | OH | Not Veg | 2014-11-23 | N | 110 | N | 36 | Y | Y | 1.1101 | 39.4971 | 160.7695
[7 empty] | 12818 | 5169 | 1178145 | 2014-11-23 21:19 | 2014-11-23 22:55 | 96 | 11kV | 96 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 143035 Single Phase, Substation DOLF Refer to related record 1178145, customer reported Lightning has hit Pole #9K50127 | November | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2014-11-23 | N | 96 | N | 36 | Y | Y | 1.1101 | 39.4971 | 70.154
[7 empty] | 13473 | 10711 | 1178014 | 2014-11-23 22:00 | 2014-11-23 23:20 | 80 | 11kV | 80 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143043 Substation DOLF, no further information supplied however there was a report from customer on related record 1178014 of exposed wires | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-11-23 | N | 80 | N | 36 | Y | Y | 1.1101 | 39.4971 | 58.4616
[7 empty] | 13410 | 10233 | 1179215 | 2014-11-23 19:21 | 2014-11-23 23:40 | 259 | 11kV | 152043 | 1532 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 143068 Earth fault times earth fault From customer reports it appears that lighting struck Pole JU86041, causing Lightning Arrestor to blow and be replaced Excluded OMS 1178051 | November | 2014 | 2015Q2 | 2015 | 261:81865 | 261:81865 | ZN00261/081865 | LAKE MACQUARIE | OH | Not Veg | 2014-11-23 | N | 99.2448 | N | 36 | Y | Y | 1.1101 | 39.4971 | 111108.5399
[7 empty] | 13899 | 14144 | 1178104 | 2014-11-23 19:50 | 2014-11-24 00:25 | 275 | 11kV | 7425 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143053 Fuse size 31 Amp Substation DOLF also refer to 1178146 | November | 2014 | 2015Q2 | 2015 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Veg | 2014-11-23 | N | 275 | N | 36 | Y | Y | 1.1101 | 39.4971 | 5425.971
[7 empty] | 14502 | 18707 | 1178146 | 2014-11-23 21:37 | 2014-11-24 01:05 | 208 | 11kV | 8944 | 43 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143054 A phase DOLF : 20 Amp excluded OMS 1178146 | November | 2014 | 2015Q2 | 2015 | 258:80778 | 258:80778 | ZN00258/080778 | NEWCASTLE | OH | Veg | 2014-11-23 | N | 208 | N | 36 | Y | Y | 1.1101 | 39.4971 | 6536.0114
[7 empty] | 14005 | 14979 | 1178035 | 2014-11-23 19:37 | 2014-11-24 01:30 | 353 | 11kV | 30005 | 85 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143070 Substation DOLF Blown L/As sub opened, Interconnected at 1.30am also refer to 1178035 | November | 2014 | 2015Q2 | 2015 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Not Veg | 2014-11-23 | N | 353 | N | 36 | Y | Y | 1.1101 | 39.4971 | 21926.769
[7 empty] | 14487 | 18578 | 1178083 | 2014-11-23 19:00 | 2014-11-24 01:45 | 405.2833 | 11kV | 12969.0667 | 32 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 143061 Fuse: 16Amp - Line DOLF Sub Isolated and LF Replaced. Note: Calls from 2 customers on Giles Rod, Seaham of Lighting Strike on Giles Road | November | 2014 | 2015Q2 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-11-23 | N | 405.2833 | N | 36 | Y | Y | 1.1101 | 39.4971 | 9477.4114
[7 empty] | 14552 | 19085 | 1178052 | 2014-11-23 18:53 | 2014-11-24 02:30 | 457 | 11kV | 3559 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143066 B & C phase Overcurrent Excluded OMS 1178052 | November | 2014 | 2015Q2 | 2015 | 235:2121 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Veg | 2014-11-23 | N | 142.36 | N | 36 | Y | Y | 1.1101 | 39.4971 | 2600.8122
[7 empty] | 13420 | 10308 | 1178173 | 2014-11-24 01:45 | 2014-11-24 03:05 | 80 | 11kV | 720 | 9 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143063 C phase DOLF SEE REPORT 143061 SUB ISOLATED TO REPAIR LA Excluded OMS 1178173 | November | 2014 | 2015Q2 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-11-24 | N | 80 | N | 41 | Y | Y | 1.1101 | 39.4971 | 526.1548
[7 empty] | 12776 | 4831 | 1178076 | 2014-11-23 20:59 | 2014-11-24 03:10 | 371 | 11kV | 15582 | 42 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143071 A & B 31A DOLF Operated during storms. A & B Phase LA's cut away | November | 2014 | 2015Q2 | 2015 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Not Veg | 2014-11-23 | N | 371 | N | 36 | Y | Y | 1.1101 | 39.4971 | 11386.866
[7 empty] | 12389 | 1304 | 1178154 | 2014-11-23 22:17 | 2014-11-24 04:00 | 343 | 11kV | 191586 | 1601 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 143055 Fdr opened for safety Broken xarm P IV-60642 Excluded OMS 1178138 | November | 2014 | 2015Q2 | 2015 | 206:34440 | 206:34440 | ZN00206/034440 | LAKE MACQUARIE | OH | Not Veg | 2014-11-23 | N | 119.6665 | N | 36 | Y | Y | 1.1101 | 39.4971 | 140005.398
[7 empty] | 14041 | 15365 | 1178165 | 2014-11-24 00:18 | 2014-11-24 05:10 | 292 | 11kV | 77758 | 1201 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 143059 Fdr opened for safety, pole fire JV-70932 see report 143058 Excluded OMS 1178165 | November | 2014 | 2015Q2 | 2015 | 220:8691 | 220:8691 | ZN00220/008691 | LAKE MACQUARIE | OH | Not Veg | 2014-11-24 | N | 64.7444 | N | 41 | Y | Y | 1.1101 | 39.4971 | 56823.2529
[7 empty] | 13036 | 7057 | 1178114 | 2014-11-23 20:52 | 2014-11-24 05:45 | 533 | 11kV | 28249 | 53 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 1178114 C Phase 40 A DOLF blew during electrical storms | November | 2014 | 2015Q2 | 2015 | 203:8089 | 204:82710 | ZN00204/082710 | NEWCASTLE | OH | Not Veg | 2014-11-23 | N | 533 | N | 36 | Y | Y | 1.1101 | 39.4971 | 20643.536
[7 empty] | 12594 | 3187 | 1178006 | 2014-11-23 19:04 | 2014-11-24 06:30 | 686 | 11kV | 36610 | 122 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143051 Earth fault blown arrestors at subs 27191,6465 A/R was OFF | November | 2014 | 2015Q2 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2014-11-23 | N | 300.082 | N | 36 | Y | Y | 1.1101 | 39.4971 | 26753.5082
[7 empty] | 12384 | 1213 | 1178150 | 2014-11-23 21:53 | 2014-11-24 09:03 | 670 | 11kV | 2010 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143102 C phase DOLF : 10 Amp Excluded OMS 1178150 | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-11-23 | N | 670 | N | 36 | Y | Y | 1.1101 | 39.4971 | 1468.8487
[7 empty] | 13582 | 11569 | 1178222 | 2014-11-24 07:48 | 2014-11-24 09:55 | 127 | 11kV | 254 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143107 C phase DOLF : 20 Amp Also replaced 16A DOLF at sub 51285. Excluded OMS 1178222 | November | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2014-11-24 | N | 127 | N | 41 | Y | Y | 1.1101 | 39.4971 | 185.6157
[7 empty] | 12332 | 732 | 1178040 | 2014-11-23 19:40 | 2014-11-24 10:12 | 872 | 11kV | 2616 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143110 C phase DOLF : 16 Amp Excluded OMS 1178040 & 1178201 | November | 2014 | 2015Q2 | 2015 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Veg | 2014-11-23 | N | 872 | N | 36 | Y | Y | 1.1101 | 39.4971 | 1911.6956
[7 empty] | 12906 | 6030 | 1178215 | 2014-11-24 07:22 | 2014-11-24 10:30 | 188 | 11kV | 564 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143109 A phase DOLF : 10 Amp Faulty HV arrester cut away. Volts = 240. Amps = 43. Excluded OMS 1178215. | November | 2014 | 2015Q2 | 2015 | 230:81432 | 230:81432 | ZN00230/081432 | PORT STEPHENS | OH | Veg | 2014-11-24 | N | 188 | N | 41 | Y | Y | 1.1101 | 39.4971 | 412.1546
[7 empty] | 13774 | 13109 | 1178018 | 2014-11-23 19:15 | 2014-11-24 11:45 | 990 | 11kV | 41631 | 70 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143032 Pole Mounted RAGCB, HV Reported Down Section isolated to repair wires down wires down between 51675 & 51655 OMS 1178018 & 1178181 & 1178063. SECTION ISOLATED TO REPAIR WIRES DOWN eXTRA DEFECT FOUND . TREE ON MAINS AT SUB53501 | November | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-11-23 | N | 594.7286 | N | 36 | Y | Y | 1.1101 | 39.4971 | 30422.7069
[7 empty] | 12789 | 4936 | 1178000 | 2014-11-24 05:09 | 2014-11-24 13:17 | 488 | 11kV | 1091 | 68 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143093 DOLF : 20 Amp Blown L/A at sub 51176 Kilner. Tripped Sw 42028. G Jones to investigate. Excluded OMS 1178185 | November | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-11-24 | N | 16.0441 | N | 41 | Y | Y | 1.1101 | 39.4971 | 797.2706
[7 empty] | 14252 | 16911 | 1178174 | 2014-11-24 06:50 | 2014-11-24 15:50 | 540 | 11kV | 1145 | 122 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143106 1 fault operation Single phase DOLF : 10 Amp Blown L/A at sub 27192. Sw 2108 Seaham Rd tripped when DOLFs retried at 855hrs. Out for 5 minutes Excluded OMS 1178200 | November | 2014 | 2015Q2 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2014-11-24 | N | 9.3852 | N | 41 | Y | Y | 1.1101 | 39.4971 | 836.7322
[7 empty] | 13435 | 10455 | 1178539 | 2014-11-24 14:39 | 2014-11-24 16:51 | 132 | 11kV | 29700 | 225 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143133 1 fault operation 3 phase Overcurrent Parkville RAGCB faulty left bypassed | November | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-11-24 | N | 132 | N | 41 | Y | Y | 1.1101 | 39.4971 | 21703.884
[7 empty] | 13869 | 13864 | 1178579 | 2014-11-24 15:50 | 2014-11-24 17:12 | 82 | 11kV | 7872 | 96 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143124 1 fault operation 3 phase Please patrol feeder - Note customer at Willow Glen reported that lighting struck nearby and then supply was lost Sw 42002 Reclose function off due to bushfire defects. | November | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-11-24 | N | 82 | N | 41 | Y | Y | 1.1101 | 39.4971 | 5752.6254
[7 empty] | 12573 | 3042 | 1178606 | 2014-11-24 16:05 | 2014-11-24 17:24 | 78.6667 | 11kV | 66630.6667 | 847 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Section of ZN.15005 Belrose 11kV feeder from RE.24831 (14 DC's) tripped on IOC & timed OC Cause:- Lightning strike outside 15 Laycock St ME:-1178606 Withdrawn:-1178611, 1178678 | November | 2014 | 2015Q2 | 2015 | ZN15005:PA6 | ZN15005:PA6 | ZN15005/000006 | NORTHERN BEACHES | OH | Not Veg | 2014-11-24 | N | 78.6667 | N | 41 | Y | Y | 1.1101 | 39.4971 | 48691.7259
[7 empty] | 13803 | 13303 | 1178550 | 2014-11-24 15:02 | 2014-11-24 17:29 | 147 | 11kV | 23126 | 195 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143125 Aph OHM in trees near sub 17668. Possible prot. Malgrade with Gundy Reg Intellirupter. Excluded OMS NO. 1178550 + 1178552 | November | 2014 | 2015Q2 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2014-11-24 | N | 118.5949 | N | 41 | Y | Y | 1.1101 | 39.4971 | 16899.7987
[7 empty] | 14321 | 17337 | 1178654 | 2014-11-24 15:57 | 2014-11-24 17:35 | 98 | 11kV | 86778 | 897 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | ZN 10994 Mortdale - Pnl 19 - SEL, 50TB, 50TN, EF, C phase leakage. Lightning strike. Electrical storm in area. ME: 1179998. Rest Step: 1179999. Withdrawn: 1178598, 654, 685. | November | 2014 | 2015Q2 | 2015 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2014-11-24 | N | 96.7425 | N | 41 | Y | Y | 1.1101 | 39.4971 | 63414.8029
[7 empty] | 12843 | 5482 | 1178563 | 2014-11-24 15:23 | 2014-11-24 17:44 | 141 | 11kV | 189816 | 1376 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Wind Storm | N | At S2466 Flemington: 11kv feeder Panel No45 "Crescent Richmond No1 etc" tripped Relays: INST O/C A+C phase, timed C phase O/C, EFI, fault check Field EFIs: S5609, 7607, 35238, 35355, 8692 Remarks: UG fault. Suspect 11kv feeder fault between S8692 Henley Arthur Sw/B and S2725 Howard Arthur Sw/A. HAZ RMI at S2725 feeder to be extended. Region to organise | November | 2014 | 2015Q2 | 2015 | ZN2466:PA45 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2014-11-24 | N | 137.9477 | N | 41 | Y | Y | 1.1101 | 39.4971 | 138711.9342
[7 empty] | 13191 | 8369 | 1178587 | 2014-11-24 15:54 | 2014-11-24 17:54 | 120 | 11kV | 206160 | 1718 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | Lightning | N | @ZN1285 Greenacre Park 11kv panel 24 "S3220 Banksia Stacey" feeder tripped and locked out on - Relays - IOC, EFI, E/F, Lockout Field EFI's: S3220, 48629, Signals: ZN E, Gorup2+3 E. 11kv trip Remarks: lightning. See sep interuption reports on Pnl 27 @ GAP and panel 38 @ punchbowl. Lightning hit AB 549 and split pole and HV into LV near PT1578 Buckwall ave. Dop found LV// links in for PT1578 tied in with S1182 cooeeyana rd. Dop removed LV// see seperate interruption report on S1182 | November | 2014 | 2015Q2 | 2015 | ZN1285:PA24 | ZN37100:PA11 | ZN37100/000011 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-11-24 | N | 120 | N | 41 | Y | Y | 1.1101 | 39.4971 | 150655.6473
[7 empty] | 12460 | 1835 | 1178737 | 2014-11-24 16:59 | 2014-11-24 17:55 | 56 | 11kV | 168 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143132 A phase DOLF : 10 Amp Excluded OMS 1178737 | November | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Veg | 2014-11-24 | N | 56 | N | 41 | Y | Y | 1.1101 | 39.4971 | 122.7694
[7 empty] | 14443 | 18248 | 1178632 | 2014-11-24 16:11 | 2014-11-24 18:22 | 131.1 | 11kV | 15600.9 | 119 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | PT 9238 Currah Rd - HDO centre and road side phase. Electrical storm in the area. Lightning affected Pnl 12 at the same time. ME: 1178628. Withdrawn: 1178632, 61. | November | 2014 | 2015Q2 | 2015 | ZN9252:PA12 | ZN9252:PA24 | ZN09252/000024 | SUTHERLAND | OH | Not Veg | 2014-11-24 | N | 131.1 | N | 41 | Y | Y | 1.1101 | 39.4971 | 11400.6776
[7 empty] | 12666 | 3882 | 1178803 | 2014-11-24 17:41 | 2014-11-24 18:29 | 48 | 11kV | 11919 | 253 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143128 2 fault operations A & C phase Instantaneous Overcurrent Customers reported lightning strikes near ABS 40673. Excluded OMS No. 1178803 | November | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-11-24 | N | 47.1107 | N | 41 | Y | Y | 1.1101 | 39.4971 | 8710.0536
[7 empty] | 12827 | 5283 | 1178593 | 2014-11-24 15:57 | 2014-11-24 18:30 | 153 | 11kV | 12632 | 1536 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Electrical Storm | N | ZN 9252 Jannali - Pnl 10 - Trip/reclose, B & C phase OC. (At PT 9070 Third Ave - Centre and Footpath phase HDO) Lightning strike during electrical storm. PT 9070 found with HDO's blown after reclose. ME: 1180371. Rest Step: 1180373. Withdrawn: 1178593, 668, 755. | November | 2014 | 2015Q2 | 2015 | ZN9252:PA10 | ZN9252:PA22 | ZN09252/000022 | SUTHERLAND | OH | Not Veg | 2014-11-24 | N | 8.224 | N | 41 | Y | Y | 1.1101 | 39.4971 | 9231.093
[7 empty] | 13018 | 6927 | 1180287 | 2014-11-24 15:50 | 2014-11-24 18:55 | 185 | 11kV | 185 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143129 Single DOLF : 10 Amp Replaced blown Lightning Arrestor Note also refer to 1181296 upstream recloser operated at the same time | November | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-11-24 | N | 185 | N | 41 | Y | Y | 1.1101 | 39.4971 | 135.1925
[7 empty] | 13719 | 12655 | 1178630 | 2014-11-24 15:50 | 2014-11-24 19:00 | 190 | 11kV | 103780 | 727 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | @ZN2196 Milperra 11kv VCB panel No.2 "S61792" feeder tripped and locked out on Relays: C phase timed O/C, EFI, E/F, Fault check Field EFIs: S61792, 6612, 35688, 8702, 5830, 1959, 7861, 5575 Signals: 11kv trip, No.3 GE+ZE Remarks: Lightning/ Surge Arrestor. Dop patrolled O/H feeder found PT916 Raliegh rd all three HVDO operated. Dop isolated PT tried feeder back and failed @ 17:35 PT1687 Bugden Ave also hit by lightning C phase lightning arrestor operated. Subs on site repairing. | November | 2014 | 2015Q2 | 2015 | ZN2196:PA2 | ZN2196:PA2 | ZN02196/000002 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-11-24 | N | 142.751 | N | 41 | Y | Y | 1.1101 | 39.4971 | 75839.363
[7 empty] | 12858 | 5625 | 1178708 | 2014-11-24 15:57 | 2014-11-24 19:49 | 232.2833 | 11kV | 15174.4167 | 182 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Electrical Storm | N | S 10144 Washington Dunmore - HV fuse Aphase (40A). Earlier trip on Pnl 17 due to lightning. Restored via LV//. ME: 1178708. ME GIS: 1178765. Withdrawn: 1178684, 765, 897. | November | 2014 | 2015Q2 | 2015 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2014-11-24 | N | 83.3759 | N | 41 | Y | Y | 1.1101 | 39.4971 | 11089.0161
[7 empty] | 14386 | 17793 | 1178913 | 2014-11-24 18:29 | 2014-11-24 20:35 | 126 | 11kV | 756 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143147 C phase DOLF : 10 Amp Tx Volts: Aph - 236V, Bph - 240V, Cph - 241V Note these customer were affected by coinciding events - refer to 1180394 where the customers first lost supply at 24/11/2014 17:41 and at the same time, this DOLF blew | November | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-11-24 | N | 126 | N | 41 | Y | Y | 1.1101 | 39.4971 | 552.4625
[7 empty] | 13129 | 7829 | 1178836 | 2014-11-24 18:15 | 2014-11-24 21:00 | 165 | 11kV | 36524 | 321 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | Zn12630 Peats Ridge Pa4 "USL44919" fdr opened & locked out on A phase timed overcurrent, reclose timing & Lockout Relays Weather related See 1179192,4,5 Exclude 1178836 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2014-11-24 | N | 113.7819 | N | 41 | Y | Y | 1.1101 | 39.4971 | 26690.6619
[7 empty] | 13166 | 8096 | 1178609 | 2014-11-24 16:05 | 2014-11-24 21:10 | 305 | 11kV | 104550 | 516 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143137 Roof off shed in 11kV OHM near sub 53415. Tree brought down LV OHM beyond LVF 59007 Halton sub. Excluded OMS 1178609, 1178634, 1178682, 1178825 & 1178946 WIND GUST RESULTED IN SHED ROOF HANGING FROM POWELINES. ROOF WITHIN REACH. POWER OFF. | November | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-11-24 | N | 202.6163 | N | 41 | Y | Y | 1.1101 | 39.4971 | 76402.0563
[7 empty] | 12480 | 2031 | 1178880 | 2014-11-24 18:47 | 2014-11-24 21:10 | 143 | 11kV | 572 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143148 B phase DOLF : 16 Amp Tx Volts : 244V | November | 2014 | 2015Q2 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2014-11-24 | N | 143 | N | 41 | Y | Y | 1.1101 | 39.4971 | 418.0007
[7 empty] | 12808 | 5081 | 1178937 | 2014-11-24 20:03 | 2014-11-24 21:15 | 72 | 11kV | 3024 | 42 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 142138 A phase DOLF : 31 Amp 62683 Bellevue Pacific no cause found. EmSO reports that two LA's have been cut away from previous storm. | November | 2014 | 2015Q2 | 2015 | 222:33602 | 222:33602 | ZN00222/033602 | LAKE MACQUARIE | OH | Veg | 2014-11-24 | N | 72 | N | 41 | Y | Y | 1.1101 | 39.4971 | 2209.85
[7 empty] | 14370 | 17678 | 1178620 | 2014-11-24 15:57 | 2014-11-24 21:18 | 321.2167 | 11kV | 401072.05 | 2149 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | Electrical Storm | N | ZN 10999 Kogarah - Pnl 22 - Trip/reclose/trip, All phases IOC, EFI, EFC, Rec, lockout, Field EFI. UGOH to S 10864 has failed in service. ME: 1180521. Rest Step: 1180522, 3. ME GIS: 1178930. Withdrawn: 1178620, 66, 1178898, 917, 938. | November | 2014 | 2015Q2 | 2015 | ZN10999:PA22 | ZN10999:PA22 | ZN10999/000022 | BAYSIDE | Unknown | Unknown | 2014-11-24 | N | 186.6319 | N | 41 | Y | Y | 1.1101 | 39.4971 | 293091.6245
[7 empty] | 13229 | 8584 | 1178696 | 2014-11-24 16:42 | 2014-11-24 21:19 | 277 | 11kV | 554 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143150 C Phase DOLF : 10 Amp Excluded OMS 1178696 | November | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-11-24 | N | 277 | N | 41 | Y | Y | 1.1101 | 39.4971 | 404.8469
[7 empty] | 13047 | 7145 | 1178640 | 2014-11-24 16:15 | 2014-11-24 21:40 | 325 | 11kV | 4550 | 14 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143140 A & C phase DOLF : 10 Amp 11kV OHM on ground near gundibri sub 70836. Suspect 11kV into LV. Excluded OMS 1178640 | November | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2014-11-24 | N | 325 | N | 41 | Y | Y | 1.1101 | 39.4971 | 3325.0058
[7 empty] | 13654 | 12161 | 1178709 | 2014-11-24 16:39 | 2014-11-24 22:14 | 335 | 11kV | 380974 | 1810 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 143139 1 fault operation A phase Earth fault mini cyclone that flew through the area causing several spans of mains to come down due to vegetation contact. | November | 2014 | 2015Q2 | 2015 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2014-11-24 | N | 210.4829 | N | 41 | Y | Y | 1.1101 | 39.4971 | 278404.5624
[7 empty] | 12530 | 2555 | 1178823 | 2014-11-24 18:03 | 2014-11-24 22:35 | 272 | 11kV | 544 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143154 Single phase DOLF : 10 Amp Excluded OMS 1178823 | November | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Veg | 2014-11-24 | N | 272 | N | 41 | Y | Y | 1.1101 | 39.4971 | 397.5392
[7 empty] | 12710 | 4221 | 1178781 | 2014-11-24 17:28 | 2014-11-24 22:37 | 309 | 11kV | 4635 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143170 A Phase DOLF : 10 Amp Excluded OMS 1178781 | November | 2014 | 2015Q2 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2014-11-24 | N | 309 | N | 41 | Y | Y | 1.1101 | 39.4971 | 3387.1213
[7 empty] | 14526 | 18929 | 1178809 | 2014-11-24 17:43 | 2014-11-24 22:55 | 312 | 11kV | 256473 | 825 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143153 2 fault operations 3 phase Rob Mitchell could not find any targets for Cb 13020. Fdr patrolled no fault found. Suggest protection checks. Excluded OMS 1178809 & 1178845 | November | 2014 | 2015Q2 | 2015 | 227:13020 | 227:13020 | ZN00227/013020 | LAKE MACQUARIE | OH | Veg | 2014-11-24 | N | 310.8764 | N | 41 | Y | Y | 1.1101 | 39.4971 | 187422.9037
[7 empty] | 13653 | 12158 | 1178701 | 2014-11-24 16:45 | 2014-11-24 23:00 | 375 | 11kV | 375 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Electrical Storm | N | REPLACED HV C KPHASE FUSE 10AMP CUSTOMER REPORTS LIGHTNING HIT TRANSFORMER BOX ON POLE - REPORTS WIRE HANGING FROM BOX ALSO also refer to 1178701 | November | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-11-24 | N | 375 | N | 41 | Y | Y | 1.1101 | 39.4971 | 274.0389
[7 empty] | 14098 | 15791 | 1178944 | 2014-11-24 20:17 | 2014-11-24 23:20 | 183 | 11kV | 183 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143151 A phase DOLF : 10 Amp Replaced blown L/A's Tx Volts: Aph - 241V, Bph - 241V, Cph - 243V | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-24 | N | 183 | N | 41 | Y | Y | 1.1101 | 39.4971 | 133.731
[7 empty] | 14224 | 16699 | 1178775 | 2014-11-24 17:25 | 2014-11-25 00:40 | 435 | 11kV | 870 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143184 A phase DOLF : 5 Amp Excluded OMS 1178775 25/11/14 00:40 CASS: REPLACED 5A 'A' PHASE DOLF ELEMENT AT SUB 54388. SUPPLY CHECKED AND OK FOLLOWING FUSE REPLACEMENT. DETAILS GIVEN TO SYS OP 3 OVER THE PHONE. | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-11-24 | N | 435 | N | 41 | Y | Y | 1.1101 | 39.4971 | 635.7703
[7 empty] | 14027 | 15264 | 1178837 | 2014-11-25 00:45 | 2014-11-25 01:00 | 15 | 11kV | 15 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143195 C phase DOLF : 10 Amp excluded OMS 1178837 | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-11-25 | N | 15 | N | 15 | N | N | 1.1101 | 39.4971 | 10.9616
[7 empty] | 13020 | 6948 | 1178677 | 2014-11-24 16:24 | 2014-11-25 01:30 | 546 | 11kV | 26034 | 66 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143198 2 fault operations B & C phase Overcurrent WIRES DOWN BETWEEN POLES JQ-41395 & JQ-41396. Excluded OMS REPORT 1178753. | November | 2014 | 2015Q2 | 2015 | 508:82580 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-11-24 | N | 394.4545 | N | 41 | Y | Y | 1.1101 | 39.4971 | 19024.8793
[7 empty] | 13336 | 9621 | 1178990 | 2014-11-25 01:04 | 2014-11-25 01:53 | 49 | 11kV | 27244 | 556 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ZN35900 Potts Hill 11kv panel 25 "S8773 Botanica Cedar" feeder tripped on - Relays - 50TN, 51N, EFI Field EFIs - S8773, 395, 5107, 6570, 139, 46349, 47658, 35364, 35084, 35085 Signals: 11kv trip, group earth, protection trip Remarks: UG fault. Suspect 11kv feeder fault from S35085 Betty Grevillia to ZN3472 Sefton Panel 7 | November | 2014 | 2015Q2 | 2015 | ZN35900:PA25 | ZN3472:PA7 | ZN03472/000007 | CUMBERLAND | UG | Not Veg | 2014-11-25 | N | 49 | N | 15 | N | N | 1.1101 | 39.4971 | 19909.1116
[7 empty] | 14139 | 16108 | 1178756 | 2014-11-24 17:15 | 2014-11-25 02:00 | 525.4667 | 11kV | 43613.7333 | 83 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 143182 B & C phase cartridge fuses : 40 Amp Excluded OMS 1178756 | November | 2014 | 2015Q2 | 2015 | 224:80337 | 224:80337 | ZN00224/080337 | LAKE MACQUARIE | UG | Not Veg | 2014-11-24 | N | 525.4667 | N | 41 | Y | Y | 1.1101 | 39.4971 | 31871.6299
[7 empty] | 13727 | 12749 | 1178788 | 2014-11-24 16:58 | 2014-11-25 02:30 | 572 | 11kV | 23453 | 82 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143165 1 fault operation Overcurrent Excluded 1178788 | November | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2014-11-24 | N | 286.0122 | N | 41 | Y | Y | 1.1101 | 39.4971 | 17138.7607
[7 empty] | 12420 | 1563 | 1179735 | 2014-11-25 02:53 | 2014-11-25 04:20 | 87 | 11kV | 1131 | 13 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143200 Isolated section for clearance to replace 33kV main on pin at pole IU-41266. | November | 2014 | 2015Q2 | 2015 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Not Veg | 2014-11-25 | N | 87 | N | 15 | N | N | 1.1101 | 39.4971 | 826.5014
[7 empty] | 14664 | 20233 | 1178586 | 2014-11-24 15:54 | 2014-11-25 05:00 | 786 | 11kV | 92035 | 1760 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | @ZN1285 Greenacre Park 11kv Panel 27 "S4861 Stiller Pl" tripped and reclosed on - Relays: A+C INST, Ceiling contactor, lockout, EFI Field EFI's: S4861, 36235, 47526, 47009, 7730, 7806 Signals: 11kv trip Remarks: lightning. See seperate interruption report on PNL 24 @ GAP and 38 @ Punchbowl | November | 2014 | 2015Q2 | 2015 | ZN1285:PA27 | ZN2310:PA23 | ZN02310/000023 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-11-24 | N | 52.2926 | N | 41 | Y | Y | 1.1101 | 39.4971 | 67256.4634
[7 empty] | 14184 | 16379 | 1178774 | 2014-11-24 17:23 | 2014-11-25 05:20 | 717 | 11kV | 1434 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 143203 Single phase DOLF : 10 Amp Replaced faulty LA's.Also see report 143202 Excluded OMS 1178774 | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-11-24 | N | 717 | N | 41 | Y | Y | 1.1101 | 39.4971 | 1047.9249
[7 empty] | 13645 | 12089 | 1179009 | 2014-11-25 07:39 | 2014-11-25 08:08 | 28.9333 | 11kV | 434 | 15 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143205 A & B Phase 40A DOLF's operated Electrical Storm the previous evening | November | 2014 | 2015Q2 | 2015 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2014-11-25 | N | 28.9333 | N | 15 | N | N | 1.1101 | 39.4971 | 317.1544
[7 empty] | 14295 | 17206 | 1179016 | 2014-11-25 06:46 | 2014-11-25 08:10 | 84 | 11kV | 420 | 5 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 143204 A Phase DOLF Operated. Failed HV arrestor cutaway. | November | 2014 | 2015Q2 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2014-11-25 | N | 84 | N | 15 | N | N | 1.1101 | 39.4971 | 306.9236
[7 empty] | 13342 | 9682 | 1178996 | 2014-11-25 03:41 | 2014-11-25 08:50 | 309 | 11kV | 927 | 3 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143209 B & C Phase 10A DOLF's. Electrical Storms during previous evening | November | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2014-11-25 | N | 309 | N | 15 | N | N | 1.1101 | 39.4971 | 677.4243
[7 empty] | 13447 | 10544 | 1179086 | 2014-11-25 08:46 | 2014-11-25 09:30 | 44 | 11kV | 88 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143210 B Phase 10A DOLF operated Electrical Storms the previous evening | November | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2014-11-25 | N | 44 | N | 15 | N | N | 1.1101 | 39.4971 | 64.3078
[7 empty] | 14507 | 18767 | 1178998 | 2014-11-25 03:52 | 2014-11-25 10:30 | 398 | 11kV | 9883 | 56 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section Pa12 "Yarramalong" @RE45015 Brush Creek tripped on overcurrent & Earth Fault 11kv OH Mains down just below tee off PT13355 Brush Creek Yarra 5.9 See 1179539,41,2 Exclude 1178998 | November | 2014 | 2015Q2 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2014-11-25 | N | 176.4821 | N | 15 | N | N | 1.1101 | 39.4971 | 7222.2049
[7 empty] | 14639 | 20067 | 1179024 | 2014-11-25 07:12 | 2014-11-25 11:00 | 228 | 11kV | 228 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143216 B Phase DOLF : 10 Amp Excluded OMS 1179024 | November | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-11-25 | N | 228 | N | 15 | N | N | 1.1101 | 39.4971 | 166.6157
[7 empty] | 13880 | 13931 | 1179165 | 2014-11-25 10:05 | 2014-11-25 11:10 | 65 | 11kV | 130 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143217 10A B Phase DOLF operated. Storms the previous evening | November | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2014-11-25 | N | 65 | N | 15 | N | N | 1.1101 | 39.4971 | 95.0002
[7 empty] | 12410 | 1489 | 1179124 | 2014-11-25 09:20 | 2014-11-25 11:50 | 150 | 11kV | 150 | 1 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Wind Strong | N | LID 143218 A Phase 10 A Dolf Operated Sheet of iron blown into mains during storms | November | 2014 | 2015Q2 | 2015 | 802:82225 | 802:82225 | ZN00802/082225 | MUSWELLBROOK | OH | Veg | 2014-11-25 | N | 150 | N | 15 | N | N | 1.1101 | 39.4971 | 109.6156
[7 empty] | 13304 | 9171 | 1178929 | 2014-11-24 19:51 | 2014-11-25 12:40 | 1009 | 11kV | 22198 | 22 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | N | S 10642 Depot Rd - HV Fuse All phases. Lightning in the area. ME: 1180109. Withdrawn: 1178929. | November | 2014 | 2015Q2 | 2015 | ZN10994:PA19 | ZN10994:PA19 | ZN10994/000019 | GEORGES RIVER | OH | Not Veg | 2014-11-24 | N | 1009 | N | 41 | Y | Y | 1.1101 | 39.4971 | 16221.6437
[7 empty] | 14428 | 18124 | 1179243 | 2014-11-25 12:01 | 2014-11-25 12:42 | 41 | 11kV | 19024 | 464 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa12 "Yarramalong" @RE48838 Yarramalong Maitland 1.2 tripped on overucreent & lockout Branch on HV overhead mains @ tee off PT12717 Henry Yarra | November | 2014 | 2015Q2 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Veg | 2014-11-25 | N | 41 | N | 15 | N | N | 1.1101 | 39.4971 | 13902.1781
[7 empty] | 13943 | 14549 | 1179232 | 2014-11-25 11:47 | 2014-11-25 15:25 | 218 | 11kV | 436 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143224 B Phase 10 A Fuse replaced. Storms the previous evening. No Cause Found From job 1179232: CHECKED CUSTOMERS SWITCHBOARD AFTER REPLACING HV DOF FROM LIGHTNING STRIKE AND FOUND 3 PHASE MAIN CB TO SUB BOARD OPEN CCT ON 1 PHASE ON LOAD SIDE . CUSTOMER DECLINED SERVICE TO REPAIR. LEFT CB OFF FOR SAFETY. | November | 2014 | 2015Q2 | 2015 | 232:33413 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2014-11-25 | N | 218 | N | 15 | N | N | 1.1101 | 39.4971 | 318.6159
[7 empty] | 12729 | 4451 | 1179423 | 2014-11-25 15:00 | 2014-11-25 18:35 | 215 | 11kV | 215 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143227 10A Substation DOLF Operated. Storms the previous evening | November | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-11-25 | N | 215 | N | 15 | N | N | 1.1101 | 39.4971 | 157.1157
[7 empty] | 14668 | 20267 | 1179445 | 2014-11-25 18:03 | 2014-11-25 23:00 | 297 | 11kV | 297 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 143230 B Phase 10A DOLF Operated Replaced B Phase Lightning Arrestor | November | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-11-25 | N | 297 | N | 15 | N | N | 1.1101 | 39.4971 | 217.0388
[7 empty] | 12612 | 3301 | 1179758 | 2014-11-26 14:10 | 2014-11-26 16:39 | 149 | 11kV | 149 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 1179758 Broken Live Line Clamp | November | 2014 | 2015Q2 | 2015 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Not Veg | 2014-11-26 | N | 149 | N | 1 | N | N | 1.1101 | 39.4971 | 108.8848
[7 empty] | 12439 | 1705 | 1179880 | 2014-11-27 01:57 | 2014-11-27 03:22 | 85 | 11kV | 56483 | 756 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN 9550 Gwawley Bay - Pnl 36 - A and B phase OC, Earth leakage, EFI. Dead possum at UGOH for S 9954. ME: 1180544. REst Step: 1180545. Withdrawn: 1179880. | November | 2014 | 2015Q2 | 2015 | ZN9550:PA36 | ZN9550:PA36 | ZN09550/000036 | SUTHERLAND | OH | Not Veg | 2014-11-27 | N | 74.713 | N | 6 | N | N | 1.1101 | 39.4971 | 41276.1104
[7 empty] | 14381 | 17765 | 1179887 | 2014-11-27 03:35 | 2014-11-27 05:47 | 132 | 11kV | 160332 | 1464 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9037 Miranda - Pnl 10 - Trip/reclose/trip, A phase IOC, Lockout, timing, EFI, Field EFIs. Front line feeder fault just out of zone. Field EFIs gave false indication of fault location. ME: 1180546. Rest Step: 1180547. Withdrawn: 1179887, 1180261. | November | 2014 | 2015Q2 | 2015 | ZN9037:PA10 | ZN9037:PA10 | ZN09037/000010 | SUTHERLAND | UG | Not Veg | 2014-11-27 | N | 109.5164 | N | 6 | N | N | 1.1101 | 39.4971 | 117165.8966
[7 empty] | 14379 | 17760 | 1179985 | 2014-11-27 08:40 | 2014-11-27 10:49 | 129 | 11kV | 2322 | 18 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | At CP560 Peebles Nollands Tripped on on Overload. Suspect Faulty Tx at PT2078 - Failed On Restoration of planned interruption Also planned interruption record - see OMS 1192177 | November | 2014 | 2015Q2 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Not Veg | 2014-11-27 | N | 129 | N | 6 | N | N | 1.1101 | 39.4971 | 1696.8491
[7 empty] | 13426 | 10368 | 1179963 | 2014-11-27 09:20 | 2014-11-27 11:19 | 119 | 11kV | 192729 | 1711 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | S1610 Homebush Bay Panel 19 "evans Asia" fdr tripped Relays - Overcurrent, Earth fault, EFI Signals- Tx2 Group Earth. EFI's: S36068, S6305, S4805, S4790, S3019, S2071, S4804, S4820 Remarks: UG fault. Feeder fault from S4820 Theile Pereira Sw/B to S4819 Konrads Hawkes Sw/B | November | 2014 | 2015Q2 | 2015 | ZN1610:PA19 | ZN1610:PA19 | ZN01610/000019 | PARRAMATTA | UG | Not Veg | 2014-11-27 | N | 112.6411 | N | 6 | N | N | 1.1101 | 39.4971 | 140840.6687
[7 empty] | 13300 | 9127 | 1179968 | 2014-11-27 12:00 | 2014-11-27 13:45 | 105 | 11kV | 210 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 143262 C phase DOLF : 10 Amp Excluded OMS 1179968 | November | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2014-11-27 | N | 105 | N | 6 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 12790 | 4937 | 1180044 | 2014-11-27 11:50 | 2014-11-27 17:10 | 320 | 11kV | 320 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 143259 A phase DOLF : 10 Amp 11kV Arrestor Note: customer at 27/11/2014 14:15 was also affected by T&R on device HC42028 | November | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-11-27 | N | 320 | N | 6 | N | N | 1.1101 | 39.4971 | 233.8466
[7 empty] | 14394 | 17869 | 1180273 | 2014-11-28 06:13 | 2014-11-28 07:20 | 67 | 11kV | 201 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143267 Single phase DOLF : 10 Amp Excluded OMS 1180273 | November | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-11-28 | N | 67 | N | 4 | N | N | 1.1101 | 39.4971 | 146.8849
[7 empty] | 12748 | 4599 | 1180533 | 2014-11-28 15:20 | 2014-11-28 16:30 | 70 | 11kV | 490 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143270 A phase DOLF : 20 Amp Excluded OMS 1180533 | November | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-11-28 | N | 70 | N | 4 | N | N | 1.1101 | 39.4971 | 358.0775
[7 empty] | 12609 | 3279 | 1180584 | 2014-11-28 17:54 | 2014-11-28 22:00 | 246 | 11kV | 246 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143273 A & C phase DOLF : 10 Amp Excluded OMS 1180584 | November | 2014 | 2015Q2 | 2015 | 206:34432 | 206:34432 | ZN00206/034432 | LAKE MACQUARIE | OH | Veg | 2014-11-28 | N | 246 | N | 4 | N | N | 1.1101 | 39.4971 | 179.7695
[7 empty] | 14031 | 15300 | 1180621 | 2014-11-28 23:47 | 2014-11-29 04:07 | 260.7667 | 11kV | 198964.9667 | 763 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 143274 car hit pole HQ-92375 section isolated for repairs no protection operation Excluded OMS 1180595 | November | 2014 | 2015Q2 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2014-11-28 | N | 260.7667 | N | 4 | N | N | 1.1101 | 39.4971 | 145397.7292
[7 empty] | 14560 | 19161 | 1180671 | 2014-11-29 11:07 | 2014-11-29 12:11 | 63.5667 | 11kV | 5004.8 | 87 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 143277 B phase DOLF : 40 Amp Suspected fuse fatigue Excluded 1180675 | November | 2014 | 2015Q2 | 2015 | 256:80646 | 256:80646 | ZN00256/080646 | NEWCASTLE | OH | Not Veg | 2014-11-29 | N | 57.5264 | N | 4 | N | N | 1.1101 | 39.4971 | 3657.3602
[7 empty] | 13776 | 13116 | 1180705 | 2014-11-29 16:19 | 2014-11-29 16:30 | 11 | 11kV | 16082 | 1462 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ ZN.15011 Beacon Hill 11kV Panel 10L Feeder tripped on SEL Cause:- Unknown ME:-1180705 | November | 2014 | 2015Q2 | 2015 | ZN15011:PA10 | ZN15011:PA10 | ZN15011/000010 | NORTHERN BEACHES | OH | Not Veg | 2014-11-29 | N | 11 | N | 4 | N | N | 1.1101 | 39.4971 | 11752.2513
[7 empty] | 14037 | 15342 | 1180746 | 2014-11-29 21:05 | 2014-11-29 22:44 | 99 | 11kV | 195017 | 2231 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ ZN.15001 Brookvale 11kV Panel 2 tripped on:- 2L Earth Fault Field EFI's:- S.16706, S.16845, S.16802, S.17129, S.16888, S.17067, S.17110, S.16990 Cause:- 11kV UG Cable fault between S.16690 SW/B, S.17007 SW/A and S.16318 SW/B ME:-1180985 RS:-1180987, 1180988 GIS Model Error:-1180748, 1180747 Withdrawn:-1180746 | November | 2014 | 2015Q2 | 2015 | ZN15001:PA2 | ZN15001:PA2 | ZN15001/000002 | NORTHERN BEACHES | UG | Not Veg | 2014-11-29 | N | 87.4124 | N | 4 | N | N | 1.1101 | 39.4971 | 142512.6716
[7 empty] | 14294 | 17204 | 1180739 | 2014-11-29 21:39 | 2014-11-30 13:55 | 976 | 11kV | 976 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 143278 Single phase Staff suspect DOLF's and damage done duringa recent storm the customer had been away and returned to find they had no supply. TX FAULTY. | November | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Not Veg | 2014-11-29 | N | 976 | N | 4 | N | N | 1.1101 | 39.4971 | 713.232
[7 empty] | 14167 | 16266 | 1181109 | 2014-11-30 15:49 | 2014-11-30 16:39 | 50 | 11kV | 65050 | 1301 | HV | Equipment Failed in Service | Equipment Failure | Recloser / Sectionaliser | Unplanned | Electrical Storm | N | LID 143282 1 fault operation 3 phase Instantaneous Overcurrent Fdr reclose off for SI 44213 | November | 2014 | 2015Q2 | 2015 | 507:80917 | 507:80917 | ZN00507/080917 | CESSNOCK | OH | Not Veg | 2014-11-30 | N | 50 | N | 14 | N | N | 1.1101 | 39.4971 | 47536.6213
[7 empty] | 12409 | 1482 | 1180844 | 2014-11-30 15:49 | 2014-11-30 16:46 | 57 | 11kV | 37107 | 651 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143283 1 fault operation A & C phase Instantaneous Overcurrent PROT 50 T AC; RECLOSE OFF FOR SI 44213 | November | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2014-11-30 | N | 57 | N | 14 | N | N | 1.1101 | 39.4971 | 27116.7011
[7 empty] | 14467 | 18457 | 1180822 | 2014-11-30 14:13 | 2014-11-30 17:05 | 172 | 11kV | 1204 | 7 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex Zn12630 Peats Ridge section of Pa1 PT11857 Collins George 11kv HDO footpath 16 amp fuse operated Storm at time of failure no damage visisble. Lightining See 1181025 exclude 1180822,38 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-11-30 | N | 172 | N | 14 | N | N | 1.1101 | 39.4971 | 879.8477
[7 empty] | 13162 | 8066 | 1181728 | 2014-11-30 16:10 | 2014-11-30 17:15 | 65 | 11kV | 37765 | 581 | HV | Customer Installation Fault | Customer Installation | DC Not Transformer | Unplanned | No Weather Impact | N | LID 143289 Dist fuse :1000 Amp customers bus tie CB was closed tripping both LVF 264 & LVF 6734 UG LV CCT 264 Fault | November | 2014 | 2015Q2 | 2015 | 202:34238 43 48 | 202:34238 43 48 | ZN00202/34238 43 48 | NEWCASTLE | Unknown | Unknown | 2014-11-30 | N | 65 | N | 14 | N | N | 1.1101 | 39.4971 | 27597.5481
[7 empty] | 12519 | 2455 | 1180819 | 2014-11-30 15:49 | 2014-11-30 18:30 | 161 | 11kV | 1610 | 10 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 143288 SECTION ISOLATED TO REPAIR BURNT OFF TAPPING ABS 41013 AND WIRE OFF PIN POLE FR 40018 Excluded OMS 1180819; 11800924; 1180881 | November | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-11-30 | N | 161 | N | 14 | N | N | 1.1101 | 39.4971 | 1176.5405
[7 empty] | 14514 | 18815 | 1180858 | 2014-11-30 16:11 | 2014-11-30 19:50 | 219 | 11kV | 4818 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143286 3 phase DOLF : 20 Amp FDR ISOLATED TO REPAIR MAINS NEAR SUB 52073 | November | 2014 | 2015Q2 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2014-11-30 | N | 219 | N | 14 | N | N | 1.1101 | 39.4971 | 3520.8523
[7 empty] | 13145 | 7959 | 1180861 | 2014-11-30 16:18 | 2014-11-30 20:38 | 260 | 11kV | 520 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Lightning | N | Ex Zn12630 Peats Ridge Panel 1 PT11858 Collins George 11kv HDO roadside 16 amp fuse operated Storm at time of failure See 1180893 exclude 1180861 CC1: 22-"Refer to SOp" | November | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-11-30 | N | 260 | N | 14 | N | N | 1.1101 | 39.4971 | 380.0007
[7 empty] | 12360 | 1020 | 1181212 | 2014-11-30 16:11 | 2014-11-30 21:30 | 319 | 11kV | 8294 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143294 3 Phase DOLF : 40 Amp | November | 2014 | 2015Q2 | 2015 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2014-11-30 | N | 319 | N | 14 | N | N | 1.1101 | 39.4971 | 6061.0106
[7 empty] | 14392 | 17859 | 1180926 | 2014-11-30 20:48 | 2014-11-30 22:06 | 78 | 11kV | 41262 | 529 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" RE45189 Cooks PEats Ridge 0.5 tripped and locked out Heavy rain at time fo failure. Possum trying to get out of rain took short cut and flashed over outside 100 glenworth rd, Lower Mangrove. Overhead mains to inspect for damage in daylight See 1180926 Exclude 1180929 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2014-11-30 | N | 78 | N | 14 | N | N | 1.1101 | 39.4971 | 30153.0526
[7 empty] | 14444 | 18252 | 1180882 | 2014-11-30 17:40 | 2014-11-30 22:20 | 280 | 11kV | 46670 | 216 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143292 ohm down at pole HQ-81455 section isolated to make repairs | November | 2014 | 2015Q2 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2014-11-30 | N | 216.0648 | N | 14 | N | N | 1.1101 | 39.4971 | 34105.0595
[7 empty] | 13231 | 8594 | 1180936 | 2014-11-30 21:56 | 2014-11-30 22:38 | 41.7167 | 11kV | 11638.95 | 279 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Ex Zn35370 Galston Panel 8 Recloser CP554 Arcadia Rosscommon tripped reclosed tripped and locked out on Overcurrent Cause: Tree branch found on Tee off to PT656 - Branch removed by DOp See OMS 1180939 1180952 1180936 CC1: 22-"Refer to SOp" | November | 2014 | 2015Q2 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2014-11-30 | N | 41.7167 | N | 14 | N | N | 1.1101 | 39.4971 | 8505.4014
[7 empty] | 12490 | 2174 | 1180951 | 2014-11-30 22:00 | 2014-11-30 23:15 | 75 | 11kV | 225 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143291 A phase DOLF : 10 Amp Excluded OMS 1180951 | November | 2014 | 2015Q2 | 2015 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2014-11-30 | N | 75 | N | 14 | N | N | 1.1101 | 39.4971 | 164.4234
[7 empty] | 13352 | 9749 | 1180935 | 2014-11-30 21:53 | 2014-11-30 23:42 | 109 | 11kV | 109 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn8000 Macquarie Park LB2672 AB2141 Footpath phase 11kV bond found burnt off See OMS 1181304 1180935 | November | 2014 | 2015Q2 | 2015 |  |  |  | WILLOUGHBY | OH | Not Veg | 2014-11-30 | N | 109 | N | 14 | N | N | 1.1101 | 39.4971 | 79.654
[7 empty] | 12793 | 4955 | 1180879 | 2014-12-01 01:24 | 2014-12-01 02:55 | 91 | 11kV | 5096 | 56 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 143293 section isolated to make repairs at pole JR-55048 Excluded OMS 1180961 | December | 2014 | 2015Q2 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2014-12-01 | N | 91 | N | 24 | Y | Y | 1.1101 | 39.4971 | 3724.0065
[7 empty] | 14246 | 16889 | 1181128 | 2014-12-01 11:15 | 2014-12-01 12:00 | 45 | 11kV | 2025 | 45 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge Pa1 "Grants Rd" had low volts At 30/11/2014 20:58 11kv tee off to PT135247 Williams George 2.9 had burnt bond off on A phase - see OMS 1181528 then at 01/12/14 11:15 11kv from AB44188 to end of feeder interrupted to repair rusted connections to tee off to PT13527 See 1181528 2nd 1181529 exclude 1180930,1002,128 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-12-01 | N | 45 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1479.8103
[7 empty] | 14619 | 19875 | 1180930 | 2014-11-30 20:58 | 2014-12-01 12:10 | 912 | 11kV | 2736 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge Pa1 "Grants Rd" had low volts 11kv tee off to PT135247 Williams George 2.9 had burnt bond off on A phase 2nd Event 11kv from AB44188 to end of feeder interrupted to repair rusted connections to tee off to PT13527 See 1181528 2nd 1181529 exclude 1180930,1002,128 | November | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-11-30 | N | 912 | N | 14 | N | N | 1.1101 | 39.4971 | 1999.3881
[7 empty] | 13989 | 14826 | 1181161 | 2014-12-01 12:11 | 2014-12-01 13:54 | 103 | 11kV | 342 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | Zn2568 St Peters - 11kV feeder panel 8 tripped on: Overcurrent, Fault Check, EFI Field EFIs: NIL Cause not ascertained see 1181486 1181487 1181488 | December | 2014 | 2015Q2 | 2015 | ZN2568:PA8 | ZN2568:PA8 | ZN02568/000008 | SYDNEY | UG | Not Veg | 2014-12-01 | N | 85.5 | N | 24 | Y | Y | 1.1101 | 39.4971 | 249.9235
[7 empty] | 13529 | 11110 | 1181101 | 2014-12-01 10:38 | 2014-12-01 14:45 | 247 | 11kV | 741 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143301 DOLF : 10 Amp Excluded OMS 1181101 | December | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 247 | N | 24 | Y | Y | 1.1101 | 39.4971 | 541.5009
[7 empty] | 14597 | 19596 | 1181269 | 2014-12-01 15:28 | 2014-12-01 15:39 | 11 | 11kV | 26210 | 2464 | HV | Staff Operation | Utility Process Issue | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | ZN 9252 Jannali - Tx 1C - Busbar protection C phase High Impedance. T/Pe inadvertantly cracked incorrect protection link in preparation for the reforming of Pnl 31. Both Pnls 28 and 30 tripped as well. ME: 1187867. Rest Step: 1187868. Withdrawn: 1181266, 69, 83. | December | 2014 | 2015Q2 | 2015 | ZN9252:PA8 | ZN9252:PA31 | ZN09252/000031 | SUTHERLAND | Exclude | Not Veg | 2014-12-01 | N | 10.6372 | N | 24 | Y | Y | 1.1101 | 39.4971 | 19153.4949
[7 empty] | 12470 | 1905 | 1182021 | 2014-12-01 17:23 | 2014-12-01 17:33 | 10 | 11kV | 1208 | 604 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143306 Trip & reclose 1 fault operation Earth fault | December | 2014 | 2015Q2 | 2015 |  |  |  | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 2 | N | 24 | Y | Y | 1.1101 | 39.4971 | 882.7708
[7 empty] | 13532 | 11133 | 1181196 | 2014-12-01 13:23 | 2014-12-01 17:40 | 257 | 11kV | 514 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143303 A phase DOLF : 10 Amp Excluded OMS 1181196 | December | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-12-01 | N | 257 | N | 24 | Y | Y | 1.1101 | 39.4971 | 375.616
[7 empty] | 14624 | 19921 | 1181349 | 2014-12-01 17:26 | 2014-12-01 18:35 | 69 | 11kV | 345 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143308 fuse size 20amp no cause found - storm conditions refer OMS 1181349 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 69 | N | 24 | Y | Y | 1.1101 | 39.4971 | 252.1158
[7 empty] | 14479 | 18547 | 1182029 | 2014-12-01 18:53 | 2014-12-01 19:12 | 19 | 11kV | 345 | 175 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143312 Trip & reclose 1 fault operation Overcurrent | December | 2014 | 2015Q2 | 2015 |  |  |  | MUSWELLBROOK | OH | Veg | 2014-12-01 | N | 1.9714 | N | 24 | Y | Y | 1.1101 | 39.4971 | 252.1158
[7 empty] | 13863 | 13805 | 1182037 | 2014-12-01 18:56 | 2014-12-01 19:26 | 30 | 11kV | 275 | 139 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143313 Trip & reclose 1 fault operation Overcurrent | December | 2014 | 2015Q2 | 2015 |  |  |  | MUSWELLBROOK | OH | Veg | 2014-12-01 | N | 1.9784 | N | 24 | Y | Y | 1.1101 | 39.4971 | 200.9619
[7 empty] | 14153 | 16197 | 1181366 | 2014-12-01 18:07 | 2014-12-01 19:45 | 98.0667 | 11kV | 2059.4 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143314 fuse size 16 amp no cause found - storm conditions | December | 2014 | 2015Q2 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 98.0667 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1504.9488
[7 empty] | 12414 | 1520 | 1181260 | 2014-12-01 16:32 | 2014-12-01 21:05 | 273 | 11kV | 2184 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143315 OHM down at P: CQ-40343, broken X-arm Excluded OMS 1181313 | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-12-01 | N | 273 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1596.0028
[7 empty] | 12696 | 4125 | 1181569 | 2014-12-01 16:11 | 2014-12-01 21:30 | 319 | 11kV | 8294 | 26 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143294 3 phase DOLF : 40 Amp | December | 2014 | 2015Q2 | 2015 | 526:34639 | 526:34639 | ZN00526/034639 | CESSNOCK | OH | Veg | 2014-12-01 | N | 319 | N | 24 | Y | Y | 1.1101 | 39.4971 | 6061.0106
[7 empty] | 13484 | 10820 | 1181400 | 2014-12-01 19:33 | 2014-12-01 22:00 | 147.2167 | 11kV | 2061.0333 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143321 DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 147.2167 | N | 24 | Y | Y | 1.1101 | 39.4971 | 1506.1424
[7 empty] | 12725 | 4432 | 1181398 | 2014-12-01 19:30 | 2014-12-01 22:00 | 150 | 11kV | 150 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143322 DOLF : 3 Amp excluded OMS 1181398 | December | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Veg | 2014-12-01 | N | 150 | N | 24 | Y | Y | 1.1101 | 39.4971 | 109.6156
[7 empty] | 12865 | 5665 | 1181411 | 2014-12-01 20:40 | 2014-12-01 22:05 | 85 | 11kV | 1105 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143324 A & C phase : 20 Amp Excluded OMS 1181411 & 1181413 | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 85 | N | 24 | Y | Y | 1.1101 | 39.4971 | 807.5014
[7 empty] | 13864 | 13820 | 1181386 | 2014-12-01 18:56 | 2014-12-01 22:20 | 204 | 11kV | 408 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143328 A phase DOLF : 10 Amp Excluded OMS 1181386 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-01 | N | 204 | N | 24 | Y | Y | 1.1101 | 39.4971 | 298.1544
[7 empty] | 12278 | 194 | 1181326 | 2014-12-01 17:00 | 2014-12-01 22:55 | 355 | 11kV | 94530 | 281 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143331 no fault found - please patrol feeder Excluded oms 1181326 & 1181338 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-01 | N | 336.4057 | N | 24 | Y | Y | 1.1101 | 39.4971 | 69079.7358
[7 empty] | 13729 | 12763 | 1181405 | 2014-12-01 20:06 | 2014-12-01 23:00 | 174 | 11kV | 522 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143325 A phase DOLF : 10 Amp Excluded OMS 1181405 | December | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-12-01 | N | 174 | N | 24 | Y | Y | 1.1101 | 39.4971 | 381.4622
[7 empty] | 12987 | 6727 | 1181420 | 2014-12-01 21:34 | 2014-12-01 23:05 | 91 | 11kV | 91 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143327 DOLF 10 Amp Excluded OMS 1181420 | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-12-01 | N | 91 | N | 24 | Y | Y | 1.1101 | 39.4971 | 66.5001
[7 empty] | 14571 | 19238 | 1181403 | 2014-12-01 19:59 | 2014-12-01 23:20 | 201 | 11kV | 201 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143330 DOLF : 10 Amp Excluded job OMS 1181403 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-01 | N | 201 | N | 24 | Y | Y | 1.1101 | 39.4971 | 146.8849
[7 empty] | 13384 | 10009 | 1181433 | 2014-12-02 00:36 | 2014-12-02 01:14 | 38 | 11kV | 36214 | 953 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | U/G Cable | Unplanned | No Weather Impact | N | S1850 Bass Hill Panel 10 "Bellevue Birdwood" fdr tripped Relays - A and C phase overcurrent Signals - 1kkv trip Remarks: Cause not ascertained. No cause found | December | 2014 | 2015Q2 | 2015 | ZN1850:PA10 | ZN1850:PA40 | ZN01850/000040 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-12-02 | N | 38 | N | 16 | N | N | 1.1101 | 39.4971 | 26464.1231
[7 empty] | 14399 | 17930 | 1181419 | 2014-12-01 21:31 | 2014-12-02 01:45 | 254 | 11kV | 5588 | 22 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 132332 3 phase DOLF : 10 Amp replaced 3 x LA's, 3 x DOLF's Excluded oms 1181425 & 1181419 | December | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Not Veg | 2014-12-01 | N | 254 | N | 24 | Y | Y | 1.1101 | 39.4971 | 4083.5456
[7 empty] | 14368 | 17652 | 1181388 | 2014-12-01 19:05 | 2014-12-02 02:10 | 425 | 11kV | 1275 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 143333 DOLF : 10 Amp replaced faulty tx Excluded oms 1181388 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-12-01 | N | 425 | N | 24 | Y | Y | 1.1101 | 39.4971 | 931.7324
[7 empty] | 12581 | 3113 | 1181481 | 2014-12-02 07:31 | 2014-12-02 09:45 | 134 | 11kV | 268 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143336 DOLF : 10 Amp Excluded OMS 1181481 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-02 | N | 134 | N | 16 | N | N | 1.1101 | 39.4971 | 195.8465
[7 empty] | 12689 | 4033 | 1181540 | 2014-12-02 11:00 | 2014-12-02 11:55 | 55 | 11kV | 55 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143345 A phase DOLF : 10 Amp Excluded OMS 1181540 | December | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2014-12-02 | N | 55 | N | 16 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 13135 | 7866 | 1181593 | 2014-12-02 08:00 | 2014-12-02 12:25 | 265 | 11kV | 265 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143346 A phase DOLF : 10 Amp Excluded OMS 1181593 | December | 2014 | 2015Q2 | 2015 | 807:74180 | 807:74180 | ZN00807/074180 | MUSWELLBROOK | OH | Veg | 2014-12-02 | N | 265 | N | 16 | N | N | 1.1101 | 39.4971 | 193.6542
[7 empty] | 13625 | 11924 | 1181428 | 2014-12-01 22:52 | 2014-12-02 12:31 | 819 | 11kV | 819 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 143348 Single phase DOLF : 10 Amp FAULTY TX. Excluded OMS REPORT NO 1181428. | December | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2014-12-01 | N | 819 | N | 24 | Y | Y | 1.1101 | 39.4971 | 598.501
[7 empty] | 12256 | 23 | 1170466 | 2014-12-02 07:08 | 2014-12-02 15:32 | 504 | 11kV | 1512 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Bond | Unplanned | Lightning | N | Repaired Hv tapping at Fuses 40778 | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-12-02 | N | 504 | N | 16 | N | N | 1.1101 | 39.4971 | 1104.925
[7 empty] | 13732 | 12786 | 1182215 | 2014-12-02 10:00 | 2014-12-02 15:45 | 345 | 11kV | 345 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 143351 Fault Tx replaced | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-12-02 | N | 345 | N | 16 | N | N | 1.1101 | 39.4971 | 252.1158
[7 empty] | 14604 | 19729 | 1181798 | 2014-12-02 15:55 | 2014-12-02 16:00 | 5 | 11kV | 55 | 11 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143350 Tree found leaning against OHM adj sub 71811 | December | 2014 | 2015Q2 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2014-12-02 | N | 5 | N | 16 | N | N | 1.1101 | 39.4971 | 40.1924
[7 empty] | 14231 | 16764 | 1181817 | 2014-12-02 16:18 | 2014-12-02 21:07 | 289 | 11kV | 83527 | 590 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | At ZN35500 Top Ryde Panel 18 tripped on Signals: 11 KV Trip, Group Earth Zone Earth Relays Earth fault, EFI and Fault Check. Abnormal Switching: SW/B Closed @ S8258, AB Open and defective. Cause: Cable Fault on Panel 18 at ZN35500 Top Ryde Between SW/B - SW/B at S6350 - SW/A at S2303 and SW/A at S8258 See OMS 1182246 1182247 1181817 1181824 1181917 | December | 2014 | 2015Q2 | 2015 | ZN35500:PA18 | ZN35500:PA18 | ZN35500/000018 | RYDE | UG | Not Veg | 2014-12-02 | N | 141.5712 | N | 16 | N | N | 1.1101 | 39.4971 | 61039.068
[7 empty] | 12671 | 3903 | 1181937 | 2014-12-02 19:33 | 2014-12-02 22:00 | 147 | 11kV | 124656 | 848 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143359 A & C phase Overcurrent; Sensitive Earth Fault Reclose set to non-auto due to bush fire defects | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-12-02 | N | 147 | N | 16 | N | N | 1.1101 | 39.4971 | 91094.9281
[7 empty] | 13633 | 11988 | 1181803 | 2014-12-02 15:59 | 2014-12-02 22:50 | 411 | 11kV | 2055 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 143353 No protection operations. Txf found overheating & bubbling. Changed for 63kVA under AP. Excluded OMS1181803 | December | 2014 | 2015Q2 | 2015 | 232:33413 | 232:33407 | ZN00232/033407 | PORT STEPHENS | OH | Not Veg | 2014-12-02 | N | 411 | N | 16 | N | N | 1.1101 | 39.4971 | 1501.7334
[7 empty] | 13080 | 7473 | 1181969 | 2014-12-02 22:16 | 2014-12-02 23:35 | 79 | 11kV | 158 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" @PT12183 Reservoir Grants 0.8 10Amp roadside HDO operated Lightning in area at time of failure, all restored ok no further action required See 1182971 exclude 1181969 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA13 | ZN12630/000013 | CENTRAL COAST | OH | Veg | 2014-12-02 | N | 79 | N | 16 | N | N | 1.1101 | 39.4971 | 115.4617
[7 empty] | 13974 | 14709 | 1181934 | 2014-12-02 19:26 | 2014-12-02 23:50 | 264 | 11kV | 1056 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143363 DOLF Excluded OMS 1181934 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-02 | N | 264 | N | 16 | N | N | 1.1101 | 39.4971 | 771.6937
[7 empty] | 14289 | 17162 | 1181963 | 2014-12-02 21:19 | 2014-12-03 01:05 | 226 | 11kV | 1356 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143364 C phase DOLF : 10 Amp Excluded OMS 1181963 | December | 2014 | 2015Q2 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2014-12-02 | N | 226 | N | 16 | N | N | 1.1101 | 39.4971 | 990.9248
[7 empty] | 12428 | 1621 | 1181948 | 2014-12-02 20:17 | 2014-12-03 01:35 | 317.7667 | 11kV | 3813.2 | 12 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143365 DOLF : 3 Amp CASS 24767; 24773 | December | 2014 | 2015Q2 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2014-12-02 | N | 317.7667 | N | 16 | N | N | 1.1101 | 39.4971 | 2786.5741
[7 empty] | 12341 | 822 | 1181980 | 2014-12-03 01:54 | 2014-12-03 03:11 | 77 | 11kV | 29081 | 413 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12570 Avoca Panel 26 fdr CB tripped on: Relays: 50TB, 150Tn Signals: Trip EFI's: Nil Mains to Patrol Feeder Cause: Lightning See 1182998,9 exclude 1181980 | December | 2014 | 2015Q2 | 2015 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Not Veg | 2014-12-03 | N | 70.414 | N | 28 | Y | Y | 1.1101 | 39.4971 | 21251.5371
[7 empty] | 12720 | 4317 | 1181942 | 2014-12-02 20:12 | 2014-12-03 05:10 | 538 | 11kV | 538 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143366 A phase DOLF : 10 Amp cass 24768 A - 0.5A B - 1.5A C - 22A | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-12-02 | N | 538 | N | 16 | N | N | 1.1101 | 39.4971 | 393.1545
[7 empty] | 14227 | 16726 | 1182096 | 2014-12-03 09:49 | 2014-12-03 10:05 | 16 | 11kV | 3792 | 237 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of pa14 @RE45181 Mcpherson rd tripped on overcurrent Cause: cross circulating current in Tx Switching for darow 350415 See 1183045 exclude 1182096,9,106,15 | December | 2014 | 2015Q2 | 2015 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Not Veg | 2014-12-03 | N | 16 | N | 28 | Y | Y | 1.1101 | 39.4971 | 2771.0818
[7 empty] | 12393 | 1376 | 1181836 | 2014-12-02 16:44 | 2014-12-03 10:08 | 1044.0667 | 11kV | 217165.8667 | 208 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Ex Panel of Zn2400 Berowra - Auto link 46854 tripped Cause: Suspect lightning strike See OMS 1181836 - 1181901 CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2014-12-02 | N | 1044.0667 | N | 16 | N | N | 1.1101 | 39.4971 | 158698.4101
[7 empty] | 13881 | 13934 | 1182043 | 2014-12-03 08:16 | 2014-12-03 10:10 | 114 | 11kV | 228 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143371 Single phase DOLF : 3 Amp Excluded OMS 1182043 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-03 | N | 114 | N | 28 | Y | Y | 1.1101 | 39.4971 | 166.6157
[7 empty] | 13240 | 8660 | 1181984 | 2014-12-03 05:36 | 2014-12-03 12:10 | 394 | 11kV | 1182 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Ex Zn12600 Lisarow section Pa2 "Chamberlain Taylor" @PT14479 The Ridgeway Paroo centre & roadside phase 16k Suspected lightning strikes overnight See 1183015 exclude 1181984,2137 | December | 2014 | 2015Q2 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2014-12-03 | N | 394 | N | 28 | Y | Y | 1.1101 | 39.4971 | 863.7707
[7 empty] | 14538 | 19011 | 1182121 | 2014-12-03 05:36 | 2014-12-03 12:25 | 409 | 11kV | 7771 | 19 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Rain Wind Storm | N | Ex Zn12600 Lisarow section Pa2 "Chamberlain Taylor" @PT13986 The Ridgeway Paroo 1.5 centre & roadside phase 16k Suspected lightning strikes overnight.Mains to check crossarm intergrity at PT | December | 2014 | 2015Q2 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2014-12-03 | N | 409 | N | 28 | Y | Y | 1.1101 | 39.4971 | 5678.8176
[7 empty] | 13661 | 12190 | 1182255 | 2014-12-03 13:51 | 2014-12-03 15:00 | 69 | 11kV | 276 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143381 A phase DOLF : 10 Amp Excluded OMS 1182255 | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-12-03 | N | 69 | N | 28 | Y | Y | 1.1101 | 39.4971 | 201.6927
[7 empty] | 13203 | 8448 | 1182105 | 2014-12-03 10:05 | 2014-12-03 15:50 | 345 | 11kV | 345 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143382 Single phase DOLF : 10 Amp Excluded OMS 1182105 | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-12-03 | N | 345 | N | 28 | Y | Y | 1.1101 | 39.4971 | 252.1158
[7 empty] | 14566 | 19188 | 1182541 | 2014-12-03 18:36 | 2014-12-03 19:21 | 45 | 11kV | 15480 | 344 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S702 Bayview Point - Failed explosivley causing - Zn.711 Blackwattle Bay Pnl. 16 tripping on: A & C Phase O/C, EFI (Restored 3/12/14 @ 19:22) Zn 711 Blackwattle Bay P.3 tripping on : Earth Fault, EFI (Restored 3/12/14 @ 19:21) S702 has an open point between feeders 3 & 16. Sub rebuilt and restored 4/12/14 @ 19:30 See 1185347 1185348 1185349 | December | 2014 | 2015Q2 | 2015 | ZN711:PA3 | ZN7481:PA21 | ZN07481/000021 | SYDNEY | UG | Not Veg | 2014-12-03 | N | 45 | N | 28 | Y | Y | 1.1101 | 39.4971 | 11312.3274
[7 empty] | 13588 | 11619 | 1182536 | 2014-12-03 18:33 | 2014-12-03 19:22 | 49 | 11kV | 882 | 18 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S702 Bayview Point - Failed explosivley causing - Zn.711 Blackwattle Bay Pnl. 16 tripping on: A & C Phase O/C, EFI (Restored 3/12/14 @ 19:22) Zn 711 Blackwattle Bay P.3 tripping on : Earth Fault, EFI (Restored 3/12/14 @ 19:21) S702 has an open point between feeders 3 & 16. Sub rebuilt and restored 4/12/14 @ 19:30 See 1185347 1185348 1185349 | December | 2014 | 2015Q2 | 2015 | ZN711:PA16 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2014-12-03 | N | 49 | N | 28 | Y | Y | 1.1101 | 39.4971 | 644.5396
[7 empty] | 12803 | 5054 | 1182296 | 2014-12-03 14:47 | 2014-12-03 20:00 | 313 | 11kV | 26225 | 160 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 143399 2 fault operations Truck brought down OHM at T-off to sub 54026 Broke Rd X McDonalds Rd Pokolbin Excluded OMS 1182296, 1182342,1182443. | December | 2014 | 2015Q2 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-12-03 | N | 163.9062 | N | 28 | Y | Y | 1.1101 | 39.4971 | 19164.4565
[7 empty] | 14594 | 19536 | 1182415 | 2014-12-03 16:53 | 2014-12-03 20:20 | 207 | 11kV | 129716 | 826 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | At S35370 Galston Panel 10 tripped, reclosed tripped and locked out on A and C phase IOC, EFI Lockout and Time delay. Cause: AB482 Open. SW/B at S8401 Closed. Cause: Tree branch on OH mains. See OMS 1182854 1182859 1182858 1182876 1182415/2417/2418/2422/2423/2424/2429/2440/2444/2489 | December | 2014 | 2015Q2 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2014-12-03 | N | 157.0412 | N | 28 | Y | Y | 1.1101 | 39.4971 | 94792.6268
[7 empty] | 13165 | 8084 | 1182628 | 2014-12-03 19:46 | 2014-12-03 20:30 | 44 | 11kV | 53944 | 1376 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn2466 Flemington; 11kv feeder Panel No 45 "Crescent Richmond No1" tripped Relays: C phase timed O/C, EFI, Fault check Field EFI's: S5609, S7607, S35238, S35355, S8692 Signals: No3 grp earth, Zone earth, 11kv trip Remarks: UG fault. Suspect 11kv feeder fault between S-8692 Henley Arthur Sw/B and S2725 Howard Arthur Sw/A. Haz RMI at S2725 feeder to be extended. | December | 2014 | 2015Q2 | 2015 | ZN2466:PA45 | ZN36000:PA7 | ZN36000/000007 | STRATHFIELD | UG | Not Veg | 2014-12-03 | N | 39.2035 | N | 28 | Y | Y | 1.1101 | 39.4971 | 39420.6841
[7 empty] | 12869 | 5703 | 1182352 | 2014-12-03 15:47 | 2014-12-03 20:45 | 298 | 11kV | 135285 | 810 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143380 2 fault operations B & C phase Overcurrent Branch on mains pole JS-37035. Excluded OMS # 1182352. SI n0580. | December | 2014 | 2015Q2 | 2015 | 264:81232 | 264:81232 | ZN00264/081232 | PORT STEPHENS | OH | Veg | 2014-12-03 | N | 167.0185 | N | 28 | Y | Y | 1.1101 | 39.4971 | 98862.2878
[7 empty] | 12424 | 1594 | 1182468 | 2014-12-03 17:38 | 2014-12-03 20:50 | 192 | 11kV | 21119 | 136 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Lightning | N | At S35370 Galston Panel 4 from Recloser 555 Arcadia Parked Opened. Cause: PT1297 Charltons Bay Footpaths surge arrestors See OMS 1185121 1185125 1185126 1185127 1182468 1182548 | December | 2014 | 2015Q2 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2014-12-03 | N | 155.2868 | N | 28 | Y | Y | 1.1101 | 39.4971 | 15433.1423
[7 empty] | 12596 | 3198 | 1182483 | 2014-12-03 17:54 | 2014-12-03 20:50 | 176 | 11kV | 7452 | 58 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 143391 2 fault operation A & C phases Overcurrent | December | 2014 | 2015Q2 | 2015 | 227:13014 | 227:13014 | ZN00227/013014 | LAKE MACQUARIE | OH | Not Veg | 2014-12-03 | N | 128.4828 | N | 28 | Y | Y | 1.1101 | 39.4971 | 5445.7018
[7 empty] | 14178 | 16314 | 1182485 | 2014-12-03 17:29 | 2014-12-03 21:20 | 231 | 11kV | 180050 | 1042 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @Zn1290 Leightonfield 11kv Panel 12 "S-3043 Miller Bill No.1" tripped re-closed tripped and locked out on Relays - A & C ph IOC, A & C ph timed Signals: 11kv trip Field EFI's Remarks: cause not ascertained. Mains to patrol in daylight | December | 2014 | 2015Q2 | 2015 | ZN1290:PA12 | ZN1290:PA12 | ZN01290/000012 | CANTERBURY-BANKSTOWN | OH | Veg | 2014-12-03 | N | 172.7927 | N | 28 | Y | Y | 1.1101 | 39.4971 | 131575.2294
[7 empty] | 13554 | 11354 | 1182595 | 2014-12-03 19:13 | 2014-12-03 22:00 | 167 | 11kV | 501 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143402 DOLF : 10 Amp Replaced 2 arrestors Excluded OMS 1182595 | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-12-03 | N | 167 | N | 28 | Y | Y | 1.1101 | 39.4971 | 366.116
[7 empty] | 14472 | 18505 | 1182484 | 2014-12-03 17:44 | 2014-12-03 22:50 | 306 | 11kV | 65306.2 | 222 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Lightning | N | EX S847 Hornsby Panel 47 Footpath 11kV Bond at AB1337 Burnt off and Welded onto a different Phase. The above outage effected the volts at S4485 and PT2478 See OMS 1182475 1182484 | December | 2014 | 2015Q2 | 2015 | ZN847:PA47 | ZN847:PA47 | ZN00847/000047 | HORNSBY | OH | Not Veg | 2014-12-03 | N | 294.1721 | N | 28 | Y | Y | 1.1101 | 39.4971 | 47723.8448
[7 empty] | 13238 | 8646 | 1182578 | 2014-12-03 19:00 | 2014-12-04 00:15 | 315 | 11kV | 315 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143403 DOLF : 10 Amp Replace blown arrestors Excluded OMS 1182578 | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Not Veg | 2014-12-03 | N | 315 | N | 28 | Y | Y | 1.1101 | 39.4971 | 230.1927
[7 empty] | 14171 | 16274 | 1182610 | 2014-12-03 19:33 | 2014-12-04 00:20 | 287 | 11kV | 861 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143405 C phase DOLF 10 Amp Excluded OMS 1182610 | December | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-12-03 | N | 287 | N | 28 | Y | Y | 1.1101 | 39.4971 | 629.1934
[7 empty] | 14306 | 17277 | 1182608 | 2014-12-03 19:28 | 2014-12-04 00:45 | 316.7 | 11kV | 5067.2 | 16 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | LID 143404 B & C phase DOLF also repaired stranded mains beyond | December | 2014 | 2015Q2 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2014-12-03 | N | 316.7 | N | 28 | Y | Y | 1.1101 | 39.4971 | 3702.9603
[7 empty] | 13860 | 13770 | 1182600 | 2014-12-03 19:18 | 2014-12-04 02:25 | 427 | 11kV | 2135 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143408 C phase DOLF : 10 Amp Excluded OMS 1182600 | December | 2014 | 2015Q2 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2014-12-03 | N | 427 | N | 28 | Y | Y | 1.1101 | 39.4971 | 1560.195
[7 empty] | 12610 | 3292 | 1182694 | 2014-12-03 22:13 | 2014-12-04 02:51 | 278 | 11kV | 2780 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143409 A phase DOLF : 40 Amp Excluded OMS 1182694 | December | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2014-12-03 | N | 278 | N | 28 | Y | Y | 1.1101 | 39.4971 | 2031.542
[7 empty] | 14380 | 17762 | 1182501 | 2014-12-03 18:13 | 2014-12-04 03:40 | 567 | 11kV | 3360 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143401 B phase DOLF : 31 Amp Excluded OMS 1182501 & 1182705 | December | 2014 | 2015Q2 | 2015 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2014-12-03 | N | 336 | N | 28 | Y | Y | 1.1101 | 39.4971 | 2455.3889
[7 empty] | 14042 | 15367 | 1182605 | 2014-12-03 19:23 | 2014-12-04 03:55 | 512 | 11kV | 2560 | 5 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143412 Replaced faulty lightning arrestors Excluded OMS 1182681 & 1182605 | December | 2014 | 2015Q2 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2014-12-03 | N | 512 | N | 28 | Y | Y | 1.1101 | 39.4971 | 1870.7725
[7 empty] | 13213 | 8500 | 1182447 | 2014-12-03 17:19 | 2014-12-04 04:30 | 671 | 11kV | 671 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143413 A phase DOLF : 10 Amp Excluded OMS 1182447 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-03 | N | 671 | N | 28 | Y | Y | 1.1101 | 39.4971 | 490.347
[7 empty] | 12261 | 49 | 1182732 | 2014-12-04 06:39 | 2014-12-04 07:45 | 66 | 11kV | 66 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143415 A phase DOLF : 10 Amp Excluded OMS 1182732 | December | 2014 | 2015Q2 | 2015 | 227:13015 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Veg | 2014-12-04 | N | 66 | N | 11 | N | N | 1.1101 | 39.4971 | 48.2309
[7 empty] | 13307 | 9186 | 1182757 | 2014-12-04 07:56 | 2014-12-04 08:55 | 59 | 11kV | 59 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143416 A phase DOLF : 10 Amp Excluded OMS 1182757 | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-12-04 | N | 59 | N | 11 | N | N | 1.1101 | 39.4971 | 43.1155
[7 empty] | 12633 | 3523 | 1182713 | 2014-12-03 19:46 | 2014-12-04 10:05 | 859 | 11kV | 859 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143419 C phase DOLF : 63 Amp | December | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80923 | ZN00507/080923 | CESSNOCK | OH | Veg | 2014-12-03 | N | 859 | N | 28 | Y | Y | 1.1101 | 39.4971 | 627.7319
[7 empty] | 14596 | 19585 | 1182716 | 2014-12-04 04:28 | 2014-12-04 11:00 | 392 | 11kV | 1567.1667 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT2281 Charltons MacFarlane 16A HDO blown ex Panel 4 Galston Cause: HVDO fuse operated - No cause found. See OMS 1186476 1182716 | December | 2014 | 2015Q2 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2014-12-04 | N | 391.7917 | N | 11 | N | N | 1.1101 | 39.4971 | 1145.2392
[7 empty] | 14466 | 18456 | 1183089 | 2014-12-04 15:22 | 2014-12-04 17:05 | 103 | 11kV | 309 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge section of Pa1 "Grants Rd" fdr PT14248 Ky9ola Mangrove Dam 1.1 Roadside phase 16Amp HDO fuse operated Cause: unknown See 1183599 exclude 1183089,121 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Veg | 2014-12-04 | N | 103 | N | 11 | N | N | 1.1101 | 39.4971 | 225.8081
[7 empty] | 14263 | 16978 | 1183140 | 2014-12-04 17:44 | 2014-12-04 18:04 | 20 | 11kV | 6400 | 320 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143429 1 fault operation Overcurrent Feeder did not reclose as it was disabled for operating work. B. Blackadder was attempting to replace DOLF at PT. 70722 Kingslyn. TX needs replacement. | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-04 | N | 20 | N | 11 | N | N | 1.1101 | 39.4971 | 4676.9312
[7 empty] | 13370 | 9855 | 1182519 | 2014-12-03 18:25 | 2014-12-04 19:30 | 1505 | 11kV | 442470 | 294 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S702 Bayview Point - Failed explosivley causing - Zn.711 Blackwattle Bay Pnl. 16 tripping on: A & C Phase O/C, EFI (Restored 3/12/14 @ 19:22) Zn 711 Blackwattle Bay P.3 tripping on : Earth Fault, EFI (Restored 3/12/14 @ 19:21) S702 has an open point between feeders 3 & 16. Sub rebuilt and restored 4/12/14 @ 19:30 See 1185347 1185348 1185349 | December | 2014 | 2015Q2 | 2015 | ZN711:PA16 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2014-12-03 | N | 1505 | N | 28 | Y | Y | 1.1101 | 39.4971 | 323344.0253
[7 empty] | 12616 | 3331 | 1183141 | 2014-12-04 17:00 | 2014-12-04 20:05 | 185 | 11kV | 185 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 143430 Single phase DOLF : 10 Amp Defective Transformer | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-04 | N | 185 | N | 11 | N | N | 1.1101 | 39.4971 | 135.1925
[7 empty] | 12877 | 5807 | 1183201 | 2014-12-04 18:43 | 2014-12-04 21:15 | 152 | 11kV | 456 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143432 A phase DOLF : 10 Amp suspected lightning | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-04 | N | 152 | N | 11 | N | N | 1.1101 | 39.4971 | 333.2314
[7 empty] | 12631 | 3500 | 1183203 | 2014-12-04 18:50 | 2014-12-04 21:30 | 160 | 11kV | 160 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143431 Single DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-04 | N | 160 | N | 11 | N | N | 1.1101 | 39.4971 | 116.9233
[7 empty] | 13312 | 9315 | 1183231 | 2014-12-04 22:26 | 2014-12-05 00:17 | 111 | 11kV | 135376 | 1278 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Electrical Storm | N | Zn35900 Potts Hill Panel 1 "hume Rock, Rookwood rd" fdr tripped Relays: Earth Fault, EFI Signals: 11kv trip, Zone Earth, Tx1 Group Earth EFI's: S3741 S5220 S6513 S222 suspected UG Fault between S5222 to S36006 to S6596 See 1185470,1 Exclude 1183231 | December | 2014 | 2015Q2 | 2015 | ZN35900:PA1 | ZN35900:PA1 | ZN35900/000001 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-12-04 | N | 105.928 | N | 11 | N | N | 1.1101 | 39.4971 | 98928.7879
[7 empty] | 12291 | 350 | 1183254 | 2014-12-04 22:43 | 2014-12-05 02:01 | 198 | 11kV | 198 | 1 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | At S.15015 North Head, Zone Earth plus an efi down on Panel 15 At CP.1623 B and C phase fuses operated - suspect lightning strike CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 |  |  |  | NORTHERN BEACHES | OH | Not Veg | 2014-12-04 | N | 198 | N | 11 | N | N | 1.1101 | 39.4971 | 144.6926
[7 empty] | 12627 | 3463 | 1183229 | 2014-12-04 21:59 | 2014-12-05 02:43 | 284 | 11kV | 3976 | 14 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143434 A phase DOLF : 10 Amp Excluded OMS 1183229 Suspected lightning | December | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Not Veg | 2014-12-04 | N | 284 | N | 11 | N | N | 1.1101 | 39.4971 | 2905.5435
[7 empty] | 14232 | 16773 | 1183281 | 2014-12-05 05:50 | 2014-12-05 07:16 | 85.65 | 11kV | 1969.95 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143435 1 fault operation Single phase Sectionaliser Autolink would not close. Left Bypassed | December | 2014 | 2015Q2 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2014-12-05 | N | 85.65 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1439.5814
[7 empty] | 13556 | 11365 | 1183644 | 2014-12-05 16:59 | 2014-12-05 18:36 | 97 | 11kV | 52865 | 545 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S1193 Lindfield Panel 10 tripped on OC, EFI, Fault Check, TX2 Fault Check. Cause not ascertained for outage | December | 2014 | 2015Q2 | 2015 | ZN1193:PA10 | ZN1193:PA10 | ZN01193/000010 | KU-RING-GAI | OH | Veg | 2014-12-05 | N | 97 | N | 22 | Y | Y | 1.1101 | 39.4971 | 38632.1827
[7 empty] | 13785 | 13183 | 1183672 | 2014-12-05 17:41 | 2014-12-05 19:20 | 99 | 11kV | 198 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12630 Peats Ridge 11kv Panel 4 "Kulnura" fdr @PT12006 Peats Ridge Eulos right hand side 10Amp HVDO operated Fuse failure See 1184984 exclude 1183672 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Not Veg | 2014-12-05 | N | 99 | N | 22 | Y | Y | 1.1101 | 39.4971 | 144.6926
[7 empty] | 12588 | 3150 | 1183643 | 2014-12-05 16:55 | 2014-12-05 19:31 | 156 | 11kV | 103653 | 743 | HV | Lightning Strike | Adverse Weather/Environment | Cable End Box | Unplanned | Lightning | N | At S195 Pymble section of Panel 30 - Recloser CP46113 Fiddens Wharf Coronga tripped, reclosed and locked out on OC and IOC Cause: Defective Endbox at S2599. 11kV On cross arm See OMS 1185465 1185466 1183643 | December | 2014 | 2015Q2 | 2015 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | UG | Not Veg | 2014-12-05 | N | 139.5061 | N | 22 | Y | Y | 1.1101 | 39.4971 | 75746.5552
[7 empty] | 12481 | 2061 | 1183667 | 2014-12-05 17:16 | 2014-12-05 19:35 | 139 | 11kV | 33440 | 260 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser 1126 tripped, reclosed and locked out on IOC and timed OC - Cause not known | December | 2014 | 2015Q2 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Veg | 2014-12-05 | N | 128.6154 | N | 22 | Y | Y | 1.1101 | 39.4971 | 24436.9657
[7 empty] | 13459 | 10615 | 1183764 | 2014-12-05 19:49 | 2014-12-05 20:45 | 56 | 11kV | 31360 | 560 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 143505 no protection operation tapping off at UGOH pole IU-91642. Excluded oms # 1183761 | December | 2014 | 2015Q2 | 2015 | 214:8670 | 214:8667 | ZN00214/008667 | LAKE MACQUARIE | OH | Not Veg | 2014-12-05 | N | 56 | N | 22 | Y | Y | 1.1101 | 39.4971 | 22916.963
[7 empty] | 13207 | 8465 | 1183817 | 2014-12-05 21:03 | 2014-12-05 22:30 | 87.15 | 11kV | 1655.85 | 19 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143515 10 amp fuse Libe DOLF | December | 2014 | 2015Q2 | 2015 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2014-12-05 | N | 87.15 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1210.0463
[7 empty] | 12523 | 2504 | 1183743 | 2014-12-05 20:05 | 2014-12-05 23:05 | 180 | 11kV | 9720 | 54 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143533 C phase DOLF : 31 Amp | December | 2014 | 2015Q2 | 2015 | 261:81864 | 261:81864 | ZN00261/081864 | LAKE MACQUARIE | OH | Veg | 2014-12-05 | N | 180 | N | 22 | Y | Y | 1.1101 | 39.4971 | 7103.0893
[7 empty] | 14118 | 15965 | 1183848 | 2014-12-05 21:43 | 2014-12-05 23:28 | 105 | 11kV | 21606 | 252 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143518 2 fault operations 3 phase Earth fault | December | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-12-05 | N | 85.7381 | N | 22 | Y | Y | 1.1101 | 39.4971 | 15789.0275
[7 empty] | 13750 | 12905 | 1183683 | 2014-12-05 17:43 | 2014-12-05 23:49 | 366 | 11kV | 288774 | 789 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | Ex ZN 9118 Cronulla - Rec 62657 - Trip/reclose/trip, Overcurrent, lockout. Replaced 3 sets of blown lightning arrestors at PT 9679, UGOH to S 9096 and PT 9235. ME: 1183683. Withdrawn: 1183887, 8, 9. | December | 2014 | 2015Q2 | 2015 | ZN9118:PA11 | ZN9118:PA11 | ZN09118/000011 | SUTHERLAND | OH | Not Veg | 2014-12-05 | N | 366 | N | 22 | Y | Y | 1.1101 | 39.4971 | 211027.5218
[7 empty] | 14068 | 15566 | 1183818 | 2014-12-05 21:04 | 2014-12-06 00:10 | 186.2167 | 11kV | 2607.0333 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143519 Single phase DOLF : 20 Amp | December | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-12-05 | N | 186.2167 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1905.1431
[7 empty] | 12400 | 1426 | 1183836 | 2014-12-05 21:42 | 2014-12-06 00:24 | 162 | 11kV | 8424 | 52 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn1850 Bass hill section of Pa3 AB2594 burnt off roadside bond ABNORMAL: AB435 open S4898:A closed See 1186536 exclude 1183836,57 | December | 2014 | 2015Q2 | 2015 | ZN1850:PA3 | ZN3472:PA28 | ZN03472/000028 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-12-05 | N | 162 | N | 22 | Y | Y | 1.1101 | 39.4971 | 6156.0107
[7 empty] | 12469 | 1904 | 1183798 | 2014-12-05 20:39 | 2014-12-06 00:51 | 252 | 11kV | 296712 | 1263 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143522 2 fault operation A & B phase Overcurrent | December | 2014 | 2015Q2 | 2015 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2014-12-05 | N | 234.9264 | N | 22 | Y | Y | 1.1101 | 39.4971 | 216828.3781
[7 empty] | 12949 | 6448 | 1183891 | 2014-12-06 00:05 | 2014-12-06 01:15 | 70 | 11kV | 210 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143523 Single phase DOLF : 10 Amp Excluded OMS 1183891 | December | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-12-06 | N | 70 | N | 23 | Y | Y | 1.1101 | 39.4971 | 153.4618
[7 empty] | 12630 | 3493 | 1190102 | 2014-12-05 21:42 | 2014-12-06 01:27 | 225 | 11kV | 225 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143521 1 fault operation Overcurrent Could not locate OMS job | December | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-12-05 | N | 225 | N | 22 | Y | Y | 1.1101 | 39.4971 | 164.4234
[7 empty] | 12598 | 3217 | 1183864 | 2014-12-05 22:13 | 2014-12-06 02:30 | 256.2167 | 11kV | 4355.6833 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143527 B phase DOLF : 20 Amp | December | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | MAITLAND | OH | Veg | 2014-12-05 | N | 256.2167 | N | 22 | Y | Y | 1.1101 | 39.4971 | 3183.0049
[7 empty] | 12734 | 4513 | 1183854 | 2014-12-05 22:02 | 2014-12-06 02:31 | 269.1333 | 11kV | 2422.2 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143530 3 phase DOLF : 16 Amp | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-05 | N | 269.1333 | N | 22 | Y | Y | 1.1101 | 39.4971 | 1770.0723
[7 empty] | 13995 | 14898 | 1183897 | 2014-12-06 01:24 | 2014-12-06 02:38 | 74 | 11kV | 45954 | 621 | HV | Vandalism | 3rd Party Impact | Air Break Switch | Unplanned | No Weather Impact | N | Ex Zn1287 Revesby section of Pa15 fdr from AB1522to LB2039 to Pa15 interrupted after down rod disconnected and opened by local kids. Bottom section of down rod removed by DOp as only way of securing. See 1186551 exclude 1183897 | December | 2014 | 2015Q2 | 2015 | ZN1287:PA15 | ZN1287:PA15 | ZN01287/000015 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2014-12-06 | N | 74 | N | 23 | Y | Y | 1.1101 | 39.4971 | 33581.8278
[7 empty] | 12592 | 3174 | 1183795 | 2014-12-05 20:50 | 2014-12-06 03:46 | 416 | 11kV | 6929 | 17 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143529 DOLF : 20 Amp Excluded OMS 1183801 | December | 2014 | 2015Q2 | 2015 | 526:34637 | 526:34637 | ZN00526/034637 | SINGLETON | OH | Veg | 2014-12-05 | N | 407.5882 | N | 22 | Y | Y | 1.1101 | 39.4971 | 5063.5088
[7 empty] | 14312 | 17296 | 1183748 | 2014-12-05 20:01 | 2014-12-06 04:05 | 484 | 11kV | 99620 | 535 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143528 2 fault operations A & B phase Overcurrent | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-12-05 | N | 186.2056 | N | 22 | Y | Y | 1.1101 | 39.4971 | 72799.3577
[7 empty] | 13509 | 11000 | 1183729 | 2014-12-05 19:36 | 2014-12-06 04:56 | 560 | 11kV | 16055 | 98 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143526 Blown dolfs dound at subs 70446, 70097 and 70141. Overcurrent | December | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2014-12-05 | N | 163.8265 | N | 22 | Y | Y | 1.1101 | 39.4971 | 11732.5205
[7 empty] | 14007 | 14996 | 1183951 | 2014-12-06 07:25 | 2014-12-06 08:26 | 61 | 11kV | 183 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143535 A phase DOLF : 10 Amp Excluded OMS 1183951 | December | 2014 | 2015Q2 | 2015 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2014-12-06 | N | 61 | N | 23 | Y | Y | 1.1101 | 39.4971 | 133.731
[7 empty] | 13524 | 11098 | 1183968 | 2014-12-06 08:20 | 2014-12-06 08:27 | 7 | 11kV | 7 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143534 A phase DOLF : 16 Amp Excluded OMS 1183968 | December | 2014 | 2015Q2 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2014-12-06 | N | 7 | N | 23 | Y | Y | 1.1101 | 39.4971 | 5.1154
[7 empty] | 14247 | 16897 | 1183913 | 2014-12-05 21:00 | 2014-12-06 09:15 | 735 | 11kV | 2940 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143536 10 amp fuse Substation DOLF Excluded OMS 1189699 | December | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-12-05 | N | 735 | N | 22 | Y | Y | 1.1101 | 39.4971 | 2148.4653
[7 empty] | 13872 | 13886 | 1183916 | 2014-12-06 05:46 | 2014-12-06 10:10 | 264 | 11kV | 528 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 143537 B phase DOLF : 31 Amp Excluded OMS 1183916 | December | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | UG | Not Veg | 2014-12-06 | N | 264 | N | 23 | Y | Y | 1.1101 | 39.4971 | 385.8468
[7 empty] | 12792 | 4950 | 1183789 | 2014-12-05 20:40 | 2014-12-06 10:50 | 850 | 11kV | 28050 | 33 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143540 16 amp fuse Line DOLF refer also OMS 1184010 | December | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-12-05 | N | 850 | N | 22 | Y | Y | 1.1101 | 39.4971 | 20498.1127
[7 empty] | 13959 | 14638 | 1186201 | 2014-12-06 06:00 | 2014-12-06 11:20 | 320 | 11kV | 960 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143542 B phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2014-12-06 | N | 320 | N | 23 | Y | Y | 1.1101 | 39.4971 | 701.5397
[7 empty] | 12822 | 5267 | 1184002 | 2014-12-06 06:00 | 2014-12-06 12:10 | 370 | 11kV | 3330 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143544 DOLF : 16 Amp | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-06 | N | 370 | N | 23 | Y | Y | 1.1101 | 39.4971 | 2433.4658
[7 empty] | 14640 | 20070 | 1183980 | 2014-12-06 08:34 | 2014-12-06 12:10 | 216 | 11kV | 648 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143543 A phase DOLF : 10 Amp 240 Volt; 12, 17 & 3 Amp Excluded OMS 1183980 | December | 2014 | 2015Q2 | 2015 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2014-12-06 | N | 216 | N | 23 | Y | Y | 1.1101 | 39.4971 | 473.5393
[7 empty] | 13780 | 13169 | 1183940 | 2014-12-06 07:03 | 2014-12-06 12:10 | 307 | 11kV | 307 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143545 A phase DOLF : 10 Amp Excluded OMS 1183940 | December | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-12-06 | N | 307 | N | 23 | Y | Y | 1.1101 | 39.4971 | 224.3465
[7 empty] | 12625 | 3436 | 1183917 | 2014-12-06 05:47 | 2014-12-06 14:00 | 493 | 11kV | 493 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143548 A phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2014-12-06 | N | 493 | N | 23 | Y | Y | 1.1101 | 39.4971 | 360.2699
[7 empty] | 12510 | 2351 | 1183903 | 2014-12-06 01:30 | 2014-12-06 14:20 | 770 | 11kV | 20790 | 27 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC Not Transformer | Unplanned | Electrical Storm | N | LID 143546 B Phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | UG | Not Veg | 2014-12-06 | N | 770 | Y | 23 | N | Y | 1.1101 | 39.4971 | 15192.7188
[7 empty] | 12618 | 3369 | 1184055 | 2014-12-06 11:30 | 2014-12-06 14:30 | 180 | 11kV | 180 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143549 C phase DOLF : 10 Amp Excluded OMS 1184055 | December | 2014 | 2015Q2 | 2015 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Veg | 2014-12-06 | N | 180 | N | 23 | Y | Y | 1.1101 | 39.4971 | 131.5387
[7 empty] | 13347 | 9717 | 1183963 | 2014-12-06 08:15 | 2014-12-06 15:00 | 405 | 11kV | 1215 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143551 B phase DOLF : 10 Amp Excluded OMS 1183963 | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-12-06 | N | 405 | N | 23 | Y | Y | 1.1101 | 39.4971 | 887.8862
[7 empty] | 12770 | 4718 | 1183879 | 2014-12-05 22:46 | 2014-12-06 16:45 | 1079 | 11kV | 1079 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143554 A & C phase DOLF : 10 Amp Excluded OMS 1183879 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-05 | N | 1079 | N | 22 | Y | Y | 1.1101 | 39.4971 | 788.5014
[7 empty] | 13941 | 14491 | 1184037 | 2014-12-06 10:38 | 2014-12-06 17:20 | 402 | 11kV | 804 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Previous Storm | N | LID 143559 Burned tapping between LK 74744 and LLC. Isolated for safety to repair LLC and LK. | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-12-06 | N | 402 | N | 23 | Y | Y | 1.1101 | 39.4971 | 587.5395
[7 empty] | 14117 | 15949 | 1184041 | 2014-12-06 10:43 | 2014-12-06 17:26 | 403.1167 | 11kV | 12093.5 | 30 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 143560 A phase DOLF : 20 Amp Also replaced LA's at PT. 2879 Issac. | December | 2014 | 2015Q2 | 2015 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2014-12-06 | N | 403.1167 | N | 23 | Y | Y | 1.1101 | 39.4971 | 8837.5731
[7 empty] | 13051 | 7171 | 1184147 | 2014-12-06 18:12 | 2014-12-06 19:00 | 48.3333 | 11kV | 47608.3333 | 985 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At S847 Hornsby Panel 5 Tripped on B phase O/C, EFI and TX3 Fault Check Cause: Tree on CP2378 Dural Pacific | December | 2014 | 2015Q2 | 2015 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Veg | 2014-12-06 | N | 48.3333 | N | 23 | Y | Y | 1.1101 | 39.4971 | 34790.7658
[7 empty] | 13620 | 11887 | 1184042 | 2014-12-06 10:50 | 2014-12-06 19:10 | 500 | 11kV | 1500 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 143563 Soingle DOLF : 10 Amp L/A's replaced Excluded OMS 1184042 | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-12-06 | N | 500 | N | 23 | Y | Y | 1.1101 | 39.4971 | 1096.1558
[7 empty] | 13194 | 8393 | 1184160 | 2014-12-06 18:42 | 2014-12-06 20:14 | 92 | 11kV | 6716 | 73 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 143564 2 fault operations B & C phase Overcurrent Pole fire on pole DP-70522 Hedley Rd. Excluded OMS 1184160 | December | 2014 | 2015Q2 | 2015 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2014-12-06 | N | 92 | N | 23 | Y | Y | 1.1101 | 39.4971 | 4907.8547
[7 empty] | 13045 | 7118 | 1184118 | 2014-12-06 16:05 | 2014-12-06 21:30 | 325 | 11kV | 5393 | 55 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | Electrical Storm | N | LID 143565 1 fault operation Sensitive Earth Fault Fire on pT pole 72404 A Ratkai. Excluded OMS 1184118/1184119/1184143 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-06 | N | 98.0545 | N | 23 | Y | Y | 1.1101 | 39.4971 | 3941.0453
[7 empty] | 14009 | 15001 | 1183767 | 2014-12-06 20:18 | 2014-12-06 22:40 | 142 | 11kV | 106638 | 849 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143516 A & C phase Overcurrent | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-12-06 | N | 125.6042 | N | 23 | Y | Y | 1.1101 | 39.4971 | 77927.9051
[7 empty] | 12361 | 1026 | 1185883 | 2014-12-06 21:52 | 2014-12-06 23:32 | 100 | 11kV | 93100 | 931 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 143517 A & C phases Overcurent tapping burnt off at ugoh on pole IS-62401 feeder opened by sop quail 2316hrs. dq see report # 143503 | December | 2014 | 2015Q2 | 2015 | 235:2124 | 235:2124 | ZN00235/002124 | MAITLAND | OH | Not Veg | 2014-12-06 | N | 100 | N | 23 | Y | Y | 1.1101 | 39.4971 | 68034.734
[7 empty] | 14261 | 16972 | 1184155 | 2014-12-06 18:23 | 2014-12-07 00:10 | 347 | 11kV | 27501 | 98 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143566 4 fault operations 3 phase Overcurrent Tree branch 1 pole beyond AB75001. But still tripped. 11kv main off pin at pole ai50107 | December | 2014 | 2015Q2 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2014-12-06 | N | 280.6224 | N | 23 | Y | Y | 1.1101 | 39.4971 | 20096.9197
[7 empty] | 13150 | 7992 | 1184196 | 2014-12-06 21:25 | 2014-12-07 00:40 | 195 | 11kV | 4875 | 25 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143570 3 phase DOLF : 10 Amp suspected lightning Excluded OMS 1184196 | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-12-06 | N | 195 | N | 23 | Y | Y | 1.1101 | 39.4971 | 3562.5062
[7 empty] | 13196 | 8409 | 1183847 | 2014-12-06 21:35 | 2014-12-07 00:42 | 187 | 11kV | 21938 | 148 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143520 2 fault operationsd C phase Overcurrent Excluded OMS 1183847 | December | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-12-06 | N | 148.2297 | N | 23 | Y | Y | 1.1101 | 39.4971 | 16031.6433
[7 empty] | 13104 | 7691 | 1184212 | 2014-12-07 04:59 | 2014-12-07 07:23 | 144 | 11kV | 288 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 143573 Single phase DOLF : 10 Amp Note DOLF carriers are different -150 & 350MVA. Please investigate & change to make the same. Excluded OMS 1184212. | December | 2014 | 2015Q2 | 2015 | 235:2124 | 235:2124 | ZN00235/002124 | NEWCASTLE | OH | Veg | 2014-12-07 | Y | 144 | N | 13 | N | Y | 1.1101 | 39.4971 | 210.4619
[7 empty] | 13683 | 12406 | 1184289 | 2014-12-07 12:02 | 2014-12-07 13:44 | 102 | 11kV | 612 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | Y | LID 143578 3 phase DOLF : 10 Amp Excluded OMS 1184289 & 1184293 | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-12-07 | Y | 102 | N | 13 | N | Y | 1.1101 | 39.4971 | 447.2315
[7 empty] | 13552 | 11326 | 1184297 | 2014-12-07 12:27 | 2014-12-07 13:57 | 90 | 11kV | 450 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143579 A & B phase DOLF : 20 Amp | December | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-12-07 | N | 90 | N | 13 | N | N | 1.1101 | 39.4971 | 328.8467
[7 empty] | 13348 | 9726 | 1184303 | 2014-12-07 13:33 | 2014-12-07 15:00 | 87 | 11kV | 87 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 143581 A & B phase DOLF : 10 Amp Excluded OMS 1184303 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-07 | N | 87 | N | 13 | N | N | 1.1101 | 39.4971 | 63.577
[7 empty] | 14054 | 15442 | 1184431 | 2014-12-07 16:30 | 2014-12-07 17:15 | 45 | 11kV | 90 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 143613 Single phase DOLF : 3 Amp Excluded OMS 1184431 | December | 2014 | 2015Q2 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2014-12-07 | N | 45 | N | 13 | N | N | 1.1101 | 39.4971 | 65.7693
[7 empty] | 12998 | 6812 | 1184409 | 2014-12-07 16:12 | 2014-12-07 17:20 | 68 | 11kV | 68 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 143591 Single phase DOLF : 3 Amp Excluded OMS 1184409 | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-12-07 | Y | 68 | N | 13 | N | Y | 1.1101 | 39.4971 | 49.6924
[7 empty] | 14599 | 19616 | 1184484 | 2014-12-07 16:40 | 2014-12-07 17:50 | 70 | 11kV | 1330 | 19 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | Y | @PT13599 Bruce Sparks footpath HDO 20K fuse blown due to lightning @Zn14891 Wyong Pa21 "Virginia Rd" tripped and reclosed on overcurrent and earth fault - see 1185135 Timing/Lockout Relay Transformer @ B protection panel. Earth Fault check relay See 1185135 2nd 1185133 exclude 1184484 | December | 2014 | 2015Q2 | 2015 | ZN14891:PA21 | ZN14891:PA21 | ZN14891/000021 | CENTRAL COAST | OH | Not Veg | 2014-12-07 | N | 70 | N | 13 | N | N | 1.1101 | 39.4971 | 971.9248
[7 empty] | 12304 | 495 | 1184454 | 2014-12-07 16:42 | 2014-12-07 17:50 | 68.3833 | 11kV | 1436.05 | 21 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143614 Single phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-12-07 | Y | 68.3833 | N | 13 | N | Y | 1.1101 | 39.4971 | 1049.423
[7 empty] | 12457 | 1831 | 1184466 | 2014-12-07 16:49 | 2014-12-07 18:00 | 71 | 11kV | 426 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143606 Fuse size 10amp Substation DOLF OMS # 1184466 1184617 | December | 2014 | 2015Q2 | 2015 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2014-12-07 | N | 71 | N | 13 | N | N | 1.1101 | 39.4971 | 311.3082
[7 empty] | 14489 | 18602 | 1184464 | 2014-12-07 16:47 | 2014-12-07 18:35 | 108 | 11kV | 216 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 143616 Single phase DOLF : 10 Amp also refer to 1184464 | December | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-12-07 | Y | 108 | N | 13 | N | Y | 1.1101 | 39.4971 | 157.8464
[7 empty] | 13144 | 7953 | 1184512 | 2014-12-07 17:18 | 2014-12-07 18:50 | 92 | 11kV | 78872 | 997 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | ZN 10997 Sans Souci - Pnl 1 - Trip/reclose/trip, A & B phase IOC, B phase Timed OC, EFI, timing, lockout, Field EFIs. Section of UG feeder from S 10071 to open bonds tee PT10411 failed in service. ME: 1187683. Rest Step: 1187684. Withdrawn: 1184512. | December | 2014 | 2015Q2 | 2015 | ZN10997:PA1 | ZN10997:PA1 | ZN10997/000001 | BAYSIDE | UG | Not Veg | 2014-12-07 | Y | 79.1093 | N | 13 | N | Y | 1.1101 | 39.4971 | 57637.3313
[7 empty] | 13690 | 12433 | 1184401 | 2014-12-07 15:51 | 2014-12-07 19:06 | 195 | 11kV | 91585 | 710 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Electrical Storm | Y | AT S.15001 Brookvale, Panel 16 Fdr CB tripped on 51 OC relay A,B and C phase. Tree brnach on OH mains in Corrie Rd Brookvale | December | 2014 | 2015Q2 | 2015 | ZN15001:PA16 | ZN15001:PA16 | ZN15001/000016 | NORTHERN BEACHES | OH | Veg | 2014-12-07 | N | 128.993 | N | 13 | N | N | 1.1101 | 39.4971 | 66927.6167
[7 empty] | 14527 | 18930 | 1184338 | 2014-12-07 15:12 | 2014-12-07 19:10 | 238 | 11kV | 224111 | 1265 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Wind Storm | Y | At ZN965 Pennant Hills Panel 33 tripped reclosed tripped and locked out on Relays: C phase timed Overcurrent. EFI and Reclose Timing/Lockout Cause: arrestors blown at PT2217 See OMS 1188471/473/475/472/478 1184339 1184338 | December | 2014 | 2015Q2 | 2015 | ZN965:PA33 | ZN965:PA33 | ZN00965/000033 | HORNSBY | OH | Not Veg | 2014-12-07 | Y | 177.1628 | N | 13 | N | Y | 1.1101 | 39.4971 | 163773.7086
[7 empty] | 13741 | 12846 | 1184618 | 2014-12-07 18:22 | 2014-12-07 19:15 | 53.0833 | 11kV | 265.4167 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 143618 B phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-07 | Y | 53.0833 | N | 13 | N | Y | 1.1101 | 39.4971 | 193.9587
[7 empty] | 12579 | 3077 | 1184373 | 2014-12-07 17:35 | 2014-12-07 19:30 | 115 | 11kV | 273125 | 2375 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Bare | Unplanned | Lightning | Y | ZN 10999 Kogarh - Pnl 29 - A phase OC, EFI, EFC, Field EFIs. Lightning in area. | December | 2014 | 2015Q2 | 2015 | ZN10999:PA29 | ZN10999:PA29 | ZN10999/000029 | BAYSIDE | OH | Not Veg | 2014-12-07 | Y | 115 | N | 13 | N | Y | 1.1101 | 39.4971 | 199591.6942
[7 empty] | 14497 | 18655 | 1184709 | 2014-12-07 19:14 | 2014-12-07 19:55 | 41 | 11kV | 2255 | 55 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | Y | LID 143612 C phase dolf : 20 Amp Excluded OMS 1184709 & 1184735 | December | 2014 | 2015Q2 | 2015 | 258:80787 | 258:80787 | ZN00258/080787 | NEWCASTLE | OH | Veg | 2014-12-07 | Y | 41 | N | 13 | N | Y | 1.1101 | 39.4971 | 1647.8875
[7 empty] | 14219 | 16652 | 1185366 | 2014-12-07 19:25 | 2014-12-07 20:06 | 41 | 11kV | 19270 | 470 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | Y | Zn12620 Noraville Pa2 "Budgewoi" tripped and locked out on SEF, 11kv trip Cause not ascertained. Mains to patrol in daylight. Previous Storm See 1185366 exclude 1184608 | December | 2014 | 2015Q2 | 2015 | ZN12620:PA2 | ZN12620:PA2 | ZN12620/000002 | CENTRAL COAST | OH | Veg | 2014-12-07 | N | 41 | N | 13 | N | N | 1.1101 | 39.4971 | 14081.9476
[7 empty] | 13713 | 12630 | 1184706 | 2014-12-07 19:12 | 2014-12-07 20:35 | 83 | 11kV | 415 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143625 10 Amp fuse Substation DOLFOMS 1184706 | December | 2014 | 2015Q2 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2014-12-07 | N | 83 | N | 13 | N | N | 1.1101 | 39.4971 | 303.2698
[7 empty] | 13271 | 8927 | 1184657 | 2014-12-07 18:37 | 2014-12-07 20:45 | 128 | 11kV | 52576 | 547 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143624 B & C Phase OC No Reclose as Feeder is on one shot as per TOBAN rules for feeders with Defects beyond them. No SCADA on reclose. PT.19145 had Blown 10A DOLF. Replaced at 2045. | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-12-07 | Y | 96.117 | N | 13 | N | Y | 1.1101 | 39.4971 | 38420.9901
[7 empty] | 13929 | 14437 | 1186652 | 2014-12-07 19:00 | 2014-12-07 20:45 | 105 | 11kV | 525 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143627 A & B DOLF : 40 Amp Line fuse 407180 A & B phase blown. Sub fuse 51616 B phase blown Both back on same time. | December | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-12-07 | Y | 105 | N | 13 | N | Y | 1.1101 | 39.4971 | 383.6545
[7 empty] | 14393 | 17868 | 1184685 | 2014-12-07 18:59 | 2014-12-07 20:59 | 120 | 11kV | 3120 | 26 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | Y | LID 143626 A phase DOLF : 31 Amp faulty arrestors | December | 2014 | 2015Q2 | 2015 | 235:8684 | 235:8684 | ZN00235/008684 | NEWCASTLE | OH | Not Veg | 2014-12-07 | Y | 120 | N | 13 | N | Y | 1.1101 | 39.4971 | 2280.004
[7 empty] | 14685 | 20410 | 1184510 | 2014-12-07 17:10 | 2014-12-07 21:35 | 265 | 11kV | 154804 | 858 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | Y | At S.3154 St Ives Panel 11 Fdr CB tripped on A phase IOC and timed OC with H/L volt alarm and group earth. large tree in contact with OH mains Note: unable to find any signs of HV dammage to Switchboards in the surrounding area | December | 2014 | 2015Q2 | 2015 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | OH | Veg | 2014-12-07 | N | 180.4242 | N | 13 | N | N | 1.1101 | 39.4971 | 113126.1973
[7 empty] | 13400 | 10162 | 1184312 | 2014-12-07 14:03 | 2014-12-07 21:38 | 455 | 11kV | 632058 | 1392 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | Y | At S.15012 Killarney, Panel 6 Fdr CB tripped on C phase IOC, efi, frame leakage plus zone earth. UG cable fault between Panel 6 and S.16579, S.16651 and S.16570 | December | 2014 | 2015Q2 | 2015 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | UG | Not Veg | 2014-12-07 | N | 454.0647 | N | 13 | N | N | 1.1101 | 39.4971 | 461889.3438
[7 empty] | 13607 | 11762 | 1184777 | 2014-12-07 20:30 | 2014-12-07 22:50 | 140 | 11kV | 420 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | Y | LID 143631 10 Amp fuse Substation DOLF OMS 1184777 | December | 2014 | 2015Q2 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Veg | 2014-12-07 | Y | 140 | N | 13 | N | Y | 1.1101 | 39.4971 | 306.9236
[7 empty] | 14648 | 20123 | 1186660 | 2014-12-07 19:20 | 2014-12-07 23:10 | 230 | 11kV | 1150 | 5 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | Y | LID 143569 Single phase DOLF : 10 Amp sub dolf found blown due to defective arrestor at 71617. LF 74337 opened by dop due to damaged x arm near 71617 sub 1920hrs. nil oms?## DQ | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-12-07 | N | 230 | N | 13 | N | N | 1.1101 | 39.4971 | 840.3861
[7 empty] | 14039 | 15353 | 1184530 | 2014-12-07 17:32 | 2014-12-08 00:32 | 420.4833 | 11kV | 18103.6333 | 71 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | Y | LID 143629 1 fault operation A phase Overhead earth wire damaged adjacent to Mt Thorley Zn. Excluded OMS 1184530/1184806 | December | 2014 | 2015Q2 | 2015 | 515:35198 | 515:35198 | ZN00515/035198 | SINGLETON | OH | Not Veg | 2014-12-07 | Y | 254.9808 | N | 13 | N | Y | 1.1101 | 39.4971 | 13229.6013
[7 empty] | 13477 | 10750 | 1184814 | 2014-12-07 22:07 | 2014-12-08 00:56 | 169 | 11kV | 364346 | 2234 | HV | Lightning Strike | Adverse Weather/Environment | UGOH | Unplanned | Lightning | Y | ZN 10994 Mortdale - Pnl 4 - Trip/reclose/trip, EF, EFI, lockout. Lightning strike to 11kV UGOH below LK 30188. ME: 1186537. Rest Step: 1186538. Withdrawn: 1184814. | December | 2014 | 2015Q2 | 2015 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2014-12-07 | N | 163.0913 | N | 13 | N | N | 1.1101 | 39.4971 | 266253.3104
[7 empty] | 12861 | 5643 | 1184670 | 2014-12-07 16:52 | 2014-12-08 01:20 | 508 | 11kV | 25592 | 100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | CP559 Cobah Rd Tripped, reclosed tripped and locked out on O/C Cause: Large Tree branch on 11kV near AB2063. AR 92966 bust LV insulators and X arm AR 92963 mains adrift AR92964 mains adrift 1186410 1186411 1184492 | December | 2014 | 2015Q2 | 2015 | ZN35370:PA8 | ZN35370:PA8 | ZN35370/000008 | HORNSBY | OH | Veg | 2014-12-07 | Y | 255.92 | N | 13 | N | Y | 1.1101 | 39.4971 | 18701.8788
[7 empty] | 12611 | 3293 | 1184721 | 2014-12-07 19:53 | 2014-12-08 03:20 | 447 | 11kV | 15258 | 107 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | Y | LID 143628 Blown Transformer at sub 17020 | December | 2014 | 2015Q2 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Not Veg | 2014-12-07 | N | 142.5981 | N | 13 | N | N | 1.1101 | 39.4971 | 11150.0964
[7 empty] | 14501 | 18691 | 1184478 | 2014-12-07 16:50 | 2014-12-08 03:40 | 650 | 11kV | 88400 | 136 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | Y | Recloser CP555 Arcadia Park Tripped, Reclosed Tripped and Locked out on Overcurrenr Cause: Large Tree brancheson 11kV Mains on tee off to PT659 Calabash Bay | December | 2014 | 2015Q2 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2014-12-07 | Y | 650 | N | 13 | N | Y | 1.1101 | 39.4971 | 64600.1126
[7 empty] | 14362 | 17610 | 1184877 | 2014-12-08 05:38 | 2014-12-08 07:17 | 99 | 11kV | 213042 | 2202 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn3922 Drummoyne Panel 5 "Byrnes Manning" fdr tripped on: Relays: C phase IOC, EFI, Fault check Signals: Zone Group Earth 11kv trip EFI's: S36165 S7583 S7681 S7682 UG cable fault form S7682 Warayama Margaret to S7683 Margaret Warayama See 1186709,12 Exclude 1184877 | December | 2014 | 2015Q2 | 2015 | ZN3922:PA5 | ZN3922:PA5 | ZN03922/000005 | INNER WEST | UG | Not Veg | 2014-12-08 | N | 96.7493 | N | 35 | Y | Y | 1.1101 | 39.4971 | 155684.8099
[7 empty] | 14356 | 17590 | 1184801 | 2014-12-08 06:00 | 2014-12-08 08:05 | 125 | 11kV | 375 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143639 10 amp fuse Substation DOLF replaced OMS 1184801 | December | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-12-08 | N | 125 | N | 35 | Y | Y | 1.1101 | 39.4971 | 274.0389
[7 empty] | 13815 | 13381 | 1184887 | 2014-12-08 06:16 | 2014-12-08 08:30 | 134 | 11kV | 134 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Fuse | Unplanned | Previous Storm | N | LID 143641 100 amp low voltage fuse loaded as OMS 1184887 | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-12-08 | N | 134 | N | 35 | Y | Y | 1.1101 | 39.4971 | 97.9232
[7 empty] | 12388 | 1285 | 1184935 | 2014-12-08 07:00 | 2014-12-08 08:46 | 106 | 11kV | 212 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Electrical Storm | N | LID 143640 10 amp fuse Substation DOLF replaced OMS 1184935 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-08 | N | 106 | N | 35 | Y | Y | 1.1101 | 39.4971 | 154.9233
[7 empty] | 14262 | 16975 | 1184875 | 2014-12-08 04:55 | 2014-12-08 09:40 | 285 | 11kV | 11400 | 40 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143637 2 fault operations B & C phase Sectionaliser | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-08 | N | 285 | N | 35 | Y | Y | 1.1101 | 39.4971 | 8330.7838
[7 empty] | 13353 | 9750 | 1184908 | 2014-12-08 06:00 | 2014-12-08 10:05 | 245 | 11kV | 1225 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143642 20 amp fuse DORF, Line DORF replaced OMS 1184908 | December | 2014 | 2015Q2 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2014-12-08 | N | 245 | N | 35 | Y | Y | 1.1101 | 39.4971 | 895.1939
[7 empty] | 14582 | 19371 | 1184897 | 2014-12-08 07:00 | 2014-12-08 10:25 | 205 | 11kV | 615 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143643 16 amp fuse Substation DOLF replaced OMS 1184897 | December | 2014 | 2015Q2 | 2015 | 508:82575 | 508:82575 | ZN00508/082575 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 205 | N | 35 | Y | Y | 1.1101 | 39.4971 | 449.4239
[7 empty] | 14094 | 15744 | 1184995 | 2014-12-08 06:00 | 2014-12-08 10:35 | 275 | 11kV | 550 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Rain Light | N | LID 143644 10 amp fuse Substation DOLF Replaces OMS 1184995 NB; sub 70503 originally loaded on above OMS also - same fuses blown on sub 72509 Aph DOLF carrier burned in half power on 1020 on sub 70503 blown Bph DOLF 10A power on 1035 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-12-08 | N | 275 | N | 35 | Y | Y | 1.1101 | 39.4971 | 401.9238
[7 empty] | 13605 | 11748 | 1184903 | 2014-12-08 06:52 | 2014-12-08 11:15 | 262.8167 | 11kV | 2365.35 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143646 20 amp fuse Line DOLF | December | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2014-12-08 | N | 262.8167 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1728.528
[7 empty] | 12634 | 3525 | 1185120 | 2014-12-08 10:09 | 2014-12-08 12:20 | 131 | 11kV | 131 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143648 10 amp fuse Substation DOLF | December | 2014 | 2015Q2 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2014-12-08 | N | 131 | N | 35 | Y | Y | 1.1101 | 39.4971 | 95.7309
[7 empty] | 13391 | 10102 | 1184971 | 2014-12-08 12:30 | 2014-12-08 13:30 | 60 | 11kV | 4500 | 75 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143651 A phase DOLF Earth fault Excluded OMS 1184971 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-08 | N | 60 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3288.4673
[7 empty] | 14108 | 15845 | 1185183 | 2014-12-08 10:57 | 2014-12-08 14:00 | 183 | 11kV | 366 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | pole no 8M20001 high voltage fuse dropped out near telstra radio tower at mount denman lookout. feeds telstra meter no 369720 also refer to 1185183 | December | 2014 | 2015Q2 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Not Veg | 2014-12-08 | N | 183 | N | 35 | Y | Y | 1.1101 | 39.4971 | 267.462
[7 empty] | 13147 | 7964 | 1185044 | 2014-12-08 09:25 | 2014-12-08 15:00 | 335 | 11kV | 209375 | 625 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn 10994 Mortdale - Pnl 4 - Interrupted for safety. Bond burnt off at AB 31100. Supply interrupted at AB 30349 to allow for repairs. ME: 1187258. Withdrawn: 1185044, 214. | December | 2014 | 2015Q2 | 2015 | ZN10994:PA4 | ZN10994:PA4 | ZN10994/000004 | GEORGES RIVER | OH | Not Veg | 2014-12-08 | N | 335 | N | 35 | Y | Y | 1.1101 | 39.4971 | 153005.0745
[7 empty] | 13985 | 14805 | 1185308 | 2014-12-08 12:58 | 2014-12-08 15:07 | 128.8 | 11kV | 19062.4 | 148 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143672 2 fault operations A & c phase Overcurrent | December | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2014-12-08 | N | 128.8 | N | 35 | Y | Y | 1.1101 | 39.4971 | 13930.2397
[7 empty] | 12464 | 1867 | 1185468 | 2014-12-08 15:01 | 2014-12-08 16:43 | 101.55 | 11kV | 1320.15 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143670 Single phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-08 | N | 101.55 | N | 35 | Y | Y | 1.1101 | 39.4971 | 964.7267
[7 empty] | 14557 | 19134 | 1185531 | 2014-12-08 15:28 | 2014-12-08 17:08 | 100 | 11kV | 80000 | 800 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | At S1673 Turramurra Pa2 Tripped on A and B phase Overcurrent and Earth Fault Cause Not ascertained (lightning at the time) Note Customer at 88 Roland Ave, reports large tree has fallen in dist wires. | December | 2014 | 2015Q2 | 2015 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2014-12-08 | N | 100 | N | 35 | Y | Y | 1.1101 | 39.4971 | 58461.6404
[7 empty] | 12362 | 1027 | 1185398 | 2014-12-08 14:13 | 2014-12-08 18:00 | 227.15 | 11kV | 2044.35 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143662 16 amp fuse Line DOLF Includes OMS 1185439 CC1: 06-"Urgent - O.H Mains - No others" | December | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-12-08 | N | 227.15 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1493.9507
[7 empty] | 13380 | 9973 | 1185606 | 2014-12-08 16:19 | 2014-12-08 18:00 | 101 | 11kV | 707 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143665 10 amp fuse Substation DOLF Aph LA cutaway, Maitland afternoon shift advised replaced OMS 1185606 (linked to wrong sub) | December | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 101 | N | 35 | Y | Y | 1.1101 | 39.4971 | 516.6547
[7 empty] | 12491 | 2183 | 1185482 | 2014-12-08 14:39 | 2014-12-08 18:20 | 221 | 11kV | 30197 | 175 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143685 2 fault operation 3 Phase Sensitive Earth Fault Faulty Tx sub 13065, struck by lightning | December | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-12-08 | N | 172.5543 | N | 35 | Y | Y | 1.1101 | 39.4971 | 22067.0769
[7 empty] | 12870 | 5708 | 1185687 | 2014-12-08 17:46 | 2014-12-08 18:27 | 41 | 11kV | 71791 | 1751 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143656 5 fault operations Trees growing into mains Crossarm Multiple trips Tree on ohn pole IU-61583 RELAYS 51 AB LARGE BRANCH ON DISTRIBUTION WIRES, LOUD BANG AND FLASH BEFORE POWER WENT OUT. LOCATED IN FRONT OF EVANS OVAL | December | 2014 | 2015Q2 | 2015 | 261:81870 | 261:81870 | ZN00261/081870 | LAKE MACQUARIE | OH | Veg | 2014-12-08 | N | 41 | N | 35 | Y | Y | 1.1101 | 39.4971 | 52462.7453
[7 empty] | 13329 | 9544 | 1185653 | 2014-12-08 17:11 | 2014-12-08 18:55 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 143666 Single phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-08 | N | 104 | N | 35 | Y | Y | 1.1101 | 39.4971 | 76.0001
[7 empty] | 13363 | 9813 | 1185389 | 2014-12-08 14:11 | 2014-12-08 19:00 | 289.0167 | 11kV | 4335.25 | 15 | HV | Lightning Strike | Adverse Weather/Environment | DC Transformer | Unplanned | Lightning | N | LID 143668 40 amp fuse Substation DOLF Replaced faulty TX at sub 72027 wallarah Road sub. amalgamated with OMS 1185389 blwon TX from direct lightning strreike to pole CC1: 06-"Urgent - O.H Mains - No others" | December | 2014 | 2015Q2 | 2015 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | UG | Not Veg | 2014-12-08 | N | 289.0167 | N | 35 | Y | Y | 1.1101 | 39.4971 | 3168.0728
[7 empty] | 13066 | 7348 | 1185676 | 2014-12-08 17:36 | 2014-12-08 19:50 | 134 | 11kV | 119934 | 1077 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143695 2 fault operation B & C phase Overcurrent Tree into OHM at pole HU-90064 Excluded 1185676, 1185700 | December | 2014 | 2015Q2 | 2015 | 224:80340 | 224:80340 | ZN00224/080340 | LAKE MACQUARIE | OH | Veg | 2014-12-08 | N | 111.3593 | N | 35 | Y | Y | 1.1101 | 39.4971 | 87644.2297
[7 empty] | 12874 | 5753 | 1187035 | 2014-12-08 14:37 | 2014-12-08 19:51 | 314 | 11kV | 24318 | 90 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143680 2 fault operations 3 phase Sensitive Earth Fault Tree into OHM adj sub 42581 | December | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 270.2 | N | 35 | Y | Y | 1.1101 | 39.4971 | 17770.8771
[7 empty] | 13577 | 11523 | 1185682 | 2014-12-08 17:43 | 2014-12-08 20:05 | 142 | 11kV | 305016 | 2148 | HV | Lightning Strike | Adverse Weather/Environment | Pole | Unplanned | Electrical Storm | N | LID 143661 2 fault operations Also refer OMS 1185732 + 1185756 prot 50TAB UGOH LA pole JU-70278, LV X arm sub 150 | December | 2014 | 2015Q2 | 2015 | 261:81879 | 261:81879 | ZN00261/081879 | LAKE MACQUARIE | OH | Not Veg | 2014-12-08 | N | 142 | N | 35 | Y | Y | 1.1101 | 39.4971 | 222896.6964
[7 empty] | 14235 | 16798 | 1185808 | 2014-12-08 21:27 | 2014-12-08 22:50 | 83 | 11kV | 249 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143698 10 amp fuse Substation DOLF replaced OMS 1185808 | December | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 83 | N | 35 | Y | Y | 1.1101 | 39.4971 | 181.9619
[7 empty] | 14481 | 18554 | 1185418 | 2014-12-08 14:26 | 2014-12-08 23:00 | 514 | 11kV | 41645 | 227 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143694 2 fault operations Tree brought down OHM adj sub 52630, branch on OHM sub 5472 Excluded OMS 1185418, 1185642, 1185436, 1185441 ## | December | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 183.4581 | N | 35 | Y | Y | 1.1101 | 39.4971 | 30432.9377
[7 empty] | 13761 | 12963 | 1185035 | 2014-12-08 15:09 | 2014-12-08 23:25 | 496 | 11kV | 102909 | 809 | HV | Lightning Strike | Adverse Weather/Environment | Air Break Switch | Unplanned | No Weather Impact | N | At S35370 Galston Zn Pa10 Pa10 Opened By AOp Abnormal switching: IR50015 Quarry Old Northern Open(Tripped) - SW/A at S8401 Closed - CP487 Open and Defective Cause: Lightning at CP498 See OMS 1187008 1187014 1185542 1185553 1185564 1185605 | December | 2014 | 2015Q2 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2014-12-08 | N | 127.2052 | N | 35 | Y | Y | 1.1101 | 39.4971 | 75202.8619
[7 empty] | 14069 | 15567 | 1185645 | 2014-12-08 17:01 | 2014-12-08 23:30 | 389 | 11kV | 21860 | 94 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143689 2 fault operations 3 phase Earth fault HV & LV OHM down between poles EV-41702 & EV-41704. Excluded OMS No. 1185645 + 1185661 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-08 | N | 232.5532 | N | 35 | Y | Y | 1.1101 | 39.4971 | 15974.6432
[7 empty] | 13896 | 14097 | 1185449 | 2014-12-08 14:41 | 2014-12-09 | 559 | 11kV | 21987 | 56 | HV | Wind Blown Debris | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143693 2 fault operations Earth Fault; Overcurrent Mains down adj sub 23184, tree into OHM adj sub 26237, corrugated iron into OHM near sub 16320 Excluded OMS 1185449, 1185495 | December | 2014 | 2015Q2 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 392.625 | N | 35 | Y | Y | 1.1101 | 39.4971 | 16067.4511
[7 empty] | 13947 | 14573 | 1185625 | 2014-12-08 16:35 | 2014-12-09 00:10 | 455 | 11kV | 455 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143696 replaced OMS 1185625 Broken lead LLC to DOLF | December | 2014 | 2015Q2 | 2015 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Veg | 2014-12-08 | N | 455 | N | 35 | Y | Y | 1.1101 | 39.4971 | 332.5006
[7 empty] | 14456 | 18367 | 1185516 | 2014-12-08 15:24 | 2014-12-09 01:04 | 580 | 11kV | 322351 | 1287 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Zn847 Hornsby Pa21 tripped, reclosed and locked out on Tree branch brought down overhead HV into LV at Amor st, Hornsby Surge Diverter blown at UGOH to AB2702 See 1190123,5 Exclude 1185516,672,776,9,93 | December | 2014 | 2015Q2 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2014-12-08 | N | 250.467 | N | 35 | Y | Y | 1.1101 | 39.4971 | 235564.6031
[7 empty] | 14670 | 20280 | 1185764 | 2014-12-08 12:25 | 2014-12-09 01:25 | 780 | 11kV | 10140 | 13 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Previous Storm | N | LID 143697 Broken insulator & OHM hanging low. Fdr remained on Excluded OMS 1185820, 1185809,1185764,1185796 | December | 2014 | 2015Q2 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Not Veg | 2014-12-08 | N | 780 | Y | 35 | N | Y | 1.1101 | 39.4971 | 7410.0129
[7 empty] | 13133 | 7853 | 1185848 | 2014-12-09 00:01 | 2014-12-09 08:25 | 504 | 11kV | 1512 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143703 C phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-12-09 | N | 504 | N | 11 | N | N | 1.1101 | 39.4971 | 1104.925
[7 empty] | 12755 | 4632 | 1185843 | 2014-12-09 07:18 | 2014-12-09 11:25 | 247 | 11kV | 247 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143707 10 amp fuse Substation DOLF replaced OMS 1185843 | December | 2014 | 2015Q2 | 2015 | 524:33572 | 522:83124 | ZN00522/083124 | CESSNOCK | OH | Veg | 2014-12-09 | N | 247 | N | 11 | N | N | 1.1101 | 39.4971 | 180.5003
[7 empty] | 12996 | 6791 | 1186022 | 2014-12-09 07:00 | 2014-12-09 11:55 | 295 | 11kV | 2360 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143711 31 amp fuse Substation DOLF replaced OMS 1186022 replaced dolf on sub 53592 31.5A | December | 2014 | 2015Q2 | 2015 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Veg | 2014-12-09 | N | 295 | N | 11 | N | N | 1.1101 | 39.4971 | 1724.6184
[7 empty] | 12356 | 995 | 1185788 | 2014-12-08 20:47 | 2014-12-09 12:00 | 913 | 11kV | 2498.7667 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Previous Storm | N | PT.1969 Vision Valley End - Foofpath phase 16k HDO blew Cause:- Storm ME:-1187090 GIS Model Error:-1185788 | December | 2014 | 2015Q2 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Not Veg | 2014-12-08 | N | 832.9222 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1826.025
[7 empty] | 12647 | 3725 | 1186051 | 2014-12-08 14:36 | 2014-12-09 12:40 | 1324 | 11kV | 16051 | 49 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143673 2 fault operations 3 phase Sensitive Earth Fault; Earth Fault Faulty Tx sub 20985, struck by lightning Excluded OMS 1185444 | December | 2014 | 2015Q2 | 2015 | 508:82578 | 508:82578 | ZN00508/082578 | PORT STEPHENS | OH | Not Veg | 2014-12-08 | N | 327.5714 | N | 35 | Y | Y | 1.1101 | 39.4971 | 11729.5974
[7 empty] | 13094 | 7609 | 1186923 | 2014-12-09 12:05 | 2014-12-09 13:05 | 60 | 11kV | 180 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143714 Line DOLF 11Kv main on crossarm at pole 5G-50086 | December | 2014 | 2015Q2 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2014-12-09 | N | 60 | N | 11 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 13321 | 9448 | 1187327 | 2014-12-09 13:16 | 2014-12-09 14:00 | 44 | 11kV | 1584 | 366 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 143717 OMS 1186140sw 47754 opened to allow staff to remove tree from mains pole IQ-41579 LVF ISOLATED AT SUB 26791 FOR LV MAINS REPAIR | December | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Veg | 2014-12-09 | N | 4.3279 | N | 11 | N | N | 1.1101 | 39.4971 | 1157.5405
[7 empty] | 12489 | 2169 | 1186315 | 2014-12-09 18:21 | 2014-12-09 19:45 | 84 | 11kV | 84 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143722 10 amp fuse Substation DOLF LOaded as OMS 1186315 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-09 | N | 84 | N | 11 | N | N | 1.1101 | 39.4971 | 61.3847
[7 empty] | 13337 | 9631 | 1186308 | 2014-12-09 17:53 | 2014-12-09 20:00 | 127 | 11kV | 635 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143723 10 amp fuse Substation DOLF | December | 2014 | 2015Q2 | 2015 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Veg | 2014-12-09 | N | 127 | N | 11 | N | N | 1.1101 | 39.4971 | 464.0393
[7 empty] | 14256 | 16943 | 1189101 | 2014-12-09 20:51 | 2014-12-09 21:05 | 14 | 11kV | 1032 | 132 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 143727 Feeder de-energised to offload burning ABS 74648. | December | 2014 | 2015Q2 | 2015 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2014-12-09 | N | 7.8182 | N | 11 | N | N | 1.1101 | 39.4971 | 754.1552
[7 empty] | 13693 | 12444 | 1186316 | 2014-12-09 20:45 | 2014-12-09 21:30 | 45 | 11kV | 45 | 1 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143728 replaced OMS 1186316 Replaced burnt up LVF assembly | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2014-12-09 | N | 45 | N | 11 | N | N | 1.1101 | 39.4971 | 32.8847
[7 empty] | 13767 | 13051 | 1186375 | 2014-12-09 22:18 | 2014-12-09 23:28 | 70 | 11kV | 6639 | 132 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 143729 Bypass burning up ABS 74647. excluded OMS No. 1186375 | December | 2014 | 2015Q2 | 2015 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2014-12-09 | N | 50.2955 | N | 11 | N | N | 1.1101 | 39.4971 | 4851.5854
[7 empty] | 14233 | 16775 | 1186332 | 2014-12-09 19:23 | 2014-12-09 23:35 | 252 | 11kV | 13626 | 173 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ S.4702 Campbell Clyde - 11kV A phase 40A EMP OC10M fuse operated tripping RMI Cause:- Tree/branch on OH mains ME:-1187731 SE:-1187733 GIS Model Error:-1186336 Withdrawn:-1186380, 1186379, 1186342, 1186338, 1186378, 1186381, 1186332 | December | 2014 | 2015Q2 | 2015 | ZN1673:PA2 | ZN1673:PA2 | ZN01673/000002 | KU-RING-GAI | OH | Veg | 2014-12-09 | N | 78.763 | N | 11 | N | N | 1.1101 | 39.4971 | 9957.4789
[7 empty] | 13971 | 14693 | 1186416 | 2014-12-10 08:00 | 2014-12-10 10:15 | 135 | 11kV | 135 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143735 3 amp fuse Substation DOLF Issued from depot | December | 2014 | 2015Q2 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2014-12-10 | N | 135 | N | 16 | N | N | 1.1101 | 39.4971 | 98.654
[7 empty] | 14096 | 15761 | 1186597 | 2014-12-10 12:29 | 2014-12-10 13:40 | 71 | 11kV | 284 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143742 10 amp fuse Substation DOLF replaces OMS 1186597 Tx volts: 247V | December | 2014 | 2015Q2 | 2015 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2014-12-10 | N | 71 | N | 16 | N | N | 1.1101 | 39.4971 | 207.5388
[7 empty] | 13894 | 14069 | 1185452 | 2014-12-08 14:49 | 2014-12-10 15:31 | 2922.1167 | 33kV Distribution | 1578 | 18 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 143652 2 fault operations Overcurrent; Earth Fault wires down, tapping burnt off A Prot = O/C E/F A/B/C & Multitrip B Prot = O/C E/F 51B 51N & Multitrip | December | 2014 | 2015Q2 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2014-12-08 | N | 87.6667 | N | 35 | Y | Y | 1.1101 | 39.4971 | 1153.1559
[7 empty] | 14107 | 15843 | 1186703 | 2014-12-10 15:45 | 2014-12-10 16:21 | 36 | 11kV | 38916 | 1081 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | ZN 10994 Mortdale - Pnl 3 - Trip/reclose/trip, A & B phase IOC, lockout. Trees on OH near Rosa and Wonoona, Oatley. Removed by DOp and OH. | December | 2014 | 2015Q2 | 2015 | ZN10994:PA3 | ZN10994:PA3 | ZN10994/000003 | GEORGES RIVER | OH | Veg | 2014-12-10 | N | 36 | N | 16 | N | N | 1.1101 | 39.4971 | 28438.665
[7 empty] | 14533 | 18976 | 1186702 | 2014-12-10 15:40 | 2014-12-10 18:05 | 145 | 11kV | 181004 | 1564 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2196 Milperra Panel 5 fdr tripped, reclosed and locked out Relays: C phase IOC and timed overcurrent, fault check, EFI, Lockout & timing relays Signals: 11kv trip, Zone earth, #3Group Earth EFI's: S8696 S5487 S35865 11kB UGOH adj PT1896 11kv Ug fault from S35865 to AB3077 tee PT1896 See 1187105,8,9 Exclude 1186702 | December | 2014 | 2015Q2 | 2015 | ZN2196:PA5 | ZN2196:PA5 | ZN02196/000005 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-12-10 | N | 115.7315 | N | 16 | N | N | 1.1101 | 39.4971 | 132272.3845
[7 empty] | 12264 | 71 | 1186740 | 2014-12-10 16:42 | 2014-12-10 19:00 | 138 | 11kV | 138 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143767 3 amp fuse Substation DOLF replaces OMS 1186740 | December | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2014-12-10 | N | 138 | N | 16 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 12741 | 4569 | 1191588 | 2014-12-10 17:52 | 2014-12-10 21:10 | 198 | 11kV | 594 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143774 5 amp fuse Substation DOLF Replaced blown LA's replaced OMS 1186763 | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2014-12-10 | N | 198 | N | 16 | N | N | 1.1101 | 39.4971 | 434.0777
[7 empty] | 14522 | 18877 | 1186804 | 2014-12-10 20:42 | 2014-12-10 21:51 | 68.8667 | 11kV | 63150.7333 | 917 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 173773 2 fault operations overcurrent, earth fault Bypassed Sw 42021 Queen St RAGCB due to burnt up PG clamps on line side of outgoing links. Targets: L1/L2/L3/L4 OCEF | December | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-12-10 | N | 68.8667 | N | 16 | N | N | 1.1101 | 39.4971 | 46148.6933
[7 empty] | 13105 | 7694 | 1186800 | 2014-12-10 20:20 | 2014-12-10 22:40 | 140 | 11kV | 38609 | 283 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143775 2 fault operations 3 phase instantaneous overcurrent | December | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-12-10 | N | 136.4276 | N | 16 | N | N | 1.1101 | 39.4971 | 28214.3184
[7 empty] | 13611 | 11779 | 1186801 | 2014-12-10 20:20 | 2014-12-10 22:42 | 142 | 11kV | 12913 | 96 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143776 2 fault operations Earth fault overcurrent Targets: reclosed on Bhp EF Lockout on A/B/Cph OC replaced OMS 1186801 | December | 2014 | 2015Q2 | 2015 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2014-12-10 | N | 134.5104 | N | 16 | N | N | 1.1101 | 39.4971 | 9436.4395
[7 empty] | 14226 | 16725 | 1186813 | 2014-12-10 21:23 | 2014-12-10 23:16 | 113 | 11kV | 46542 | 433 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn14891 Wyong Pa14 tripped on: Relays: A & B phase IOC, EFI Siganls: 11kv trip EFI's Nil @RE45181 McPherson rd tripped and reclosed and tripped in conjunction with Wyong Pa14. There appears to be a protection grading issue on Pa14R. T/PE to be notified Tree branch on mains See 1186989,91 Exclude 1186813 | December | 2014 | 2015Q2 | 2015 | ZN14891:PA14 | ZN14891:PA14 | ZN14891/000014 | CENTRAL COAST | OH | Veg | 2014-12-10 | N | 107.4873 | N | 16 | N | N | 1.1101 | 39.4971 | 34011.5208
[7 empty] | 12467 | 1892 | 1186817 | 2014-12-11 00:16 | 2014-12-11 01:30 | 74 | 11kV | 3330 | 45 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Electrical Storm | N | LID 143785 16 amp fuse Line DOLF replaces OMS 1186827 11/12/14 00:43 t43454: in line pole fuse down redonberry bridge pole#SI 90029 fuse #80617 | December | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2014-12-11 | N | 74 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2433.4658
[7 empty] | 14110 | 15863 | 1186781 | 2014-12-10 19:08 | 2014-12-11 01:44 | 396 | 11kV | 34802 | 99 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143781 1 fault operation Excluded OMS 1186781 | December | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2014-12-10 | N | 351.5354 | N | 16 | N | N | 1.1101 | 39.4971 | 25432.2751
[7 empty] | 13364 | 9824 | 1186823 | 2014-12-10 23:37 | 2014-12-11 03:05 | 208 | 11kV | 208 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143780 10 amp fuse Substation DOLF Replace LA's amalgamated with OMS 1186826 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-10 | N | 208 | N | 16 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 14675 | 20330 | 1186807 | 2014-12-10 20:50 | 2014-12-11 04:45 | 475 | 11kV | 1425 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143789 10 amp fuse Substation DOLF | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-10 | N | 475 | N | 16 | N | N | 1.1101 | 39.4971 | 1041.348
[7 empty] | 14158 | 16220 | 1187707 | 2014-12-11 07:05 | 2014-12-11 08:38 | 93 | 11kV | 93 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143800 1 fault operation Earth fault No reclose function | December | 2014 | 2015Q2 | 2015 |  |  |  | SINGLETON | OH | Veg | 2014-12-11 | N | 93 | N | 31 | Y | Y | 1.1101 | 39.4971 | 67.9617
[7 empty] | 14298 | 17216 | 1186838 | 2014-12-11 05:23 | 2014-12-11 09:00 | 217 | 11kV | 217 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143805 10 amp fuse Replaced blown dolf on sub 51595 Aphase 10A replaced OMS 1186838 | December | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2014-12-11 | N | 217 | N | 31 | Y | Y | 1.1101 | 39.4971 | 158.5772
[7 empty] | 13801 | 13290 | 1186814 | 2014-12-11 06:12 | 2014-12-11 09:20 | 188 | 11kV | 1316 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143803 20 amp fuse Line DOLF | December | 2014 | 2015Q2 | 2015 | 807:74183 | 807:74183 | ZN00807/074183 | MUSWELLBROOK | OH | Veg | 2014-12-11 | N | 188 | N | 31 | Y | Y | 1.1101 | 39.4971 | 961.694
[7 empty] | 12554 | 2854 | 1186879 | 2014-12-11 07:09 | 2014-12-11 09:25 | 136 | 11kV | 952 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143812 Line DOLF | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-12-11 | N | 136 | N | 31 | Y | Y | 1.1101 | 39.4971 | 695.6935
[7 empty] | 12386 | 1241 | 1187713 | 2014-12-11 07:06 | 2014-12-11 09:25 | 139 | 11kV | 278 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143802 10 amp fuse Line DOLF | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-11 | N | 139 | N | 31 | Y | Y | 1.1101 | 39.4971 | 203.1542
[7 empty] | 12282 | 250 | 1186847 | 2014-12-11 07:15 | 2014-12-11 09:50 | 155 | 11kV | 465 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143810 10 amp fuse Substation DOLF | December | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2014-12-11 | N | 155 | N | 31 | Y | Y | 1.1101 | 39.4971 | 339.8083
[7 empty] | 13178 | 8229 | 1186867 | 2014-12-11 07:00 | 2014-12-11 10:00 | 180 | 11kV | 2520 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143806 20 amp fuse Line DOLF Connected kVA ->238 CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2014-12-11 | N | 180 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1841.5417
[7 empty] | 12500 | 2252 | 1186839 | 2014-12-11 06:30 | 2014-12-11 10:55 | 265 | 11kV | 6625 | 25 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143809 Phases A+C: 10 amp fuse Line DOLF | December | 2014 | 2015Q2 | 2015 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2014-12-11 | N | 265 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4841.3546
[7 empty] | 12526 | 2534 | 1186897 | 2014-12-11 08:45 | 2014-12-11 10:58 | 133 | 11kV | 133 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143808 10 amp fuse Substation DOLF replace blown surge arrestor | December | 2014 | 2015Q2 | 2015 | 526:34636 | 526:34636 | ZN00526/034636 | CESSNOCK | OH | Not Veg | 2014-12-11 | N | 133 | N | 31 | Y | Y | 1.1101 | 39.4971 | 97.1925
[7 empty] | 14345 | 17511 | 1186918 | 2014-12-11 08:15 | 2014-12-11 11:00 | 165 | 11kV | 330 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143799 10 amp fuse Substation DOLF replaces OMS 1186918 | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-12-11 | N | 165 | N | 31 | Y | Y | 1.1101 | 39.4971 | 241.1543
[7 empty] | 13710 | 12622 | 1186939 | 2014-12-11 07:00 | 2014-12-11 11:45 | 285 | 11kV | 285 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143813 3 amp fuse Substation DOLF replaces OMS 1186939 | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-11 | N | 285 | N | 31 | Y | Y | 1.1101 | 39.4971 | 208.2696
[7 empty] | 13897 | 14112 | 1186836 | 2014-12-11 04:24 | 2014-12-11 12:00 | 456 | 11kV | 1824 | 4 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge Zone section of Pa1 "the kulnura" fdr PT13324 Colins George Downs 11kv 2 phases 10Amp HDO fuse blown. Road and middle phase. See 1188696 exclude 1186836 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2014-12-11 | N | 456 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1332.9254
[7 empty] | 13175 | 8167 | 1187070 | 2014-12-11 10:50 | 2014-12-11 12:18 | 88 | 11kV | 28512 | 324 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Section of ZN.15014 Mona Vale 11kV Panel 14 from RE.22381 to extent of feeder (11 DC's) tripped, reclosed, tripped on:- Instantaneous and timed over current Cause:- Tree bark on OH mains near PT.15577, removed by D/Op ME:-1187070 | December | 2014 | 2015Q2 | 2015 | ZN15014:PA14 | ZN15014:PA14 | ZN15014/000014 | NORTHERN BEACHES | OH | Veg | 2014-12-11 | N | 88 | N | 31 | Y | Y | 1.1101 | 39.4971 | 20835.7286
[7 empty] | 13306 | 9174 | 1186779 | 2014-12-10 18:59 | 2014-12-11 12:30 | 1051 | 11kV | 23070 | 82 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 143782 1 fault operations Replaced blown LAs at sub 53329 Minimbah House. Sub 53329 faulty. tx replaced 11/12/2014 supply restored at 1230 pm. Excluded OMS No. 1186779 | December | 2014 | 2015Q2 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2014-12-10 | N | 281.3415 | N | 16 | N | N | 1.1101 | 39.4971 | 16858.8756
[7 empty] | 13409 | 10204 | 1187751 | 2014-12-11 12:23 | 2014-12-11 12:31 | 8 | 11kV | 528 | 66 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143817 1 fault operation Earth fault reclose switched off for operating faulty tx 46605 | December | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2014-12-11 | N | 8 | N | 31 | Y | Y | 1.1101 | 39.4971 | 385.8468
[7 empty] | 13537 | 11164 | 1186776 | 2014-12-10 19:00 | 2014-12-11 12:39 | 1059 | 11kV | 2118 | 2 | HV | Lightning Strike | Adverse Weather/Environment | DC Transformer | Unplanned | Lightning | N | LID 143778 10 amp fuse Substation DOLF Near- direct hit from lightning on building Replaced faulty transformer 53544 replaces OMS 1186776 | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | UG | Not Veg | 2014-12-10 | N | 1059 | N | 16 | N | N | 1.1101 | 39.4971 | 1547.7719
[7 empty] | 13408 | 10200 | 1187591 | 2014-12-11 11:55 | 2014-12-11 12:55 | 60 | 11kV | 60 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 143816 1 fault operation Pole mounted RAGCB | December | 2014 | 2015Q2 | 2015 |  |  |  | LAKE MACQUARIE | OH | Veg | 2014-12-11 | N | 60 | N | 31 | Y | Y | 1.1101 | 39.4971 | 43.8462
[7 empty] | 13088 | 7522 | 1187092 | 2014-12-11 12:14 | 2014-12-11 13:40 | 86 | 11kV | 86 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 143823 sub isolated to repair la Excluded OMS 1187749 | December | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2014-12-11 | N | 86 | N | 31 | Y | Y | 1.1101 | 39.4971 | 62.8463
[7 empty] | 13505 | 10975 | 1187218 | 2014-12-11 13:30 | 2014-12-11 14:54 | 83.9 | 11kV | 20136 | 240 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Section of ZN.3154 St Ives 11kV Panel 23 from RE.527 to the extent of the feeder (4 DC's) tripped, reclosed, tripped on:- Instantaneous and timed over current Cause:- Twiggs on OH mains adjacent to RE.527 ME:-1187128 | December | 2014 | 2015Q2 | 2015 | ZN3154:PA23 | ZN3154:PA23 | ZN03154/000023 | KU-RING-GAI | OH | Veg | 2014-12-11 | N | 83.9 | N | 31 | Y | Y | 1.1101 | 39.4971 | 14714.7949
[7 empty] | 12440 | 1729 | 1187338 | 2014-12-11 15:17 | 2014-12-11 16:20 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143832 10 amp fuse Substation DOLF replaces OMS 1187338 | December | 2014 | 2015Q2 | 2015 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2014-12-11 | N | 63 | N | 31 | Y | Y | 1.1101 | 39.4971 | 46.0385
[7 empty] | 12333 | 758 | 1187389 | 2014-12-11 16:00 | 2014-12-11 16:20 | 20 | 11kV | 40 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143831 16 amp fuse Line DOLF | December | 2014 | 2015Q2 | 2015 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2014-12-11 | N | 20 | N | 31 | Y | Y | 1.1101 | 39.4971 | 29.2308
[7 empty] | 14267 | 16999 | 1187362 | 2014-12-11 15:52 | 2014-12-11 16:20 | 28 | 11kV | 28 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143829 3 amp fuse Substation DOLF replaces OMS 1187362 | December | 2014 | 2015Q2 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | UPPER HUNTER | OH | Veg | 2014-12-11 | N | 28 | N | 31 | Y | Y | 1.1101 | 39.4971 | 20.4616
[7 empty] | 12716 | 4299 | 1187354 | 2014-12-11 15:38 | 2014-12-11 17:15 | 97 | 11kV | 388 | 4 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 143830 100 amp fuse Distribution LV fuse Trees growing into mains Conductor Private LV OHM down replaces OMS 1187354 | December | 2014 | 2015Q2 | 2015 | 227:13015 | 227:13015 | ZN00227/013015 | LAKE MACQUARIE | OH | Veg | 2014-12-11 | N | 97 | N | 31 | Y | Y | 1.1101 | 39.4971 | 283.539
[7 empty] | 12419 | 1562 | 1187344 | 2014-12-11 15:26 | 2014-12-11 17:22 | 116 | 11kV | 71516 | 876 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn874 Concrod - Pnl.7 tripped on: EFI, L1 O/C and trip signals: 11kV trip, Tx 1 GE, ZE UG Cable fault from Concord Pnl.7 to Sw A @ S2103 Mackenzie Vic see 1189028 GIS: 1189036 1189034 1189033 1187373 1187367 | December | 2014 | 2015Q2 | 2015 | ZN874:PA7 | ZN874:PA7 | ZN00874/000007 | CANADA BAY | UG | Not Veg | 2014-12-11 | N | 81.6393 | N | 31 | Y | Y | 1.1101 | 39.4971 | 52261.7834
[7 empty] | 12732 | 4502 | 1186791 | 2014-12-10 19:52 | 2014-12-11 17:25 | 1293 | 11kV | 21359 | 59 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143783 4 fault operations Sensitive Earth Fault Faulty L/A's sub 70880 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-12-10 | N | 362.0169 | N | 16 | N | N | 1.1101 | 39.4971 | 15608.5272
[7 empty] | 12964 | 6528 | 1187307 | 2014-12-11 14:50 | 2014-12-11 17:30 | 160 | 11kV | 71272 | 1100 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | Rain Light | N | Ex Zn13000 Lake Munmorah section of Pa11 "Lake Munmorah Aux No.2" @Cp45095 Mannering Park tripped reclosed and locked out on overucrrent protection Cause: Tree branch on overhead mains. Catherine st Mannering Park See 1188702,4 exclude 1187307 | December | 2014 | 2015Q2 | 2015 | ZN13000:PA11 | ZN13000:PA11 | ZN13000/000011 | CENTRAL COAST | OH | Veg | 2014-12-11 | N | 64.7927 | N | 31 | Y | Y | 1.1101 | 39.4971 | 52083.4754
[7 empty] | 14593 | 19529 | 1187423 | 2014-12-11 17:26 | 2014-12-11 18:04 | 37.55 | 11kV | 50617.4 | 1348 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Section of ZN.15011 Beacon Hill 11kV Panel 6 from RE.21685 to the extent of the feeder (11 DC's) tripped on:- Sensitive Earth Leakage Cause:- Not ascertained Mains to patrol in daylight AM Friday ME:-1187423 Withdrawn:-1187441 CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | ZN15011:PA6 | ZN15006:PA16 | ZN15006/000016 | NORTHERN BEACHES | OH | Veg | 2014-12-11 | N | 37.55 | N | 31 | Y | Y | 1.1101 | 39.4971 | 36989.703
[7 empty] | 12673 | 3921 | 1187414 | 2014-12-11 17:09 | 2014-12-11 18:59 | 110 | 11kV | 8250 | 75 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | Section of ZN.2400 Berowra 11kV Panel 18 from RE.3281 to extent of feeder (10 DC's) tripped, reclosed, tripped and locked out on:- EF trip Cause:- @ PT.660 Chillcott Bay - Footpath phase lightning arrestor found operated. D/Op cut away and feeder back in service. Subs and region to organise repair. Note:- DMA @ PT.1297 in LV// at time of event ME:-1187415 SE:-1187411 Withdrawn:-1187454, 1187440, 187421, 1187414 | December | 2014 | 2015Q2 | 2015 | ZN2400:PA18 | ZN2400:PA18 | ZN02400/000018 | HORNSBY | OH | Not Veg | 2014-12-11 | N | 110 | N | 31 | Y | Y | 1.1101 | 39.4971 | 6028.8567
[7 empty] | 14180 | 16344 | 1187472 | 2014-12-11 18:42 | 2014-12-11 20:06 | 84 | 11kV | 84 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143836 10 amp fuse Substation DOLF CASS 29523 | December | 2014 | 2015Q2 | 2015 |  |  |  | SINGLETON | OH | Veg | 2014-12-11 | N | 84 | N | 31 | Y | Y | 1.1101 | 39.4971 | 61.3847
[7 empty] | 14581 | 19357 | 1187490 | 2014-12-11 19:40 | 2014-12-11 21:31 | 111 | 11kV | 1998 | 18 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143835 Pole mounted RAGCB, overcurrent stranded conductor between HQ-51563 & HQ51564. Suspect pelican hit mains. Please investigate conductor | December | 2014 | 2015Q2 | 2015 | 528:83019 | 528:83019 | ZN00528/083019 | MAITLAND | OH | Not Veg | 2014-12-11 | N | 111 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1460.0795
[7 empty] | 14020 | 15164 | 1187397 | 2014-12-11 16:44 | 2014-12-11 22:00 | 316 | 11kV | 632 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 143828 Substation DOLF SUB ISOLATED TO REPAIR LA | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33397 | ZN00509/033397 | CESSNOCK | OH | Not Veg | 2014-12-11 | N | 316 | N | 31 | Y | Y | 1.1101 | 39.4971 | 461.847
[7 empty] | 12750 | 4603 | 1187399 | 2014-12-11 14:43 | 2014-12-11 23:30 | 527 | 11kV | 43181 | 133 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143828 3 fault operations 3 phase Sensitive Earth Fault Excluded OMS 1187399 | December | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-12-11 | N | 324.6692 | N | 31 | Y | Y | 1.1101 | 39.4971 | 31555.4012
[7 empty] | 12682 | 3988 | 1187506 | 2014-12-11 20:51 | 2014-12-12 00:05 | 194 | 11kV | 582 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Wind Strong | N | LID 143840 No protection operations. B ph dropper to DOLF broken. Repaired under AP. Excluded OMS 1187506 | December | 2014 | 2015Q2 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | NEWCASTLE | OH | Not Veg | 2014-12-11 | N | 194 | N | 31 | Y | Y | 1.1101 | 39.4971 | 425.3084
[7 empty] | 13602 | 11725 | 1187705 | 2014-12-12 07:00 | 2014-12-12 10:20 | 200 | 11kV | 200 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143846 10 amp fuse Substation DOLF replaced OMS 1187705 | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-12 | N | 200 | N | 14 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 12557 | 2866 | 1187699 | 2014-12-12 09:31 | 2014-12-12 12:15 | 164 | 11kV | 328 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143851 200 amp fuse replaces OMS 1187699 | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Veg | 2014-12-12 | N | 164 | N | 14 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 14150 | 16173 | 1187783 | 2014-12-12 12:00 | 2014-12-12 14:00 | 120 | 11kV | 120 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143852 20 amp fuse Substation DOLF replaces OMS 1187783 | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-12-12 | N | 120 | N | 14 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 13946 | 14572 | 1187756 | 2014-12-12 10:35 | 2014-12-12 16:30 | 355 | 11kV | 121048 | 1580 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa33 "Macmasters Beach" fdr tripped, reclosed and locked out on A Phase IOC, EF, EFI, reclose and lockout EFI's: S14155 UG fdr from S14155 Scaybrook Waldron to S12595 Scaysbrook Monica tee to S12814 Scaysbrook Brentwood See 1188724,6,7 Exclude 1187742,56 | December | 2014 | 2015Q2 | 2015 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | UG | Not Veg | 2014-12-12 | N | 76.6127 | N | 14 | N | N | 1.1101 | 39.4971 | 88458.3081
[7 empty] | 13390 | 10086 | 1187946 | 2014-12-12 17:00 | 2014-12-12 18:50 | 110 | 11kV | 110 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143857 16 amp fuse Substation DOLF cass 29912 replaced 2 x fuses | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-12 | N | 110 | N | 14 | N | N | 1.1101 | 39.4971 | 80.3848
[7 empty] | 14411 | 17995 | 1187981 | 2014-12-12 17:56 | 2014-12-12 19:40 | 104 | 11kV | 4472 | 43 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 143855 Distribution LV fuse replaces OMS 1187981 RH LVF 25493 loose Wind <40 k | December | 2014 | 2015Q2 | 2015 | 233:82821 | 233:82815 | ZN00233/082815 | PORT STEPHENS | OH | Not Veg | 2014-12-12 | N | 104 | N | 14 | N | N | 1.1101 | 39.4971 | 3268.0057
[7 empty] | 14034 | 15312 | 1187816 | 2014-12-12 19:29 | 2014-12-12 19:53 | 24 | 11kV | 2650 | 160 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | LID 143856 1 fault operation Sensative earth fault sw 34640 sef failure of abs 41434 caused fdr 34640 to trip.This fdr was backfeeding Nulkaba fdr 33576 via sw 3821 back to abs 3270 which also failed earlier today and had to be opened. Excluded OMS ##oms 1187995, 1187987 | December | 2014 | 2015Q2 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Not Veg | 2014-12-12 | N | 16.5625 | N | 14 | N | N | 1.1101 | 39.4971 | 1936.5418
[7 empty] | 12837 | 5405 | 1187940 | 2014-12-12 15:45 | 2014-12-12 20:05 | 260 | 11kV | 1040 | 4 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Insulated | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford Pa1 section of "Dog Trap Rd" 11kV Oh wire down to ground on single phase line adjacent LK43412 to PT12553 Ourimbah Reid tee PT12537 Spiers Ourimbah No.1 Tree branch brought down OH. One span from LK43412 See 1188734 exclude 1187940,8011 | December | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-12-12 | N | 260 | N | 14 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 13437 | 10459 | 1189265 | 2014-12-12 19:55 | 2014-12-12 20:10 | 15 | 11kV | 880 | 82 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Wind Strong | N | LID 143856 1 fault operation Sensative earth fault 2 events covered by one LID sw 34640 sef failure of abs 41434 caused fdr 34640 to trip.This fdr was backfeeding Nulkaba fdr 33576 via sw 3821 back to abs 3270 which also failed earlier today and had to be opened. | December | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2014-12-12 | N | 10.7317 | N | 14 | N | N | 1.1101 | 39.4971 | 643.078
[7 empty] | 13096 | 7620 | 1188001 | 2014-12-12 18:36 | 2014-12-12 20:20 | 104 | 11kV | 104 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143858 10 amp fuse Substation DOLF replaces OMS 1188001 Wind <40 k | December | 2014 | 2015Q2 | 2015 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2014-12-12 | N | 104 | N | 14 | N | N | 1.1101 | 39.4971 | 76.0001
[7 empty] | 13871 | 13869 | 1187991 | 2014-12-12 19:00 | 2014-12-12 21:05 | 125 | 11kV | 250 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143859 10 amp fuse Substation DOLF replaced OMS 1187991 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-12 | N | 125 | N | 14 | N | N | 1.1101 | 39.4971 | 182.6926
[7 empty] | 13921 | 14298 | 1187854 | 2014-12-12 14:39 | 2014-12-12 22:53 | 494 | 11kV | 55822 | 113 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor CCT | Unplanned | Wind Strong | N | LID 143854 Large tree fell across 11kV CCT OHM between poles IS-72163 & IS-72162. Excluded OMS No. 1187916, 1187854 & 1187932. | December | 2014 | 2015Q2 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Veg | 2014-12-12 | N | 494 | N | 14 | N | N | 1.1101 | 39.4971 | 40793.0711
[7 empty] | 14417 | 18035 | 1188051 | 2014-12-13 03:20 | 2014-12-13 07:45 | 265 | 11kV | 50880 | 192 | HV | 3rd Party Action | 3rd Party Impact | OTHER - REFER COMMENTS | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa33 "Macmasters Beach" fdr MG supplying S12814 Scaybrook Brentwood tripped. Abnomral: S12814 isolated running on MG due to 11kv fdr fault Cause: MG set tripped off. 13/12/14 04:49 t41401: Aggreko Generator onsite, suspected passerby turned off generator. Power restored by Dop. See 1188738 exclude 1188051,6,7,65 | December | 2014 | 2015Q2 | 2015 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | Unknown | Not Veg | 2014-12-13 | N | 265 | N | 7 | N | N | 1.1101 | 39.4971 | 37181.6033
[7 empty] | 12274 | 153 | 1188050 | 2014-12-13 02:58 | 2014-12-13 08:56 | 358 | 11kV | 358 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 143863 10 amp fuse Substation DOLF Failure or defect Sub DOLF Operated but failed to drop. Fuse carrier was replaced after being burned up. Sub desparately needs maintenance and retrofit | December | 2014 | 2015Q2 | 2015 | 504:48031 | 522:83132 | ZN00522/083132 | CESSNOCK | OH | Veg | 2014-12-13 | N | 358 | N | 7 | N | N | 1.1101 | 39.4971 | 261.6158
[7 empty] | 12839 | 5427 | 1187838 | 2014-12-12 12:42 | 2014-12-13 10:15 | 1293 | 11kV | 5076 | 38 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2196 Milperra - Pnl.10 tripped on: Earth Fault, EFI Signals: 11kv trip, ZE, Tx 3 GE Field EFIs: S7206 & S7105 UG Cable fault from S7105 Sw B to S6563 tee S1168 (N//) - S1168 restored via MG see 1189045 1189046 1189048 | December | 2014 | 2015Q2 | 2015 | ZN2196:PA10 | ZN2196:PA10 | ZN02196/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2014-12-12 | N | 133.5789 | N | 14 | N | N | 1.1101 | 39.4971 | 3709.3911
[7 empty] | 13319 | 9427 | 1188117 | 2014-12-13 11:46 | 2014-12-13 12:45 | 59 | 11kV | 1770 | 30 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143865 Failure or defect LV fuse burned up. Sub put in LV// to restore supply. Sub fuse to be replaced by on call staff | December | 2014 | 2015Q2 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2014-12-13 | N | 59 | N | 7 | N | N | 1.1101 | 39.4971 | 1293.4638
[7 empty] | 14641 | 20086 | 1188123 | 2014-12-13 11:59 | 2014-12-13 13:00 | 61 | 11kV | 109459 | 1939 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 398 Dulwich Hill - Pnl 24 - B phase OC, EFI, Field EFIs. Underground feeder fault between S 2263 to S 63664. ME: 1189061. Rest Step: 1189062. Withdrawn: 1188123. | December | 2014 | 2015Q2 | 2015 | ZN398:PA24 | ZN398:PA24 | ZN00398/000024 | INNER WEST | UG | Not Veg | 2014-12-13 | N | 56.4513 | N | 7 | N | N | 1.1101 | 39.4971 | 79989.4087
[7 empty] | 12305 | 496 | 1188137 | 2014-12-13 12:43 | 2014-12-13 15:25 | 162 | 11kV | 44286 | 748 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7900 Campbell St - Pnl. 7 trippedon: Earth Fault, Check relay, 11kV trip UG cable fault from S133 Goodchamp St #3 RMI tee off to S35851 Reservoir Riley #1 see 1188388 1188390 | December | 2014 | 2015Q2 | 2015 | ZN7900:PA7 | ZN7900:PA7 | ZN07900/000007 | SYDNEY | UG | Not Veg | 2014-12-13 | N | 59.2059 | N | 7 | N | N | 1.1101 | 39.4971 | 32362.9026
[7 empty] | 13314 | 9355 | 1188146 | 2014-12-13 13:05 | 2014-12-13 15:45 | 160 | 11kV | 480 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 143866 Single phase Burnt up DOLF carrier replaced OMS 1188146 | December | 2014 | 2015Q2 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Not Veg | 2014-12-13 | N | 160 | N | 7 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 13569 | 11457 | 1187999 | 2014-12-12 18:33 | 2014-12-13 16:55 | 1342 | 11kV | 2684 | 2 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | 12/12/14 20:39 t48154: PT 14855 has Failed and is to be replaced 13/12. No // available See 1188105 for interruption to replace transformer. See 1188024 GIS 1187999 CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-12-12 | N | 1342 | N | 14 | N | N | 1.1101 | 39.4971 | 1961.388
[7 empty] | 14611 | 19804 | 1188105 | 2014-12-13 10:40 | 2014-12-13 16:55 | 375 | 11kV | 5250 | 14 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" 11kv fdr from LK41028 to LB445532 interrupted to change defective Tx @ PT14855 Dickson Durren 1.1 Transformer failure | December | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-12-13 | N | 375 | N | 7 | N | N | 1.1101 | 39.4971 | 3836.5452
[7 empty] | 13211 | 8489 | 1188211 | 2014-12-14 02:36 | 2014-12-14 09:20 | 404 | 11kV | 232925.7667 | 1564 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN.3154 St Ives 11kV Panel 11 feeder tripped on:- Relays:- A phase IOC, EF, EFI Field EFI's:- Nil Signals:- 11kV trip Cause:- 11kV UG cable fault located between S.47299 SW/B to S.8595 SW/A tee S.6507 ME:-1188437 RS:-1188441, 1188443, 1188447 SE:-1188212 Withdrawn:-1188217, 1188211 | December | 2014 | 2015Q2 | 2015 | ZN3154:PA11 | ZN3154:PA11 | ZN03154/000011 | KU-RING-GAI | UG | Not Veg | 2014-12-14 | N | 148.9295 | N | 4 | N | N | 1.1101 | 39.4971 | 170215.2801
[7 empty] | 13267 | 8902 | 1188223 | 2014-12-14 07:35 | 2014-12-14 09:55 | 140 | 11kV | 101190 | 816 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | @ ZN.15013 Terrey Hills 11kV Panel 4 Tripped on:- Relays:- SEF, Fault check, EFI Signals:- 11kV Trip, ZE @ PT.15854 Nillera Ave - Roadside phase 50A HDO fuse operated Cause:- Transformer failure ME:-188606 RS:-1188611 Withdrawn:-1188223 | December | 2014 | 2015Q2 | 2015 | ZN15013:PA4 | ZN15013:PA4 | ZN15013/000004 | NORTHERN BEACHES | OH | Not Veg | 2014-12-14 | N | 124.0074 | N | 4 | N | N | 1.1101 | 39.4971 | 73946.6674
[7 empty] | 14430 | 18144 | 1188300 | 2014-12-14 17:01 | 2014-12-14 18:25 | 84 | 11kV | 96600 | 1150 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex ZN 10990 Kogarah - Pnl 17 - Bond at Pole KO 17508. 11kV bond middle phase burnt off on Pole KO 17508. ME: 1189259. GIS: 1188319, 23, 25. Withdrawn: 1188300, 2. | December | 2014 | 2015Q2 | 2015 | ZN10999:PA17 | ZN10999:PA17 | ZN10999/000017 | BAYSIDE | OH | Not Veg | 2014-12-14 | N | 84 | N | 4 | N | N | 1.1101 | 39.4971 | 70592.4308
[7 empty] | 13323 | 9484 | 1188366 | 2014-12-15 07:23 | 2014-12-15 08:25 | 62 | 11kV | 62 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 143872 10 amp fuse Substation DOLF replaces OMS 1188366 - "could have been previous storm, could have been birds nesting on TX. No bird strike nor ex bird found" | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-12-15 | N | 62 | N | 6 | N | N | 1.1101 | 39.4971 | 45.3078
[7 empty] | 14318 | 17329 | 1188505 | 2014-12-15 10:41 | 2014-12-15 12:17 | 96 | 11kV | 96 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143875 10 amp fuse Substation DOLF Second time today, but different phase replaces OMS 1188505 | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-12-15 | N | 96 | N | 6 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 14559 | 19143 | 1188371 | 2014-12-15 07:31 | 2014-12-15 12:35 | 304 | 11kV | 8757 | 59 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 143877 3 fault operations B phase Earth Fault; Overcurrent OHM faulty between IU-63505 & IU-67310 | December | 2014 | 2015Q2 | 2015 | 224:80328 | 214:8672 | ZN00214/008672 | LAKE MACQUARIE | OH | Not Veg | 2014-12-15 | N | 148.4237 | N | 6 | N | N | 1.1101 | 39.4971 | 6399.3573
[7 empty] | 13756 | 12938 | 1188353 | 2014-12-14 22:11 | 2014-12-15 13:07 | 896 | 11kV | 1215 | 320 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12630 Peats Ridge 11kv fdr Pa4 "Kulnura" fdr tripped and reclosed Relays: A and C phase timed overvcurrent, EFI EFI's:Nil Cause not ascertained. Next available linesmans to Patrol See 1189068,70 exclude 1188353 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA4 | ZN12630:PA10 | ZN12630/000010 | CENTRAL COAST | OH | Veg | 2014-12-14 | N | 3.7969 | N | 4 | N | N | 1.1101 | 39.4971 | 887.8862
[7 empty] | 14646 | 20118 | 1188567 | 2014-12-15 12:17 | 2014-12-15 15:05 | 168 | 11kV | 504 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 143876 10 amp fuse Substation DOLF Surge diverters replaces OMS 1188567 - Repaced L/A on sub 51203 & blown dolf 10A | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-12-15 | N | 168 | N | 6 | N | N | 1.1101 | 39.4971 | 368.3083
[7 empty] | 12731 | 4497 | 1188775 | 2014-12-15 19:00 | 2014-12-15 21:20 | 140 | 11kV | 1120 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 143884 Distribution LV fuse Fuses (incorrect operation) fuse fell open replaces OMS 1188775 | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-12-15 | N | 140 | N | 6 | N | N | 1.1101 | 39.4971 | 818.463
[7 empty] | 14402 | 17962 | 1189006 | 2014-12-15 23:23 | 2014-12-16 00:06 | 43 | 11kV | 5762 | 134 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 143885 31 amp fuse Substation DOLF Fuses (incorrect operation) suspect fuse fatigue also refer to 1189006 | December | 2014 | 2015Q2 | 2015 | 202:34245 | 256:80653 | ZN00256/080653 | NEWCASTLE | OH | Not Veg | 2014-12-15 | N | 43 | N | 6 | N | N | 1.1101 | 39.4971 | 4210.6996
[7 empty] | 13154 | 8019 | 1189277 | 2014-12-16 14:05 | 2014-12-16 15:00 | 55 | 11kV | 10010 | 182 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 143897 A phase Aph tapping burnt off ABS 11386. Excluded OMS No. 1189277 + 1189311 | December | 2014 | 2015Q2 | 2015 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Not Veg | 2014-12-16 | N | 55 | N | 6 | N | N | 1.1101 | 39.4971 | 7315.0128
[7 empty] | 12772 | 4748 | 1189371 | 2014-12-16 16:29 | 2014-12-16 17:45 | 76 | 11kV | 6916 | 91 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | Ex Zn1193 Lindfield 11kv Panel 27 @S4893 Tryon Robinson Suspect transformer failed. Suspect Open Circuit inside tank. DOp has left Switching tag. See 1189376 Exclude 1189371,9,401 CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | ZN1193:PA27 | ZN1193:PA27 | ZN01193/000027 | KU-RING-GAI | UG | Not Veg | 2014-12-16 | N | 76 | N | 6 | N | N | 1.1101 | 39.4971 | 5054.0088
[7 empty] | 13294 | 9054 | 1189441 | 2014-12-16 18:05 | 2014-12-16 19:45 | 100 | 11kV | 800 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143904 16 amp fuse Substation DOLF replaces OMS 1189441 | December | 2014 | 2015Q2 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Veg | 2014-12-16 | N | 100 | N | 6 | N | N | 1.1101 | 39.4971 | 584.6164
[7 empty] | 12728 | 4442 | 1189462 | 2014-12-16 19:06 | 2014-12-16 20:50 | 104 | 11kV | 832 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT14988 Sparks Louisiana HDo operated 16K fuse (batch 517) Fuse Fatigue See 1189590 exclude 1189462 | December | 2014 | 2015Q2 | 2015 | ZN14892:PA10 | ZN14892:PA10 | ZN14892/000010 | CENTRAL COAST | OH | Not Veg | 2014-12-16 | N | 104 | N | 6 | N | N | 1.1101 | 39.4971 | 608.0011
[7 empty] | 13398 | 10146 | 1189504 | 2014-12-16 23:08 | 2014-12-17 03:29 | 261 | 11kV | 1566 | 6 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | LID 143907 10 amp fuse LIne DOLF Fuses (incorrect operation) oms 1189505 & 1189504 fuse appeared in tact however when tested proved to be Open Circuit hence delay in restoration. | December | 2014 | 2015Q2 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2014-12-16 | N | 261 | N | 6 | N | N | 1.1101 | 39.4971 | 1144.3866
[7 empty] | 13581 | 11559 | 1189508 | 2014-12-17 03:00 | 2014-12-17 06:06 | 186 | 11kV | 123488 | 972 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn1287 Revesby Panel 4 "Tower Condon" tripped, reclosed, tripped and locked out on: Relays: Bassler, Minor Alarm, Trip, Fault Check Relay EFI's: S46609 S49469 S5040 S47275 Signals: 11kv trip Cause not ascertained See 1189661,3,5 Exclude 1189508 | December | 2014 | 2015Q2 | 2015 | ZN1287:PA4 | ZN1287:PA4 | ZN01287/000004 | CANTERBURY-BANKSTOWN | OH | Veg | 2014-12-17 | N | 127.0453 | N | 3 | N | N | 1.1101 | 39.4971 | 90241.3881
[7 empty] | 14177 | 16312 | 1189536 | 2014-12-17 07:35 | 2014-12-17 09:20 | 105 | 11kV | 105 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 143912 2 fault oprations AG system patrolled by Dop no fault found. HWC system checked no fault found | December | 2014 | 2015Q2 | 2015 | 222:33596 | 222:33596 | ZN00222/033596 | LAKE MACQUARIE | OH | Veg | 2014-12-17 | N | 105 | N | 3 | N | N | 1.1101 | 39.4971 | 76.7309
[7 empty] | 12515 | 2393 | 1189643 | 2014-12-17 11:00 | 2014-12-17 12:15 | 75 | 11kV | 75 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143920 A phase DOLF : 10 Amp Excluded OMS 1189643 | December | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-12-17 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 14332 | 17386 | 1189418 | 2014-12-16 17:28 | 2014-12-17 16:28 | 1380 | 11kV | 41458 | 230 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 143905 1 fault operation Sensitive Earth Fault tree brought 11kV ohm down at pole FE-70080 Excluded OMS 1189418. | December | 2014 | 2015Q2 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2014-12-16 | N | 180.2522 | N | 6 | N | N | 1.1101 | 39.4971 | 30296.2836
[7 empty] | 13944 | 14566 | 1189992 | 2014-12-18 00:22 | 2014-12-18 01:56 | 94 | 11kV | 46074 | 501 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 143925 1 fault operation 3 phase Overcurrent reclose function was off for work | December | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-12-18 | N | 91.9641 | N | 6 | N | N | 1.1101 | 39.4971 | 33669.5202
[7 empty] | 14508 | 18772 | 1190001 | 2014-12-18 06:31 | 2014-12-18 08:20 | 109 | 11kV | 218 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143931 A phase DOLF : 20 Amp Excluded OMS 1190001 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-18 | N | 109 | N | 6 | N | N | 1.1101 | 39.4971 | 159.308
[7 empty] | 13692 | 12443 | 1190015 | 2014-12-18 07:00 | 2014-12-18 09:30 | 150 | 11kV | 300 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143932 3 phase DOLF : 10 Amp all three dolfs were blown Excluded OMS 1190015 | December | 2014 | 2015Q2 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2014-12-18 | N | 150 | N | 6 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 14250 | 16908 | 1190318 | 2014-12-18 13:50 | 2014-12-18 15:45 | 115 | 11kV | 95903 | 912 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor U/G | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 35 Tripped on Earth Fault with EFI Tx1 Group Earth, Zone Earth and 11kV Trip Cause not ascertained for outage | December | 2014 | 2015Q2 | 2015 | ZN965:PA35 | ZN965:PA35 | ZN00965/000035 | HORNSBY | UG | Not Veg | 2014-12-18 | N | 105.1568 | N | 6 | N | N | 1.1101 | 39.4971 | 70083.0837
[7 empty] | 12712 | 4240 | 1190464 | 2014-12-18 18:00 | 2014-12-18 19:35 | 95 | 11kV | 23244 | 260 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Section of ZN.3154 St Ives 11kV panel 12 from ABS.267 to extent of the feeder (7 DC's) Cause:- Car hit pole at ABS.2844 causing it to open, 11kV feeder isolated and earthed at ABS.267 to ABS.1663 (via ABS.2844) tee PT.1731 tee PT.931 ME:-1190601 RS:-1190604 GIS Model Error:-1190472 Withdrawn:-1190477, 1190471, 1190467, 1190464, 1190463 | December | 2014 | 2015Q2 | 2015 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Not Veg | 2014-12-18 | N | 89.4 | N | 6 | N | N | 1.1101 | 39.4971 | 16986.0296
[7 empty] | 14106 | 15832 | 1190506 | 2014-12-18 22:25 | 2014-12-19 09:53 | 688 | 11kV | 30694 | 108 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section Pa1 CP44602 Ourimbah Creek Rd recloser tripped on overcurrent & locked out Tree brought Down HV and LV mains 644 ourimbah Creek rd See 1191290,4 exclude 1190506,7,10,2 | December | 2014 | 2015Q2 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Veg | 2014-12-18 | N | 284.2037 | N | 6 | N | N | 1.1101 | 39.4971 | 22430.2699
[7 empty] | 14076 | 15610 | 1190772 | 2014-12-19 12:18 | 2014-12-19 15:13 | 175 | 11kV | 5600 | 32 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14834 Wyon section of Pa5 "Wyong" fdr @PT14834 Partridge Pacific 0.4 11kv roadside 16 Amp Dropfuse failed See 1191383 exclude 1190772 | December | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-12-19 | N | 175 | N | 3 | N | N | 1.1101 | 39.4971 | 4092.3148
[7 empty] | 13737 | 12823 | 1190698 | 2014-12-19 08:47 | 2014-12-19 17:00 | 493 | 11kV | 36482 | 74 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 143950 B & C phase ABS 42406 couldn't / wasn't closed properly causing fluctuationg supply. Excluded OMS 1190638 | December | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2014-12-19 | N | 493 | N | 3 | N | N | 1.1101 | 39.4971 | 26659.9696
[7 empty] | 12474 | 1950 | 1190894 | 2014-12-19 16:17 | 2014-12-19 21:55 | 338 | 11kV | 338 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 143955 DOLF : 10 Amp replaced B phase LA | December | 2014 | 2015Q2 | 2015 | 509:48040 | 509:33399 | ZN00509/033399 | CESSNOCK | OH | Not Veg | 2014-12-19 | N | 338 | N | 3 | N | N | 1.1101 | 39.4971 | 247.0004
[7 empty] | 12880 | 5848 | 1190992 | 2014-12-20 14:35 | 2014-12-20 16:05 | 90 | 11kV | 6300 | 70 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 143957 Mains broken of at Disc insulator. Held up by LL Leads. No Protection Operation 20/12/14 16:19 CASS: Replaced HV insulators - repaired and retensioned HV mains | December | 2014 | 2015Q2 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2014-12-20 | N | 90 | N | 2 | N | N | 1.1101 | 39.4971 | 4603.8542
[7 empty] | 13081 | 7486 | 1191065 | 2014-12-20 17:39 | 2014-12-20 22:00 | 261 | 11kV | 138982 | 1782 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 143958 2 fault operations Overcurrent Can not confirm if AR occurred. It is suspect as per DMA tag. Tappings Blown at pole HR-61034 & HR-91889. UG Cable System Voltage tested between links 3368 & Sw 29474 Wilton Dr No3 sub. Excluded OMS 1191065 | December | 2014 | 2015Q2 | 2015 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2014-12-20 | N | 77.9921 | N | 2 | N | N | 1.1101 | 39.4971 | 101563.9463
[7 empty] | 14432 | 18165 | 1191101 | 2014-12-21 00:23 | 2014-12-21 02:30 | 127 | 11kV | 3810 | 30 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 143959 A phase DOLF : 40 Amp DOLF blown but did not fall. See also outage 143958 Excluded oms 1191101 | December | 2014 | 2015Q2 | 2015 | 502:48010 | 528:83011 | ZN00528/083011 | MAITLAND | OH | Not Veg | 2014-12-21 | N | 127 | N | 5 | N | N | 1.1101 | 39.4971 | 2784.2356
[7 empty] | 13269 | 8912 | 1191105 | 2014-12-21 02:41 | 2014-12-21 04:00 | 79 | 11kV | 77043 | 1007 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of ZN.15014 Mona Vale 11kV Panel 11L from RE.20397 to the extent of the feeder (15 DC's) tripped and locked out on:- Relays:- IOC trip, OC trip Signals:- 11kV trip EFI's:- S.16490, S.47095, S.16702 Cause:- Not ascertained, Mains to patrol ME:-1191232 RS:-1191233 Withdrawn:-1191105 | December | 2014 | 2015Q2 | 2015 | ZN15014:PA11 | ZN15014:PA7 | ZN15014/000007 | NORTHERN BEACHES | OH | Veg | 2014-12-21 | N | 76.5074 | N | 5 | N | N | 1.1101 | 39.4971 | 56300.752
[7 empty] | 13320 | 9439 | 1191179 | 2014-12-21 15:25 | 2014-12-21 16:09 | 44 | 11kV | 16632 | 378 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Pa2 @CP50247 Blackett Faunce tripped and locked out on overucrrent No EFI's Tree Branch on OH Mains. Near AB44215 Exclude 1191391 exclude 1191179 | December | 2014 | 2015Q2 | 2015 | ZN12650:PA2 | ZN12650:PA2 | ZN12650/000002 | CENTRAL COAST | OH | Veg | 2014-12-21 | N | 44 | N | 5 | N | N | 1.1101 | 39.4971 | 12154.175
[7 empty] | 13523 | 11093 | 1191210 | 2014-12-21 20:23 | 2014-12-21 21:23 | 60 | 11kV | 60 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 143969 C phase DOLF : 10 Amp Excluded OMS 1191210 | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-12-21 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 14615 | 19823 | 1191215 | 2014-12-21 20:55 | 2014-12-22 06:35 | 580 | 11kV | 580 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143973 A phase dolf : 10 Amp Excluded OMS 1191215 | December | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Veg | 2014-12-21 | N | 580 | N | 5 | N | N | 1.1101 | 39.4971 | 423.8469
[7 empty] | 14055 | 15443 | 1191237 | 2014-12-22 07:16 | 2014-12-22 09:12 | 116 | 11kV | 39801 | 490 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn12650 West Gosford Panel 14 "Kariong" fdr tripped, reclosed & tripped Relays: Earth Fault, Lockout, TImer, EFI Signals: 11kv trip EFI's: Nil Cause: UG frontline feeder Fault from Zn12650 West Gosford Panel 14 to LB41669 to LB42067 to S47762 to S14090 to LB64050 to S14127 to S18014 See 1191889,93,4,5 Exclude 1191237,40,1,50 | December | 2014 | 2015Q2 | 2015 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | UG | Not Veg | 2014-12-22 | N | 81.2265 | N | 5 | N | N | 1.1101 | 39.4971 | 29085.3969
[7 empty] | 14330 | 17376 | 1191225 | 2014-12-22 05:21 | 2014-12-22 13:55 | 514 | 11kV | 21730 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 143974 3 fault operations Single phase Overcurrent 11kV OHM down at Half Moon sub 52169. Excluded OMS No. 1191225 1191226 | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-22 | N | 344.9206 | N | 5 | N | N | 1.1101 | 39.4971 | 15879.6431
[7 empty] | 13214 | 8513 | 1191525 | 2014-12-22 13:35 | 2014-12-22 15:51 | 136 | 11kV | 75175 | 703 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S8000 Macquarie Park panel 6 tripped on Relays: Overcurrent, Fault Check, EFi, TX1 Earth Fault Check Relay Signals: Group Earth Tx1 and 11kV Trip Cause: 11kV UG feeder fault from SW/B at S48819 te PT1188 to SW/A at S4647 See OMS 1192072 1192073 1191541 1191560 1191525 | December | 2014 | 2015Q2 | 2015 | ZN8000:PA6 | ZN8000:PA6 | ZN08000/000006 | KU-RING-GAI | UG | Not Veg | 2014-12-22 | N | 106.9346 | N | 5 | N | N | 1.1101 | 39.4971 | 54935.6727
[7 empty] | 14433 | 18181 | 1191665 | 2014-12-22 18:01 | 2014-12-22 19:24 | 83 | 11kV | 24795 | 300 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2568 St Peters - Pnl.42 tripped on: Earth Fault, Fault Check, EFI Signals: 11kV trip, Zone Earth, Tx #1 Group Earth Field EFIs: S5562, S35331, S3276, S49289 UG cable fault from S49289 Belmore Henry No.2 (Sw B) to S8880 Coward Coggins No.3 (Sw B) to S3397 Boral South Borrows No.1 | December | 2014 | 2015Q2 | 2015 | ZN2568:PA42 | ZN2568:PA42 | ZN02568/000042 | INNER WEST | UG | Not Veg | 2014-12-22 | N | 82.65 | N | 5 | N | N | 1.1101 | 39.4971 | 18119.4547
[7 empty] | 12411 | 1505 | 1191723 | 2014-12-22 22:30 | 2014-12-22 23:50 | 80 | 11kV | 85440 | 1068 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | At ZN4545 Meadowbank Panel 44 tripped on Relays: IOC , Earth Fault, EFI and Fault Check Cause: Possum on lightning arrestors at LB61232 See OMS 1191723 1191726 1191723 | December | 2014 | 2015Q2 | 2015 | ZN4545:PA44 | ZN4545:PA44 | ZN04545/000044 | RYDE | OH | Not Veg | 2014-12-22 | N | 80 | N | 5 | N | N | 1.1101 | 39.4971 | 62437.0319
[7 empty] | 13202 | 8447 | 1191765 | 2014-12-23 07:21 | 2014-12-23 08:30 | 69 | 11kV | 1035 | 15 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section pof Pa2 "Holgate" fdr PT12294 Manor Hill Wattle Tree centre phase 16A HDO blown Cause not ascertained See 1191766 exclude 1191765,811 CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2014-12-23 | N | 69 | N | 16 | N | N | 1.1101 | 39.4971 | 756.3475
[7 empty] | 12749 | 4600 | 1191864 | 2014-12-23 08:33 | 2014-12-23 08:55 | 22.15 | 11kV | 1329 | 60 | HV | Vegetation Blow/Fall In | Vegetation | Lightning Arrestor | Unplanned | Rain Light | N | Ex Zn12610 Long Jetty sectino of Pa2 "Bateau Bay" Relays: F/C, EFI Signals: Tx1 Group Earth, Zone Earth EFI's: S11070 S50492 @PT11546 Parkside Reserve 11kv 20Amp HDO footpath fuse blown Bark on arrestor & Condemned Pole. See 1191864 exclude 1191875,85 | December | 2014 | 2015Q2 | 2015 | ZN12610:PA2 | ZN12610:PA2 | ZN12610/000002 | CENTRAL COAST | OH | Veg | 2014-12-23 | N | 22.15 | N | 16 | N | N | 1.1101 | 39.4971 | 971.194
[7 empty] | 12891 | 5913 | 1191882 | 2014-12-23 08:43 | 2014-12-23 09:30 | 47 | 33kV Distribution | 94 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 143985 C phase DOLF : 15 Amp Replaced blown L/A & DOLF Excluded OMS 1191910, 1191920, 1191882 | December | 2014 | 2015Q2 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2014-12-23 | N | 47 | N | 16 | N | N | 1.1101 | 39.4971 | 68.6924
[7 empty] | 14194 | 16469 | 1192096 | 2014-12-23 11:49 | 2014-12-23 12:08 | 19 | 11kV | 10735 | 565 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | Ex Zn14891 Wyong section Pa5 "Wyong" fdr @ 11kv AB40068, footpath side contact fell apart Relays: SEL Signals: Tx1 Group Earth EFI's: Ni @ Pa14 Relays: Sel Signals: Tx2 Group Earth, EFi EFI's: Nil ABNORMAL: Wyong Zone Sensitive Earth/R Pa5, Sensistive Earth Panel 14R, TX1 & Tx2 During switching closed LB41336 Open Sw/A S11553 AB40068 fell apart (footpath side) during switching See 1192654 exclude 1192079,96,108 | December | 2014 | 2015Q2 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2014-12-23 | N | 19 | N | 16 | N | N | 1.1101 | 39.4971 | 7844.8214
[7 empty] | 13001 | 6828 | 1192582 | 2014-12-23 13:40 | 2014-12-23 13:48 | 8 | 33kV Distribution | 16 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 143992 De energise FDR to close DOLF on sub 13949. SEE Report 143985. | December | 2014 | 2015Q2 | 2015 |  |  |  | NEWCASTLE | OH | Veg | 2014-12-23 | N | 8 | N | 16 | N | N | 1.1101 | 39.4971 | 11.6923
[7 empty] | 13787 | 13187 | 1192086 | 2014-12-23 12:00 | 2014-12-23 14:39 | 159 | 11kV | 165070 | 1735 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | Zn12660 Woy WOy Panel 10 fdr tripped Relays: 10R Earth Fault, EFI Signals: 11kv trip, Zone Earth EFI's: S12696 Cause: UG Fault from S12617:B to LB49686 to S12618:B See 1196247,8,52,3 Exclude 1192086,111,662,3 | December | 2014 | 2015Q2 | 2015 | ZN12660:PA10 | ZN12660:PA10 | ZN12660/000010 | CENTRAL COAST | UG | Not Veg | 2014-12-23 | N | 95.1412 | N | 16 | N | N | 1.1101 | 39.4971 | 120628.2873
[7 empty] | 14612 | 19805 | 1191908 | 2014-12-23 14:53 | 2014-12-23 17:50 | 177 | 33kV Distribution | 177 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 144001 A phase DOLF : 15 Amp Excluded OMS 1192226 | December | 2014 | 2015Q2 | 2015 |  |  |  | NEWCASTLE | OH | Veg | 2014-12-23 | N | 177 | N | 16 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 13970 | 14692 | 1192396 | 2014-12-23 16:38 | 2014-12-23 18:20 | 102 | 11kV | 102 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144003 Fuse size: 16 Amp, Substation Dolf also refer to OMS 1192396 | December | 2014 | 2015Q2 | 2015 |  |  |  | SINGLETON | OH | Veg | 2014-12-23 | N | 102 | N | 16 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 13972 | 14702 | 1192431 | 2014-12-23 17:41 | 2014-12-23 20:13 | 152 | 11kV | 912 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144004 C phase DOLF VOLTS 245,245, 245 LOAD 18, 25, 8 AMPS | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-12-23 | N | 152 | N | 16 | N | N | 1.1101 | 39.4971 | 666.4627
[7 empty] | 12345 | 840 | 1192415 | 2014-12-23 17:05 | 2014-12-23 20:25 | 199.5167 | 11kV | 2593.7167 | 13 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144005 Fuse size: 10 Amp Line DOLF CC1: 22-"Refer to SOp" | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-23 | N | 199.5167 | N | 16 | N | N | 1.1101 | 39.4971 | 1895.4116
[7 empty] | 13877 | 13915 | 1192423 | 2014-12-23 16:34 | 2014-12-23 20:45 | 251 | 11kV | 502 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144006 Single phase : 10 Amp REPLACED 2 X DOLFS | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2014-12-23 | N | 251 | N | 16 | N | N | 1.1101 | 39.4971 | 366.8468
[7 empty] | 13284 | 9002 | 1192377 | 2014-12-23 15:58 | 2014-12-23 21:39 | 341 | 11kV | 25558 | 115 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144000 3 phase Earth fault | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-23 | N | 222.2435 | N | 16 | N | N | 1.1101 | 39.4971 | 18677.0326
[7 empty] | 13258 | 8807 | 1192433 | 2014-12-23 17:34 | 2014-12-24 00:35 | 421 | 11kV | 1263 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 144007 A phase DOLF : 10 Amp Arresters cut away under AP | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-12-23 | N | 421 | N | 16 | N | N | 1.1101 | 39.4971 | 922.9631
[7 empty] | 12876 | 5794 | 1192485 | 2014-12-23 20:21 | 2014-12-24 00:40 | 259 | 11kV | 777 | 3 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 144010 Fuse size: 10 Amp Faulty Arrestors replaced under AP also refer to 1192584 | December | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2014-12-23 | N | 259 | N | 16 | N | N | 1.1101 | 39.4971 | 567.8087
[7 empty] | 13730 | 12766 | 1192436 | 2014-12-23 17:41 | 2014-12-24 03:00 | 559 | 11kV | 559 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 144014 A & B phase DOLF : 16 Amp Arrestors cut away | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-12-23 | N | 559 | N | 16 | N | N | 1.1101 | 39.4971 | 408.5007
[7 empty] | 13386 | 10038 | 1192524 | 2014-12-24 04:18 | 2014-12-24 05:38 | 80 | 11kV | 139360 | 1742 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S129 Hunters Hill Panel 24 tripped on Relays: A and C phase O/C Signnals: 11kV Trip, Zone Earth and No3 Group Earth Abnormal Swicthing: SW/A at S61562 Open, SW/D closed at S3469 Cause not ascertained for outage See OMS 1192625 1192524 | December | 2014 | 2015Q2 | 2015 | ZN129:PA24 | ZN129:PA57 | ZN00129/000057 | LANE COVE | OH | Veg | 2014-12-24 | N | 80 | N | 14 | N | N | 1.1101 | 39.4971 | 101840.1776
[7 empty] | 13403 | 10183 | 1192552 | 2014-12-24 07:15 | 2014-12-24 08:30 | 75 | 11kV | 1275 | 17 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 114016 Repair burnt off tapping at pole GQ-52010 Excluded OMS 1192552, associated with report # 144008. | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-12-24 | N | 75 | N | 14 | N | N | 1.1101 | 39.4971 | 931.7324
[7 empty] | 13817 | 13392 | 1192490 | 2014-12-23 20:33 | 2014-12-24 08:35 | 722 | 11kV | 722 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 144008 Faulty txf replaced under AP. When re-energised, found a broken tapping at pole GQ-52010. | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-12-23 | N | 722 | N | 16 | N | N | 1.1101 | 39.4971 | 527.6163
[7 empty] | 12893 | 5915 | 1192806 | 2014-12-24 12:08 | 2014-12-24 13:30 | 82 | 11kV | 328 | 4 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 144020 Repair stranded wire adjacent 11kV links 40610 Excluded OMS 1192806 | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Not Veg | 2014-12-24 | N | 82 | N | 14 | N | N | 1.1101 | 39.4971 | 239.6927
[7 empty] | 13857 | 13748 | 1192694 | 2014-12-24 09:59 | 2014-12-24 14:05 | 246 | 11kV | 738 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 144019 B phase : 10 Amp Excluded OMS 1192694 | December | 2014 | 2015Q2 | 2015 | 238:34148 | 264:81240 | ZN00264/081240 | MAITLAND | OH | Veg | 2014-12-24 | N | 246 | N | 14 | N | N | 1.1101 | 39.4971 | 539.3086
[7 empty] | 13520 | 11079 | 1192866 | 2014-12-24 10:00 | 2014-12-24 14:30 | 270 | 11kV | 270 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 144022 Single phase DOLF : 3 Amp | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-24 | N | 270 | N | 14 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 13824 | 13444 | 1192812 | 2014-12-24 12:25 | 2014-12-24 14:35 | 130 | 11kV | 260 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 144023 C phase DOLF : 10 Amp sub isolated to cut away faulty arrestor Excluded OMS 1192812 | December | 2014 | 2015Q2 | 2015 | 524:33576 | 524:33576 | ZN00524/033576 | CESSNOCK | OH | Not Veg | 2014-12-24 | N | 130 | N | 14 | N | N | 1.1101 | 39.4971 | 190.0003
[7 empty] | 12959 | 6504 | 1192868 | 2014-12-24 13:32 | 2014-12-24 15:53 | 141 | 11kV | 39275 | 299 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | Wind Strong | N | @ ZN14143 Somersby, 11kv Panel 10 "Somersby East" feeder tripped, reclosed, tripped Relays: 'A' & 'B' phase timed O/C. 'B' phase IOC Signals: 11kv trip Field EFI's: Nil Remarks: cause not ascertained. Dop patrolled feeder | December | 2014 | 2015Q2 | 2015 | ZN14143:PA10 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Veg | 2014-12-24 | N | 131.3545 | N | 14 | N | N | 1.1101 | 39.4971 | 28701.0116
[7 empty] | 13248 | 8717 | 1194421 | 2014-12-24 16:59 | 2014-12-24 19:17 | 138 | 11kV | 15478 | 127 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144026 1 fault operation 3 phase Sensitive Earth Fault | December | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-12-24 | N | 121.874 | N | 14 | N | N | 1.1101 | 39.4971 | 11310.8659
[7 empty] | 12672 | 3913 | 1192960 | 2014-12-24 18:51 | 2014-12-24 19:34 | 43 | 11kV | 6497 | 158 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 144028 Single phase section isolated to repair wire down at sub 49942 Excluded oms 1192982, 1192985, 1192991 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-24 | N | 41.1203 | N | 14 | N | N | 1.1101 | 39.4971 | 4747.816
[7 empty] | 14542 | 19022 | 1192971 | 2014-12-24 16:59 | 2014-12-24 20:10 | 191 | 11kV | 191 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144033 Single phase Operator found DOLF fallen open. Replaced OK. excluded OMS 1192971. | December | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-12-24 | N | 191 | N | 14 | N | N | 1.1101 | 39.4971 | 139.5772
[7 empty] | 14519 | 18837 | 1192963 | 2014-12-24 19:17 | 2014-12-24 20:20 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144029 Single phase DOLF : 10 Amp | December | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-12-24 | N | 63 | N | 14 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 13755 | 12936 | 1193007 | 2014-12-24 20:49 | 2014-12-24 21:20 | 30.8167 | 11kV | 1910.6333 | 62 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT13972 Marina Natuna Ex S.12620 Noraville Panel 8 "Manda Av" - Road side HDO operated Remarks: Fuse fatigue | December | 2014 | 2015Q2 | 2015 | ZN12620:PA8 | ZN12620:PA8 | ZN12620/000008 | CENTRAL COAST | OH | Not Veg | 2014-12-24 | N | 30.8167 | N | 14 | N | N | 1.1101 | 39.4971 | 1396.2345
[7 empty] | 14583 | 19377 | 1192998 | 2014-12-24 20:14 | 2014-12-25 02:30 | 376 | 11kV | 752 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144030 3 phase DOLF : 10 Amp Arresters changed under AP. Fdr tripped on restore. Faulty txf changed under AP. Excluded oms 1192998. | December | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-12-24 | N | 376 | N | 14 | N | N | 1.1101 | 39.4971 | 549.5394
[7 empty] | 14063 | 15517 | 1193029 | 2014-12-25 04:05 | 2014-12-25 07:00 | 175 | 11kV | 175 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 144035 C phase DOLF : 10 Amp Faulty arresters changed under AP. | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-25 | N | 175 | N | 19 | N | N | 1.1101 | 39.4971 | 127.8848
[7 empty] | 14572 | 19239 | 1193046 | 2014-12-25 08:31 | 2014-12-25 10:15 | 104 | 11kV | 208 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 144037 Single phase DOLF : 10 Amp Excluded OMS 1193046 | December | 2014 | 2015Q2 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2014-12-25 | N | 104 | N | 19 | N | N | 1.1101 | 39.4971 | 152.0003
[7 empty] | 12999 | 6816 | 1193067 | 2014-12-25 10:55 | 2014-12-25 16:45 | 350 | 11kV | 5250 | 15 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S 6721 Botany Foreshore - HV CB - Low Gas. Low SF6 gas in HV breaker. T/PE to refill C/B. ME: 1194109. Withdrawn: 1193067. | December | 2014 | 2015Q2 | 2015 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | Unknown | Not Veg | 2014-12-25 | N | 350 | N | 19 | N | N | 1.1101 | 39.4971 | 3836.5452
[7 empty] | 12284 | 290 | 1193097 | 2014-12-25 16:04 | 2014-12-25 17:30 | 86 | 11kV | 86 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144047 DOLF : 10 Amp Excluded OMS 1193097 | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2014-12-25 | N | 86 | N | 19 | N | N | 1.1101 | 39.4971 | 62.8463
[7 empty] | 12761 | 4665 | 1193082 | 2014-12-25 07:24 | 2014-12-25 18:45 | 681 | 11kV | 11577 | 17 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | At PT18837 Wise Ferry Oyster 5.9 HDO assembly has failed. Section of Panel No.3 "USL 44917" feeder ex Sub 12630 Peats Ridge Remarsk: cause not ascertained. Dop interrupted PT's 18837 & 14007 @ 1640 pm | December | 2014 | 2015Q2 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2014-12-25 | N | 681 | N | 19 | N | N | 1.1101 | 39.4971 | 8460.1301
[7 empty] | 12875 | 5779 | 1193150 | 2014-12-25 18:10 | 2014-12-25 18:56 | 46 | 11kV | 1777 | 60 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | N | Ex Zn 12630 Peats Ridge 11kv OCB pnl 3 "Mangrove Mountain" feeder - Rec 46895 Wise Ferry Ironbark tripped and locked out on earth trip (Fault detection) Remarks: cause not ascertained. DOP patrolled nothing found. Possible lightning strike | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Veg | 2014-12-25 | N | 29.6167 | N | 19 | N | N | 1.1101 | 39.4971 | 1298.5792
[7 empty] | 13957 | 14608 | 1193182 | 2014-12-25 20:14 | 2014-12-25 20:19 | 5 | 11kV | 385 | 77 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Wind Storm | N | Ex Zn 12570 Avoca 11kv Panel 37L "Avoca Beach" feeder - Tree branch on section of 11kv feeder between S-14562 Chapman hillside to AB43305 tee to PT11045 Round Chapman Remarks: interrupted for safety reason. Dop interrupted PT11045 and isolated section of 11kv feeder for safety to remove branch | December | 2014 | 2015Q2 | 2015 | ZN12570:PA37 | ZN12570:PA37 | ZN12570/000037 | CENTRAL COAST | OH | Veg | 2014-12-25 | N | 5 | N | 19 | N | N | 1.1101 | 39.4971 | 281.3466
[7 empty] | 13296 | 9083 | 1193185 | 2014-12-25 19:15 | 2014-12-25 20:50 | 95 | 11kV | 475 | 5 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Wind Storm | N | Ex Zn12630 peats Ridge 11kv OCB panel 5 "SOMERSBY" feeder - @ PT13866 Wise Ferry Hensons 0.5 Road side 10A HVDO operated Remarks: Lightning. Possible lightning/fuse fattigue | December | 2014 | 2015Q2 | 2015 | ZN12630:PA5 | ZN12630:PA11 | ZN12630/000011 | CENTRAL COAST | OH | Not Veg | 2014-12-25 | N | 95 | N | 19 | N | N | 1.1101 | 39.4971 | 347.116
[7 empty] | 12334 | 777 | 1193207 | 2014-12-25 02:00 | 2014-12-25 21:40 | 1180 | 11kV | 3540 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144055 C phase DOLF : 10 Amp Excluded OMS 1193207 | December | 2014 | 2015Q2 | 2015 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Veg | 2014-12-25 | N | 1180 | N | 19 | N | N | 1.1101 | 39.4971 | 2586.9276
[7 empty] | 12416 | 1546 | 1193138 | 2014-12-25 17:50 | 2014-12-25 21:45 | 235 | 11kV | 10105 | 43 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Lightning | N | PT 2410 Galston Old Northern - Footpath HDO. Surge arrestor footpath side phase damaged by lightning. ME: 1194146. Withdrawn: 1193138. | December | 2014 | 2015Q2 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Not Veg | 2014-12-25 | N | 235 | N | 19 | N | N | 1.1101 | 39.4971 | 7384.436
[7 empty] | 12422 | 1582 | 1193234 | 2014-12-25 20:47 | 2014-12-25 22:00 | 73 | 11kV | 219 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 144056 B phase DOLF : 10 Amp Excluded OMS 1193234 & 1193249 | December | 2014 | 2015Q2 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2014-12-25 | N | 73 | N | 19 | N | N | 1.1101 | 39.4971 | 160.0387
[7 empty] | 13044 | 7113 | 1193223 | 2014-12-25 20:11 | 2014-12-25 23:01 | 170.4333 | 11kV | 37876.9167 | 476 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN 35370 Galston - Pnl 10 - SEF, EFI, Field EFIs. Cause not ascertained. Mains to patrol. ME: 1196425. REst STep: 1194123. GIS: 1193223. Note PT2410 already out at time of event due to previous outage | December | 2014 | 2015Q2 | 2015 | ZN35370:PA10 | ZN35370:PA10 | ZN35370/000010 | HORNSBY | OH | Veg | 2014-12-25 | N | 79.5734 | N | 19 | N | N | 1.1101 | 39.4971 | 27679.3335
[7 empty] | 13842 | 13609 | 1193183 | 2014-12-25 19:47 | 2014-12-25 23:15 | 208 | 11kV | 888 | 60 | HV | Lightning Strike | Adverse Weather/Environment | Fuse | Unplanned | Rain Wind Storm | N | Ex Zn 12630 Peats Ridge 11kv OCB pnl 3 "Mangrove Mountain" feeder Rec46895 Wise Ferry Ironbark - tripped reclosed reclosed tripped reclosed on O/C + IOC Remarks: lightning. @ PT11539 Berecry Meriki Dop found LHS HVDO operated. Suspect transformer/faulty lightning arrestors. Subs have restored supply via generator. | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2014-12-25 | N | 14.8 | N | 19 | N | N | 1.1101 | 39.4971 | 648.9242
[7 empty] | 13960 | 14649 | 1193175 | 2014-12-25 18:54 | 2014-12-25 23:40 | 286 | 11kV | 286 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144062 10 amp fuse Substation DOLF | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-25 | N | 286 | N | 19 | N | N | 1.1101 | 39.4971 | 209.0004
[7 empty] | 13298 | 9121 | 1192982 | 2014-12-24 18:51 | 2014-12-25 23:45 | 1734 | 11kV | 10352 | 163 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 144063 Single phase DOLF : 10 Amp sub isolated for replacement tx Excluded oms 1193176 | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2014-12-24 | N | 63.5092 | N | 14 | N | N | 1.1101 | 39.4971 | 7564.9363
[7 empty] | 13951 | 14587 | 1193148 | 2014-12-25 18:06 | 2014-12-26 00:21 | 375 | 11kV | 233037 | 1285 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | Lightning | N | ZN 847 Hornsby - Pnl 21 - Trip/reclose/trip, A & C phase timed OC, timing, EFI, Field EFIs. Tree branch removed by DOp outside 9 Manor Rd. All supply restored. ME: 1194682. Rest Steps: 1194683, 4, 5, 6. GIS: 1193232. Withdrawn: 1193148, 52, 93, 1193227, 42. | December | 2014 | 2015Q2 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2014-12-25 | N | 181.3518 | N | 19 | N | N | 1.1101 | 39.4971 | 170296.5662
[7 empty] | 13807 | 13328 | 1194688 | 2014-12-25 16:35 | 2014-12-26 00:44 | 489 | 11kV | 24378 | 132 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144046 1 fault operation Earth fault LID 144066 - Line Fuses at 40502 also operated 3 phase DOLF : 10 Amps replaced 3 x line fuses | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-25 | N | 184.6818 | N | 19 | N | N | 1.1101 | 39.4971 | 17814.7234
[7 empty] | 12513 | 2385 | 1193243 | 2014-12-25 21:50 | 2014-12-26 01:10 | 200 | 11kV | 1200 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 144067 20 amp fuse Line DOLF Replaces OMS 1193250 + 1193243 | December | 2014 | 2015Q2 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2014-12-25 | N | 200 | N | 19 | N | N | 1.1101 | 39.4971 | 876.9246
[7 empty] | 13630 | 11939 | 1193106 | 2014-12-25 17:18 | 2014-12-26 01:14 | 476.3833 | 11kV | 39218.7667 | 108 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Lightning | N | PT 2173 Balmoral Park Lane - Centre phase HDO Suspected transformer fault after lightning storm. ME: 1193132. GIS: 1193106. | December | 2014 | 2015Q2 | 2015 | ZN847:PA39 | ZN847:PA39 | ZN00847/000039 | HORNSBY | OH | Not Veg | 2014-12-25 | N | 363.1367 | N | 19 | N | N | 1.1101 | 39.4971 | 28659.9179
[7 empty] | 13350 | 9745 | 1193273 | 2014-12-26 04:47 | 2014-12-26 07:30 | 163 | 11kV | 1630 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 144069 DOLF : 16 Amp Excludsed OMS 1193273 | December | 2014 | 2015Q2 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2014-12-26 | N | 163 | N | 17 | N | N | 1.1101 | 39.4971 | 1191.1559
[7 empty] | 14434 | 18184 | 1193274 | 2014-12-26 05:09 | 2014-12-26 08:25 | 196 | 11kV | 784 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144070 10 Amp fuse Substation DOLF Replaces OMS 1193274 | December | 2014 | 2015Q2 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Veg | 2014-12-26 | N | 196 | N | 17 | N | N | 1.1101 | 39.4971 | 572.9241
[7 empty] | 13234 | 8602 | 1193290 | 2014-12-26 07:13 | 2014-12-26 09:00 | 107 | 11kV | 214 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144071 10 amp fuse Substation DOLF Replaces OMS 1193290 | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-12-26 | N | 107 | N | 17 | N | N | 1.1101 | 39.4971 | 156.3849
[7 empty] | 14276 | 17048 | 1193299 | 2014-12-26 08:09 | 2014-12-26 10:18 | 129.2333 | 11kV | 9567.8167 | 100 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 144072 B phase lead burnt off at top of DOLF. Excluded OMS 1193299 GIS Error Jobs 113308, 1193333. | December | 2014 | 2015Q2 | 2015 | 230:81434 | 230:81434 | ZN00230/081434 | PORT STEPHENS | OH | Not Veg | 2014-12-26 | N | 95.6782 | N | 17 | N | N | 1.1101 | 39.4971 | 6991.8782
[7 empty] | 13819 | 13397 | 1193197 | 2014-12-25 19:40 | 2014-12-26 10:30 | 890 | 11kV | 3560 | 4 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Rain Wind Storm | N | Ex ZN12630 Peats Ridge 11kv OCB Panel 3 "Mangrove Moutain Feeder - @ PT13945 Warratah Kelynack 0.6 - Roadside and centre 16A HVDO's operated Remarks: lightning @ PT13945 Warratah Kelynack suspect Transformer/faulty lightning arrestors. Dop and Subs to meet on site AM FRI 26/12/14 also refer to 1194350 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-12-25 | N | 890 | N | 19 | N | N | 1.1101 | 39.4971 | 2601.543
[7 empty] | 14032 | 15304 | 1193297 | 2014-12-26 07:40 | 2014-12-26 10:30 | 170 | 11kV | 1870 | 11 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Previous Storm | N | @ZN12630 Peats Ridge Section of Panel 3 'Mangrove Mtn' USL 42143 Opened in turn interrupting the following PTs: PT14944, PT13945, PT13974, PT11656 Remarks: interrupted for safety reasons. Repairs to PT13945 Waratah Kelynack 0.6 after lightning strike at the PT also refer to OMS 1193214 and 1193197 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA6 | ZN12630/000006 | CENTRAL COAST | OH | Not Veg | 2014-12-26 | N | 170 | N | 17 | N | N | 1.1101 | 39.4971 | 1366.5408
[7 empty] | 14114 | 15927 | 1193342 | 2014-12-26 09:43 | 2014-12-26 10:35 | 52 | 11kV | 52 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144076 Substation DOLF | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-26 | N | 52 | N | 17 | N | N | 1.1101 | 39.4971 | 38.0001
[7 empty] | 12277 | 188 | 1193267 | 2014-12-26 01:41 | 2014-12-26 11:10 | 569 | 11kV | 162678 | 1121 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Light | N | LID 144068 2 fault operation Overcurrent ; Intellirupter car hit pole wires down Excluded oms 1193267/8 | December | 2014 | 2015Q2 | 2015 | 232:33409 | 232:33409 | ZN00232/033409 | PORT STEPHENS | OH | Not Veg | 2014-12-26 | N | 145.1186 | N | 17 | N | N | 1.1101 | 39.4971 | 118880.2842
[7 empty] | 12484 | 2112 | 1193367 | 2014-12-26 10:43 | 2014-12-26 11:40 | 57 | 11kV | 57 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144075 Substation DOLF | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-26 | N | 57 | N | 17 | N | N | 1.1101 | 39.4971 | 41.6539
[7 empty] | 13367 | 9850 | 1193395 | 2014-12-26 10:50 | 2014-12-26 12:10 | 80 | 11kV | 880 | 11 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Not Transformer | Unplanned | Lightning | N | @ZN12630 Peats Ridge Section of Panel 3 "Mangrove Mtn" from USL 41548 opened in turn interrupting the following PTS:PT11539, PT18336, PT18841 Remarks: Interrupted for safety reasons. Repairs to PT11539 Berecry Meriki 0.6 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2014-12-26 | N | 80 | N | 17 | N | N | 1.1101 | 39.4971 | 643.078
[7 empty] | 12860 | 5641 | 1193406 | 2014-12-26 13:13 | 2014-12-26 13:45 | 32 | 11kV | 64 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144077 10 amp fuse Line DOLF Replaces OMS 1193406 DOLF replaced at L/F 40855 and at sub 51241 | December | 2014 | 2015Q2 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2014-12-26 | N | 32 | N | 17 | N | N | 1.1101 | 39.4971 | 46.7693
[7 empty] | 13508 | 10990 | 1193437 | 2014-12-26 15:29 | 2014-12-26 16:20 | 51 | 11kV | 102 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144078 10 amp fuse Substation DOLF Replaces OMS 1193437 | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2014-12-26 | N | 51 | N | 17 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 14036 | 15327 | 1193440 | 2014-12-26 15:46 | 2014-12-26 17:40 | 114 | 11kV | 684 | 6 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 144080 16 amp fuse Substation DOLF replaced OMS 1193440 | December | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-12-26 | N | 114 | N | 17 | N | N | 1.1101 | 39.4971 | 499.847
[7 empty] | 13242 | 8700 | 1193453 | 2014-12-26 16:55 | 2014-12-26 18:35 | 100 | 11kV | 300 | 3 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 144082 BROKEN LIVE LINE LEAD Replaces OMS 1193453 (SW IS SWINGING IN THE WIND AND ARCING AGAINST POLE) | December | 2014 | 2015Q2 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2014-12-26 | N | 100 | N | 17 | N | N | 1.1101 | 39.4971 | 219.2312
[7 empty] | 14268 | 17003 | 1193464 | 2014-12-26 18:00 | 2014-12-26 20:20 | 140 | 11kV | 280 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 144083 5 amp fuse Line DOLF replaces OMS 1193464 | December | 2014 | 2015Q2 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Veg | 2014-12-26 | N | 140 | N | 17 | N | N | 1.1101 | 39.4971 | 204.6157
[7 empty] | 12324 | 670 | 1193481 | 2014-12-26 21:40 | 2014-12-26 22:40 | 60 | 11kV | 60 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 144084 A phase LL Clamp lead broken. Isolate & repair. Excluded oms 1193481. | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | SINGLETON | OH | Not Veg | 2014-12-26 | N | 60 | N | 17 | N | N | 1.1101 | 39.4971 | 43.8462
[7 empty] | 13356 | 9760 | 1193523 | 2014-12-27 10:20 | 2014-12-27 11:00 | 40 | 11kV | 120 | 3 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Previous Storm | N | LID 144090 No protection operations, tree found leaning on 11kV CCT beyond 11kV link 3527. | December | 2014 | 2015Q2 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2014-12-27 | N | 40 | N | 8 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 12739 | 4548 | 1193492 | 2014-12-26 22:05 | 2014-12-27 11:35 | 810 | 11kV | 1514 | 9 | HV | Equipment Failed in Service | Equipment Failure | Pole | Unplanned | No Weather Impact | N | LID 144085 Replaces OMS 1193492. Isolate for fire brigade & open ll clamps to sub 47839 | December | 2014 | 2015Q2 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2014-12-26 | N | 168.2222 | N | 17 | N | N | 1.1101 | 39.4971 | 1106.3865
[7 empty] | 12938 | 6296 | 1193489 | 2014-12-26 21:08 | 2014-12-27 12:10 | 902 | 11kV | 44527 | 60 | HV | Lightning Strike | Adverse Weather/Environment | Recloser / Sectionaliser | Unplanned | Rain Wind Storm | N | Ex Zn12630 Peats Ridge 11kv OCB panel 3 "Mangrove Mountain" feeder @ PT18336 Berecry Meriki 1.1 Roadside 16A HVDO operated REC 46895 Wise Ferry Ironbark tripped and reclosed on - IOC + O/C Remarks: Possible lightning customer states without supply since 25/12/2014. Rec 46895 tripped and reclosed @ 09:08 am when Dop tried back HVDO. @ PT18336 lightning arrestors replaced by T/Con. Dop interrupted from LK 44280 @ 10:45am 27/12/14 | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2014-12-26 | N | 742.1167 | N | 17 | N | N | 1.1101 | 39.4971 | 32539.0183
[7 empty] | 14674 | 20309 | 1193559 | 2014-12-27 09:04 | 2014-12-27 12:53 | 229 | 11kV | 229 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 144091 1 fault operation Replaces OMS 1193559. LV coircuit breaker tripped reset OK after having checked with customer. | December | 2014 | 2015Q2 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2014-12-27 | N | 229 | N | 8 | N | N | 1.1101 | 39.4971 | 167.3464
[7 empty] | 12628 | 3465 | 1193587 | 2014-12-27 11:42 | 2014-12-27 13:15 | 93 | 11kV | 651 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 144092 A phase DOLF : 16 Amp Excluded OMS 1193587 | December | 2014 | 2015Q2 | 2015 | 511:29873 | 511:29873 | ZN00511/029873 | MAITLAND | OH | Veg | 2014-12-27 | N | 93 | N | 8 | N | N | 1.1101 | 39.4971 | 475.7316
[7 empty] | 13379 | 9965 | 1193504 | 2014-12-27 02:37 | 2014-12-27 14:45 | 728 | 11kV | 69029 | 364 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | LID 144088 2 fault operation Single phase Earth Fault Pole fire one pole past ABS 40388. Suspected HV and LV contact, Steve Geddes checked and said no damage. Excluded OMS 1193504 | December | 2014 | 2015Q2 | 2015 | 508:82579 | 508:82580 | ZN00508/082580 | PORT STEPHENS | OH | Not Veg | 2014-12-27 | N | 189.6401 | N | 8 | N | N | 1.1101 | 39.4971 | 50444.3572
[7 empty] | 13210 | 8473 | 1193597 | 2014-12-27 13:20 | 2014-12-27 15:45 | 145 | 11kV | 43030 | 328 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Insulated | Unplanned | No Weather Impact | N | @ZN12660 Woy Woy exiting Panel #14 labelled "South Woy Woy" Section of 11kv overhead down from Rec 48036 Rawson Woy Woy to USL 41623 Note: no relay operations Abnormal: Closed @ LB42482. Open @ LB43375 Remarks: OH Down. @ Zn12660 Woy Woy exiting Panel #14 labelled "South Woy Woy" 11kv overhead down line side of USL 41623 | December | 2014 | 2015Q2 | 2015 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Not Veg | 2014-12-27 | N | 131.189 | N | 8 | N | N | 1.1101 | 39.4971 | 31445.0548
[7 empty] | 13791 | 13228 | 1193628 | 2014-12-27 16:25 | 2014-12-27 19:10 | 165 | 11kV | 330 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 144094 10 amp fuse Substation DOLF DOLF BLOWN & LV WIRING REPAIRED | December | 2014 | 2015Q2 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2014-12-27 | N | 165 | N | 8 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 13629 | 11935 | 1193650 | 2014-12-27 19:44 | 2014-12-27 20:55 | 71 | 11kV | 90720 | 1326 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 187 Crows Nest - Pnl 17 - A & B phase OC and Earth Fault relay, EFI, Fault Check, Field EFIs. 11kV underground feeder failed in service from S 48856 to S 2462 to S 47959. ME: 1194486. Rest Step: 1194487. Withdrawn: 1193650. | December | 2014 | 2015Q2 | 2015 | ZN187:PA17 | ZN187:PA17 | ZN00187/000017 | NORTH SYDNEY | UG | Not Veg | 2014-12-27 | N | 68.4163 | N | 8 | N | N | 1.1101 | 39.4971 | 66295.5002
[7 empty] | 14621 | 19897 | 1193641 | 2014-12-27 18:56 | 2014-12-27 20:56 | 119.9667 | 11kV | 37656.4333 | 604 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 340 Botany - Pnl 3 - Earth Fault, EFI, Field EFIs. Underground feeder failed in service between S 7520 to S 3807 tee S 2122. ME: 1194381. Rest Steps: 1194383, 4. GIS: 1193646. | December | 2014 | 2015Q2 | 2015 | ZN340:PA3 | ZN340:PA3 | ZN00340/000003 | BAYSIDE | UG | Not Veg | 2014-12-27 | N | 62.3451 | N | 8 | N | N | 1.1101 | 39.4971 | 27518.2108
[7 empty] | 12946 | 6399 | 1193672 | 2014-12-28 04:24 | 2014-12-28 05:55 | 91 | 11kV | 86857 | 1140 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S12650 West Gosford Panel 9 "Wyoming" tripped, reclosed and locked out on: Relays - Panel 9R: Earth Fault, EFI, Timer, Lockout Signals: 11kv trip, Zone Earth EFI's: Nil Remarks: UG fault. UG Fault from S12650 West Gosford Panel 9 to S18466 Gertrude Dwyer Sw/A to S13582 Pacific Yallambee Sw/A | December | 2014 | 2015Q2 | 2015 | ZN12650:PA9 | ZN12650:PA9 | ZN12650/000009 | CENTRAL COAST | UG | Not Veg | 2014-12-28 | N | 76.1904 | N | 5 | N | N | 1.1101 | 39.4971 | 63472.5338
[7 empty] | 14687 | 20429 | 1193670 | 2014-12-28 00:34 | 2014-12-28 08:35 | 481 | 11kV | 1443 | 3 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 144096 5 amp fuse Substation DOLF Replaces OMS 1193670 and 1196375. Cause contact by a possum. | December | 2014 | 2015Q2 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2014-12-28 | N | 481 | N | 5 | N | N | 1.1101 | 39.4971 | 1054.5018
[7 empty] | 13846 | 13647 | 1193676 | 2014-12-28 06:42 | 2014-12-28 09:00 | 138 | 11kV | 414 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At PT18841 Berecry Meriki 1.3: 2 HDOs Operated 16 amp Section of 11kv feeder Panel No3 "Mangrove Mountain" feeder @ S12630 Peats Ridge Remarks: Fuse equipment - details below. HV crimp failure at HDO at PT18841, Dop replaced both elements | December | 2014 | 2015Q2 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2014-12-28 | N | 138 | N | 5 | N | N | 1.1101 | 39.4971 | 302.539
[7 empty] | 12910 | 6056 | 1193757 | 2014-12-28 16:41 | 2014-12-29 07:50 | 909 | 11kV | 909 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 144105 Single phase DOLF : 10 Amp Volts before leaving 249V and 15A load. Note Customer reported outage Sunday but requested staff not attend until 7am Monday. | December | 2014 | 2015Q2 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2014-12-28 | N | 909 | N | 5 | N | N | 1.1101 | 39.4971 | 664.2704
[7 empty] | 14607 | 19764 | 1193920 | 2014-12-29 09:52 | 2014-12-29 11:23 | 91 | 11kV | 63326 | 726 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 9301 Kurnell - Pnl 8 - Trip/reclose/trip, A & C phase timed OC, timing, lockout, EFI, Field EFIs. 11kV underground cable fault between S 9473 and S 9479. ME: 1194521. Rest Step: 1194523. Withdrawn: 1193920. | December | 2014 | 2015Q2 | 2015 | ZN9301:PA8 | ZN9534:PA17 | ZN09534/000017 | SUTHERLAND | UG | Not Veg | 2014-12-29 | N | 87.2259 | N | 4 | N | N | 1.1101 | 39.4971 | 46276.773
[7 empty] | 13264 | 8866 | 1193891 | 2014-12-29 09:26 | 2014-12-29 12:45 | 199 | 11kV | 4378 | 22 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 144109 A phase DOLF : 16 Amp Three spans of 11kV mains on the ground, between poles 8M-80036 and 8m-80048. Staff advised no 11kV to LV contact. Excluded OMS 1193891, 1193892, 1193911 and 1193985. repaired rusty mains | December | 2014 | 2015Q2 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2014-12-29 | N | 199 | N | 4 | N | N | 1.1101 | 39.4971 | 3199.3133
[7 empty] | 12509 | 2339 | 1194010 | 2014-12-29 06:00 | 2014-12-29 14:20 | 500 | 11kV | 500 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 144110 10 amp fuse Substation DOLF | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-29 | N | 500 | N | 4 | N | N | 1.1101 | 39.4971 | 365.3853
[7 empty] | 12787 | 4900 | 1194257 | 2014-12-29 23:16 | 2014-12-30 02:12 | 176 | 11kV | 51482 | 851 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At S12600 Lisarow: 11kv feeder Panel No13 "Brush Rd" tripped Relays: B phase O/C, lockout, reclose, timing, EFI Remarks: 11kv Bond footpath phase on cnr Shirley and Ourimbah Rd on Pole: OU 2405 (Section of: 11kv feeder Panel No13 "Brush Rd at S12600 Lisarow) | December | 2014 | 2015Q2 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Not Veg | 2014-12-29 | N | 60.4959 | N | 4 | N | N | 1.1101 | 39.4971 | 37621.5271
[7 empty] | 13893 | 14049 | 1194266 | 2014-12-30 03:25 | 2014-12-30 07:45 | 260 | 11kV | 3900 | 15 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Circuit Breaker | Unplanned | No Weather Impact | N | At S6721 Botany Foreshore 11kv RMI/CB tripped on LOW Gas Ex S1788 Matraville: Panel NO21 "S5180, S7169" feeder Remarks: Low SF6 Gas. At S6721 Botany Foreshore 11kv RMI/CB tripped on Low gas, TPE to refill until replacement to be organized ASAP, previously occurred 25/12 | December | 2014 | 2015Q2 | 2015 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | Unknown | Unknown | 2014-12-30 | N | 260 | N | 4 | N | N | 1.1101 | 39.4971 | 2850.005
[7 empty] | 12740 | 4559 | 1194667 | 2014-12-28 09:58 | 2014-12-30 13:30 | 3092 | 11kV | 28538 | 220 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | LID 144097 1 fault operation Sensitive Earth Fault Dops S Carson and B Eyeington also attended with V Hickey. sub 50462 faulty. TX to be changed 29/12/2014. Irrigation sub only. | December | 2014 | 2015Q2 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2014-12-28 | N | 129.7182 | N | 5 | N | N | 1.1101 | 39.4971 | 20854.7287
[7 empty] | 12927 | 6218 | 1194535 | 2014-12-30 17:20 | 2014-12-30 18:15 | 55 | 11kV | 220 | 4 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 144119 Interrupt to repair broken tie wire at pole BM60023 | December | 2014 | 2015Q2 | 2015 | 514:18146 | 514:18156 | ZN00514/018156 | MUSWELLBROOK | OH | Not Veg | 2014-12-30 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 160.7695
[7 empty] | 13396 | 10134 | 1194605 | 2014-12-30 23:57 | 2014-12-31 00:29 | 32 | 11kV | 20064 | 627 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN 9037 Miranda - Pnl 7 - C phase IOC, EFI, Field EFIs. Possum found at base of UGOH on Bates Rd near AB 35626. No apparent damage caused. ME: 1194605. Withdrawn: 1194606. | December | 2014 | 2015Q2 | 2015 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2014-12-30 | N | 32 | N | 4 | N | N | 1.1101 | 39.4971 | 14662.1794
[7 empty] | 13936 | 14474 | 1194657 | 2014-12-30 23:18 | 2014-12-31 07:55 | 517 | 11kV | 517 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 144122 1 fault operation Instantaneous overcurrent B/C Inst O/C B phase 3612 Amps C phase 3569 Amps Ausgrid patrol nothing found. Ian O'Brian to arrange patrol of there equipment in the morning. Site on shut down for 3 weeks | December | 2014 | 2015Q2 | 2015 |  |  |  | SINGLETON | OH | Veg | 2014-12-30 | N | 517 | N | 4 | N | N | 1.1101 | 39.4971 | 377.8084
[7 empty] | 14629 | 19975 | 1194797 | 2014-12-31 15:54 | 2014-12-31 17:35 | 101 | 11kV | 101 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 144131 10A Substation DOLF replaced - no cause found | December | 2014 | 2015Q2 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Veg | 2014-12-31 | N | 101 | N | 1 | N | N | 1.1101 | 39.4971 | 73.8078
[7 empty] | 13622 | 11919 | 1194843 | 2015-01-01 06:21 | 2015-01-01 10:00 | 219 | 11kV | 3504 | 16 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S6721 Botany Foreshore - 11kV RMCB tripped on Low Gas Low SF6 gas - T/PE refilled, replacement due 3/1/14. see 1195874 GIS: 1194845 | January | 2015 | 2015Q3 | 2015 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | Unknown | Not Veg | 2015-01-01 | N | 219 | N | 4 | N | N | 1.1101 | 39.4971 | 2560.6198
[7 empty] | 12572 | 3032 | 1194902 | 2015-01-01 16:58 | 2015-01-01 17:42 | 44 | 11kV | 30184 | 686 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | LID 154135 1 fault operation A & C phase Overcurrent Targets 51AC | January | 2015 | 2015Q3 | 2015 | 813:89065 | 813:89065 | ZN00813/089065 | UPPER HUNTER | Unknown | Unknown | 2015-01-01 | N | 44 | N | 4 | N | N | 1.1101 | 39.4971 | 22057.5769
[7 empty] | 14412 | 18000 | 1194900 | 2015-01-01 16:59 | 2015-01-01 18:00 | 61 | 11kV | 915 | 15 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 154134 B Phase 10 A DOLF - caused by animal/bird | January | 2015 | 2015Q3 | 2015 | 507:80922 | 507:80922 | ZN00507/080922 | CESSNOCK | OH | Not Veg | 2015-01-01 | N | 61 | N | 4 | N | N | 1.1101 | 39.4971 | 668.655
[7 empty] | 12292 | 352 | 1194947 | 2015-01-01 21:07 | 2015-01-02 03:38 | 391 | 11kV | 14785 | 59 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 154141 1 fault operation A & B phase Overcurrent | January | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-01-01 | N | 250.5932 | N | 4 | N | N | 1.1101 | 39.4971 | 10804.4419
[7 empty] | 13457 | 10604 | 1194981 | 2015-01-02 02:53 | 2015-01-02 03:59 | 66 | 11kV | 32340 | 490 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Lightning | N | Zn12650 West Gosford Panel 14R "Erina St" fdr tripped Relays - IOC Signals: 11kv trip Cause: tree rbanch contact - other Palm frond appears to have contacted mains near right of way in Holden st. Also appeared as though did not have a reclose attempt See 1195999 exclude 1194981,4,6 | January | 2015 | 2015Q3 | 2015 | ZN12650:PA14 | ZN12650:PA14 | ZN12650/000014 | CENTRAL COAST | OH | Veg | 2015-01-02 | N | 66 | N | 34 | Y | Y | 1.1101 | 39.4971 | 23633.1181
[7 empty] | 12788 | 4901 | 1194970 | 2015-01-02 00:50 | 2015-01-02 04:37 | 227 | 11kV | 163042 | 836 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | Zn12660 Lisarow Panel 13 "Bursh Rd" fdr tripped Relays - C phase overcurrent, SEF, Reclose TImer, Lockout Signals: 11kv trip ABNORMAL: AB44898 Open LB44503 closed Cause not ascertained. Mains to Patrol See 1195948,50 Exclude 1194970,1 | January | 2015 | 2015Q3 | 2015 | ZN12600:PA13 | ZN12600:PA13 | ZN12600/000013 | CENTRAL COAST | OH | Veg | 2015-01-02 | N | 195.0263 | N | 34 | Y | Y | 1.1101 | 39.4971 | 119146.2847
[7 empty] | 14416 | 18033 | 1194994 | 2015-01-02 06:04 | 2015-01-02 08:05 | 121.0333 | 11kV | 242.0667 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150006 Single phase DOLF : 10 Amp Replaced blown dolf on sub 51472 10A Excludes OMS 1195024 | January | 2015 | 2015Q3 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Veg | 2015-01-02 | N | 121.0333 | N | 34 | Y | Y | 1.1101 | 39.4971 | 176.8952
[7 empty] | 14495 | 18644 | 1194977 | 2015-01-02 02:28 | 2015-01-02 08:45 | 377 | 11kV | 5655 | 15 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | S6721 Botany Foreshore - 11kV RMCB tripped on Low Gas Low SF6 gas - T/PE refilled, replacement due 3/1/15. | January | 2015 | 2015Q3 | 2015 | ZN1788:PA21 | ZN35700:PA12 | ZN35700/000012 | BAYSIDE | Unknown | Not Veg | 2015-01-02 | N | 377 | N | 34 | Y | Y | 1.1101 | 39.4971 | 4132.5072
[7 empty] | 13055 | 7214 | 1194980 | 2015-01-02 02:51 | 2015-01-02 09:00 | 369.2 | 11kV | 17352.4 | 47 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150005 3 phase DOLF : 40 Amp | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-01-02 | N | 369.2 | N | 34 | Y | Y | 1.1101 | 39.4971 | 12680.6221
[7 empty] | 14590 | 19479 | 1194988 | 2015-01-02 03:44 | 2015-01-02 09:10 | 326 | 11kV | 1304 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150008 C phase DOLF : 10 Amp | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-01-02 | N | 326 | N | 34 | Y | Y | 1.1101 | 39.4971 | 952.9247
[7 empty] | 12752 | 4611 | 1195047 | 2015-01-02 08:16 | 2015-01-02 10:08 | 112 | 11kV | 224 | 2 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 150021 B phase Bph LL clamp burnt off. Excluded OMS No. 1195047 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 112 | N | 34 | Y | Y | 1.1101 | 39.4971 | 163.6926
[7 empty] | 13433 | 10448 | 1194982 | 2015-01-02 02:48 | 2015-01-02 10:10 | 442 | 11kV | 257574 | 910 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 154142 3 fault operation B & C phase Overcurrent; Earth fault Broken insulator pole SF-60016 & 11kV OHM down at pole FP-90731. Excluded OMS NO.1194982 + 1194989 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 283.0484 | N | 34 | Y | Y | 1.1101 | 39.4971 | 188227.4821
[7 empty] | 14288 | 17141 | 1195066 | 2015-01-02 09:15 | 2015-01-02 10:21 | 66 | 11kV | 46248 | 953 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @ ZN.2473 North Sydney 11kV Panel 8 feeder tripped on:- Relays:- Translay Signals:- 11kV trip, Tx.2 GE, ZE Field EFI's:- S.8429, S.7482 Cause:- 11kV UG cable fault between S.7482 SW/B and S.6391 tee Tx No.1 ME:-1195887 RS:-1195888 Withdrawn:-1195066 | January | 2015 | 2015Q3 | 2015 | ZN2473:PA8 | ZN35400:PA79 | ZN35400/000079 | NORTH SYDNEY | UG | Not Veg | 2015-01-02 | N | 48.5289 | N | 34 | Y | Y | 1.1101 | 39.4971 | 33796.6743
[7 empty] | 14438 | 18218 | 1195000 | 2015-01-02 06:28 | 2015-01-02 10:55 | 267 | 11kV | 1335 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150014 B phase DOLF : 10 Amp | January | 2015 | 2015Q3 | 2015 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2015-01-02 | N | 267 | N | 34 | Y | Y | 1.1101 | 39.4971 | 975.5786
[7 empty] | 13854 | 13717 | 1195084 | 2015-01-02 10:02 | 2015-01-02 10:56 | 54 | 11kV | 108 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150015 A & C phase DOLF : 10 Amp Tx Volts: 250V Tx Load: 1A Excluded OMS No. 1195084 | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-01-02 | N | 54 | N | 34 | Y | Y | 1.1101 | 39.4971 | 78.9232
[7 empty] | 14652 | 20139 | 1194976 | 2015-01-02 02:25 | 2015-01-02 11:00 | 515 | 11kV | 4635 | 9 | HV | Lightning Strike | Adverse Weather/Environment | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Replace A&B phase 16A on L/F 40675 Grouped with OMS 1198983 + 1195072 Replaces OMS 1194976 | January | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 515 | N | 34 | Y | Y | 1.1101 | 39.4971 | 3387.1213
[7 empty] | 13389 | 10083 | 1195012 | 2015-01-02 06:58 | 2015-01-02 11:10 | 252 | 11kV | 1008 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150016 A phase DOLF : 16 Amp Tx Volts: Aph - 246V, Bph - 248V, Cph - 246V Excluded OMS 1195012 | January | 2015 | 2015Q3 | 2015 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2015-01-02 | N | 252 | N | 34 | Y | Y | 1.1101 | 39.4971 | 736.6167
[7 empty] | 12390 | 1320 | 1195067 | 2015-01-02 09:21 | 2015-01-02 11:20 | 119 | 11kV | 476 | 4 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150017 Replaced blown dolf on sub 53190 A phase 10A Excluded OMS 1195067 | January | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 119 | N | 34 | Y | Y | 1.1101 | 39.4971 | 347.8468
[7 empty] | 13667 | 12252 | 1195034 | 2015-01-02 07:40 | 2015-01-02 11:40 | 240 | 11kV | 1680 | 7 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150019 C phase DOLF : 10 Amp Excluded OMS 1195034 | January | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2015-01-02 | N | 240 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1227.6944
[7 empty] | 13117 | 7770 | 1195040 | 2015-01-02 07:57 | 2015-01-02 11:50 | 233 | 11kV | 699 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150010 A & C phase DOLF : 10 Amp Tx volts : 247 V Excluded OMS 1195040 | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-01-02 | N | 233 | N | 34 | Y | Y | 1.1101 | 39.4971 | 510.8086
[7 empty] | 13700 | 12542 | 1194978 | 2015-01-02 02:29 | 2015-01-02 11:55 | 565.6333 | 11kV | 25453.5 | 45 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 150009 A phase DOLF : 16 Amp Remade 11KV tapping at Pole No eq400023 | January | 2015 | 2015Q3 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 565.6333 | N | 34 | Y | Y | 1.1101 | 39.4971 | 18600.667
[7 empty] | 14214 | 16609 | 1195022 | 2015-01-02 07:11 | 2015-01-02 12:15 | 304 | 11kV | 608 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150018 Single phase DOLF : 20 Amp 20A LF blown 10A 1ph sub DOLF blown replaced at 1145hrs. Excluded OMS 1195022 | January | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | MAITLAND | OH | Veg | 2015-01-02 | N | 304 | N | 34 | Y | Y | 1.1101 | 39.4971 | 444.3085
[7 empty] | 12955 | 6489 | 1195112 | 2015-01-02 11:01 | 2015-01-02 12:22 | 81 | 11kV | 162 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Lightning | N | also refer to 1195112 | January | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2015-01-02 | N | 81 | N | 34 | Y | Y | 1.1101 | 39.4971 | 118.3848
[7 empty] | 13355 | 9759 | 1194993 | 2015-01-02 06:02 | 2015-01-02 12:29 | 387 | 11kV | 8127 | 21 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 150020 Aph 11kV tapping burnt off source side of USL 6L790. Excluded OMS No. 1195007 + 1195015 + 1195025 + 1194993 | January | 2015 | 2015Q3 | 2015 | 810:74054 | 810:74054 | ZN00810/074054 | UPPER HUNTER | OH | Not Veg | 2015-01-02 | N | 387 | N | 34 | Y | Y | 1.1101 | 39.4971 | 5938.9719
[7 empty] | 13624 | 11923 | 1195001 | 2015-01-02 09:50 | 2015-01-02 12:50 | 180 | 11kV | 2340 | 13 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 150022 A phase DOLF : 20 Amp Replaced blown LA's. Excluded OMS No. 1195001 Note: LID Start time is 06:30, however these customer were also affected by 2 other concurrent sustained events refer to OMS 1196275 and 1196243 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 180 | N | 34 | Y | Y | 1.1101 | 39.4971 | 1710.003
[7 empty] | 14290 | 17175 | 1195127 | 2015-01-02 11:40 | 2015-01-02 12:56 | 76 | 11kV | 64279 | 894 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S262 Marrickville Panel 32 'S1408 Samuel St' fdr tripped on Relays - EF, EFI, Fault check Signals - 11kv trip, ZE, TX1 GE Remarks: 11kv UG fdr fault from S7164 Smith Princes to S50159 Wood Smith No.2 | January | 2015 | 2015Q3 | 2015 | ZN262:PA32 | ZN262:PA32 | ZN00262/000032 | INNER WEST | UG | Not Veg | 2015-01-02 | N | 71.9004 | N | 34 | Y | Y | 1.1101 | 39.4971 | 46973.1973
[7 empty] | 14147 | 16164 | 1195107 | 2015-01-02 10:46 | 2015-01-02 13:05 | 139 | 11kV | 417 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section fo Pa17 PT14845 Jones Peats Ridge 0.05 Centre phase 15 amp HDO operated Cause not ascertained See 1196044 exclude 1195107 | January | 2015 | 2015Q3 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-01-02 | N | 139 | N | 34 | Y | Y | 1.1101 | 39.4971 | 304.7313
[7 empty] | 14097 | 15764 | 1195119 | 2015-01-02 11:16 | 2015-01-02 13:30 | 134 | 11kV | 402 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150027 A & C phase DOLF : 10 Amp Excluded OMS 1195119,1195120,1195137 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-01-02 | N | 134 | N | 34 | Y | Y | 1.1101 | 39.4971 | 293.7697
[7 empty] | 14064 | 15530 | 1195139 | 2015-01-02 12:06 | 2015-01-02 15:10 | 184 | 11kV | 552 | 3 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of Pa21 "Somersby" PT13301 Debenham Gindura 11kV roadside 16Amp Dropout fuse operated Fuse Fatigue See 1196045 exclude 1195139 | January | 2015 | 2015Q3 | 2015 | ZN14143:PA21 | ZN14143:PA21 | ZN14143/000021 | CENTRAL COAST | OH | Not Veg | 2015-01-02 | N | 184 | N | 34 | Y | Y | 1.1101 | 39.4971 | 403.3853
[7 empty] | 14013 | 15082 | 1195191 | 2015-01-02 12:00 | 2015-01-02 15:15 | 195 | 11kV | 390 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150031 B phase DOLF : 10 Amp Excluded OMS 1195191 | January | 2015 | 2015Q3 | 2015 | 513:48050 | 513:83502 | ZN00513/083502 | SINGLETON | OH | Veg | 2015-01-02 | N | 195 | N | 34 | Y | Y | 1.1101 | 39.4971 | 285.0005
[7 empty] | 13343 | 9689 | 1196027 | 2015-01-02 09:50 | 2015-01-02 15:30 | 340 | 11kV | 680 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 150026 Replace damaged transformer & LA's. Excluded OMS 1194997 Note: LID Start time was actually 06:42 however these customers were also affected by previous and concurrent outages refer to 1196243 and 1196275 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 340 | N | 34 | Y | Y | 1.1101 | 39.4971 | 496.9239
[7 empty] | 12297 | 433 | 1194998 | 2015-01-02 06:26 | 2015-01-02 15:40 | 554 | 11kV | 554 | 1 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | LID 150025 Single phase Tapping burnt off source side of LF 40699. Excluded OMS No. 1194998 | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 554 | N | 34 | Y | Y | 1.1101 | 39.4971 | 404.8469
[7 empty] | 14324 | 17343 | 1195192 | 2015-01-02 14:45 | 2015-01-02 16:05 | 80 | 11kV | 240 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150033 A phase DOLF : 10 Amp Excluded OMS 1195192 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-01-02 | N | 80 | N | 34 | Y | Y | 1.1101 | 39.4971 | 175.3849
[7 empty] | 14371 | 17694 | 1195027 | 2015-01-02 02:55 | 2015-01-02 16:47 | 832 | 11kV | 64164 | 99 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | Electrical Storm | N | LID 150001 1 fault operation 11kV OHM down between pole GQ-14604 & Leconfield RAGCB 3989. Excluded OMS No. 1194985 | January | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 648.1212 | N | 34 | Y | Y | 1.1101 | 39.4971 | 46889.1587
[7 empty] | 13204 | 8462 | 1195115 | 2015-01-02 14:00 | 2015-01-02 17:10 | 190 | 11kV | 570 | 3 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 150034 Three phase DOLF : 10 Amp Excluded OMS 1195115 | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 190 | N | 34 | Y | Y | 1.1101 | 39.4971 | 416.5392
[7 empty] | 13221 | 8545 | 1195043 | 2015-01-02 08:08 | 2015-01-02 17:18 | 550 | 11kV | 13252 | 43 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | Electrical Storm | N | LID 150024 POLE CN-80658 BURNT DOWN. Excluded OMS REPORT NO 1195043. | January | 2015 | 2015Q3 | 2015 | 516:48065 | 516:48065 | ZN00516/048065 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 308.186 | N | 34 | Y | Y | 1.1101 | 39.4971 | 9684.1707
[7 empty] | 13141 | 7910 | 1195246 | 2015-01-02 17:45 | 2015-01-02 18:56 | 71 | 11kV | 213 | 3 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 150037 clearance to replace 66kv insulators oms 1195246 see si 3894 | January | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 71 | N | 34 | Y | Y | 1.1101 | 39.4971 | 155.6541
[7 empty] | 13074 | 7425 | 1195240 | 2015-01-02 16:48 | 2015-01-02 19:16 | 148 | 11kV | 296 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 150039 Cross reference with earlier OMS 1196321 + 1196671 Customers out from 02.55 to 16.47 10 amp Substation DOLF blown also 11kV OHM down between pole GQ-14604 & Leconfield RAGCB 3989. | January | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83736 | ZN00512/083736 | SINGLETON | OH | Not Veg | 2015-01-02 | N | 148 | N | 34 | Y | Y | 1.1101 | 39.4971 | 216.3081
[7 empty] | 13299 | 9125 | 1195345 | 2015-01-03 07:00 | 2015-01-03 09:00 | 120 | 11kV | 480 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150041 A Phgase DOLF : 10 Amp excluded OMS 1195345 | January | 2015 | 2015Q3 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-01-03 | N | 120 | N | 9 | N | N | 1.1101 | 39.4971 | 350.7698
[7 empty] | 12817 | 5166 | 1195347 | 2015-01-03 03:16 | 2015-01-03 11:05 | 469 | 11kV | 2345 | 5 | HV | Animal Possum | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | Ex Zn14143 Somersby section of pa17 "Somersby Falls" RElays - Earth Fault and EFI EFI's - S18569 not down, S18639 EFI LED 160 Amps @PT11371 Pacific Ashrbooke 0.7 HDO operated middle phase 10Amp Possum on PT See 1196361 exclude 1195347 | January | 2015 | 2015Q3 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Not Veg | 2015-01-03 | N | 469 | N | 9 | N | N | 1.1101 | 39.4971 | 1713.6568
[7 empty] | 13402 | 10182 | 1195371 | 2015-01-03 12:30 | 2015-01-03 14:10 | 100 | 11kV | 200 | 2 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150042 SUB ISOLATED TO REPAIR CONDUCTOR AT POLE 7F- 40001 WYBONG CREEK Excluded OMS 1195371 | January | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Not Veg | 2015-01-03 | N | 100 | N | 9 | N | N | 1.1101 | 39.4971 | 146.1541
[7 empty] | 13772 | 13089 | 1195426 | 2015-01-03 14:52 | 2015-01-03 17:55 | 183 | 11kV | 8418 | 46 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | No Weather Impact | N | Ex Zn12610 Long Jetty section of Pa9 "Denning St" fdr HV fuse blown. Suspect Transformer fault. See 1196367 exclude 1195424,6 | January | 2015 | 2015Q3 | 2015 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | OH | Not Veg | 2015-01-03 | N | 183 | N | 9 | N | N | 1.1101 | 39.4971 | 6151.6261
[7 empty] | 13019 | 6938 | 1195441 | 2015-01-03 17:07 | 2015-01-03 17:56 | 49 | 11kV | 67032 | 1368 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ ZN.1193 Linfield 11kV Panel 26 feeder tripped on:- Relays:- B & C phase IOC Signals:- 11kV Trip Cause:- Not ascetained, OH patrolled by D/Op ME:-1195441 | January | 2015 | 2015Q3 | 2015 | ZN1193:PA26 | ZN1193:PA26 | ZN01193/000026 | KU-RING-GAI | OH | Veg | 2015-01-03 | N | 49 | N | 9 | N | N | 1.1101 | 39.4971 | 48985.0085
[7 empty] | 13038 | 7070 | 1195402 | 2015-01-03 16:36 | 2015-01-03 18:00 | 83.9333 | 11kV | 755.4 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 150043 3 phase opened L/F due to unwrapped pin insulator Excluded oms 1195402 | January | 2015 | 2015Q3 | 2015 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Not Veg | 2015-01-03 | N | 83.9333 | N | 9 | N | N | 1.1101 | 39.4971 | 552.024
[7 empty] | 13565 | 11428 | 1195438 | 2015-01-03 17:00 | 2015-01-03 18:25 | 85 | 11kV | 170 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150044 A & B phase DOLF : 5 Amp excluded OMS 1195438 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-01-03 | N | 85 | N | 9 | N | N | 1.1101 | 39.4971 | 124.231
[7 empty] | 14555 | 19115 | 1195506 | 2015-01-03 21:21 | 2015-01-03 22:06 | 45 | 11kV | 50040 | 1112 | HV | Animal Flying Fox | Animal | O/H Conductor Bare | Unplanned | No Weather Impact | N | At Zn1287 Revesby Panel 5 "S6360" feeder has tripped Signals: 11kv trip Relays: B & C phase O/C, lockout Remarks: Bat flew into mains in Tallawarra rd, Padstow causing mains to clash. Mains will inspect for damage | January | 2015 | 2015Q3 | 2015 | ZN1287:PA5 | ZN1287:PA5 | ZN01287/000005 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-01-03 | N | 45 | N | 9 | N | N | 1.1101 | 39.4971 | 36567.7561
[7 empty] | 12784 | 4886 | 1195466 | 2015-01-03 18:48 | 2015-01-04 00:30 | 342 | 11kV | 90058 | 927 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | @ ZN.3154 St Ives 11kV Panel 17 feeder tripped, reclosed, tripped & locked out on:- Relays:- A & B phase time, lockout, reclose timing, EFI Signals:- TX3 GE, ZE, 11kV Trip Field EFI's:- Operated down to & including S.7417 Cause:- HV down into LV @ PT.1402 Hunter waterhouse & PT.39 Waterhouse Torrens. EMSO required to inspect. ME:-1195804 RS:-1195806, 1195805, 1195471 (No LV// or GIS Model Error to support this outage) GIS Model Error:-1195486 Withdrawn:-1195517, 1195497, 1195495, 1195469, 1195468, 1195466 | January | 2015 | 2015Q3 | 2015 | ZN3154:PA17 | ZN3154:PA17 | ZN03154/000017 | KU-RING-GAI | OH | Veg | 2015-01-03 | N | 97.1499 | N | 9 | N | N | 1.1101 | 39.4971 | 65811.7301
[7 empty] | 14040 | 15360 | 1195545 | 2015-01-04 08:34 | 2015-01-04 09:08 | 34 | 11kV | 11254 | 331 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa2 "Holgate" fdr @AB41934 open bond on one phase. Region to repair live line or cut out required CC1: 22-"Refer to SOp" | January | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-01-04 | N | 34 | N | 8 | N | N | 1.1101 | 39.4971 | 8224.0913
[7 empty] | 12771 | 4733 | 1195524 | 2015-01-04 01:03 | 2015-01-04 09:10 | 487 | 11kV | 10333 | 62 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150045 1 fault operation A phase Sensitive Earth Fault OHM down at 9N-20139 Excluded OMS 1195524 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-04 | N | 166.6613 | N | 8 | N | N | 1.1101 | 39.4971 | 7551.0516
[7 empty] | 12497 | 2228 | 1195575 | 2015-01-04 10:56 | 2015-01-04 11:40 | 44 | 11kV | 44 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150046 Single phase DOLF : 10 Amp excluded OMS 1195575 | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-01-04 | N | 44 | N | 8 | N | N | 1.1101 | 39.4971 | 32.1539
[7 empty] | 14326 | 17356 | 1195653 | 2015-01-04 17:56 | 2015-01-04 19:00 | 64 | 11kV | 64 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150049 A phase DOLF : 10 Amp Excluded OMS 1195653 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-04 | N | 64 | N | 8 | N | N | 1.1101 | 39.4971 | 46.7693
[7 empty] | 12825 | 5278 | 1195665 | 2015-01-04 17:49 | 2015-01-04 19:15 | 86 | 11kV | 1892 | 22 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At Sub 2540 Daisy Car No 1, B phase 11kv Tx fuse has blown (75A OEFMA) Remarks: cause not ascertained | January | 2015 | 2015Q3 | 2015 | ZN2196:PA11 | ZN2196:PA11 | ZN02196/000011 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-01-04 | N | 86 | N | 8 | N | N | 1.1101 | 39.4971 | 1382.6178
[7 empty] | 13060 | 7298 | 1195670 | 2015-01-04 17:00 | 2015-01-04 20:00 | 180 | 11kV | 180 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150053 A phase DOLF : 10 Amp Includes OMS 1195670 | January | 2015 | 2015Q3 | 2015 | 523:33508 | 523:33508 | ZN00523/033508 | SINGLETON | OH | Veg | 2015-01-04 | N | 180 | N | 8 | N | N | 1.1101 | 39.4971 | 131.5387
[7 empty] | 12933 | 6254 | 1195694 | 2015-01-04 20:00 | 2015-01-04 21:40 | 100 | 11kV | 45918 | 498 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150056 C Phase Overcurrent Excluded oms 1195653,1195694,1195696,1195697,1195717 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-04 | N | 92.2048 | N | 8 | N | N | 1.1101 | 39.4971 | 33555.52
[7 empty] | 13594 | 11659 | 1195727 | 2015-01-04 23:09 | 2015-01-05 02:05 | 176 | 11kV | 355538 | 2223 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN 398 Dulwich Hill - Pnl 16 - Earth Fault, EFI, Field EFIs. Underground cable fault from S 1900 to S 482 to S 1551. ME: 1197047. Rest Step: 1197048. Withdrawn: 1195727, 30, 34. | January | 2015 | 2015Q3 | 2015 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2015-01-04 | N | 159.9361 | N | 8 | N | N | 1.1101 | 39.4971 | 259816.6838
[7 empty] | 13735 | 12817 | 1195745 | 2015-01-05 04:37 | 2015-01-05 05:40 | 63 | 11kV | 63 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150057 A phase DOLF : 10 Amp Excluded OMS 1195745 | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-01-05 | N | 63 | N | 6 | N | N | 1.1101 | 39.4971 | 46.0385
[7 empty] | 13752 | 12917 | 1195800 | 2015-01-05 08:48 | 2015-01-05 11:10 | 142 | 11kV | 426 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150063 C phase DOLF : 16 Amp volts 252, 252, 252 load 15, 2, 10 amps Excluded oms1195800 | January | 2015 | 2015Q3 | 2015 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2015-01-05 | N | 142 | N | 6 | N | N | 1.1101 | 39.4971 | 311.3082
[7 empty] | 14570 | 19233 | 1195846 | 2015-01-05 09:58 | 2015-01-05 11:15 | 77 | 11kV | 231 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150064 B hase DOLF : 10 Amp replaced 3 x fuses load 1, 23, 8 amps Excluded oms 1195846 | January | 2015 | 2015Q3 | 2015 | 512:48048 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Veg | 2015-01-05 | N | 77 | N | 6 | N | N | 1.1101 | 39.4971 | 168.808
[7 empty] | 13028 | 7021 | 1195882 | 2015-01-05 10:49 | 2015-01-05 13:31 | 161.6333 | 11kV | 5625.8667 | 38 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150062 2 fault operation 3 Phase Earth Fault | January | 2015 | 2015Q3 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-01-05 | N | 148.0491 | N | 6 | N | N | 1.1101 | 39.4971 | 4111.2174
[7 empty] | 12705 | 4197 | 1197037 | 2015-01-05 14:00 | 2015-01-05 16:15 | 135 | 11kV | 270 | 2 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 150066 LLC burned up at S.51591 Tudor. Interruption Reported to T. Horn at 1400hrs. Clamps repaired under permit. | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Not Veg | 2015-01-05 | N | 135 | N | 6 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 13676 | 12344 | 1196063 | 2015-01-05 16:36 | 2015-01-05 17:27 | 51 | 11kV | 15963 | 313 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.188 Zetland - Pnl.14 tripped on: Earth Fault, EFI, Fault Check Field EFIs: NIL UG cable fault from P14 to S2937 Merton Port (Sw A) | January | 2015 | 2015Q3 | 2015 | ZN188:PA14 | ZN8100:PA28 | ZN08100/000028 | SYDNEY | UG | Not Veg | 2015-01-05 | N | 51 | N | 6 | N | N | 1.1101 | 39.4971 | 11665.2896
[7 empty] | 13769 | 13076 | 1196143 | 2015-01-06 06:02 | 2015-01-06 08:10 | 128 | 11kV | 4480 | 35 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | replaced 31.5a dolf - also refer to 1196143 | January | 2015 | 2015Q3 | 2015 | 813:89063 | 813:89063 | ZN00813/089063 | UPPER HUNTER | OH | Veg | 2015-01-06 | N | 128 | N | 7 | N | N | 1.1101 | 39.4971 | 3273.8519
[7 empty] | 13746 | 12877 | 1196180 | 2015-01-06 08:19 | 2015-01-06 09:20 | 61 | 11kV | 122 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150070 3 amp fuse Substation DOLF replaces OMS 1196180 | January | 2015 | 2015Q3 | 2015 | 520:48172 | 520:48172 | ZN00520/048172 | SINGLETON | OH | Veg | 2015-01-06 | N | 61 | N | 7 | N | N | 1.1101 | 39.4971 | 89.154
[7 empty] | 14056 | 15445 | 1196202 | 2015-01-06 09:00 | 2015-01-06 11:25 | 145 | 11kV | 6670 | 46 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S18382 Torrens Fairview 11kv C phase fuse operated Transformer failure. See 1196646 GIS 1196203,72 exclude 1196202 | January | 2015 | 2015Q3 | 2015 | ZN12610:PA9 | ZN12610:PA9 | ZN12610/000009 | CENTRAL COAST | UG | Not Veg | 2015-01-06 | N | 145 | N | 7 | N | N | 1.1101 | 39.4971 | 4874.2393
[7 empty] | 13030 | 7026 | 1196660 | 2015-01-06 11:30 | 2015-01-06 11:39 | 9 | 11kV | 549 | 61 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of 33 "Macmasters Beach" 11kv section between LB50716 to AB41823 de-energised for safety to allow lineworker to remove large tree branch from mains. Tree branch adjacent LB50716. No follow up inspection required | January | 2015 | 2015Q3 | 2015 | ZN12570:PA33 | ZN12570:PA33 | ZN12570/000033 | CENTRAL COAST | OH | Veg | 2015-01-06 | N | 9 | N | 7 | N | N | 1.1101 | 39.4971 | 401.193
[7 empty] | 12295 | 377 | 1196356 | 2015-01-06 11:48 | 2015-01-06 14:00 | 132 | 11kV | 264 | 2 | HV | Overload | Utility Process Issue | Circuit Breaker | Unplanned | No Weather Impact | N | @Sub 8103 Durby Suttor #3 RMCB trip Pickup 2119 Amps Remarks: overload. Cust drawing more load than Sub rating known problems cust investigating | January | 2015 | 2015Q3 | 2015 | ZN167:PA17 | ZN167:PA17 | ZN00167/000017 | PARRAMATTA | Unknown | Not Veg | 2015-01-06 | N | 132 | N | 7 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 14553 | 19097 | 1196544 | 2015-01-06 19:15 | 2015-01-06 20:15 | 60 | 11kV | 120 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 150086 10 amp fuse Substation DOLF OMS 1196544. A phase LA blown. Replaced under permit.Both fuses replaced on restoration. | January | 2015 | 2015Q3 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2015-01-06 | N | 60 | N | 7 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 12645 | 3696 | 1196573 | 2015-01-06 22:06 | 2015-01-07 01:00 | 174 | 11kV | 75860 | 1018 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 150087 2 fault operation A & B phase Overcurrent possum at JU-63686 | January | 2015 | 2015Q3 | 2015 | 256:80638 | 256:80638 | ZN00256/080638 | NEWCASTLE | OH | Not Veg | 2015-01-06 | N | 74.5187 | N | 7 | N | N | 1.1101 | 39.4971 | 55436.2505
[7 empty] | 14127 | 16052 | 1196623 | 2015-01-07 08:26 | 2015-01-07 09:35 | 69 | 11kV | 69 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150092 10 amp fuse Substation DOLF Replaces OMS # 1196623 Suspect it was possibly damaged in a previous storm. | January | 2015 | 2015Q3 | 2015 | 238:34141 | 238:34141 | ZN00238/034141 | MAITLAND | OH | Veg | 2015-01-07 | N | 69 | N | 6 | N | N | 1.1101 | 39.4971 | 50.4232
[7 empty] | 14157 | 16215 | 1196677 | 2015-01-07 09:55 | 2015-01-07 10:53 | 58 | 11kV | 37062 | 639 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.711 Blackwattle Bay - Pnl.14 (5kV) tripped on: 14R timed EF, EFI Signals: ZE, Tx#2 GE, 5kV Trip UG cable fault (5kV) from S7538 Pyrmont Fig to S4085 Macarthur Harris Previous EFI flag at Blackwattle Bay 6/5/15 22:13 #1196630 - no trip, developing fault | January | 2015 | 2015Q3 | 2015 | ZN711:PA14 | ZN7481:PA12 | ZN07481/000012 | SYDNEY | UG | Not Veg | 2015-01-07 | N | 58 | N | 6 | N | N | 1.1101 | 39.4971 | 27083.8165
[7 empty] | 14311 | 17293 | 1196918 | 2015-01-07 15:38 | 2015-01-07 16:13 | 35 | 11kV | 65192 | 1893 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 150103 1 fault operation broke tapping at abs 40132 when closing // for RSI 44368. feeder abnormal ABS 42597 was closed. Excluded oms 1196912 & 1196918 relates to report 150104 | January | 2015 | 2015Q3 | 2015 | 502:48010 | 502:48010 | ZN00502/048010 | MAITLAND | OH | Not Veg | 2015-01-07 | N | 34.4385 | N | 6 | N | N | 1.1101 | 39.4971 | 47640.3908
[7 empty] | 14608 | 19779 | 1196827 | 2015-01-07 13:25 | 2015-01-07 18:25 | 300 | 33kV Distribution | 600 | 2 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | No Weather Impact | N | LID 150102 C phase DOLF : 15 Amp Blown DOLF & L/A at sub 9715. Section 2747/42355 isolated for repairs. Excluded OMS 1196827 | January | 2015 | 2015Q3 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-01-07 | N | 300 | N | 6 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 14354 | 17582 | 1196912 | 2015-01-07 16:00 | 2015-01-07 18:39 | 159 | 11kV | 49789 | 315 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 150104 Earth fault broke tapping at abs 40132 when closing // for RSI 44368. feeder abnormal ABS 42597 was closed. Excluded oms 1196912 & 1196918 relates to report 150103 | January | 2015 | 2015Q3 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2015-01-07 | N | 158.0603 | N | 6 | N | N | 1.1101 | 39.4971 | 36384.3327
[7 empty] | 13344 | 9697 | 1196988 | 2015-01-07 20:07 | 2015-01-07 23:50 | 223 | 11kV | 11596 | 52 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT.83 Banockburn Mcrae 11kV centre phase 31.5A HVDO operated - batch no.653 Cause:- Tree/branch brought down OH mains, Mains have repaired and D/Op has restored ME:-1197021 GIS Model Error:-1196998, 1197022 Withdrawn:-1197006, 1196996, 1196993, 1196991, 1196990, 1196988 | January | 2015 | 2015Q3 | 2015 | ZN3154:PA12 | ZN3154:PA12 | ZN03154/000012 | KU-RING-GAI | OH | Veg | 2015-01-07 | N | 223 | N | 6 | N | N | 1.1101 | 39.4971 | 8474.0148
[7 empty] | 13288 | 9032 | 1197169 | 2015-01-08 12:21 | 2015-01-08 13:53 | 92 | 11kV | 51227 | 934 | HV | Equipment Failed in Service | Equipment Failure | ZS STS Secondary Equip | Unplanned | No Weather Impact | N | Zn14892 Charmhaven Pa14 triped on 51 AB basler/ overcurrent trip Re40149 Blue Haven tripped on overcurrent Appears to have been a protection malgrade between Pa14 and RE40149 See 1197428,9 Exclude 1197169 | January | 2015 | 2015Q3 | 2015 | ZN14892:PA14 | ZN14892:PA14 | ZN14892/000014 | CENTRAL COAST | Exclude | Not Veg | 2015-01-08 | N | 54.8469 | N | 5 | N | N | 1.1101 | 39.4971 | 37435.1807
[7 empty] | 14071 | 15590 | 1197319 | 2015-01-08 17:51 | 2015-01-08 18:41 | 50 | 11kV | 86350 | 1727 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12570 Avoca Pa24 "Kincumber" tripped on A&B phase IOC reclose lockout 11kv trip Branch on mains near PT47538 See 1197319 exclude 1197320 | January | 2015 | 2015Q3 | 2015 | ZN12570:PA24 | ZN12570:PA24 | ZN12570/000024 | CENTRAL COAST | OH | Veg | 2015-01-08 | N | 50 | N | 5 | N | N | 1.1101 | 39.4971 | 63102.0331
[7 empty] | 12376 | 1153 | 1197325 | 2015-01-08 18:19 | 2015-01-08 19:45 | 86 | 11kV | 60160 | 840 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @Zn1285 Greenacre Park 11kv Panel #10 labelled "S4109 + S8025" tripped on: Relays: B phase O/C & timed, Sealing Contact, EFI, Fault Check Signals: 11kv trip, Tx.1 Group Earth, Zone Earth Field EFI's: Nil Remarks: UG fault. Front line feeder fault from Panel 10 @ Zn1285 Greenacre Park to Sw/A @ S4109 East Terrace to Sw/A @ S8025 East Tce South Tce | January | 2015 | 2015Q3 | 2015 | ZN1285:PA10 | ZN1285:PA10 | ZN01285/000010 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-01-08 | N | 71.619 | N | 5 | N | N | 1.1101 | 39.4971 | 43963.1536
[7 empty] | 13907 | 14178 | 1197216 | 2015-01-08 13:25 | 2015-01-08 20:35 | 430 | 11kV | 111576 | 500 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Wind Strong | N | ZN 10990 Arncliffe - Pnl 5 - Trip/reclose/trip, C phase IOC and timed OC, timing, lockout. Tree branch brought down OH adjacent to LB 31208. ME: 1198591. Rest Steps: 1198593, 4. Withdrawn: 1197213, 6. | January | 2015 | 2015Q3 | 2015 | ZN10990:PA5 | ZN10998:PA26 | ZN10998/000026 | BAYSIDE | OH | Veg | 2015-01-08 | N | 223.152 | N | 5 | N | N | 1.1101 | 39.4971 | 81536.4499
[7 empty] | 12347 | 866 | 1197353 | 2015-01-08 20:56 | 2015-01-08 23:36 | 159.7333 | 11kV | 4153.0667 | 26 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 150114 Broken 11kV X arm at West sub 53338 Excluded OMS 1197341/344 | January | 2015 | 2015Q3 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Not Veg | 2015-01-08 | N | 159.7333 | N | 5 | N | N | 1.1101 | 39.4971 | 3034.9386
[7 empty] | 13876 | 13914 | 1197398 | 2015-01-09 07:48 | 2015-01-09 09:24 | 96 | 11kV | 192 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150117 10 amp fuse Substation DOLF replaces OMS 1197398 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-09 | N | 96 | N | 10 | N | N | 1.1101 | 39.4971 | 140.3079
[7 empty] | 13703 | 12558 | 1197467 | 2015-01-09 10:15 | 2015-01-09 11:41 | 86 | 11kV | 35190 | 414 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Hot >35C | N | Zn12570 Avoca Pa26 tripped Relays: A & B phase IOC Signals: 11kv trip EFI's: Nil Cause not ascertained. Feeder Patrolled. Auto Reclosing permanently Non Auto See 1197467 exclude 1197475 | January | 2015 | 2015Q3 | 2015 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Veg | 2015-01-09 | N | 85 | N | 10 | N | N | 1.1101 | 39.4971 | 25715.8141
[7 empty] | 13562 | 11412 | 1197563 | 2015-01-09 13:38 | 2015-01-09 14:45 | 67 | 11kV | 166314 | 2532 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Hot >35C | N | Zn2568 St Peters - 11kV panel 26 tripped on: A & B phase timed O/C, Earth Fault check relay, EFI UG cable fault between S5719 and S5857 See separate interruption reports S8881 & S35418 which were in LV // with subs supplied from Pnl.26 see 1198276 1198277 - LV //: 1198279 1198280 | January | 2015 | 2015Q3 | 2015 | ZN2568:PA26 | ZN2568:PA26 | ZN02568/000026 | INNER WEST | UG | Not Veg | 2015-01-09 | N | 65.6848 | N | 10 | N | N | 1.1101 | 39.4971 | 121537.3658
[7 empty] | 13617 | 11851 | 1197590 | 2015-01-09 14:43 | 2015-01-09 17:30 | 167 | 11kV | 334 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | LID 150129 10 amp fuse Substation DOLF Replaces OMS 1197590 + 1197591 | January | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-01-09 | N | 167 | N | 10 | N | N | 1.1101 | 39.4971 | 244.0773
[7 empty] | 13331 | 9590 | 1197613 | 2015-01-09 15:34 | 2015-01-09 17:51 | 137 | 11kV | 138025 | 1235 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN 10995 Riverwood - Pnl 6 - Trip/reclose/trip, A phase IOC and timed OC, timing, lockout, EFI. UGOH went short circuit. ME: 1198423. Rest Step: 1198426. Withdrawn: 1197613. | January | 2015 | 2015Q3 | 2015 | ZN10995:PA6 | ZN10995:PA6 | ZN10995/000006 | GEORGES RIVER | Unknown | Unknown | 2015-01-09 | N | 111.7611 | N | 10 | N | N | 1.1101 | 39.4971 | 100864.599
[7 empty] | 13359 | 9778 | 1197633 | 2015-01-09 16:03 | 2015-01-09 19:20 | 197 | 11kV | 9560 | 148 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | Ex Zn12630 Peats Ridge section of Pa3 "Mangrove Mountain" @RE46935 Ironbark Kirks 0.8 tripped on SEF Cause: OH Down. Electrical Storm See 1198853,4 Exclude 1197633,51 | January | 2015 | 2015Q3 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2015-01-09 | N | 64.5946 | N | 10 | N | N | 1.1101 | 39.4971 | 6986.166
[7 empty] | 13021 | 6952 | 1197701 | 2015-01-09 19:59 | 2015-01-09 21:20 | 81 | 11kV | 891 | 11 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | Electrical Storm | N | Ex Zn12630 Peats Ridge section Pa3 "Mangrove Mountain" Near LB40554 centre phase bond burnt off See 1198857 exclude 1197701 | January | 2015 | 2015Q3 | 2015 | ZN12630:PA3 | ZN12630:PA3 | ZN12630/000003 | CENTRAL COAST | OH | Not Veg | 2015-01-09 | N | 81 | N | 10 | N | N | 1.1101 | 39.4971 | 651.1165
[7 empty] | 12366 | 1034 | 1197707 | 2015-01-09 20:28 | 2015-01-09 23:20 | 172 | 11kV | 172 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150132 10 amp fuse Substation DOLF Replaces OMS 1197707 | January | 2015 | 2015Q3 | 2015 | 526:34640 | 526:34640 | ZN00526/034640 | CESSNOCK | OH | Veg | 2015-01-09 | N | 172 | N | 10 | N | N | 1.1101 | 39.4971 | 125.6925
[7 empty] | 13466 | 10669 | 1197720 | 2015-01-09 23:38 | 2015-01-10 00:20 | 42 | 11kV | 1008 | 24 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 10 amp fuse Substation DOLF Replaces OMS 1197720 | January | 2015 | 2015Q3 | 2015 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | OH | Veg | 2015-01-09 | N | 42 | N | 10 | N | N | 1.1101 | 39.4971 | 736.6167
[7 empty] | 13883 | 13946 | 1197706 | 2015-01-09 20:25 | 2015-01-10 01:30 | 305 | 11kV | 77174 | 532 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Previous Storm | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" Section of OH mains from RE45189 Cooks Peats Ridge 0.5 to extent of feeder Abnormal: RE44945 Lower Mangrove defective by pass ab closed Lineworker reports 11kv down in river with small boats in area. RE45189 cooks Peats Ridge Ridge 0.5 opened by AOp. See 1197706,28 | January | 2015 | 2015Q3 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Not Veg | 2015-01-09 | N | 145.0639 | N | 10 | N | N | 1.1101 | 39.4971 | 56396.483
[7 empty] | 13440 | 10498 | 1197731 | 2015-01-10 03:24 | 2015-01-10 05:50 | 146 | 11kV | 8312 | 80 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Section of ZN.15005 Belrose 11kV feeder from RE.24722 to extent of the feeder (13 DC's) tripped on IOC Cause:- 11kV phases touching after tree branch contact ME:-1198265 RS:-1198266, 1198267 Withdrawn:-1197731, 1197732, 1197734 | January | 2015 | 2015Q3 | 2015 | ZN15005:PA10 | ZN15005:PA10 | ZN15005/000010 | NORTHERN BEACHES | OH | Veg | 2015-01-10 | N | 103.9 | N | 2 | N | N | 1.1101 | 39.4971 | 6074.1644
[7 empty] | 14425 | 18118 | 1197939 | 2015-01-10 22:44 | 2015-01-11 00:55 | 131 | 11kV | 7729 | 59 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Section of ZN.36300 Balgowlah North from PT.15287 Cuter Rd 57 (1 DC) - Footpath phase 31.5A HDO operated Cause:- Weather related ME:-1198272 Withdrawn:-1197938, 1197939, 1197948 | January | 2015 | 2015Q3 | 2015 | ZN36300:PA3 | ZN36300:PA3 | ZN36300/000003 | NORTHERN BEACHES | OH | Veg | 2015-01-10 | N | 131 | N | 2 | N | N | 1.1101 | 39.4971 | 5648.1252
[7 empty] | 12561 | 2939 | 1197992 | 2015-01-11 07:04 | 2015-01-11 07:55 | 51 | 11kV | 51969 | 1019 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Z.1193 Linfield 11kV Panel 15 feeder tripped Relays:- B & C phase IOC Signals:- 11kv Trip ME:-1197992 | January | 2015 | 2015Q3 | 2015 | ZN1193:PA15 | ZN1193:PA15 | ZN01193/000015 | WILLOUGHBY | OH | Veg | 2015-01-11 | N | 51 | N | 10 | N | N | 1.1101 | 39.4971 | 37977.4124
[7 empty] | 13464 | 10662 | 1197954 | 2015-01-11 00:42 | 2015-01-11 08:40 | 478 | 11kV | 5258 | 11 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | Ex Zn14891 Wyong section of Pa5 "Wyong" PT13968 Alison Hue Hue 1.0 11kv HDO footpath phase 31.5k replaced Fuse failure See 1198907 GIS 1197991 exclude 1197954 | January | 2015 | 2015Q3 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-01-11 | N | 478 | N | 10 | N | N | 1.1101 | 39.4971 | 3842.3913
[7 empty] | 12936 | 6288 | 1198023 | 2015-01-11 09:18 | 2015-01-11 10:41 | 83 | 11kV | 45708 | 684 | HV | Vegetation Blow/Fall In | Vegetation | Bond | Unplanned | Rain Light | N | ZN.129 Hunters Hill 11kV Panel 21 feeder tripped Relays:- A phase timed over current Signals:- 11kV trip Cause:- Falling tree branch has caused roadside phase bond to oben at 11kV UGOH @ pole GL.38068 11kV feeder at S.5233 SW/D to S.2773 SW/A to S.46610 SW/A is isolated with SW/tag @ S.5233 ME:-1198316 RS:-1198317, 1198318 Withdrawn:-1198023 | January | 2015 | 2015Q3 | 2015 | ZN129:PA21 | ZN129:PA63 | ZN00129/000063 | LANE COVE | OH | Veg | 2015-01-11 | N | 66.8246 | N | 10 | N | N | 1.1101 | 39.4971 | 33402.0582
[7 empty] | 13215 | 8515 | 1198022 | 2015-01-11 09:19 | 2015-01-11 10:45 | 86.35 | 11kV | 2676.85 | 31 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 150136 16 amp fuse Line DOLF | January | 2015 | 2015Q3 | 2015 | 243:80075 | 243:80075 | ZN00243/080075 | LAKE MACQUARIE | OH | Veg | 2015-01-11 | N | 86.35 | N | 10 | N | N | 1.1101 | 39.4971 | 1956.163
[7 empty] | 14458 | 18381 | 1198045 | 2015-01-11 10:25 | 2015-01-11 11:14 | 49 | 11kV | 137396 | 2804 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | ZN.1193 Linfield 11kV Panel 28 feeder tripped, reclosed and tripped Relays:- B & C phase over current, Lockout Signals:- 11kV trip Cause:- Tree/branch on OH mains removed from OH outside 110 Millwood Ave ME:-1198045 Withdrawn:-1198060, 1198062, 1198066 | January | 2015 | 2015Q3 | 2015 | ZN1193:PA28 | ZN1193:PA28 | ZN01193/000028 | KU-RING-GAI | OH | Veg | 2015-01-11 | N | 49 | N | 10 | N | N | 1.1101 | 39.4971 | 100404.9443
[7 empty] | 13808 | 13330 | 1198098 | 2015-01-11 12:45 | 2015-01-11 22:55 | 610 | 11kV | 499231 | 1780 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN.80 Chatswood 11kV Panel 22 feeder tripped on:- Relays:- E/F, F/C Signals:- 11kV trip, ZE Field EFI's:- S.35000 Abnormal switching:- S.46610 SW/B closed Cause:- UG cable fault, LV// left in caused wires down and blown fuses @ S.5877 & S.3819 ME:-1198427 RS:-1198429, 1198434, 1198138, 1198142 SE:-1198566, 1198549 GIS Model Error:-1198556 Withdrawn:-1198093, 1198098, 1198100, 1198101, 1198102, 1198103, 1198104, 1198107, 1198110, 1198112, 1198119, 1198123, 1198126, 1198133, 1198144, 1198148 | January | 2015 | 2015Q3 | 2015 | ZN80:PA22 | ZN80:PA22 | ZN00080/000022 | LANE COVE | UG | Not Veg | 2015-01-11 | N | 280.4669 | N | 10 | N | N | 1.1101 | 39.4971 | 364823.29
[7 empty] | 13898 | 14125 | 1198229 | 2015-01-11 22:05 | 2015-01-11 22:59 | 54 | 11kV | 378 | 7 | HV | Equipment Failed in Service | Equipment Failure | Circuit Breaker | Unplanned | No Weather Impact | N | LID 150138 Air circuit breaker Ongoing problem with Ausgrid CB tripping. Happened last thursday morning as advised by Woolworths. 400A per phase Replaces OMS 1198229 | January | 2015 | 2015Q3 | 2015 |  |  |  |  | Unknown | Not Veg | 2015-01-11 | N | 54 | N | 10 | N | N | 1.1101 | 39.4971 | 276.2313
[7 empty] | 13161 | 8065 | 1198108 | 2015-01-11 13:20 | 2015-01-11 23:00 | 580 | 11kV | 16742 | 101 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | LID 150137 Overcurrent Tree on 11kV OHM near Sub 5221. Includes OMS 1198108, 1199248/50/52 | January | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-01-11 | N | 165.7624 | N | 10 | N | N | 1.1101 | 39.4971 | 12234.5598
[7 empty] | 14419 | 18045 | 1198234 | 2015-01-11 23:21 | 2015-01-12 03:39 | 258 | 11kV | 258 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 150141 10 amp fuse Substation DOLF Blown DOLF caused by short in service wire Service wire replaced also refer to 1198234 | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Not Veg | 2015-01-11 | N | 258 | N | 10 | N | N | 1.1101 | 39.4971 | 188.5388
[7 empty] | 12916 | 6098 | 1198245 | 2015-01-12 04:47 | 2015-01-12 07:20 | 153 | 11kV | 1377 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Section of ZN.35500 Top Ryde from F.1835 to extent for 11kV Panel 3 feeder (2 DC's) - Road side & centre phase fuses blown Cause:- Not ascertained ME:-1198760 Withdrawn:-1198245 | January | 2015 | 2015Q3 | 2015 | ZN35500:PA32 | ZN35500:PA32 | ZN35500/000032 | RYDE | OH | Veg | 2015-01-12 | N | 153 | N | 4 | N | N | 1.1101 | 39.4971 | 1006.271
[7 empty] | 13275 | 8954 | 1198244 | 2015-01-12 04:37 | 2015-01-12 09:55 | 318 | 11kV | 5445 | 33 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Ex Zn12600 Lisarow section of Pa9 "Wyoming South" fdr RE42120 Holgate tripped on SEF Car hit pole No. WL1168 outside 451 Ridgeway Rd Tumbi Umbi. Black Honda Accord REGO NBG 86J. cause damage to pole and wire to snap insulator pin. See 1198918,9 exclude 119824 | January | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-01-12 | N | 165 | N | 4 | N | N | 1.1101 | 39.4971 | 3979.0454
[7 empty] | 13315 | 9357 | 1198241 | 2015-01-12 02:17 | 2015-01-12 11:45 | 568 | 11kV | 14618 | 101 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 150143 1 fault operation Overcurrent replace insulators at pole 9V-40009 near links 5116 Replaces OMS 1198241, 1198242, 1199031 | January | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-01-12 | N | 144.7327 | N | 4 | N | N | 1.1101 | 39.4971 | 10682.4032
[7 empty] | 14047 | 15399 | 1198448 | 2015-01-12 10:30 | 2015-01-12 11:45 | 75 | 11kV | 75 | 1 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150139 31 amp fuse Substation DOLF wires smoking due to magpie stuck on wires Replaces OMS 1198448 | January | 2015 | 2015Q3 | 2015 | 515:35200 | 515:35200 | ZN00515/035200 | SINGLETON | OH | Not Veg | 2015-01-12 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 54.8078
[7 empty] | 14485 | 18564 | 1198072 | 2015-01-11 11:35 | 2015-01-12 12:30 | 1495 | 11kV | 4485 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150146 - no details included on LID re cause of outage OMS 1198072 advised Found transformer blown - to be replaced on the 12th - Start time amended as per 1198072 | January | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-01-11 | N | 1495 | N | 10 | N | N | 1.1101 | 39.4971 | 3277.5057
[7 empty] | 12970 | 6577 | 1198922 | 2015-01-13 12:24 | 2015-01-13 13:15 | 51 | 11kV | 1008 | 30 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 150163 SECTION FDR REQUIRED OUT OF SERVICE FOR GAS LEAK AT SERVICE STATION IN DORA ST Excludes OMS 1198934/922/937/940, and rest steps 1199315/317/320 | January | 2015 | 2015Q3 | 2015 | 243:80080 | 243:80080 | ZN00243/080080 | LAKE MACQUARIE | Unknown | Not Veg | 2015-01-13 | N | 33.6 | N | 3 | N | N | 1.1101 | 39.4971 | 736.6167
[7 empty] | 13996 | 14899 | 1198964 | 2015-01-13 13:20 | 2015-01-13 15:48 | 148 | 11kV | 223213 | 2548 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | @ZN1287 Revesby 11kv Panel 21 "S1287 Vega Mars" feeder tripped on - Relays - SEL & Lockout, Field EFI's - Nil Signals - 11kv trip Abnormal: Pnl 22 O/O/S for CB replacement. SW-B is closed at S3962 lesley Weston. Closed @ LB593 (refer DMA) Open @ AB147 Remarks: Cause not ascertained. | January | 2015 | 2015Q3 | 2015 | ZN1287:PA21 | ZN1287:PA21 | ZN01287/000021 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-01-13 | N | 87.6032 | N | 3 | N | N | 1.1101 | 39.4971 | 163117.4767
[7 empty] | 13884 | 13956 | 1198963 | 2015-01-13 13:23 | 2015-01-13 17:25 | 242 | 11kV | 8446 | 38 | HV | Vegetation Cut Down Ausgrid/Contractor | Utility Process Issue | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150168 3 fault operations Tree clearing pushed tree onto mains. Replaces OMS 1198963, 1199066 + rest step 1199280 | January | 2015 | 2015Q3 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-01-13 | N | 222.2632 | N | 3 | N | N | 1.1101 | 39.4971 | 6172.0877
[7 empty] | 14388 | 17844 | 1199149 | 2015-01-14 04:30 | 2015-01-14 07:25 | 175 | 11kV | 3675 | 21 | HV | Animal Flying Fox | Animal | O/H Conductor Unknown | Unplanned | Rain Light | N | LID 150171 31 amp fuse Substation DOLF Bat on OHM Replaces OMS 1199149 | January | 2015 | 2015Q3 | 2015 | 264:81236 | 264:81236 | ZN00264/081236 | PORT STEPHENS | OH | Not Veg | 2015-01-14 | N | 175 | N | 9 | N | N | 1.1101 | 39.4971 | 2685.5816
[7 empty] | 12279 | 219 | 1199302 | 2015-01-14 11:11 | 2015-01-14 12:10 | 59 | 11kV | 1180 | 20 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150174 Ex miner bird found at base of pole. 10 for a 10 Bph Excludes OMS 1199302 | January | 2015 | 2015Q3 | 2015 | 814:82285 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2015-01-14 | N | 59 | N | 9 | N | N | 1.1101 | 39.4971 | 862.3092
[7 empty] | 13086 | 7510 | 1199385 | 2015-01-14 13:20 | 2015-01-14 14:15 | 55 | 11kV | 605 | 11 | HV | Animal Bird | Animal | DC-PT Not Transformer | Unplanned | Hot >35C | N | LID 150178 20 amp fuse Substation DOLF Replaced blown dolf on sub 51887 20A | January | 2015 | 2015Q3 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Not Veg | 2015-01-14 | N | 55 | N | 9 | N | N | 1.1101 | 39.4971 | 442.1162
[7 empty] | 12263 | 68 | 1199440 | 2015-01-14 14:22 | 2015-01-14 15:40 | 78.2833 | 11kV | 2191.9333 | 28 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Hot >35C | N | LID 150180 20 amp fuse Line DOLF fuse fatigue 232V, 232V, 231V | January | 2015 | 2015Q3 | 2015 | 507:80923 | 507:80914 | ZN00507/080914 | CESSNOCK | OH | Not Veg | 2015-01-14 | N | 78.2833 | N | 9 | N | N | 1.1101 | 39.4971 | 1601.8002
[7 empty] | 13378 | 9955 | 1199587 | 2015-01-14 18:49 | 2015-01-14 20:01 | 72 | 11kV | 44784 | 622 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At S965 Pennant Hills Panel 12 "Brokenwood Millbrook" tripped on: Relays: A ph Timed OC Signals: 11kv trip EFI's: Nil Remarks: tree/branch on OH mains | January | 2015 | 2015Q3 | 2015 | ZN965:PA12 | ZN965:PA13 | ZN00965/000013 | HORNSBY | OH | Veg | 2015-01-14 | N | 72 | N | 9 | N | N | 1.1101 | 39.4971 | 32726.8263
[7 empty] | 14568 | 19190 | 1199566 | 2015-01-14 17:43 | 2015-01-14 20:15 | 151.55 | 11kV | 36372 | 240 | HV | Overload Operational | Utility Process Issue | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150183 Feeder 11455 overloaded. SW 39512 opened, system abnormal and feeder fault on feeder 33413. Refer to LID 150187 - OMS 1199467, 1199419 and 1199465 | January | 2015 | 2015Q3 | 2015 | 232:11455 | 232:11455 | ZN00232/011455 | PORT STEPHENS | OH | Not Veg | 2015-01-14 | N | 151.55 | N | 9 | N | N | 1.1101 | 39.4971 | 26579.5848
[7 empty] | 13416 | 10295 | 1199606 | 2015-01-14 20:02 | 2015-01-14 21:15 | 73 | 11kV | 136771 | 1899 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.3672 Maroubra - Pnl.44 tripped on: EF, EFI, Fault Check Field EFi @ S8454 UG Cable fault from S8454 Ferguson Wise to S993 Anzac Pde see 1199724 1199723 | January | 2015 | 2015Q3 | 2015 | ZN3672:PA44 | ZN3672:PA44 | ZN03672/000044 | RANDWICK | UG | Not Veg | 2015-01-14 | N | 72.0226 | N | 9 | N | N | 1.1101 | 39.4971 | 99948.2127
[7 empty] | 12544 | 2713 | 1199630 | 2015-01-14 22:19 | 2015-01-14 23:40 | 81 | 11kV | 60254 | 764 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn.342 Paddington - Pnl.31 tripped on: Timed O/C A & C phase, EFI Field EFIs: NIL US cable fault - front line feeder from P21 to S35817 Springfield Ave (Sw A). Fault in HV pit outside S935 Couny Ave (opposite 3 Weedon Ave) see 1199734 | January | 2015 | 2015Q3 | 2015 | ZN342:PA21 | ZN342:PA21 | ZN00342/000021 | SYDNEY | UG | Not Veg | 2015-01-14 | N | 78.8665 | N | 9 | N | N | 1.1101 | 39.4971 | 44031.846
[7 empty] | 13599 | 11699 | 1199465 | 2015-01-14 14:44 | 2015-01-14 23:44 | 540 | 11kV | 188195 | 2116 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 150185 and LID 150187 Broken xarm at pole OS-27111 Note - reports of pole fire also refer to OMS 1200282 and OMS 1199419 and 33kV event LID 150184 (1199412) | January | 2015 | 2015Q3 | 2015 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2015-01-14 | N | 88.939 | N | 9 | N | N | 1.1101 | 39.4971 | 137527.3552
[7 empty] | 12566 | 2987 | 1199644 | 2015-01-15 01:45 | 2015-01-15 02:40 | 55 | 11kV | 13035 | 237 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn.3425 Castle Cove - Ex Pnl.33 iR64824 Deepwater Holly - tripped & locked out on: Overcurrent trip, lockout Dead possum adjacent LB62053 | January | 2015 | 2015Q3 | 2015 | ZN3425:PA33 | ZN3425:PA33 | ZN03425/000033 | WILLOUGHBY | OH | Not Veg | 2015-01-15 | N | 55 | N | 7 | N | N | 1.1101 | 39.4971 | 9525.5935
[7 empty] | 13216 | 8516 | 1199649 | 2015-01-15 05:54 | 2015-01-15 07:55 | 121 | 11kV | 4376 | 40 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150191 3 fault operations Pole mounted RAGCB mains found twisted between poles 9N-20172 & 9N-20173. repaired & fdr restored Includes OMS 1199649, 1200816/17/19/21 | January | 2015 | 2015Q3 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Not Veg | 2015-01-15 | N | 109.4 | N | 7 | N | N | 1.1101 | 39.4971 | 3197.8517
[7 empty] | 13560 | 11382 | 1199863 | 2015-01-15 13:42 | 2015-01-15 15:17 | 95 | 11kV | 8584 | 112 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | LID 150205 Contractor ( AllDay Concret ) cement truck backed into 11kv pole moving pole and breaking H/V pin ties AL-30018 & AL-30031 Includes OMS 1199841/63, 1200899/901/3/6 | January | 2015 | 2015Q3 | 2015 | 812:19065 | 812:19065 | ZN00812/019065 | MUSWELLBROOK | OH | Not Veg | 2015-01-15 | N | 76.6429 | N | 7 | N | N | 1.1101 | 39.4971 | 6272.934
[7 empty] | 13471 | 10707 | 1199879 | 2015-01-15 14:22 | 2015-01-15 18:30 | 248 | 11kV | 61412 | 964 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 150207 2 fault operations Overcurrent, earth fault underground borer thru cable at sub 24701 . taps opened at ugoh pole JT-80242. generator connected to sub 24701. protection details Sw 34835 50TN & 51N Excludes OMS 1199879/94/970/998, 1200961/65/66/80/81 | January | 2015 | 2015Q3 | 2015 | 240:34835 | 240:34835 | ZN00240/034835 | NEWCASTLE | UG | Not Veg | 2015-01-15 | N | 63.7054 | N | 7 | N | N | 1.1101 | 39.4971 | 44878.0783
[7 empty] | 13006 | 6857 | 1200171 | 2015-01-15 18:20 | 2015-01-15 19:30 | 70 | 11kV | 210 | 3 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | Ex Zn15012 Killarney section of pa6 "Killarney West" from LK22297 to PT16261 Davidson Park S and PT16304 Roseville Reserve was interrupted for emergency repairs to HV UGOH below PT16261 See 1200171,2 | January | 2015 | 2015Q3 | 2015 | ZN15012:PA6 | ZN15012:PA6 | ZN15012/000006 | NORTHERN BEACHES | Unknown | Unknown | 2015-01-15 | N | 70 | N | 7 | N | N | 1.1101 | 39.4971 | 153.4618
[7 empty] | 13160 | 8050 | 1200043 | 2015-01-15 22:07 | 2015-01-15 23:43 | 96 | 11kV | 192 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 1500210 20 amp fuse Substation DOLF Replaced burnt up DOLF fuse & carrier Replaces OMS 1200043 | January | 2015 | 2015Q3 | 2015 | 264:81241 | 264:81241 | ZN00264/081241 | PORT STEPHENS | OH | Not Veg | 2015-01-15 | N | 96 | N | 7 | N | N | 1.1101 | 39.4971 | 140.3079
[7 empty] | 12871 | 5716 | 1200049 | 2015-01-15 23:36 | 2015-01-16 01:30 | 114 | 11kV | 6042 | 53 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn12570 Avoca section of Pa25 "Hillcrest st" PT46696 ENA Quarang 11kv roadside 63K HVDO operated Fuse Fatigue See 1200161 exclude 1200049,52,53 | January | 2015 | 2015Q3 | 2015 | ZN12570:PA25 | ZN12570:PA25 | ZN12570/000025 | CENTRAL COAST | OH | Not Veg | 2015-01-15 | N | 114 | N | 7 | N | N | 1.1101 | 39.4971 | 4415.3154
[7 empty] | 13115 | 7753 | 1200075 | 2015-01-16 08:03 | 2015-01-16 10:39 | 156 | 11kV | 27826 | 196 | HV | Excavation 3rd Party | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | ZN 690 Campsie - Pnl 27 - Fault check, EFI, Earth Leakage, Field EFI. Contractor dug up UG cable on Rickland Rd near Kingsgrove Rd. Section of cable between S 8884, S 1676 and S 47931. ME: 1207186. Rest Steps: 1207187, 8. GIS: 1200140. Withdrawn: 1200075. | January | 2015 | 2015Q3 | 2015 | ZN690:PA27 | ZN690:PA6 | ZN00690/000006 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-01-16 | N | 141.9694 | N | 3 | N | N | 1.1101 | 39.4971 | 20334.4201
[7 empty] | 13665 | 12241 | 1200357 | 2015-01-16 19:33 | 2015-01-16 20:45 | 72 | 11kV | 864 | 12 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2635 Epping Panel 33 Tripped on Relays: B phase IOC and EFI Cause: UG feeder fault from ZN2635 Epping Panel 33 to SW/A at S7740 Herring Talavera No2 | January | 2015 | 2015Q3 | 2015 | ZN2635:PA33 | ZN2635:PA33 | ZN02635/000033 | RYDE | UG | Not Veg | 2015-01-16 | N | 72 | N | 3 | N | N | 1.1101 | 39.4971 | 631.3857
[7 empty] | 14463 | 18441 | 1200371 | 2015-01-16 23:55 | 2015-01-17 01:10 | 75 | 11kV | 1350 | 18 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 150219 Broken HV lead bottom of DOLF Bph, replaced DOLF assembly & repaired HV lead. Includes OMS 1200371 | January | 2015 | 2015Q3 | 2015 | 238:34150 | 238:34137 | ZN00238/034137 | MAITLAND | OH | Not Veg | 2015-01-16 | N | 75 | N | 3 | N | N | 1.1101 | 39.4971 | 986.5402
[7 empty] | 13903 | 14168 | 1201145 | 2015-01-19 11:00 | 2015-01-19 12:30 | 90 | 11kV | 120 | 2 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | No Weather Impact | N | LID 150246 10 amp fuse Line DOLF associated with outage LID 150247 Possible cause being customers installation for both outages. Original jobs 1201145 (on 74845) and 1201147 (on 72096) created overlap | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | Unknown | Not Veg | 2015-01-19 | N | 60 | N | 5 | N | N | 1.1101 | 39.4971 | 87.6925
[7 empty] | 12985 | 6724 | 1200936 | 2015-01-19 14:24 | 2015-01-19 14:58 | 34 | 11kV | 102 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150248 10 amp fuse Substation DOLF High Voltage Fuse replaced replaces OMS 1200936 | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-01-19 | N | 34 | N | 5 | N | N | 1.1101 | 39.4971 | 74.5386
[7 empty] | 13811 | 13341 | 1201066 | 2015-01-19 17:35 | 2015-01-19 19:50 | 135 | 11kV | 270 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 150250 10 amp fuse Substation DOLF s/w fuse has come apart hanging - not on ground Includes OMS 1201084 + 1201066 | January | 2015 | 2015Q3 | 2015 | 508:82574 | 508:82574 | ZN00508/082574 | PORT STEPHENS | OH | Not Veg | 2015-01-19 | N | 135 | N | 5 | N | N | 1.1101 | 39.4971 | 197.308
[7 empty] | 13241 | 8678 | 1200784 | 2015-01-19 10:21 | 2015-01-19 22:15 | 714 | 33kV Distribution | 4452 | 18 | HV | Lightning Strike | Adverse Weather/Environment | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150245 1 fault operation Overcurrent, earth fault Excludes OMS 1200784, 1200796, 1200884, 1201851 relates to report 150244 A prot - o/c & e/f ABC EF B prot - 51 AB | January | 2015 | 2015Q3 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-01-19 | N | 247.3333 | N | 5 | N | N | 1.1101 | 39.4971 | 3253.3903
[7 empty] | 12754 | 4621 | 1201101 | 2015-01-19 21:18 | 2015-01-20 01:20 | 242 | 11kV | 157916 | 1099 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa9 "Taylors Lutheran" RE47607 Toomeys Rd tripped on Sensitive Earth, overcurrent, lockout Tree brought down 11kv Overhead from USL44256 to LB45039 tee to S14191. Inside Henry Kendall Village See 1201289,92,3,4 Exclude 1201101,4 | January | 2015 | 2015Q3 | 2015 | ZN12600:PA9 | ZN12600:PA9 | ZN12600/000009 | CENTRAL COAST | OH | Veg | 2015-01-19 | N | 143.6906 | N | 5 | N | N | 1.1101 | 39.4971 | 115400.3551
[7 empty] | 14585 | 19422 | 1201155 | 2015-01-20 07:26 | 2015-01-20 08:13 | 46.6167 | 11kV | 10115.8167 | 217 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | Rain Heavy | N | LID 150260 Overcurrent Excluded OMS 1201155, 1201165, 1201170 tree on mains at Delia sub 26967 18 Abundance Rd | January | 2015 | 2015Q3 | 2015 | 233:82812 | 233:82812 | ZN00233/082812 | PORT STEPHENS | OH | Veg | 2015-01-20 | N | 46.6167 | N | 14 | N | N | 1.1101 | 39.4971 | 7392.3405
[7 empty] | 12442 | 1750 | 1201210 | 2015-01-20 08:18 | 2015-01-20 09:34 | 76 | 11kV | 111646 | 1506 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S.180 Mosman, 11kV Fdr Panel CB tripped on earth fault, efi, fault check, #3 Tx fault check with 11kV trip and #3 Tx group earth signals. No field efi's operated. Front Line feeder fault from Panel 20 | January | 2015 | 2015Q3 | 2015 | ZN180:PA20 | ZN180:PA20 | ZN00180/000020 | NORTH SYDNEY | UG | Not Veg | 2015-01-20 | N | 74.1341 | N | 14 | N | N | 1.1101 | 39.4971 | 81587.6038
[7 empty] | 13543 | 11232 | 1201240 | 2015-01-20 09:00 | 2015-01-20 10:30 | 90 | 11kV | 4320 | 48 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | At S1285 Greenacre Park Zn section of P20 the 'Islington Cres' fdr from PT62804 Karauh Roberts C phase 63A HDO operated. Remarks: Cause not ascertained | January | 2015 | 2015Q3 | 2015 | ZN1285:PA20 | ZN1285:PA20 | ZN01285/000020 | CANTERBURY-BANKSTOWN | OH | Veg | 2015-01-20 | N | 90 | N | 14 | N | N | 1.1101 | 39.4971 | 3156.9286
[7 empty] | 13249 | 8751 | 1201282 | 2015-01-20 09:39 | 2015-01-20 10:30 | 51 | 11kV | 3723 | 73 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | Previous Storm | N | LID 150265 20 amp fuse Substation DOLF Excludes OMS 1201282 | January | 2015 | 2015Q3 | 2015 | 504:48026 | 522:83123 | ZN00522/083123 | CESSNOCK | OH | Veg | 2015-01-20 | N | 51 | N | 14 | N | N | 1.1101 | 39.4971 | 2720.6586
[7 empty] | 12700 | 4161 | 1201176 | 2015-01-20 07:32 | 2015-01-20 11:20 | 228 | 11kV | 11948 | 61 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150267 3 fault operations Overcurrent Excludes OMS 1201176, 1201730, 1201732 | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-01-20 | N | 195.8689 | N | 14 | N | N | 1.1101 | 39.4971 | 8731.246
[7 empty] | 12272 | 139 | 1201279 | 2015-01-20 09:32 | 2015-01-20 11:45 | 133 | 11kV | 266 | 2 | HV | Lightning Strike | Adverse Weather/Environment | Lightning Arrestor | Unplanned | Previous Storm | N | LID 150268 10 amp fuse Substation DOLF Replaced arrestors Excludes OMS 1201279 | January | 2015 | 2015Q3 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2015-01-20 | N | 133 | N | 14 | N | N | 1.1101 | 39.4971 | 194.385
[7 empty] | 12472 | 1937 | 1201184 | 2015-01-20 07:53 | 2015-01-20 13:00 | 307 | 11kV | 614 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150269 3 amp fuse Substatoin DOLF REPLACED BLOWN DOLF | January | 2015 | 2015Q3 | 2015 | 810:74050 | 810:74050 | ZN00810/074050 | UPPER HUNTER | OH | Veg | 2015-01-20 | N | 307 | N | 14 | N | N | 1.1101 | 39.4971 | 448.6931
[7 empty] | 13427 | 10371 | 1201214 | 2015-01-20 08:23 | 2015-01-20 13:10 | 286.9167 | 11kV | 1434.5833 | 5 | HV | Staff Operation | Utility Process Issue | Fuse | Unplanned | Electrical Storm | N | LID 150270 All three Spur fuses were replaced / blown 31.5 amp AB & C phases, these fuses were incorrectly loaded with 3.15 amp insted of 31.5 amp at some stage | January | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2015-01-20 | N | 286.9167 | N | 14 | N | N | 1.1101 | 39.4971 | 1048.3512
[7 empty] | 14087 | 15697 | 1201207 | 2015-01-20 08:17 | 2015-01-20 13:15 | 298 | 11kV | 41452 | 204 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | No Weather Impact | N | Jeep hit pole; causing 11kV fuse (JOS 63 amp) B phase fuse replaced. 3 customers # 93, 95 and 97 Eastern Valley Rd experienced extended delays for repairs | January | 2015 | 2015Q3 | 2015 | ZN180:PA41 | ZN180:PA41 | ZN00180/000041 | WILLOUGHBY | OH | Not Veg | 2015-01-20 | N | 203.1961 | N | 14 | N | N | 1.1101 | 39.4971 | 30291.899
[7 empty] | 14662 | 20226 | 1201245 | 2015-01-20 09:00 | 2015-01-20 13:20 | 260 | 11kV | 17986 | 283 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Rain Light | N | Ex Zn12600 Lisarow section of Pa9 "Wyoming South" RE41845 North Erina tripped, reclosed, tripped, reclosed, tripped and locked out on overcurrent Overhead wire down on tee PT11410 See 1201739,41 exclude 1201245,54,393 | January | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Not Veg | 2015-01-20 | N | 63.5548 | N | 14 | N | N | 1.1101 | 39.4971 | 13143.6383
[7 empty] | 14613 | 19806 | 1201348 | 2015-01-20 11:50 | 2015-01-20 13:24 | 94 | 11kV | 4324 | 46 | HV | Equipment Failed in Service | Equipment Failure | DC Transformer | Unplanned | No Weather Impact | N | S 10822 Park Westfield - Tx 3 - Low Gas Tx tripped on low SF6 gas. Multi trip protection took out the other 2 txs in the sub also. ME: 1202464. Withdrawn: 1201348, 50, 58, 72. | January | 2015 | 2015Q3 | 2015 | ZN10999:PA3 | ZN10993:PA34 | ZN10993/000034 | GEORGES RIVER | UG | Not Veg | 2015-01-20 | N | 94 | N | 14 | N | N | 1.1101 | 39.4971 | 3159.8517
[7 empty] | 13684 | 12408 | 1201522 | 2015-01-20 16:49 | 2015-01-20 17:34 | 45 | 11kV | 612 | 16 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 150277 Wire off pin at DP-40783. No Protection Operation Excludes OMS 1201522, 1201744 | January | 2015 | 2015Q3 | 2015 | 515:35193 | 515:35193 | ZN00515/035193 | SINGLETON | OH | Not Veg | 2015-01-20 | N | 38.25 | N | 14 | N | N | 1.1101 | 39.4971 | 447.2315
[7 empty] | 14277 | 17051 | 1201586 | 2015-01-20 21:31 | 2015-01-21 01:05 | 214 | 11kV | 18815 | 146 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At Zn35500 Top Ryde Panel 19 Tripped on Relays: Earth Fault. EFI and Fault Check Signals: 11kV trip Tx2 Group Earth Suspect Cable fault See OMS 1202331 1202332 1201586/588 | January | 2015 | 2015Q3 | 2015 | ZN35500:PA19 | ZN35500:PA19 | ZN35500/000019 | RYDE | UG | Not Veg | 2015-01-20 | N | 128.8699 | N | 14 | N | N | 1.1101 | 39.4971 | 13749.4471
[7 empty] | 14292 | 17189 | 1201577 | 2015-01-20 21:23 | 2015-01-21 10:20 | 777 | 11kV | 50727 | 101 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150279 1 fault operation Pole mounted RAGCB, Sensitive earth fault Excludes OMS 1201577/697, 1202156/57/58/59 | January | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Veg | 2015-01-20 | N | 502.2475 | N | 14 | N | N | 1.1101 | 39.4971 | 37069.7954
[7 empty] | 12951 | 6469 | 1201725 | 2015-01-21 09:46 | 2015-01-21 13:30 | 224 | 11kV | 25088 | 112 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 150285 2 fault operations Overcurrent Fault found, crew to re-tie conductor using LL technique Excludes OMS 1201725, 1202175 | January | 2015 | 2015Q3 | 2015 | 243:80083 | 243:80083 | ZN00243/080083 | LAKE MACQUARIE | OH | Not Veg | 2015-01-21 | N | 224 | N | 6 | N | N | 1.1101 | 39.4971 | 18333.5704
[7 empty] | 13062 | 7334 | 1201940 | 2015-01-21 15:46 | 2015-01-21 16:23 | 37 | 11kV | 17094 | 462 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Bare | Unplanned | No Weather Impact | N | Recloser 2378 Dural Pacific ex Panel 5 Hornsby Cause: Tree branch fell and clashed on OH mains - DOp reports no damage See OMS 1201973 1201940 CC1: 22-"Refer to SOp" | January | 2015 | 2015Q3 | 2015 | ZN847:PA5 | ZN847:PA5 | ZN00847/000005 | HORNSBY | OH | Veg | 2015-01-21 | N | 37 | N | 6 | N | N | 1.1101 | 39.4971 | 12491.791
[7 empty] | 12382 | 1207 | 1201957 | 2015-01-21 16:30 | 2015-01-21 19:48 | 198.1667 | 11kV | 7065.2 | 520 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 150287 Bypass ABS replaced. Crossarm burnt in half at Sw 5975 glenarvon RAGCB. No Protection Operation. | January | 2015 | 2015Q3 | 2015 | 528:83020 | 528:83020 | ZN00528/083020 | MAITLAND | OH | Not Veg | 2015-01-21 | N | 13.5869 | N | 6 | N | N | 1.1101 | 39.4971 | 5163.0398
[7 empty] | 12268 | 96 | 1202008 | 2015-01-21 18:53 | 2015-01-21 21:50 | 177 | 11kV | 177 | 1 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 150290 10 amp fuse Substation DOLF Cross arm came down hit s/w Excludes OMS 1202008 | January | 2015 | 2015Q3 | 2015 | 810:74058 | 810:74058 | ZN00810/074058 | MUSWELLBROOK | OH | Not Veg | 2015-01-21 | N | 177 | N | 6 | N | N | 1.1101 | 39.4971 | 129.3464
[7 empty] | 14205 | 16539 | 1201980 | 2015-01-21 17:25 | 2015-01-21 22:45 | 320 | 11kV | 4768 | 71 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn14891 Wyong section of Pa5 "Wyong" RE45016 Dickson - tripped, reclosed, tripped and locked out on OC, IOC, EF Tree branch brought down Overhead. Note: Auto Links 44787 Bloomfield Rd did not operate region to investigate See 1202278,9 Exclude 1201980,93 | January | 2015 | 2015Q3 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Veg | 2015-01-21 | N | 67.1549 | N | 6 | N | N | 1.1101 | 39.4971 | 3484.3138
[7 empty] | 13387 | 10059 | 1202041 | 2015-01-21 22:35 | 2015-01-22 00:55 | 140 | 11kV | 173740 | 1241 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Zn12660 Woy Woy Panel 14 "South Woy WOy" fdr tripped on Relays: C phase timed overcurrent Signals: 11kv trip DOp patrolled and found nothing Cause not ascertained See 1202041 exclude 1202042 | January | 2015 | 2015Q3 | 2015 | ZN12660:PA14 | ZN12660:PA14 | ZN12660/000014 | CENTRAL COAST | OH | Veg | 2015-01-21 | N | 140 | N | 6 | N | N | 1.1101 | 39.4971 | 126964.0675
[7 empty] | 14405 | 17977 | 1202047 | 2015-01-22 00:34 | 2015-01-22 01:30 | 56 | 11kV | 5682 | 1997 | HV | Animal Possum | Animal | DC-PT Transformer | Unplanned | No Weather Impact | N | Zn12640 Umina Panel 13 "Patonga" fdr tripped and reclosed on Relays: A phase overcurrent, IOC, EFI Signals: 11kv trip @PT18022 Lace Cowper road Phase 31Amp HDO fuse operated Possum dead @ Base of PT18022 See 1202300,3 exclude 1202047 | January | 2015 | 2015Q3 | 2015 | ZN12640:PA13 | ZN12640:PA13 | ZN12640/000013 | CENTRAL COAST | OH | Not Veg | 2015-01-22 | N | 2.8453 | N | 2 | N | N | 1.1101 | 39.4971 | 4152.238
[7 empty] | 13596 | 11669 | 1202049 | 2015-01-22 01:17 | 2015-01-22 06:20 | 303 | 11kV | 269339 | 1166 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | LID 150291 4 fault operations Earth fault, Sensitive earth fault cable fault between sw 36529 (sub 36531) & sw 41632 Excludes OMS 1202049/053 1203662/63/65/66/69/770/74/75/78/82/83/84 | January | 2015 | 2015Q3 | 2015 | 511:29877 | 511:29877 | ZN00511/029877 | MAITLAND | UG | Not Veg | 2015-01-22 | N | 230.994 | N | 2 | N | N | 1.1101 | 39.4971 | 196824.997
[7 empty] | 14335 | 17440 | 1202632 | 2015-01-23 12:41 | 2015-01-23 12:56 | 15 | 11kV | 4170 | 278 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12640 Umina Pa18 "Pearl Beach" tripped on Relays - B & C phase IOC & Timed overcurrent Signals: 11kv trip Abnormal: Close LB49566 Open AB42533 Close LB45096 Open LB49531, LV//35682,30050 & PT IDT Cause: Tree Branch on 11kv OH in Edgecliff Rd. DOp was switching and isolating affected section of fdr when tree came down on to mains. RE45090 Pearl Beach may not grade with Pa18 at Umina See 1203715 exclude 1202632,43 | January | 2015 | 2015Q3 | 2015 | ZN12640:PA18 | ZN12640:PA4 | ZN12640/000004 | CENTRAL COAST | OH | Veg | 2015-01-23 | N | 15 | N | 5 | N | N | 1.1101 | 39.4971 | 3047.313
[7 empty] | 13723 | 12736 | 1202760 | 2015-01-23 15:41 | 2015-01-23 17:10 | 89 | 11kV | 63257 | 773 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Ex Zn12570 section of Pa29 "Bensville" RE44982 Bensville tripped on A&B phase overcurrent Cause not ascertained. Windy at times - supect tree branch See 1203782,3,4 Exclude 1202760 | January | 2015 | 2015Q3 | 2015 | ZN12570:PA29 | ZN36200:PA4 | ZN36200/000004 | CENTRAL COAST | OH | Veg | 2015-01-23 | N | 81.8331 | N | 5 | N | N | 1.1101 | 39.4971 | 46226.3498
[7 empty] | 13587 | 11599 | 1202787 | 2015-01-23 16:14 | 2015-01-23 17:12 | 58 | 11kV | 60262 | 1039 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | At Zn 9550 Gwawley Bay Panel 43 'Sub 48722 etc' feeder has tripped Signals: 11kv trip Relays: 51BC EFI's: S48722, S49698 Remarks: tree/branch on OH mains. Branch hit mains OS No.47 and fell clear. No AR on feeder | January | 2015 | 2015Q3 | 2015 | ZN9550:PA43 | ZN9550:PA43 | ZN09550/000043 | SUTHERLAND | OH | Veg | 2015-01-23 | N | 58 | N | 5 | N | N | 1.1101 | 39.4971 | 44037.6922
[7 empty] | 13557 | 11369 | 1202799 | 2015-01-23 15:32 | 2015-01-23 19:00 | 208 | 11kV | 1040 | 5 | HV | Animal Possum | Animal | Lightning Arrestor | Unplanned | No Weather Impact | N | PT13229 Greta Springs 0.3 C phase HVDO fuse operated due to Possum. Cut awau by DOp Wilson. Possum on PT caused damage to C phase poly LA Subs to check condition of HV fuse. Requires replacement with new type See 1203762 exclude 1202799 | January | 2015 | 2015Q3 | 2015 | ZN12630:PA1 | ZN12630:PA8 | ZN12630/000008 | CENTRAL COAST | OH | Not Veg | 2015-01-23 | N | 208 | N | 5 | N | N | 1.1101 | 39.4971 | 760.0013
[7 empty] | 13657 | 12167 | 1202770 | 2015-01-23 15:55 | 2015-01-23 21:41 | 346 | 11kV | 43706 | 600 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150312 1 fault operation A phase Earth Fault E/F current at trip: 392A. 11kV mains down Adj PT.54866 Frazer G. Note: Feeder failed while it was abnormally switched. See SI 3473. ABS 40196 was left open post this switching for possible live line repair but no crews were available. While awaiting Dop to return, Feeder tripped with ELB 40158 closed. | January | 2015 | 2015Q3 | 2015 | 507:80932 | 507:80932 | ZN00507/080932 | CESSNOCK | OH | Veg | 2015-01-23 | N | 72.8433 | N | 5 | N | N | 1.1101 | 39.4971 | 31939.0557
[7 empty] | 13109 | 7714 | 1202896 | 2015-01-24 09:59 | 2015-01-24 11:05 | 66 | 11kV | 330 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150319 B phase DOLF : 10 Amp Excluded OMS 1202896 | January | 2015 | 2015Q3 | 2015 | 513:48059 | 513:83495 | ZN00513/083495 | SINGLETON | OH | Veg | 2015-01-24 | N | 66 | N | 19 | N | N | 1.1101 | 39.4971 | 241.1543
[7 empty] | 14676 | 20339 | 1202898 | 2015-01-24 10:01 | 2015-01-24 11:10 | 69 | 11kV | 207 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150318 B phase DOLF : 10 Amp Excluded OMS 1202898 | January | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 69 | N | 19 | N | N | 1.1101 | 39.4971 | 151.2695
[7 empty] | 12703 | 4182 | 1202942 | 2015-01-24 14:13 | 2015-01-24 15:50 | 97 | 11kV | 153108 | 1762 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | @Zn2196 Milperra 11kv Panel #3 labelled "S4449 & S1764" tripped & locked out: Relays: SEF Signals: 11kv trip Field EFIs Abnormal: Close Sw/A @ S8011 Truscott Batchelor Open IS3265 Remarks: bond. B phase/Centre phase open bond line side of AB3133. Refer DMA | January | 2015 | 2015Q3 | 2015 | ZN2196:PA3 | ZN2196:PA3 | ZN02196/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-01-24 | N | 86.8944 | N | 19 | N | N | 1.1101 | 39.4971 | 111886.8105
[7 empty] | 14659 | 20216 | 1202958 | 2015-01-24 15:25 | 2015-01-24 19:25 | 240 | 11kV | 91399 | 1287 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At ZN847 Hornsby Panel 21 feeder tripped reclosed tripped and locked out on Relays: A and C phase IOC, A and C phase O/C, Earth Fault, Lockout, Fault Check and EFI 11kV down O/S 43 Manor Rd Hornsby See OMS 1207255 1207259 1207258 1202990 1202958 | January | 2015 | 2015Q3 | 2015 | ZN847:PA21 | ZN847:PA21 | ZN00847/000021 | HORNSBY | OH | Veg | 2015-01-24 | N | 71.0171 | N | 19 | N | N | 1.1101 | 39.4971 | 66791.6934
[7 empty] | 12757 | 4635 | 1203001 | 2015-01-24 19:12 | 2015-01-24 19:56 | 44 | 11kV | 264 | 6 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | LID 150321 C phase No protection operated High Resisitance fault at ABS 43826. Excluded OMS 1203001 | January | 2015 | 2015Q3 | 2015 | 514:18141 | 514:18141 | ZN00514/018141 | SINGLETON | OH | Not Veg | 2015-01-24 | N | 44 | N | 19 | N | N | 1.1101 | 39.4971 | 192.9234
[7 empty] | 13439 | 10470 | 1204458 | 2015-01-24 20:50 | 2015-01-24 20:56 | 6 | 11kV | 138 | 23 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150348 1 fault operation Overcurrent | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 6 | N | 19 | N | N | 1.1101 | 39.4971 | 100.8463
[7 empty] | 12844 | 5484 | 1204849 | 2015-01-24 21:17 | 2015-01-24 22:35 | 78 | 11kV | 10788 | 141 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150322 2 fault operations Excluded OMS 1203021 | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 76.5106 | N | 19 | N | N | 1.1101 | 39.4971 | 7883.5522
[7 empty] | 12599 | 3218 | 1203051 | 2015-01-24 22:22 | 2015-01-24 22:47 | 25 | 11kV | 1515 | 95 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150343 2 fault operations Overcurrent; Earth fault | January | 2015 | 2015Q3 | 2015 | 516:48066 | 516:48066 | ZN00516/048066 | SINGLETON | OH | Veg | 2015-01-24 | N | 15.9474 | N | 19 | N | N | 1.1101 | 39.4971 | 1107.1173
[7 empty] | 12253 | 5 | 1204615 | 2015-01-24 22:00 | 2015-01-24 23:30 | 90 | 11kV | 1260 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150362 3 Phase DOLF : 20Amp Staff not provided with an OMS number or the time outage was reported. So outage time guessed, | January | 2015 | 2015Q3 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | SINGLETON | OH | Veg | 2015-01-24 | N | 90 | N | 19 | N | N | 1.1101 | 39.4971 | 920.7708
[7 empty] | 12767 | 4709 | 1203074 | 2015-01-25 00:10 | 2015-01-25 01:20 | 70 | 11kV | 560 | 8 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150370 C phase DOLF : 10 Amp Excluded OMS 1203074 | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-01-25 | N | 70 | N | 31 | Y | Y | 1.1101 | 39.4971 | 409.2315
[7 empty] | 13097 | 7643 | 1203050 | 2015-01-24 22:28 | 2015-01-25 02:20 | 232 | 11kV | 2088 | 9 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150372 Three phase: 16 amp fuse Line DOLF Replaces OMS 1203050 | January | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2015-01-24 | N | 232 | N | 19 | N | N | 1.1101 | 39.4971 | 1525.8488
[7 empty] | 13100 | 7659 | 1203055 | 2015-01-24 22:34 | 2015-01-25 02:30 | 236 | 11kV | 70362 | 448 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Electrical Storm | N | LID 150368/150375 2 fault operations Earth fault excluded OMS 1205001, 1203055 & 1203057 | January | 2015 | 2015Q3 | 2015 | 523:33509 | 523:33509 | ZN00523/033509 | SINGLETON | OH | Not Veg | 2015-01-24 | N | 157.058 | N | 19 | N | N | 1.1101 | 39.4971 | 51418.4743
[7 empty] | 13739 | 12831 | 1203037 | 2015-01-24 22:08 | 2015-01-25 02:55 | 287 | 11kV | 12915 | 45 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150374 DOLF : 10 Amp Blown DOLF and Arrestor Excluded OMS 1203037 | January | 2015 | 2015Q3 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 287 | N | 19 | N | N | 1.1101 | 39.4971 | 9437.9011
[7 empty] | 14521 | 18850 | 1203077 | 2015-01-25 01:38 | 2015-01-25 05:14 | 216 | 11kV | 1728 | 8 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | Electrical Storm | N | LID 150376 10 amp fuse Substation DOLF crossarm fallen off pole Replaces OMS 1203077 | January | 2015 | 2015Q3 | 2015 | 801:74121 | 801:74121 | ZN00801/074121 | MUSWELLBROOK | OH | Not Veg | 2015-01-25 | N | 216 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1262.7714
[7 empty] | 13553 | 11339 | 1203084 | 2015-01-25 04:18 | 2015-01-25 07:45 | 207 | 11kV | 207 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150379 B & C phase DOLF : 16 Amp also 10A sub dolfs 54264. Excluded oms 1203084 | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-01-25 | N | 207 | N | 31 | Y | Y | 1.1101 | 39.4971 | 151.2695
[7 empty] | 13763 | 13009 | 1203096 | 2015-01-25 06:59 | 2015-01-25 08:20 | 81 | 11kV | 162 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150380 B phase DOLF : 3 Amp Excluded OMS 1203096 + 1203105 | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Veg | 2015-01-25 | N | 81 | N | 31 | Y | Y | 1.1101 | 39.4971 | 118.3848
[7 empty] | 13867 | 13851 | 1203035 | 2015-01-24 22:01 | 2015-01-25 09:05 | 664 | 11kV | 2656 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150382 3 Phase DOLF : 10 Amp excluded OMS 1203035 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 664 | N | 19 | N | N | 1.1101 | 39.4971 | 1940.9265
[7 empty] | 13460 | 10649 | 1203081 | 2015-01-25 03:56 | 2015-01-25 09:50 | 354 | 11kV | 199962 | 1579 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150377 2 fault operations ohm down at pole IU-80302 Excluded oms 1203081 | January | 2015 | 2015Q3 | 2015 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Veg | 2015-01-25 | N | 126.6384 | N | 31 | Y | Y | 1.1101 | 39.4971 | 146126.3317
[7 empty] | 13580 | 11553 | 1203109 | 2015-01-25 07:40 | 2015-01-25 10:10 | 150 | 11kV | 750 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150384 10 amp fuse Substation DOLF Replaces OMS 1203109 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-01-25 | N | 150 | N | 31 | Y | Y | 1.1101 | 39.4971 | 548.0779
[7 empty] | 13525 | 11102 | 1203042 | 2015-01-24 22:39 | 2015-01-25 11:00 | 741 | 11kV | 741 | 1 | HV | Customer Installation Fault | Customer Installation | 3rd Party Asset | Unplanned | Electrical Storm | N | LID 150386 C phase DOLF : 10 Amp Cust Sw/Bd blown up - sub 70497 LVFs left open Excluded oms 1203054 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | Unknown | Not Veg | 2015-01-24 | N | 741 | N | 19 | N | N | 1.1101 | 39.4971 | 541.5009
[7 empty] | 12512 | 2381 | 1203072 | 2015-01-24 23:39 | 2015-01-25 11:35 | 716 | 11kV | 24344 | 34 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Electrical Storm | N | LID 150383 Excluded OMS 1203072 | January | 2015 | 2015Q3 | 2015 | 807:74181 | 807:74181 | ZN00807/074181 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 716 | N | 19 | N | N | 1.1101 | 39.4971 | 17789.8772
[7 empty] | 13290 | 9038 | 1203165 | 2015-01-25 11:15 | 2015-01-25 12:15 | 60 | 11kV | 60 | 1 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Unknown | Unplanned | Electrical Storm | N | LID 150387 10 amp fuse Substation DOLF AT POLE NUMBER AN40173 - D.W PULLED AWAY AT POLE - CLOSER TO SERVICE FUSES Excludes OMS 1203165 | January | 2015 | 2015Q3 | 2015 | 516:48067 | 516:48067 | ZN00516/048067 | MUSWELLBROOK | OH | Not Veg | 2015-01-25 | N | 60 | N | 31 | Y | Y | 1.1101 | 39.4971 | 43.8462
[7 empty] | 14154 | 16198 | 1203103 | 2015-01-25 06:56 | 2015-01-25 12:18 | 322 | 11kV | 3220 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150396 16 amp fuse Line DOLF REPLACED DROP OUT FUSES Start time amended per time of first call Replaces OMS 1203127 + 1203094 + 1203103 Note: LID report 150399 DOLF on sub 70245 replaced at 25/01/2015 06:56:00 to 25/01/2015 12:38:00. This single customer outage ran concurrently with this upstream device | January | 2015 | 2015Q3 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 322 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2353.081
[7 empty] | 13157 | 8022 | 1203094 | 2015-01-25 06:56 | 2015-01-25 12:38 | 342 | 11kV | 2052 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150397 10 amp fuse Line DOLF REPLACED DROP OUT FUSES Start time amended per time of first call Replaces OMS 1203127 ## concurrent with OMS 1205098/LID 150396 on device 74786## | January | 2015 | 2015Q3 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 342 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1499.5411
[7 empty] | 12804 | 5057 | 1205592 | 2015-01-25 06:56 | 2015-01-25 12:38 | 342 | 11kV | 1368 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150401 10 amp fuse Substation DOLF REPLACED DROP OUT FUSES Start time amended per time of first call Replaces OMS 1203127 + 1203094 + 1203103 ## concurrent with OMS 1205106/LID 150397 on device 74431 & OMS 1205108/LID 150399 on device 70245 & OMS 1205598/LID 150400 on device 73208## | January | 2015 | 2015Q3 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 342 | N | 31 | Y | Y | 1.1101 | 39.4971 | 999.6941
[7 empty] | 13016 | 6920 | 1206679 | 2015-01-25 06:56 | 2015-01-25 12:38 | 342 | 11kV | 342 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150400 10 amp fuse Substation DOLF REPLACED DROP OUT FUSES Start time amended per time of first call Replaces OMS 1203127 + 1203094 + 1203103 ## concurrent with OMS 1205106/LID 150397 on device 74431 & OMS 1205108/LID 150399 on device 70245 & OMS 1205592/LID 150401 on device 64940## | January | 2015 | 2015Q3 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 342 | N | 31 | Y | Y | 1.1101 | 39.4971 | 249.9235
[7 empty] | 14429 | 18138 | 1203095 | 2015-01-25 06:57 | 2015-01-25 13:50 | 413 | 11kV | 5782 | 14 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150392 3 phase DOLF : 15 Amp | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 413 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4225.3151
[7 empty] | 12706 | 4202 | 1205099 | 2015-01-25 06:57 | 2015-01-25 13:50 | 413 | 11kV | 826 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150393 Cphase DOLF : 10 Amp Excluded OMS 1203098 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 413 | N | 31 | Y | Y | 1.1101 | 39.4971 | 603.6164
[7 empty] | 13778 | 13141 | 1203134 | 2015-01-25 09:31 | 2015-01-25 14:15 | 284 | 11kV | 284 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150391 10 amp fuse Substation DOLF POLE 73136 9N20010 DROP OUT FUSE DOWN ON TRANSFORMER IN FRONT PREMISES Excludes OMS 1203134 | January | 2015 | 2015Q3 | 2015 | 812:19072 | 812:19072 | ZN00812/019072 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 284 | N | 31 | Y | Y | 1.1101 | 39.4971 | 207.5388
[7 empty] | 13392 | 10103 | 1203202 | 2015-01-25 14:05 | 2015-01-25 15:03 | 58 | 11kV | 11890 | 205 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150394 Feeder was abnormally switched due to several OMS jobs 1203017 and others. The feeder was switched this was switched this way so we could restore supply to most customers by closing ELBS 42431 via DNMS as we could not get staff to attend. B Phase was reading under 10A, however A and C phase loads are not displayed and the load crept up on these two phases causing overcurrent trips. We had it bypassed and altered the parallel as soon as we had staff available. | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 58 | N | 31 | Y | Y | 1.1101 | 39.4971 | 8688.8613
[7 empty] | 13619 | 11876 | 1205204 | 2015-01-25 06:57 | 2015-01-25 15:20 | 503 | 11kV | 2515 | 5 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150393 Cphase DOLF : 10 Amp Excluded OMS 1203098 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 503 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1837.8878
[7 empty] | 13118 | 7778 | 1203182 | 2015-01-25 11:00 | 2015-01-25 17:00 | 360 | 11kV | 720 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150405 A phase 10 amp fuse Substation DOLF Pole fuse down Replaces OMS 1203044 + 1203182 | January | 2015 | 2015Q3 | 2015 | 813:89055 | 813:89055 | ZN00813/089055 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 360 | N | 31 | Y | Y | 1.1101 | 39.4971 | 526.1548
[7 empty] | 14490 | 18606 | 1211489 | 2015-01-24 21:46 | 2015-01-25 17:30 | 1184 | 11kV | 260553 | 503 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150333 2 fault operations - feeder patroled in conjunction with 1205188 Sub 70146 a faulty transformer | January | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Veg | 2015-01-24 | N | 517.998 | N | 19 | N | N | 1.1101 | 39.4971 | 190404.4474
[7 empty] | 12452 | 1795 | 1205191 | 2015-01-25 01:45 | 2015-01-25 17:30 | 945 | 11kV | 5670 | 6 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 1505191 A phase DOLF : 10 Amp Excluded OMS 1203078 & 1203120 | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 945 | N | 31 | Y | Y | 1.1101 | 39.4971 | 4143.4688
[7 empty] | 14367 | 17650 | 1203117 | 2015-01-25 08:18 | 2015-01-25 18:10 | 592 | 11kV | 592 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150414 Singe phase DOLF : 10 Amp excluded OMS 1203117 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 592 | N | 31 | Y | Y | 1.1101 | 39.4971 | 432.6161
[7 empty] | 13073 | 7416 | 1203275 | 2015-01-25 06:00 | 2015-01-25 18:20 | 740 | 11kV | 1480 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | Electrical Storm | N | LID 150420 10 amp fuse Substation DOLF Replaces OMS 1203275 | January | 2015 | 2015Q3 | 2015 | 813:89061 | 813:89061 | ZN00813/089061 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 740 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1081.5403
[7 empty] | 14148 | 16169 | 1205215 | 2015-01-25 08:00 | 2015-01-25 18:30 | 630 | 11kV | 1260 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150424 A phase DOLF : 10 Amp NO OMS NUMBER LOCLA CREW SPOTTED THIS JOB. TIME ESTIMATED. | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-01-25 | N | 630 | N | 31 | Y | Y | 1.1101 | 39.4971 | 920.7708
[7 empty] | 14249 | 16902 | 1204714 | 2015-01-24 21:15 | 2015-01-25 19:50 | 1355 | 11kV | 14683 | 63 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150365 1 fault operation Sensitive Earth Fault Excluded OMS 1200307 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-24 | N | 233.0635 | N | 19 | N | N | 1.1101 | 39.4971 | 10729.9033
[7 empty] | 13206 | 8464 | 1203267 | 2015-01-24 23:00 | 2015-01-25 19:50 | 1250 | 11kV | 1250 | 1 | HV | Lightning Strike | Adverse Weather/Environment | DC-PT Transformer | Unplanned | Previous Storm | N | LID 150433 10 amp fuse Substation DOLF POLE TRANSFORMER DAMAGED OUTSIDE THIS PROPERTY - HIT BY LIGHTNING LAST NIGHT Replaces OMS 1203267 | January | 2015 | 2015Q3 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Not Veg | 2015-01-24 | N | 1250 | N | 19 | N | N | 1.1101 | 39.4971 | 913.4631
[7 empty] | 13220 | 8542 | 1203265 | 2015-01-25 17:18 | 2015-01-25 20:59 | 221 | 11kV | 135723 | 1162 | HV | Vegetation Grow In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150408 2 fault operations Earth fault Tree branch, Mains down at pole GT-14293 Excluded OMS 1203265, 1203274 | January | 2015 | 2015Q3 | 2015 | 504:48033 | 522:83126 | ZN00522/083126 | CESSNOCK | OH | Veg | 2015-01-25 | N | 116.8012 | N | 31 | Y | Y | 1.1101 | 39.4971 | 99182.3652
[7 empty] | 12574 | 3048 | 1203137 | 2015-01-25 09:52 | 2015-01-25 21:00 | 668 | 11kV | 668 | 1 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Previous Storm | N | LID 150413 3 Phase DOLF : 10 Amp | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-01-25 | N | 668 | N | 31 | Y | Y | 1.1101 | 39.4971 | 488.1547
[7 empty] | 13852 | 13693 | 1213610 | 2015-01-25 14:25 | 2015-01-25 21:26 | 421 | 11kV | 141456 | 336 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 150449 2 fault operations A & C phase Overcurrent OMS REPORT NO 1203390 & 1203210.X-ARM at pole DQ-10052 burnt. | January | 2015 | 2015Q3 | 2015 | 515:35192 | 515:35192 | ZN00515/035192 | SINGLETON | OH | Not Veg | 2015-01-25 | N | 421 | N | 31 | Y | Y | 1.1101 | 39.4971 | 103371.8726
[7 empty] | 14273 | 17040 | 1203283 | 2015-01-25 18:51 | 2015-01-25 22:55 | 244 | 11kV | 488 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150434 10 amp fuse Substation DOLF Excludes OMS 1203283 + 1203327 | January | 2015 | 2015Q3 | 2015 | 813:89062 | 813:89062 | ZN00813/089062 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 244 | N | 31 | Y | Y | 1.1101 | 39.4971 | 356.616
[7 empty] | 13075 | 7433 | 1203194 | 2015-01-25 13:19 | 2015-01-25 23:30 | 611 | 11kV | 611 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150388 10 amp fuse Substation DOLF high voltage fuse replaced pole#AN70095 Excludes OMS 1203194 | January | 2015 | 2015Q3 | 2015 |  |  |  | SINGLETON | OH | Veg | 2015-01-25 | N | 611 | N | 31 | Y | Y | 1.1101 | 39.4971 | 446.5008
[7 empty] | 14410 | 17987 | 1203149 | 2015-01-25 21:00 | 2015-01-25 23:59 | 179 | 11kV | 179 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150431 10 amp fuse Substation DOLF SPOTTED BY STAFF NO OMS NUMBER. | January | 2015 | 2015Q3 | 2015 | 811:74234 | 811:74234 | ZN00811/074234 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 179 | N | 31 | Y | Y | 1.1101 | 39.4971 | 130.8079
[7 empty] | 13969 | 14691 | 1203341 | 2015-01-25 22:18 | 2015-01-26 00:55 | 157 | 11kV | 471 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150438 10 amp fuse Substation DOLF, Distribution LV fuse Excludes OMS 1203341 A DOLF 10amp & A & C LVF 100amp | January | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82285 | ZN00814/082285 | UPPER HUNTER | OH | Veg | 2015-01-25 | N | 157 | N | 31 | Y | Y | 1.1101 | 39.4971 | 344.1929
[7 empty] | 13137 | 7881 | 1203152 | 2015-01-25 12:45 | 2015-01-26 11:25 | 1360 | 11kV | 2086 | 7 | HV | 3rd Party Vehicle | 3rd Party Impact | U/G Cable | Unplanned | No Weather Impact | N | LID 150421 INITIAL FAULT WAS A REPAIR AFTER HUNTER WATER DUG UP AND DAMAGED 11kV CONDUIT. The cross arm at 11kV links 41521 was found defective so a second permit with an extended area was later issued. Staff could not operate fuse switch at sub 54682 during restoration switching so another permit had to be issued. | January | 2015 | 2015Q3 | 2015 | 507:80926 | 507:80926 | ZN00507/080926 | CESSNOCK | UG | Not Veg | 2015-01-25 | N | 298 | N | 31 | Y | Y | 1.1101 | 39.4971 | 1524.3873
[7 empty] | 14512 | 18802 | 1203360 | 2015-01-26 06:58 | 2015-01-26 12:15 | 317 | 11kV | 317 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150445 10 amp fuse Substation DOLF Excludes OMS 1203360 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-26 | N | 317 | N | 12 | N | N | 1.1101 | 39.4971 | 231.6543
[7 empty] | 14666 | 20245 | 1203416 | 2015-01-26 11:05 | 2015-01-26 12:40 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150447 10 amp fuse Substation DOLF Excludes OMS 1203416 | January | 2015 | 2015Q3 | 2015 | 514:18137 | 514:18137 | ZN00514/018137 | SINGLETON | OH | Veg | 2015-01-26 | N | 95 | N | 12 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 13882 | 13942 | 1203421 | 2015-01-26 11:29 | 2015-01-26 12:55 | 86 | 11kV | 688 | 8 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | PT14988 Sparks Louisiana 16K roadside phase HDO blown Fuse Fatigue See 1203853 exclude 1203421 | January | 2015 | 2015Q3 | 2015 | ZN14892:PA10 | ZN14892:PA10 | ZN14892/000010 | CENTRAL COAST | OH | Not Veg | 2015-01-26 | N | 86 | N | 12 | N | N | 1.1101 | 39.4971 | 502.7701
[7 empty] | 13422 | 10363 | 1203439 | 2015-01-26 13:09 | 2015-01-26 14:00 | 51 | 11kV | 51 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150448 10 amp fuse Substation DOLF Excluded OMS 1203439 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-26 | N | 51 | N | 12 | N | N | 1.1101 | 39.4971 | 37.2693
[7 empty] | 13349 | 9738 | 1203322 | 2015-01-25 20:40 | 2015-01-26 15:10 | 1110 | 11kV | 3330 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Previous Storm | N | LID 150442 10 amp fuse Substation DOLF Replaces OMS 1203322 26/01/15 05:25 t45925: faulty trans to be replaced 26/01/15 | January | 2015 | 2015Q3 | 2015 | 515:35197 | 515:35197 | ZN00515/035197 | SINGLETON | OH | Not Veg | 2015-01-25 | N | 1110 | N | 31 | Y | Y | 1.1101 | 39.4971 | 2433.4658
[7 empty] | 13902 | 14157 | 1203490 | 2015-01-26 18:10 | 2015-01-26 19:23 | 73 | 11kV | 161004 | 2332 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Heavy | N | At Zn72 Five Dock Panel 10 'S7651' feeder has tripped Signals: 11kv trip, ZE, AGE Relays: C phase OC and EFI EFI's: S7651, S3714, S2255, S3263, S35570, S3660 Remarks: UG fault. UG fault between Sw/B @ S3660 Bland Julia and Sw/A @ Sub 4256 Bland Parra | January | 2015 | 2015Q3 | 2015 | ZN72:PA10 | ZN35555:PA9 | ZN35555/000009 | INNER WEST | UG | Not Veg | 2015-01-26 | N | 69.0412 | N | 12 | N | N | 1.1101 | 39.4971 | 117656.9744
[7 empty] | 12569 | 3015 | 1203516 | 2015-01-26 19:11 | 2015-01-26 19:55 | 44 | 11kV | 6160 | 140 | HV | OTHER - REFER COMMENTS | OTHER - REFER COMMENTS | Pole | Unplanned | No Weather Impact | N | At S4545 Meadowbank section of Pa42 - S4056 Gaza Victoria - B Phase HDO 40A fuse operated Cause: Pole Fire at AB2881 See OMS 1204673 1203516 1203519 | January | 2015 | 2015Q3 | 2015 | ZN4545:PA42 | ZN4545:PA42 | ZN04545/000042 | RYDE | OH | Not Veg | 2015-01-26 | N | 44 | N | 12 | N | N | 1.1101 | 39.4971 | 4501.5463
[7 empty] | 13209 | 8470 | 1203502 | 2015-01-26 18:52 | 2015-01-26 20:40 | 108 | 11kV | 37369 | 1071 | HV | Fire (Non Ausgrid) | UNKNOWN | Pole | Unplanned | No Weather Impact | N | At S4545 Meadowbank Panel 27 Tripped, Reclosed Tripped and Locked out on A phase IOC and OC - Reclose Lockout and Reclose Time Delay. Cause: Pole Fire at AB2881. See OMS 1204611 1204613 1204614 1203502 | January | 2015 | 2015Q3 | 2015 | ZN4545:PA27 | ZN4545:PA27 | ZN04545/000027 | RYDE | OH | Not Veg | 2015-01-26 | N | 34.8917 | N | 12 | N | N | 1.1101 | 39.4971 | 27308.163
[7 empty] | 14275 | 17044 | 1203526 | 2015-01-26 19:45 | 2015-01-26 21:20 | 95 | 11kV | 95 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 150450 10 amp fuse Substation DOLF Excludes OMS 1203526 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-26 | N | 95 | N | 12 | N | N | 1.1101 | 39.4971 | 69.4232
[7 empty] | 13179 | 8235 | 1203558 | 2015-01-26 23:14 | 2015-01-27 01:00 | 106 | 11kV | 106 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID 150451 10 amp fuse Substation DOLF Excludes OMS 1203558 | January | 2015 | 2015Q3 | 2015 | 806:82667 | 806:82667 | ZN00806/082667 | UPPER HUNTER | OH | Veg | 2015-01-26 | N | 106 | N | 12 | N | N | 1.1101 | 39.4971 | 77.4617
[7 empty] | 12309 | 526 | 1203557 | 2015-01-26 23:11 | 2015-01-27 01:55 | 164 | 11kV | 25886 | 164 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Light | N | Zn14144 Wamberal ex Pa2 RE44946 Kunarra rd has tripped Signals: Overcurrent, IOC Tree branch found resting just above crossarm near Tee to PT13871. See 1203858,9,65 Exclude 1203557 | January | 2015 | 2015Q3 | 2015 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Veg | 2015-01-26 | N | 157.8415 | N | 12 | N | N | 1.1101 | 39.4971 | 18916.7253
[7 empty] | 14364 | 17625 | 1206419 | 2015-01-27 01:53 | 2015-01-27 04:11 | 138 | 11kV | 342240 | 2480 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | ZN 9700 Kirrawee - Pnl 20 - Trip/reclose/trip, B & C phase IOC and Timed OC, Timer, Lockout. Cause not ascertained. ME: 1206419. Withdrawn: 1203566. | January | 2015 | 2015Q3 | 2015 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Veg | 2015-01-27 | N | 138 | N | 12 | N | N | 1.1101 | 39.4971 | 250098.8976
[7 empty] | 14038 | 15344 | 1203595 | 2015-01-27 07:31 | 2015-01-27 07:45 | 14 | 11kV | 140 | 10 | HV | Arcing | Equipment Failure | DC-PT Transformer | Unplanned | Rain Light | N | Ex Zn14144 Wamberal section of Pa2 "Glen Eagles Fairway" @PT11285 Oak Coachwood 0.5 road and centre HDO's blown DOp arrived to find bushings on fire. See 1205596 exclude 1203595,7,8 | January | 2015 | 2015Q3 | 2015 | ZN14144:PA2 | ZN14144:PA2 | ZN14144/000002 | CENTRAL COAST | OH | Not Veg | 2015-01-27 | N | 14 | N | 12 | N | N | 1.1101 | 39.4971 | 102.3079
[7 empty] | 12473 | 1941 | 1203613 | 2015-01-27 07:51 | 2015-01-27 08:16 | 25 | 11kV | 18525 | 741 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | Recloser CP46113 Fiddens Wharf Coronga Tripped reclosed tripped and locked out on Cause not ascertained for outage Feeder patrolled by DOp | January | 2015 | 2015Q3 | 2015 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2015-01-27 | N | 25 | N | 12 | N | N | 1.1101 | 39.4971 | 13537.5236
[7 empty] | 13615 | 11824 | 1203609 | 2015-01-27 07:49 | 2015-01-27 08:50 | 61 | 11kV | 244 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | LID 150453 40 amp fuse Substation DOLF Found B phase DOLF link dropped and burnt in half. Replaces OMS 1203609 | January | 2015 | 2015Q3 | 2015 | 224:80346 | 224:80346 | ZN00224/080346 | LAKE MACQUARIE | OH | Veg | 2015-01-27 | N | 61 | N | 12 | N | N | 1.1101 | 39.4971 | 178.308
[7 empty] | 13904 | 14169 | 1205022 | 2015-01-24 20:57 | 2015-01-27 11:55 | 3778 | 11kV | 18761 | 171 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Electrical Storm | N | LID 150366 Sensitive Earth Fault Mains off insulators past links 74599 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-01-24 | N | 109.7135 | N | 19 | N | N | 1.1101 | 39.4971 | 13709.9854
[7 empty] | 14618 | 19858 | 1203606 | 2015-01-27 07:45 | 2015-01-27 12:15 | 270 | 11kV | 2700 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Light | N | Ex Zn12630 Peats Ridge section of Pa2 "Gunderman" PT13636 Wise Ferry Laven 22.15 footpath phase HDO blown 20A Cause not ascertained See 1205603 exclude 1203606,728 | January | 2015 | 2015Q3 | 2015 | ZN12630:PA2 | ZN12630:PA1 | ZN12630/000001 | CENTRAL COAST | OH | Veg | 2015-01-27 | N | 270 | N | 12 | N | N | 1.1101 | 39.4971 | 1973.0804
[7 empty] | 14587 | 19436 | 1203523 | 2015-01-26 19:37 | 2015-01-27 12:25 | 1008 | 11kV | 9348 | 95 | HV | Equipment Failed in Service | Equipment Failure | Lightning Arrestor | Unplanned | Rain Light | N | Ex Zn12690 Berkeley Vale section of Pa24 RE45117 Glenning Valley tripped, relcosed, tripped and locked out on Earth Fault, IOC ABNORMAL LB44503 closed, AB44898 Open Lightning Arrestor blown PT12251 Brush Ourimbah 2.0 See 1205251,3,4,5 Exclude 1203523,4,35 | January | 2015 | 2015Q3 | 2015 | ZN12690:PA24 | ZN12690:PA24 | ZN12690/000024 | CENTRAL COAST | OH | Not Veg | 2015-01-26 | N | 98.4 | N | 12 | N | N | 1.1101 | 39.4971 | 6831.2427
[7 empty] | 14315 | 17312 | 1205701 | 2015-01-27 11:38 | 2015-01-27 12:27 | 49 | 11kV | 15506 | 322 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150458 2 fault operations C Phase Overcurrent; Excludes restoration OMS 1205703/4/5 Replaces OMS 1204725 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-27 | N | 48.1553 | N | 12 | N | N | 1.1101 | 39.4971 | 11331.3275
[7 empty] | 13388 | 10079 | 1203240 | 2015-01-25 07:45 | 2015-01-27 12:40 | 3175 | 11kV | 9525 | 3 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Electrical Storm | N | LID 150437 10 amp fuse Substation DOLF 26/01/15 00:24 t45925: faulty transformer, repairs to be completed 26/01/15 Replaces OMS 1203240 & 1205188 | January | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82283 | ZN00814/082283 | UPPER HUNTER | OH | Not Veg | 2015-01-25 | N | 3175 | N | 31 | Y | Y | 1.1101 | 39.4971 | 6960.5891
[7 empty] | 12730 | 4479 | 1204019 | 2015-01-27 15:19 | 2015-01-27 16:30 | 71 | 11kV | 142 | 2 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150462 10 amp fuse Line DOLF | January | 2015 | 2015Q3 | 2015 | 807:74179 | 807:74179 | ZN00807/074179 | MUSWELLBROOK | OH | Veg | 2015-01-27 | N | 71 | N | 12 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 14293 | 17196 | 1203559 | 2015-01-26 23:22 | 2015-01-27 16:45 | 1043 | 11kV | 19063 | 56 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | Rain Light | N | Ex Zn14891 Wyong section of Pa12 RE45015 Brush Creek has tripped Relays: overcurrent trip, SEF trip About the first tee off after auto links 44776 Brush Creek suspect defective insulator. See 1205227,8 exclude 1203559,67 | January | 2015 | 2015Q3 | 2015 | ZN14891:PA12 | ZN14891:PA12 | ZN14891/000012 | CENTRAL COAST | OH | Not Veg | 2015-01-26 | N | 340.4107 | N | 12 | N | N | 1.1101 | 39.4971 | 13930.6781
[7 empty] | 13751 | 12916 | 1204035 | 2015-01-27 15:47 | 2015-01-27 16:55 | 68 | 11kV | 6052 | 89 | HV | Burnt Contacts | Equipment Failure | Live Line Tap/Clamp | Unplanned | Electrical Storm | N | LID 150463 LIVE LINE LEAD BURNT OFF ON A PHASE.SUB INTERCONNECTED & REPAIRED LATER. corrected restore time per LID Excludes OMS 1204035 | January | 2015 | 2015Q3 | 2015 | 512:48046 | 512:83733 | ZN00512/083733 | CESSNOCK | OH | Not Veg | 2015-01-27 | N | 68 | N | 12 | N | N | 1.1101 | 39.4971 | 4422.6231
[7 empty] | 12819 | 5200 | 1204097 | 2015-01-27 17:28 | 2015-01-27 18:15 | 47 | 11kV | 47 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | LID 150466 10 amp fuse Substation DOLF Replaces OMS 1204097 | January | 2015 | 2015Q3 | 2015 | 523:33501 | 523:33501 | ZN00523/033501 | SINGLETON | OH | Veg | 2015-01-27 | N | 47 | N | 12 | N | N | 1.1101 | 39.4971 | 34.3462
[7 empty] | 13308 | 9195 | 1203956 | 2015-01-27 14:00 | 2015-01-27 18:59 | 299 | 11kV | 299 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Unselected | N | LID 150464 10 amp fuse Substation DOLF Replaces OMS 1203956 (CROSS TIMBER HOLDING INSULATOR TO THE TRANSFORMER WAS ON FIRE AND STILL ARCING POLE NO 50077) | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-01-27 | N | 299 | N | 12 | N | N | 1.1101 | 39.4971 | 218.5004
[7 empty] | 13706 | 12584 | 1204124 | 2015-01-27 18:43 | 2015-01-27 22:50 | 247 | 11kV | 158630 | 2480 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | Rain Light | N | ZN 9700 Kirrawee - Pnl 20 - Trip/reclose/trip, A & C phase IOC and timed OC, timing, lockout. AB 35937 exploded. Cut away both sides and energised up to cross arm. ME: 1207079. Rest Steps: 1207082, 3, 4. Withdrawn: Heaps... | January | 2015 | 2015Q3 | 2015 | ZN9700:PA20 | ZN9700:PA20 | ZN09700/000020 | SUTHERLAND | OH | Not Veg | 2015-01-27 | N | 63.9637 | N | 12 | N | N | 1.1101 | 39.4971 | 115922.1252
[7 empty] | 13799 | 13276 | 1204178 | 2015-01-27 22:22 | 2015-01-28 00:25 | 123 | 11kV | 234315 | 2227 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | Rain Light | N | ZN 398 Dulwich Hill - Pnl 16 - OC, Earth Fault, EFI, Field EFIs. Underground fault between S 1900 to S 482. ME: 1206980. Rest Step: 1206981. Withdrawn: 1204178, 80. | January | 2015 | 2015Q3 | 2015 | ZN398:PA16 | ZN398:PA16 | ZN00398/000016 | INNER WEST | UG | Not Veg | 2015-01-27 | N | 105.2155 | N | 12 | N | N | 1.1101 | 39.4971 | 171230.4909
[7 empty] | 13108 | 7709 | 1204200 | 2015-01-28 01:40 | 2015-01-28 02:26 | 46 | 11kV | 21665 | 471 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn7481 Darling Harbour - Pnl.6 tripped on: OC and EF Field EFIs: S35376, S7567, S8203, S35479 UG cable fault from S35479 (Sw B) to S64484 (Sw A) to S1634 (Sw B) | January | 2015 | 2015Q3 | 2015 | ZN7481:PA6 | ZN7481:PA14 | ZN07481/000014 | SYDNEY | UG | Not Veg | 2015-01-28 | N | 45.9979 | N | 10 | N | N | 1.1101 | 39.4971 | 15832.143
[7 empty] | 13158 | 8023 | 1204236 | 2015-01-28 06:42 | 2015-01-28 07:30 | 48 | 11kV | 4032 | 84 | HV | Vegetation Blow/Fall In | Vegetation | DC-PT Transformer | Unplanned | Rain Wind Storm | N | PT11286 Bluebell Dill centre and footpath phase HDO operated. Branch on oh mains See 1206271 exclude 1204216,20,33,6 | January | 2015 | 2015Q3 | 2015 | ZN14144:PA7 | ZN14144:PA7 | ZN14144/000007 | CENTRAL COAST | OH | Veg | 2015-01-28 | N | 48 | N | 10 | N | N | 1.1101 | 39.4971 | 2946.4667
[7 empty] | 12747 | 4591 | 1204366 | 2015-01-28 10:17 | 2015-01-28 10:50 | 33 | 11kV | 99 | 3 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150472 Phase C; 10 amp fuse TX Volts 244V Replaced 10amp C phase HV fuse on Sub 51120 Replaces OMS 1204366 | January | 2015 | 2015Q3 | 2015 | 512:48049 | 512:83743 | ZN00512/083743 | SINGLETON | OH | Veg | 2015-01-28 | N | 33 | N | 10 | N | N | 1.1101 | 39.4971 | 72.3463
[7 empty] | 14477 | 18530 | 1205820 | 2015-01-28 10:55 | 2015-01-28 11:55 | 60 | 11kV | 600 | 10 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Electrical Storm | N | Planned LID 150475 SINO 4286 | January | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Veg | 2015-01-28 | N | 60 | N | 10 | N | N | 1.1101 | 39.4971 | 438.4623
[7 empty] | 14446 | 18263 | 1204600 | 2015-01-28 13:54 | 2015-01-28 15:16 | 82 | 11kV | 46066 | 619 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | Rain Heavy | N | Ex Zn12650 West Gosford section of Pa13 Intelliruptor 62731 Narrara Creek Manns tripped on overcurrent Tree fell over overhead wires. See 1206329,30 Exclude 1204598,600 | January | 2015 | 2015Q3 | 2015 | ZN12650:PA13 | ZN12650:PA13 | ZN12650/000013 | CENTRAL COAST | OH | Veg | 2015-01-28 | N | 74.42 | N | 10 | N | N | 1.1101 | 39.4971 | 33663.6741
[7 empty] | 13499 | 10942 | 1204557 | 2015-01-28 13:26 | 2015-01-28 17:30 | 244 | 11kV | 25140 | 261 | HV | Equipment Failed in Service | Equipment Failure | Air Break Switch | Unplanned | No Weather Impact | N | Section of ZN.15013 Terrey Hills 11kV Panel 10 from RE.1126 to extent of feeder (20 DC's) - Opened & Locked Out on OC & Earth Fault @ ZN.15013:- Zone Earth, No.2 Tx Group Earth, Panel 10 Fault Check & EFI Field EFI:- S.16910 Cause:- Fire @ ABS.20129 ME:-1204836 RS:-1204839 Withdrawn:-1204557 | January | 2015 | 2015Q3 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2015-01-28 | N | 96.3218 | N | 10 | N | N | 1.1101 | 39.4971 | 18371.5705
[7 empty] | 12824 | 5276 | 1204771 | 2015-01-28 17:32 | 2015-01-28 18:00 | 28 | 11kV | 112 | 4 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Previous Storm | N | LID 150477 Phase A: 10 amp fuse Substation DOLF pole fuse dropped down Replaces OMS 1204771 | January | 2015 | 2015Q3 | 2015 | 513:48056 | 513:83500 | ZN00513/083500 | SINGLETON | OH | Veg | 2015-01-28 | N | 28 | N | 10 | N | N | 1.1101 | 39.4971 | 81.8463
[7 empty] | 14011 | 15020 | 1204286 | 2015-01-28 08:48 | 2015-01-28 18:40 | 592 | 11kV | 592221 | 2417 | HV | 3rd Party Vehicle | 3rd Party Impact | Pole | Unplanned | Rain Heavy | N | ZN.10995 Riverwood 11kV Panel 2 tripped, reclosed, tripped and locked out on:- Relays:- A, B phase OC. Reclose timer, Lock out Signals:- Tx.1 Group Earth and 11kV Trip Cause:- Truck hit pole between ABS.31044 to LBS.31042 tee PT.10850 ME:-1206377 RS:-1206381 SE:-1206388, 1206390, 1206392, 1206393, 1206395 (Found in LV//) GIS Model Errors:-1206401, 1206399, 1206403, 1206405, 1206406, 1204298 Other RS:-1206411, 1206413, 1206415 Withdrawn:-1204489, 1204457, 1204463, 1204438, 1204286 | January | 2015 | 2015Q3 | 2015 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2015-01-28 | N | 245.0232 | N | 10 | N | N | 1.1101 | 39.4971 | 432777.6392
[7 empty] | 12828 | 5289 | 1204787 | 2015-01-28 18:42 | 2015-01-28 19:58 | 76.4667 | 11kV | 10170.0667 | 133 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Transformer | Unplanned | Rain Heavy | N | Section of ZN.15006 Dee Why West 11kV Panel 8 from F.21009 to extent of feeder (1 DC - PT.15286 Karoola St) - Street Phase HDO Operated @ ZN.15006 - Zone Earth & EFI Field EFI - S.16833 Cause:- Transformer failure Notes:- HDO failed a 2nd time when attempting to restore, PT restored via LV// (USL's 7972, 32958, 18238, 25841) ME:-1204787 Withdrawn:-1204795, 1204797 | January | 2015 | 2015Q3 | 2015 | ZN15006:PA8 | ZN15006:PA8 | ZN15006/000008 | NORTHERN BEACHES | OH | Not Veg | 2015-01-28 | N | 76.4667 | N | 10 | N | N | 1.1101 | 39.4971 | 7431.9848
[7 empty] | 13089 | 7549 | 1204796 | 2015-01-28 19:14 | 2015-01-28 20:25 | 71 | 11kV | 710 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | Rain Light | N | LID 150478 16 amp fuse Phase C Substation DOLF FUSE FATIGUE Replaces OMS 1204796 | January | 2015 | 2015Q3 | 2015 | 235:2120 | 235:2120 | ZN00235/002120 | CESSNOCK | OH | Not Veg | 2015-01-28 | N | 71 | N | 10 | N | N | 1.1101 | 39.4971 | 518.8471
[7 empty] | 12546 | 2742 | 1204871 | 2015-01-29 08:10 | 2015-01-29 09:09 | 58.9167 | 11kV | 21033.25 | 357 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor ABC | Unplanned | No Weather Impact | N | LID 150481 2 fault operations tree brought down comms wire pole JS-30909. RH Leg Sw 81240 relay 51BC # SEE OUTAGE 150480 | January | 2015 | 2015Q3 | 2015 | 264:81240 | 264:81240 | ZN00264/081240 | PORT STEPHENS | OH | Veg | 2015-01-29 | N | 58.9167 | N | 3 | N | N | 1.1101 | 39.4971 | 15370.4787
[7 empty] | 12668 | 3890 | 1205336 | 2015-01-29 17:49 | 2015-01-29 18:45 | 56 | 11kV | 56 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | LID150495 Phase B 10 amp fuse SUbstation DOLF Excludes OMS 1205336 | January | 2015 | 2015Q3 | 2015 | 802:82220 | 802:82220 | ZN00802/082220 | MUSWELLBROOK | OH | Veg | 2015-01-29 | N | 56 | N | 3 | N | N | 1.1101 | 39.4971 | 40.9231
[7 empty] | 14186 | 16393 | 1205238 | 2015-01-29 15:41 | 2015-01-29 19:25 | 224 | 11kV | 276189 | 2605 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Zn2602 Clovelly Pnl. 21 tripped on: Earth Fault Right, EFI Left UG cable fault front line feeder from pnl. 21 to S4532 Bligh Clo to S1374 Pine Carr Multiple LV // failures at a result of feeder trip See 1205650 LV //'s 1205655 1205656 1205657 1205658 1205662 1205663 | January | 2015 | 2015Q3 | 2015 | ZN2602:PA21 | ZN36800:PA36 | ZN36800/000036 | WAVERLEY | UG | Not Veg | 2015-01-29 | N | 106.0226 | N | 3 | N | N | 1.1101 | 39.4971 | 201830.775
[7 empty] | 13721 | 12726 | 1205401 | 2015-01-30 00:19 | 2015-01-30 08:00 | 460.75 | 11kV | 5529 | 12 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 150498 B & C phase DOLF : 20 Amp broken x arm 11kV wires down. dq CC1: 22-"Refer to SOp" | January | 2015 | 2015Q3 | 2015 | 511:29876 | 511:29876 | ZN00511/029876 | MAITLAND | OH | Not Veg | 2015-01-30 | N | 460.75 | N | 2 | N | N | 1.1101 | 39.4971 | 4040.4301
[7 empty] | 12726 | 4435 | 1205527 | 2015-01-30 09:11 | 2015-01-30 12:35 | 204 | 11kV | 2244 | 11 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | 30/01/15 10:38 CASS: 1 X HDO OPERATION @ PT#11472 FRC1: 329-"High Voltage Fuse - Requires replacement" Unable to find control room interruption report. See 1206368 GIS 1205527 | January | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-01-30 | N | 204 | N | 2 | N | N | 1.1101 | 39.4971 | 1639.849
[7 empty] | 12945 | 6392 | 1205897 | 2015-01-31 05:07 | 2015-01-31 06:54 | 107 | 11kV | 65512 | 735 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | ZN.398 Dulwich Hill Panel 24 Feeder tripped on:- Relays:- Earth Fault & EFI Signals:- 11kV trip & Zone Earth Field EFI's:- S.1458, S.35032 Abnormal Switching:- S.238 SW/B closed, Defective and Open @ S.2263 SW/B to S.63664 SW/A Cause:- 11kV UG cable fault located between S.35032 SW/B to S.2263 SW/A, S.2263 restored via LV//'s USL.12760 & 24583 - SW/tag left @ S.2263 ME:-1206175 RS:-1206176 Withdrawn:-1205897 | January | 2015 | 2015Q3 | 2015 | ZN398:PA24 | ZN398:PA24 | ZN00398/000024 | INNER WEST | UG | Not Veg | 2015-01-31 | N | 89.132 | N | 4 | N | N | 1.1101 | 39.4971 | 47874.2373
[7 empty] | 14656 | 20158 | 1205914 | 2015-01-31 09:22 | 2015-01-31 10:10 | 48 | 11kV | 96 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 150509 A phase DOLF : 5 Amp HV Fuse carrier burnt up. 5 Amp Fuse fitted instead of 3.15A. Please get correct fuse element installed. | January | 2015 | 2015Q3 | 2015 | 511:29878 | 511:29878 | ZN00511/029878 | MAITLAND | OH | Not Veg | 2015-01-31 | N | 48 | N | 4 | N | N | 1.1101 | 39.4971 | 70.154
[7 empty] | 14504 | 18739 | 1205985 | 2015-01-31 16:40 | 2015-01-31 17:55 | 75 | 11kV | 15750 | 210 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Ex Zn12650 West Gosford section of Panel 1 "the dog trap rd" HV link 43806 bond on road side phase open circuit. See 1206398 exclude 1205985,93 | January | 2015 | 2015Q3 | 2015 | ZN12650:PA1 | ZN12650:PA1 | ZN12650/000001 | CENTRAL COAST | OH | Not Veg | 2015-01-31 | N | 75 | N | 4 | N | N | 1.1101 | 39.4971 | 11509.6355
[7 empty] | 14025 | 15217 | 1206014 | 2015-01-31 19:39 | 2015-01-31 21:01 | 81.7833 | 11kV | 49397.1333 | 604 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 11 Rec1239 Brooklyn Tripped Relays: B and C phase OC Bird bridged wires at pole BR83811 See OMS 1206014 1206021 1206023 1206022 | January | 2015 | 2015Q3 | 2015 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Not Veg | 2015-01-31 | N | 81.7833 | N | 4 | N | N | 1.1101 | 39.4971 | 36097.9681
[7 empty] | 13878 | 13922 | 1206126 | 2015-02-01 20:29 | 2015-02-01 21:55 | 86 | 11kV | 56176 | 1050 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN.15012 Killarney 11kV Panel 8 OCB Feeder tripped on:- Relays:- A phase instantaneous and timed, EFI, Frame leakage, Lockout, Recloser, Timming, Frame leakage Fault Check Field EFI's: Nil Signals:- 11kV trip, Zone Earth Cause:- 11kV fault between ZN.15012 to CP.23766[LK] tee to S.16137, UGOH located at 46 Cook St at Pole FF-88884 surge arrestor operated ME:-1206153 RS:-1206155 Withdrawn:-1206126, 1206128 | February | 2015 | 2015Q3 | 2015 | ZN15012:PA8 | ZN15012:PA8 | ZN15012/000008 | NORTHERN BEACHES | Unknown | Unknown | 2015-02-01 | N | 53.501 | N | 3 | N | N | 1.1101 | 39.4971 | 41051.7639
[7 empty] | 13760 | 12961 | 1206134 | 2015-02-01 23:27 | 2015-02-02 00:59 | 92 | 11kV | 58144 | 632 | HV | Animal Possum | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Zn12640 Umina Pa1 fdr tripped, reclosed, tripped & locked out on Relays: IOC, EF, EFI, Lockout Signals: 11kv trip, 66kv trip OH earth wire from fdr 830 fell into 11kv corner Hillview & Vernon st Umina. Possum found at base of pole. see also 66kv 830 fdr interruption report See 1206134 and 1206412 for the subtransmission entry | February | 2015 | 2015Q3 | 2015 | ZN12640:PA1 | ZN12640:PA1 | ZN12640/000001 | CENTRAL COAST | OH | Not Veg | 2015-02-01 | N | 92 | N | 3 | N | N | 1.1101 | 39.4971 | 42489.9202
[7 empty] | 14461 | 18390 | 1206135 | 2015-02-01 23:29 | 2015-02-02 10:00 | 631 | 11kV | 110795 | 1029 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | @S3922 Drummoyne Panel 17 "S35126 Jersey Barnstaple" fdr tripped on Relays: A phase OC, EFI, Fault Check Signals: 11kv trip, ZE, Tx2 GE Field EFI operated @ S8369 Remarks: UG fault. UG fault between S8369 Cockatoo Island No5 (sw B) & S49979 Lonview Bayville (sw B) | February | 2015 | 2015Q3 | 2015 | ZN3922:PA17 | ZN3922:PA17 | ZN03922/000017 | INNER WEST | UG | Not Veg | 2015-02-01 | N | 107.6725 | N | 3 | N | N | 1.1101 | 39.4971 | 80965.7181
[7 empty] | 13201 | 8443 | 1206157 | 2015-02-02 07:31 | 2015-02-02 10:06 | 155 | 11kV | 2013.7333 | 13 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | PT.11789 The Ridgeway Fagans - 20A footpath phase HDO blown Cause: Flaskover/arcing due to tree bark on bushing ME:-1206976 GIS Model Error:-1206157 Withdrawn:-1206166 | February | 2015 | 2015Q3 | 2015 | ZN12600:PA2 | ZN12600:PA2 | ZN12600/000002 | CENTRAL COAST | OH | Veg | 2015-02-02 | N | 154.9026 | N | 4 | N | N | 1.1101 | 39.4971 | 1471.5769
[7 empty] | 12762 | 4667 | 1206463 | 2015-02-02 15:40 | 2015-02-02 16:35 | 55 | 11kV | 5812.5 | 106 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Section of ZN.18447 Umina 11kV Panel 6 from PT.11482 Albion Springwood to extent of feeder (1 DC) - Footpath phase 31.5A HDO fuse operated Cause:- Fuse fatigue due to age ME:-1206463 GIS Model Error:-1206491 | February | 2015 | 2015Q3 | 2015 | ZN12640:PA6 | ZN12640:PA12 | ZN12640/000012 | CENTRAL COAST | OH | Not Veg | 2015-02-02 | N | 54.8349 | N | 4 | N | N | 1.1101 | 39.4971 | 4247.6036
[7 empty] | 14280 | 17074 | 1206549 | 2015-02-02 18:11 | 2015-02-02 20:30 | 139 | 11kV | 139 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Previous Storm | N | LID 150521 A phase DOLF : 10 Amp Excluded OMS 1206549 | February | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Veg | 2015-02-02 | N | 139 | N | 4 | N | N | 1.1101 | 39.4971 | 101.5771
[7 empty] | 13550 | 11314 | 1206577 | 2015-02-02 20:52 | 2015-02-02 22:02 | 69.7167 | 11kV | 4671.0167 | 67 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | Rain Light | N | LID 150522 B phase DOLF : 20 Amp no cause found | February | 2015 | 2015Q3 | 2015 | 225:13446 | 270:83587 | ZN00270/083587 | LAKE MACQUARIE | OH | Veg | 2015-02-02 | N | 69.7167 | N | 4 | N | N | 1.1101 | 39.4971 | 3413.4412
[7 empty] | 13407 | 10192 | 1206594 | 2015-02-03 05:01 | 2015-02-03 06:01 | 60 | 11kV | 90544 | 1524 | HV | Equipment Failed in Service | Equipment Failure | UGOH | Unplanned | No Weather Impact | N | ZN 10999 Kogarah - Pnl 32 - Trip/reclose/trip, B phase IOC, timing, lockout, Fault Check, EFI, Field EFI. UGOH went short circuit betwee S 10658 to S 10259. ME: 1208951. Rest STep: 1208952. Withdrawn: 1206594, 5, 6. | February | 2015 | 2015Q3 | 2015 | ZN10999:PA32 | ZN10999:PA32 | ZN10999/000032 | BAYSIDE | Unknown | Unknown | 2015-02-03 | N | 59.4121 | N | 4 | N | N | 1.1101 | 39.4971 | 66166.8846
[7 empty] | 12838 | 5406 | 1206685 | 2015-02-03 09:39 | 2015-02-03 11:11 | 92.4667 | 33kV Distribution | 92.4667 | 1 | HV | Equipment Failed in Service | Equipment Failure | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 149526 This sub was found to have a rotation issue and was left off at customers advice as not in use reconnected to network with correct rotation 3/2/15 - no customers interrupted | February | 2015 | 2015Q3 | 2015 |  |  |  | NEWCASTLE | OH | Not Veg | 2015-02-03 | N | 92.4667 | N | 4 | N | N | 1.1101 | 39.4971 | 67.5719
[7 empty] | 14169 | 16272 | 1206750 | 2015-02-03 12:07 | 2015-02-03 19:50 | 463 | 11kV | 36480 | 304 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 150531 1 fault operation A & C phase Overcurrent excluded OMS 1206780,1206750,1206759,1206899 | February | 2015 | 2015Q3 | 2015 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2015-02-03 | N | 120 | N | 4 | N | N | 1.1101 | 39.4971 | 26658.508
[7 empty] | 12649 | 3741 | 1207157 | 2015-02-04 12:44 | 2015-02-04 18:15 | 331 | 11kV | 331 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Fuse | Unplanned | No Weather Impact | N | S 5962 Love NB No.3 - 11kV C phase OQFRN fuse. Fuse operated without cause which tripped off the High voltage in the sub. ME: 1207636. Withdrawn: 1207157. | February | 2015 | 2015Q3 | 2015 | ZN1648:PA2 | ZN4853:PA27 | ZN04853/000027 | STRATHFIELD | OH | Veg | 2015-02-04 | N | 331 | N | 2 | N | N | 1.1101 | 39.4971 | 241.885
[7 empty] | 14215 | 16614 | 1207331 | 2015-02-04 20:52 | 2015-02-04 22:16 | 84 | 11kV | 115836 | 1379 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | Section of ZN.13000 Lake Munmorah 11kV Panel 7 from RE.45061 to the extent of Feeder (28 DC's) tripped on SEF Cause:- @ ABS.43823 on the line side centre phase bond open/burnt off ME:-1207331 | February | 2015 | 2015Q3 | 2015 | ZN13000:PA7 | ZN13000:PA7 | ZN13000/000007 | CENTRAL COAST | OH | Not Veg | 2015-02-04 | N | 84 | N | 2 | N | N | 1.1101 | 39.4971 | 84649.5322
[7 empty] | 14067 | 15561 | 1207360 | 2015-02-05 03:40 | 2015-02-05 04:50 | 70 | 11kV | 28910 | 413 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Lightning | N | ZN.12570 Avoca 11kV Panel 26 feeder tripped on:- Relays:- IOC AB phase & EFI Signals:- See DNMS log Field EFI's:- S.49886, S.14846, S.49472, S.12855, S.14126 (x2) Cause:- Storm Note:- See also ME:-1207382 for interruption on Panel 39 from RE.44855, common point RE.40425 ME:-1207360 Withdrawn:-1207361 | February | 2015 | 2015Q3 | 2015 | ZN12570:PA26 | ZN12570:PA26 | ZN12570/000026 | CENTRAL COAST | OH | Veg | 2015-02-05 | N | 70 | N | 5 | N | N | 1.1101 | 39.4971 | 21126.5753
[7 empty] | 12412 | 1514 | 1207550 | 2015-02-05 13:00 | 2015-02-05 14:39 | 99 | 11kV | 594 | 6 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 150560 Single phase TAPPING BROKEN AT POLE HD-80019 TO SUB 48061. oms# 1207550 | February | 2015 | 2015Q3 | 2015 | 806:82662 | 806:82662 | ZN00806/082662 | UPPER HUNTER | OH | Not Veg | 2015-02-05 | N | 99 | N | 5 | N | N | 1.1101 | 39.4971 | 434.0777
[7 empty] | 14476 | 18522 | 1207571 | 2015-02-05 13:59 | 2015-02-05 17:01 | 182 | 11kV | 282221 | 1935 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | At S2310 Punchbowl Panel 33 "Denman Tucker" feeder tripped on; Earth Leakage EFI Field EFI's: All down to S4693 EFI at S35638 is defective electronic type useless Remarks: UG cable fault in 11kv feeder from S35638 Minnie Benaroon to S1244 Punchbowl Benaroon Sw/A. Subs to investigate defective EFI & maybe fit reliable old style EFI. See interruption on Panel 31 associated due to faulty EFI indication. | February | 2015 | 2015Q3 | 2015 | ZN2310:PA33 | ZN2310:PA15 | ZN02310/000015 | CANTERBURY-BANKSTOWN | UG | Not Veg | 2015-02-05 | N | 145.8506 | N | 5 | N | N | 1.1101 | 39.4971 | 206238.7827
[7 empty] | 12503 | 2298 | 1208325 | 2015-02-05 14:20 | 2015-02-05 17:25 | 185 | 11kV | 555 | 3 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 150564 Isolated for safety reasons Low 11kV OHM new pole installed | February | 2015 | 2015Q3 | 2015 | 216:10724 | 216:10724 | ZN00216/010724 | NEWCASTLE | OH | Not Veg | 2015-02-05 | N | 185 | N | 5 | N | N | 1.1101 | 39.4971 | 405.5776
[7 empty] | 13992 | 14855 | 1207706 | 2015-02-05 22:36 | 2015-02-05 23:25 | 49 | 11kV | 31017 | 633 | HV | Animal Possum | Animal | UGOH | Unplanned | No Weather Impact | N | ZN 9037 Miranda - Pnl 7 - A phase IOC, EFI, Field EFIs. Possum on HV UGOH to S 9907. DOp reports no damage to UGOH. ME: 1207706. Withdrawn: 1207707. | February | 2015 | 2015Q3 | 2015 | ZN9037:PA7 | ZN9037:PA7 | ZN09037/000007 | SUTHERLAND | OH | Not Veg | 2015-02-05 | N | 49 | N | 5 | N | N | 1.1101 | 39.4971 | 22666.3088
[7 empty] | 12759 | 4659 | 1208318 | 2015-02-06 16:56 | 2015-02-06 18:50 | 114 | 11kV | 1278 | 261 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | A blown 11kV HDO fusE WAS FOUND AT pt.15672 - SUSPECT FATIGUE | February | 2015 | 2015Q3 | 2015 | ZN15013:PA10 | ZN15013:PA10 | ZN15013/000010 | NORTHERN BEACHES | OH | Not Veg | 2015-02-06 | N | 4.8966 | N | 3 | N | N | 1.1101 | 39.4971 | 933.9247
[7 empty] | 13259 | 8809 | 1206600 | 2015-02-03 06:25 | 2015-02-06 19:30 | 5105 | 11kV | 702710 | 160 | HV | Equipment Failed in Service | Equipment Failure | U/G Cable | Unplanned | No Weather Impact | N | Submarine/UG cable fault in section of 11kV from CP.24702 to S.16528 failed 0625 hours 3/2/2015 4 dc's were previuosly restored via generators on the afternoon of 4/2/2015. Due to dist laods higher than expected coupled with failed generator cause repeated trips; 72 customers were unable to have power restored until a bigger generator installed and faulty generator repaired 6/2/2015. Contact Morgan Young for more information See OMS 1216517 1216520 1216524 1216523 | February | 2015 | 2015Q3 | 2015 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2015-02-03 | N | 4391.9375 | N | 4 | N | N | 1.1101 | 39.4971 | 513519.7416
[7 empty] | 14517 | 18825 | 1207994 | 2015-02-06 18:50 | 2015-02-06 20:00 | 70 | 11kV | 3990 | 57 | HV | Equipment Failed in Service | Equipment Failure | Cross arm | Unplanned | No Weather Impact | N | LID 150588 emergency interuption to repair cross arm brace at pole OS20179 Excluded OMS 1207994 | February | 2015 | 2015Q3 | 2015 | 232:11457 | 232:33413 | ZN00232/033413 | PORT STEPHENS | OH | Not Veg | 2015-02-06 | N | 70 | N | 3 | N | N | 1.1101 | 39.4971 | 2915.7743
[7 empty] | 12387 | 1282 | 1207965 | 2015-02-06 16:28 | 2015-02-07 00:30 | 482 | 11kV | 119888 | 842 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 150590 1 fault operation C phase Overcurrent; Earth Fault 11kV main down pole FQ-52543. Repaired under AP excluded OMS 1207965 | February | 2015 | 2015Q3 | 2015 | 512:48048 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2015-02-06 | N | 142.3848 | N | 3 | N | N | 1.1101 | 39.4971 | 87610.6143
[7 empty] | 12582 | 3116 | 1208519 | 2015-02-07 14:15 | 2015-02-07 15:35 | 80 | 11kV | 240 | 3 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 150594 broken ll lead at pole 7m-10261 | February | 2015 | 2015Q3 | 2015 | 802:82215 | 802:82215 | ZN00802/082215 | MUSWELLBROOK | OH | Not Veg | 2015-02-07 | N | 80 | N | 1 | N | N | 1.1101 | 39.4971 | 175.3849
[7 empty] | 14539 | 19014 | 1208189 | 2015-02-08 11:49 | 2015-02-08 14:10 | 141 | 11kV | 141 | 1 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | DC-PT Not Transformer | Unplanned | No Weather Impact | N | LID 150599 C phase DOLF : 10 Amp Excluded OMS 1208189 | February | 2015 | 2015Q3 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Veg | 2015-02-08 | N | 141 | N | 1 | N | N | 1.1101 | 39.4971 | 103.0386
[7 empty] | 14245 | 16879 | 1208383 | 2015-02-09 12:00 | 2015-02-09 13:55 | 115 | 11kV | 115 | 1 | HV | Equipment Failed in Service | Equipment Failure | Live Line Tap/Clamp | Unplanned | No Weather Impact | N | LID 150610 live line lead broken off at top of DOLF. Excluded oms report no 1208383. | February | 2015 | 2015Q3 | 2015 | 807:74184 | 807:74184 | ZN00807/074184 | MUSWELLBROOK | OH | Not Veg | 2015-02-09 | N | 115 | N | 2 | N | N | 1.1101 | 39.4971 | 84.0386
[7 empty] | 13759 | 12954 | 1208485 | 2015-02-09 12:49 | 2015-02-09 17:40 | 291 | 11kV | 582 | 2 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | At Zn14891 Wyong ex Pa5 PT12299 Robbinvale Durren No1 16A fuse blown Cause: Fuse Fatigue | February | 2015 | 2015Q3 | 2015 | ZN14891:PA5 | ZN14891:PA5 | ZN14891/000005 | CENTRAL COAST | OH | Not Veg | 2015-02-09 | N | 291 | N | 2 | N | N | 1.1101 | 39.4971 | 425.3084
[7 empty] | 14531 | 18957 | 1208686 | 2015-02-10 02:30 | 2015-02-10 03:13 | 43 | 11kV | 6837 | 159 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | Rain Light | N | LID 150613 A & B phase DOLF : 40 Amp No protection operations. B ph DOLF found burning up. A ph also suspect. Replaced both & left OK. Volts = 242. LH crt amps = 70, 70, 55. RH crt amps = 100, 70, 100. Excluded OMS 1208686. CC1: 22-"Refer to SOp" | February | 2015 | 2015Q3 | 2015 | 202:34250 | 202:34250 | ZN00202/034250 | NEWCASTLE | OH | Not Veg | 2015-02-10 | N | 43 | N | 2 | N | N | 1.1101 | 39.4971 | 4996.2779
[7 empty] | 13495 | 10908 | 1208670 | 2015-02-10 15:50 | 2015-02-10 17:25 | 95 | 11kV | 165040 | 1871 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | ZN 10995 Riverwood - Pnl 2 - CP 30458 Open Circuit. Bond failed at USL 30458, line side of roadside link. ME: 1216836. Withdrawn: 1210920. | February | 2015 | 2015Q3 | 2015 | ZN10995:PA2 | ZN10995:PA2 | ZN10995/000002 | GEORGES RIVER | OH | Not Veg | 2015-02-10 | N | 88.2095 | N | 2 | N | N | 1.1101 | 39.4971 | 120606.3641
[7 empty] | 14010 | 15004 | 1209124 | 2015-02-11 06:57 | 2015-02-11 08:36 | 99 | 11kV | 128497 | 1533 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | At Zn1287 Revesby 11kv Pnl 3 "Mars Virginius" feeder tripped on Relays: C phase IOC, timing, lock out and SEF Signals: 11kv trip and efi Field efis: S5046 Remarks: bond. Footpath phase bond burnt at AB 2371 (towards pnl 3) | February | 2015 | 2015Q3 | 2015 | ZN1287:PA3 | ZN1287:PA3 | ZN01287/000003 | CANTERBURY-BANKSTOWN | OH | Not Veg | 2015-02-11 | N | 83.8206 | N | 3 | N | N | 1.1101 | 39.4971 | 93901.8176
[7 empty] | 13584 | 11581 | 1209108 | 2015-02-11 06:06 | 2015-02-11 08:46 | 160 | 11kV | 105886 | 1179 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | Rain Heavy | N | At S195 Pymble Panel 30 Tripped on Relays: SEL, Fault Check and EFI Signals: 11kV Trip Cause Not ascertained for outage - Mains to Patrol section of 11kV in Gully Near PT1522 - Blaxland Terrace. See OMS 1210114 1210119 1210120 1210121 1210122 1209108/109/144 | February | 2015 | 2015Q3 | 2015 | ZN195:PA30 | ZN195:PA30 | ZN00195/000030 | KU-RING-GAI | OH | Veg | 2015-02-11 | N | 89.81 | N | 3 | N | N | 1.1101 | 39.4971 | 77378.3657
[7 empty] | 13266 | 8895 | 1209480 | 2015-02-11 16:26 | 2015-02-11 18:10 | 104 | 11kV | 8031 | 615 | HV | Animal Goanna | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Section of ZN.3154 St Ives 11kV Panel 16 from RE.1622 to the extent of the feeder (10 DC's):- @ ZN.3154 St Ives:- 33kV Zone Earth, 33kV Tx.3 Earth @ RE.1622:- OC Trip, IOC Trip @ PT.1624 Davidson Park Lookout:- Footpath side 11kV HDO found blown Cause:- Goanna found hanging to the pole next to Tx tank Supply restored via LV//'s and Tx isolated until Goanna can be removed ME:-1209557 RS:-1209558 Withdrawn:-1209480, 1209489, 1209488, 1209483, 1209502 | February | 2015 | 2015Q3 | 2015 | ZN3154:PA16 | ZN3154:PA16 | ZN03154/000016 | KU-RING-GAI | OH | Not Veg | 2015-02-11 | N | 13.0585 | N | 3 | N | N | 1.1101 | 39.4971 | 5868.8179
[7 empty] | 13116 | 7756 | 1209654 | 2015-02-12 09:41 | 2015-02-12 13:16 | 215 | 11kV | 97710 | 1103 | HV | Load Shed - Ausgrid | Load Shed | U/G Cable | Unplanned | No Weather Impact | N | Zn3288 City South 41/42 E feeder was opened for load shedding. 41/42 D & F feeders previously failed at 8:44 #1210132 1210133 Load at S6404 and 3880 was over 1x TX rating - Feeder load was exceeding cable rating 310A @ 335A and increasing. Restored via load restrictions to customers. Restrictions were lifted later that night after repairs. FDR 41/42D #1210133 - FDR 41/42 F #1210132 FDR 42/42E (Outage) - #1210138 1210139 1210140 1210141 | February | 2015 | 2015Q3 | 2015 | ZN3288:PA41 42DEF | ZN3288:PA41 42DEF | ZN03288/41 42DEF | SYDNEY | Exclude | Not Veg | 2015-02-12 | N | 88.5857 | N | 4 | N | N | 1.1101 | 39.4971 | 71403.586
[7 empty] | 12963 | 6527 | 1209975 | 2015-02-12 19:27 | 2015-02-12 20:12 | 45 | 11kV | 14400 | 320 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Rec 428 Bayfield rd Tripped Reclosed tripped and locked out Cause: AB2063 Closed and AB451 Open Branch on mains outaside 16 Smalls Rd - Tree/branch on OH mains Abnormal Switching: AB2063 Closed, AB451 Open 1210070 1209978 1209977 1209976 1209975 | February | 2015 | 2015Q3 | 2015 | ZN35370:PA4 | ZN35370:PA4 | ZN35370/000004 | HORNSBY | OH | Veg | 2015-02-12 | N | 45 | N | 4 | N | N | 1.1101 | 39.4971 | 10523.0953
[7 empty] | 12892 | 5914 | 1209985 | 2015-02-12 20:17 | 2015-02-12 21:40 | 83 | 11kV | 2407 | 29 | HV | Equipment Failed in Service | Equipment Failure | O/H Conductor Bare | Unplanned | No Weather Impact | N | LID 150652 No protection operated, interruption required to fix 11kV steel overhead conductor between poles IQ-21620 and IQ-21625. Several strands of the conductor had failed. | February | 2015 | 2015Q3 | 2015 | 508:82579 | 508:82579 | ZN00508/082579 | PORT STEPHENS | OH | Not Veg | 2015-02-12 | N | 83 | N | 4 | N | N | 1.1101 | 39.4971 | 1758.9646
[7 empty] | 13366 | 9844 | 1210001 | 2015-02-13 00:27 | 2015-02-13 04:00 | 213 | 11kV | 91371 | 494 | HV | Self Clear (No Cause Found) | Self Clearing Trigger | Feeder/Distributor O/H | Unplanned | No Weather Impact | N | At S2635 Epping Panel 32 Tripped Reclosed Tripped and locked out on A and C phase IOC, EFI, Lockout and UF Signals: 11kV Trip Field EFI' Operated at S5190 and S2492 Cause not ascertained for outage See OMS 1216591/592/593/594/595/596 | February | 2015 | 2015Q3 | 2015 | ZN2635:PA32 | ZN2635:PA32 | ZN02635/000032 | RYDE | OH | Veg | 2015-02-13 | N | 184.9615 | N | 4 | N | N | 1.1101 | 39.4971 | 66771.2318
[7 empty] | 12862 | 5648 | 1209983 | 2015-02-12 20:06 | 2015-02-13 09:03 | 777 | 11kV | 7770 | 10 | HV | Equipment Failed in Service | Equipment Failure | Fuse | Unplanned | No Weather Impact | N | Ex Zn14144 Wamberal section of Pa10L @PT61658 High Valley Central Coast Footpath phase 16K HDO failed due to fuse fatigue Excludes OMS 1209923 | February | 2015 | 2015Q3 | 2015 | ZN14144:PA10 | ZN14144:PA10 | ZN14144/000010 | CENTRAL COAST | OH | Not Veg | 2015-02-12 | N | 777 | N | 4 | N | N | 1.1101 | 39.4971 | 5678.0868
[7 empty] | 13873 | 13888 | 1210207 | 2015-02-13 13:08 | 2015-02-13 15:30 | 142 | 11kV | 142 | 1 | HV | Equipment Failed in Service | Equipment Failure | Fuse Assembly | Unplanned | No Weather Impact | N | LID 150667 B phase DOLF : 10 Amp Fuse carrier was all burnt up it appeared to have been full of dust and dirt. Excluded OMS # 1210207. | February | 2015 | 2015Q3 | 2015 | 509:48039 | 509:33395 | ZN00509/033395 | CESSNOCK | OH | Not Veg | 2015-02-13 | N | 142 | N | 4 | N | N | 1.1101 | 39.4971 | 103.7694
[7 empty] | 14344 | 17506 | 1210061 | 2015-02-13 08:43 | 2015-02-13 19:05 | 622 | 11kV | 146990 | 604 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | At Zn2400 Berowra Panel 11 Recloser 1239 Brooklyn Tripped and Lockedout C phase Overcurrent and Earth Fault Tree down outside 76B Brooklyn Rd 5 Bays of HV and LV Overhead down between LB1188 to IS474 tee to PT643 Wharf Rd Brooklyn SRA Notified of supply taken by S1586 Brooklyn Causeway at 1200 Access Permits issued at 1330 to lineworker See OMS 1211188 1211189 1211191 1210061 1210063 1210073 1210118 1210123 1210312 | February | 2015 | 2015Q3 | 2015 | ZN2400:PA11 | ZN2400:PA11 | ZN02400/000011 | HORNSBY | OH | Veg | 2015-02-13 | N | 243.3609 | N | 4 | N | N | 1.1101 | 39.4971 | 107415.9565
[7 empty] | 13292 | 9043 | 1210371 | 2015-02-13 21:25 | 2015-02-14 01:25 | 240 | 11kV | 40820 | 487 | HV | Vegetation Blow/Fall In | Vegetation | O/H Conductor Unknown | Unplanned | No Weather Impact | N | Ex Zn141143 Somersby section of pa17 "Lazzoroni WiseFerry" RE45202 Pacific Ashbrooke feeder tripped, Section og 11kv overhead down between LB61531 to USl65168 on tee to PT61530 See 1210764,5 exclude 1210371,2,4,5,89,91,2 | February | 2015 | 2015Q3 | 2015 | ZN14143:PA17 | ZN14143:PA17 | ZN14143/000017 | CENTRAL COAST | OH | Veg | 2015-02-13 | N | 83.8193 | N | 4 | N | N | 1.1101 | 39.4971 | 29830.052
[7 empty] | 14361 | 17602 | 1210409 | 2015-02-14 04:42 | 2015-02-14 06:21 | 99 | 11kV | 63974 | 824 | HV | Animal Flying Fox | Animal | Insulator | Unplanned | No Weather Impact | N | ZN 9037 Miranda - Pnl 9 - Trip/reclose/trip, C phase Timed OC and IOC, Timing, Lockout, EFI. Bat has damaged insulators at PT 9510. Damaged ages before this outage and there have been several trip and recloses since.. ME: 1212215. Rest Step: 1212216. Withdrawn: 1210409, 10, 35. | February | 2015 | 2015Q3 | 2015 | ZN9037:PA9 | ZN9037:PA9 | ZN09037/000009 | SUTHERLAND | OH | Not Veg | 2015-02-14 | N | 77.6383 | N | 4 | N | N | 1.1101 | 39.4971 | 46750.3123
[7 empty] | 12717 | 4311 | 1210405 | 2015-02-14 03:05 | 2015-02-14 08:40 | 335 | 11kV | 11725 | 35 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | At S16419 Towlers Bay 9 (ex Zn15014 Mona Vale Panel 12) has been isolated and is running off a generator due to cable fault between CP24702 Western Foreshores and S16528 Elvina Bay South See OMS 1211519 1210405 | February | 2015 | 2015Q3 | 2015 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2015-02-14 | N | 335 | N | 4 | N | N | 1.1101 | 39.4971 | 8568.2842
[7 empty] | 13906 | 14173 | 1210403 | 2015-02-14 01:47 | 2015-02-14 09:00 | 433 | 11kV | 21217 | 49 | HV | Equipment Failed in Service | Equipment Failure | Bond | Unplanned | No Weather Impact | N | LID 150673 11kV Tapping burnt off Line Fuse 40438 Excluded oms 1210403 | February | 2015 | 2015Q3 | 2015 | 524:33580 | 524:33580 | ZN00524/033580 | CESSNOCK | OH | Not Veg | 2015-02-14 | N | 433 | N | 4 | N | N | 1.1101 | 39.4971 | 15504.7578
[7 empty] | 12314 | 579 | 1210424 | 2015-02-14 11:00 | 2015-02-14 11:55 | 55 | 11kV | 495 | 9 | HV | Equipment Failed in Service | Equipment Failure | Insulator | Unplanned | No Weather Impact | N | LID 150674 low mains due to broken pin Excluded oms 1210424 | February | 2015 | 2015Q3 | 2015 | 814:82283 | 814:82289 | ZN00814/082289 | UPPER HUNTER | OH | Not Veg | 2015-02-14 | N | 55 | N | 4 | N | N | 1.1101 | 39.4971 | 361.7314
[7 empty] | 13601 | 11723 | 1210556 | 2015-02-15 08:10 | 2015-02-15 09:59 | 109 | 11kV | 92105 | 845 | HV | Animal Bird | Animal | O/H Conductor Unknown | Unplanned | No Weather Impact | N | LID 150676 A & B phase Overcurrent Bird across mains at three way pole FQ-54715 DOP reported lack of clearance at pole and disc blackened PLEASE INVESTIGATE | February | 2015 | 2015Q3 | 2015 | 512:48048 | 512:83741 | ZN00512/083741 | CESSNOCK | OH | Not Veg | 2015-02-15 | N | 109 | N | 6 | N | N | 1.1101 | 39.4971 | 67307.6174
[7 empty] | 13208 | 8467 | 1210613 | 2015-02-15 15:35 | 2015-02-15 16:45 | 70 | 11kV | 2310 | 33 | HV | Equipment Failed in Service | Equipment Failure | DC Not Transformer | Unplanned | No Weather Impact | N | At S16530 Lovett Bay - S16530 Lovett Bay (Ex Zn15014 Mona Vale: Panel 12) has been isolated and is running off a generatordue to UG cable fault between CP24702 Western Foreshores ans S16528 Elvina Bay SOuth See OMS 1211525 1210613 | February | 2015 | 2015Q3 | 2015 | ZN15014:PA12 | ZN15014:PA10 | ZN15014/000010 | NORTHERN BEACHES | UG | Not Veg | 2015-02-15 | N | 70 | N | 6 | N | N | 1.1101 | 39.4971 | 1688.0799